## Cover Page
QUALSERV ENGINEERING LAB TEST REPORT
TITLE: | 2.0 Street side DVT1 and DVT2
EEO# / IEO# | None
EP#:
ENGINEER(S): | Rolando Williams
TECHNICIAN(S): | Brunno Stantos
FILE NAME: | 2.0 Street side DVT1 and DVT2.xlsx
START DATE: | 2022-09-07
FINISH DATE: | 2022-09-14
MODEL#: | 100076760
SERIAL#:
PART#(S): | Charge during ALL tests was 62.36 grams. (2.2oz)
| WRITTEN BY: | Rolando |  |  |  | DATE: | 2022-09-15
| REVISED BY: |  |  |  |  | DATE:
| REVISED BY: | Rolando |  |  |  | DATE: | 2022-09-20
| REVIEWED BY: |  |  |  |  | DATE:
PURPOSE:
RESULTS:
PROCEDURE:
ENGINEER'S COMMENTS & CONCLUSIONS:
EQUIPMENT/ PARTS: | INSTRUMENT | MODEL | ASSET TAG | LAST CALIBRATION DATE | CALIBRATION DUE DATE
| Hoiki Power Meter | PW3360-21 Clam on power logger | PS1001
To evaluate the performance of the DVT1 with new condensing unit configuration per Wonder
See Testing 2.0 Streetside DVT1
Location: I:\REMARKABLE FOODS\2.0 refrigeration cabinets\TEST\DVT1 test 2\DVT1
DVT1
New condensing unit design per request of Wonder. Condensing unit is a semi cicrcle design with 2 fans and using outside ambient for intake air through condenser and exhaust air back to outside. Refrigerant charge and piping has changed from EVT.
T38 compressor oil added using same oil test from EVT. Oil added 0.3oz (8.9CC).
The manufacturer specification for amps on the compressor is 15AMPS. With the rated amps the charge level will be limited
to the operate below the 15amp thresshold. R290 charge is 2.2oz
The Compressor control board also power the both intake and exhuast fans. The intake fan operates with the compressor cycle.
The exhaust fans stays on when power is ON.
See Testing Report Refrigeration 2.0 DVT testing QS
Location: I:\REMARKABLE FOODS\2.0 refrigeration cabinets\TEST\DVT1 test 2\DVT1

## Summary 2
Test | Ambient Temperature (°F) | Maximum High Side Pressure (psig) | Condensing Temperature (°F) | Delta
1 | 85 | 150 | 89.78 | 4.78
2 | 95 | 195 | 108.3 | 13.3
3 | 110 | 230 | 120.8 | 10.8
4 | 105 | 215 | 115.6 | 10.6

## T1
Pull-down 95F System pressures and Temperatures
Fluke DAQ 6.0.4 | [37 empty] | Limits: | Limits:
[31 empty] | Limit | Limit | Limit | Limit |  | Limit | Limit | 10 | 90 | Limit
[23 empty] | Superheat and Sub-Cooling | [7 empty] | 8 | 1 | 8 | 20 |  | 30 | 265 | 90 | 230 | 8
[21 empty] | Saturation Temperature |  | Compressor |  | Evap Outlet SH |  | Evap Outlet SH |  |  |  | System Checks
Duration (H:M:S) | TIME | AMBIENT (°F) | COMP SUMP (°F) | COMP DOME (°F) | COMP DISCHARGE (°F) | COMP SUCTION (°F) | COND OUTLET (°F) | DIST INLET (°F) | LEFT EVAP IN (°F) | LEFT EVAP OUT (°F) | RT EVAP IN (°F) | RIGHT EVAP OUT (°F) | RH (%) | LOW SIDE PRESSURE (psig) | HIGH SIDE PRESSURE (psig) | LEFT PROBE (°F) | RIGHT PROBE (°F) | COND AIR OUT (°F) | System on/Discharge >145 psig | Tsat Suction (°F) | Tsat Discharge (°F) | Suction Superheat (°R) | Discharge Superheat (°R) | Up Left Evap Out SH (°R) | Up Right Evap Out SH (°R) | Condenser Outlet Sub-cooling (°R) | DIST INLET Sub-cooling (°R) | Compression Ratio |  | Condenser Outlet Sub-cooling | Distributor Inlet Sub-cooling | Suction Superheat Check | Discharge Superheat | Sump - Tsat | Sump Temperature | Discharge Temperature | Suction Pressure | Discharge Pressure | Pressure Ratio | Compressor Duty Cycle 1 = ON 0 = OFF
44811.7667 | 0:00 | 95 | 94.1612 | 94.0341 | 93.8175 | 94.0613 | 93.8506 | 93.8506 | 91.9984 | 92.0048 | 89.1489 | 91.3694 | 50 | 159.3681 | 157.9125 | 93.4336 | 92.3625 | 93.8582 | OFF | 92.01 | 92.01 | 2.0513 | 1.8075 | -0.00522 | -0.63535 | -1.8406 | -1.8406 | 0.99164
44811.7668 | 0:00 | 95 | 94.1277 | 93.9686 | 93.7664 | 94.0405 | 93.7895 | 93.7895 | 91.9973 | 92.0164 | 89.1572 | 91.3719 | 50 | 159.4089 | 157.8829 | 93.41 | 92.2803 | 93.7772 | OFF | 92.01 | 92.01 | 2.0305 | 1.7564 | 0.0064 | -0.64447 | -1.7795 | -1.7795 | 0.99124
44811.7669 | 0:00 | 95 | 94.0707 | 93.9104 | 93.6859 | 94.0073 | 93.7168 | 93.7168 | 91.9728 | 92.0091 | 89.183 | 91.3506 | 50 | 159.3935 | 157.9393 | 93.3774 | 92.309 | 93.6955 | OFF | 92.01 | 92.01 | 1.9973 | 1.6759 | -0.00094 | -0.65845 | -1.7068 | -1.7068 | 0.99165
44811.767 | 0:00 | 95 | 94.033 | 93.8603 | 93.6094 | 93.9645 | 93.6578 | 93.6578 | 91.971 | 92.0089 | 89.198 | 91.3384 | 50 | 159.4137 | 157.9205 | 93.395 | 92.3034 | 93.6349 | OFF | 92.01 | 92.01 | 1.9545 | 1.5994 | -0.00113 | -0.67047 | -1.6478 | -1.6478 | 0.99142
44811.7671 | 0:01 | 95 | 94.0064 | 93.8056 | 93.5448 | 93.9454 | 93.5882 | 93.5882 | 91.9557 | 92.0098 | 89.1935 | 91.3329 | 50 | 159.4055 | 157.929 | 93.3135 | 92.3207 | 93.5596 | OFF | 92.01 | 92.01 | 1.9354 | 1.5348 | -0.0002 | -0.67693 | -1.5782 | -1.5782 | 0.99152
44811.7673 | 0:01 | 95 | 93.9586 | 93.7604 | 93.4708 | 93.8989 | 93.5127 | 93.5127 | 91.9463 | 92.0237 | 89.2159 | 91.3222 | 50 | 159.4071 | 157.9452 | 93.2934 | 92.287 | 93.5093 | OFF | 92.01 | 92.01 | 1.8889 | 1.4608 | 0.01366 | -0.70141 | -1.5027 | -1.5027 | 0.9916
44811.7674 | 0:01 | 95 | 93.9049 | 93.7012 | 93.413 | 93.8701 | 93.4657 | 93.4657 | 91.9349 | 92.0054 | 89.2314 | 91.279 | 50 | 159.3857 | 157.956 | 93.3249 | 92.2673 | 93.4627 | OFF | 92.01 | 92.01 | 1.8601 | 1.403 | -0.00464 | -0.72634 | -1.4557 | -1.4557 | 0.99179
44811.7675 | 0:01 | 95 | 93.896 | 93.6559 | 93.3674 | 93.8309 | 93.4144 | 93.4144 | 91.921 | 92.0181 | 89.2174 | 91.2499 | 50 | 159.3924 | 157.9307 | 93.243 | 92.291 | 93.4216 | OFF | 92.01 | 92.01 | 1.8209 | 1.3574 | 0.00813 | -0.76824 | -1.4044 | -1.4044 | 0.9916
44811.7676 | 0:01 | 95 | 93.877 | 93.6267 | 93.3163 | 93.7889 | 93.3632 | 93.3632 | 91.8991 | 92.0054 | 89.2349 | 91.2264 | 50 | 159.4247 | 157.9446 | 93.2063 | 92.0454 | 93.4022 | OFF | 92.01 | 92.01 | 1.7789 | 1.3063 | -0.00458 | -0.77897 | -1.3532 | -1.3532 | 0.9915
44811.7677 | 0:02 | 95 | 93.8283 | 93.5953 | 93.2873 | 93.7518 | 93.3444 | 93.3444 | 91.8703 | 91.9741 | 89.2339 | 91.1595 | 50 | 159.3641 | 157.98 | 93.1872 | 91.944 | 93.3626 | OFF | 92.01 | 92.01 | 1.7418 | 1.2772 | -0.03589 | -0.81456 | -1.3344 | -1.3344 | 0.99205
44811.7678 | 0:02 | 95 | 93.8195 | 93.5761 | 93.2533 | 93.7334 | 93.3191 | 93.3191 | 91.8557 | 91.9815 | 89.2521 | 91.0449 | 50 | 159.3542 | 157.8885 | 93.0899 | 91.9373 | 93.3493 | OFF | 92.01 | 92.01 | 1.7233 | 1.2433 | -0.02853 | -0.93656 | -1.3091 | -1.3091 | 0.99158
44811.768 | 0:02 | 95 | 93.7827 | 93.5288 | 93.2181 | 93.6841 | 93.2877 | 93.2877 | 91.8429 | 91.9564 | 89.2606 | 90.9209 | 50 | 159.3342 | 157.9223 | 93.122 | 91.9079 | 93.3627 | OFF | 92.01 | 92.01 | 1.6741 | 1.2081 | -0.05359 | -1.0355 | -1.2777 | -1.2777 | 0.99189
44811.7681 | 0:02 | 95 | 93.7925 | 93.5132 | 93.2021 | 93.6468 | 93.2535 | 93.2535 | 91.8446 | 91.9431 | 89.2486 | 90.8483 | 50 | 159.2325 | 157.9055 | 93.0811 | 91.8698 | 93.3582 | OFF | 92.01 | 92.01 | 1.6368 | 1.1921 | -0.06689 | -1.0948 | -1.2435 | -1.2435 | 0.99237
44811.7682 | 0:02 | 95 | 93.7566 | 93.5058 | 93.1769 | 93.6059 | 93.2348 | 93.2348 | 91.8163 | 91.9557 | 89.2651 | 90.8022 | 50 | 159.2786 | 157.8029 | 93.0878 | 91.8735 | 93.3511 | OFF | 92.01 | 92.01 | 1.5959 | 1.1669 | -0.05431 | -1.1535 | -1.2248 | -1.2248 | 0.99152
44811.7683 | 0:02 | 95 | 93.7313 | 93.4821 | 93.1615 | 93.5775 | 93.2221 | 93.2221 | 91.7961 | 91.929 | 89.2816 | 90.7402 | 50 | 159.1771 | 157.7994 | 93.0479 | 91.8211 | 93.3523 | OFF | 92.01 | 92.01 | 1.5675 | 1.1515 | -0.08103 | -1.1888 | -1.2121 | -1.2121 | 0.99208
44811.7684 | 0:02 | 95 | 93.7223 | 93.4775 | 93.1421 | 93.5455 | 93.2113 | 93.2113 | 91.798 | 91.9087 | 89.2799 | 90.72 | 50 | 159.1901 | 157.7473 | 93.0789 | 91.8029 | 93.3439 | OFF | 92.01 | 92.01 | 1.5355 | 1.1321 | -0.10128 | -1.1887 | -1.2013 | -1.2013 | 0.9917
44811.7685 | 0:03 | 95 | 93.7212 | 93.4623 | 93.1518 | 93.5274 | 93.214 | 93.214 | 91.7948 | 91.9118 | 89.2899 | 90.6723 | 50 | 159.1913 | 157.7323 | 93.0429 | 91.8315 | 93.3636 | OFF | 92.01 | 92.01 | 1.5174 | 1.1418 | -0.09817 | -1.2395 | -1.204 | -1.204 | 0.99161
44811.7686 | 0:03 | 95 | 93.7106 | 93.4481 | 93.1352 | 93.5055 | 93.2024 | 93.2024 | 91.7759 | 91.8959 | 89.2939 | 90.6596 | 50 | 159.1561 | 157.7226 | 93.0027 | 91.8263 | 93.3725 | OFF | 92.01 | 92.01 | 1.4955 | 1.1252 | -0.11413 | -1.2363 | -1.1924 | -1.1924 | 0.99175
44811.7688 | 0:03 | 95 | 93.6993 | 93.4403 | 93.136 | 93.473 | 93.2068 | 93.2068 | 91.7852 | 91.8858 | 89.3288 | 90.6459 | 50 | 159.1449 | 157.688 | 93.0335 | 91.771 | 93.3626 | OFF | 92.01 | 92.01 | 1.463 | 1.126 | -0.12418 | -1.2399 | -1.1968 | -1.1968 | 0.99162
44811.7689 | 0:03 | 95 | 93.6951 | 93.4311 | 93.1299 | 93.4642 | 93.1876 | 93.1876 | 91.7671 | 91.8865 | 89.3372 | 90.6054 | 50 | 159.1367 | 157.7065 | 93.0211 | 91.7798 | 93.3776 | OFF | 92.01 | 92.01 | 1.4542 | 1.1199 | -0.12353 | -1.2811 | -1.1776 | -1.1776 | 0.99177
44811.769 | 0:03 | 95 | 93.684 | 93.4197 | 93.1275 | 93.4295 | 93.1902 | 93.1902 | 91.7611 | 91.8643 | 89.3772 | 90.5717 | 50 | 159.1573 | 157.6734 | 92.9709 | 91.7782 | 93.3872 | OFF | 92.01 | 92.01 | 1.4195 | 1.1175 | -0.14572 | -1.2926 | -1.1802 | -1.1802 | 0.99146
44811.7691 | 0:04 | 95 | 93.6757 | 93.441 | 93.1421 | 93.4081 | 93.1923 | 93.1923 | 91.7587 | 91.8901 | 89.4127 | 90.5623 | 50 | 159.1313 | 157.6938 | 93.0039 | 91.8128 | 93.3962 | OFF | 92.01 | 92.01 | 1.3981 | 1.1321 | -0.11987 | -1.3278 | -1.1823 | -1.1823 | 0.99173
44811.7692 | 0:04 | 95 | 93.671 | 93.427 | 93.1533 | 93.3825 | 93.1864 | 93.1864 | 91.7551 | 91.8638 | 89.4127 | 90.5327 | 50 | 159.199 | 157.6877 | 93 | 91.7626 | 93.4254 | OFF | 92.01 | 92.01 | 1.3725 | 1.1433 | -0.14624 | -1.3311 | -1.1764 | -1.1764 | 0.99131
44811.7693 | 0:04 | 95 | 93.6707 | 93.424 | 93.1377 | 93.3673 | 93.2052 | 93.2052 | 91.7608 | 91.8649 | 89.434 | 90.5049 | 50 | 159.1853 | 157.6654 | 92.9835 | 91.7344 | 93.4504 | OFF | 92.01 | 92.01 | 1.3573 | 1.1277 | -0.14505 | -1.36 | -1.1952 | -1.1952 | 0.99126
44811.7695 | 0:04 | 95 | 93.6598 | 93.4282 | 93.1449 | 93.3396 | 93.2115 | 93.2115 | 91.7816 | 91.8663 | 89.4487 | 90.5017 | 50 | 159.1473 | 157.7232 | 92.8998 | 91.8024 | 93.4457 | OFF | 92.01 | 92.01 | 1.3296 | 1.1349 | -0.14367 | -1.3646 | -1.2015 | -1.2015 | 0.99181
44811.7696 | 0:04 | 95 | 93.6737 | 93.4276 | 93.135 | 93.3439 | 93.2014 | 93.2014 | 91.7724 | 91.8661 | 89.4794 | 90.4624 | 50 | 159.1806 | 157.7057 | 92.9333 | 91.7703 | 93.4547 | OFF | 92.01 | 92.01 | 1.3339 | 1.1249 | -0.14389 | -1.4037 | -1.1914 | -1.1914 | 0.99152
44811.7697 | 0:04 | 95 | 93.6778 | 93.4358 | 93.1741 | 93.3236 | 93.2235 | 93.2235 | 91.7731 | 91.8601 | 89.521 | 90.4569 | 50 | 159.2237 | 157.6781 | 92.9703 | 91.7556 | 93.4801 | OFF | 92.01 | 92.01 | 1.3136 | 1.1641 | -0.14988 | -1.4032 | -1.2135 | -1.2135 | 0.99111
44811.7698 | 0:04 | 95 | 93.6859 | 93.4547 | 93.1998 | 93.31 | 93.2433 | 93.2433 | 91.7889 | 91.8514 | 89.5342 | 90.4451 | 50 | 159.2334 | 157.7038 | 92.9334 | 91.7298 | 93.517 | OFF | 92.01 | 92.01 | 1.3 | 1.1898 | -0.15855 | -1.4063 | -1.2332 | -1.2332 | 0.99121
44811.7699 | 0:05 | 95 | 93.6878 | 93.4884 | 93.2428 | 93.3155 | 93.2683 | 93.2683 | 91.7715 | 91.8572 | 89.5618 | 90.3971 | 50 | 159.2024 | 157.7446 | 92.9057 | 91.7562 | 93.5783 | OFF | 92.01 | 92.01 | 1.3055 | 1.2328 | -0.15282 | -1.4601 | -1.2583 | -1.2583 | 0.99162
44811.77 | 0:05 | 95 | 93.7511 | 93.5522 | 93.2844 | 93.3099 | 93.3117 | 93.3117 | 91.7902 | 91.8655 | 89.5829 | 90.3956 | 50 | 159.2404 | 157.7312 | 92.951 | 91.7451 | 93.7171 | OFF | 92.01 | 92.01 | 1.2999 | 1.2744 | -0.14448 | -1.4699 | -1.3017 | -1.3017 | 0.99132
44811.7702 | 0:05 | 95 | 93.7888 | 93.6182 | 93.3616 | 93.3297 | 93.3964 | 93.3964 | 91.8004 | 91.8628 | 89.5996 | 90.4061 | 50 | 159.2559 | 157.7945 | 92.8955 | 91.7472 | 93.8574 | OFF | 92.01 | 92.01 | 1.3197 | 1.3516 | -0.14716 | -1.4567 | -1.3864 | -1.3864 | 0.9916
44811.7703 | 0:05 | 95 | 93.8335 | 93.7096 | 93.464 | 93.3311 | 93.5168 | 93.5168 | 91.8011 | 91.861 | 89.6316 | 90.3721 | 50 | 159.2861 | 157.8002 | 92.9302 | 91.7269 | 94.024 | OFF | 92.01 | 92.01 | 1.3211 | 1.454 | -0.14905 | -1.4889 | -1.5068 | -1.5068 | 0.99146
44811.7704 | 0:05 | 95 | 93.886 | 93.7871 | 93.6016 | 93.3662 | 93.6325 | 93.6325 | 91.8118 | 91.8592 | 89.6494 | 90.334 | 50 | 159.3381 | 157.859 | 92.9241 | 91.7356 | 94.165 | OFF | 92.01 | 92.01 | 1.3562 | 1.5916 | -0.15077 | -1.5253 | -1.6225 | -1.6225 | 0.9915
44811.7705 | 0:06 | 95 | 93.9588 | 93.856 | 93.7244 | 93.3758 | 93.7406 | 93.7406 | 91.8109 | 91.8835 | 89.6761 | 90.3223 | 50 | 159.3761 | 157.8603 | 92.8779 | 91.7631 | 94.3015 | OFF | 92.01 | 92.01 | 1.3658 | 1.7144 | -0.12654 | -1.5611 | -1.7306 | -1.7306 | 0.99129
44811.7706 | 0:06 | 95 | 93.9995 | 93.9462 | 93.8007 | 93.3878 | 93.8205 | 93.8205 | 91.8247 | 91.8756 | 89.6785 | 90.3335 | 50 | 159.3623 | 157.9105 | 92.907 | 91.7184 | 94.4166 | OFF | 92.01 | 92.01 | 1.3778 | 1.7907 | -0.13441 | -1.5421 | -1.8105 | -1.8105 | 0.99166
44811.7707 | 0:06 | 95 | 94.0753 | 93.9984 | 93.896 | 93.4175 | 93.9145 | 93.9145 | 91.8321 | 91.879 | 89.7134 | 90.3326 | 50 | 159.3975 | 157.8992 | 92.8605 | 91.7538 | 94.4792 | OFF | 92.01 | 92.01 | 1.4075 | 1.886 | -0.13099 | -1.5464 | -1.9045 | -1.9045 | 0.99139
44811.7708 | 0:06 | 95 | 94.1087 | 94.0595 | 93.9925 | 93.4905 | 93.9942 | 93.9942 | 91.8277 | 91.8737 | 89.7251 | 90.3135 | 50 | 159.382 | 157.9441 | 92.8299 | 91.7372 | 94.5686 | OFF | 92.01 | 92.01 | 1.4805 | 1.9825 | -0.13627 | -1.5602 | -1.9842 | -1.9842 | 0.99174
44811.771 | 0:06 | 95 | 95.7196 | 96.5292 | 97.8779 | 90.332 | 96.2225 | 96.2225 | 91.1193 | 91.8546 | 85.5783 | 84.6721 | 50 | 139.7464 | 171.0843 | 92.8772 | 91.7042 | 96.1955 | OFF | 82.79 | 98.41 | 7.542 | -0.53206 | 9.0646 | -7.1825 | 2.1875 | 2.1875 | 1.2029
44811.7711 | 0:06 | 95 | 101.5687 | 102.7031 | 107.0911 | 87.5423 | 92.4887 | 92.4887 | 81.4238 | 91.6628 | 75.5037 | 84.7469 | 50 | 104.4657 | 157.7894 | 92.7466 | 91.4169 | 101.3396 | OFF | 64.21 | 92.01 | 23.3323 | 15.0811 | 27.4528 | -6.9159 | -0.4787 | -0.4787 | 1.4475
44811.7712 | 0:07 | 95 | 107.6183 | 108.1679 | 110.8844 | 89.2458 | 96.6621 | 96.6621 | 71.7904 | 89.5209 | 71.0992 | 85.1955 | 50 | 107.1733 | 170.4206 | 92.2298 | 91.2043 | 102.7545 | OFF | 67.1 | 98.41 | 22.1458 | 12.4744 | 22.4209 | -4.3254 | 1.7479 | 1.7479 | 1.519
44811.7713 | 0:07 | 95 | 111.748 | 110.827 | 113.8652 | 91.3089 | 99.4169 | 99.4169 | 74.4591 | 85.4336 | 73.0465 | 83.868 | 50 | 113.7874 | 177.2097 | 91.4359 | 90.8704 | 104.9562 | ON | 69.9 | 100.5 | 21.4089 | 13.3652 | 15.5336 | -1.5656 | 1.0831 | 1.0831 | 1.4936 |  | OK | OK | OK | Too Low | 41.848 | OK | OK | High | OK | OK
44811.7714 | 0:07 | 95 | 114.5663 | 113.2832 | 116.8765 | 92.1958 | 101.5867 | 101.5867 | 75.7648 | 82.1492 | 73.5494 | 82.1606 | 50 | 114.5994 | 182.6267 | 90.815 | 90.4992 | 106.7103 | ON | 69.9 | 102.5 | 22.2958 | 14.3765 | 12.2492 | 0.01145 | 0.9133 | 0.9133 | 1.5261 |  | OK | Low Charge | OK | Too Low | 44.6663 | OK | OK | High | OK | OK
44811.7715 | 0:07 | 95 | 116.6607 | 115.2804 | 119.5525 | 92.2438 | 103.1932 | 103.1932 | 75.2474 | 79.346 | 73.8152 | 80.5841 | 50 | 115.0375 | 186.7593 | 90.2792 | 90.2177 | 108.0459 | ON | 72.62 | 104.4 | 19.6238 | 15.1525 | 6.726 | 1.2381 | 1.2068 | 1.2068 | 1.5528 |  | OK | OK | OK | Too Low | 44.0407 | OK | OK | High | OK | OK
44811.7717 | 0:07 | 95 | 118.4309 | 116.9679 | 121.8739 | 92.0522 | 104.378 | 104.378 | 74.5091 | 75.6916 | 73.6315 | 79.2924 | 50 | 114.8566 | 189.6475 | 89.7297 | 89.8398 | 109.0619 | ON | 69.9 | 104.4 | 22.1522 | 17.4739 | 5.7916 | 3.6007 | 0.022 | 0.022 | 1.5773 |  | OK | Low Charge | OK | Too Low | 48.5309 | OK | OK | High | OK | OK
44811.7718 | 0:07 | 95 | 119.8559 | 118.382 | 123.7769 | 91.7624 | 105.2649 | 105.2649 | 73.76 | 72.5084 | 73.31 | 78.2867 | 50 | 114.4008 | 192.0006 | 89.2961 | 89.5504 | 109.7753 | ON | 69.9 | 106.4 | 21.8624 | 17.3769 | 2.6084 | 5.7783 | 1.1351 | 1.1351 | 1.6011 |  | OK | OK | OK | Too Low | 49.9559 | OK | OK | High | OK | OK
44811.7719 | 0:07 | 95 | 121.1429 | 119.6381 | 125.4171 | 91.3361 | 105.9684 | 105.9684 | 73.1862 | 71.5383 | 72.7832 | 77.3897 | 50 | 113.7393 | 193.7677 | 88.9627 | 89.3388 | 110.377 | ON | 69.9 | 106.4 | 21.4361 | 19.0171 | 1.6382 | 5.8514 | 0.4316 | 0.4316 | 1.6231 |  | OK | Low Charge | OK | Too Low | 51.2429 | OK | OK | High | OK | OK
44811.772 | 0:08 | 95 | 122.2269 | 120.6758 | 126.7495 | 90.6819 | 106.5741 | 106.5741 | 72.5829 | 70.86 | 72.2215 | 76.6094 | 50 | 112.6957 | 195.1461 | 88.6184 | 88.9996 | 110.8963 | ON | 69.9 | 108.3 | 20.7819 | 18.4495 | 0.95997 | 5.7494 | 1.7259 | 1.7259 | 1.6472 |  | OK | OK | OK | Too Low | 52.3269 | OK | OK | High | OK | OK
44811.7721 | 0:08 | 95 | 123.0767 | 121.551 | 127.7885 | 90.0123 | 107.0217 | 107.0217 | 72.0069 | 70.2917 | 71.6734 | 75.9001 | 50 | 111.7819 | 196.2738 | 88.2239 | 88.7912 | 111.2572 | ON | 69.9 | 108.3 | 20.1123 | 19.4885 | 0.39169 | 5.6084 | 1.2783 | 1.2783 | 1.668 |  | OK | OK | OK | Too Low | 53.1767 | OK | OK | High | OK | OK
44811.7722 | 0:08 | 95 | 123.801 | 122.2922 | 128.7145 | 89.6427 | 107.338 | 107.338 | 71.4994 | 69.7819 | 71.1923 | 75.2856 | 50 | 111.0006 | 197.2004 | 88.0155 | 88.5062 | 111.5231 | ON | 69.9 | 108.3 | 19.7427 | 20.4145 | -0.11812 | 5.5037 | 0.962 | 0.962 | 1.6858 |  | OK | Low Charge | OK | OK | 53.901 | OK | OK | High | OK | OK
44811.7724 | 0:08 | 95 | 124.4039 | 122.8814 | 129.5226 | 89.4511 | 107.6926 | 107.6926 | 70.9259 | 69.2364 | 70.6413 | 74.6576 | 50 | 110.0315 | 198.0131 | 87.6439 | 88.1977 | 111.7822 | ON | 69.9 | 108.3 | 19.5511 | 21.2226 | -0.66364 | 5.4212 | 0.6074 | 0.6074 | 1.7054 |  | OK | Low Charge | OK | OK | 54.5039 | OK | OK | High | OK | OK
44811.7725 | 0:08 | 95 | 124.9839 | 123.4584 | 130.2619 | 89.3945 | 107.968 | 107.968 | 70.4143 | 68.764 | 70.1669 | 74.0983 | 50 | 109.2221 | 198.8006 | 87.1869 | 88.0029 | 112.0132 | ON | 67.1 | 108.3 | 22.2945 | 21.9619 | 1.664 | 5.3343 | 0.332 | 0.332 | 1.7229 |  | OK | Low Charge | OK | OK | 57.8839 | OK | OK | High | OK | OK
44811.7726 | 0:08 | 95 | 125.4461 | 123.87 | 130.888 | 89.4666 | 108.0877 | 108.0877 | 69.8841 | 68.2495 | 69.6601 | 73.5479 | 50 | 108.3792 | 199.17 | 86.8602 | 87.7639 | 112.1151 | ON | 67.1 | 108.3 | 22.3666 | 22.588 | 1.1495 | 5.2983 | 0.2123 | 0.2123 | 1.7377 |  | OK | Low Charge | OK | OK | 58.3461 | OK | OK | High | OK | OK
44811.7727 | 0:09 | 95 | 125.8961 | 124.3394 | 131.4627 | 89.5729 | 108.2796 | 108.2796 | 69.3747 | 67.8051 | 69.2046 | 73.0411 | 50 | 107.4676 | 199.4498 | 86.7427 | 87.5857 | 112.2357 | ON | 67.1 | 108.3 | 22.4729 | 23.1627 | 0.70515 | 5.2359 | 0.0204 | 0.0204 | 1.7529 |  | OK | Low Charge | OK | OK | 58.7961 | OK | OK | High | OK | OK
44811.7728 | 0:09 | 95 | 126.2846 | 124.7219 | 131.9915 | 89.6139 | 108.4512 | 108.4512 | 68.8749 | 67.3474 | 68.7266 | 72.5864 | 50 | 106.7432 | 200.0942 | 86.4321 | 87.3069 | 112.3224 | ON | 67.1 | 110.2 | 22.5139 | 21.7915 | 0.24739 | 5.239 | 1.7488 | 1.7488 | 1.7687 |  | OK | OK | OK | OK | 59.1846 | OK | OK | High | OK | OK
44811.7729 | 0:09 | 95 | 126.6 | 125.0668 | 132.5256 | 89.6555 | 108.5307 | 108.5307 | 68.3939 | 66.9069 | 68.2896 | 72.089 | 50 | 106.0556 | 200.1984 | 86.1453 | 86.995 | 112.3681 | ON | 67.1 | 110.2 | 22.5555 | 22.3256 | -0.19306 | 5.1821 | 1.6693 | 1.6693 | 1.7796 |  | OK | OK | OK | OK | 59.5 | OK | OK | High | OK | OK
44811.773 | 0:09 | 95 | 126.922 | 125.3706 | 132.9647 | 89.7339 | 108.589 | 108.589 | 67.8955 | 66.4417 | 67.8369 | 71.6179 | 50 | 105.2645 | 200.5101 | 85.8592 | 86.7228 | 112.3853 | ON | 67.1 | 110.2 | 22.6339 | 22.7647 | -0.65827 | 5.1762 | 1.611 | 1.611 | 1.7939 |  | OK | OK | OK | OK | 59.822 | OK | OK | High | OK | OK
44811.7732 | 0:09 | 95 | 127.1985 | 125.6568 | 133.3645 | 89.8166 | 108.7124 | 108.7124 | 67.4379 | 66.0166 | 67.394 | 71.1758 | 50 | 104.5379 | 200.6062 | 85.5685 | 86.535 | 112.4155 | ON | 64.21 | 110.2 | 25.6066 | 23.1645 | 1.8066 | 5.1592 | 1.4876 | 1.4876 | 1.8057 |  | OK | OK | OK | OK | 62.9885 | OK | OK | High | OK | OK
44811.7733 | 0:09 | 95 | 127.4803 | 125.927 | 133.776 | 89.8796 | 108.7595 | 108.7595 | 66.9262 | 65.5278 | 66.905 | 70.7205 | 50 | 103.6499 | 200.8163 | 85.0868 | 86.2369 | 112.4317 | ON | 64.21 | 110.2 | 25.6696 | 23.576 | 1.3178 | 5.1927 | 1.4405 | 1.4405 | 1.821 |  | OK | OK | OK | OK | 63.2703 | OK | OK | High | OK | OK
44811.7734 | 0:10 | 95 | 127.7004 | 126.1506 | 134.1349 | 89.9085 | 108.7908 | 108.7908 | 66.4482 | 65.104 | 66.4694 | 70.3151 | 50 | 102.9299 | 200.8884 | 84.9926 | 86.0567 | 112.4351 | ON | 64.21 | 110.2 | 25.6985 | 23.9349 | 0.89403 | 5.2111 | 1.4092 | 1.4092 | 1.8328 |  | OK | OK | OK | OK | 63.4904 | OK | OK | High | OK | OK
44811.7735 | 0:10 | 95 | 127.9411 | 126.4053 | 134.4809 | 89.9647 | 108.9422 | 108.9422 | 66.0175 | 64.6692 | 66.0931 | 69.8881 | 50 | 102.2165 | 201.3144 | 84.667 | 85.7663 | 112.4949 | ON | 64.21 | 110.2 | 25.7547 | 24.2809 | 0.45922 | 5.2189 | 1.2578 | 1.2578 | 1.8476 |  | OK | OK | OK | OK | 63.7311 | OK | OK | High | OK | OK
44811.7736 | 0:10 | 95 | 128.1283 | 126.5896 | 134.7933 | 89.9394 | 108.9363 | 108.9363 | 65.5333 | 64.3093 | 65.6464 | 69.514 | 50 | 101.4422 | 201.3042 | 84.3881 | 85.509 | 112.4745 | ON | 64.21 | 110.2 | 25.7294 | 24.5933 | 0.09935 | 5.2047 | 1.2637 | 1.2637 | 1.8598 |  | OK | OK | OK | OK | 63.9183 | OK | OK | High | OK | OK
44811.7737 | 0:10 | 95 | 128.3074 | 126.7538 | 135.0543 | 90.0164 | 108.933 | 108.933 | 65.0596 | 63.891 | 65.2344 | 69.1015 | 50 | 100.698 | 201.3861 | 84.0406 | 85.3322 | 112.4328 | ON | 64.21 | 110.2 | 25.8064 | 24.8543 | -0.31896 | 5.2105 | 1.267 | 1.267 | 1.8725 |  | OK | OK | OK | OK | 64.0974 | OK | OK | High | OK | OK
44811.7739 | 0:10 | 95 | 128.4659 | 126.9445 | 135.3624 | 90.0535 | 108.9392 | 108.9392 | 64.5993 | 63.4989 | 64.8031 | 68.6981 | 50 | 100.0155 | 201.2106 | 83.7966 | 84.993 | 112.3896 | ON | 64.21 | 110.2 | 25.8435 | 25.1624 | -0.71111 | 5.1992 | 1.2608 | 1.2608 | 1.8821 |  | OK | OK | OK | OK | 64.2559 | OK | OK | High | OK | OK
44811.774 | 0:10 | 95 | 128.6287 | 127.1479 | 135.656 | 90.0995 | 108.9654 | 108.9654 | 64.1637 | 63.1611 | 64.3903 | 68.3218 | 50 | 99.2993 | 201.3676 | 83.5249 | 84.8209 | 112.3971 | ON | 61.23 | 110.2 | 28.8695 | 25.456 | 1.9311 | 5.1608 | 1.2346 | 1.2346 | 1.8953 |  | OK | OK | OK | OK | 67.3987 | OK | OK | High | OK | OK
44811.7741 | 0:11 | 95 | 128.8247 | 127.2842 | 135.9065 | 90.1053 | 108.9623 | 108.9623 | 63.7516 | 62.7473 | 64.0159 | 67.93 | 50 | 98.593 | 201.3324 | 83.2348 | 84.6371 | 112.3728 | ON | 61.23 | 110.2 | 28.8753 | 25.7065 | 1.5173 | 5.1827 | 1.2377 | 1.2377 | 1.9068 |  | OK | OK | OK | OK | 67.5947 | OK | OK | High | OK | OK
44811.7742 | 0:11 | 95 | 128.9822 | 127.462 | 136.1738 | 90.1377 | 109.0414 | 109.0414 | 63.3363 | 62.3705 | 63.6095 | 67.5747 | 50 | 98.0169 | 201.5008 | 83.024 | 84.2311 | 112.3766 | ON | 61.23 | 110.2 | 28.9077 | 25.9738 | 1.1405 | 5.2042 | 1.1586 | 1.1586 | 1.9181 |  | OK | OK | OK | OK | 67.7522 | OK | OK | High | OK | OK
44811.7743 | 0:11 | 95 | 129.1224 | 127.6074 | 136.419 | 90.185 | 109.0543 | 109.0543 | 62.9355 | 62.0371 | 63.2362 | 67.2161 | 50 | 97.431 | 201.5166 | 82.7124 | 84.0445 | 112.3645 | ON | 61.23 | 110.2 | 28.955 | 26.219 | 0.80705 | 5.1791 | 1.1457 | 1.1457 | 1.9282 |  | OK | OK | OK | OK | 67.8924 | OK | OK | High | OK | OK
44811.7744 | 0:11 | 95 | 129.2675 | 127.7376 | 136.6367 | 90.1092 | 109.0844 | 109.0844 | 62.515 | 61.8353 | 62.8758 | 66.8637 | 50 | 96.7861 | 201.7709 | 82.3707 | 83.7953 | 112.3539 | ON | 61.23 | 110.2 | 28.8792 | 26.4367 | 0.60534 | 5.0283 | 1.1156 | 1.1156 | 1.9417 |  | OK | OK | OK | OK | 68.0375 | OK | OK | High | OK | OK
44811.7746 | 0:11 | 95 | 129.4115 | 127.8809 | 136.8216 | 90.0749 | 109.0413 | 109.0413 | 62.1292 | 61.4995 | 62.513 | 66.5021 | 50 | 96.2427 | 201.562 | 82.1932 | 83.6161 | 112.3088 | ON | 61.23 | 110.2 | 28.8449 | 26.6216 | 0.26946 | 5.0027 | 1.1587 | 1.1587 | 1.9493 |  | OK | OK | OK | OK | 68.1815 | OK | OK | High | OK | OK
44811.7747 | 0:11 | 95 | 129.5426 | 128.0113 | 137.0359 | 90.065 | 109.108 | 109.108 | 61.8166 | 61.3385 | 62.1641 | 66.1567 | 50 | 95.63 | 201.7709 | 81.9147 | 83.3264 | 112.3058 | ON | 61.23 | 110.2 | 28.835 | 26.8359 | 0.10852 | 4.8182 | 1.092 | 1.092 | 1.962 |  | OK | OK | OK | OK | 68.3126 | OK | OK | High | OK | OK
44811.7748 | 0:12 | 95 | 129.6275 | 128.1674 | 137.2379 | 90.025 | 109.1115 | 109.1115 | 61.4877 | 61.2244 | 61.8182 | 65.8544 | 50 | 95.1431 | 201.6473 | 81.6448 | 83.1491 | 112.3138 | ON | 61.23 | 110.2 | 28.795 | 27.0379 | -0.00565 | 4.63 | 1.0885 | 1.0885 | 1.9696 |  | OK | OK | OK | OK | 68.3975 | OK | OK | High | OK | OK
44811.7749 | 0:12 | 95 | 129.7879 | 128.2379 | 137.4552 | 90.0219 | 109.166 | 109.166 | 61.1647 | 61.084 | 61.5065 | 65.5548 | 50 | 94.5684 | 201.8938 | 81.3381 | 82.9031 | 112.3347 | ON | 58.13 | 110.2 | 31.8919 | 27.2552 | 2.954 | 4.4707 | 1.034 | 1.034 | 1.9822 |  | OK | OK | OK | OK | 71.6579 | OK | OK | High | OK | OK
44811.775 | 0:12 | 95 | 129.8896 | 128.3929 | 137.663 | 90.0008 | 109.2252 | 109.2252 | 60.8426 | 60.6607 | 61.1869 | 65.284 | 50 | 94.0948 | 202.0055 | 80.8678 | 82.6791 | 112.382 | ON | 58.13 | 110.2 | 31.8708 | 27.463 | 2.5307 | 4.6232 | 0.9748 | 0.9748 | 1.9919 |  | OK | Low Charge | OK | OK | 71.7596 | OK | OK | High | OK | OK
44811.7751 | 0:12 | 95 | 129.9848 | 128.5305 | 137.8471 | 89.9492 | 109.2451 | 109.2451 | 60.5496 | 60.7056 | 60.896 | 65.0054 | 50 | 93.6459 | 202.0976 | 80.7346 | 82.4132 | 112.3561 | ON | 58.13 | 110.2 | 31.8192 | 27.6471 | 2.5756 | 4.2998 | 0.9549 | 0.9549 | 2.001 |  | OK | Low Charge | OK | OK | 71.8548 | OK | OK | High | OK | OK
44811.7752 | 0:12 | 95 | 130.1151 | 128.6096 | 138.0084 | 89.9111 | 109.2875 | 109.2875 | 60.2332 | 60.6318 | 60.5853 | 64.732 | 50 | 93.2562 | 202.1148 | 80.4438 | 82.2176 | 112.3739 | ON | 58.13 | 110.2 | 31.7811 | 27.8084 | 2.5018 | 4.1002 | 0.9125 | 0.9125 | 2.0084 |  | OK | Low Charge | OK | OK | 71.9851 | OK | OK | High | OK | OK
44811.7754 | 0:12 | 95 | 130.2069 | 128.7379 | 138.1688 | 89.8895 | 109.215 | 109.215 | 59.9823 | 60.291 | 60.2876 | 64.4458 | 50 | 92.6918 | 202.0064 | 80.3048 | 81.9804 | 112.3085 | ON | 58.13 | 110.2 | 31.7595 | 27.9688 | 2.161 | 4.1548 | 0.985 | 0.985 | 2.0179 |  | OK | Low Charge | OK | OK | 72.0769 | OK | OK | High | OK | OK
44811.7755 | 0:13 | 95 | 130.2722 | 128.7913 | 138.2464 | 89.894 | 109.2029 | 109.2029 | 59.6741 | 60.2561 | 60.0051 | 64.1962 | 50 | 92.254 | 201.8955 | 80.0381 | 81.7341 | 112.3127 | ON | 58.13 | 110.2 | 31.764 | 28.0464 | 2.1261 | 3.9401 | 0.9971 | 0.9971 | 2.0251 |  | OK | Low Charge | OK | OK | 72.1422 | OK | OK | High | OK | OK
44811.7756 | 0:13 | 95 | 130.3667 | 128.8723 | 138.4167 | 89.8273 | 109.2139 | 109.2139 | 59.4126 | 59.9612 | 59.7022 | 63.946 | 50 | 91.8626 | 202.1044 | 79.7342 | 81.5981 | 112.2728 | ON | 58.13 | 110.2 | 31.6973 | 28.2167 | 1.8312 | 3.9848 | 0.9861 | 0.9861 | 2.0345 |  | OK | Low Charge | OK | OK | 72.2367 | OK | OK | High | OK | OK
44811.7757 | 0:13 | 95 | 130.4518 | 128.9781 | 138.5581 | 89.7839 | 109.3081 | 109.3081 | 59.1514 | 59.7885 | 59.444 | 63.7115 | 50 | 91.3849 | 202.2507 | 79.4855 | 81.3231 | 112.3086 | ON | 58.13 | 110.2 | 31.6539 | 28.3581 | 1.6585 | 3.9231 | 0.8919 | 0.8919 | 2.0451 |  | OK | Low Charge | OK | OK | 72.3218 | OK | OK | High | OK | OK
44811.7758 | 0:13 | 95 | 130.5168 | 129.041 | 138.7014 | 89.7399 | 109.368 | 109.368 | 58.894 | 59.5564 | 59.1979 | 63.4796 | 50 | 90.9296 | 202.4714 | 79.4555 | 81.0606 | 112.3625 | ON | 58.13 | 110.2 | 31.6099 | 28.5014 | 1.4264 | 3.9232 | 0.832 | 0.832 | 2.056 |  | OK | Low Charge | OK | OK | 72.3868 | OK | OK | High | OK | OK
44811.7759 | 0:13 | 95 | 130.5748 | 129.1453 | 138.8292 | 89.7226 | 109.3279 | 109.3279 | 58.6031 | 59.4886 | 58.9134 | 63.2075 | 50 | 90.6599 | 202.194 | 79.0874 | 80.8323 | 112.2977 | ON | 58.13 | 110.2 | 31.5926 | 28.6292 | 1.3586 | 3.7189 | 0.8721 | 0.8721 | 2.0586 |  | OK | Low Charge | OK | OK | 72.4448 | OK | OK | High | OK | OK
44811.7761 | 0:13 | 95 | 130.6208 | 129.2133 | 138.9337 | 89.6897 | 109.2883 | 109.2883 | 58.3525 | 59.3193 | 58.6379 | 62.9691 | 50 | 90.2046 | 202.2267 | 78.8592 | 80.6525 | 112.2371 | ON | 58.13 | 110.2 | 31.5597 | 28.7337 | 1.1893 | 3.6498 | 0.9117 | 0.9117 | 2.0678 |  | OK | Low Charge | OK | OK | 72.4908 | OK | OK | High | OK | OK
44811.7762 | 0:14 | 95 | 130.7085 | 129.2703 | 139.0638 | 89.6857 | 109.3062 | 109.3062 | 58.1062 | 58.9976 | 58.4144 | 62.7581 | 50 | 89.8629 | 202.1897 | 78.5172 | 80.3106 | 112.2364 | ON | 54.95 | 110.2 | 34.7358 | 28.8638 | 4.0476 | 3.7605 | 0.8938 | 0.8938 | 2.0743 |  | OK | Low Charge | OK | OK | 75.7585 | OK | OK | OK | OK | OK
44811.7763 | 0:14 | 95 | 130.7917 | 129.383 | 139.1945 | 89.6028 | 109.3784 | 109.3784 | 57.8909 | 58.8528 | 58.1686 | 62.5421 | 50 | 89.4047 | 202.4901 | 78.4732 | 80.1565 | 112.2829 | ON | 54.95 | 110.2 | 34.6528 | 28.9945 | 3.9028 | 3.6893 | 0.8216 | 0.8216 | 2.0863 |  | OK | Low Charge | OK | OK | 75.8417 | OK | OK | OK | OK | OK
44811.7764 | 0:14 | 95 | 130.8554 | 129.3887 | 139.2986 | 89.5346 | 109.3951 | 109.3951 | 57.6502 | 58.8125 | 57.9572 | 62.3403 | 50 | 89.18 | 202.4797 | 78.1415 | 79.868 | 112.297 | ON | 54.95 | 110.2 | 34.5846 | 29.0986 | 3.8625 | 3.5278 | 0.8049 | 0.8049 | 2.0907 |  | OK | Low Charge | OK | OK | 75.9054 | OK | OK | OK | OK | OK
44811.7765 | 0:14 | 95 | 130.9089 | 129.4779 | 139.3833 | 89.4566 | 109.3908 | 109.3908 | 57.413 | 58.7098 | 57.6838 | 62.1227 | 50 | 88.7918 | 202.5079 | 77.9631 | 79.7131 | 112.2945 | ON | 54.95 | 110.2 | 34.5067 | 29.1833 | 3.7598 | 3.4129 | 0.8092 | 0.8092 | 2.0988 |  | OK | Low Charge | OK | OK | 75.9589 | OK | OK | OK | OK | OK
44811.7766 | 0:14 | 95 | 130.9569 | 129.5579 | 139.5045 | 89.3849 | 109.4088 | 109.4088 | 57.1754 | 58.5724 | 57.4705 | 61.9114 | 50 | 88.4513 | 202.6853 | 77.5711 | 79.5458 | 112.3017 | ON | 54.95 | 110.2 | 34.4349 | 29.3045 | 3.6224 | 3.339 | 0.7912 | 0.7912 | 2.1074 |  | OK | Low Charge | OK | OK | 76.0069 | OK | OK | OK | OK | OK
44811.7768 | 0:14 | 95 | 131.0274 | 129.5998 | 139.576 | 89.4096 | 109.4537 | 109.4537 | 56.9455 | 58.3841 | 57.2502 | 61.7227 | 50 | 88.0098 | 202.6031 | 77.4817 | 79.2533 | 112.2878 | ON | 54.95 | 110.2 | 34.4596 | 29.376 | 3.4341 | 3.3386 | 0.7463 | 0.7463 | 2.1157 |  | OK | Low Charge | OK | OK | 76.0774 | OK | OK | OK | OK | OK
44811.7769 | 0:15 | 95 | 131.1164 | 129.6502 | 139.7122 | 89.4318 | 109.5055 | 109.5055 | 56.749 | 58.1792 | 57.0486 | 61.5041 | 50 | 87.7286 | 202.7343 | 77.2723 | 79.0801 | 112.3374 | ON | 54.95 | 110.2 | 34.4818 | 29.5122 | 3.2292 | 3.3249 | 0.6945 | 0.6945 | 2.1228 |  | OK | Low Charge | OK | OK | 76.1664 | OK | OK | OK | OK | OK
44811.777 | 0:15 | 95 | 131.2211 | 129.7561 | 139.8479 | 89.398 | 109.6547 | 109.6547 | 56.5758 | 58.1152 | 56.8422 | 61.2978 | 50 | 87.4944 | 203.334 | 77.1559 | 78.8426 | 112.4724 | ON | 54.95 | 110.2 | 34.448 | 29.6479 | 3.1652 | 3.1826 | 0.5453 | 0.5453 | 2.1335 |  | OK | Low Charge | OK | OK | 76.2711 | OK | OK | OK | OK | OK
44811.7771 | 0:15 | 95 | 131.3881 | 129.9463 | 140.042 | 89.4408 | 109.8207 | 109.8207 | 56.3562 | 58.0391 | 56.6288 | 61.0613 | 50 | 87.2075 | 203.7614 | 76.9671 | 78.6402 | 112.5926 | ON | 54.95 | 110.2 | 34.4908 | 29.842 | 3.0891 | 3.0222 | 0.3793 | 0.3793 | 2.1437 |  | OK | Low Charge | OK | OK | 76.4381 | OK | OK | OK | OK | OK
44811.7772 | 0:15 | 95 | 131.5407 | 130.1149 | 140.22 | 89.5196 | 110.0141 | 110.0141 | 56.1888 | 57.9735 | 56.4435 | 60.817 | 50 | 86.9813 | 204.1991 | 76.5652 | 78.4841 | 112.7371 | ON | 54.95 | 110.2 | 34.5697 | 30.02 | 3.0235 | 2.8435 | 0.1859 | 0.1859 | 2.1528 |  | OK | Low Charge | OK | OK | 76.5907 | OK | OK | OK | OK | OK
44811.7773 | 0:15 | 95 | 131.723 | 130.2321 | 140.4078 | 89.6267 | 110.1579 | 110.1579 | 55.9856 | 57.9275 | 56.2472 | 60.6067 | 50 | 86.7354 | 204.5481 | 76.2535 | 78.2007 | 112.8592 | ON | 54.95 | 110.2 | 34.6767 | 30.2078 | 2.9775 | 2.6791 | 0.0421 | 0.0421 | 2.1615 |  | OK | Low Charge | OK | OK | 76.773 | OK | OK | OK | OK | OK
44811.7774 | 0:16 | 95 | 131.8651 | 130.4104 | 140.6034 | 89.7255 | 110.2386 | 110.2386 | 55.8144 | 57.8564 | 56.0622 | 60.4043 | 50 | 86.4023 | 204.7226 | 76.2823 | 77.9881 | 112.9297 | ON | 54.95 | 110.2 | 34.7755 | 30.4034 | 2.9064 | 2.5479 | -0.0386 | -0.0386 | 2.1703 |  | OK | Low Charge | OK | OK | 76.9151 | OK | OK | OK | OK | OK
44811.7776 | 0:16 | 95 | 132.0349 | 130.5743 | 140.8241 | 89.9212 | 110.3643 | 110.3643 | 55.6061 | 57.7633 | 55.83 | 60.1962 | 50 | 86.0442 | 205.2661 | 75.9689 | 77.8944 | 113.0591 | ON | 54.95 | 112 | 34.9712 | 28.8241 | 2.8133 | 2.4329 | 1.6357 | 1.6357 | 2.1834 |  | OK | OK | OK | OK | 77.0849 | OK | OK | OK | OK | OK
44811.7777 | 0:16 | 95 | 132.1831 | 130.7764 | 141.0391 | 90.0666 | 110.5064 | 110.5064 | 55.4404 | 57.6653 | 55.6336 | 59.9853 | 50 | 85.7793 | 205.5735 | 75.7037 | 77.6599 | 113.1449 | ON | 54.95 | 112 | 35.1166 | 29.0391 | 2.7153 | 2.32 | 1.4936 | 1.4936 | 2.1922 |  | OK | OK | OK | OK | 77.2331 | OK | OK | OK | OK | OK
44811.7778 | 0:16 | 95 | 132.3774 | 130.9279 | 141.263 | 90.1908 | 110.5119 | 110.5119 | 55.283 | 57.5665 | 55.4439 | 59.7995 | 50 | 85.5885 | 205.7625 | 75.5548 | 77.4499 | 113.1591 | ON | 54.95 | 112 | 35.2408 | 29.263 | 2.6164 | 2.233 | 1.4881 | 1.4881 | 2.1983 |  | OK | OK | OK | OK | 77.4274 | OK | OK | OK | OK | OK
44811.7779 | 0:16 | 95 | 132.4688 | 131.0441 | 141.3843 | 90.268 | 110.5409 | 110.5409 | 55.1337 | 57.4681 | 55.2993 | 59.644 | 50 | 85.3472 | 205.5724 | 75.3353 | 77.1494 | 113.1641 | ON | 54.95 | 112 | 35.318 | 29.3843 | 2.5181 | 2.1759 | 1.4591 | 1.4591 | 2.2017 |  | OK | OK | OK | OK | 77.5188 | OK | OK | OK | OK | OK
44811.778 | 0:16 | 95 | 132.6373 | 131.161 | 141.6166 | 90.3619 | 110.6325 | 110.6325 | 54.9626 | 57.3396 | 55.1174 | 59.4768 | 50 | 85.0684 | 206.088 | 75.1466 | 77.0934 | 113.2456 | ON | 54.95 | 112 | 35.4119 | 29.6166 | 2.3896 | 2.1372 | 1.3675 | 1.3675 | 2.213 |  | OK | OK | OK | OK | 77.6873 | OK | OK | OK | OK | OK
44811.7781 | 0:16 | 95 | 132.7744 | 131.3187 | 141.7743 | 90.454 | 110.6811 | 110.6811 | 54.8007 | 57.1598 | 54.9522 | 59.3285 | 50 | 84.7404 | 206.1325 | 74.9587 | 76.7545 | 113.265 | ON | 51.63 | 112 | 38.824 | 29.7743 | 5.5298 | 2.1687 | 1.3189 | 1.3189 | 2.2208 |  | OK | OK | OK | OK | 81.1444 | OK | OK | OK | OK | OK
44811.7783 | 0:17 | 95 | 132.8745 | 131.4297 | 141.953 | 90.5154 | 110.6894 | 110.6894 | 54.6281 | 57.031 | 54.7684 | 59.1324 | 50 | 84.5645 | 205.9424 | 74.8289 | 76.6291 | 113.2542 | ON | 51.63 | 112 | 38.8854 | 29.953 | 5.401 | 2.1015 | 1.3106 | 1.3106 | 2.2228 |  | OK | OK | OK | OK | 81.2445 | OK | OK | OK | OK | OK
44811.7784 | 0:17 | 95 | 132.9941 | 131.5536 | 142.1105 | 90.5996 | 110.7284 | 110.7284 | 54.4683 | 56.8482 | 54.5589 | 58.9559 | 50 | 84.2549 | 206.2012 | 74.7161 | 76.3181 | 113.2936 | ON | 51.63 | 112 | 38.9696 | 30.1105 | 5.2182 | 2.1077 | 1.2716 | 1.2716 | 2.2323 |  | OK | OK | OK | OK | 81.3641 | OK | OK | OK | OK | OK
44811.7785 | 0:17 | 95 | 133.1372 | 131.6823 | 142.2977 | 90.6537 | 110.7809 | 110.7809 | 54.3311 | 56.6828 | 54.4436 | 58.7886 | 50 | 84.1424 | 206.3138 | 74.3202 | 76.2087 | 113.3044 | ON | 51.63 | 112 | 39.0237 | 30.2977 | 5.0528 | 2.1059 | 1.2191 | 1.2191 | 2.236 |  | OK | OK | OK | OK | 81.5072 | OK | OK | OK | OK | OK
44811.7786 | 0:17 | 95 | 133.2281 | 131.7833 | 142.4382 | 90.6574 | 110.6971 | 110.6971 | 54.145 | 56.5108 | 54.208 | 58.6061 | 50 | 83.8289 | 206.1269 | 74.2374 | 76.0516 | 113.2533 | ON | 51.63 | 112 | 39.0274 | 30.4382 | 4.8808 | 2.0953 | 1.3029 | 1.3029 | 2.2412 |  | OK | OK | OK | OK | 81.5981 | OK | OK | OK | OK | OK
44811.7787 | 0:17 | 95 | 133.3026 | 131.8421 | 142.5823 | 90.6796 | 110.7107 | 110.7107 | 53.9736 | 56.3401 | 54.0541 | 58.4334 | 50 | 83.6138 | 206.2193 | 73.9583 | 75.8811 | 113.2341 | ON | 51.63 | 112 | 39.0496 | 30.5823 | 4.7101 | 2.0933 | 1.2893 | 1.2893 | 2.2471 |  | OK | OK | OK | OK | 81.6726 | OK | OK | OK | OK | OK
44811.7788 | 0:17 | 95 | 133.3302 | 131.9154 | 142.6624 | 90.6711 | 110.612 | 110.612 | 53.808 | 56.1582 | 53.8615 | 58.2807 | 50 | 83.2994 | 205.9325 | 73.9219 | 75.7124 | 113.1536 | ON | 51.63 | 112 | 39.0411 | 30.6624 | 4.5282 | 2.1224 | 1.388 | 1.388 | 2.2514 |  | OK | OK | OK | OK | 81.7002 | OK | OK | OK | OK | OK
44811.779 | 0:18 | 95 | 133.398 | 131.9797 | 142.7868 | 90.6869 | 110.6246 | 110.6246 | 53.6412 | 55.9485 | 53.6788 | 58.0976 | 50 | 82.9916 | 205.7685 | 73.71 | 75.5302 | 113.1102 | ON | 51.63 | 112 | 39.0568 | 30.7868 | 4.3185 | 2.1491 | 1.3754 | 1.3754 | 2.2568 |  | OK | OK | OK | OK | 81.768 | OK | OK | OK | OK | OK
44811.7791 | 0:18 | 95 | 133.4359 | 132.0074 | 142.8222 | 90.6795 | 110.485 | 110.485 | 53.469 | 55.7183 | 53.4977 | 57.9136 | 50 | 82.719 | 205.5472 | 73.5791 | 75.3435 | 112.9971 | ON | 51.63 | 112 | 39.0495 | 30.8222 | 4.0883 | 2.1952 | 1.515 | 1.515 | 2.2608 |  | OK | OK | OK | OK | 81.8059 | OK | OK | OK | OK | OK
44811.7792 | 0:18 | 95 | 133.4763 | 132.004 | 142.9029 | 90.6434 | 110.4373 | 110.4373 | 53.3264 | 55.5417 | 53.3603 | 57.7567 | 50 | 82.5421 | 205.3311 | 73.4209 | 75.0929 | 112.9343 | ON | 51.63 | 112 | 39.0134 | 30.9029 | 3.9117 | 2.215 | 1.5627 | 1.5627 | 2.2627 |  | OK | OK | OK | OK | 81.8463 | OK | OK | OK | OK | OK
44811.7793 | 0:18 | 95 | 133.4684 | 132.0309 | 142.9792 | 90.5719 | 110.3178 | 110.3178 | 53.1586 | 55.3238 | 53.1591 | 57.5822 | 50 | 82.2678 | 205.1519 | 73.0897 | 74.876 | 112.8395 | ON | 51.63 | 112 | 38.9419 | 30.9792 | 3.6938 | 2.2584 | 1.6822 | 1.6822 | 2.2673 |  | OK | OK | OK | OK | 81.8384 | OK | OK | OK | OK | OK
44811.7794 | 0:18 | 95 | 133.4951 | 132.007 | 142.9658 | 90.5168 | 110.2229 | 110.2229 | 52.9232 | 55.1142 | 52.9465 | 57.3974 | 50 | 81.9287 | 204.9066 | 72.899 | 74.7262 | 112.7198 | ON | 51.63 | 110.2 | 38.8868 | 32.7658 | 3.4842 | 2.2832 | -0.0229 | -0.0229 | 2.2727 |  | OK | Low Charge | OK | OK | 81.8651 | OK | OK | OK | OK | OK
44811.7795 | 0:18 | 95 | 133.5016 | 132.0304 | 143.0505 | 90.4931 | 110.3461 | 110.3461 | 52.7616 | 54.8973 | 52.7907 | 57.1958 | 50 | 81.7027 | 205.2793 | 72.7566 | 74.5661 | 112.7873 | ON | 51.63 | 112 | 38.8631 | 31.0505 | 3.2673 | 2.2985 | 1.6539 | 1.6539 | 2.2819 |  | OK | OK | OK | OK | 81.8716 | OK | OK | OK | OK | OK
44811.7796 | 0:19 | 95 | 133.4959 | 132.0461 | 143.0919 | 90.3943 | 110.1812 | 110.1812 | 52.5924 | 54.7061 | 52.5742 | 56.9613 | 50 | 81.5085 | 204.6907 | 72.6551 | 74.252 | 112.6443 | ON | 51.63 | 110.2 | 38.7643 | 32.8919 | 3.0761 | 2.2552 | 0.0188 | 0.0188 | 2.2804 |  | OK | Low Charge | OK | OK | 81.8659 | OK | OK | OK | OK | OK
44811.7798 | 0:19 | 95 | 133.4915 | 132.0389 | 143.0723 | 90.3215 | 110.0575 | 110.0575 | 52.4183 | 54.4656 | 52.4112 | 56.7583 | 50 | 81.2408 | 204.2361 | 72.3731 | 74.2672 | 112.5345 | ON | 51.63 | 110.2 | 38.6915 | 32.8723 | 2.8356 | 2.2927 | 0.1425 | 0.1425 | 2.282 |  | OK | Low Charge | OK | OK | 81.8615 | OK | OK | OK | OK | OK
44811.7799 | 0:19 | 95 | 133.4709 | 132.0261 | 143.0815 | 90.2714 | 109.947 | 109.947 | 52.2651 | 54.2597 | 52.2336 | 56.5779 | 50 | 80.9994 | 204.2096 | 72.2773 | 73.9775 | 112.4266 | ON | 51.63 | 110.2 | 38.6414 | 32.8815 | 2.6297 | 2.3181 | 0.253 | 0.253 | 2.2875 |  | OK | Low Charge | OK | OK | 81.8409 | OK | OK | OK | OK | OK
44811.78 | 0:19 | 95 | 133.3851 | 131.9994 | 143.0722 | 90.1416 | 109.8681 | 109.8681 | 52.0666 | 54.0714 | 52.0613 | 56.3871 | 50 | 80.7706 | 203.8275 | 71.8386 | 73.7245 | 112.3191 | ON | 51.63 | 110.2 | 38.5116 | 32.8722 | 2.4413 | 2.3158 | 0.3319 | 0.3319 | 2.289 |  | OK | Low Charge | OK | OK | 81.7551 | OK | OK | OK | OK | OK
44811.7801 | 0:19 | 95 | 133.3529 | 131.9294 | 143.0507 | 90.0378 | 109.7806 | 109.7806 | 51.9006 | 53.8831 | 51.8593 | 56.1934 | 50 | 80.4194 | 203.7499 | 71.6486 | 73.5512 | 112.2154 | ON | 51.63 | 110.2 | 38.4078 | 32.8507 | 2.2531 | 2.3103 | 0.4194 | 0.4194 | 2.2966 |  | OK | Low Charge | OK | OK | 81.7229 | OK | OK | OK | OK | OK
44811.7802 | 0:19 | 95 | 133.3256 | 131.8737 | 143.049 | 89.9536 | 109.7411 | 109.7411 | 51.7261 | 53.688 | 51.676 | 56.0132 | 50 | 80.1102 | 203.686 | 71.5552 | 73.3806 | 112.1612 | ON | 51.63 | 110.2 | 38.3236 | 32.849 | 2.058 | 2.3252 | 0.4589 | 0.4589 | 2.3034 |  | OK | Low Charge | OK | OK | 81.6956 | OK | OK | OK | OK | OK
44811.7803 | 0:20 | 95 | 133.3026 | 131.8704 | 143.0476 | 89.8802 | 109.6764 | 109.6764 | 51.5388 | 53.4611 | 51.4883 | 55.8233 | 50 | 79.931 | 203.2545 | 71.4041 | 73.2347 | 112.0969 | ON | 48.19 | 110.2 | 41.6902 | 32.8476 | 5.2711 | 2.3621 | 0.5236 | 0.5236 | 2.3032 |  | OK | Low Charge | OK | OK | 85.1126 | OK | OK | OK | OK | OK
44811.7805 | 0:20 | 95 | 133.2657 | 131.7932 | 143.0304 | 89.8063 | 109.5808 | 109.5808 | 51.3664 | 53.2525 | 51.2827 | 55.6456 | 50 | 79.653 | 203.2175 | 71.205 | 72.9423 | 111.9854 | ON | 48.19 | 110.2 | 41.6163 | 32.8304 | 5.0625 | 2.3932 | 0.6192 | 0.6192 | 2.3096 |  | OK | Low Charge | OK | OK | 85.0757 | OK | OK | OK | OK | OK
44811.7806 | 0:20 | 95 | 133.222 | 131.7608 | 143.012 | 89.6877 | 109.5531 | 109.5531 | 51.1805 | 53.0515 | 51.1219 | 55.4997 | 50 | 79.3985 | 203.0567 | 71.1413 | 72.8874 | 111.9765 | ON | 48.19 | 110.2 | 41.4978 | 32.812 | 4.8615 | 2.4482 | 0.6469 | 0.6469 | 2.3141 |  | OK | Low Charge | OK | OK | 85.032 | OK | OK | OK | OK | OK
44811.7807 | 0:20 | 95 | 133.1639 | 131.7067 | 142.9713 | 89.5565 | 109.4807 | 109.4807 | 51.017 | 52.8374 | 50.9684 | 55.3034 | 50 | 79.1569 | 202.7479 | 70.8883 | 72.6266 | 111.8483 | ON | 48.19 | 110.2 | 41.3665 | 32.7713 | 4.6474 | 2.466 | 0.7193 | 0.7193 | 2.3168 |  | OK | Low Charge | OK | OK | 84.9739 | OK | OK | OK | OK | OK
44811.7808 | 0:20 | 95 | 133.0821 | 131.6311 | 142.9592 | 89.4528 | 109.3829 | 109.3829 | 50.8488 | 52.6708 | 50.7803 | 55.0699 | 50 | 78.8928 | 202.6056 | 70.7931 | 72.3944 | 111.7645 | ON | 48.19 | 110.2 | 41.2628 | 32.7592 | 4.4808 | 2.3991 | 0.8171 | 0.8171 | 2.3218 |  | OK | Low Charge | OK | OK | 84.8921 | OK | OK | OK | OK | OK
44811.7809 | 0:20 | 95 | 133.0294 | 131.5533 | 142.859 | 89.3864 | 109.164 | 109.164 | 50.6605 | 52.4893 | 50.5961 | 54.9038 | 50 | 78.6596 | 202.0008 | 70.4655 | 72.2973 | 111.5732 | ON | 48.19 | 110.2 | 41.1964 | 32.659 | 4.2993 | 2.4145 | 1.036 | 1.036 | 2.3211 |  | OK | OK | OK | OK | 84.8394 | OK | OK | OK | OK | OK
44811.781 | 0:21 | 95 | 132.9288 | 131.4527 | 142.8107 | 89.2648 | 109.0743 | 109.0743 | 50.4597 | 52.2772 | 50.4293 | 54.7541 | 50 | 78.4779 | 201.7937 | 70.3596 | 72.0874 | 111.4553 | ON | 48.19 | 110.2 | 41.0748 | 32.6107 | 4.0872 | 2.4768 | 1.1257 | 1.1257 | 2.3234 |  | OK | OK | OK | OK | 84.7388 | OK | OK | OK | OK | OK
44811.7811 | 0:21 | 95 | 132.8271 | 131.3747 | 142.7235 | 89.1156 | 108.9658 | 108.9658 | 50.2858 | 52.0497 | 50.2353 | 54.6224 | 50 | 78.1494 | 201.468 | 70.0341 | 71.8471 | 111.3391 | ON | 48.19 | 110.2 | 40.9256 | 32.5235 | 3.8597 | 2.5727 | 1.2342 | 1.2342 | 2.3282 |  | OK | OK | OK | OK | 84.6371 | OK | OK | OK | OK | OK
44811.7813 | 0:21 | 95 | 132.6956 | 131.2398 | 142.6246 | 88.9607 | 108.8353 | 108.8353 | 50.0992 | 51.8323 | 50.0431 | 54.4582 | 50 | 77.9106 | 201.123 | 70.0502 | 71.6983 | 111.2235 | ON | 48.19 | 110.2 | 40.7707 | 32.4246 | 3.6423 | 2.626 | 1.3647 | 1.3647 | 2.3304 |  | OK | OK | OK | OK | 84.5056 | OK | OK | OK | OK | OK
44811.7814 | 0:21 | 95 | 132.6426 | 131.1852 | 142.5469 | 88.8805 | 108.7645 | 108.7645 | 49.9765 | 51.5806 | 49.8989 | 54.2551 | 50 | 77.7641 | 200.7866 | 69.6442 | 71.5925 | 111.1436 | ON | 48.19 | 110.2 | 40.6905 | 32.3469 | 3.3906 | 2.6745 | 1.4355 | 1.4355 | 2.3305 |  | OK | OK | OK | OK | 84.4526 | OK | OK | OK | OK | OK
44811.7815 | 0:21 | 95 | 132.542 | 131.0904 | 142.5035 | 88.7615 | 108.7135 | 108.7135 | 49.7694 | 51.4024 | 49.6974 | 54.0588 | 50 | 77.4008 | 200.9738 | 69.6416 | 71.465 | 111.0865 | ON | 48.19 | 110.2 | 40.5715 | 32.3035 | 3.2124 | 2.6564 | 1.4865 | 1.4865 | 2.3417 |  | OK | OK | OK | OK | 84.352 | OK | OK | OK | OK | OK
44811.7816 | 0:21 | 95 | 132.4671 | 131.0243 | 142.4198 | 88.6611 | 108.626 | 108.626 | 49.6144 | 51.2095 | 49.5345 | 53.8772 | 50 | 77.0537 | 200.7896 | 69.2373 | 71.1929 | 111.0032 | ON | 48.19 | 110.2 | 40.4711 | 32.2198 | 3.0195 | 2.6677 | 1.574 | 1.574 | 2.3486 |  | OK | OK | OK | OK | 84.2771 | OK | OK | OK | OK | OK
44811.7817 | 0:22 | 95 | 132.4081 | 130.9562 | 142.3567 | 88.569 | 108.486 | 108.486 | 49.4397 | 51.0214 | 49.3755 | 53.7112 | 50 | 77.0201 | 199.9691 | 69.1124 | 71.0106 | 110.8589 | ON | 48.19 | 108.3 | 40.379 | 34.0567 | 2.8314 | 2.6898 | -0.186 | -0.186 | 2.3405 |  | OK | Low Charge | OK | OK | 84.2181 | OK | OK | OK | OK | OK
44811.7818 | 0:22 | 95 | 132.3545 | 130.8645 | 142.3395 | 88.4926 | 108.4851 | 108.4851 | 49.2512 | 50.7718 | 49.1978 | 53.5168 | 50 | 76.7854 | 200.2169 | 69.0541 | 70.6717 | 110.8349 | ON | 48.19 | 110.2 | 40.3026 | 32.1395 | 2.5818 | 2.745 | 1.7149 | 1.7149 | 2.3492 |  | OK | OK | OK | OK | 84.1645 | OK | OK | OK | OK | OK
44811.782 | 0:22 | 95 | 132.3059 | 130.7935 | 142.3112 | 88.4021 | 108.4625 | 108.4625 | 49.0961 | 50.51 | 49.0251 | 53.3448 | 50 | 76.5029 | 200.234 | 68.918 | 70.675 | 110.8263 | ON | 48.19 | 110.2 | 40.2121 | 32.1112 | 2.32 | 2.8348 | 1.7375 | 1.7375 | 2.3567 |  | OK | OK | OK | OK | 84.1159 | OK | OK | OK | OK | OK
44811.7821 | 0:22 | 95 | 132.2938 | 130.7606 | 142.2553 | 88.3004 | 108.3779 | 108.3779 | 48.9092 | 50.3935 | 48.8441 | 53.1596 | 50 | 76.1936 | 199.9865 | 68.9074 | 70.4708 | 110.7283 | ON | 48.19 | 108.3 | 40.1104 | 33.9553 | 2.2035 | 2.7661 | -0.0779 | -0.0779 | 2.362 |  | OK | Low Charge | OK | OK | 84.1038 | OK | OK | OK | OK | OK
44811.7822 | 0:22 | 95 | 132.2107 | 130.6825 | 142.1888 | 88.1915 | 108.3598 | 108.3598 | 48.7715 | 50.3069 | 48.6886 | 52.9832 | 50 | 75.9869 | 200.0187 | 68.6185 | 70.2343 | 110.6826 | ON | 48.19 | 110.2 | 40.0015 | 31.9888 | 2.1169 | 2.6763 | 1.8402 | 1.8402 | 2.3677 |  | OK | OK | OK | OK | 84.0207 | OK | OK | OK | OK | OK
44811.7823 | 0:22 | 95 | 132.1358 | 130.6342 | 142.1597 | 88.1066 | 108.264 | 108.264 | 48.6096 | 50.1629 | 48.5171 | 52.8229 | 50 | 75.8805 | 199.7052 | 68.4703 | 70.0689 | 110.6015 | ON | 48.19 | 108.3 | 39.9166 | 33.8597 | 1.9729 | 2.66 | 0.036 | 0.036 | 2.367 |  | OK | Low Charge | OK | OK | 83.9458 | OK | OK | OK | OK | OK
44811.7824 | 0:23 | 95 | 132.143 | 130.6427 | 142.1684 | 88.0235 | 108.3245 | 108.3245 | 48.3999 | 50.0114 | 48.3761 | 52.6487 | 50 | 75.6106 | 199.8377 | 68.127 | 69.8839 | 110.6487 | ON | 48.19 | 108.3 | 39.8335 | 33.8684 | 1.8214 | 2.6372 | -0.0245 | -0.0245 | 2.3756 |  | OK | Low Charge | OK | OK | 83.953 | OK | OK | OK | OK | OK
44811.7825 | 0:23 | 95 | 132.1345 | 130.6392 | 142.1665 | 87.9685 | 108.3482 | 108.3482 | 48.2559 | 49.8108 | 48.2255 | 52.4797 | 50 | 75.374 | 199.9161 | 68.0376 | 69.6547 | 110.6504 | ON | 48.19 | 108.3 | 39.7785 | 33.8665 | 1.6208 | 2.6689 | -0.0482 | -0.0482 | 2.3827 |  | OK | Low Charge | OK | OK | 83.9445 | OK | OK | OK | OK | OK
44811.7827 | 0:23 | 95 | 132.1124 | 130.5322 | 142.1538 | 87.9063 | 108.3335 | 108.3335 | 48.0955 | 49.7064 | 48.0909 | 52.3005 | 50 | 75.2195 | 199.8447 | 67.8911 | 69.5331 | 110.6338 | ON | 48.19 | 108.3 | 39.7163 | 33.8538 | 1.5164 | 2.5941 | -0.0335 | -0.0335 | 2.386 |  | OK | Low Charge | OK | OK | 83.9224 | OK | OK | OK | OK | OK
44811.7828 | 0:23 | 95 | 132.0968 | 130.5682 | 142.1627 | 87.9059 | 108.3345 | 108.3345 | 47.9626 | 49.5667 | 47.938 | 52.1262 | 50 | 74.9426 | 200.0026 | 67.685 | 69.4712 | 110.6446 | ON | 44.59 | 110.2 | 43.3159 | 31.9627 | 4.9767 | 2.5594 | 1.8655 | 1.8655 | 2.3951 |  | OK | OK | OK | OK | 87.5068 | OK | OK | OK | OK | OK
44811.7829 | 0:23 | 95 | 132.1176 | 130.5499 | 142.171 | 87.8549 | 108.3683 | 108.3683 | 47.8026 | 49.4051 | 47.7729 | 51.9561 | 50 | 74.7831 | 200.0469 | 67.5021 | 69.3322 | 110.634 | ON | 44.59 | 110.2 | 43.2649 | 31.971 | 4.8151 | 2.551 | 1.8317 | 1.8317 | 2.3999 |  | OK | OK | OK | OK | 87.5276 | OK | OK | OK | OK | OK
44811.783 | 0:23 | 95 | 132.107 | 130.577 | 142.1634 | 87.7902 | 108.3128 | 108.3128 | 47.6977 | 49.3102 | 47.6306 | 51.7912 | 50 | 74.6266 | 199.7135 | 67.5035 | 69.1536 | 110.6 | ON | 44.59 | 108.3 | 43.2002 | 33.8634 | 4.7202 | 2.481 | -0.0128 | -0.0128 | 2.4003 |  | OK | Low Charge | OK | OK | 87.517 | OK | OK | OK | OK | OK
44811.7831 | 0:24 | 95 | 132.0737 | 130.5764 | 142.1855 | 87.7879 | 108.2685 | 108.2685 | 47.5585 | 49.1474 | 47.4867 | 51.6329 | 50 | 74.4061 | 199.8189 | 67.0942 | 68.8557 | 110.5748 | ON | 44.59 | 108.3 | 43.1979 | 33.8855 | 4.5574 | 2.4855 | 0.0315 | 0.0315 | 2.4075 |  | OK | Low Charge | OK | OK | 87.4837 | OK | OK | OK | OK | OK
44811.7832 | 0:24 | 95 | 132.1356 | 130.5671 | 142.1741 | 87.7275 | 108.3192 | 108.3192 | 47.3841 | 49.0507 | 47.3197 | 51.5138 | 50 | 74.218 | 199.9441 | 66.8161 | 68.6784 | 110.6036 | ON | 44.59 | 108.3 | 43.1375 | 33.8741 | 4.4607 | 2.4631 | -0.0192 | -0.0192 | 2.414 |  | OK | Low Charge | OK | OK | 87.5456 | OK | OK | OK | OK | OK
44811.7833 | 0:24 | 95 | 132.1614 | 130.595 | 142.2603 | 87.7386 | 108.3655 | 108.3655 | 47.2433 | 48.9059 | 47.1617 | 51.3373 | 50 | 74.0534 | 200.2464 | 66.7119 | 68.6102 | 110.651 | ON | 44.59 | 110.2 | 43.1486 | 32.0603 | 4.3159 | 2.4314 | 1.8345 | 1.8345 | 2.4218 |  | OK | OK | OK | OK | 87.5714 | OK | OK | OK | OK | OK
44811.7835 | 0:24 | 95 | 132.1863 | 130.5397 | 142.2594 | 87.7144 | 108.3184 | 108.3184 | 47.1211 | 48.7539 | 47.0224 | 51.184 | 50 | 73.817 | 199.9747 | 66.646 | 68.3899 | 110.5789 | ON | 44.59 | 108.3 | 43.1244 | 33.9594 | 4.1639 | 2.4302 | -0.0184 | -0.0184 | 2.4252 |  | OK | Low Charge | OK | OK | 87.5963 | OK | OK | OK | OK | OK
44811.7836 | 0:24 | 95 | 132.1863 | 130.5487 | 142.2611 | 87.6697 | 108.3562 | 108.3562 | 46.9733 | 48.6215 | 46.8976 | 51.0393 | 50 | 73.674 | 199.9994 | 66.4926 | 68.1071 | 110.6021 | ON | 44.59 | 108.3 | 43.0797 | 33.9611 | 4.0315 | 2.4178 | -0.0562 | -0.0562 | 2.4294 |  | OK | Low Charge | OK | OK | 87.5963 | OK | OK | OK | OK | OK
44811.7837 | 0:24 | 95 | 132.2466 | 130.6199 | 142.3234 | 87.6498 | 108.4221 | 108.4221 | 46.8288 | 48.4627 | 46.7615 | 50.8937 | 50 | 73.4585 | 200.1438 | 66.2616 | 68.0037 | 110.6567 | ON | 44.59 | 110.2 | 43.0598 | 32.1234 | 3.8727 | 2.431 | 1.7779 | 1.7779 | 2.437 |  | OK | OK | OK | OK | 87.6566 | OK | OK | OK | OK | OK
44811.7838 | 0:25 | 95 | 132.2577 | 130.6725 | 142.3694 | 87.6613 | 108.4236 | 108.4236 | 46.6887 | 48.3573 | 46.6042 | 50.7026 | 50 | 73.2912 | 200.1173 | 66.2496 | 67.8803 | 110.6469 | ON | 44.59 | 110.2 | 43.0713 | 32.1694 | 3.7673 | 2.3453 | 1.7764 | 1.7764 | 2.4414 |  | OK | OK | OK | OK | 87.6677 | OK | OK | OK | OK | OK
44811.7839 | 0:25 | 95 | 132.3305 | 130.7041 | 142.4246 | 87.6183 | 108.3959 | 108.3959 | 46.5763 | 48.2832 | 46.4851 | 50.5577 | 50 | 73.1195 | 200.1105 | 65.9455 | 67.7158 | 110.6227 | ON | 44.59 | 110.2 | 43.0282 | 32.2246 | 3.6932 | 2.2745 | 1.8041 | 1.8041 | 2.446 |  | OK | OK | OK | OK | 87.7405 | OK | OK | OK | OK | OK
44811.784 | 0:25 | 95 | 132.3945 | 130.7216 | 142.4819 | 87.6096 | 108.4058 | 108.4058 | 46.4507 | 48.1064 | 46.3181 | 50.3862 | 50 | 72.9274 | 200.151 | 65.9724 | 67.549 | 110.6228 | ON | 44.59 | 110.2 | 43.0196 | 32.2819 | 3.5164 | 2.2798 | 1.7942 | 1.7942 | 2.4519 |  | OK | OK | OK | OK | 87.8045 | OK | OK | OK | OK | OK
44811.7842 | 0:25 | 95 | 132.4417 | 130.8062 | 142.5419 | 87.6355 | 108.4626 | 108.4626 | 46.3273 | 47.9648 | 46.2166 | 50.2514 | 50 | 72.7377 | 200.1151 | 65.7158 | 67.2255 | 110.6716 | ON | 44.59 | 110.2 | 43.0455 | 32.3419 | 3.3748 | 2.2867 | 1.7374 | 1.7374 | 2.4568 |  | OK | OK | OK | OK | 87.8517 | OK | OK | OK | OK | OK
44811.7843 | 0:25 | 95 | 132.4063 | 130.8143 | 142.6125 | 87.6275 | 108.4782 | 108.4782 | 46.1737 | 47.8093 | 46.0811 | 50.1071 | 50 | 72.5945 | 200.4405 | 65.507 | 67.1801 | 110.6761 | ON | 44.59 | 110.2 | 43.0375 | 32.4125 | 3.2193 | 2.2978 | 1.7218 | 1.7218 | 2.4645 |  | OK | OK | OK | OK | 87.8163 | OK | OK | OK | OK | OK
44811.7844 | 0:25 | 95 | 132.5182 | 130.9448 | 142.7074 | 87.6479 | 108.6494 | 108.6494 | 46.0563 | 47.6934 | 45.9559 | 49.955 | 50 | 72.4688 | 200.7993 | 65.3303 | 67.0128 | 110.8317 | ON | 44.59 | 110.2 | 43.0579 | 32.5074 | 3.1035 | 2.2615 | 1.5506 | 1.5506 | 2.4722 |  | OK | OK | OK | OK | 87.9282 | OK | OK | OK | OK | OK
44811.7845 | 0:26 | 95 | 132.6487 | 131.099 | 142.8707 | 87.6774 | 108.8674 | 108.8674 | 45.9477 | 47.5921 | 45.8695 | 49.8029 | 50 | 72.297 | 201.3652 | 65.2241 | 66.7775 | 111.0438 | ON | 44.59 | 110.2 | 43.0874 | 32.6707 | 3.0021 | 2.2108 | 1.3326 | 1.3326 | 2.4836 |  | OK | OK | OK | OK | 88.0587 | OK | OK | OK | OK | OK
44811.7846 | 0:26 | 95 | 132.865 | 131.2605 | 143.1063 | 87.7409 | 109.0935 | 109.0935 | 45.818 | 47.5228 | 45.7408 | 49.6498 | 50 | 72.1239 | 202.1478 | 65.1743 | 66.5566 | 111.2298 | ON | 44.59 | 110.2 | 43.1509 | 32.9063 | 2.9328 | 2.1269 | 1.1065 | 1.1065 | 2.4976 |  | OK | OK | OK | OK | 88.275 | OK | OK | OK | OK | OK
44811.7847 | 0:26 | 95 | 132.9958 | 131.4437 | 143.2463 | 87.7742 | 109.2314 | 109.2314 | 45.7141 | 47.4891 | 45.6303 | 49.5006 | 50 | 71.9383 | 202.4081 | 64.9767 | 66.6599 | 111.3601 | ON | 44.59 | 110.2 | 43.1842 | 33.0463 | 2.8991 | 2.0114 | 0.9686 | 0.9686 | 2.5059 |  | OK | Low Charge | OK | OK | 88.4058 | OK | OK | OK | OK | OK
44811.7849 | 0:26 | 95 | 133.2036 | 131.5964 | 143.4184 | 87.8747 | 109.3986 | 109.3986 | 45.6383 | 47.416 | 45.5518 | 49.378 | 50 | 71.9662 | 202.998 | 64.6787 | 66.3858 | 111.4883 | ON | 44.59 | 110.2 | 43.2847 | 33.2184 | 2.826 | 1.962 | 0.8014 | 0.8014 | 2.5119 |  | OK | Low Charge | OK | OK | 88.6136 | OK | OK | OK | OK | OK
44811.785 | 0:26 | 95 | 133.3692 | 131.7701 | 143.6321 | 87.9884 | 109.5428 | 109.5428 | 45.5215 | 47.3387 | 45.4015 | 49.2121 | 50 | 71.7768 | 203.1791 | 64.6455 | 66.1974 | 111.647 | ON | 44.59 | 110.2 | 43.3984 | 33.4321 | 2.7487 | 1.8734 | 0.6572 | 0.6572 | 2.5195 |  | OK | Low Charge | OK | OK | 88.7792 | OK | OK | OK | OK | OK
44811.7851 | 0:26 | 95 | 133.5227 | 131.8954 | 143.8092 | 88.1341 | 109.6806 | 109.6806 | 45.3931 | 47.277 | 45.2606 | 49.1162 | 50 | 71.6366 | 203.504 | 64.487 | 66.0649 | 111.7434 | ON | 44.59 | 110.2 | 43.5441 | 33.6092 | 2.687 | 1.8392 | 0.5194 | 0.5194 | 2.5274 |  | OK | Low Charge | OK | OK | 88.9327 | OK | OK | OK | OK | OK
44811.7852 | 0:27 | 95 | 133.6659 | 132.0878 | 143.9678 | 88.1895 | 109.6951 | 109.6951 | 45.2971 | 47.1984 | 45.1567 | 49.0028 | 50 | 71.4129 | 203.7456 | 64.4251 | 65.9026 | 111.7513 | ON | 44.59 | 110.2 | 43.5995 | 33.7678 | 2.6084 | 1.8044 | 0.5049 | 0.5049 | 2.5367 |  | OK | Low Charge | OK | OK | 89.0759 | OK | OK | OK | OK | OK
44811.7853 | 0:27 | 95 | 133.7864 | 132.1621 | 144.0989 | 88.273 | 109.7566 | 109.7566 | 45.1911 | 47.1793 | 45.0626 | 48.8788 | 50 | 71.3161 | 203.8538 | 64.2796 | 65.6248 | 111.8033 | ON | 44.59 | 110.2 | 43.683 | 33.8989 | 2.5893 | 1.6995 | 0.4434 | 0.4434 | 2.5408 |  | OK | Low Charge | OK | OK | 89.1964 | OK | OK | OK | OK | OK
44811.7854 | 0:27 | 95 | 133.9666 | 132.2896 | 144.2754 | 88.2989 | 109.8202 | 109.8202 | 45.0683 | 47.0698 | 44.9473 | 48.7801 | 50 | 71.1878 | 204.1017 | 64.0763 | 65.4893 | 111.8478 | ON | 44.59 | 110.2 | 43.7089 | 34.0754 | 2.4798 | 1.7103 | 0.3798 | 0.3798 | 2.5475 |  | OK | Low Charge | OK | OK | 89.3766 | OK | OK | OK | OK | OK
44811.7855 | 0:27 | 95 | 134.0939 | 132.4441 | 144.4566 | 88.3084 | 109.8368 | 109.8368 | 44.9845 | 47.009 | 44.8247 | 48.6572 | 50 | 71.1091 | 204.034 | 64.0575 | 65.4019 | 111.8639 | ON | 44.59 | 110.2 | 43.7184 | 34.2566 | 2.419 | 1.6481 | 0.3632 | 0.3632 | 2.5491 |  | OK | Low Charge | OK | OK | 89.5039 | OK | OK | OK | OK | OK
44811.7857 | 0:27 | 95 | 134.1515 | 132.5474 | 144.5462 | 88.3349 | 109.8261 | 109.8261 | 44.8723 | 46.8463 | 44.7121 | 48.5585 | 50 | 70.8498 | 204.1677 | 63.6612 | 65.2185 | 111.8841 | ON | 44.59 | 110.2 | 43.7449 | 34.3462 | 2.2563 | 1.7122 | 0.3739 | 0.3739 | 2.5584 |  | OK | Low Charge | OK | OK | 89.5615 | OK | OK | OK | OK | OK
44811.7858 | 0:27 | 95 | 134.2531 | 132.6826 | 144.6889 | 88.3903 | 109.9542 | 109.9542 | 44.7756 | 46.7122 | 44.6067 | 48.4461 | 50 | 70.7624 | 204.5262 | 63.577 | 65.2339 | 111.9633 | ON | 44.59 | 110.2 | 43.8003 | 34.4889 | 2.1222 | 1.7339 | 0.2458 | 0.2458 | 2.5652 |  | OK | Low Charge | OK | OK | 89.6631 | OK | OK | OK | OK | OK
44811.7859 | 0:28 | 95 | 134.3932 | 132.7723 | 144.8474 | 88.4364 | 109.9668 | 109.9668 | 44.6902 | 46.6122 | 44.4953 | 48.3198 | 50 | 70.6254 | 204.4874 | 63.3815 | 64.993 | 111.9949 | ON | 44.59 | 110.2 | 43.8464 | 34.6474 | 2.0222 | 1.7075 | 0.2332 | 0.2332 | 2.5688 |  | OK | Low Charge | OK | OK | 89.8032 | OK | OK | OK | OK | OK
44811.786 | 0:28 | 95 | 134.5053 | 132.8568 | 144.9633 | 88.4962 | 109.9745 | 109.9745 | 44.5718 | 46.5295 | 44.3726 | 48.1787 | 50 | 70.4426 | 204.4225 | 63.3462 | 64.862 | 111.9968 | ON | 44.59 | 110.2 | 43.9062 | 34.7633 | 1.9395 | 1.6492 | 0.2255 | 0.2255 | 2.5736 |  | OK | Low Charge | OK | OK | 89.9153 | OK | OK | OK | OK | OK
44811.7861 | 0:28 | 95 | 134.5825 | 132.9453 | 144.9953 | 88.5071 | 109.9011 | 109.9011 | 44.4668 | 46.4111 | 44.2536 | 48.0577 | 50 | 70.3218 | 204.1049 | 63.1145 | 64.6729 | 111.9076 | ON | 44.59 | 110.2 | 43.9171 | 34.7953 | 1.8211 | 1.6466 | 0.2989 | 0.2989 | 2.5735 |  | OK | Low Charge | OK | OK | 89.9925 | OK | OK | OK | OK | OK
44811.7862 | 0:28 | 95 | 134.6213 | 132.9409 | 145.041 | 88.4947 | 109.8275 | 109.8275 | 44.3629 | 46.2812 | 44.1268 | 47.9415 | 50 | 70.2782 | 204.1497 | 62.8349 | 64.6239 | 111.8366 | ON | 44.59 | 110.2 | 43.9047 | 34.841 | 1.6912 | 1.6603 | 0.3725 | 0.3725 | 2.5754 |  | OK | Low Charge | OK | OK | 90.0313 | OK | OK | OK | OK | OK
44811.7864 | 0:28 | 95 | 134.6481 | 132.9488 | 145.1873 | 88.4765 | 109.7735 | 109.7735 | 44.2385 | 46.1212 | 44.0185 | 47.8229 | 50 | 69.9624 | 203.9931 | 62.7837 | 64.3226 | 111.7694 | ON | 43.86 | 110.2 | 44.6165 | 34.9873 | 2.2612 | 1.7016 | 0.4265 | 0.4265 | 2.5831 |  | OK | Low Charge | OK | OK | 90.7881 | OK | OK | OK | OK | OK
44811.7865 | 0:28 | 95 | 134.7018 | 132.998 | 145.2601 | 88.4783 | 109.7647 | 109.7647 | 44.1379 | 45.9697 | 43.8701 | 47.7147 | 50 | 69.8425 | 204.1239 | 62.7929 | 64.1844 | 111.7511 | ON | 43.86 | 110.2 | 44.6183 | 35.0601 | 2.1097 | 1.745 | 0.4353 | 0.4353 | 2.5883 |  | OK | Low Charge | OK | OK | 90.8418 | OK | OK | OK | OK | OK
44811.7866 | 0:29 | 95 | 134.7035 | 133.0195 | 145.2908 | 88.4303 | 109.6408 | 109.6408 | 44.0337 | 45.8123 | 43.7551 | 47.6111 | 50 | 69.7177 | 203.4052 | 62.6857 | 64.0166 | 111.6498 | ON | 43.86 | 110.2 | 44.5703 | 35.0908 | 1.9523 | 1.7988 | 0.5592 | 0.5592 | 2.5836 |  | OK | Low Charge | OK | OK | 90.8435 | OK | OK | OK | OK | OK
44811.7867 | 0:29 | 95 | 134.6656 | 133.0376 | 145.265 | 88.4016 | 109.6102 | 109.6102 | 43.9275 | 45.6135 | 43.6764 | 47.5319 | 50 | 69.6076 | 203.3096 | 62.4672 | 63.8242 | 111.5778 | ON | 43.86 | 110.2 | 44.5416 | 35.065 | 1.7535 | 1.9184 | 0.5898 | 0.5898 | 2.5859 |  | OK | Low Charge | OK | OK | 90.8056 | OK | OK | OK | OK | OK
44811.7868 | 0:29 | 95 | 134.682 | 132.9967 | 145.2798 | 88.3522 | 109.4722 | 109.4722 | 43.8069 | 45.4849 | 43.556 | 47.4055 | 50 | 69.4773 | 202.9861 | 62.467 | 63.7578 | 111.476 | ON | 43.86 | 110.2 | 44.4922 | 35.0798 | 1.6249 | 1.9206 | 0.7278 | 0.7278 | 2.586 |  | OK | Low Charge | OK | OK | 90.822 | OK | OK | OK | OK | OK
44811.7869 | 0:29 | 95 | 134.6916 | 132.9884 | 145.3053 | 88.2717 | 109.4256 | 109.4256 | 43.7181 | 45.3321 | 43.425 | 47.2915 | 50 | 69.341 | 203.101 | 62.057 | 63.5995 | 111.4089 | ON | 43.86 | 110.2 | 44.4117 | 35.1053 | 1.4721 | 1.9594 | 0.7744 | 0.7744 | 2.5916 |  | OK | Low Charge | OK | OK | 90.8316 | OK | OK | OK | OK | OK
44811.7871 | 0:29 | 95 | 134.6864 | 132.9542 | 145.3562 | 88.1816 | 109.3109 | 109.3109 | 43.5558 | 45.1272 | 43.2745 | 47.1706 | 50 | 69.0899 | 202.6615 | 61.9705 | 63.4269 | 111.3142 | ON | 43.86 | 110.2 | 44.3216 | 35.1562 | 1.2671 | 2.0435 | 0.8891 | 0.8891 | 2.5941 |  | OK | Low Charge | OK | OK | 90.8264 | OK | OK | OK | OK | OK
44811.7872 | 0:29 | 95 | 134.6364 | 132.9166 | 145.3103 | 88.0864 | 109.301 | 109.301 | 43.4513 | 45.0382 | 43.1596 | 47.0804 | 50 | 68.9798 | 202.6937 | 61.9597 | 63.299 | 111.2762 | ON | 43.11 | 110.2 | 44.9764 | 35.1103 | 1.9282 | 2.0421 | 0.899 | 0.899 | 2.5979 |  | OK | Low Charge | OK | OK | 91.5264 | OK | OK | OK | OK | OK
44811.7873 | 0:30 | 95 | 134.6788 | 132.861 | 145.3027 | 87.9783 | 109.3219 | 109.3219 | 43.3169 | 44.9059 | 43.0624 | 46.9616 | 50 | 68.8304 | 202.6599 | 61.6976 | 63.0703 | 111.2732 | ON | 43.11 | 110.2 | 44.8683 | 35.1027 | 1.7959 | 2.0556 | 0.8781 | 0.8781 | 2.6022 |  | OK | Low Charge | OK | OK | 91.5688 | OK | OK | OK | OK | OK
44811.7874 | 0:30 | 95 | 134.6178 | 132.8677 | 145.31 | 87.8466 | 109.1787 | 109.1787 | 43.1933 | 44.7699 | 42.9356 | 46.8308 | 50 | 68.706 | 202.2281 | 61.5165 | 63.0768 | 111.1157 | ON | 43.11 | 110.2 | 44.7366 | 35.11 | 1.6599 | 2.0609 | 1.0213 | 1.0213 | 2.6009 |  | OK | OK | OK | OK | 91.5078 | OK | OK | OK | OK | OK
44811.7875 | 0:30 | 95 | 134.5054 | 132.7962 | 145.2586 | 87.7516 | 108.9893 | 108.9893 | 43.0635 | 44.6446 | 42.792 | 46.7255 | 50 | 68.5577 | 201.8826 | 61.5118 | 62.9559 | 111.0119 | ON | 43.11 | 110.2 | 44.6416 | 35.0586 | 1.5346 | 2.0809 | 1.2107 | 1.2107 | 2.6014 |  | OK | OK | OK | OK | 91.3954 | OK | OK | OK | OK | OK
44811.7876 | 0:30 | 95 | 134.4163 | 132.6575 | 145.207 | 87.6262 | 108.8776 | 108.8776 | 43.001 | 44.4785 | 42.6917 | 46.6016 | 50 | 68.3453 | 201.5588 | 61.2666 | 62.7875 | 110.8632 | ON | 43.11 | 110.2 | 44.5162 | 35.007 | 1.3684 | 2.1232 | 1.3224 | 1.3224 | 2.6041 |  | OK | OK | OK | OK | 91.3063 | OK | OK | OK | OK | OK
44811.7877 | 0:30 | 95 | 134.3518 | 132.5937 | 145.1108 | 87.5721 | 108.7811 | 108.7811 | 42.8416 | 44.2586 | 42.5534 | 46.4666 | 50 | 68.2271 | 201.1818 | 60.9896 | 62.6125 | 110.7637 | ON | 43.11 | 110.2 | 44.4622 | 34.9108 | 1.1486 | 2.208 | 1.4189 | 1.4189 | 2.6033 |  | OK | OK | OK | OK | 91.2418 | OK | OK | OK | OK | OK
44811.7879 | 0:30 | 95 | 134.2428 | 132.5313 | 145.0143 | 87.4832 | 108.6661 | 108.6661 | 42.7143 | 44.0448 | 42.4217 | 46.3666 | 50 | 68.0315 | 200.9565 | 61.135 | 62.4075 | 110.6457 | ON | 43.11 | 110.2 | 44.3732 | 34.8143 | 0.93479 | 2.3218 | 1.5339 | 1.5339 | 2.6067 |  | OK | OK | OK | OK | 91.1328 | OK | OK | OK | OK | OK
44811.788 | 0:31 | 95 | 134.1444 | 132.3991 | 144.9413 | 87.3691 | 108.5022 | 108.5022 | 42.5886 | 43.9208 | 42.2782 | 46.2538 | 50 | 67.8468 | 200.4813 | 60.9588 | 62.2268 | 110.4839 | ON | 42.36 | 110.2 | 45.0091 | 34.7413 | 1.5608 | 2.3331 | 1.6978 | 1.6978 | 2.6068 |  | OK | OK | OK | OK | 91.7844 | OK | OK | OK | OK | OK
44811.7881 | 0:31 | 95 | 134.1051 | 132.2485 | 144.8105 | 87.209 | 108.3388 | 108.3388 | 42.4775 | 43.6828 | 42.191 | 46.1334 | 50 | 67.7084 | 200.1242 | 60.9363 | 62.0886 | 110.3397 | ON | 42.36 | 110.2 | 44.849 | 34.6105 | 1.3228 | 2.4506 | 1.8612 | 1.8612 | 2.6068 |  | OK | OK | OK | OK | 91.7451 | OK | OK | OK | OK | OK
44811.7882 | 0:31 | 95 | 133.9896 | 132.1164 | 144.7263 | 87.1065 | 108.3694 | 108.3694 | 42.3558 | 43.513 | 42.0757 | 46.0207 | 50 | 67.5663 | 200.1833 | 60.6796 | 62.073 | 110.305 | ON | 42.36 | 110.2 | 44.7465 | 34.5263 | 1.153 | 2.5077 | 1.8306 | 1.8306 | 2.612 |  | OK | OK | OK | OK | 91.6296 | OK | OK | OK | OK | OK
44811.7883 | 0:31 | 95 | 133.8785 | 132.0144 | 144.6618 | 86.9691 | 108.2215 | 108.2215 | 42.2063 | 43.4039 | 41.9418 | 45.864 | 50 | 67.3863 | 199.8463 | 60.4751 | 61.9007 | 110.1791 | ON | 42.36 | 108.3 | 44.6091 | 36.3618 | 1.0439 | 2.4601 | 0.0785 | 0.0785 | 2.6137 |  | OK | Low Charge | OK | OK | 91.5185 | OK | OK | OK | OK | OK
44811.7884 | 0:31 | 95 | 133.8098 | 131.9681 | 144.6093 | 86.8757 | 108.2897 | 108.2897 | 42.0976 | 43.1818 | 41.8188 | 45.7532 | 50 | 67.2983 | 199.8992 | 60.3581 | 61.726 | 110.2282 | ON | 42.36 | 108.3 | 44.5157 | 36.3093 | 0.82175 | 2.5715 | 0.0103 | 0.0103 | 2.6171 |  | OK | Low Charge | OK | OK | 91.4498 | OK | OK | OK | OK | OK
44811.7886 | 0:31 | 95 | 133.7838 | 131.9388 | 144.6052 | 86.8325 | 108.406 | 108.406 | 41.963 | 43.0442 | 41.7112 | 45.5941 | 50 | 67.1191 | 200.0522 | 60.2383 | 61.6175 | 110.3129 | ON | 42.36 | 110.2 | 44.4725 | 34.4052 | 0.68425 | 2.5498 | 1.794 | 1.794 | 2.6247 |  | OK | OK | OK | OK | 91.4238 | OK | OK | OK | OK | OK
44811.7887 | 0:32 | 95 | 133.7665 | 131.9171 | 144.5773 | 86.7578 | 108.2843 | 108.2843 | 41.8616 | 43.0214 | 41.5962 | 45.4564 | 50 | 66.9866 | 199.7502 | 60.1041 | 61.3246 | 110.1975 | ON | 41.6 | 108.3 | 45.1578 | 36.2773 | 1.4214 | 2.4351 | 0.0157 | 0.0157 | 2.6253 |  | OK | Low Charge | OK | OK | 92.1665 | OK | OK | OK | OK | OK
44811.7888 | 0:32 | 95 | 133.6161 | 131.7834 | 144.4309 | 86.6652 | 107.9951 | 107.9951 | 41.7229 | 42.9881 | 41.4451 | 45.3441 | 50 | 66.818 | 199.1023 | 59.7733 | 61.3655 | 109.969 | ON | 41.6 | 108.3 | 45.0652 | 36.1309 | 1.3881 | 2.356 | 0.3049 | 0.3049 | 2.6228 |  | OK | Low Charge | OK | OK | 92.0161 | OK | OK | OK | OK | OK
44811.7889 | 0:32 | 95 | 133.5492 | 131.6607 | 144.3047 | 86.544 | 107.8645 | 107.8645 | 41.5899 | 42.8332 | 41.317 | 45.2195 | 50 | 66.6855 | 198.6663 | 59.8253 | 61.0686 | 109.8268 | ON | 41.6 | 108.3 | 44.944 | 36.0047 | 1.2332 | 2.3863 | 0.4355 | 0.4355 | 2.6217 |  | OK | Low Charge | OK | OK | 91.9492 | OK | OK | OK | OK | OK
44811.789 | 0:32 | 95 | 133.4243 | 131.5207 | 144.1537 | 86.4202 | 107.652 | 107.652 | 41.4489 | 42.6168 | 41.1774 | 45.1292 | 50 | 66.5442 | 198.3594 | 59.7077 | 61.0904 | 109.6291 | ON | 41.6 | 108.3 | 44.8202 | 35.8537 | 1.0168 | 2.5124 | 0.648 | 0.648 | 2.6225 |  | OK | Low Charge | OK | OK | 91.8243 | OK | OK | OK | OK | OK
44811.7891 | 0:32 | 95 | 133.2404 | 131.3634 | 144.0658 | 86.2816 | 107.5007 | 107.5007 | 41.3443 | 42.3938 | 41.0687 | 45.0297 | 50 | 66.3349 | 197.9891 | 59.4363 | 60.8932 | 109.5065 | ON | 41.6 | 108.3 | 44.6816 | 35.7658 | 0.79377 | 2.636 | 0.7993 | 0.7993 | 2.6247 |  | OK | Low Charge | OK | OK | 91.6404 | OK | OK | OK | OK | OK
44811.7893 | 0:32 | 95 | 133.1631 | 131.3291 | 143.9387 | 86.0893 | 107.3975 | 107.3975 | 41.1771 | 42.1623 | 40.9393 | 44.8931 | 50 | 66.1642 | 197.6039 | 59.3521 | 60.886 | 109.4153 | ON | 41.6 | 108.3 | 44.4893 | 35.6387 | 0.56226 | 2.7309 | 0.9025 | 0.9025 | 2.6254 |  | OK | Low Charge | OK | OK | 91.5631 | OK | OK | OK | OK | OK
44811.7894 | 0:33 | 95 | 133.0288 | 131.2211 | 143.7852 | 85.9585 | 107.3448 | 107.3448 | 41.0794 | 42.0139 | 40.8107 | 44.7712 | 50 | 65.9993 | 197.405 | 59.3386 | 60.6331 | 109.3538 | ON | 40.84 | 108.3 | 45.1185 | 35.4852 | 1.1739 | 2.7573 | 0.9552 | 0.9552 | 2.6283 |  | OK | Low Charge | OK | OK | 92.1888 | OK | OK | OK | OK | OK
44811.7895 | 0:33 | 95 | 132.9392 | 131.1218 | 143.728 | 85.83 | 107.2569 | 107.2569 | 40.9228 | 41.8603 | 40.6804 | 44.6234 | 50 | 65.874 | 197.1496 | 59.122 | 60.52 | 109.2757 | ON | 40.84 | 108.3 | 44.99 | 35.428 | 1.0203 | 2.763 | 1.0431 | 1.0431 | 2.6293 |  | OK | OK | OK | OK | 92.0992 | OK | OK | OK | OK | OK
44811.7896 | 0:33 | 95 | 132.853 | 131.0062 | 143.6362 | 85.7084 | 107.2789 | 107.2789 | 40.8178 | 41.7214 | 40.5476 | 44.4888 | 50 | 65.6108 | 197.3526 | 59.0682 | 60.2737 | 109.265 | ON | 40.84 | 108.3 | 44.8684 | 35.3362 | 0.88138 | 2.7674 | 1.0211 | 1.0211 | 2.6404 |  | OK | OK | OK | OK | 92.013 | OK | OK | OK | OK | OK
44811.7897 | 0:33 | 95 | 132.8115 | 130.8876 | 143.5576 | 85.5526 | 107.208 | 107.208 | 40.7079 | 41.662 | 40.4397 | 44.3601 | 50 | 65.542 | 197.0602 | 58.8862 | 60.1356 | 109.1942 | ON | 40.84 | 108.3 | 44.7126 | 35.2576 | 0.82199 | 2.6982 | 1.092 | 1.092 | 2.639 |  | OK | OK | OK | OK | 91.9715 | OK | OK | OK | OK | OK
44811.7898 | 0:33 | 95 | 132.7266 | 130.8631 | 143.4468 | 85.4195 | 107.1033 | 107.1033 | 40.5479 | 41.6075 | 40.3144 | 44.206 | 50 | 65.3593 | 196.9654 | 58.6004 | 60.0661 | 109.1356 | ON | 40.84 | 108.3 | 44.5795 | 35.1468 | 0.76751 | 2.5985 | 1.1967 | 1.1967 | 2.6439 |  | OK | OK | OK | OK | 91.8866 | OK | OK | OK | OK | OK
44811.7899 | 0:33 | 95 | 132.578 | 130.768 | 143.4072 | 85.308 | 107.0796 | 107.0796 | 40.448 | 41.4567 | 40.2186 | 44.0784 | 50 | 65.2529 | 196.8243 | 58.6509 | 60.0665 | 109.0808 | ON | 40.84 | 108.3 | 44.468 | 35.1072 | 0.61675 | 2.6217 | 1.2204 | 1.2204 | 2.6456 |  | OK | OK | OK | OK | 91.738 | OK | OK | OK | OK | OK
44811.7901 | 0:34 | 95 | 132.6361 | 130.6873 | 143.3631 | 85.2332 | 107.1343 | 107.1343 | 40.309 | 41.2903 | 40.0759 | 43.9152 | 50 | 65.1071 | 196.9851 | 58.5444 | 59.7763 | 109.1428 | ON | 40.84 | 108.3 | 44.3932 | 35.0631 | 0.45031 | 2.6249 | 1.1657 | 1.1657 | 2.6525 |  | OK | OK | OK | OK | 91.7961 | OK | OK | OK | OK | OK
44811.7902 | 0:34 | 95 | 132.6136 | 130.6688 | 143.3516 | 85.2052 | 107.2325 | 107.2325 | 40.1952 | 41.1339 | 39.9721 | 43.8145 | 50 | 64.9233 | 197.2092 | 58.416 | 59.6317 | 109.1671 | ON | 40.07 | 108.3 | 45.1352 | 35.0516 | 1.0639 | 2.6806 | 1.0675 | 1.0675 | 2.6614 |  | OK | OK | OK | OK | 92.5436 | OK | OK | OK | OK | OK
44811.7903 | 0:34 | 95 | 132.6271 | 130.6784 | 143.3111 | 85.1574 | 107.2817 | 107.2817 | 40.0944 | 41.0886 | 39.8589 | 43.6992 | 50 | 64.8628 | 197.511 | 58.3244 | 59.4446 | 109.235 | ON | 40.07 | 108.3 | 45.0874 | 35.0111 | 1.0186 | 2.6106 | 1.0183 | 1.0183 | 2.6672 |  | OK | OK | OK | OK | 92.5571 | OK | OK | OK | OK | OK
44811.7904 | 0:34 | 95 | 132.6458 | 130.6985 | 143.3669 | 85.084 | 107.4508 | 107.4508 | 39.9699 | 41.0617 | 39.7529 | 43.5909 | 50 | 64.591 | 197.8807 | 58.2514 | 59.4457 | 109.3636 | ON | 40.07 | 108.3 | 45.014 | 35.0669 | 0.99171 | 2.5292 | 0.8492 | 0.8492 | 2.681 |  | OK | Low Charge | OK | OK | 92.5758 | OK | OK | OK | OK | OK
44811.7905 | 0:34 | 95 | 132.6637 | 130.7198 | 143.3966 | 85.0552 | 107.5325 | 107.5325 | 39.8503 | 41.0795 | 39.6407 | 43.4803 | 50 | 64.5366 | 198.2972 | 58.0861 | 59.3819 | 109.4859 | ON | 40.07 | 108.3 | 44.9852 | 35.0966 | 1.0094 | 2.4008 | 0.7675 | 0.7675 | 2.6881 |  | OK | Low Charge | OK | OK | 92.5937 | OK | OK | OK | OK | OK
44811.7906 | 0:34 | 95 | 132.6536 | 130.7899 | 143.4124 | 85.021 | 107.5851 | 107.5851 | 39.7865 | 41.0623 | 39.581 | 43.3781 | 50 | 64.5195 | 198.1868 | 57.985 | 59.1855 | 109.489 | ON | 40.07 | 108.3 | 44.951 | 35.1124 | 0.99229 | 2.3159 | 0.7149 | 0.7149 | 2.6873 |  | OK | Low Charge | OK | OK | 92.5836 | OK | OK | OK | OK | OK
44811.7908 | 0:35 | 95 | 132.718 | 130.8302 | 143.4914 | 85.0428 | 107.6588 | 107.6588 | 39.6648 | 41.0162 | 39.4669 | 43.2592 | 50 | 64.4511 | 198.1884 | 57.7693 | 59.0927 | 109.5493 | ON | 40.07 | 108.3 | 44.9728 | 35.1914 | 0.94625 | 2.2429 | 0.6412 | 0.6412 | 2.6896 |  | OK | Low Charge | OK | OK | 92.648 | OK | OK | OK | OK | OK
44811.7909 | 0:35 | 95 | 132.7049 | 130.7881 | 143.4354 | 85.0156 | 107.4478 | 107.4478 | 39.5495 | 40.9789 | 39.3303 | 43.1495 | 50 | 64.2161 | 197.6618 | 57.4227 | 58.8454 | 109.3952 | ON | 40.07 | 108.3 | 44.9457 | 35.1354 | 0.90885 | 2.1706 | 0.8522 | 0.8522 | 2.691 |  | OK | Low Charge | OK | OK | 92.6349 | OK | OK | OK | OK | OK
44811.791 | 0:35 | 95 | 132.7088 | 130.7145 | 143.3966 | 84.9995 | 107.2985 | 107.2985 | 39.4736 | 40.9132 | 39.2165 | 43.0622 | 50 | 63.9994 | 197.5333 | 57.3331 | 58.7397 | 109.2812 | ON | 39.29 | 108.3 | 45.7095 | 35.0966 | 1.6232 | 2.149 | 1.0015 | 1.0015 | 2.6968 |  | OK | OK | OK | OK | 93.4188 | OK | OK | OK | OK | OK
44811.7911 | 0:35 | 95 | 132.7022 | 130.6636 | 143.3316 | 84.9527 | 107.2373 | 107.2373 | 39.3508 | 40.634 | 39.093 | 43.0025 | 50 | 63.9041 | 197.2073 | 57.2458 | 58.6341 | 109.2029 | ON | 39.29 | 108.3 | 45.6627 | 35.0316 | 1.344 | 2.3685 | 1.0627 | 1.0627 | 2.6959 |  | OK | OK | OK | OK | 93.4122 | OK | OK | OK | OK | OK
44811.7912 | 0:35 | 95 | 132.6301 | 130.6566 | 143.3263 | 84.9229 | 107.179 | 107.179 | 39.2717 | 40.4189 | 39.0148 | 42.8969 | 50 | 63.8384 | 197.3937 | 57.0646 | 58.5508 | 109.1789 | ON | 39.29 | 108.3 | 45.6329 | 35.0263 | 1.1289 | 2.478 | 1.121 | 1.121 | 2.7005 |  | OK | OK | OK | OK | 93.3401 | OK | OK | OK | OK | OK
44811.7913 | 0:35 | 95 | 132.6245 | 130.7084 | 143.3216 | 84.8623 | 107.1193 | 107.1193 | 39.1784 | 40.231 | 38.8904 | 42.809 | 50 | 63.6316 | 197.1984 | 57.1101 | 58.5023 | 109.1497 | ON | 39.29 | 108.3 | 45.5723 | 35.0216 | 0.94098 | 2.578 | 1.1807 | 1.1807 | 2.7051 |  | OK | OK | OK | OK | 93.3345 | OK | OK | OK | OK | OK
44811.7914 | 0:36 | 95 | 132.6153 | 130.6595 | 143.3188 | 84.8246 | 107.2153 | 107.2153 | 39.0922 | 40.0544 | 38.8101 | 42.7305 | 50 | 63.6334 | 197.2218 | 56.9227 | 58.2195 | 109.1746 | ON | 39.29 | 108.3 | 45.5346 | 35.0188 | 0.76444 | 2.6761 | 1.0847 | 1.0847 | 2.7054 |  | OK | OK | OK | OK | 93.3253 | OK | OK | OK | OK | OK
44811.7916 | 0:36 | 95 | 132.6407 | 130.6781 | 143.3553 | 84.8087 | 107.3039 | 107.3039 | 38.9462 | 39.9582 | 38.6879 | 42.6033 | 50 | 63.3481 | 197.5059 | 56.7926 | 58.212 | 109.2537 | ON | 39.29 | 108.3 | 45.5187 | 35.0553 | 0.66817 | 2.6451 | 0.9961 | 0.9961 | 2.7189 |  | OK | Low Charge | OK | OK | 93.3507 | OK | OK | OK | OK | OK
44811.7917 | 0:36 | 95 | 132.6843 | 130.6759 | 143.4414 | 84.7698 | 107.2901 | 107.2901 | 38.8368 | 39.8628 | 38.5801 | 42.5096 | 50 | 63.3288 | 197.63 | 56.6539 | 58.0127 | 109.2819 | ON | 39.29 | 108.3 | 45.4798 | 35.1414 | 0.57277 | 2.6469 | 1.0099 | 1.0099 | 2.7212 |  | OK | OK | OK | OK | 93.3943 | OK | OK | OK | OK | OK
44811.7918 | 0:36 | 95 | 132.7451 | 130.7766 | 143.4732 | 84.7185 | 107.4561 | 107.4561 | 38.7818 | 39.7966 | 38.5168 | 42.4044 | 50 | 63.2304 | 197.874 | 56.5592 | 57.8711 | 109.4033 | ON | 39.29 | 108.3 | 45.4285 | 35.1732 | 0.5066 | 2.6078 | 0.8439 | 0.8439 | 2.7277 |  | OK | Low Charge | OK | OK | 93.4551 | OK | OK | OK | OK | OK
44811.7919 | 0:36 | 95 | 132.8243 | 130.8494 | 143.5675 | 84.7128 | 107.5637 | 107.5637 | 38.6763 | 39.7826 | 38.3968 | 42.2815 | 50 | 63.1133 | 198.3156 | 56.258 | 57.7169 | 109.5033 | ON | 39.29 | 108.3 | 45.4228 | 35.2675 | 0.49263 | 2.4989 | 0.7363 | 0.7363 | 2.7375 |  | OK | Low Charge | OK | OK | 93.5343 | OK | OK | OK | OK | OK
44811.792 | 0:36 | 95 | 132.9313 | 130.895 | 143.6664 | 84.7222 | 107.6687 | 107.6687 | 38.581 | 39.6335 | 38.306 | 42.1973 | 50 | 62.9788 | 198.4816 | 56.4846 | 57.6548 | 109.6188 | ON | 38.5 | 108.3 | 46.2222 | 35.3664 | 1.1335 | 2.5638 | 0.6313 | 0.6313 | 2.7444 |  | OK | Low Charge | OK | OK | 94.4313 | OK | OK | OK | OK | OK
44811.7921 | 0:37 | 95 | 132.9977 | 130.997 | 143.7715 | 84.7728 | 107.845 | 107.845 | 38.4719 | 39.5787 | 38.2138 | 42.085 | 50 | 62.8791 | 199.1072 | 56.2408 | 57.4593 | 109.7464 | ON | 38.5 | 108.3 | 46.2728 | 35.4715 | 1.0787 | 2.5064 | 0.455 | 0.455 | 2.756 |  | OK | Low Charge | OK | OK | 94.4977 | OK | OK | OK | OK | OK
44811.7923 | 0:37 | 95 | 133.1463 | 131.1453 | 143.9099 | 84.791 | 108.0033 | 108.0033 | 38.365 | 39.5634 | 38.1287 | 41.9605 | 50 | 62.6678 | 199.3961 | 56.1283 | 57.3314 | 109.8897 | ON | 38.5 | 108.3 | 46.291 | 35.6099 | 1.0634 | 2.3971 | 0.2967 | 0.2967 | 2.7673 |  | OK | Low Charge | OK | OK | 94.6463 | OK | OK | OK | OK | OK
44811.7924 | 0:37 | 95 | 133.2627 | 131.2664 | 143.9886 | 84.8465 | 108.132 | 108.132 | 38.3175 | 39.6096 | 38.0424 | 41.8624 | 50 | 62.5624 | 199.9215 | 56.0225 | 57.3057 | 109.9962 | ON | 38.5 | 108.3 | 46.3465 | 35.6886 | 1.1096 | 2.2528 | 0.168 | 0.168 | 2.7778 |  | OK | Low Charge | OK | OK | 94.7627 | OK | OK | OK | OK | OK
44811.7925 | 0:37 | 95 | 133.4155 | 131.3562 | 144.1288 | 84.8765 | 108.217 | 108.217 | 38.2242 | 39.5758 | 37.9508 | 41.7719 | 50 | 62.5455 | 199.932 | 55.8071 | 57.2282 | 110.0938 | ON | 38.5 | 108.3 | 46.3764 | 35.8288 | 1.0758 | 2.196 | 0.083 | 0.083 | 2.7786 |  | OK | Low Charge | OK | OK | 94.9155 | OK | OK | OK | OK | OK
44811.7926 | 0:37 | 95 | 133.4838 | 131.4974 | 144.2661 | 84.951 | 108.3134 | 108.3134 | 38.1699 | 39.5773 | 37.8523 | 41.6895 | 50 | 62.445 | 200.4435 | 55.7489 | 56.9623 | 110.1681 | ON | 38.5 | 110.2 | 46.451 | 34.0661 | 1.0773 | 2.1122 | 1.8866 | 1.8866 | 2.7888 |  | OK | OK | OK | OK | 94.9838 | OK | OK | OK | OK | OK
44811.7927 | 0:37 | 95 | 133.6075 | 131.6553 | 144.3994 | 85.0191 | 108.3846 | 108.3846 | 38.0505 | 39.5502 | 37.7795 | 41.5428 | 50 | 62.3387 | 200.2502 | 55.5833 | 56.7583 | 110.243 | ON | 38.5 | 110.2 | 46.5192 | 34.1994 | 1.0502 | 1.9925 | 1.8154 | 1.8154 | 2.7902 |  | OK | OK | OK | OK | 95.1075 | OK | OK | OK | OK | OK
44811.7928 | 0:38 | 95 | 133.7268 | 131.6984 | 144.5185 | 85.0981 | 108.4698 | 108.4698 | 38.0006 | 39.4501 | 37.6769 | 41.4756 | 50 | 62.2207 | 200.6569 | 55.3831 | 56.7929 | 110.3294 | ON | 38.5 | 110.2 | 46.5981 | 34.3185 | 0.95011 | 2.0255 | 1.7302 | 1.7302 | 2.7997 |  | OK | OK | OK | OK | 95.2268 | OK | OK | OK | OK | OK
44811.793 | 0:38 | 95 | 133.8295 | 131.8466 | 144.661 | 85.1672 | 108.5634 | 108.5634 | 37.8977 | 39.3776 | 37.5791 | 41.3695 | 50 | 62.1431 | 201.0449 | 55.3657 | 56.6863 | 110.3759 | ON | 38.5 | 110.2 | 46.6671 | 34.461 | 0.87764 | 1.9918 | 1.6366 | 1.6366 | 2.8076 |  | OK | OK | OK | OK | 95.3295 | OK | OK | OK | OK | OK
44811.7931 | 0:38 | 95 | 133.9759 | 131.9355 | 144.7677 | 85.2614 | 108.6023 | 108.6023 | 37.8485 | 39.2843 | 37.4928 | 41.3293 | 50 | 62.0728 | 200.7267 | 55.3364 | 56.5578 | 110.4045 | ON | 38.5 | 110.2 | 46.7614 | 34.5677 | 0.78433 | 2.045 | 1.5977 | 1.5977 | 2.806 |  | OK | OK | OK | OK | 95.4759 | OK | OK | OK | OK | OK
44811.7932 | 0:38 | 95 | 134.0393 | 132.0588 | 144.9005 | 85.3223 | 108.6026 | 108.6026 | 37.7737 | 39.242 | 37.3925 | 41.221 | 50 | 61.9686 | 200.9423 | 55.1307 | 56.3612 | 110.4414 | ON | 37.71 | 110.2 | 47.6123 | 34.7005 | 1.532 | 1.9789 | 1.5974 | 1.5974 | 2.8127 |  | OK | OK | OK | OK | 96.3293 | OK | OK | OK | OK | OK
44811.7933 | 0:38 | 95 | 134.1291 | 132.1254 | 145.0493 | 85.3848 | 108.7532 | 108.7532 | 37.7173 | 39.1554 | 37.3373 | 41.1765 | 50 | 61.8357 | 201.4133 | 55.1127 | 56.2311 | 110.5752 | ON | 37.71 | 110.2 | 47.6748 | 34.8493 | 1.4454 | 2.0211 | 1.4468 | 1.4468 | 2.8237 |  | OK | OK | OK | OK | 96.4191 | OK | OK | OK | OK | OK
44811.7934 | 0:38 | 95 | 134.217 | 132.2317 | 145.2028 | 85.4346 | 108.8442 | 108.8442 | 37.6378 | 39.0876 | 37.2372 | 41.088 | 50 | 61.7259 | 201.8069 | 55.0627 | 56.1173 | 110.6396 | ON | 37.71 | 110.2 | 47.7246 | 35.0028 | 1.3776 | 2.0004 | 1.3558 | 1.3558 | 2.8329 |  | OK | OK | OK | OK | 96.507 | OK | OK | OK | OK | OK
44811.7935 | 0:39 | 95 | 134.2685 | 132.3853 | 145.3236 | 85.4801 | 108.7899 | 108.7899 | 37.5666 | 39.0259 | 37.1583 | 41.0019 | 50 | 61.66 | 201.4793 | 54.8584 | 56.0954 | 110.5958 | ON | 37.71 | 110.2 | 47.7701 | 35.1236 | 1.3159 | 1.9759 | 1.4101 | 1.4101 | 2.8311 |  | OK | OK | OK | OK | 96.5585 | OK | OK | OK | OK | OK
44811.7936 | 0:39 | 95 | 134.3983 | 132.4456 | 145.3564 | 85.4769 | 108.7146 | 108.7146 | 37.4832 | 38.9932 | 37.064 | 40.9424 | 50 | 61.6021 | 201.1815 | 54.7056 | 55.9477 | 110.5318 | ON | 37.71 | 110.2 | 47.7669 | 35.1564 | 1.2832 | 1.9493 | 1.4854 | 1.4854 | 2.8293 |  | OK | OK | OK | OK | 96.6883 | OK | OK | OK | OK | OK
44811.7938 | 0:39 | 95 | 134.509 | 132.4772 | 145.4441 | 85.4971 | 108.677 | 108.677 | 37.3854 | 38.8815 | 37.0126 | 40.8922 | 50 | 61.5355 | 201.2645 | 54.5041 | 55.8995 | 110.5066 | ON | 37.71 | 110.2 | 47.7871 | 35.2441 | 1.1715 | 2.0107 | 1.523 | 1.523 | 2.8329 |  | OK | OK | OK | OK | 96.799 | OK | OK | OK | OK | OK
44811.7939 | 0:39 | 95 | 134.5737 | 132.5306 | 145.5142 | 85.4417 | 108.6358 | 108.6358 | 37.309 | 38.7214 | 36.9225 | 40.8409 | 50 | 61.3991 | 201.0583 | 54.3735 | 55.7482 | 110.4293 | ON | 37.71 | 110.2 | 47.7317 | 35.3142 | 1.0114 | 2.1195 | 1.5642 | 1.5642 | 2.8352 |  | OK | OK | OK | OK | 96.8637 | OK | OK | OK | OK | OK
44811.794 | 0:39 | 95 | 134.5809 | 132.5325 | 145.5806 | 85.4216 | 108.6678 | 108.6678 | 37.2315 | 38.56 | 36.8318 | 40.7769 | 50 | 61.2627 | 201.2823 | 54.367 | 55.5016 | 110.4582 | ON | 37.71 | 110.2 | 47.7116 | 35.3806 | 0.85004 | 2.2169 | 1.5322 | 1.5322 | 2.8433 |  | OK | OK | OK | OK | 96.8709 | OK | OK | OK | OK | OK
44811.7941 | 0:39 | 95 | 134.5825 | 132.5447 | 145.5619 | 85.3886 | 108.5228 | 108.5228 | 37.1512 | 38.4416 | 36.75 | 40.6765 | 50 | 61.16 | 200.6521 | 54.2446 | 55.3158 | 110.3397 | ON | 37.71 | 110.2 | 47.6786 | 35.3619 | 0.73156 | 2.235 | 1.6772 | 1.6772 | 2.8388 |  | OK | OK | OK | OK | 96.8725 | OK | OK | OK | OK | OK
44811.7942 | 0:40 | 95 | 134.6382 | 132.504 | 145.5857 | 85.3618 | 108.4239 | 108.4239 | 37.0867 | 38.3213 | 36.6737 | 40.5814 | 50 | 61.0648 | 200.4056 | 54.1919 | 55.2039 | 110.2264 | ON | 37.71 | 110.2 | 47.6518 | 35.3857 | 0.6113 | 2.2601 | 1.7761 | 1.7761 | 2.8391 |  | OK | OK | OK | OK | 96.9282 | OK | OK | OK | OK | OK
44811.7943 | 0:40 | 95 | 134.5578 | 132.5094 | 145.5719 | 85.3383 | 108.3057 | 108.3057 | 36.9997 | 38.2195 | 36.5819 | 40.4849 | 50 | 61.0938 | 200.2376 | 54.0997 | 55.1621 | 110.0962 | ON | 37.71 | 110.2 | 47.6283 | 35.3719 | 0.50951 | 2.2654 | 1.8943 | 1.8943 | 2.8358 |  | OK | OK | OK | OK | 96.8478 | OK | OK | OK | OK | OK
44811.7945 | 0:40 | 95 | 134.4832 | 132.456 | 145.6292 | 85.2945 | 108.2737 | 108.2737 | 36.8849 | 38.0935 | 36.459 | 40.4078 | 50 | 60.8252 | 200.161 | 54.0451 | 55.116 | 110.0959 | ON | 36.91 | 110.2 | 48.3845 | 35.4292 | 1.1835 | 2.3143 | 1.9263 | 1.9263 | 2.8449 |  | OK | OK | OK | OK | 97.5732 | OK | OK | OK | OK | OK
44811.7946 | 0:40 | 95 | 134.4943 | 132.4861 | 145.604 | 85.2246 | 108.1722 | 108.1722 | 36.7768 | 37.8935 | 36.3714 | 40.3099 | 50 | 60.761 | 199.6879 | 53.8143 | 54.9141 | 109.9624 | ON | 36.91 | 108.3 | 48.3146 | 37.304 | 0.98351 | 2.4164 | 0.1278 | 0.1278 | 2.841 |  | OK | Low Charge | OK | OK | 97.5843 | OK | OK | OK | OK | OK
44811.7947 | 0:40 | 95 | 134.5456 | 132.4457 | 145.5634 | 85.1333 | 108.0565 | 108.0565 | 36.6767 | 37.7236 | 36.2739 | 40.2355 | 50 | 60.6676 | 199.6168 | 53.6863 | 54.817 | 109.8781 | ON | 36.91 | 108.3 | 48.2233 | 37.2634 | 0.81356 | 2.5119 | 0.2435 | 0.2435 | 2.8436 |  | OK | Low Charge | OK | OK | 97.6356 | OK | OK | OK | OK | OK
44811.7948 | 0:40 | 95 | 134.429 | 132.3822 | 145.4667 | 84.9862 | 108.0254 | 108.0254 | 36.592 | 37.56 | 36.1686 | 40.1467 | 50 | 60.5408 | 199.3765 | 53.7943 | 54.6658 | 109.8032 | ON | 36.91 | 108.3 | 48.0763 | 37.1667 | 0.65 | 2.5867 | 0.2746 | 0.2746 | 2.8452 |  | OK | Low Charge | OK | OK | 97.519 | OK | OK | OK | OK | OK
44811.7949 | 0:41 | 95 | 134.4002 | 132.3677 | 145.4848 | 84.8432 | 107.9983 | 107.9983 | 36.5275 | 37.3759 | 36.1353 | 40.0868 | 50 | 60.5093 | 199.2522 | 53.4216 | 54.5947 | 109.7698 | ON | 36.91 | 108.3 | 47.9332 | 37.1848 | 0.46587 | 2.7109 | 0.3017 | 0.3017 | 2.8448 |  | OK | Low Charge | OK | OK | 97.4902 | OK | OK | OK | OK | OK
44811.795 | 0:41 | 95 | 134.4128 | 132.2817 | 145.4804 | 84.7704 | 108.0143 | 108.0143 | 36.4181 | 37.2425 | 36.0192 | 39.9861 | 50 | 60.3301 | 199.2803 | 53.2802 | 54.5752 | 109.7792 | ON | 36.91 | 108.3 | 47.8604 | 37.1804 | 0.33248 | 2.7436 | 0.2857 | 0.2857 | 2.8519 |  | OK | Low Charge | OK | OK | 97.5028 | OK | OK | OK | OK | OK
44811.7952 | 0:41 | 95 | 134.3201 | 132.2512 | 145.4009 | 84.6775 | 107.84 | 107.84 | 36.3144 | 37.1878 | 35.8928 | 39.8787 | 50 | 60.1487 | 198.8261 | 53.4169 | 54.457 | 109.6145 | ON | 36.91 | 108.3 | 47.7675 | 37.1009 | 0.2778 | 2.6909 | 0.46 | 0.46 | 2.8528 |  | OK | Low Charge | OK | OK | 97.4101 | OK | OK | OK | OK | OK
44811.7953 | 0:41 | 95 | 134.2596 | 132.1309 | 145.3743 | 84.6242 | 107.6909 | 107.6909 | 36.1919 | 37.1318 | 35.7946 | 39.8104 | 50 | 60.09 | 198.4104 | 53.304 | 54.3302 | 109.4946 | ON | 36.91 | 108.3 | 47.7142 | 37.0743 | 0.22178 | 2.6786 | 0.6091 | 0.6091 | 2.8495 |  | OK | Low Charge | OK | OK | 97.3496 | OK | OK | OK | OK | OK
44811.7954 | 0:41 | 95 | 134.1686 | 132.0816 | 145.312 | 84.561 | 107.5856 | 107.5856 | 36.0841 | 36.9705 | 35.7253 | 39.6975 | 50 | 59.9444 | 198.2059 | 53.2824 | 54.0412 | 109.3878 | ON | 36.1 | 108.3 | 48.461 | 37.012 | 0.87054 | 2.7269 | 0.7144 | 0.7144 | 2.8523 |  | OK | Low Charge | OK | OK | 98.0686 | OK | OK | OK | OK | OK
44811.7955 | 0:41 | 95 | 134.0901 | 132.0473 | 145.2399 | 84.4713 | 107.6353 | 107.6353 | 36.0023 | 36.8417 | 35.6313 | 39.6212 | 50 | 59.8401 | 198.4703 | 53.1355 | 53.9809 | 109.4214 | ON | 36.1 | 108.3 | 48.3713 | 36.9399 | 0.74175 | 2.7795 | 0.6647 | 0.6647 | 2.8598 |  | OK | Low Charge | OK | OK | 97.9901 | OK | OK | OK | OK | OK
44811.7956 | 0:42 | 95 | 134.0451 | 131.9701 | 145.1917 | 84.3943 | 107.5352 | 107.5352 | 35.8941 | 36.6455 | 35.547 | 39.5137 | 50 | 59.7517 | 197.9733 | 52.9523 | 53.8448 | 109.304 | ON | 36.1 | 108.3 | 48.2943 | 36.8917 | 0.54549 | 2.8682 | 0.7648 | 0.7648 | 2.8565 |  | OK | Low Charge | OK | OK | 97.9451 | OK | OK | OK | OK | OK
44811.7957 | 0:42 | 95 | 133.9313 | 131.9277 | 145.102 | 84.3252 | 107.3445 | 107.3445 | 35.8073 | 36.5879 | 35.4001 | 39.3754 | 50 | 59.645 | 197.464 | 52.685 | 53.8486 | 109.1425 | ON | 36.1 | 108.3 | 48.2252 | 36.802 | 0.48789 | 2.7875 | 0.9555 | 0.9555 | 2.8538 |  | OK | Low Charge | OK | OK | 97.8313 | OK | OK | OK | OK | OK
44811.7958 | 0:42 | 95 | 133.9698 | 131.8154 | 145.0913 | 84.234 | 107.392 | 107.392 | 35.7229 | 36.5247 | 35.3248 | 39.2563 | 50 | 59.4585 | 197.7172 | 52.5798 | 53.7453 | 109.1475 | ON | 36.1 | 108.3 | 48.134 | 36.7913 | 0.42474 | 2.7316 | 0.908 | 0.908 | 2.8644 |  | OK | Low Charge | OK | OK | 97.8698 | OK | OK | OK | OK | OK
44811.796 | 0:42 | 95 | 133.9642 | 131.7388 | 145.0471 | 84.1497 | 107.419 | 107.419 | 35.624 | 36.4321 | 35.2382 | 39.1564 | 50 | 59.335 | 198.0539 | 52.5598 | 53.5943 | 109.1539 | ON | 36.1 | 108.3 | 48.0497 | 36.7471 | 0.33206 | 2.7243 | 0.881 | 0.881 | 2.8737 |  | OK | Low Charge | OK | OK | 97.8642 | OK | OK | OK | OK | OK
44811.7961 | 0:42 | 95 | 133.8896 | 131.7346 | 145.009 | 84.0283 | 107.3378 | 107.3378 | 35.5386 | 36.3566 | 35.1247 | 39.0902 | 50 | 59.2092 | 197.7532 | 52.335 | 53.4552 | 109.081 | ON | 36.1 | 108.3 | 47.9283 | 36.709 | 0.25664 | 2.7336 | 0.9622 | 0.9622 | 2.8745 |  | OK | Low Charge | OK | OK | 97.7896 | OK | OK | OK | OK | OK
44811.7962 | 0:42 | 95 | 133.8439 | 131.662 | 144.9832 | 83.9217 | 107.2672 | 107.2672 | 35.4259 | 36.2625 | 35.0708 | 39.0111 | 50 | 59.1876 | 197.3156 | 52.449 | 53.3791 | 109.0163 | ON | 36.1 | 108.3 | 47.8217 | 36.6832 | 0.16254 | 2.7486 | 1.0328 | 1.0328 | 2.8694 |  | OK | OK | OK | OK | 97.7439 | OK | OK | OK | OK | OK
44811.7963 | 0:43 | 95 | 133.8911 | 131.6435 | 145.0046 | 83.8371 | 107.5376 | 107.5376 | 35.3468 | 36.1773 | 34.9626 | 38.9295 | 50 | 59.0301 | 198.0475 | 52.0337 | 53.1765 | 109.2382 | ON | 36.1 | 108.3 | 47.7371 | 36.7046 | 0.07728 | 2.7522 | 0.7624 | 0.7624 | 2.8855 |  | OK | Low Charge | OK | OK | 97.7911 | OK | OK | OK | OK | OK
44811.7964 | 0:43 | 95 | 133.8029 | 131.6642 | 144.9491 | 83.7801 | 107.3748 | 107.3748 | 35.2242 | 36.0284 | 34.8652 | 38.8386 | 50 | 58.9526 | 197.5671 | 52.1375 | 53.151 | 109.0916 | ON | 35.28 | 108.3 | 48.5001 | 36.6491 | 0.7484 | 2.8102 | 0.9252 | 0.9252 | 2.882 |  | OK | Low Charge | OK | OK | 98.5229 | OK | OK | OK | OK | OK
44811.7965 | 0:43 | 95 | 133.6568 | 131.5647 | 144.9045 | 83.6995 | 107.285 | 107.285 | 35.1513 | 35.9895 | 34.7858 | 38.755 | 50 | 58.9039 | 197.6049 | 52.0316 | 53.0602 | 109.006 | ON | 35.28 | 108.3 | 48.4195 | 36.6045 | 0.70949 | 2.7655 | 1.015 | 1.015 | 2.8844 |  | OK | OK | OK | OK | 98.3768 | OK | OK | OK | OK | OK
44811.7967 | 0:43 | 95 | 133.6003 | 131.5467 | 144.8999 | 83.6864 | 107.2301 | 107.2301 | 35.0881 | 35.8205 | 34.6958 | 38.6683 | 50 | 58.77 | 197.4303 | 51.8608 | 52.9129 | 108.9795 | ON | 35.28 | 108.3 | 48.4064 | 36.5999 | 0.54053 | 2.8478 | 1.0699 | 1.0699 | 2.8873 |  | OK | OK | OK | OK | 98.3203 | OK | OK | OK | OK | OK
44811.7968 | 0:43 | 95 | 133.5411 | 131.511 | 144.7946 | 83.6551 | 107.0705 | 107.0705 | 34.9681 | 35.6895 | 34.5895 | 38.601 | 50 | 58.6334 | 196.7281 | 51.7819 | 52.8798 | 108.799 | ON | 35.28 | 108.3 | 48.3751 | 36.4946 | 0.40955 | 2.9114 | 1.2295 | 1.2295 | 2.8831 |  | OK | OK | OK | OK | 98.2611 | OK | OK | OK | OK | OK
44811.7969 | 0:43 | 95 | 133.5325 | 131.3737 | 144.7347 | 83.6076 | 107.0534 | 107.0534 | 34.8974 | 35.5776 | 34.5213 | 38.5477 | 50 | 58.6773 | 196.767 | 51.6283 | 52.602 | 108.8066 | ON | 35.28 | 108.3 | 48.3276 | 36.4347 | 0.29761 | 2.9701 | 1.2466 | 1.2466 | 2.8819 |  | OK | OK | OK | OK | 98.2525 | OK | OK | OK | OK | OK
44811.797 | 0:44 | 95 | 133.4677 | 131.4012 | 144.7568 | 83.4932 | 107.1381 | 107.1381 | 34.7863 | 35.4105 | 34.4441 | 38.4603 | 50 | 58.4074 | 197.0465 | 51.5528 | 52.6393 | 108.856 | ON | 35.28 | 108.3 | 48.2132 | 36.4568 | 0.13054 | 3.0498 | 1.1619 | 1.1619 | 2.8964 |  | OK | OK | OK | OK | 98.1877 | OK | OK | OK | OK | OK
44811.7971 | 0:44 | 95 | 133.4136 | 131.3628 | 144.6783 | 83.387 | 106.9728 | 106.9728 | 34.6977 | 35.3625 | 34.3432 | 38.3887 | 50 | 58.3247 | 196.5619 | 51.6313 | 52.5727 | 108.7161 | ON | 35.28 | 108.3 | 48.107 | 36.3783 | 0.08247 | 3.0262 | 1.3272 | 1.3272 | 2.893 |  | OK | OK | OK | OK | 98.1336 | OK | OK | OK | OK | OK
44811.7972 | 0:44 | 95 | 133.408 | 131.2503 | 144.5777 | 83.2969 | 106.8502 | 106.8502 | 34.6256 | 35.3587 | 34.2642 | 38.3232 | 50 | 58.2838 | 196.0182 | 51.4316 | 52.3565 | 108.5826 | ON | 35.28 | 108.3 | 48.0169 | 36.2777 | 0.07866 | 2.9645 | 1.4498 | 1.4498 | 2.8872 |  | OK | OK | OK | OK | 98.128 | OK | OK | OK | OK | OK
44811.7974 | 0:44 | 95 | 133.3674 | 131.2081 | 144.5228 | 83.2013 | 106.7853 | 106.7853 | 34.5457 | 35.1048 | 34.1705 | 38.23 | 50 | 58.1975 | 196.4054 | 51.2704 | 52.2483 | 108.546 | ON | 35.28 | 108.3 | 47.9213 | 36.2228 | -0.17517 | 3.1252 | 1.5147 | 1.5147 | 2.8959 |  | OK | OK | OK | OK | 98.0874 | OK | OK | OK | OK | OK
44811.7975 | 0:44 | 95 | 133.2755 | 131.138 | 144.4488 | 83.1065 | 106.704 | 106.704 | 34.4648 | 34.8642 | 34.0909 | 38.1511 | 50 | 58.0457 | 196.0716 | 51.2314 | 52.199 | 108.4794 | ON | 35.28 | 108.3 | 47.8265 | 36.1488 | -0.41577 | 3.2869 | 1.596 | 1.596 | 2.8974 |  | OK | OK | OK | OK | 97.9955 | OK | OK | OK | OK | OK
44811.7976 | 0:44 | 95 | 133.2158 | 131.0573 | 144.4121 | 83.0242 | 106.6427 | 106.6427 | 34.3309 | 34.7715 | 34.0047 | 38.0621 | 50 | 57.9549 | 195.8558 | 50.9495 | 52.1295 | 108.4033 | ON | 34.45 | 108.3 | 48.5742 | 36.1121 | 0.32148 | 3.2906 | 1.6573 | 1.6573 | 2.898 |  | OK | OK | OK | OK | 98.7658 | OK | OK | OK | OK | OK
44811.7977 | 0:45 | 95 | 133.1434 | 131.0389 | 144.3002 | 82.9392 | 106.5834 | 106.5834 | 34.237 | 34.5434 | 33.9183 | 37.9723 | 50 | 57.8379 | 195.5811 | 50.9699 | 52.0549 | 108.3564 | ON | 34.45 | 108.3 | 48.4892 | 36.0002 | 0.09342 | 3.4289 | 1.7166 | 1.7166 | 2.8989 |  | OK | OK | OK | OK | 98.6934 | OK | OK | OK | OK | OK
44811.7978 | 0:45 | 95 | 133.1356 | 130.9366 | 144.25 | 82.835 | 106.6172 | 106.6172 | 34.1405 | 34.582 | 33.8293 | 37.9011 | 50 | 57.722 | 195.4544 | 50.833 | 52.0485 | 108.3736 | ON | 34.45 | 108.3 | 48.385 | 35.95 | 0.13202 | 3.3191 | 1.6828 | 1.6828 | 2.9018 |  | OK | OK | OK | OK | 98.6856 | OK | OK | OK | OK | OK
44811.7979 | 0:45 | 95 | 133.1652 | 130.947 | 144.2551 | 82.8206 | 106.6791 | 106.6791 | 34.0228 | 34.4302 | 33.7377 | 37.7862 | 50 | 57.6418 | 195.9916 | 50.9229 | 51.8287 | 108.4071 | ON | 34.45 | 108.3 | 48.3706 | 35.9551 | -0.01984 | 3.356 | 1.6209 | 1.6209 | 2.9124 |  | OK | OK | OK | OK | 98.7152 | OK | OK | OK | OK | OK
44811.798 | 0:45 | 95 | 133.0302 | 130.8999 | 144.2231 | 82.8274 | 106.573 | 106.573 | 33.9337 | 34.492 | 33.6158 | 37.6632 | 50 | 57.4204 | 195.4152 | 50.8274 | 51.7074 | 108.318 | ON | 34.45 | 108.3 | 48.3774 | 35.9231 | 0.04205 | 3.1711 | 1.727 | 1.727 | 2.9134 |  | OK | OK | OK | OK | 98.5802 | OK | OK | OK | OK | OK
44811.7982 | 0:45 | 95 | 132.9548 | 130.8981 | 144.1983 | 82.7794 | 106.5131 | 106.5131 | 33.8423 | 34.3648 | 33.559 | 37.5843 | 50 | 57.3849 | 195.5556 | 50.7326 | 51.5082 | 108.3182 | ON | 34.45 | 108.3 | 48.3294 | 35.8983 | -0.08516 | 3.2194 | 1.7869 | 1.7869 | 2.9168 |  | OK | OK | OK | OK | 98.5048 | OK | OK | OK | OK | OK
44811.7983 | 0:45 | 95 | 133.0737 | 130.8503 | 144.1904 | 82.7413 | 106.5919 | 106.5919 | 33.7998 | 34.1929 | 33.4653 | 37.4934 | 50 | 57.3161 | 195.7776 | 50.5139 | 51.5044 | 108.3438 | ON | 34.45 | 108.3 | 48.2913 | 35.8904 | -0.25713 | 3.3006 | 1.7081 | 1.7081 | 2.9226 |  | OK | OK | OK | OK | 98.6237 | OK | OK | OK | OK | OK
44811.7984 | 0:46 | 95 | 132.9486 | 130.7849 | 144.1399 | 82.712 | 106.5241 | 106.5241 | 33.6702 | 34.152 | 33.358 | 37.3995 | 50 | 57.1475 | 195.5062 | 50.476 | 51.4192 | 108.2731 | ON | 34.45 | 108.3 | 48.262 | 35.8399 | -0.29804 | 3.2475 | 1.7759 | 1.7759 | 2.9257 |  | OK | OK | OK | OK | 98.4986 | OK | OK | OK | OK | OK
44811.7985 | 0:46 | 95 | 132.9685 | 130.8079 | 144.162 | 82.6786 | 106.6013 | 106.6013 | 33.5632 | 34.1451 | 33.2647 | 37.2892 | 50 | 57.1288 | 195.7041 | 50.2766 | 51.2889 | 108.345 | ON | 34.45 | 108.3 | 48.2286 | 35.862 | -0.30488 | 3.1441 | 1.6987 | 1.6987 | 2.9292 |  | OK | OK | OK | OK | 98.5185 | OK | OK | OK | OK | OK
44811.7986 | 0:46 | 95 | 132.9963 | 130.7724 | 144.1529 | 82.6865 | 106.6362 | 106.6362 | 33.5219 | 34.0351 | 33.1972 | 37.1862 | 50 | 57.0561 | 195.7685 | 50.2936 | 51.3636 | 108.4034 | ON | 34.45 | 108.3 | 48.2366 | 35.8529 | -0.41492 | 3.1511 | 1.6638 | 1.6638 | 2.9331 |  | OK | OK | OK | OK | 98.5463 | OK | OK | OK | OK | OK
44811.7987 | 0:46 | 95 | 133.0792 | 130.8674 | 144.2251 | 82.6923 | 106.8547 | 106.8547 | 33.4626 | 33.9418 | 33.1414 | 37.1036 | 50 | 56.976 | 196.4811 | 50.0833 | 51.0284 | 108.5389 | ON | 33.62 | 108.3 | 49.0723 | 35.9251 | 0.32177 | 3.1618 | 1.4453 | 1.4453 | 2.9463 |  | OK | OK | OK | OK | 99.4592 | OK | OK | OK | OK | OK
44811.7989 | 0:46 | 95 | 133 | 130.9154 | 144.2707 | 82.6869 | 106.7571 | 106.7571 | 33.3473 | 33.9597 | 33.0388 | 37.0225 | 50 | 56.7977 | 196.0083 | 50.137 | 50.9348 | 108.4813 | ON | 33.62 | 108.3 | 49.0669 | 35.9707 | 0.33965 | 3.0628 | 1.5429 | 1.5429 | 2.9471 |  | OK | OK | OK | OK | 99.38 | OK | OK | OK | OK | OK
44811.799 | 0:46 | 95 | 133.0566 | 130.899 | 144.3009 | 82.6909 | 106.6514 | 106.6514 | 33.2731 | 34.013 | 32.9391 | 36.9076 | 50 | 56.7688 | 195.7212 | 49.8332 | 50.724 | 108.4041 | ON | 33.62 | 108.3 | 49.0709 | 36.0009 | 0.39303 | 2.8946 | 1.6486 | 1.6486 | 2.9442 |  | OK | OK | OK | OK | 99.4366 | OK | OK | OK | OK | OK
44811.7991 | 0:47 | 95 | 133.087 | 130.8599 | 144.2199 | 82.7126 | 106.59 | 106.59 | 33.1844 | 33.8038 | 32.847 | 36.8435 | 50 | 56.5921 | 195.7802 | 49.9062 | 50.7623 | 108.364 | ON | 33.62 | 108.3 | 49.0926 | 35.9199 | 0.18384 | 3.0397 | 1.71 | 1.71 | 2.9524 |  | OK | OK | OK | OK | 99.467 | OK | OK | OK | OK | OK
44811.7992 | 0:47 | 95 | 133.1457 | 130.9031 | 144.2462 | 82.7204 | 106.6825 | 106.6825 | 33.1261 | 33.6422 | 32.7877 | 36.7407 | 50 | 56.5508 | 195.8303 | 49.8367 | 50.6689 | 108.4348 | ON | 33.62 | 108.3 | 49.1004 | 35.9462 | 0.02217 | 3.0985 | 1.6175 | 1.6175 | 2.9548 |  | OK | OK | OK | OK | 99.5257 | OK | OK | OK | OK | OK
44811.7993 | 0:47 | 95 | 133.2452 | 130.9883 | 144.3243 | 82.7172 | 106.8235 | 106.8235 | 33.048 | 33.5077 | 32.7022 | 36.687 | 50 | 56.4493 | 196.3544 | 49.6196 | 50.5451 | 108.5501 | ON | 33.62 | 108.3 | 49.0972 | 36.0243 | -0.11228 | 3.1793 | 1.4765 | 1.4765 | 2.9664 |  | OK | OK | OK | OK | 99.6252 | OK | OK | OK | OK | OK
44811.7994 | 0:47 | 95 | 133.2874 | 131.0507 | 144.4923 | 82.7322 | 107.0908 | 107.0908 | 32.9699 | 33.5582 | 32.6195 | 36.5969 | 50 | 56.3873 | 197.2495 | 49.5424 | 50.5185 | 108.7833 | ON | 33.62 | 108.3 | 49.1122 | 36.1923 | -0.06178 | 3.0387 | 1.2092 | 1.2092 | 2.9815 |  | OK | OK | OK | OK | 99.6674 | OK | OK | OK | OK | OK
44811.7996 | 0:47 | 95 | 133.4204 | 131.233 | 144.6448 | 82.7181 | 107.2747 | 107.2747 | 32.9304 | 33.4863 | 32.5595 | 36.5054 | 50 | 56.3606 | 197.3724 | 49.5416 | 50.5151 | 108.9259 | ON | 33.62 | 108.3 | 49.0981 | 36.3448 | -0.13366 | 3.019 | 1.0253 | 1.0253 | 2.9844 |  | OK | OK | OK | OK | 99.8004 | OK | OK | OK | OK | OK
44811.7997 | 0:47 | 95 | 133.5867 | 131.3338 | 144.7201 | 82.8016 | 107.3941 | 107.3941 | 32.8443 | 33.4121 | 32.4832 | 36.4162 | 50 | 56.2589 | 197.7696 | 49.4061 | 50.3241 | 109.0471 | ON | 33.62 | 108.3 | 49.1816 | 36.4201 | -0.20795 | 3.0041 | 0.9059 | 0.9059 | 2.9943 |  | OK | Low Charge | OK | OK | 99.9667 | OK | OK | OK | OK | OK
44811.7998 | 0:48 | 95 | 133.7466 | 131.4912 | 144.8867 | 82.8848 | 107.5436 | 107.5436 | 32.7675 | 33.5027 | 32.4126 | 36.3248 | 50 | 56.1534 | 198.1675 | 49.3999 | 50.1334 | 109.1853 | ON | 33.62 | 108.3 | 49.2648 | 36.5867 | -0.11727 | 2.822 | 0.7564 | 0.7564 | 3.0043 |  | OK | Low Charge | OK | OK | 100.1266 | OK | OK | OK | OK | OK
44811.7999 | 0:48 | 95 | 133.7812 | 131.6418 | 144.9664 | 82.9788 | 107.6025 | 107.6025 | 32.7061 | 33.5904 | 32.3192 | 36.2519 | 50 | 56.1141 | 198.4089 | 49.21 | 50.1386 | 109.2781 | ON | 33.62 | 108.3 | 49.3588 | 36.6664 | -0.0296 | 2.6615 | 0.6975 | 0.6975 | 3.0094 |  | OK | Low Charge | OK | OK | 100.1612 | OK | OK | OK | OK | OK
44811.8 | 0:48 | 95 | 133.8788 | 131.708 | 145.0897 | 83.0076 | 107.6983 | 107.6983 | 32.67 | 33.5119 | 32.2734 | 36.1758 | 50 | 55.9684 | 198.5927 | 49.1324 | 49.9774 | 109.3217 | ON | 32.77 | 108.3 | 50.2377 | 36.7897 | 0.74189 | 2.6639 | 0.6017 | 0.6017 | 3.0182 |  | OK | Low Charge | OK | OK | 101.1088 | OK | OK | OK | OK | OK
44811.8001 | 0:48 | 95 | 134.0463 | 131.7958 | 145.2281 | 83.1223 | 107.8041 | 107.8041 | 32.5849 | 33.4615 | 32.2144 | 36.1455 | 50 | 55.9451 | 199.1926 | 48.9912 | 49.9372 | 109.4163 | ON | 32.77 | 108.3 | 50.3523 | 36.9281 | 0.69151 | 2.684 | 0.4959 | 0.4959 | 3.0277 |  | OK | Low Charge | OK | OK | 101.2763 | OK | OK | OK | OK | OK
44811.8002 | 0:48 | 95 | 134.1676 | 131.9051 | 145.3592 | 83.2023 | 107.8363 | 107.8363 | 32.5306 | 33.3628 | 32.118 | 36.048 | 50 | 55.8203 | 199.0495 | 48.6154 | 49.6267 | 109.461 | ON | 32.77 | 108.3 | 50.4323 | 37.0592 | 0.5928 | 2.6852 | 0.4637 | 0.4637 | 3.031 |  | OK | Low Charge | OK | OK | 101.3976 | OK | OK | OK | OK | OK
44811.8004 | 0:48 | 95 | 134.2891 | 132.0623 | 145.4407 | 83.2541 | 107.8513 | 107.8513 | 32.4638 | 33.2587 | 32.0638 | 35.9793 | 50 | 55.8097 | 199.0301 | 48.6689 | 49.4668 | 109.4783 | ON | 32.77 | 108.3 | 50.4841 | 37.1407 | 0.48871 | 2.7206 | 0.4487 | 0.4487 | 3.0312 |  | OK | Low Charge | OK | OK | 101.5191 | OK | OK | OK | OK | OK
44811.8005 | 0:49 | 95 | 134.4096 | 132.1084 | 145.5716 | 83.3073 | 107.8904 | 107.8904 | 32.391 | 33.2104 | 31.9869 | 35.9504 | 50 | 55.792 | 199.119 | 48.6408 | 49.4158 | 109.5067 | ON | 32.77 | 108.3 | 50.5374 | 37.2716 | 0.44039 | 2.74 | 0.4096 | 0.4096 | 3.0332 |  | OK | Low Charge | OK | OK | 101.6396 | OK | OK | OK | OK | OK
44811.8006 | 0:49 | 95 | 134.4052 | 132.248 | 145.7414 | 83.3628 | 107.924 | 107.924 | 32.3432 | 33.1795 | 31.9313 | 35.8736 | 50 | 55.698 | 199.1987 | 48.578 | 49.4695 | 109.533 | ON | 32.77 | 108.3 | 50.5928 | 37.4414 | 0.40948 | 2.6941 | 0.376 | 0.376 | 3.0384 |  | OK | Low Charge | OK | OK | 101.6352 | OK | OK | OK | OK | OK
44811.8007 | 0:49 | 95 | 134.4909 | 132.3348 | 145.7981 | 83.4065 | 107.9669 | 107.9669 | 32.3126 | 33.1617 | 31.832 | 35.8162 | 50 | 55.5665 | 199.409 | 48.6128 | 49.3677 | 109.5738 | ON | 32.77 | 108.3 | 50.6365 | 37.4981 | 0.39174 | 2.6544 | 0.3331 | 0.3331 | 3.0471 |  | OK | Low Charge | OK | OK | 101.7209 | OK | OK | OK | OK | OK
44811.8008 | 0:49 | 95 | 134.5981 | 132.3839 | 145.8778 | 83.3966 | 107.9623 | 107.9623 | 32.2056 | 33.1369 | 31.7863 | 35.7494 | 50 | 55.614 | 199.4576 | 48.2674 | 49.2966 | 109.5655 | ON | 32.77 | 108.3 | 50.6266 | 37.5778 | 0.36693 | 2.6125 | 0.3377 | 0.3377 | 3.0457 |  | OK | Low Charge | OK | OK | 101.8281 | OK | OK | OK | OK | OK
44811.8009 | 0:49 | 95 | 134.6874 | 132.4863 | 145.975 | 83.438 | 107.9497 | 107.9497 | 32.1373 | 33.0166 | 31.6977 | 35.7179 | 50 | 55.499 | 199.235 | 48.2231 | 49.2088 | 109.5494 | ON | 32.77 | 108.3 | 50.668 | 37.675 | 0.24662 | 2.7013 | 0.3503 | 0.3503 | 3.0475 |  | OK | Low Charge | OK | OK | 101.9174 | OK | OK | OK | OK | OK
44811.8011 | 0:49 | 95 | 134.7395 | 132.5196 | 146.0137 | 83.3493 | 107.9293 | 107.9293 | 32.0987 | 32.9113 | 31.6704 | 35.682 | 50 | 55.4226 | 199.0777 | 48.3168 | 49.2099 | 109.5255 | ON | 32.77 | 108.3 | 50.5793 | 37.7137 | 0.14132 | 2.7706 | 0.3707 | 0.3707 | 3.0486 |  | OK | Low Charge | OK | OK | 101.9695 | OK | OK | OK | OK | OK
44811.8012 | 0:50 | 95 | 134.7283 | 132.595 | 146.1017 | 83.321 | 107.8459 | 107.8459 | 32.0027 | 32.8191 | 31.5886 | 35.6312 | 50 | 55.3439 | 198.988 | 48.325 | 49.0257 | 109.4663 | ON | 32.77 | 108.3 | 50.551 | 37.8017 | 0.04909 | 2.8121 | 0.4541 | 0.4541 | 3.0508 |  | OK | Low Charge | OK | OK | 101.9583 | OK | OK | OK | OK | OK
44811.8013 | 0:50 | 95 | 134.8049 | 132.5784 | 146.0825 | 83.2982 | 107.8106 | 107.8106 | 31.9835 | 32.7522 | 31.5209 | 35.5706 | 50 | 55.1907 | 199.1982 | 48.1235 | 49.0769 | 109.4186 | ON | 32.77 | 108.3 | 50.5282 | 37.7825 | -0.01781 | 2.8184 | 0.4894 | 0.4894 | 3.0605 |  | OK | Low Charge | OK | OK | 102.0349 | OK | OK | OK | OK | OK
44811.8014 | 0:50 | 95 | 134.7512 | 132.5939 | 146.1318 | 83.2678 | 107.7407 | 107.7407 | 31.9062 | 32.7231 | 31.4434 | 35.504 | 50 | 55.1418 | 198.8521 | 47.9558 | 48.8302 | 109.3168 | ON | 32.77 | 108.3 | 50.4978 | 37.8318 | -0.04688 | 2.7809 | 0.5593 | 0.5593 | 3.0577 |  | OK | Low Charge | OK | OK | 101.9812 | OK | OK | OK | OK | OK
44811.8015 | 0:50 | 95 | 134.8172 | 132.5421 | 146.1715 | 83.2159 | 107.7335 | 107.7335 | 31.8237 | 32.571 | 31.3759 | 35.456 | 50 | 55.104 | 198.7093 | 47.9556 | 48.7628 | 109.3011 | ON | 32.77 | 108.3 | 50.4459 | 37.8715 | -0.19905 | 2.8851 | 0.5665 | 0.5665 | 3.0573 |  | OK | Low Charge | OK | OK | 102.0472 | OK | OK | OK | OK | OK
44811.8016 | 0:50 | 95 | 134.7943 | 132.5961 | 146.1908 | 83.1947 | 107.6409 | 107.6409 | 31.78 | 32.4218 | 31.3047 | 35.4047 | 50 | 54.9659 | 198.4867 | 47.9469 | 48.8038 | 109.2249 | ON | 31.92 | 108.3 | 51.2747 | 37.8908 | 0.5018 | 2.9829 | 0.6591 | 0.6591 | 3.0601 |  | OK | Low Charge | OK | OK | 102.8743 | OK | OK | OK | OK | OK
44811.8018 | 0:50 | 95 | 134.7852 | 132.5352 | 146.1872 | 83.1526 | 107.6717 | 107.6717 | 31.6961 | 32.2599 | 31.2359 | 35.3313 | 50 | 54.9785 | 198.6073 | 47.6792 | 48.537 | 109.2296 | ON | 31.92 | 108.3 | 51.2326 | 37.8872 | 0.33989 | 3.0714 | 0.6283 | 0.6283 | 3.0613 |  | OK | Low Charge | OK | OK | 102.8652 | OK | OK | OK | OK | OK
44811.8019 | 0:51 | 95 | 134.7813 | 132.6009 | 146.2322 | 83.1451 | 107.6056 | 107.6056 | 31.6199 | 32.1284 | 31.1594 | 35.2501 | 50 | 54.8642 | 198.6712 | 47.6636 | 48.5167 | 109.1801 | ON | 31.92 | 108.3 | 51.2251 | 37.9322 | 0.20841 | 3.1217 | 0.6944 | 0.6944 | 3.0673 |  | OK | Low Charge | OK | OK | 102.8613 | OK | OK | OK | OK | OK
44811.802 | 0:51 | 95 | 134.7195 | 132.5657 | 146.2504 | 83.0986 | 107.6513 | 107.6513 | 31.5601 | 32.0158 | 31.1182 | 35.1851 | 50 | 54.7582 | 198.3732 | 47.7142 | 48.4493 | 109.1831 | ON | 31.92 | 108.3 | 51.1786 | 37.9504 | 0.09577 | 3.1694 | 0.6487 | 0.6487 | 3.0676 |  | OK | Low Charge | OK | OK | 102.7995 | OK | OK | OK | OK | OK
44811.8021 | 0:51 | 95 | 134.7574 | 132.5761 | 146.3086 | 83.0722 | 107.4965 | 107.4965 | 31.4499 | 31.9783 | 31.0082 | 35.1124 | 50 | 54.6349 | 197.9505 | 47.3137 | 48.2995 | 109.0634 | ON | 31.92 | 108.3 | 51.1522 | 38.0086 | 0.05832 | 3.134 | 0.8035 | 0.8035 | 3.067 |  | OK | Low Charge | OK | OK | 102.8374 | OK | OK | OK | OK | OK
44811.8022 | 0:51 | 95 | 134.7313 | 132.521 | 146.2538 | 83.0122 | 107.2971 | 107.2971 | 31.3898 | 32.024 | 30.9563 | 35.0693 | 50 | 54.5348 | 197.6339 | 47.4888 | 48.2375 | 108.9093 | ON | 31.92 | 108.3 | 51.0922 | 37.9538 | 0.10399 | 3.0453 | 1.0029 | 1.0029 | 3.0669 |  | OK | OK | OK | OK | 102.8113 | OK | OK | OK | OK | OK
44811.8023 | 0:51 | 95 | 134.7567 | 132.4995 | 146.2131 | 82.9364 | 107.2203 | 107.2203 | 31.3262 | 31.9477 | 30.909 | 35.0209 | 50 | 54.593 | 197.1807 | 47.3587 | 48.1391 | 108.8042 | ON | 31.92 | 108.3 | 51.0164 | 37.9131 | 0.02774 | 3.0731 | 1.0797 | 1.0797 | 3.0577 |  | OK | OK | OK | OK | 102.8367 | OK | OK | OK | OK | OK
44811.8024 | 0:51 | 95 | 134.6342 | 132.4467 | 146.2044 | 82.8323 | 107.0625 | 107.0625 | 31.2364 | 31.5813 | 30.8048 | 34.9828 | 50 | 54.3344 | 196.8314 | 47.1878 | 48.0459 | 108.6676 | ON | 31.92 | 108.3 | 50.9123 | 37.9044 | -0.33873 | 3.4015 | 1.2375 | 1.2375 | 3.0641 |  | OK | OK | OK | OK | 102.7142 | OK | OK | OK | OK | OK
44811.8026 | 0:52 | 95 | 134.513 | 132.2902 | 146.1073 | 82.7228 | 106.9321 | 106.9321 | 31.1381 | 31.3925 | 30.7072 | 34.9225 | 50 | 54.3377 | 196.716 | 47.0742 | 47.9011 | 108.5376 | ON | 31.92 | 108.3 | 50.8028 | 37.8073 | -0.52747 | 3.53 | 1.3679 | 1.3679 | 3.0623 |  | OK | OK | OK | OK | 102.593 | OK | OK | OK | OK | OK
44811.8027 | 0:52 | 95 | 134.5323 | 132.1775 | 146.0216 | 82.6137 | 106.925 | 106.925 | 31.0495 | 31.3443 | 30.6512 | 34.8621 | 50 | 54.2241 | 196.7633 | 46.7989 | 47.9355 | 108.5162 | ON | 31.92 | 108.3 | 50.6937 | 37.7216 | -0.57574 | 3.5178 | 1.375 | 1.375 | 3.0681 |  | OK | OK | OK | OK | 102.6123 | OK | OK | OK | OK | OK
44811.8028 | 0:52 | 95 | 134.4777 | 132.1797 | 146.0048 | 82.4615 | 106.8341 | 106.8341 | 31.0019 | 31.0768 | 30.572 | 34.8082 | 50 | 54.1291 | 196.2958 | 46.7097 | 47.7675 | 108.4241 | ON | 31.92 | 108.3 | 50.5415 | 37.7048 | -0.84322 | 3.7314 | 1.4659 | 1.4659 | 3.0655 |  | OK | OK | OK | OK | 102.5577 | OK | OK | OK | OK | OK
44811.8029 | 0:52 | 95 | 134.4651 | 132.0848 | 145.9475 | 82.3601 | 106.7878 | 106.7878 | 30.914 | 30.701 | 30.5178 | 34.7139 | 50 | 54.0328 | 196.6746 | 46.6938 | 47.7001 | 108.3915 | ON | 31.92 | 108.3 | 50.4401 | 37.6475 | -1.219 | 4.0129 | 1.5122 | 1.5122 | 3.0753 |  | OK | OK | OK | OK | 102.5451 | OK | OK | OK | OK | OK
44811.803 | 0:52 | 95 | 134.4577 | 132.0233 | 145.9033 | 82.2825 | 106.8822 | 106.8822 | 30.7993 | 30.8842 | 30.4398 | 34.6469 | 50 | 54.0543 | 196.3627 | 46.6834 | 47.543 | 108.4155 | ON | 31.92 | 108.3 | 50.3625 | 37.6033 | -1.0358 | 3.7627 | 1.4178 | 1.4178 | 3.0698 |  | OK | OK | OK | OK | 102.5377 | OK | OK | OK | OK | OK
44811.8031 | 0:52 | 95 | 134.371 | 131.9388 | 145.882 | 82.1734 | 106.7596 | 106.7596 | 30.6995 | 30.853 | 30.3277 | 34.5448 | 50 | 53.7833 | 196.2101 | 46.6649 | 47.5715 | 108.2978 | ON | 31.06 | 108.3 | 51.1134 | 37.582 | -0.20702 | 3.6918 | 1.5404 | 1.5404 | 3.0797 |  | OK | OK | OK | OK | 103.311 | OK | OK | OK | OK | OK
44811.8033 | 0:53 | 95 | 134.2278 | 131.9287 | 145.7723 | 82.0722 | 106.6288 | 106.6288 | 30.6043 | 31.1374 | 30.2589 | 34.437 | 50 | 53.7122 | 195.6509 | 46.5219 | 47.4049 | 108.1939 | ON | 31.06 | 108.3 | 51.0122 | 37.4723 | 0.07739 | 3.2996 | 1.6712 | 1.6712 | 3.0748 |  | OK | OK | OK | OK | 103.1678 | OK | OK | OK | OK | OK
44811.8034 | 0:53 | 95 | 134.0919 | 131.8238 | 145.6647 | 82.0092 | 106.5362 | 106.5362 | 30.5375 | 30.9703 | 30.1653 | 34.3851 | 50 | 53.6444 | 195.7709 | 46.4345 | 47.3028 | 108.1084 | ON | 31.06 | 108.3 | 50.9492 | 37.3647 | -0.08968 | 3.4147 | 1.7638 | 1.7638 | 3.0796 |  | OK | OK | OK | OK | 103.0319 | OK | OK | OK | OK | OK
44811.8035 | 0:53 | 95 | 134.0128 | 131.7432 | 145.6028 | 81.9363 | 106.4554 | 106.4554 | 30.4414 | 30.392 | 30.097 | 34.2904 | 50 | 53.6639 | 195.4093 | 46.3912 | 47.2021 | 108.0431 | ON | 31.06 | 108.3 | 50.8763 | 37.3028 | -0.66802 | 3.8984 | 1.8446 | 1.8446 | 3.0734 |  | OK | OK | OK | OK | 102.9528 | OK | OK | OK | OK | OK
44811.8036 | 0:53 | 95 | 133.9458 | 131.7009 | 145.5843 | 81.8308 | 106.3722 | 106.3722 | 30.3803 | 30.5555 | 30.0409 | 34.2384 | 50 | 53.4928 | 195.2697 | 46.1761 | 47.0722 | 107.9464 | ON | 31.06 | 108.3 | 50.7708 | 37.2843 | -0.50452 | 3.6829 | 1.9278 | 1.9278 | 3.0791 |  | OK | OK | OK | OK | 102.8858 | OK | OK | OK | OK | OK
44811.8037 | 0:53 | 95 | 133.9564 | 131.6432 | 145.5094 | 81.7242 | 106.5101 | 106.5101 | 30.2977 | 30.1865 | 29.9772 | 34.1686 | 50 | 53.3595 | 195.9487 | 46.2106 | 47.1649 | 108.1296 | ON | 31.06 | 108.3 | 50.6642 | 37.2094 | -0.87355 | 3.9822 | 1.7899 | 1.7899 | 3.0951 |  | OK | OK | OK | OK | 102.8964 | OK | OK | OK | OK | OK
44811.8038 | 0:53 | 95 | 133.8823 | 131.6272 | 145.5482 | 81.7005 | 106.6026 | 106.6026 | 30.2337 | 29.8778 | 29.89 | 34.0909 | 50 | 53.3346 | 195.8222 | 45.9908 | 46.8841 | 108.1149 | ON | 31.06 | 108.3 | 50.6405 | 37.2482 | -1.1822 | 4.2131 | 1.6974 | 1.6974 | 3.0943 |  | OK | OK | OK | OK | 102.8223 | OK | OK | OK | OK | OK
44811.804 | 0:54 | 95 | 133.9271 | 131.6157 | 145.4465 | 81.6228 | 106.51 | 106.51 | 30.0868 | 30.402 | 29.777 | 33.9999 | 50 | 53.0998 | 195.2874 | 46.01 | 46.9304 | 108.0481 | ON | 31.06 | 108.3 | 50.5628 | 37.1465 | -0.65801 | 3.5979 | 1.79 | 1.79 | 3.0972 |  | OK | OK | OK | OK | 102.8671 | OK | OK | OK | OK | OK
44811.8041 | 0:54 | 95 | 133.9268 | 131.5514 | 145.4217 | 81.6149 | 106.3454 | 106.3454 | 30.0341 | 30.6056 | 29.7151 | 33.9084 | 50 | 53.1191 | 195.129 | 45.9648 | 46.7462 | 107.879 | ON | 31.06 | 108.3 | 50.5549 | 37.1217 | -0.45445 | 3.3028 | 1.9546 | 1.9546 | 3.0939 |  | OK | OK | OK | OK | 102.8668 | OK | OK | OK | OK | OK
44811.8042 | 0:54 | 95 | 133.8562 | 131.4948 | 145.3464 | 81.5411 | 106.2925 | 106.2925 | 29.9549 | 30.4599 | 29.6275 | 33.8539 | 50 | 53.0578 | 194.7262 | 45.8378 | 46.5841 | 107.817 | ON | 31.06 | 106.4 | 50.4811 | 38.9464 | -0.6001 | 3.394 | 0.1075 | 0.1075 | 3.0908 |  | OK | Low Charge | OK | OK | 102.7962 | OK | OK | OK | OK | OK
44811.8043 | 0:54 | 95 | 133.8069 | 131.405 | 145.2765 | 81.4864 | 106.2284 | 106.2284 | 29.8752 | 30.2946 | 29.572 | 33.7999 | 50 | 53.0975 | 194.669 | 45.742 | 46.6134 | 107.767 | ON | 31.06 | 106.4 | 50.4264 | 38.8765 | -0.76544 | 3.5053 | 0.1716 | 0.1716 | 3.0882 |  | OK | Low Charge | OK | OK | 102.7469 | OK | OK | OK | OK | OK
44811.8044 | 0:54 | 95 | 133.7456 | 131.3628 | 145.2157 | 81.4056 | 106.1618 | 106.1618 | 29.8251 | 30.1633 | 29.4578 | 33.7199 | 50 | 52.8272 | 194.6019 | 45.6755 | 46.4276 | 107.6826 | ON | 30.19 | 106.4 | 51.2156 | 38.8157 | -0.02672 | 3.5566 | 0.2382 | 0.2382 | 3.0995 |  | OK | Low Charge | OK | OK | 103.5556 | OK | OK | OK | OK | OK
44811.8045 | 0:54 | 95 | 133.7194 | 131.3012 | 145.2436 | 81.3199 | 106.1481 | 106.1481 | 29.7713 | 29.7767 | 29.4464 | 33.6758 | 50 | 52.9149 | 194.5823 | 45.584 | 46.4453 | 107.7016 | ON | 30.19 | 106.4 | 51.1299 | 38.8436 | -0.41326 | 3.8991 | 0.2519 | 0.2519 | 3.0952 |  | OK | Low Charge | OK | OK | 103.5294 | OK | OK | OK | OK | OK
44811.8046 | 0:55 | 95 | 133.6212 | 131.297 | 145.2106 | 81.2764 | 106.1556 | 106.1556 | 29.6406 | 29.6928 | 29.3314 | 33.604 | 50 | 52.6778 | 194.7576 | 45.6414 | 46.4034 | 107.7682 | ON | 30.19 | 106.4 | 51.0864 | 38.8106 | -0.49724 | 3.9112 | 0.2444 | 0.2444 | 3.1087 |  | OK | Low Charge | OK | OK | 103.4312 | OK | OK | OK | OK | OK
44811.8048 | 0:55 | 95 | 133.6143 | 131.3024 | 145.2163 | 81.1909 | 106.1911 | 106.1911 | 29.6068 | 30.0776 | 29.2847 | 33.5253 | 50 | 52.6585 | 194.6578 | 45.4006 | 46.2092 | 107.7334 | ON | 30.19 | 106.4 | 51.0009 | 38.8163 | -0.11236 | 3.4477 | 0.2089 | 0.2089 | 3.1081 |  | OK | Low Charge | OK | OK | 103.4243 | OK | OK | OK | OK | OK
44811.8049 | 0:55 | 95 | 133.5132 | 131.2496 | 145.1024 | 81.1101 | 105.9219 | 105.9219 | 29.4986 | 29.4626 | 29.1667 | 33.4374 | 50 | 52.5716 | 194.0131 | 45.3029 | 46.2241 | 107.4818 | ON | 30.19 | 106.4 | 50.9201 | 38.7024 | -0.72739 | 3.9747 | 0.4781 | 0.4781 | 3.1025 |  | OK | Low Charge | OK | OK | 103.3232 | OK | OK | OK | OK | OK
44811.805 | 0:55 | 95 | 133.4986 | 131.1536 | 145.0112 | 81.0234 | 105.8225 | 105.8225 | 29.4174 | 29.7148 | 29.1071 | 33.3845 | 50 | 52.4896 | 193.5671 | 45.3508 | 46.1607 | 107.4079 | ON | 30.19 | 106.4 | 50.8334 | 38.6112 | -0.47515 | 3.6697 | 0.5775 | 0.5775 | 3.0997 |  | OK | Low Charge | OK | OK | 103.3086 | OK | OK | OK | OK | OK
44811.8051 | 0:55 | 95 | 133.5143 | 131.0634 | 144.989 | 80.9613 | 105.8525 | 105.8525 | 29.3896 | 29.1009 | 29.0626 | 33.3228 | 50 | 52.4621 | 193.9022 | 45.1373 | 46.1262 | 107.4116 | ON | 30.19 | 106.4 | 50.7713 | 38.589 | -1.0891 | 4.2219 | 0.5475 | 0.5475 | 3.106 |  | OK | Low Charge | OK | OK | 103.3243 | OK | OK | OK | OK | OK
44811.8052 | 0:55 | 95 | 133.395 | 131.0105 | 144.9443 | 80.867 | 105.7911 | 105.7911 | 29.2756 | 28.7397 | 28.9843 | 33.2577 | 50 | 52.2863 | 193.8005 | 45.2258 | 45.9881 | 107.3885 | ON | 30.19 | 106.4 | 50.6769 | 38.5443 | -1.4503 | 4.518 | 0.6089 | 0.6089 | 3.1126 |  | OK | Low Charge | OK | OK | 103.205 | OK | OK | OK | OK | OK
44811.8053 | 0:56 | 95 | 133.3202 | 131.0153 | 144.8923 | 80.7866 | 105.7757 | 105.7757 | 29.1816 | 29.4626 | 28.8784 | 33.1953 | 50 | 52.2172 | 193.5344 | 45.0344 | 45.8797 | 107.3452 | ON | 30.19 | 106.4 | 50.5966 | 38.4923 | -0.72744 | 3.7328 | 0.6243 | 0.6243 | 3.1118 |  | OK | Low Charge | OK | OK | 103.1302 | OK | OK | OK | OK | OK
44811.8055 | 0:56 | 95 | 133.3676 | 130.9936 | 144.8757 | 80.7399 | 105.7862 | 105.7862 | 29.088 | 29.0571 | 28.819 | 33.0912 | 50 | 52.0662 | 193.6163 | 44.8142 | 45.7397 | 107.37 | ON | 30.19 | 106.4 | 50.5499 | 38.4757 | -1.1329 | 4.0341 | 0.6138 | 0.6138 | 3.1201 |  | OK | Low Charge | OK | OK | 103.1776 | OK | OK | OK | OK | OK
44811.8056 | 0:56 | 95 | 133.3362 | 130.9795 | 144.8584 | 80.6589 | 105.8723 | 105.8723 | 29.0515 | 28.8951 | 28.7423 | 33.0131 | 50 | 52.0205 | 193.9524 | 44.8854 | 45.7809 | 107.4186 | ON | 30.19 | 106.4 | 50.4689 | 38.4584 | -1.2949 | 4.1179 | 0.5277 | 0.5277 | 3.1273 |  | OK | Low Charge | OK | OK | 103.1462 | OK | OK | OK | OK | OK
44811.8057 | 0:56 | 95 | 133.3112 | 130.9386 | 144.8375 | 80.6397 | 105.8096 | 105.8096 | 28.9764 | 28.531 | 28.6687 | 32.9554 | 50 | 51.9964 | 193.4592 | 44.7868 | 45.6444 | 107.4176 | ON | 29.31 | 106.4 | 51.3297 | 38.4375 | -0.77903 | 4.4245 | 0.5904 | 0.5904 | 3.121 |  | OK | Low Charge | OK | OK | 104.0012 | OK | OK | OK | OK | OK
44811.8058 | 0:56 | 95 | 133.3848 | 130.9374 | 144.8524 | 80.6571 | 105.8715 | 105.8715 | 28.8732 | 28.9395 | 28.6265 | 32.8864 | 50 | 52.0782 | 193.7347 | 44.6921 | 45.4946 | 107.445 | ON | 30.19 | 106.4 | 50.4671 | 38.4524 | -1.2505 | 3.9469 | 0.5285 | 0.5285 | 3.1213 |  | OK | Low Charge | OK | OK | 103.1948 | OK | OK | OK | OK | OK
44811.8059 | 0:56 | 95 | 133.3462 | 130.9344 | 144.8679 | 80.6487 | 105.9407 | 105.9407 | 28.8162 | 28.403 | 28.5435 | 32.7851 | 50 | 51.8233 | 193.9484 | 44.4068 | 45.4535 | 107.5204 | ON | 29.31 | 106.4 | 51.3387 | 38.4679 | -0.90701 | 4.3821 | 0.4593 | 0.4593 | 3.1365 |  | OK | Low Charge | OK | OK | 104.0362 | OK | OK | OK | OK | OK
44811.806 | 0:57 | 95 | 133.3709 | 130.9555 | 144.9435 | 80.6849 | 106.1566 | 106.1566 | 28.7324 | 28.5439 | 28.4602 | 32.7326 | 50 | 51.7357 | 194.7383 | 44.5 | 45.3253 | 107.6887 | ON | 29.31 | 106.4 | 51.3749 | 38.5435 | -0.7661 | 4.1887 | 0.2434 | 0.2434 | 3.1525 |  | OK | Low Charge | OK | OK | 104.0609 | OK | OK | OK | OK | OK
44811.8062 | 0:57 | 95 | 133.5023 | 131.029 | 145.0394 | 80.6987 | 106.3584 | 106.3584 | 28.6898 | 28.6313 | 28.4026 | 32.6288 | 50 | 51.7032 | 195.3579 | 44.5462 | 45.2891 | 107.884 | ON | 29.31 | 108.3 | 51.3887 | 36.7394 | -0.67866 | 3.9975 | 1.9416 | 1.9416 | 3.1634 |  | OK | OK | OK | OK | 104.1923 | OK | OK | OK | OK | OK
44811.8063 | 0:57 | 95 | 133.569 | 131.1936 | 145.1256 | 80.7599 | 106.427 | 106.427 | 28.6079 | 28.4388 | 28.3527 | 32.5285 | 50 | 51.5785 | 195.2537 | 44.3313 | 45.2313 | 107.9055 | ON | 29.31 | 108.3 | 51.4499 | 36.8256 | -0.87122 | 4.0898 | 1.873 | 1.873 | 3.1678 |  | OK | OK | OK | OK | 104.259 | OK | OK | OK | OK | OK
44811.8064 | 0:57 | 95 | 133.6634 | 131.227 | 145.1707 | 80.7987 | 106.4308 | 106.4308 | 28.4959 | 28.6243 | 28.2165 | 32.4642 | 50 | 51.5162 | 195.1757 | 44.36 | 45.0703 | 107.9025 | ON | 29.31 | 108.3 | 51.4887 | 36.8707 | -0.68573 | 3.8399 | 1.8692 | 1.8692 | 3.1695 |  | OK | OK | OK | OK | 104.3534 | OK | OK | OK | OK | OK
44811.8065 | 0:57 | 95 | 133.6959 | 131.2385 | 145.1437 | 80.8746 | 106.1741 | 106.1741 | 28.4343 | 29.0079 | 28.1607 | 32.3647 | 50 | 51.4866 | 194.6961 | 44.1262 | 44.9427 | 107.7265 | ON | 29.31 | 106.4 | 51.5646 | 38.7437 | -0.30207 | 3.3567 | 0.2259 | 0.2259 | 3.1637 |  | OK | Low Charge | OK | OK | 104.3859 | OK | OK | OK | OK | OK
44811.8066 | 0:57 | 95 | 133.7106 | 131.187 | 145.0991 | 80.9219 | 106.1664 | 106.1664 | 28.4126 | 29.0241 | 28.1424 | 32.3191 | 50 | 51.486 | 194.9042 | 44.0341 | 44.8979 | 107.7237 | ON | 29.31 | 106.4 | 51.6119 | 38.6991 | -0.28589 | 3.295 | 0.2336 | 0.2336 | 3.1669 |  | OK | Low Charge | OK | OK | 104.4006 | OK | OK | OK | OK | OK
44811.8067 | 0:58 | 95 | 133.6662 | 131.2523 | 145.2345 | 80.9139 | 106.3342 | 106.3342 | 28.4062 | 28.4535 | 28.0923 | 32.2555 | 50 | 51.3523 | 195.09 | 44.0822 | 44.8596 | 107.8446 | ON | 29.31 | 108.3 | 51.6039 | 36.9345 | -0.85652 | 3.802 | 1.9658 | 1.9658 | 3.1761 |  | OK | OK | OK | OK | 104.3562 | OK | OK | OK | OK | OK
44811.8068 | 0:58 | 95 | 133.7507 | 131.3957 | 145.3107 | 80.9557 | 106.4645 | 106.4645 | 28.3306 | 28.2388 | 28.0088 | 32.2042 | 50 | 51.3203 | 195.4938 | 44.0112 | 44.7254 | 107.9709 | ON | 29.31 | 108.3 | 51.6457 | 37.0107 | -1.0712 | 3.9655 | 1.8355 | 1.8355 | 3.1838 |  | OK | OK | OK | OK | 104.4407 | OK | OK | OK | OK | OK
44811.807 | 0:58 | 95 | 133.9089 | 131.5704 | 145.4623 | 80.9714 | 106.6271 | 106.6271 | 28.2691 | 28.5558 | 27.9516 | 32.1361 | 50 | 51.2559 | 195.6461 | 43.8695 | 44.6766 | 108.1175 | ON | 29.31 | 108.3 | 51.6614 | 37.1623 | -0.75422 | 3.5803 | 1.6729 | 1.6729 | 3.1892 |  | OK | OK | OK | OK | 104.5989 | OK | OK | OK | OK | OK
44811.8071 | 0:58 | 95 | 134.0945 | 131.6113 | 145.5871 | 81.0545 | 106.7757 | 106.7757 | 28.2267 | 28.1476 | 27.911 | 32.0767 | 50 | 51.2745 | 196.418 | 43.7239 | 44.6283 | 108.2459 | ON | 29.31 | 108.3 | 51.7445 | 37.2871 | -1.1624 | 3.929 | 1.5243 | 1.5243 | 3.2 |  | OK | OK | OK | OK | 104.7845 | OK | OK | OK | OK | OK
44811.8072 | 0:58 | 95 | 134.1854 | 131.7834 | 145.7281 | 81.177 | 106.8977 | 106.8977 | 28.1414 | 28.5731 | 27.8746 | 31.9893 | 50 | 51.2061 | 196.4448 | 43.8204 | 44.6151 | 108.3341 | ON | 29.31 | 108.3 | 51.867 | 37.4281 | -0.73687 | 3.4161 | 1.4023 | 1.4023 | 3.2037 |  | OK | OK | OK | OK | 104.8754 | OK | OK | OK | OK | OK
44811.8073 | 0:58 | 95 | 134.3015 | 131.8963 | 145.8227 | 81.2657 | 107.0309 | 107.0309 | 28.0958 | 28.8356 | 27.7905 | 31.8916 | 50 | 51.1328 | 196.8161 | 43.7227 | 44.4891 | 108.4787 | ON | 29.31 | 108.3 | 51.9558 | 37.5227 | -0.47442 | 3.056 | 1.2691 | 1.2691 | 3.2129 |  | OK | OK | OK | OK | 104.9915 | OK | OK | OK | OK | OK
44811.8074 | 0:59 | 95 | 134.3957 | 132.0082 | 145.9643 | 81.3457 | 107.081 | 107.081 | 28.0721 | 28.8094 | 27.7196 | 31.8212 | 50 | 50.992 | 197.018 | 43.5362 | 44.3406 | 108.5569 | ON | 28.42 | 108.3 | 52.9257 | 37.6643 | 0.38941 | 3.0118 | 1.219 | 1.219 | 3.2229 |  | OK | OK | OK | OK | 105.9757 | OK | OK | OK | OK | OK
44811.8075 | 0:59 | 95 | 134.6396 | 132.1179 | 146.0799 | 81.4244 | 107.1715 | 107.1715 | 28.0084 | 28.7125 | 27.6358 | 31.7476 | 50 | 50.9472 | 197.4806 | 43.6131 | 44.2977 | 108.6133 | ON | 28.42 | 108.3 | 53.0044 | 37.7799 | 0.29249 | 3.0351 | 1.1285 | 1.1285 | 3.2321 |  | OK | OK | OK | OK | 106.2196 | OK | OK | OK | OK | OK
44811.8077 | 0:59 | 95 | 134.7083 | 132.2216 | 146.1568 | 81.4766 | 107.2004 | 107.2004 | 27.9722 | 28.7174 | 27.6008 | 31.6965 | 50 | 50.9211 | 197.3507 | 43.4634 | 44.1471 | 108.6383 | ON | 28.42 | 108.3 | 53.0566 | 37.8568 | 0.29738 | 2.9791 | 1.0996 | 1.0996 | 3.2314 |  | OK | OK | OK | OK | 106.2883 | OK | OK | OK | OK | OK
44811.8078 | 0:59 | 95 | 134.8402 | 132.2234 | 146.2904 | 81.5609 | 107.2252 | 107.2252 | 27.9295 | 28.66 | 27.5302 | 31.6407 | 50 | 50.9142 | 197.7336 | 43.3929 | 44.128 | 108.7148 | ON | 28.42 | 108.3 | 53.1409 | 37.9904 | 0.23998 | 2.9807 | 1.0748 | 1.0748 | 3.2376 |  | OK | OK | OK | OK | 106.4202 | OK | OK | OK | OK | OK
44811.8079 | 0:59 | 95 | 134.8875 | 132.3569 | 146.396 | 81.6462 | 107.2962 | 107.2962 | 27.8708 | 28.5608 | 27.5015 | 31.5746 | 50 | 50.8792 | 197.5497 | 43.2591 | 44.1127 | 108.754 | ON | 28.42 | 108.3 | 53.2262 | 38.096 | 0.14076 | 3.0138 | 1.0038 | 1.0038 | 3.2365 |  | OK | OK | OK | OK | 106.4675 | OK | OK | OK | OK | OK
44811.808 | 0:59 | 95 | 134.9076 | 132.5117 | 146.5077 | 81.7185 | 107.2539 | 107.2539 | 27.863 | 28.4192 | 27.4496 | 31.5135 | 50 | 50.7076 | 197.7054 | 43.2671 | 43.9711 | 108.7106 | ON | 28.42 | 108.3 | 53.2985 | 38.2077 | -0.00082 | 3.0943 | 1.0461 | 1.0461 | 3.2474 |  | OK | OK | OK | OK | 106.4876 | OK | OK | OK | OK | OK
44811.8081 | 1:00 | 95 | 134.9424 | 132.5949 | 146.6106 | 81.7862 | 107.344 | 107.344 | 27.8329 | 28.3565 | 27.4302 | 31.4568 | 50 | 50.8337 | 197.6358 | 43.1578 | 43.8255 | 108.7685 | ON | 28.42 | 108.3 | 53.3662 | 38.3106 | -0.06348 | 3.1003 | 0.956 | 0.956 | 3.2401 |  | OK | Low Charge | OK | OK | 106.5224 | OK | OK | OK | OK | OK
44811.8082 | 1:00 | 95 | 135.0686 | 132.633 | 146.7107 | 81.8125 | 107.3485 | 107.3485 | 27.7878 | 28.3175 | 27.3263 | 31.4142 | 50 | 50.6158 | 197.9006 | 43.0006 | 43.7615 | 108.7922 | ON | 28.42 | 108.3 | 53.3925 | 38.4107 | -0.10252 | 3.0967 | 0.9515 | 0.9515 | 3.255 |  | OK | Low Charge | OK | OK | 106.6486 | OK | OK | OK | OK | OK
44811.8084 | 1:00 | 95 | 135.1601 | 132.7606 | 146.8708 | 81.8562 | 107.3637 | 107.3637 | 27.7052 | 28.3351 | 27.2615 | 31.3524 | 50 | 50.5757 | 197.7379 | 43.0181 | 43.7273 | 108.7856 | ON | 28.42 | 108.3 | 53.4362 | 38.5708 | -0.08488 | 3.0173 | 0.9363 | 0.9363 | 3.2545 |  | OK | Low Charge | OK | OK | 106.7401 | OK | OK | OK | OK | OK
44811.8085 | 1:00 | 95 | 135.2002 | 132.8062 | 146.8788 | 81.8805 | 107.2406 | 107.2406 | 27.667 | 28.3569 | 27.2411 | 31.3168 | 50 | 50.5722 | 197.3591 | 42.9854 | 43.7392 | 108.7047 | ON | 28.42 | 108.3 | 53.4605 | 38.5788 | -0.0631 | 2.9599 | 1.0594 | 1.0594 | 3.2488 |  | OK | OK | OK | OK | 106.7802 | OK | OK | OK | OK | OK
44811.8086 | 1:00 | 95 | 135.2054 | 132.8414 | 146.9402 | 81.8772 | 107.2831 | 107.2831 | 27.6189 | 28.3171 | 27.175 | 31.2644 | 50 | 50.5455 | 197.4184 | 42.7377 | 43.5256 | 108.7022 | ON | 28.42 | 108.3 | 53.4572 | 38.6402 | -0.10286 | 2.9472 | 1.0169 | 1.0169 | 3.2511 |  | OK | OK | OK | OK | 106.7854 | OK | OK | OK | OK | OK
44811.8087 | 1:00 | 95 | 135.2487 | 132.8801 | 147.0327 | 81.8717 | 107.1968 | 107.1968 | 27.5692 | 28.0358 | 27.1327 | 31.1957 | 50 | 50.4895 | 197.2245 | 42.7616 | 43.6181 | 108.6492 | ON | 28.42 | 108.3 | 53.4517 | 38.7327 | -0.38416 | 3.1598 | 1.1032 | 1.1032 | 3.2509 |  | OK | OK | OK | OK | 106.8287 | OK | OK | OK | OK | OK
44811.8088 | 1:01 | 95 | 135.198 | 132.9034 | 146.9882 | 81.8254 | 107.1353 | 107.1353 | 27.5503 | 28.0106 | 27.0806 | 31.1635 | 50 | 50.4967 | 197.2116 | 42.8145 | 43.4897 | 108.5901 | ON | 28.42 | 108.3 | 53.4054 | 38.6882 | -0.40935 | 3.1529 | 1.1647 | 1.1647 | 3.2503 |  | OK | OK | OK | OK | 106.778 | OK | OK | OK | OK | OK
44811.8089 | 1:01 | 95 | 135.3372 | 132.9404 | 147.0368 | 81.7817 | 107.1704 | 107.1704 | 27.6363 | 28.014 | 27.0572 | 31.1255 | 50 | 50.4227 | 197.206 | 42.6532 | 43.3504 | 108.6191 | ON | 28.42 | 108.3 | 53.3617 | 38.7368 | -0.40605 | 3.1115 | 1.1296 | 1.1296 | 3.254 |  | OK | OK | OK | OK | 106.9172 | OK | OK | OK | OK | OK
44811.809 | 1:01 | 95 | 135.3189 | 132.888 | 147.1149 | 81.7542 | 107.118 | 107.118 | 29.2563 | 27.9121 | 26.9533 | 31.0364 | 50 | 50.2995 | 197.0454 | 42.5029 | 43.2947 | 108.545 | ON | 28.42 | 108.3 | 53.3342 | 38.8149 | -0.50795 | 3.1243 | 1.182 | 1.182 | 3.2576 |  | OK | OK | OK | OK | 106.8989 | OK | OK | OK | OK | OK
44811.8092 | 1:01 | 95 | 135.3827 | 132.9439 | 147.1049 | 81.7177 | 107.0906 | 107.0906 | 29.0048 | 27.9494 | 26.9313 | 31.0028 | 50 | 50.2873 | 197.1528 | 42.5878 | 43.2197 | 108.4985 | ON | 28.42 | 108.3 | 53.2977 | 38.8049 | -0.47059 | 3.0534 | 1.2094 | 1.2094 | 3.2599 |  | OK | OK | OK | OK | 106.9627 | OK | OK | OK | OK | OK
44811.8093 | 1:01 | 95 | 135.3917 | 132.9412 | 147.1441 | 81.7213 | 107.0008 | 107.0008 | 28.4157 | 27.6461 | 26.8466 | 30.9491 | 50 | 50.1811 | 196.6166 | 42.416 | 43.145 | 108.4197 | ON | 28.42 | 108.3 | 53.3013 | 38.8441 | -0.77389 | 3.303 | 1.2992 | 1.2992 | 3.257 |  | OK | OK | OK | OK | 106.9717 | OK | OK | OK | OK | OK
44811.8094 | 1:01 | 95 | 135.4286 | 132.965 | 147.1276 | 81.6826 | 106.9773 | 106.9773 | 27.3781 | 27.625 | 26.7931 | 30.9023 | 50 | 50.1052 | 196.7249 | 42.405 | 43.046 | 108.4048 | ON | 28.42 | 108.3 | 53.2626 | 38.8276 | -0.79497 | 3.2773 | 1.3227 | 1.3227 | 3.2625 |  | OK | OK | OK | OK | 107.0086 | OK | OK | OK | OK | OK
44811.8095 | 1:02 | 95 | 135.4799 | 132.8759 | 147.081 | 81.6056 | 106.8351 | 106.8351 | 27.2534 | 27.1053 | 26.7436 | 30.8311 | 50 | 50.0077 | 196.5066 | 42.2222 | 43.0151 | 108.2628 | ON | 28.42 | 108.3 | 53.1857 | 38.781 | -1.3147 | 3.7258 | 1.4649 | 1.4649 | 3.264 |  | OK | OK | OK | OK | 107.0599 | OK | OK | OK | OK | OK
44811.8096 | 1:02 | 95 | 135.3531 | 132.8243 | 147.0758 | 81.501 | 106.7437 | 106.7437 | 27.1627 | 27.2747 | 26.6947 | 30.807 | 50 | 50.0513 | 196.0872 | 42.3088 | 42.9215 | 108.1787 | ON | 28.42 | 108.3 | 53.081 | 38.7758 | -1.1453 | 3.5322 | 1.5563 | 1.5563 | 3.2553 |  | OK | OK | OK | OK | 106.9331 | OK | OK | OK | OK | OK
44811.8097 | 1:02 | 95 | 135.2604 | 132.8015 | 147.0795 | 81.3985 | 106.6769 | 106.6769 | 27.1559 | 27.0642 | 26.638 | 30.7675 | 50 | 49.9666 | 195.8327 | 42.1162 | 42.8109 | 108.0897 | ON | 27.51 | 108.3 | 53.8885 | 38.7795 | -0.44584 | 3.7034 | 1.6231 | 1.6231 | 3.2557 |  | OK | OK | OK | OK | 107.7504 | OK | OK | OK | OK | OK
44811.8099 | 1:02 | 95 | 135.2846 | 132.7571 | 146.998 | 81.2903 | 106.6117 | 106.6117 | 27.0963 | 26.7208 | 26.5798 | 30.7223 | 50 | 49.9389 | 195.6165 | 42.1585 | 42.6585 | 108.008 | ON | 27.51 | 108.3 | 53.7803 | 38.698 | -0.78924 | 4.0015 | 1.6883 | 1.6883 | 3.2537 |  | OK | OK | OK | OK | 107.7746 | OK | OK | OK | OK | OK
44811.81 | 1:02 | 95 | 135.2083 | 132.7287 | 146.9685 | 81.1899 | 106.5094 | 106.5094 | 27.0087 | 26.6685 | 26.5149 | 30.6417 | 50 | 49.9637 | 195.4683 | 42.1207 | 42.6109 | 107.9179 | ON | 27.51 | 108.3 | 53.6799 | 38.6685 | -0.84152 | 3.9732 | 1.7906 | 1.7906 | 3.2502 |  | OK | OK | OK | OK | 107.6983 | OK | OK | OK | OK | OK
44811.8101 | 1:02 | 95 | 135.1348 | 132.6322 | 146.9455 | 81.082 | 106.4532 | 106.4532 | 26.908 | 26.6568 | 26.4731 | 30.6033 | 50 | 49.7865 | 195.4941 | 42.0059 | 42.561 | 107.8545 | ON | 27.51 | 108.3 | 53.572 | 38.6455 | -0.85324 | 3.9465 | 1.8468 | 1.8468 | 3.2595 |  | OK | OK | OK | OK | 107.6248 | OK | OK | OK | OK | OK
44811.8102 | 1:03 | 95 | 135.0703 | 132.5606 | 146.9211 | 81.0052 | 106.3553 | 106.3553 | 26.8513 | 26.5068 | 26.355 | 30.524 | 50 | 49.6458 | 195.0334 | 41.9203 | 42.4803 | 107.7645 | ON | 27.51 | 108.3 | 53.4952 | 38.6211 | -1.0032 | 4.0171 | 1.9447 | 1.9447 | 3.2595 |  | OK | OK | OK | OK | 107.5603 | OK | OK | OK | OK | OK
44811.8103 | 1:03 | 95 | 134.9565 | 132.4438 | 146.8606 | 80.9109 | 106.2834 | 106.2834 | 26.7621 | 26.2409 | 26.2852 | 30.4837 | 50 | 49.5963 | 194.9772 | 41.7777 | 42.4275 | 107.6704 | ON | 27.51 | 106.4 | 53.4009 | 40.4606 | -1.2691 | 4.2428 | 0.1166 | 0.1166 | 3.2611 |  | OK | Low Charge | OK | OK | 107.4465 | OK | OK | OK | OK | OK
44811.8104 | 1:03 | 95 | 134.8659 | 132.4053 | 146.7742 | 80.8371 | 106.1603 | 106.1603 | 26.682 | 26.271 | 26.2229 | 30.4584 | 50 | 49.4798 | 194.718 | 41.6041 | 42.4331 | 107.5689 | ON | 27.51 | 106.4 | 53.3271 | 40.3742 | -1.2389 | 4.1874 | 0.2397 | 0.2397 | 3.263 |  | OK | Low Charge | OK | OK | 107.3559 | OK | OK | OK | OK | OK
44811.8105 | 1:03 | 95 | 134.7672 | 132.3409 | 146.6967 | 80.7603 | 106.088 | 106.088 | 26.5979 | 26.3398 | 26.152 | 30.3822 | 50 | 49.4629 | 194.3989 | 41.7801 | 42.3134 | 107.5075 | ON | 27.51 | 106.4 | 53.2503 | 40.2967 | -1.1702 | 4.0424 | 0.312 | 0.312 | 3.2589 |  | OK | Low Charge | OK | OK | 107.2572 | OK | OK | OK | OK | OK
44811.8107 | 1:03 | 95 | 134.8276 | 132.2644 | 146.6049 | 80.6388 | 105.9581 | 105.9581 | 26.5273 | 26.13 | 26.0773 | 30.3275 | 50 | 49.4637 | 194.0126 | 41.6946 | 42.283 | 107.3892 | ON | 27.51 | 106.4 | 53.1288 | 40.2049 | -1.38 | 4.1975 | 0.4419 | 0.4419 | 3.2528 |  | OK | Low Charge | OK | OK | 107.3176 | OK | OK | OK | OK | OK
44811.8108 | 1:03 | 95 | 134.6329 | 132.1607 | 146.5412 | 80.5492 | 105.8471 | 105.8471 | 26.3948 | 26.1979 | 25.9914 | 30.245 | 50 | 49.3139 | 193.9132 | 41.688 | 42.2396 | 107.2495 | ON | 27.51 | 106.4 | 53.0392 | 40.1412 | -1.3121 | 4.0472 | 0.5529 | 0.5529 | 3.2589 |  | OK | Low Charge | OK | OK | 107.1229 | OK | OK | OK | OK | OK
44811.8109 | 1:04 | 95 | 134.6087 | 132.0813 | 146.3963 | 80.4263 | 105.7981 | 105.7981 | 26.3558 | 26.0044 | 25.9341 | 30.196 | 50 | 49.2552 | 193.6461 | 41.3369 | 42.1098 | 107.1789 | ON | 27.51 | 106.4 | 52.9163 | 39.9963 | -1.5056 | 4.1916 | 0.6019 | 0.6019 | 3.2577 |  | OK | Low Charge | OK | OK | 107.0987 | OK | OK | OK | OK | OK
44811.811 | 1:04 | 95 | 134.4585 | 132.0213 | 146.3146 | 80.3556 | 105.6791 | 105.6791 | 26.259 | 25.8269 | 25.8318 | 30.1213 | 50 | 49.128 | 193.2764 | 41.3838 | 42.0091 | 107.0788 | ON | 27.51 | 106.4 | 52.8456 | 39.9146 | -1.6831 | 4.2944 | 0.7209 | 0.7209 | 3.2584 |  | OK | Low Charge | OK | OK | 106.9485 | OK | OK | OK | OK | OK
44811.8111 | 1:04 | 95 | 134.2903 | 131.827 | 146.2472 | 80.3224 | 105.5912 | 105.5912 | 26.1865 | 25.9324 | 25.7931 | 30.0586 | 50 | 49.2104 | 193.0157 | 41.3991 | 41.9511 | 106.9978 | ON | 27.51 | 106.4 | 52.8124 | 39.8472 | -1.5776 | 4.1261 | 0.8088 | 0.8088 | 3.2501 |  | OK | Low Charge | OK | OK | 106.7803 | OK | OK | OK | OK | OK
44811.8112 | 1:04 | 95 | 134.216 | 131.7352 | 146.1398 | 80.2109 | 105.4997 | 105.4997 | 26.2429 | 25.658 | 25.7351 | 29.9853 | 50 | 49.0836 | 193.0172 | 41.2927 | 41.8631 | 106.929 | ON | 27.51 | 106.4 | 52.7009 | 39.7398 | -1.852 | 4.3273 | 0.9003 | 0.9003 | 3.2566 |  | OK | Low Charge | OK | OK | 106.706 | OK | OK | OK | OK | OK
44811.8114 | 1:04 | 95 | 134.1535 | 131.6682 | 146.0451 | 80.0545 | 105.3962 | 105.3962 | 26.1027 | 25.6483 | 25.6775 | 29.9107 | 50 | 48.92 | 192.5582 | 41.2253 | 41.8838 | 106.8089 | ON | 26.6 | 106.4 | 53.4545 | 39.6451 | -0.95172 | 4.2624 | 1.0038 | 1.0038 | 3.2578 |  | OK | OK | OK | OK | 107.5535 | OK | OK | OK | OK | OK
44811.8115 | 1:04 | 95 | 134.2115 | 131.6392 | 146.0567 | 79.8838 | 105.5925 | 105.5925 | 26.303 | 26.1991 | 25.6266 | 29.8745 | 50 | 48.8232 | 193.2788 | 41.0683 | 41.6926 | 106.9051 | ON | 26.6 | 106.4 | 53.2838 | 39.6567 | -0.40094 | 3.6755 | 0.8075 | 0.8075 | 3.2741 |  | OK | Low Charge | OK | OK | 107.6115 | OK | OK | OK | OK | OK
44811.8116 | 1:05 | 95 | 134.1105 | 131.6209 | 146.0028 | 79.7803 | 105.6005 | 105.6005 | 26.1109 | 27.919 | 25.571 | 29.8038 | 50 | 48.9265 | 193.0855 | 41.0761 | 41.6118 | 106.9264 | ON | 26.6 | 106.4 | 53.1803 | 39.6028 | 1.319 | 1.8848 | 0.7995 | 0.7995 | 3.2657 |  | OK | Low Charge | OK | OK | 107.5105 | OK | OK | OK | OK | OK
44811.8117 | 1:05 | 95 | 134.1514 | 131.6154 | 146.0013 | 79.686 | 105.6064 | 105.6064 | 26.1061 | 28.7673 | 25.5551 | 29.7425 | 50 | 48.9215 | 193.3032 | 41.0017 | 41.5764 | 106.9257 | ON | 26.6 | 106.4 | 53.086 | 39.6013 | 2.1673 | 0.97522 | 0.7936 | 0.7936 | 3.2694 |  | OK | Low Charge | OK | OK | 107.5514 | OK | OK | OK | OK | OK
44811.8118 | 1:05 | 95 | 134.1333 | 131.6025 | 146.0229 | 79.5549 | 105.7376 | 105.7376 | 26.3233 | 28.9603 | 25.6391 | 29.6747 | 50 | 49.1556 | 193.9409 | 41.1916 | 41.6125 | 107.0588 | ON | 27.51 | 106.4 | 52.0449 | 39.6229 | 1.4503 | 0.71441 | 0.6624 | 0.6624 | 3.2674 |  | OK | Low Charge | OK | OK | 106.6233 | OK | OK | OK | OK | OK
44811.8119 | 1:05 | 95 | 134.2562 | 131.6691 | 146.048 | 79.4757 | 106.0159 | 106.0159 | 26.4858 | 29.5161 | 25.6231 | 29.6061 | 50 | 49.1202 | 194.3952 | 41.1792 | 41.4712 | 107.2434 | ON | 27.51 | 106.4 | 51.9657 | 39.648 | 2.0061 | 0.08998 | 0.3841 | 0.3841 | 3.2763 |  | OK | Low Charge | OK | OK | 106.7462 | OK | OK | OK | OK | OK
44811.8121 | 1:05 | 95 | 134.2043 | 131.6714 | 146.1018 | 79.3112 | 106.055 | 106.055 | 26.4988 | 30.2574 | 25.5819 | 29.5566 | 50 | 49.0432 | 194.7367 | 41.3845 | 41.3476 | 107.3032 | ON | 27.51 | 106.4 | 51.8012 | 39.7018 | 2.7474 | -0.70081 | 0.345 | 0.345 | 3.2856 |  | OK | Low Charge | OK | OK | 106.6943 | OK | OK | OK | OK | OK
44811.8122 | 1:05 | 95 | 134.1671 | 131.6703 | 146.0323 | 78.974 | 106.0079 | 106.0079 | 26.5501 | 30.4543 | 25.527 | 29.4923 | 50 | 48.9286 | 194.1831 | 41.3197 | 41.3984 | 107.2828 | ON | 26.6 | 106.4 | 52.374 | 39.6323 | 3.8543 | -0.96202 | 0.3921 | 0.3921 | 3.2828 |  | OK | Low Charge | OK | OK | 107.5671 | OK | OK | OK | OK | OK
44811.8123 | 1:06 | 95 | 134.2209 | 131.7122 | 146.0229 | 78.7671 | 105.9629 | 105.9629 | 26.5341 | 30.4211 | 25.5342 | 29.5 | 50 | 49.0949 | 194.1167 | 41.2621 | 41.3146 | 107.2564 | ON | 27.51 | 106.4 | 51.2571 | 39.6229 | 2.9111 | -0.9211 | 0.4371 | 0.4371 | 3.2733 |  | OK | Low Charge | OK | OK | 106.7109 | OK | OK | OK | OK | OK
44811.8124 | 1:06 | 95 | 134.189 | 131.6329 | 145.9484 | 78.5966 | 105.9302 | 105.9302 | 26.549 | 30.2651 | 25.4741 | 29.456 | 50 | 49.0682 | 194.1141 | 41.137 | 41.2871 | 107.2381 | ON | 27.51 | 106.4 | 51.0866 | 39.5484 | 2.7551 | -0.80918 | 0.4698 | 0.4698 | 3.2746 |  | OK | Low Charge | OK | OK | 106.679 | OK | OK | OK | OK | OK
44811.8125 | 1:06 | 95 | 134.0959 | 131.6077 | 145.8746 | 78.5951 | 105.8865 | 105.8865 | 26.5675 | 30.1727 | 25.5239 | 29.4636 | 50 | 49.0278 | 194.2102 | 41.0737 | 41.2471 | 107.2286 | ON | 27.51 | 106.4 | 51.0851 | 39.4746 | 2.6627 | -0.70914 | 0.5135 | 0.5135 | 3.2782 |  | OK | Low Charge | OK | OK | 106.5859 | OK | OK | OK | OK | OK
44811.8126 | 1:06 | 95 | 134.049 | 131.6016 | 145.8135 | 78.6128 | 105.8669 | 105.8669 | 26.6338 | 30.0202 | 25.6819 | 29.4503 | 50 | 49.2521 | 194.0469 | 41.0054 | 41.2376 | 107.2116 | ON | 27.51 | 106.4 | 51.1028 | 39.4135 | 2.5101 | -0.56985 | 0.5331 | 0.5331 | 3.2641 |  | OK | Low Charge | OK | OK | 106.539 | OK | OK | OK | OK | OK
44811.8127 | 1:06 | 95 | 134.0205 | 131.4746 | 145.7255 | 78.6467 | 105.8063 | 105.8063 | 26.6151 | 29.8274 | 25.6113 | 29.4738 | 50 | 49.0544 | 193.6587 | 40.9382 | 41.1236 | 107.1616 | ON | 27.51 | 106.4 | 51.1367 | 39.3255 | 2.3174 | -0.3536 | 0.5937 | 0.5937 | 3.2681 |  | OK | Low Charge | OK | OK | 106.5105 | OK | OK | OK | OK | OK
44811.8129 | 1:06 | 95 | 134.0058 | 131.4375 | 145.7332 | 78.6327 | 105.7889 | 105.7889 | 26.6089 | 29.6127 | 25.6143 | 29.5099 | 50 | 49.0602 | 193.9565 | 40.991 | 41.0769 | 107.1348 | ON | 27.51 | 106.4 | 51.1227 | 39.3332 | 2.1027 | -0.10281 | 0.6111 | 0.6111 | 3.2725 |  | OK | Low Charge | OK | OK | 106.4958 | OK | OK | OK | OK | OK
44811.813 | 1:07 | 95 | 133.9485 | 131.3736 | 145.6406 | 78.5354 | 105.8021 | 105.8021 | 26.6342 | 29.3464 | 25.6729 | 29.5542 | 50 | 49.1769 | 193.767 | 40.8881 | 40.9391 | 107.1406 | ON | 27.51 | 106.4 | 51.0254 | 39.2406 | 1.8364 | 0.20777 | 0.5979 | 0.5979 | 3.2636 |  | OK | Low Charge | OK | OK | 106.4385 | OK | OK | OK | OK | OK
44811.8131 | 1:07 | 95 | 133.8917 | 131.3305 | 145.5654 | 78.4686 | 105.7585 | 105.7585 | 26.5885 | 29.0521 | 25.7567 | 29.51 | 50 | 49.0423 | 193.7003 | 40.6719 | 40.9951 | 107.1329 | ON | 27.51 | 106.4 | 50.9586 | 39.1654 | 1.5421 | 0.45789 | 0.6415 | 0.6415 | 3.2694 |  | OK | Low Charge | OK | OK | 106.3817 | OK | OK | OK | OK | OK
44811.8132 | 1:07 | 95 | 133.8005 | 131.322 | 145.5452 | 78.4578 | 105.7374 | 105.7374 | 26.5804 | 28.745 | 26.0247 | 29.5548 | 50 | 49.0117 | 193.66 | 40.6822 | 40.9064 | 107.1204 | ON | 27.51 | 106.4 | 50.9478 | 39.1452 | 1.235 | 0.8098 | 0.6626 | 0.6626 | 3.2704 |  | OK | Low Charge | OK | OK | 106.2905 | OK | OK | OK | OK | OK
44811.8133 | 1:07 | 95 | 133.8681 | 131.3298 | 145.5064 | 78.4409 | 105.7719 | 105.7719 | 26.455 | 28.3582 | 25.5046 | 29.4705 | 50 | 48.7016 | 193.6931 | 40.5773 | 40.8829 | 107.1388 | ON | 26.6 | 106.4 | 51.8409 | 39.1064 | 1.7582 | 1.1123 | 0.6281 | 0.6281 | 3.2869 |  | OK | Low Charge | OK | OK | 107.2681 | OK | OK | OK | OK | OK
44811.8134 | 1:07 | 95 | 133.7468 | 131.307 | 145.4584 | 78.491 | 105.7183 | 105.7183 | 26.4184 | 27.3156 | 25.3871 | 29.4692 | 50 | 48.7135 | 193.3822 | 40.4667 | 40.8342 | 107.0953 | ON | 26.6 | 106.4 | 51.891 | 39.0584 | 0.71563 | 2.1535 | 0.6817 | 0.6817 | 3.2814 |  | OK | Low Charge | OK | OK | 107.1468 | OK | OK | OK | OK | OK
44811.8136 | 1:07 | 95 | 133.6794 | 131.258 | 145.4631 | 78.5335 | 105.6849 | 105.6849 | 26.3138 | 26.2636 | 25.367 | 29.5371 | 50 | 49.0448 | 193.5215 | 40.4101 | 40.6443 | 107.0894 | ON | 27.51 | 106.4 | 51.0234 | 39.0631 | -1.2464 | 3.2735 | 0.7151 | 0.7151 | 3.2665 |  | OK | Low Charge | OK | OK | 106.1694 | OK | OK | OK | OK | OK
44811.8137 | 1:08 | 95 | 133.6435 | 131.2618 | 145.4162 | 78.4783 | 105.6863 | 105.6863 | 26.2179 | 25.4931 | 25.2158 | 29.585 | 50 | 48.5809 | 193.5707 | 40.4977 | 40.7024 | 107.082 | ON | 26.6 | 106.4 | 51.8783 | 39.0162 | -1.107 | 4.0919 | 0.7137 | 0.7137 | 3.2912 |  | OK | Low Charge | OK | OK | 107.0435 | OK | OK | OK | OK | OK
44811.8138 | 1:08 | 95 | 133.6115 | 131.2317 | 145.3912 | 78.5237 | 105.6813 | 105.6813 | 26.0749 | 25.16 | 25.1439 | 29.5766 | 50 | 48.5 | 193.329 | 40.2106 | 40.7268 | 107.0624 | ON | 26.6 | 106.4 | 51.9237 | 38.9912 | -1.44 | 4.4166 | 0.7187 | 0.7187 | 3.2916 |  | OK | Low Charge | OK | OK | 107.0115 | OK | OK | OK | OK | OK
44811.8139 | 1:08 | 95 | 133.7818 | 131.2069 | 145.3907 | 78.5937 | 105.6317 | 105.6317 | 25.9045 | 25.0207 | 25.0478 | 29.5137 | 50 | 48.3812 | 193.1832 | 40.3015 | 40.5425 | 107.0225 | ON | 26.6 | 106.4 | 51.9937 | 38.9907 | -1.5793 | 4.493 | 0.7683 | 0.7683 | 3.2955 |  | OK | Low Charge | OK | OK | 107.1818 | OK | OK | OK | OK | OK
44811.814 | 1:08 | 95 | 133.741 | 131.1478 | 145.3705 | 78.6315 | 105.6405 | 105.6405 | 25.8148 | 24.9633 | 24.976 | 29.4554 | 50 | 48.3417 | 193.4219 | 40.1163 | 40.538 | 107.0237 | ON | 26.6 | 106.4 | 52.0315 | 38.9705 | -1.6367 | 4.4921 | 0.7595 | 0.7595 | 3.3013 |  | OK | Low Charge | OK | OK | 107.141 | OK | OK | OK | OK | OK
44811.8141 | 1:08 | 95 | 133.8119 | 131.17 | 145.3878 | 78.6644 | 105.7852 | 105.7852 | 25.6979 | 24.7904 | 24.9309 | 29.3394 | 50 | 48.2365 | 193.8867 | 40.1461 | 40.3911 | 107.1606 | ON | 26.6 | 106.4 | 52.0644 | 38.9878 | -1.8096 | 4.549 | 0.6148 | 0.6148 | 3.3142 |  | OK | Low Charge | OK | OK | 107.2119 | OK | OK | OK | OK | OK
44811.8143 | 1:08 | 95 | 133.847 | 131.3644 | 145.5431 | 78.8019 | 106.0368 | 106.0368 | 25.5979 | 24.7252 | 24.8992 | 29.2781 | 50 | 48.3058 | 194.6156 | 39.9871 | 40.4134 | 107.4085 | ON | 26.6 | 106.4 | 52.2019 | 39.1431 | -1.8748 | 4.5529 | 0.3632 | 0.3632 | 3.3222 |  | OK | Low Charge | OK | OK | 107.247 | OK | OK | OK | OK | OK
44811.8144 | 1:09 | 95 | 134.004 | 131.4745 | 145.634 | 78.9129 | 106.279 | 106.279 | 25.4808 | 24.6848 | 24.8488 | 29.1501 | 50 | 48.1728 | 195.0771 | 39.8305 | 40.3045 | 107.6159 | ON | 26.6 | 108.3 | 52.3129 | 37.334 | -1.9152 | 4.4653 | 2.021 | 2.021 | 3.3365 |  | OK | OK | OK | OK | 107.404 | OK | OK | OK | OK | OK
44811.8145 | 1:09 | 95 | 134.142 | 131.6862 | 145.8612 | 79.0842 | 106.5199 | 106.5199 | 25.3978 | 24.9518 | 24.8976 | 29.0641 | 50 | 48.3 | 195.7186 | 39.8475 | 40.2725 | 107.8175 | ON | 26.6 | 108.3 | 52.4842 | 37.5612 | -1.6482 | 4.1123 | 1.7801 | 1.7801 | 3.34 |  | OK | OK | OK | OK | 107.542 | OK | OK | OK | OK | OK
44811.8146 | 1:09 | 95 | 134.2757 | 131.8484 | 145.9914 | 79.2333 | 106.6726 | 106.6726 | 25.315 | 24.7498 | 24.7717 | 29.0801 | 50 | 48.0528 | 196.059 | 39.8435 | 40.1476 | 107.9617 | ON | 26.6 | 108.3 | 52.6333 | 37.6914 | -1.8502 | 4.3303 | 1.6274 | 1.6274 | 3.3586 |  | OK | OK | OK | OK | 107.6757 | OK | OK | OK | OK | OK
44811.8147 | 1:09 | 95 | 134.4741 | 131.9918 | 146.1377 | 79.4089 | 106.8746 | 106.8746 | 25.2858 | 25.0074 | 24.7864 | 29.2587 | 50 | 48.02 | 196.6924 | 39.7908 | 40.1297 | 108.1703 | ON | 26.6 | 108.3 | 52.8088 | 37.8377 | -1.5926 | 4.2514 | 1.4254 | 1.4254 | 3.3704 |  | OK | OK | OK | OK | 107.8741 | OK | OK | OK | OK | OK
44811.8148 | 1:09 | 95 | 134.717 | 132.1526 | 146.3239 | 79.5702 | 106.9924 | 106.9924 | 25.131 | 24.5052 | 24.9691 | 29.6012 | 50 | 47.934 | 197.0938 | 39.7488 | 40.1453 | 108.2491 | ON | 25.68 | 108.3 | 53.8902 | 38.0239 | -1.1748 | 5.0961 | 1.3076 | 1.3076 | 3.3814 |  | OK | OK | OK | OK | 109.037 | OK | OK | OK | OK | OK
44811.8149 | 1:09 | 95 | 134.9732 | 132.3021 | 146.5034 | 79.692 | 107.049 | 107.049 | 25.1882 | 25.0543 | 25.0189 | 29.8973 | 50 | 48.0344 | 197.0959 | 39.7071 | 40.2166 | 108.3334 | ON | 26.6 | 108.3 | 53.092 | 38.2034 | -1.5457 | 4.843 | 1.251 | 1.251 | 3.3761 |  | OK | OK | OK | OK | 108.3732 | OK | OK | OK | OK | OK
44811.8151 | 1:10 | 95 | 135.1331 | 132.4775 | 146.6321 | 79.8242 | 107.1027 | 107.1027 | 25.0514 | 24.44 | 24.9579 | 30.1059 | 50 | 47.8856 | 197.2451 | 39.6213 | 40.1681 | 108.3578 | ON | 25.68 | 108.3 | 54.1442 | 38.3321 | -1.24 | 5.6659 | 1.1973 | 1.1973 | 3.3865 |  | OK | OK | OK | OK | 109.4531 | OK | OK | OK | OK | OK
44811.8152 | 1:10 | 95 | 135.2283 | 132.5611 | 146.8239 | 80.0495 | 107.1126 | 107.1126 | 25.0562 | 24.4702 | 24.8278 | 30.1389 | 50 | 47.8518 | 197.4922 | 39.5858 | 40.1465 | 108.4002 | ON | 25.68 | 108.3 | 54.3695 | 38.5239 | -1.2098 | 5.6687 | 1.1874 | 1.1874 | 3.3923 |  | OK | OK | OK | OK | 109.5483 | OK | OK | OK | OK | OK
44811.8153 | 1:10 | 95 | 135.3141 | 132.7273 | 146.9886 | 80.1998 | 107.0942 | 107.0942 | 25.001 | 24.4199 | 24.8201 | 30.0556 | 50 | 47.818 | 197.2981 | 39.5248 | 40.0003 | 108.3699 | ON | 25.68 | 108.3 | 54.5198 | 38.6886 | -1.2601 | 5.6356 | 1.2058 | 1.2058 | 3.391 |  | OK | OK | OK | OK | 109.6341 | OK | OK | OK | OK | OK
44811.8154 | 1:10 | 95 | 135.4481 | 132.7842 | 147.0836 | 80.3452 | 107.1743 | 107.1743 | 24.9437 | 24.45 | 24.7507 | 29.9274 | 50 | 47.8154 | 197.325 | 39.3224 | 39.9305 | 108.4371 | ON | 25.68 | 108.3 | 54.6653 | 38.7836 | -1.23 | 5.4774 | 1.1257 | 1.1257 | 3.3916 |  | OK | OK | OK | OK | 109.7681 | OK | OK | OK | OK | OK
44811.8155 | 1:10 | 95 | 135.614 | 132.8807 | 147.2287 | 80.4912 | 107.2084 | 107.2084 | 24.9027 | 24.4702 | 24.7678 | 29.763 | 50 | 47.8419 | 197.4774 | 39.4427 | 39.8961 | 108.4803 | ON | 25.68 | 108.3 | 54.8112 | 38.9287 | -1.2098 | 5.2929 | 1.0916 | 1.0916 | 3.3926 |  | OK | OK | OK | OK | 109.934 | OK | OK | OK | OK | OK
44811.8156 | 1:10 | 95 | 135.6701 | 132.9987 | 147.3532 | 80.5979 | 107.217 | 107.217 | 24.8518 | 24.5142 | 24.6749 | 29.5825 | 50 | 47.6494 | 197.4557 | 39.2122 | 39.8362 | 108.4884 | ON | 25.68 | 108.3 | 54.9179 | 39.0532 | -1.1658 | 5.0683 | 1.083 | 1.083 | 3.4027 |  | OK | OK | OK | OK | 109.9901 | OK | OK | OK | OK | OK
44811.8158 | 1:11 | 95 | 135.8755 | 133.1545 | 147.4849 | 80.6982 | 107.1939 | 107.1939 | 24.8264 | 24.8927 | 24.7218 | 29.4123 | 50 | 47.6782 | 197.4479 | 39.2838 | 39.7773 | 108.4628 | ON | 25.68 | 108.3 | 55.0182 | 39.1849 | -0.78728 | 4.5196 | 1.1061 | 1.1061 | 3.401 |  | OK | OK | OK | OK | 110.1955 | OK | OK | OK | OK | OK
44811.8159 | 1:11 | 95 | 135.9681 | 133.1717 | 147.582 | 80.7262 | 107.137 | 107.137 | 24.7192 | 24.936 | 24.5793 | 29.2383 | 50 | 47.6033 | 197.0508 | 39.054 | 39.6602 | 108.3944 | ON | 25.68 | 108.3 | 55.0462 | 39.282 | -0.74404 | 4.3023 | 1.163 | 1.163 | 3.3987 |  | OK | OK | OK | OK | 110.2881 | OK | OK | OK | OK | OK
44811.816 | 1:11 | 95 | 135.9883 | 133.2374 | 147.6351 | 80.7998 | 107.0682 | 107.0682 | 24.7319 | 25.1631 | 24.5606 | 29.1093 | 50 | 47.6199 | 197.184 | 39.1943 | 39.695 | 108.3663 | ON | 25.68 | 108.3 | 55.1198 | 39.3351 | -0.51687 | 3.9461 | 1.2318 | 1.2318 | 3.3999 |  | OK | OK | OK | OK | 110.3083 | OK | OK | OK | OK | OK
44811.8161 | 1:11 | 95 | 136.0315 | 133.2984 | 147.7482 | 80.8458 | 107.0443 | 107.0443 | 24.7136 | 25.0366 | 24.5186 | 28.9244 | 50 | 47.6639 | 197.0003 | 39.0227 | 39.5186 | 108.3379 | ON | 25.68 | 108.3 | 55.1658 | 39.4482 | -0.64337 | 3.8877 | 1.2557 | 1.2557 | 3.3946 |  | OK | OK | OK | OK | 110.3515 | OK | OK | OK | OK | OK
44811.8162 | 1:11 | 95 | 136.0136 | 133.3513 | 147.8174 | 80.884 | 106.9727 | 106.9727 | 24.6547 | 24.7741 | 24.4213 | 28.7941 | 50 | 47.5841 | 196.835 | 39.0435 | 39.4847 | 108.2584 | ON | 25.68 | 108.3 | 55.204 | 39.5174 | -0.90594 | 4.0201 | 1.3273 | 1.3273 | 3.3963 |  | OK | OK | OK | OK | 110.3336 | OK | OK | OK | OK | OK
44811.8163 | 1:11 | 95 | 136.1502 | 133.3577 | 147.877 | 80.9397 | 106.9266 | 106.9266 | 24.5803 | 24.8883 | 24.3721 | 28.6527 | 50 | 47.4241 | 196.7699 | 38.9109 | 39.4298 | 108.2118 | ON | 25.68 | 108.3 | 55.2597 | 39.577 | -0.79166 | 3.7644 | 1.3734 | 1.3734 | 3.404 |  | OK | OK | OK | OK | 110.4702 | OK | OK | OK | OK | OK
44811.8165 | 1:12 | 95 | 136.2216 | 133.3976 | 147.9519 | 80.9543 | 106.8843 | 106.8843 | 24.5405 | 25.0111 | 24.2791 | 28.5419 | 50 | 47.3937 | 196.3418 | 38.8836 | 39.4517 | 108.1465 | ON | 25.68 | 108.3 | 55.2743 | 39.6519 | -0.66892 | 3.5308 | 1.4157 | 1.4157 | 3.3988 |  | OK | OK | OK | OK | 110.5416 | OK | OK | OK | OK | OK
44811.8166 | 1:12 | 95 | 136.2512 | 133.4058 | 147.9964 | 80.9556 | 106.7759 | 106.7759 | 24.4888 | 25.0661 | 24.2309 | 28.4376 | 50 | 47.3618 | 196.0861 | 38.7605 | 39.297 | 108.0457 | ON | 25.68 | 108.3 | 55.2756 | 39.6964 | -0.61386 | 3.3715 | 1.5241 | 1.5241 | 3.3964 |  | OK | OK | OK | OK | 110.5712 | OK | OK | OK | OK | OK
44811.8167 | 1:12 | 95 | 136.2226 | 133.4269 | 147.9822 | 80.9588 | 106.7063 | 106.7063 | 24.4682 | 24.805 | 24.2054 | 28.3163 | 50 | 47.178 | 195.975 | 38.8962 | 39.1794 | 107.9941 | ON | 25.68 | 108.3 | 55.2788 | 39.6822 | -0.87505 | 3.5114 | 1.5937 | 1.5937 | 3.4047 |  | OK | OK | OK | OK | 110.5426 | OK | OK | OK | OK | OK
44811.8168 | 1:12 | 95 | 136.2965 | 133.463 | 148.0361 | 80.8652 | 106.6276 | 106.6276 | 24.4123 | 24.4189 | 24.1175 | 28.2195 | 50 | 47.3014 | 195.7884 | 38.672 | 39.1353 | 107.9225 | ON | 25.68 | 108.3 | 55.1852 | 39.7361 | -1.2611 | 3.8006 | 1.6724 | 1.6724 | 3.3949 |  | OK | OK | OK | OK | 110.6165 | OK | OK | OK | OK | OK
44811.8169 | 1:12 | 95 | 136.3006 | 133.3845 | 148.0323 | 80.842 | 106.5568 | 106.5568 | 24.3511 | 24.3738 | 24.0411 | 28.0828 | 50 | 47.1387 | 195.6823 | 38.6126 | 39.0557 | 107.827 | ON | 25.68 | 108.3 | 55.162 | 39.7323 | -1.3062 | 3.709 | 1.7432 | 1.7432 | 3.4021 |  | OK | OK | OK | OK | 110.6206 | OK | OK | OK | OK | OK
44811.817 | 1:12 | 95 | 136.1668 | 133.4026 | 148.0493 | 80.7863 | 106.441 | 106.441 | 24.3498 | 24.2299 | 24.0378 | 28.0117 | 50 | 47.3973 | 195.5972 | 38.659 | 39.0395 | 107.7414 | ON | 25.68 | 108.3 | 55.1063 | 39.7493 | -1.4501 | 3.7818 | 1.859 | 1.859 | 3.3866 |  | OK | OK | OK | OK | 110.4868 | OK | OK | OK | OK | OK
44811.8171 | 1:13 | 95 | 136.1048 | 133.3314 | 148.0207 | 80.7298 | 106.3346 | 106.3346 | 24.2105 | 23.8383 | 23.8723 | 27.9039 | 50 | 47.1354 | 195.3561 | 38.4411 | 39.1438 | 107.6321 | ON | 25.68 | 108.3 | 55.0498 | 39.7207 | -1.8417 | 4.0656 | 1.9654 | 1.9654 | 3.397 |  | OK | OK | OK | OK | 110.4248 | OK | OK | OK | OK | OK
44811.8173 | 1:13 | 95 | 136.1678 | 133.27 | 148.0014 | 80.6531 | 106.2776 | 106.2776 | 24.1946 | 23.9471 | 23.8148 | 27.7956 | 50 | 47.0128 | 194.9391 | 38.4468 | 38.9259 | 107.5738 | ON | 25.68 | 106.4 | 54.9731 | 41.6014 | -1.7329 | 3.8485 | 0.1224 | 0.1224 | 3.397 |  | OK | Low Charge | OK | OK | 110.4878 | OK | OK | OK | OK | OK
44811.8174 | 1:13 | 95 | 136.0996 | 133.1518 | 147.9685 | 80.6222 | 106.1878 | 106.1878 | 24.1137 | 23.6874 | 23.8067 | 27.7327 | 50 | 46.9344 | 194.8162 | 38.4508 | 38.8118 | 107.4759 | ON | 24.74 | 106.4 | 55.8822 | 41.5685 | -1.0526 | 4.0453 | 0.2122 | 0.2122 | 3.3993 |  | OK | Low Charge | OK | OK | 111.3596 | OK | OK | OK | OK | OK
44811.8175 | 1:13 | 95 | 135.9529 | 133.1984 | 147.9897 | 80.4538 | 106.1768 | 106.1768 | 24.065 | 23.7134 | 23.7329 | 27.6151 | 50 | 46.89 | 194.7107 | 38.3712 | 38.8173 | 107.4518 | ON | 24.74 | 106.4 | 55.7138 | 41.5897 | -1.0266 | 3.9017 | 0.2232 | 0.2232 | 3.4001 |  | OK | Low Charge | OK | OK | 111.2129 | OK | OK | OK | OK | OK
44811.8176 | 1:13 | 95 | 135.9578 | 133.106 | 147.9769 | 80.3825 | 106.1227 | 106.1227 | 24.0038 | 23.5401 | 23.6307 | 27.5035 | 50 | 46.7612 | 194.5399 | 38.3935 | 38.6934 | 107.3998 | ON | 24.74 | 106.4 | 55.6425 | 41.5769 | -1.2 | 3.9635 | 0.2773 | 0.2773 | 3.4044 |  | OK | Low Charge | OK | OK | 111.2178 | OK | OK | OK | OK | OK
44811.8177 | 1:13 | 95 | 135.9309 | 133.1492 | 147.9201 | 80.2907 | 106.0027 | 106.0027 | 23.9218 | 23.4299 | 23.5241 | 27.4205 | 50 | 46.746 | 194.3082 | 38.2189 | 38.6287 | 107.2766 | ON | 24.74 | 106.4 | 55.5507 | 41.5201 | -1.3101 | 3.9906 | 0.3973 | 0.3973 | 3.4015 |  | OK | Low Charge | OK | OK | 111.1909 | OK | OK | OK | OK | OK
44811.8178 | 1:14 | 95 | 135.8124 | 133.0616 | 147.862 | 80.1881 | 105.9006 | 105.9006 | 23.8471 | 23.4457 | 23.4783 | 27.3663 | 50 | 46.671 | 193.8652 | 38.1618 | 38.5478 | 107.149 | ON | 24.74 | 106.4 | 55.4481 | 41.462 | -1.2943 | 3.9205 | 0.4994 | 0.4994 | 3.3984 |  | OK | Low Charge | OK | OK | 111.0724 | OK | OK | OK | OK | OK
44811.818 | 1:14 | 95 | 135.8171 | 132.9467 | 147.7418 | 80.097 | 105.8176 | 105.8176 | 23.776 | 23.5039 | 23.3525 | 27.2836 | 50 | 46.5266 | 193.8818 | 38.0559 | 38.4918 | 107.0957 | ON | 24.74 | 106.4 | 55.357 | 41.3418 | -1.2361 | 3.7797 | 0.5824 | 0.5824 | 3.4067 |  | OK | Low Charge | OK | OK | 111.0771 | OK | OK | OK | OK | OK
44811.8181 | 1:14 | 95 | 135.7821 | 132.8612 | 147.705 | 79.9194 | 105.7167 | 105.7167 | 23.6976 | 23.2992 | 23.2823 | 27.2208 | 50 | 46.4905 | 193.6184 | 37.9617 | 38.4043 | 107.0126 | ON | 24.74 | 106.4 | 55.1794 | 41.305 | -1.4408 | 3.9216 | 0.6833 | 0.6833 | 3.4044 |  | OK | Low Charge | OK | OK | 111.0421 | OK | OK | OK | OK | OK
44811.8182 | 1:14 | 95 | 135.7505 | 132.7824 | 147.6448 | 79.7806 | 105.6167 | 105.6167 | 23.6417 | 23.19 | 23.1667 | 27.137 | 50 | 46.352 | 192.8087 | 37.982 | 38.4321 | 106.9011 | ON | 24.74 | 106.4 | 55.0406 | 41.2448 | -1.55 | 3.947 | 0.7833 | 0.7833 | 3.3989 |  | OK | Low Charge | OK | OK | 111.0105 | OK | OK | OK | OK | OK
44811.8183 | 1:14 | 95 | 135.6686 | 132.6918 | 147.5966 | 79.7209 | 105.5305 | 105.5305 | 23.52 | 23.0507 | 23.0823 | 27.0438 | 50 | 46.2633 | 193.017 | 37.8707 | 38.3299 | 106.797 | ON | 24.74 | 106.4 | 54.9809 | 41.1966 | -1.6893 | 3.9932 | 0.8695 | 0.8695 | 3.4072 |  | OK | Low Charge | OK | OK | 110.9286 | OK | OK | OK | OK | OK
44811.8184 | 1:14 | 95 | 135.4969 | 132.6394 | 147.5103 | 79.7012 | 105.3944 | 105.3944 | 23.439 | 23.0053 | 22.9632 | 26.985 | 50 | 46.1743 | 192.5541 | 37.7352 | 38.2404 | 106.6879 | ON | 24.74 | 106.4 | 54.9612 | 41.1103 | -1.7347 | 3.9797 | 1.0056 | 1.0056 | 3.4046 |  | OK | OK | OK | OK | 110.7569 | OK | OK | OK | OK | OK
44811.8185 | 1:15 | 95 | 135.4077 | 132.5767 | 147.4443 | 79.6918 | 105.341 | 105.341 | 23.3534 | 22.8276 | 22.8998 | 26.9406 | 50 | 46.1807 | 192.7926 | 37.4512 | 38.1318 | 106.6287 | ON | 24.74 | 106.4 | 54.9518 | 41.0443 | -1.9124 | 4.1129 | 1.059 | 1.059 | 3.4082 |  | OK | OK | OK | OK | 110.6677 | OK | OK | OK | OK | OK
44811.8187 | 1:15 | 95 | 135.3844 | 132.3927 | 147.3587 | 79.6245 | 105.1766 | 105.1766 | 23.2757 | 22.7131 | 22.8338 | 26.8809 | 50 | 46.1023 | 192.1014 | 37.7023 | 38.0421 | 106.4803 | ON | 24.74 | 106.4 | 54.8845 | 40.9587 | -2.0269 | 4.1678 | 1.2234 | 1.2234 | 3.4012 |  | OK | OK | OK | OK | 110.6444 | OK | OK | OK | OK | OK
44811.8188 | 1:15 | 95 | 135.2873 | 132.3328 | 147.3037 | 79.5501 | 105.027 | 105.027 | 23.1923 | 22.7122 | 22.7628 | 26.8068 | 50 | 46.0583 | 191.4104 | 37.616 | 37.9708 | 106.3292 | ON | 24.74 | 106.4 | 54.8101 | 40.9037 | -2.0278 | 4.0946 | 1.373 | 1.373 | 3.3923 |  | OK | OK | OK | OK | 110.5473 | OK | OK | OK | OK | OK
44811.8189 | 1:15 | 95 | 135.1895 | 132.2618 | 147.1582 | 79.4442 | 104.932 | 104.932 | 23.0914 | 22.5271 | 22.6716 | 26.7602 | 50 | 45.96 | 191.3688 | 37.5572 | 37.9495 | 106.2402 | ON | 23.8 | 106.4 | 55.6442 | 40.7582 | -1.2729 | 4.2332 | 1.468 | 1.468 | 3.3971 |  | OK | OK | OK | OK | 111.3895 | OK | OK | OK | OK | OK
44811.819 | 1:15 | 95 | 135.099 | 132.1469 | 147.0953 | 79.3257 | 104.8809 | 104.8809 | 22.9965 | 22.5955 | 22.5721 | 26.7351 | 50 | 45.7691 | 191.4353 | 37.4964 | 37.8588 | 106.1864 | ON | 23.8 | 106.4 | 55.5257 | 40.6953 | -1.2045 | 4.1395 | 1.5191 | 1.5191 | 3.4089 |  | OK | OK | OK | OK | 111.299 | OK | OK | OK | OK | OK
44811.8191 | 1:15 | 95 | 135.1086 | 132.1043 | 147.0308 | 79.0326 | 104.8536 | 104.8536 | 22.9423 | 22.4123 | 22.5428 | 26.668 | 50 | 45.7869 | 191.4503 | 37.5136 | 37.8513 | 106.1561 | ON | 23.8 | 106.4 | 55.2326 | 40.6308 | -1.3877 | 4.2556 | 1.5464 | 1.5464 | 3.4082 |  | OK | OK | OK | OK | 111.3086 | OK | OK | OK | OK | OK
44811.8192 | 1:16 | 95 | 135.0059 | 132.0814 | 147.0182 | 78.6769 | 104.9244 | 104.9244 | 22.8692 | 22.2568 | 22.4679 | 26.5907 | 50 | 45.6483 | 191.4947 | 37.2768 | 37.7749 | 106.2072 | ON | 23.8 | 106.4 | 54.8768 | 40.6182 | -1.5432 | 4.3339 | 1.4756 | 1.4756 | 3.4167 |  | OK | OK | OK | OK | 111.2059 | OK | OK | OK | OK | OK
44811.8193 | 1:16 | 95 | 135.157 | 132.014 | 146.9531 | 78.3572 | 104.8636 | 104.8636 | 22.844 | 22.2427 | 22.4401 | 26.529 | 50 | 45.7712 | 191.3379 | 37.3324 | 37.6344 | 106.1589 | ON | 23.8 | 106.4 | 54.5572 | 40.5531 | -1.5574 | 4.2864 | 1.5364 | 1.5364 | 3.4072 |  | OK | OK | OK | OK | 111.357 | OK | OK | OK | OK | OK
44811.8195 | 1:16 | 95 | 134.996 | 131.9315 | 146.8873 | 78.1219 | 104.7467 | 104.7467 | 22.7218 | 22.1896 | 22.2958 | 26.4373 | 50 | 45.5237 | 190.9956 | 37.2837 | 37.6979 | 106.0378 | ON | 23.8 | 106.4 | 54.3219 | 40.4873 | -1.6104 | 4.2477 | 1.6533 | 1.6533 | 3.4155 |  | OK | OK | OK | OK | 111.196 | OK | OK | OK | OK | OK
44811.8196 | 1:16 | 95 | 134.9022 | 131.8904 | 146.8551 | 78.0009 | 104.7158 | 104.7158 | 22.6016 | 22.2025 | 22.24 | 26.3681 | 50 | 45.401 | 191.1515 | 37.0725 | 37.5956 | 106.0165 | ON | 23.8 | 106.4 | 54.2009 | 40.4551 | -1.5975 | 4.1656 | 1.6842 | 1.6842 | 3.4251 |  | OK | OK | OK | OK | 111.1022 | OK | OK | OK | OK | OK
44811.8197 | 1:16 | 95 | 134.8113 | 131.834 | 146.7968 | 77.8871 | 104.6578 | 104.6578 | 22.5715 | 22.0927 | 22.1881 | 26.3134 | 50 | 45.3853 | 190.9757 | 37.1745 | 37.6032 | 105.9603 | ON | 23.8 | 106.4 | 54.0871 | 40.3968 | -1.7073 | 4.2207 | 1.7422 | 1.7422 | 3.4231 |  | OK | OK | OK | OK | 111.0113 | OK | OK | OK | OK | OK
44811.8198 | 1:16 | 95 | 134.8103 | 131.8056 | 146.7455 | 77.7617 | 104.6774 | 104.6774 | 22.5625 | 22.0096 | 22.1673 | 26.2584 | 50 | 45.3954 | 190.9179 | 37.0978 | 37.3772 | 105.9595 | ON | 23.8 | 106.4 | 53.9617 | 40.3455 | -1.7904 | 4.2487 | 1.7226 | 1.7226 | 3.4215 |  | OK | OK | OK | OK | 111.0103 | OK | OK | OK | OK | OK
44811.8199 | 1:17 | 95 | 134.8497 | 131.8037 | 146.6928 | 77.6966 | 104.7172 | 104.7172 | 22.4823 | 21.9057 | 22.0734 | 26.1924 | 50 | 45.2608 | 190.8715 | 36.901 | 37.3487 | 106.0047 | ON | 23.8 | 106.4 | 53.8966 | 40.2928 | -1.8943 | 4.2867 | 1.6828 | 1.6828 | 3.4284 |  | OK | OK | OK | OK | 111.0497 | OK | OK | OK | OK | OK
44811.82 | 1:17 | 95 | 134.831 | 131.7867 | 146.6645 | 77.6489 | 104.6821 | 104.6821 | 22.3458 | 22.1221 | 21.9931 | 26.1327 | 50 | 45.2445 | 191.0208 | 36.9293 | 37.336 | 105.9735 | ON | 23.8 | 106.4 | 53.8489 | 40.2645 | -1.6779 | 4.0107 | 1.7179 | 1.7179 | 3.4319 |  | OK | OK | OK | OK | 111.031 | OK | OK | OK | OK | OK
44811.8202 | 1:17 | 95 | 134.8075 | 131.7551 | 146.6378 | 77.6579 | 104.6822 | 104.6822 | 22.3096 | 21.8808 | 21.9296 | 26.0696 | 50 | 45.1597 | 191.0143 | 36.8007 | 37.2398 | 105.9902 | ON | 23.8 | 106.4 | 53.8579 | 40.2378 | -1.9192 | 4.1888 | 1.7178 | 1.7178 | 3.4366 |  | OK | OK | OK | OK | 111.0075 | OK | OK | OK | OK | OK
44811.8203 | 1:17 | 95 | 134.852 | 131.7454 | 146.6638 | 77.611 | 104.6934 | 104.6934 | 22.2465 | 21.7845 | 21.8938 | 26.0147 | 50 | 45.1511 | 190.9907 | 36.7578 | 37.2942 | 105.9952 | ON | 23.8 | 106.4 | 53.8109 | 40.2638 | -2.0155 | 4.2302 | 1.7066 | 1.7066 | 3.4367 |  | OK | OK | OK | OK | 111.052 | OK | OK | OK | OK | OK
44811.8204 | 1:17 | 95 | 134.768 | 131.7922 | 146.6847 | 77.6303 | 104.837 | 104.837 | 22.1531 | 21.8132 | 21.8717 | 25.9514 | 50 | 45.0985 | 191.4246 | 36.7098 | 37.1385 | 106.1285 | ON | 23.8 | 106.4 | 53.8303 | 40.2847 | -1.9868 | 4.1381 | 1.563 | 1.563 | 3.447 |  | OK | OK | OK | OK | 110.968 | OK | OK | OK | OK | OK
44811.8205 | 1:17 | 95 | 134.7854 | 131.8022 | 146.7923 | 77.6054 | 104.8929 | 104.8929 | 22.1755 | 22.0058 | 21.8279 | 25.8666 | 50 | 45.0403 | 191.4654 | 36.7403 | 37.0865 | 106.1952 | ON | 23.8 | 106.4 | 53.8054 | 40.3923 | -1.7942 | 3.8608 | 1.5071 | 1.5071 | 3.451 |  | OK | OK | OK | OK | 110.9854 | OK | OK | OK | OK | OK
44811.8206 | 1:18 | 95 | 134.8364 | 131.7766 | 146.7454 | 77.5839 | 104.8166 | 104.8166 | 22.139 | 21.7343 | 21.7737 | 25.8032 | 50 | 45.0998 | 191.303 | 36.6242 | 37.1026 | 106.1128 | ON | 23.8 | 106.4 | 53.7839 | 40.3454 | -2.0657 | 4.069 | 1.5834 | 1.5834 | 3.4449 |  | OK | OK | OK | OK | 111.0364 | OK | OK | OK | OK | OK
44811.8207 | 1:18 | 95 | 134.7683 | 131.8315 | 146.7421 | 77.5942 | 104.8304 | 104.8304 | 22.0372 | 21.5875 | 21.656 | 25.7625 | 50 | 44.919 | 191.2272 | 36.4761 | 36.8853 | 106.1216 | ON | 22.84 | 106.4 | 54.7542 | 40.3421 | -1.2525 | 4.175 | 1.5696 | 1.5696 | 3.4541 |  | OK | OK | OK | OK | 111.9283 | OK | OK | OK | OK | OK
44811.8208 | 1:18 | 95 | 134.8863 | 131.8595 | 146.7647 | 77.5665 | 104.8924 | 104.8924 | 21.9584 | 21.6619 | 21.634 | 25.6798 | 50 | 44.8364 | 191.4128 | 36.344 | 36.9275 | 106.1681 | ON | 22.84 | 106.4 | 54.7264 | 40.3647 | -1.1781 | 4.0179 | 1.5076 | 1.5076 | 3.462 |  | OK | OK | OK | OK | 112.0463 | OK | OK | OK | OK | OK
44811.821 | 1:18 | 95 | 135.0015 | 131.9138 | 146.8038 | 77.5594 | 104.9227 | 104.9227 | 21.9314 | 21.5311 | 21.5752 | 25.6378 | 50 | 44.8324 | 191.7807 | 36.5293 | 36.7363 | 106.2153 | ON | 22.84 | 106.4 | 54.7194 | 40.4038 | -1.3089 | 4.1067 | 1.4773 | 1.4773 | 3.4684 |  | OK | OK | OK | OK | 112.1615 | OK | OK | OK | OK | OK
44811.8211 | 1:18 | 95 | 135.0228 | 131.8386 | 146.7878 | 77.5369 | 104.944 | 104.944 | 21.9276 | 21.4807 | 21.5316 | 25.5927 | 50 | 44.8003 | 191.5851 | 36.4074 | 36.6699 | 106.2356 | ON | 22.84 | 106.4 | 54.6969 | 40.3878 | -1.3593 | 4.112 | 1.456 | 1.456 | 3.467 |  | OK | OK | OK | OK | 112.1828 | OK | OK | OK | OK | OK
44811.8212 | 1:18 | 95 | 135.0858 | 131.8277 | 146.8233 | 77.5708 | 104.9823 | 104.9823 | 21.861 | 21.6217 | 21.4589 | 25.5339 | 50 | 44.7364 | 191.9135 | 36.2769 | 36.7168 | 106.2707 | ON | 22.84 | 106.4 | 54.7308 | 40.4233 | -1.2183 | 3.9122 | 1.4177 | 1.4177 | 3.4762 |  | OK | OK | OK | OK | 112.2458 | OK | OK | OK | OK | OK
44811.8213 | 1:19 | 95 | 135.0595 | 132.0138 | 146.8907 | 77.5938 | 105.0024 | 105.0024 | 21.7962 | 21.5739 | 21.3967 | 25.4705 | 50 | 44.6868 | 191.8869 | 36.3104 | 36.628 | 106.2961 | ON | 22.84 | 106.4 | 54.7538 | 40.4907 | -1.2661 | 3.8966 | 1.3976 | 1.3976 | 3.4787 |  | OK | OK | OK | OK | 112.2195 | OK | OK | OK | OK | OK
44811.8214 | 1:19 | 95 | 135.188 | 131.9854 | 146.9243 | 77.5858 | 105.062 | 105.062 | 21.7041 | 21.6892 | 21.3888 | 25.4356 | 50 | 44.986 | 191.8837 | 36.1969 | 36.5421 | 106.3343 | ON | 22.84 | 106.4 | 54.7458 | 40.5243 | -1.1508 | 3.7464 | 1.338 | 1.338 | 3.4612 |  | OK | OK | OK | OK | 112.348 | OK | OK | OK | OK | OK
44811.8215 | 1:19 | 95 | 135.2436 | 131.9902 | 146.9766 | 77.5214 | 105.0627 | 105.0627 | 21.6624 | 21.6615 | 21.1936 | 25.3457 | 50 | 44.4272 | 192.0575 | 36.1924 | 36.5715 | 106.3531 | ON | 22.84 | 106.4 | 54.6814 | 40.5766 | -1.1785 | 3.6842 | 1.3373 | 1.3373 | 3.4968 |  | OK | OK | OK | OK | 112.4036 | OK | OK | OK | OK | OK
44811.8217 | 1:19 | 95 | 135.2872 | 132.1117 | 147.0107 | 77.601 | 105.2079 | 105.2079 | 21.5773 | 21.4227 | 21.1648 | 25.2987 | 50 | 44.5014 | 192.4446 | 36.1123 | 36.4649 | 106.5063 | ON | 22.84 | 106.4 | 54.761 | 40.6107 | -1.4174 | 3.876 | 1.1921 | 1.1921 | 3.499 |  | OK | OK | OK | OK | 112.4472 | OK | OK | OK | OK | OK
44811.8218 | 1:19 | 95 | 135.4075 | 132.2603 | 147.1932 | 77.7647 | 105.4322 | 105.4322 | 21.5491 | 21.2923 | 21.1295 | 25.2469 | 50 | 44.2929 | 193.0192 | 35.9349 | 36.3806 | 106.6983 | ON | 22.84 | 106.4 | 54.9247 | 40.7932 | -1.5477 | 3.9546 | 0.9678 | 0.9678 | 3.5211 |  | OK | Low Charge | OK | OK | 112.5675 | OK | OK | OK | OK | OK
44811.8219 | 1:19 | 95 | 135.5359 | 132.3883 | 147.3229 | 77.8741 | 105.6538 | 105.6538 | 21.575 | 21.7804 | 21.128 | 25.2027 | 50 | 44.4736 | 193.7503 | 35.953 | 36.3504 | 106.9066 | ON | 22.84 | 106.4 | 55.0341 | 40.9229 | -1.0596 | 3.4223 | 0.7462 | 0.7462 | 3.5227 |  | OK | Low Charge | OK | OK | 112.6959 | OK | OK | OK | OK | OK
44811.822 | 1:20 | 95 | 135.751 | 132.5092 | 147.4402 | 78.0116 | 105.8456 | 105.8456 | 21.5227 | 21.1571 | 21.1092 | 25.1657 | 50 | 44.4426 | 194.0673 | 35.9037 | 36.2761 | 107.0587 | ON | 22.84 | 106.4 | 55.1716 | 41.0402 | -1.6829 | 4.0086 | 0.5544 | 0.5544 | 3.5299 |  | OK | Low Charge | OK | OK | 112.911 | OK | OK | OK | OK | OK
44811.8221 | 1:20 | 95 | 135.7235 | 132.6959 | 147.5686 | 78.1618 | 105.994 | 105.994 | 21.5449 | 21.4443 | 21.1398 | 25.1052 | 50 | 44.4584 | 194.6252 | 35.933 | 36.2831 | 107.2234 | ON | 22.84 | 106.4 | 55.3218 | 41.1686 | -1.3957 | 3.661 | 0.406 | 0.406 | 3.5384 |  | OK | Low Charge | OK | OK | 112.8835 | OK | OK | OK | OK | OK
44811.8222 | 1:20 | 95 | 135.9514 | 132.8465 | 147.7165 | 78.354 | 106.151 | 106.151 | 21.5406 | 21.4328 | 21.0415 | 25.038 | 50 | 44.3957 | 194.8425 | 35.9153 | 36.2728 | 107.3538 | ON | 22.84 | 106.4 | 55.514 | 41.3165 | -1.4072 | 3.6052 | 0.249 | 0.249 | 3.5458 |  | OK | Low Charge | OK | OK | 113.1114 | OK | OK | OK | OK | OK
44811.8224 | 1:20 | 95 | 136.1089 | 133.018 | 147.9557 | 78.5172 | 106.235 | 106.235 | 21.4683 | 21.5767 | 21.0289 | 24.958 | 50 | 44.2617 | 195.083 | 35.7457 | 36.1818 | 107.4682 | ON | 22.84 | 108.3 | 55.6772 | 39.6557 | -1.2633 | 3.3813 | 2.065 | 2.065 | 3.558 |  | OK | OK | OK | OK | 113.2689 | OK | OK | OK | OK | OK
44811.8225 | 1:20 | 95 | 136.4156 | 133.1896 | 148.0313 | 78.6747 | 106.3578 | 106.3578 | 21.4721 | 21.7126 | 20.9641 | 24.8767 | 50 | 44.1759 | 195.5 | 35.8223 | 36.0154 | 107.5572 | ON | 22.84 | 108.3 | 55.8347 | 39.7313 | -1.1274 | 3.1641 | 1.9422 | 1.9422 | 3.5702 |  | OK | OK | OK | OK | 113.5756 | OK | OK | OK | OK | OK
44811.8226 | 1:20 | 95 | 136.5907 | 133.313 | 148.2053 | 78.824 | 106.4029 | 106.4029 | 21.4387 | 21.4408 | 20.9505 | 24.8471 | 50 | 44.3992 | 195.5948 | 35.6787 | 35.9918 | 107.617 | ON | 22.84 | 108.3 | 55.984 | 39.9053 | -1.3992 | 3.4063 | 1.8971 | 1.8971 | 3.5583 |  | OK | OK | OK | OK | 113.7507 | OK | OK | OK | OK | OK
44811.8227 | 1:21 | 95 | 136.7091 | 133.4284 | 148.3846 | 78.9442 | 106.4917 | 106.4917 | 21.387 | 21.394 | 20.8944 | 24.809 | 50 | 44.2757 | 195.7618 | 35.7495 | 35.9116 | 107.7013 | ON | 22.84 | 108.3 | 56.1042 | 40.0846 | -1.446 | 3.415 | 1.8083 | 1.8083 | 3.5686 |  | OK | OK | OK | OK | 113.8691 | OK | OK | OK | OK | OK
44811.8228 | 1:21 | 95 | 136.8239 | 133.492 | 148.5061 | 79.0667 | 106.4973 | 106.4973 | 21.3458 | 21.7962 | 20.8801 | 24.7586 | 50 | 44.2998 | 195.7411 | 35.4903 | 35.8862 | 107.7087 | ON | 22.84 | 108.3 | 56.2267 | 40.2061 | -1.0438 | 2.9625 | 1.8027 | 1.8027 | 3.5668 |  | OK | OK | OK | OK | 113.9839 | OK | OK | OK | OK | OK
44811.8229 | 1:21 | 95 | 136.9791 | 133.6063 | 148.6648 | 79.1811 | 106.5752 | 106.5752 | 21.2975 | 21.9128 | 20.8014 | 24.7353 | 50 | 44.1838 | 196.0896 | 35.4533 | 35.7004 | 107.7991 | ON | 22.84 | 108.3 | 56.3411 | 40.3648 | -0.92718 | 2.8225 | 1.7248 | 1.7248 | 3.5798 |  | OK | OK | OK | OK | 114.1391 | OK | OK | OK | OK | OK
44811.823 | 1:21 | 95 | 137.0077 | 133.7813 | 148.8034 | 79.2781 | 106.627 | 106.627 | 21.3231 | 21.6749 | 20.7528 | 24.6956 | 50 | 44.1249 | 196.0931 | 35.4188 | 35.7613 | 107.84 | ON | 22.84 | 108.3 | 56.4381 | 40.5034 | -1.1651 | 3.0207 | 1.673 | 1.673 | 3.5834 |  | OK | OK | OK | OK | 114.1677 | OK | OK | OK | OK | OK
44811.8232 | 1:21 | 95 | 137.2147 | 133.9186 | 148.9372 | 79.386 | 106.661 | 106.661 | 21.3019 | 21.2382 | 20.7537 | 24.6703 | 50 | 44.1616 | 196.1141 | 35.5186 | 35.6796 | 107.8737 | ON | 22.84 | 108.3 | 56.5461 | 40.6372 | -1.6018 | 3.4322 | 1.639 | 1.639 | 3.5815 |  | OK | OK | OK | OK | 114.3747 | OK | OK | OK | OK | OK
44811.8233 | 1:21 | 95 | 137.2424 | 134.0329 | 149.0439 | 79.4475 | 106.7036 | 106.7036 | 21.2809 | 21.0934 | 20.7112 | 24.6361 | 50 | 44.1243 | 196.401 | 35.4301 | 35.6123 | 107.885 | ON | 22.84 | 108.3 | 56.6075 | 40.7439 | -1.7466 | 3.5427 | 1.5964 | 1.5964 | 3.5887 |  | OK | OK | OK | OK | 114.4024 | OK | OK | OK | OK | OK
44811.8234 | 1:22 | 95 | 137.4231 | 134.1693 | 149.1091 | 79.5023 | 106.6707 | 106.6707 | 21.2218 | 21.2892 | 20.6108 | 24.6107 | 50 | 44.047 | 196.0757 | 35.4337 | 35.5589 | 107.8782 | ON | 22.84 | 108.3 | 56.6623 | 40.8091 | -1.5508 | 3.3214 | 1.6293 | 1.6293 | 3.5879 |  | OK | OK | OK | OK | 114.5831 | OK | OK | OK | OK | OK
44811.8235 | 1:22 | 95 | 137.5177 | 134.2049 | 149.1882 | 79.5354 | 106.635 | 106.635 | 21.1606 | 21.4028 | 20.5509 | 24.5598 | 50 | 43.9553 | 195.9001 | 35.2492 | 35.545 | 107.8508 | ON | 21.87 | 108.3 | 57.6654 | 40.8882 | -0.46717 | 3.157 | 1.665 | 1.665 | 3.5905 |  | OK | OK | OK | OK | 115.6477 | OK | OK | OK | OK | OK
44811.8236 | 1:22 | 95 | 137.4247 | 134.2724 | 149.3177 | 79.5481 | 106.6268 | 106.6268 | 21.1828 | 21.6731 | 20.5689 | 24.5263 | 50 | 44.0235 | 196.1656 | 35.2176 | 35.4792 | 107.808 | ON | 22.84 | 108.3 | 56.7081 | 41.0177 | -1.1669 | 2.8532 | 1.6732 | 1.6732 | 3.5908 |  | OK | OK | OK | OK | 114.5847 | OK | OK | OK | OK | OK
44811.8237 | 1:22 | 95 | 137.6008 | 134.2251 | 149.3562 | 79.6064 | 106.5099 | 106.5099 | 21.168 | 21.0381 | 20.4723 | 24.5098 | 50 | 43.9088 | 195.8961 | 35.3331 | 35.4369 | 107.7483 | ON | 21.87 | 108.3 | 57.7364 | 41.0562 | -0.83187 | 3.4716 | 1.7901 | 1.7901 | 3.5933 |  | OK | OK | OK | OK | 115.7308 | OK | OK | OK | OK | OK
44811.8239 | 1:22 | 95 | 137.6414 | 134.2593 | 149.4243 | 79.5744 | 106.4479 | 106.4479 | 21.1149 | 20.7342 | 20.3968 | 24.4529 | 50 | 43.9101 | 195.4184 | 35.0504 | 35.3575 | 107.6537 | ON | 21.87 | 108.3 | 57.7044 | 41.1243 | -1.1358 | 3.7187 | 1.8521 | 1.8521 | 3.585 |  | OK | OK | OK | OK | 115.7714 | OK | OK | OK | OK | OK
44811.824 | 1:22 | 95 | 138.0785 | 134.5683 | 149.7169 | 79.592 | 108.2069 | 108.2069 | 20.8912 | 20.4314 | 20.0842 | 24.4098 | 50 | 42.978 | 202.7871 | 35.0315 | 35.3161 | 108.9038 | ON | 20.88 | 110.2 | 58.712 | 39.5169 | -0.44862 | 3.9784 | 1.9931 | 1.9931 | 3.7707 |  | OK | OK | OK | OK | 117.1985 | OK | OK | OK | OK | OK
44811.8241 | 1:23 | 95 | 138.5503 | 135.1479 | 150.0818 | 79.0825 | 109.1469 | 109.1469 | 20.2048 | 18.193 | 20.8465 | 24.5582 | 50 | 41.133 | 204.2219 | 34.9374 | 35.2973 | 109.6502 | ON | 19.89 | 110.2 | 59.1925 | 39.8818 | -1.697 | 6.3653 | 1.0531 | 1.0531 | 3.921 |  | OK | OK | OK | OK | 118.6603 | OK | OK | OK | OK | OK
44811.8242 | 1:23 | 95 | 138.8675 | 135.3466 | 150.2847 | 77.0929 | 109.0791 | 109.0791 | 19.8668 | 17.5695 | 22.1493 | 25.2045 | 50 | 40.2606 | 203.6481 | 34.7311 | 35.4272 | 109.6148 | ON | 18.88 | 110.2 | 58.2129 | 40.0847 | -1.3105 | 7.635 | 1.1209 | 1.1209 | 3.9728 |  | OK | OK | OK | OK | 119.9875 | OK | OK | OK | OK | OK
44811.8243 | 1:23 | 95 | 138.8883 | 135.4116 | 150.3208 | 74.1681 | 108.8949 | 108.8949 | 19.5532 | 17.1993 | 23.596 | 26.0161 | 50 | 40.2268 | 202.9251 | 34.637 | 35.477 | 109.4803 | ON | 18.88 | 110.2 | 55.2881 | 40.1208 | -1.6807 | 8.8169 | 1.3051 | 1.3051 | 3.9621 |  | OK | OK | OK | OK | 120.0083 | OK | OK | OK | OK | OK
44811.8244 | 1:23 | 95 | 138.8972 | 135.3804 | 150.2121 | 70.7901 | 108.7679 | 108.7679 | 19.2519 | 16.8094 | 24.9752 | 26.8712 | 50 | 39.9661 | 203.0049 | 34.4655 | 35.6212 | 109.391 | ON | 17.86 | 110.2 | 52.9301 | 40.0121 | -1.0506 | 10.0619 | 1.4321 | 1.4321 | 3.9824 |  | OK | OK | OK | OK | 121.0372 | OK | OK | OK | OK | OK
44811.8246 | 1:23 | 95 | 138.771 | 135.2001 | 149.9835 | 66.823 | 108.6216 | 108.6216 | 18.9168 | 16.4865 | 26.1871 | 27.6733 | 50 | 39.5749 | 202.2603 | 34.5824 | 35.5734 | 109.2689 | ON | 17.86 | 110.2 | 48.963 | 39.7835 | -1.3735 | 11.1867 | 1.5784 | 1.5784 | 3.9974 |  | OK | OK | OK | OK | 120.911 | OK | OK | OK | OK | OK
44811.8247 | 1:23 | 95 | 138.2636 | 134.9274 | 149.5708 | 63.2038 | 108.5564 | 108.5564 | 18.6553 | 16.1733 | 27.1633 | 28.361 | 50 | 39.2216 | 202.4435 | 34.53 | 35.724 | 109.2256 | ON | 17.86 | 110.2 | 45.3438 | 39.3708 | -1.6867 | 12.1877 | 1.6436 | 1.6436 | 4.027 |  | OK | OK | OK | OK | 120.4036 | OK | OK | OK | OK | OK
44811.8248 | 1:24 | 95 | 137.6484 | 134.4484 | 148.995 | 59.9277 | 108.4791 | 108.4791 | 18.3185 | 15.808 | 27.9608 | 28.9762 | 50 | 39.1148 | 201.7808 | 34.2677 | 35.6109 | 109.1541 | ON | 17.86 | 110.2 | 42.0677 | 38.795 | -2.052 | 13.1682 | 1.7209 | 1.7209 | 4.0227 |  | OK | OK | OK | OK | 119.7884 | OK | OK | OK | OK | OK
44811.8249 | 1:24 | 95 | 137.0014 | 134.0342 | 148.3708 | 55.0191 | 108.4692 | 108.4692 | 18.1277 | 15.5557 | 28.5769 | 29.4861 | 50 | 38.8185 | 201.8288 | 34.0997 | 35.6538 | 109.1534 | ON | 16.82 | 110.2 | 38.1991 | 38.1708 | -1.2643 | 13.9305 | 1.7308 | 1.7308 | 4.0459 |  | OK | OK | OK | OK | 120.1814 | OK | OK | OK | OK | OK
44811.825 | 1:24 | 95 | 136.2062 | 133.4834 | 147.6913 | 52.1773 | 108.2428 | 108.2428 | 17.8282 | 15.3148 | 29.0415 | 29.9161 | 50 | 38.4958 | 201.4427 | 33.9511 | 35.658 | 108.9371 | ON | 16.82 | 110.2 | 35.3573 | 37.4913 | -1.5052 | 14.6013 | 1.9572 | 1.9572 | 4.0632 |  | OK | OK | OK | OK | 119.3862 | OK | OK | OK | OK | OK
44811.8251 | 1:24 | 95 | 135.4269 | 132.9735 | 147.0168 | 51.4045 | 108.1404 | 108.1404 | 17.5848 | 15.0649 | 29.3941 | 30.3148 | 50 | 38.1642 | 201.2994 | 34.0176 | 35.6665 | 108.8331 | ON | 16.82 | 110.2 | 34.5845 | 36.8168 | -1.7551 | 15.2499 | 2.0596 | 2.0596 | 4.0859 |  | OK | OK | OK | OK | 118.6069 | OK | OK | OK | OK | OK
44811.8252 | 1:24 | 95 | 134.7724 | 132.4745 | 146.391 | 50.6918 | 108.0909 | 108.0909 | 17.3714 | 14.9025 | 29.6726 | 30.5954 | 50 | 38.1453 | 200.6474 | 33.8929 | 35.6977 | 108.735 | ON | 16.82 | 110.2 | 33.8718 | 36.191 | -1.9175 | 15.6929 | 2.1091 | 2.1091 | 4.0751 |  | OK | OK | OK | OK | 117.9524 | OK | OK | OK | OK | OK
44811.8254 | 1:24 | 95 | 134.2055 | 131.8443 | 145.717 | 50.9357 | 107.8121 | 107.8121 | 17.0847 | 14.5532 | 29.8937 | 30.869 | 50 | 37.7535 | 200.1279 | 33.8397 | 35.7711 | 108.5001 | ON | 15.76 | 110.2 | 35.1757 | 35.517 | -1.2068 | 16.3158 | 2.3879 | 2.3879 | 4.0956 |  | OK | OK | OK | OK | 118.4455 | OK | OK | OK | OK | OK
44811.8255 | 1:25 | 95 | 133.6542 | 131.4153 | 145.1378 | 50.9242 | 107.699 | 107.699 | 16.8795 | 14.4178 | 30.0554 | 31.0951 | 50 | 37.5984 | 199.5453 | 33.7274 | 35.752 | 108.3951 | ON | 15.76 | 108.3 | 35.1642 | 36.8378 | -1.3422 | 16.6773 | 0.601 | 0.601 | 4.0966 |  | OK | Low Charge | OK | OK | 117.8942 | OK | OK | OK | OK | OK
44811.8256 | 1:25 | 95 | 133.1572 | 130.9332 | 144.5979 | 50.4738 | 107.5032 | 107.5032 | 16.6786 | 14.218 | 30.1901 | 31.2817 | 50 | 37.4541 | 199.4146 | 33.5149 | 35.7178 | 108.1919 | ON | 15.76 | 108.3 | 34.7138 | 36.2979 | -1.542 | 17.0637 | 0.7968 | 0.7968 | 4.1054 |  | OK | Low Charge | OK | OK | 117.3972 | OK | OK | OK | OK | OK
44811.8257 | 1:25 | 95 | 132.8307 | 130.4909 | 144.0812 | 51.2459 | 107.2499 | 107.2499 | 16.4444 | 13.9895 | 30.3163 | 31.4592 | 50 | 37.2101 | 198.596 | 33.5348 | 35.7298 | 107.9947 | ON | 15.76 | 108.3 | 35.4859 | 35.7812 | -1.7705 | 17.4697 | 1.0501 | 1.0501 | 4.109 |  | OK | OK | OK | OK | 117.0707 | OK | OK | OK | OK | OK
44811.8258 | 1:25 | 95 | 132.4536 | 130.0633 | 143.5903 | 51.6637 | 107.1147 | 107.1147 | 16.2485 | 13.7981 | 30.3958 | 31.5876 | 50 | 37.1629 | 198.2241 | 33.4066 | 35.5802 | 107.8848 | ON | 15.76 | 108.3 | 35.9037 | 35.2903 | -1.9619 | 17.7895 | 1.1853 | 1.1853 | 4.1055 |  | OK | OK | OK | OK | 116.6936 | OK | OK | OK | OK | OK
44811.8259 | 1:25 | 95 | 132.1251 | 129.6904 | 143.2005 | 51.9812 | 106.959 | 106.959 | 16.0242 | 13.6232 | 30.4301 | 31.7079 | 50 | 37.0772 | 197.8214 | 33.4751 | 35.5465 | 107.7266 | ON | 15.76 | 108.3 | 36.2212 | 34.9005 | -2.1368 | 18.0847 | 1.341 | 1.341 | 4.1045 |  | OK | OK | OK | OK | 116.3651 | OK | OK | OK | OK | OK
44811.8261 | 1:25 | 95 | 131.7914 | 129.4067 | 142.7783 | 51.8864 | 106.7778 | 106.7778 | 15.8276 | 13.4014 | 30.5187 | 31.8142 | 50 | 36.7802 | 197.4256 | 33.3231 | 35.5114 | 107.5124 | ON | 14.7 | 108.3 | 37.1864 | 34.4783 | -1.2986 | 18.4128 | 1.5222 | 1.5222 | 4.1205 |  | OK | OK | OK | OK | 117.0914 | OK | OK | OK | OK | OK
44811.8262 | 1:26 | 95 | 131.5508 | 129.088 | 142.4308 | 52.0341 | 106.6492 | 106.6492 | 15.6474 | 13.2522 | 30.5556 | 31.9069 | 50 | 36.575 | 196.9988 | 33.0477 | 35.5521 | 107.3716 | ON | 14.7 | 108.3 | 37.3341 | 34.1308 | -1.4478 | 18.6547 | 1.6508 | 1.6508 | 4.1287 |  | OK | OK | OK | OK | 116.8508 | OK | OK | OK | OK | OK
44811.8263 | 1:26 | 95 | 131.8067 | 129.007 | 142.3257 | 52.8443 | 107.7726 | 107.7726 | 14.6331 | 12.8748 | 30.5751 | 31.9663 | 50 | 35.4845 | 205.8723 | 33.1341 | 35.4822 | 108.5842 | ON | 13.61 | 112 | 39.2343 | 30.3257 | -0.73522 | 19.0916 | 4.2274 | 4.2274 | 4.3952 |  | OK | OK | OK | OK | 118.1967 | OK | OK | OK | OK | OK
44811.8264 | 1:26 | 95 | 131.5893 | 129.268 | 141.1604 | 53.7659 | 107.4252 | 107.4252 | 13.9815 | 13.9516 | 30.5895 | 31.956 | 50 | 18.7599 | 199.9232 | 33.0317 | 35.4507 | 107.9413 | ON | -7.99 | 108.3 | 61.7559 | 32.8604 | 21.9416 | 18.0044 | 0.8748 | 0.8748 | 6.4143 |  | OK | Low Charge | OK | OK | 139.5793 | OK | OK | OK | OK | OK
44811.8265 | 1:26 | 95 | 131.3913 | 128.3877 | 139.0243 | 55.1856 | 104.7838 | 104.7838 | 16.502 | 16.4165 | 30.6275 | 32.0113 | 50 | 16.4974 | 195.4935 | 33.498 | 35.7012 | 106.2536 | ON | -11.06 | 108.3 | 66.2456 | 30.7243 | 27.4765 | 15.5948 | 3.5162 | 3.5162 | 6.7375 |  | OK | OK | OK | OK | 142.4513 | OK | OK | OK | OK | OK
44811.8266 | 1:26 | 95 | 131.4387 | 127.8033 | 137.9024 | 57.4737 | 103.1881 | 103.1881 | 19.339 | 18.7425 | 30.7032 | 32.1184 | 50 | 15.9324 | 192.3311 | 34.1247 | 35.8299 | 105.4174 | ON | -12.65 | 106.4 | 70.1237 | 31.5024 | 31.3925 | 13.3759 | 3.2119 | 3.2119 | 6.7586 |  | OK | OK | OK | OK | 144.0887 | OK | OK | OK | OK | OK
44811.8268 | 1:26 | 95 | 131.817 | 127.455 | 137.2529 | 59.089 | 103.1234 | 103.1234 | 21.9606 | 20.7696 | 30.826 | 32.197 | 50 | 15.4769 | 190.8909 | 34.656 | 36.0279 | 104.7364 | ON | -12.65 | 106.4 | 71.739 | 30.8529 | 33.4196 | 11.4273 | 3.2766 | 3.2766 | 6.8129 |  | OK | OK | OK | OK | 144.467 | OK | OK | OK | OK | OK
44811.8269 | 1:27 | 95 | 132.3472 | 127.247 | 136.8667 | 60.1216 | 102.2511 | 102.2511 | 24.2752 | 22.5314 | 30.9588 | 32.3034 | 50 | 14.5541 | 189.8166 | 35.0022 | 36.1761 | 104.3316 | ON | -14.28 | 104.4 | 74.4016 | 32.4667 | 36.8114 | 9.772 | 2.1489 | 2.1489 | 6.991 |  | OK | OK | OK | OK | 146.6272 | OK | OK | OK | OK | OK
44811.827 | 1:27 | 95 | 132.7389 | 127.2205 | 136.8026 | 60.6105 | 101.9035 | 101.9035 | 26.1045 | 23.9792 | 31.0769 | 32.4214 | 50 | 13.9152 | 188.9032 | 35.4155 | 36.3611 | 104.0058 | ON | -15.96 | 104.4 | 76.5705 | 32.4026 | 39.9392 | 8.4422 | 2.4965 | 2.4965 | 7.1152 |  | OK | OK | OK | OK | 148.6989 | OK | OK | OK | OK | OK
44811.8271 | 1:27 | 95 | 133.2533 | 127.1738 | 136.8068 | 60.7639 | 101.4439 | 101.4439 | 27.5497 | 25.2043 | 31.1946 | 32.5235 | 50 | 13.557 | 188.1609 | 35.773 | 36.4647 | 103.7296 | ON | -15.96 | 104.4 | 76.7239 | 32.4068 | 41.1643 | 7.3192 | 2.9561 | 2.9561 | 7.1791 |  | OK | OK | OK | OK | 149.2133 | OK | OK | OK | OK | OK
44811.8272 | 1:27 | 95 | 133.678 | 127.3377 | 136.8923 | 60.7185 | 101.3939 | 101.3939 | 28.6816 | 26.1804 | 31.2847 | 32.6314 | 50 | 12.9561 | 187.7838 | 35.8218 | 36.4436 | 103.5422 | ON | -17.69 | 104.4 | 78.4085 | 32.4923 | 43.8704 | 6.451 | 3.0061 | 3.0061 | 7.3215 |  | OK | OK | OK | OK | 151.368 | OK | OK | OK | OK | OK
44811.8273 | 1:27 | 95 | 134.1546 | 127.3637 | 136.8737 | 60.6264 | 100.874 | 100.874 | 29.4914 | 26.9771 | 31.3681 | 32.778 | 50 | 12.7572 | 186.606 | 36.0716 | 36.5515 | 103.2123 | ON | -17.69 | 104.4 | 78.3164 | 32.4737 | 44.6671 | 5.8008 | 3.526 | 3.526 | 7.3316 |  | OK | OK | OK | OK | 151.8446 | OK | OK | OK | OK | OK
44811.8274 | 1:27 | 95 | 134.6749 | 127.4716 | 137.0863 | 60.1214 | 100.7013 | 100.7013 | 30.0756 | 27.5648 | 31.4245 | 32.9195 | 50 | 12.8164 | 186.6226 | 36.2138 | 36.6682 | 103.0917 | ON | -17.69 | 104.4 | 77.8114 | 32.6863 | 45.2548 | 5.3547 | 3.6987 | 3.6987 | 7.3164 |  | OK | OK | OK | OK | 152.3649 | OK | OK | OK | OK | OK
44811.8276 | 1:28 | 95 | 135.1417 | 127.7175 | 137.3548 | 59.4867 | 100.5447 | 100.5447 | 30.4811 | 28.0727 | 31.4676 | 33.0484 | 50 | 12.2357 | 186.3408 | 36.4189 | 36.7565 | 103.0216 | ON | -17.69 | 104.4 | 77.1767 | 32.9548 | 45.7627 | 4.9757 | 3.8553 | 3.8553 | 7.4637 |  | OK | OK | OK | OK | 152.8317 | OK | OK | OK | OK | OK
44811.8277 | 1:28 | 95 | 135.6245 | 127.9922 | 137.5691 | 58.8407 | 100.5279 | 100.5279 | 30.7674 | 28.4908 | 31.524 | 33.1944 | 50 | 11.8949 | 185.8335 | 36.3261 | 36.822 | 102.8922 | ON | -19.46 | 104.4 | 78.3007 | 33.1691 | 47.9508 | 4.7036 | 3.8721 | 3.8721 | 7.5403 |  | OK | OK | OK | OK | 155.0845 | OK | OK | OK | OK | OK
44811.8278 | 1:28 | 95 | 136.065 | 128.1605 | 137.8344 | 57.9695 | 100.4687 | 100.4687 | 30.9846 | 28.8152 | 31.5423 | 33.3404 | 50 | 11.748 | 185.9294 | 36.5188 | 36.8596 | 102.8337 | ON | -19.46 | 104.4 | 77.4295 | 33.4344 | 48.2752 | 4.5252 | 3.9313 | 3.9313 | 7.5858 |  | OK | OK | OK | OK | 155.525 | OK | OK | OK | OK | OK
44811.8279 | 1:28 | 95 | 136.5029 | 128.406 | 138.1448 | 57.0061 | 100.3437 | 100.3437 | 31.1384 | 29.0902 | 31.5896 | 33.4674 | 50 | 11.6145 | 185.7038 | 36.6857 | 36.989 | 102.7879 | ON | -19.46 | 104.4 | 76.4661 | 33.7448 | 48.5502 | 4.3772 | 4.0563 | 4.0563 | 7.6157 |  | OK | OK | OK | OK | 155.9629 | OK | OK | OK | OK | OK
44811.828 | 1:28 | 95 | 136.9604 | 128.6747 | 138.4047 | 55.865 | 100.3104 | 100.3104 | 31.2569 | 29.3359 | 31.5942 | 33.6251 | 50 | 11.6583 | 185.6972 | 36.7626 | 37.0894 | 102.7652 | ON | -19.46 | 104.4 | 75.325 | 34.0047 | 48.7959 | 4.2892 | 4.0896 | 4.0896 | 7.6028 |  | OK | OK | OK | OK | 156.4204 | OK | OK | OK | OK | OK
44811.8281 | 1:28 | 95 | 137.1799 | 128.8951 | 138.6161 | 54.3668 | 100.1237 | 100.1237 | 31.3562 | 29.5911 | 31.6254 | 33.7745 | 50 | 11.0846 | 185.1027 | 36.8179 | 37.1939 | 102.6118 | ON | -19.46 | 104.4 | 73.8268 | 34.2161 | 49.0511 | 4.1834 | 4.2763 | 4.2763 | 7.7489 |  | OK | OK | OK | OK | 156.6399 | OK | OK | OK | OK | OK
44811.8283 | 1:29 | 95 | 141.5087 | 127.8949 | 137.2043 | 56.4077 | 92.5738 | 92.5738 | 25.429 | 30.438 | 27.8295 | 34.2771 | 50 | 51.611 | 132.1567 | 36.8681 | 37.328 | 99.279 | OFF | 29.31 | 80.35 | 27.0977 | 56.8543 | 1.128 | 3.839 | -12.2238 | -12.2238 | 2.2147
44811.8284 | 1:29 | 95 | 141.9342 | 125.0366 | 130.9197 | 65.76 | 91.4577 | 91.4577 | 28.811 | 30.4617 | 29.375 | 34.1552 | 50 | 55.0917 | 122.1205 | 36.7404 | 37.297 | 98.3529 | OFF | 32.77 | 75.27 | 32.99 | 55.6497 | -2.3083 | 3.6935 | -16.1877 | -16.1877 | 1.9604
44811.8285 | 1:29 | 95 | 141.011 | 123.4887 | 124.4372 | 71.8198 | 90.8623 | 90.8623 | 29.588 | 31.0583 | 30.7022 | 34.0898 | 50 | 56.9025 | 113.2079 | 36.8731 | 37.3624 | 97.4999 | OFF | 33.62 | 69.9 | 38.1998 | 54.5372 | -2.5617 | 3.0315 | -20.9623 | -20.9623 | 1.7864
44811.8286 | 1:29 | 95 | 139.7247 | 121.9015 | 119.0918 | 77.0587 | 90.1738 | 90.1738 | 30.5195 | 31.5872 | 31.3674 | 34.1561 | 50 | 57.5654 | 104.958 | 36.9374 | 37.3546 | 96.9872 | OFF | 34.45 | 64.21 | 42.6087 | 54.8818 | -2.8628 | 2.5689 | -25.9638 | -25.9638 | 1.6558
44811.8287 | 1:29 | 95 | 138.3137 | 120.4541 | 114.7306 | 81.5996 | 89.4941 | 89.4941 | 31.0028 | 32.0434 | 31.6697 | 34.3198 | 50 | 58.5324 | 96.6598 | 37.1253 | 37.4654 | 96.556 | OFF | 35.28 | 61.23 | 46.3196 | 53.5006 | -3.2366 | 2.2764 | -28.2641 | -28.2641 | 1.5206
44811.8288 | 1:29 | 95 | 137.0832 | 119.1594 | 111.3904 | 85.0182 | 88.7795 | 88.7795 | 31.4805 | 32.6781 | 31.7449 | 34.4639 | 50 | 59.14 | 92.5999 | 37.1317 | 37.5742 | 96.2398 | OFF | 36.1 | 58.13 | 48.9182 | 53.2604 | -3.4219 | 1.7857 | -30.6495 | -30.6495 | 1.4531
44811.8289 | 1:30 | 95 | 135.8028 | 117.9864 | 108.4441 | 88.7547 | 86.5282 | 86.5282 | 31.8472 | 33.651 | 31.8004 | 34.7955 | 50 | 60.6121 | 87.3539 | 37.2187 | 37.6382 | 96.0092 | OFF | 36.91 | 54.95 | 51.8447 | 53.4941 | -3.259 | 1.1445 | -31.5782 | -31.5782 | 1.3551
44811.8291 | 1:30 | 95 | 134.6223 | 116.8447 | 105.4429 | 93.7738 | 83.4853 | 83.4853 | 31.8884 | 34.7034 | 31.7837 | 35.2792 | 50 | 61.7114 | 83.1599 | 37.3677 | 37.6796 | 95.8887 | OFF | 37.71 | 51.63 | 56.0638 | 53.8129 | -3.0066 | 0.57581 | -31.8553 | -31.8553 | 1.2807
44811.8292 | 1:30 | 95 | 133.4515 | 115.7987 | 103.3271 | 97.5823 | 81.5097 | 81.5097 | 31.8984 | 35.662 | 31.7843 | 35.9306 | 50 | 62.7436 | 79.1609 | 37.6907 | 37.7626 | 95.7739 | OFF | 38.5 | 48.19 | 59.0823 | 55.1371 | -2.838 | 0.26863 | -33.3197 | -33.3197 | 1.212
44811.8293 | 1:30 | 95 | 132.3825 | 114.8727 | 102.0136 | 100.1665 | 80.7595 | 80.7595 | 31.9478 | 36.6269 | 31.9496 | 36.7075 | 50 | 64.1187 | 74.2819 | 37.7588 | 37.9668 | 95.7488 | OFF | 40.07 | 44.59 | 60.0965 | 57.4236 | -3.4431 | 0.08068 | -36.1695 | -36.1695 | 1.1289
44811.8294 | 1:30 | 95 | 131.4075 | 114.1209 | 101.4626 | 101.221 | 81.6931 | 81.6931 | 32.0089 | 37.1085 | 31.8894 | 37.0948 | 50 | 64.5512 | 69.6553 | 37.8127 | 38.0664 | 95.7711 | OFF | 40.07 | 43.86 | 61.151 | 57.6026 | -2.9615 | -0.01365 | -37.8331 | -37.8331 | 1.0644
44811.8295 | 1:30 | 95 | 130.5068 | 113.4247 | 101.4452 | 101.2042 | 83.4442 | 83.4442 | 32.1588 | 37.3238 | 31.9275 | 37.3622 | 50 | 64.8783 | 68.0261 | 38.1575 | 38.2173 | 95.8561 | OFF | 40.07 | 43.11 | 61.1342 | 58.3352 | -2.7462 | 0.03844 | -40.3342 | -40.3342 | 1.0396
44811.8296 | 1:31 | 95 | 129.6044 | 112.8342 | 101.5529 | 100.9102 | 85.0775 | 85.0775 | 32.3685 | 37.4904 | 32.1838 | 37.5845 | 50 | 65.0763 | 67.1884 | 38.3177 | 38.3991 | 95.9311 | OFF | 40.84 | 42.36 | 60.0702 | 59.1929 | -3.3496 | 0.09409 | -42.7175 | -42.7175 | 1.0265
44811.8298 | 1:31 | 95 | 128.8541 | 112.3395 | 101.6393 | 100.691 | 86.5965 | 86.5965 | 32.5829 | 37.6519 | 32.2441 | 37.7875 | 50 | 65.3574 | 66.8319 | 38.551 | 38.4662 | 95.9727 | OFF | 40.84 | 41.6 | 59.851 | 60.0393 | -3.1881 | 0.13568 | -44.9965 | -44.9965 | 1.0184
44811.8299 | 1:31 | 95 | 128.1087 | 111.9448 | 101.6771 | 100.6178 | 87.6336 | 87.6336 | 32.8055 | 37.966 | 32.4949 | 38.0384 | 50 | 65.7385 | 65.3517 | 38.8078 | 38.5531 | 96.0597 | OFF | 40.84 | 40.84 | 59.7778 | 60.8371 | -2.874 | 0.07248 | -46.7936 | -46.7936 | 0.99519
44811.83 | 1:31 | 95 | 127.3672 | 111.5413 | 101.7065 | 100.5515 | 88.768 | 88.768 | 33.1924 | 38.1291 | 33.2686 | 38.2584 | 50 | 65.9626 | 65.3919 | 38.8591 | 38.6144 | 96.108 | OFF | 40.84 | 40.84 | 59.7115 | 60.8665 | -2.7109 | 0.12926 | -47.928 | -47.928 | 0.99293
44811.8301 | 1:31 | 95 | 126.6888 | 111.2044 | 101.7719 | 100.3684 | 89.738 | 89.738 | 33.5857 | 38.3176 | 33.9405 | 38.4879 | 50 | 66.2204 | 65.477 | 38.8899 | 38.7833 | 96.1261 | OFF | 41.6 | 40.84 | 58.7684 | 60.9319 | -3.2824 | 0.17037 | -48.898 | -48.898 | 0.99081
44811.8302 | 1:31 | 95 | 126.0884 | 110.8871 | 101.8219 | 100.2432 | 90.6124 | 90.6124 | 34.3663 | 38.4601 | 34.7811 | 38.7019 | 50 | 66.3586 | 65.6472 | 39.0603 | 38.9123 | 96.203 | OFF | 41.6 | 40.84 | 58.6432 | 60.9819 | -3.1399 | 0.24183 | -49.7724 | -49.7724 | 0.99122
44811.8303 | 1:32 | 95 | 125.4256 | 110.6261 | 101.8597 | 100.0336 | 91.3204 | 91.3204 | 35.4761 | 38.6712 | 35.5187 | 38.8976 | 50 | 66.6818 | 65.8902 | 39.2738 | 38.9838 | 96.2663 | OFF | 41.6 | 40.84 | 58.4336 | 61.0197 | -2.9288 | 0.2264 | -50.4804 | -50.4804 | 0.99027
44811.8305 | 1:32 | 95 | 124.8486 | 110.3575 | 101.868 | 99.8122 | 91.8927 | 91.8927 | 36.253 | 38.8039 | 36.0656 | 39.0249 | 50 | 66.8432 | 66.046 | 39.3849 | 39.092 | 96.2972 | OFF | 41.6 | 41.6 | 58.2122 | 60.268 | -2.7961 | 0.22096 | -50.2927 | -50.2927 | 0.99022
44811.8306 | 1:32 | 95 | 124.2967 | 110.1302 | 101.8695 | 99.7422 | 92.352 | 92.352 | 36.7263 | 38.7759 | 36.4572 | 39.1806 | 50 | 67.0421 | 66.2452 | 39.563 | 39.2079 | 96.3398 | OFF | 42.36 | 41.6 | 57.3822 | 60.2695 | -3.5841 | 0.40472 | -50.752 | -50.752 | 0.99025
44811.8307 | 1:32 | 95 | 123.7571 | 109.9097 | 101.8719 | 99.6116 | 92.7568 | 92.7568 | 37.0752 | 38.8055 | 36.789 | 39.3174 | 50 | 67.268 | 66.3598 | 39.6072 | 39.3172 | 96.3918 | OFF | 42.36 | 41.6 | 57.2516 | 60.2719 | -3.5545 | 0.51186 | -51.1568 | -51.1568 | 0.98892
44811.8308 | 1:32 | 95 | 123.251 | 109.6835 | 101.8535 | 99.542 | 93.0943 | 93.0943 | 37.3428 | 38.8522 | 37.0619 | 39.467 | 50 | 67.4517 | 66.536 | 39.6754 | 39.4373 | 96.4069 | OFF | 42.36 | 41.6 | 57.182 | 60.2535 | -3.5078 | 0.61479 | -51.4943 | -51.4943 | 0.98885
44811.8309 | 1:32 | 95 | 122.7349 | 109.4969 | 101.8134 | 99.4936 | 93.3799 | 93.3799 | 37.5692 | 38.8221 | 37.3074 | 39.5889 | 50 | 67.6395 | 66.7333 | 39.8329 | 39.5415 | 96.4962 | OFF | 42.36 | 41.6 | 57.1336 | 60.2134 | -3.5379 | 0.7668 | -51.7799 | -51.7799 | 0.98899
44811.831 | 1:33 | 95 | 122.2384 | 109.3214 | 101.7757 | 99.4349 | 93.5874 | 93.5874 | 37.7489 | 39.1802 | 37.5619 | 39.7314 | 50 | 67.853 | 66.707 | 39.8888 | 39.6302 | 96.5158 | OFF | 42.36 | 41.6 | 57.0749 | 60.1757 | -3.1798 | 0.5512 | -51.9874 | -51.9874 | 0.98612
44811.8311 | 1:33 | 95 | 121.7818 | 109.1525 | 101.7738 | 99.4373 | 93.7995 | 93.7995 | 37.9435 | 39.671 | 37.8021 | 39.8939 | 50 | 68.1792 | 67.2523 | 40.0885 | 39.7134 | 96.5852 | OFF | 43.11 | 42.36 | 56.3273 | 59.4138 | -3.439 | 0.22291 | -51.4395 | -51.4395 | 0.98882
44811.8313 | 1:33 | 95 | 121.4087 | 108.9576 | 101.7454 | 99.4578 | 93.9754 | 93.9754 | 38.1456 | 39.8312 | 38.0142 | 39.9802 | 50 | 67.9962 | 67.3063 | 40.1422 | 39.7811 | 96.5935 | OFF | 42.36 | 42.36 | 57.0978 | 59.3854 | -2.5288 | 0.14904 | -51.6154 | -51.6154 | 0.99166
44811.8314 | 1:33 | 95 | 121.0513 | 108.8125 | 101.692 | 99.4609 | 94.1072 | 94.1072 | 38.3069 | 39.352 | 38.1322 | 40.0586 | 50 | 68.2558 | 67.1508 | 40.2151 | 39.8506 | 96.6343 | OFF | 43.11 | 42.36 | 56.3509 | 59.332 | -3.758 | 0.70655 | -51.7472 | -51.7472 | 0.98668
44811.8315 | 1:33 | 95 | 120.6255 | 108.6246 | 101.6732 | 99.4899 | 94.2503 | 94.2503 | 38.4008 | 38.9501 | 38.2834 | 40.1326 | 50 | 68.3245 | 67.3245 | 40.3458 | 39.9672 | 96.6077 | OFF | 43.11 | 42.36 | 56.3799 | 59.3132 | -4.1599 | 1.1825 | -51.8903 | -51.8903 | 0.98796
44811.8316 | 1:33 | 95 | 122.0949 | 108.8872 | 112.9751 | 84.9041 | 95.2936 | 95.2936 | 37.4999 | 37.6813 | 37.3318 | 37.3032 | 50 | 63.3646 | 157.8996 | 40.3846 | 40.0513 | 96.8331 | OFF | 39.29 | 92.01 | 45.6141 | 20.9651 | -1.6087 | -0.37804 | -3.2836 | -3.2836 | 2.211
44811.8317 | 1:34 | 95 | 123.5625 | 110.9173 | 131.3542 | 66.0683 | 100.0685 | 100.0685 | 32.8541 | 32.5149 | 32.2026 | 34.0212 | 50 | 54.6316 | 183.6963 | 40.2084 | 39.887 | 101.5291 | ON | 31.92 | 102.5 | 34.1483 | 28.8542 | 0.5949 | 1.5063 | 2.4315 | 2.4315 | 2.8616 |  | OK | OK | OK | OK | 91.6425 | OK | OK | OK | OK | OK
44811.8318 | 1:34 | 95 | 121.9109 | 116.1271 | 132.7286 | 62.1065 | 103.7033 | 103.7033 | 30.897 | 29.281 | 30.3616 | 30.7884 | 50 | 53.1591 | 189.4295 | 39.5589 | 39.6411 | 104.665 | ON | 31.06 | 104.4 | 31.0465 | 28.3286 | -1.7791 | 1.5075 | 0.6967 | 0.6967 | 3.0081 |  | OK | Low Charge | OK | OK | 90.8509 | OK | OK | OK | OK | OK
44811.832 | 1:34 | 95 | 121.0786 | 118.064 | 132.0573 | 59.2364 | 104.1836 | 104.1836 | 29.9593 | 28.6386 | 29.0621 | 28.3149 | 50 | 52.8359 | 191.183 | 39.1178 | 39.3452 | 105.2143 | ON | 30.19 | 106.4 | 29.0464 | 25.6573 | -1.5514 | -0.32367 | 2.2164 | 2.2164 | 3.0485 |  | OK | OK | OK | OK | 90.8886 | OK | OK | OK | OK | OK
44811.8321 | 1:34 | 95 | 120.7784 | 119.0427 | 131.7509 | 57.7913 | 104.7383 | 104.7383 | 29.4666 | 27.9732 | 28.1224 | 27.3343 | 50 | 52.0305 | 192.7673 | 38.8242 | 39.1067 | 105.7535 | ON | 30.19 | 106.4 | 27.6013 | 25.3509 | -2.2168 | -0.63892 | 1.6617 | 1.6617 | 3.109 |  | OK | OK | OK | OK | 90.5884 | OK | OK | OK | OK | OK
44811.8322 | 1:34 | 95 | 120.615 | 119.5864 | 131.4693 | 57.7989 | 105.1859 | 105.1859 | 29.1824 | 27.5642 | 27.5219 | 26.8088 | 50 | 51.6595 | 193.9043 | 38.6394 | 38.9643 | 106.2162 | ON | 29.31 | 106.4 | 28.4889 | 25.0693 | -1.7458 | -0.75542 | 1.2141 | 1.2141 | 3.1435 |  | OK | OK | OK | OK | 91.305 | OK | OK | OK | OK | OK
44811.8323 | 1:34 | 95 | 120.7655 | 119.9779 | 131.3911 | 58.2473 | 105.4447 | 105.4447 | 28.9283 | 27.2164 | 27.0038 | 26.42 | 50 | 51.2793 | 193.8896 | 38.5164 | 38.726 | 106.4737 | ON | 29.31 | 106.4 | 28.9373 | 24.9911 | -2.0936 | -0.79637 | 0.9553 | 0.9553 | 3.1614 |  | OK | Low Charge | OK | OK | 91.4555 | OK | OK | OK | OK | OK
44811.8324 | 1:35 | 95 | 121.0677 | 120.3957 | 131.4589 | 59.4604 | 105.5156 | 105.5156 | 28.5912 | 26.8875 | 26.5396 | 26.1316 | 50 | 50.933 | 194.142 | 38.1917 | 38.67 | 106.6014 | ON | 28.42 | 106.4 | 31.0404 | 25.0589 | -1.5326 | -0.75583 | 0.8844 | 0.8844 | 3.182 |  | OK | Low Charge | OK | OK | 92.6477 | OK | OK | OK | OK | OK
44811.8325 | 1:35 | 95 | 121.4678 | 120.7473 | 131.5874 | 61.6979 | 105.5554 | 105.5554 | 28.2947 | 26.5332 | 26.151 | 26.177 | 50 | 50.3867 | 194.2529 | 38.0092 | 38.4448 | 106.6573 | ON | 28.42 | 106.4 | 33.2779 | 25.1874 | -1.8868 | -0.35621 | 0.8446 | 0.8446 | 3.2104 |  | OK | Low Charge | OK | OK | 93.0478 | OK | OK | OK | OK | OK
44811.8327 | 1:35 | 95 | 121.8615 | 121.0964 | 131.8307 | 63.989 | 105.5794 | 105.5794 | 27.9561 | 26.1943 | 25.8513 | 26.5484 | 50 | 50.174 | 194.1105 | 38.0884 | 38.3023 | 106.6937 | ON | 28.42 | 106.4 | 35.569 | 25.4307 | -2.2258 | 0.35419 | 0.8206 | 0.8206 | 3.2187 |  | OK | Low Charge | OK | OK | 93.4415 | OK | OK | OK | OK | OK
44811.8328 | 1:35 | 95 | 122.3833 | 121.4526 | 132.1713 | 65.1123 | 105.6418 | 105.6418 | 27.7188 | 26.0437 | 25.6867 | 26.7272 | 50 | 50.0178 | 194.2537 | 37.8969 | 38.2324 | 106.7727 | ON | 28.42 | 106.4 | 36.6923 | 25.7713 | -2.3763 | 0.68346 | 0.7582 | 0.7582 | 3.2287 |  | OK | Low Charge | OK | OK | 93.9633 | OK | OK | OK | OK | OK
44811.8329 | 1:35 | 95 | 122.8031 | 121.7643 | 132.5378 | 65.7419 | 105.6684 | 105.6684 | 27.4473 | 25.772 | 25.4281 | 26.6389 | 50 | 49.6813 | 194.328 | 37.8259 | 38.2119 | 106.8334 | ON | 27.51 | 106.4 | 38.2319 | 26.1378 | -1.738 | 0.86694 | 0.7316 | 0.7316 | 3.2467 |  | OK | Low Charge | OK | OK | 95.2931 | OK | OK | OK | OK | OK
44811.833 | 1:35 | 95 | 123.2867 | 122.0946 | 132.8944 | 66.4126 | 105.6777 | 105.6777 | 27.2327 | 25.5814 | 25.2377 | 26.4737 | 50 | 49.4611 | 194.3868 | 37.6694 | 38.0982 | 106.8182 | ON | 27.51 | 106.4 | 38.9026 | 26.4944 | -1.9286 | 0.89236 | 0.7223 | 0.7223 | 3.2588 |  | OK | Low Charge | OK | OK | 95.7767 | OK | OK | OK | OK | OK
44811.8331 | 1:36 | 95 | 123.6989 | 122.4075 | 133.2948 | 66.9994 | 105.7063 | 105.7063 | 26.9864 | 25.4061 | 25.0802 | 26.3417 | 50 | 49.2713 | 194.3103 | 37.5089 | 37.9329 | 106.8843 | ON | 27.51 | 106.4 | 39.4894 | 26.8948 | -2.1039 | 0.93553 | 0.6937 | 0.6937 | 3.2672 |  | OK | Low Charge | OK | OK | 96.1889 | OK | OK | OK | OK | OK
44811.8332 | 1:36 | 95 | 124.0991 | 122.7448 | 133.7456 | 67.4862 | 105.7602 | 105.7602 | 26.7344 | 25.2073 | 24.9036 | 26.1989 | 50 | 49.1342 | 194.6339 | 37.3647 | 37.8141 | 106.9539 | ON | 27.51 | 106.4 | 39.9762 | 27.3456 | -2.3027 | 0.99155 | 0.6398 | 0.6398 | 3.2793 |  | OK | Low Charge | OK | OK | 96.5891 | OK | OK | OK | OK | OK
44811.8333 | 1:36 | 95 | 124.5346 | 123.0277 | 134.114 | 67.7836 | 105.6429 | 105.6429 | 26.5302 | 25.0403 | 24.7668 | 26.0182 | 50 | 48.8165 | 194.0333 | 37.2534 | 37.867 | 106.8567 | ON | 26.6 | 106.4 | 41.1836 | 27.714 | -1.5597 | 0.97799 | 0.7571 | 0.7571 | 3.2863 |  | OK | Low Charge | OK | OK | 97.9346 | OK | OK | OK | OK | OK
44811.8335 | 1:36 | 95 | 124.8677 | 123.2916 | 134.5218 | 68.0642 | 105.6676 | 105.6676 | 26.3031 | 24.7862 | 24.5086 | 25.8584 | 50 | 48.6565 | 194.2811 | 37.2758 | 37.6761 | 106.8407 | ON | 26.6 | 106.4 | 41.4642 | 28.1218 | -1.8138 | 1.0722 | 0.7324 | 0.7324 | 3.2985 |  | OK | Low Charge | OK | OK | 98.2677 | OK | OK | OK | OK | OK
44811.8336 | 1:36 | 95 | 125.2176 | 123.5457 | 134.9037 | 68.2826 | 105.5918 | 105.5918 | 26.119 | 24.6133 | 24.3487 | 25.7731 | 50 | 48.3869 | 194.022 | 37.0689 | 37.5684 | 106.795 | ON | 26.6 | 106.4 | 41.6826 | 28.5037 | -1.9868 | 1.1599 | 0.8082 | 0.8082 | 3.3085 |  | OK | Low Charge | OK | OK | 98.6176 | OK | OK | OK | OK | OK
44811.8337 | 1:36 | 95 | 125.4931 | 123.7833 | 135.2835 | 68.4982 | 105.5247 | 105.5247 | 25.8803 | 24.4017 | 24.1662 | 25.6544 | 50 | 48.273 | 193.8716 | 37.0286 | 37.499 | 106.7417 | ON | 26.6 | 106.4 | 41.8982 | 28.8835 | -2.1983 | 1.2527 | 0.8753 | 0.8753 | 3.3121 |  | OK | Low Charge | OK | OK | 98.8931 | OK | OK | OK | OK | OK
44811.8338 | 1:37 | 95 | 125.8034 | 123.9862 | 135.6292 | 68.5183 | 105.469 | 105.469 | 25.6533 | 24.1987 | 23.9835 | 25.5745 | 50 | 48.054 | 193.6842 | 36.9205 | 37.3828 | 106.6692 | ON | 26.6 | 106.4 | 41.9183 | 29.2292 | -2.4013 | 1.3758 | 0.931 | 0.931 | 3.3207 |  | OK | Low Charge | OK | OK | 99.2034 | OK | OK | OK | OK | OK
44811.8339 | 1:37 | 95 | 126.2033 | 124.2349 | 135.9662 | 68.3812 | 105.43 | 105.43 | 25.4696 | 24.027 | 23.7822 | 25.4603 | 50 | 47.8278 | 193.4222 | 36.8827 | 37.1573 | 106.6493 | ON | 25.68 | 106.4 | 42.7012 | 29.5662 | -1.653 | 1.4333 | 0.97 | 0.97 | 3.3285 |  | OK | Low Charge | OK | OK | 100.5233 | OK | OK | OK | OK | OK
44811.834 | 1:37 | 95 | 126.4933 | 124.4508 | 136.3293 | 68.4814 | 105.4486 | 105.4486 | 25.247 | 23.9049 | 23.6581 | 25.3816 | 50 | 47.9618 | 193.4329 | 36.686 | 37.1796 | 106.6567 | ON | 25.68 | 106.4 | 42.8014 | 29.9293 | -1.7751 | 1.4767 | 0.9514 | 0.9514 | 3.3215 |  | OK | Low Charge | OK | OK | 100.8133 | OK | OK | OK | OK | OK
44811.8342 | 1:37 | 95 | 126.7183 | 124.6557 | 136.6144 | 68.2628 | 105.4208 | 105.4208 | 25.1023 | 23.7339 | 23.4168 | 25.29 | 50 | 47.4342 | 193.5427 | 36.6524 | 37.1035 | 106.6046 | ON | 25.68 | 106.4 | 42.5828 | 30.2144 | -1.9461 | 1.556 | 0.9792 | 0.9792 | 3.3515 |  | OK | Low Charge | OK | OK | 101.0383 | OK | OK | OK | OK | OK
44811.8343 | 1:37 | 95 | 126.8515 | 124.886 | 136.9559 | 68.3948 | 105.3628 | 105.3628 | 24.8274 | 23.3999 | 23.2435 | 25.2145 | 50 | 47.1287 | 193.3311 | 36.5538 | 37.0136 | 106.5756 | ON | 25.68 | 106.4 | 42.7148 | 30.5559 | -2.2801 | 1.8147 | 1.0372 | 1.0372 | 3.3646 |  | OK | OK | OK | OK | 101.1715 | OK | OK | OK | OK | OK
44811.8344 | 1:37 | 95 | 127.1592 | 125.0611 | 137.2266 | 68.4174 | 105.3474 | 105.3474 | 24.7074 | 23.3166 | 23.0624 | 25.1273 | 50 | 47.0243 | 193.0286 | 36.4605 | 36.9097 | 106.5509 | ON | 25.68 | 106.4 | 42.7374 | 30.8266 | -2.3634 | 1.8107 | 1.0526 | 1.0526 | 3.3654 |  | OK | OK | OK | OK | 101.4792 | OK | OK | OK | OK | OK
44811.8345 | 1:38 | 95 | 127.3357 | 125.1726 | 137.4556 | 68.5258 | 105.279 | 105.279 | 24.5032 | 23.1101 | 22.8573 | 25.051 | 50 | 46.922 | 193.2272 | 36.4181 | 36.8852 | 106.4668 | ON | 24.74 | 106.4 | 43.7858 | 31.0556 | -1.6299 | 1.9409 | 1.121 | 1.121 | 3.3742 |  | OK | OK | OK | OK | 102.5957 | OK | OK | OK | OK | OK
44811.8346 | 1:38 | 95 | 127.4045 | 125.3391 | 137.7019 | 68.5175 | 105.2102 | 105.2102 | 24.3855 | 23.0134 | 22.8117 | 25.0008 | 50 | 46.6553 | 192.6567 | 36.3268 | 36.8608 | 106.4385 | ON | 24.74 | 106.4 | 43.7775 | 31.3019 | -1.7266 | 1.9874 | 1.1898 | 1.1898 | 3.3796 |  | OK | OK | OK | OK | 102.6645 | OK | OK | OK | OK | OK
44811.8347 | 1:38 | 95 | 127.6537 | 125.4941 | 137.9299 | 68.2019 | 105.2645 | 105.2645 | 24.3135 | 23.0018 | 22.6526 | 24.9123 | 50 | 46.8126 | 192.9921 | 36.2205 | 36.7257 | 106.453 | ON | 24.74 | 106.4 | 43.4619 | 31.5299 | -1.7382 | 1.9105 | 1.1355 | 1.1355 | 3.3764 |  | OK | OK | OK | OK | 102.9137 | OK | OK | OK | OK | OK
44811.8349 | 1:38 | 95 | 127.7453 | 125.6745 | 138.1212 | 68.1082 | 105.2443 | 105.2443 | 23.9563 | 22.6514 | 22.892 | 24.8677 | 50 | 46.3708 | 193.0315 | 36.2208 | 36.6602 | 106.4322 | ON | 24.74 | 106.4 | 43.3683 | 31.7212 | -2.0886 | 2.2163 | 1.1557 | 1.1557 | 3.4015 |  | OK | OK | OK | OK | 103.0053 | OK | OK | OK | OK | OK
44811.835 | 1:38 | 95 | 127.909 | 125.7488 | 138.3471 | 68.37 | 105.2306 | 105.2306 | 23.9181 | 22.6202 | 23.2753 | 24.9404 | 50 | 46.3326 | 192.8562 | 35.9881 | 36.5139 | 106.4065 | ON | 24.74 | 106.4 | 43.63 | 31.9471 | -2.1197 | 2.3202 | 1.1694 | 1.1694 | 3.4007 |  | OK | OK | OK | OK | 103.169 | OK | OK | OK | OK | OK
44811.8351 | 1:38 | 95 | 128.0861 | 125.8935 | 138.5662 | 68.6623 | 105.201 | 105.201 | 23.6474 | 22.3803 | 22.8441 | 24.9577 | 50 | 46.2513 | 192.814 | 36.0183 | 36.422 | 106.3973 | ON | 24.74 | 106.4 | 43.9223 | 32.1662 | -2.3597 | 2.5774 | 1.199 | 1.199 | 3.4046 |  | OK | OK | OK | OK | 103.3461 | OK | OK | OK | OK | OK
44811.8352 | 1:39 | 95 | 128.5195 | 126.0536 | 138.8439 | 68.5471 | 105.7637 | 105.7637 | 24.234 | 23.5527 | 22.7294 | 25.158 | 50 | 46.5996 | 194.6113 | 36.0183 | 36.3158 | 106.8047 | ON | 24.74 | 106.4 | 43.8071 | 32.4439 | -1.1873 | 1.6053 | 0.6363 | 0.6363 | 3.4146 |  | OK | Low Charge | OK | OK | 103.7795 | OK | OK | OK | OK | OK
44811.8353 | 1:39 | 95 | 128.823 | 126.4992 | 139.3268 | 68.4504 | 106.4217 | 106.4217 | 24.3619 | 27.2355 | 22.6886 | 25.7442 | 50 | 46.635 | 196.4698 | 36.3726 | 36.361 | 107.3163 | ON | 24.74 | 108.3 | 43.7104 | 31.0268 | 2.4955 | -1.4913 | 1.8783 | 1.8783 | 3.4429 |  | OK | OK | OK | OK | 104.083 | OK | OK | OK | OK | OK
44811.8354 | 1:39 | 95 | 129.1196 | 126.8797 | 139.6666 | 68.632 | 106.6016 | 106.6016 | 24.3577 | 28.3746 | 22.8008 | 26.7692 | 50 | 46.6527 | 196.8293 | 36.4526 | 36.495 | 107.5198 | ON | 24.74 | 108.3 | 43.892 | 31.3666 | 3.6346 | -1.6053 | 1.6984 | 1.6984 | 3.4478 |  | OK | OK | OK | OK | 104.3796 | OK | OK | OK | OK | OK
44811.8355 | 1:39 | 95 | 129.4932 | 127.1557 | 140.0022 | 69.12 | 106.7582 | 106.7582 | 24.4482 | 28.2625 | 22.7761 | 27.5478 | 50 | 46.6534 | 196.7366 | 36.5357 | 36.5749 | 107.6925 | ON | 24.74 | 108.3 | 44.38 | 31.7022 | 3.5225 | -0.71472 | 1.5418 | 1.5418 | 3.4462 |  | OK | OK | OK | OK | 104.7532 | OK | OK | OK | OK | OK
44811.8357 | 1:39 | 95 | 129.7912 | 127.4581 | 140.4019 | 69.9329 | 106.9656 | 106.9656 | 27.3875 | 28.3786 | 22.8782 | 27.864 | 50 | 46.5988 | 197.3477 | 36.3969 | 36.5682 | 107.8926 | ON | 24.74 | 108.3 | 45.1929 | 32.1019 | 3.6386 | -0.51458 | 1.3344 | 1.3344 | 3.4592 |  | OK | OK | OK | OK | 105.0512 | OK | OK | OK | OK | OK
44811.8358 | 1:39 | 95 | 130.1267 | 127.7701 | 140.7182 | 70.8226 | 107.0465 | 107.0465 | 26.9125 | 28.087 | 22.8833 | 27.8659 | 50 | 46.6384 | 197.5588 | 36.3167 | 36.6003 | 108.0061 | ON | 24.74 | 108.3 | 46.0826 | 32.4182 | 3.347 | -0.22109 | 1.2535 | 1.2535 | 3.4605 |  | OK | OK | OK | OK | 105.3867 | OK | OK | OK | OK | OK
44811.8359 | 1:40 | 95 | 130.471 | 128.1113 | 141.0698 | 71.5883 | 107.0627 | 107.0627 | 24.7023 | 27.8196 | 22.8637 | 27.7097 | 50 | 46.6654 | 197.5083 | 36.2984 | 36.5518 | 108.0621 | ON | 24.74 | 108.3 | 46.8483 | 32.7698 | 3.0796 | -0.10995 | 1.2373 | 1.2373 | 3.4581 |  | OK | OK | OK | OK | 105.731 | OK | OK | OK | OK | OK
44811.836 | 1:40 | 95 | 130.8423 | 128.3325 | 141.4153 | 72.0126 | 107.0083 | 107.0083 | 24.3542 | 26.492 | 22.7745 | 27.4424 | 50 | 46.5078 | 197.2764 | 36.2439 | 36.4293 | 108.0382 | ON | 24.74 | 108.3 | 47.2726 | 33.1153 | 1.752 | 0.95039 | 1.2917 | 1.2917 | 3.4632 |  | OK | OK | OK | OK | 106.1023 | OK | OK | OK | OK | OK
44811.8361 | 1:40 | 95 | 131.0886 | 128.5977 | 141.7399 | 72.6 | 106.9426 | 106.9426 | 24.2611 | 23.2158 | 22.7575 | 27.1816 | 50 | 46.4438 | 197.3367 | 36.1022 | 36.3971 | 108.0349 | ON | 24.74 | 108.3 | 47.86 | 33.4399 | -1.5242 | 3.9659 | 1.3574 | 1.3574 | 3.4678 |  | OK | OK | OK | OK | 106.3486 | OK | OK | OK | OK | OK
44811.8362 | 1:40 | 95 | 131.4745 | 128.8354 | 142.0741 | 73.0018 | 106.9812 | 106.9812 | 24.1208 | 22.8003 | 22.6698 | 26.9115 | 50 | 46.5588 | 197.4339 | 35.937 | 36.3335 | 108.0878 | ON | 24.74 | 108.3 | 48.2618 | 33.7741 | -1.9397 | 4.1112 | 1.3188 | 1.3188 | 3.4629 |  | OK | OK | OK | OK | 106.7345 | OK | OK | OK | OK | OK
44811.8364 | 1:40 | 95 | 131.7122 | 129.073 | 142.4387 | 73.1491 | 106.957 | 106.957 | 23.896 | 22.652 | 22.6336 | 26.6161 | 50 | 46.5383 | 197.3263 | 35.7471 | 36.2948 | 108.128 | ON | 24.74 | 108.3 | 48.4091 | 34.1387 | -2.088 | 3.9641 | 1.343 | 1.343 | 3.4623 |  | OK | OK | OK | OK | 106.9722 | OK | OK | OK | OK | OK
44811.8365 | 1:40 | 95 | 131.9335 | 129.3797 | 142.7487 | 73.2567 | 106.9886 | 106.9886 | 23.7942 | 22.5011 | 22.4804 | 26.3559 | 50 | 46.1692 | 197.2533 | 35.7703 | 36.1841 | 108.1602 | ON | 24.74 | 108.3 | 48.5168 | 34.4487 | -2.2389 | 3.8548 | 1.3114 | 1.3114 | 3.4821 |  | OK | OK | OK | OK | 107.1935 | OK | OK | OK | OK | OK
44811.8366 | 1:41 | 95 | 132.267 | 129.6624 | 143.0885 | 73.2405 | 107.0871 | 107.0871 | 23.625 | 22.3498 | 22.3626 | 26.0975 | 50 | 45.9119 | 197.4922 | 35.702 | 36.0746 | 108.2489 | ON | 23.8 | 108.3 | 49.4405 | 34.7885 | -1.4502 | 3.7478 | 1.2129 | 1.2129 | 3.5008 |  | OK | OK | OK | OK | 108.467 | OK | OK | OK | OK | OK
44811.8367 | 1:41 | 95 | 132.5863 | 129.8916 | 143.4067 | 73.0718 | 107.1367 | 107.1367 | 23.4531 | 22.1772 | 22.2226 | 25.8269 | 50 | 45.8062 | 197.6149 | 35.7042 | 36.1158 | 108.3141 | ON | 23.8 | 108.3 | 49.2718 | 35.1067 | -1.6228 | 3.6497 | 1.1633 | 1.1633 | 3.509 |  | OK | OK | OK | OK | 108.7863 | OK | OK | OK | OK | OK
44811.8368 | 1:41 | 95 | 132.7869 | 130.085 | 143.6402 | 72.8768 | 107.2119 | 107.2119 | 23.3355 | 22.0871 | 22.1527 | 25.5874 | 50 | 45.8004 | 197.7087 | 35.5961 | 35.9637 | 108.3969 | ON | 23.8 | 108.3 | 49.0768 | 35.3402 | -1.7129 | 3.5003 | 1.0881 | 1.0881 | 3.5109 |  | OK | OK | OK | OK | 108.9869 | OK | OK | OK | OK | OK
44811.8369 | 1:41 | 95 | 132.9624 | 130.2995 | 143.8994 | 72.7804 | 107.4021 | 107.4021 | 23.097 | 21.8498 | 22.0313 | 25.3752 | 50 | 45.9144 | 198.5017 | 35.3573 | 35.8515 | 108.5503 | ON | 23.8 | 108.3 | 48.9804 | 35.5994 | -1.9502 | 3.5253 | 0.8979 | 0.8979 | 3.5173 |  | OK | Low Charge | OK | OK | 109.1624 | OK | OK | OK | OK | OK
44811.8371 | 1:41 | 95 | 133.1675 | 130.5385 | 144.1864 | 72.8238 | 107.4746 | 107.4746 | 23.0348 | 21.812 | 21.8706 | 25.1613 | 50 | 45.4819 | 198.5187 | 35.5079 | 35.8268 | 108.6249 | ON | 23.8 | 108.3 | 49.0238 | 35.8864 | -1.988 | 3.3492 | 0.8254 | 0.8254 | 3.5429 |  | OK | Low Charge | OK | OK | 109.3675 | OK | OK | OK | OK | OK
44811.8372 | 1:41 | 95 | 133.3637 | 130.7255 | 144.4212 | 73.0672 | 107.4306 | 107.4306 | 22.8296 | 21.6523 | 21.7415 | 24.9241 | 50 | 45.3683 | 198.237 | 35.2188 | 35.6486 | 108.6036 | ON | 23.8 | 108.3 | 49.2672 | 36.1212 | -2.1477 | 3.2718 | 0.8694 | 0.8694 | 3.5449 |  | OK | Low Charge | OK | OK | 109.5637 | OK | OK | OK | OK | OK
44811.8373 | 1:42 | 95 | 133.5255 | 130.9647 | 144.6837 | 73.3698 | 107.4602 | 107.4602 | 22.7253 | 21.5755 | 21.5936 | 24.7231 | 50 | 45.2475 | 198.5318 | 35.4318 | 35.5333 | 108.6506 | ON | 23.8 | 108.3 | 49.5698 | 36.3837 | -2.2245 | 3.1476 | 0.8398 | 0.8398 | 3.557 |  | OK | Low Charge | OK | OK | 109.7255 | OK | OK | OK | OK | OK
44811.8374 | 1:42 | 95 | 133.798 | 131.0885 | 144.9128 | 73.5244 | 107.4769 | 107.4769 | 22.6165 | 21.4272 | 21.5823 | 24.5937 | 50 | 45.1305 | 198.4698 | 35.2231 | 35.5026 | 108.6609 | ON | 23.8 | 108.3 | 49.7244 | 36.6128 | -2.3728 | 3.1664 | 0.8231 | 0.8231 | 3.5629 |  | OK | Low Charge | OK | OK | 109.998 | OK | OK | OK | OK | OK
44811.8375 | 1:42 | 95 | 133.9129 | 131.3128 | 145.1386 | 73.7507 | 107.5364 | 107.5364 | 22.4137 | 21.2618 | 21.4808 | 24.4313 | 50 | 44.9696 | 198.5645 | 35.0817 | 35.4947 | 108.6815 | ON | 22.84 | 108.3 | 50.9107 | 36.8386 | -1.5782 | 3.1695 | 0.7636 | 0.7636 | 3.5741 |  | OK | Low Charge | OK | OK | 111.0729 | OK | OK | OK | OK | OK
44811.8376 | 1:42 | 95 | 134.1786 | 131.4321 | 145.332 | 73.9208 | 107.5482 | 107.5482 | 22.3173 | 21.1892 | 21.3498 | 24.3105 | 50 | 45.0618 | 198.7882 | 35.0614 | 35.3399 | 108.7148 | ON | 23.8 | 108.3 | 50.1208 | 37.032 | -2.6108 | 3.1213 | 0.7518 | 0.7518 | 3.5723 |  | OK | Low Charge | OK | OK | 110.3786 | OK | OK | OK | OK | OK
44811.8377 | 1:42 | 95 | 134.3991 | 131.5696 | 145.5611 | 73.9502 | 107.5898 | 107.5898 | 22.2641 | 21.2042 | 21.2005 | 24.1923 | 50 | 45.1855 | 198.7073 | 34.9584 | 35.2977 | 108.7362 | ON | 23.8 | 108.3 | 50.1502 | 37.2611 | -2.5958 | 2.9881 | 0.7102 | 0.7102 | 3.5636 |  | OK | Low Charge | OK | OK | 110.5991 | OK | OK | OK | OK | OK
44811.8379 | 1:42 | 95 | 134.6435 | 131.7431 | 145.7253 | 74.0586 | 107.5587 | 107.5587 | 22.0882 | 20.9539 | 21.0243 | 24.0861 | 50 | 44.6651 | 198.5919 | 34.9118 | 35.1672 | 108.7117 | ON | 22.84 | 108.3 | 51.2186 | 37.4253 | -1.8861 | 3.1322 | 0.7413 | 0.7413 | 3.5929 |  | OK | Low Charge | OK | OK | 111.8035 | OK | OK | OK | OK | OK
44811.838 | 1:43 | 95 | 134.9656 | 131.8439 | 145.9198 | 74.1698 | 107.7078 | 107.7078 | 22.0736 | 20.95 | 20.9116 | 23.9611 | 50 | 44.6975 | 200.4604 | 34.8731 | 35.1869 | 108.7805 | ON | 22.84 | 110.2 | 51.3299 | 35.7198 | -1.8901 | 3.0111 | 2.4922 | 2.4922 | 3.6224 |  | OK | OK | OK | OK | 112.1256 | OK | OK | OK | OK | OK
44811.8381 | 1:43 | 95 | 135.6528 | 132.4633 | 146.5872 | 73.9451 | 109.8158 | 109.8158 | 21.717 | 20.0684 | 20.7676 | 23.9066 | 50 | 43.0163 | 207.1477 | 34.7826 | 35.1246 | 110.3057 | ON | 21.87 | 112 | 52.0751 | 34.5872 | -1.8016 | 3.8382 | 2.1842 | 2.1842 | 3.8438 |  | OK | OK | OK | OK | 113.7828 | OK | OK | OK | OK | OK
44811.8382 | 1:43 | 95 | 136.0591 | 133.1213 | 147.0562 | 72.3507 | 110.2533 | 110.2533 | 21.111 | 18.7498 | 21.7236 | 24.2361 | 50 | 41.498 | 207.2873 | 34.57 | 35.0526 | 110.7122 | ON | 19.89 | 112 | 52.4607 | 35.0562 | -1.1402 | 5.4863 | 1.7467 | 1.7467 | 3.9501 |  | OK | OK | OK | OK | 116.1691 | OK | OK | OK | OK | OK
44811.8383 | 1:43 | 95 | 136.5173 | 133.2995 | 147.2676 | 68.7711 | 110.2661 | 110.2661 | 20.7011 | 18.2328 | 23.0118 | 25.0957 | 50 | 41.1967 | 206.9834 | 34.4446 | 35.0518 | 110.7077 | ON | 19.89 | 112 | 48.8811 | 35.2676 | -1.6572 | 6.863 | 1.7339 | 1.7339 | 3.9659 |  | OK | OK | OK | OK | 116.6273 | OK | OK | OK | OK | OK
44811.8384 | 1:43 | 95 | 136.5789 | 133.4392 | 147.3372 | 62.4656 | 110.2277 | 110.2277 | 20.2869 | 17.7056 | 24.5192 | 26.0961 | 50 | 40.6454 | 206.8827 | 34.2712 | 35.1786 | 110.6907 | ON | 18.88 | 112 | 43.5856 | 35.3372 | -1.1744 | 8.3905 | 1.7723 | 1.7723 | 4.0036 |  | OK | OK | OK | OK | 117.6989 | OK | OK | OK | OK | OK
44811.8386 | 1:43 | 95 | 136.3698 | 133.3903 | 147.1087 | 53.6077 | 110.219 | 110.219 | 19.9418 | 17.2844 | 25.912 | 27.0667 | 50 | 40.2687 | 206.7318 | 34.2591 | 35.3388 | 110.7026 | ON | 18.88 | 112 | 34.7277 | 35.1087 | -1.5956 | 9.7823 | 1.781 | 1.781 | 4.0283 |  | OK | OK | OK | OK | 117.4898 | OK | OK | OK | OK | OK
44811.8387 | 1:44 | 95 | 135.8353 | 133.0336 | 146.7413 | 49.7345 | 110.1038 | 110.1038 | 19.6372 | 16.9662 | 27.1021 | 27.9097 | 50 | 39.8862 | 206.5954 | 34.2783 | 35.3453 | 110.6306 | ON | 17.86 | 112 | 31.8745 | 34.7413 | -0.89381 | 10.9435 | 1.8962 | 1.8962 | 4.0541 |  | OK | OK | OK | OK | 117.9753 | OK | OK | OK | OK | OK
44811.8388 | 1:44 | 95 | 135.2523 | 132.6156 | 146.1628 | 47.8118 | 110.0056 | 110.0056 | 19.2948 | 16.6183 | 28.0976 | 28.6605 | 50 | 39.7499 | 205.9977 | 34.0232 | 35.3854 | 110.5475 | ON | 17.86 | 112 | 29.9518 | 34.1628 | -1.2417 | 12.0422 | 1.9944 | 1.9944 | 4.0532 |  | OK | OK | OK | OK | 117.3923 | OK | OK | OK | OK | OK
44811.8389 | 1:44 | 95 | 134.6221 | 132.0791 | 145.5711 | 46.5249 | 109.848 | 109.848 | 19.0374 | 16.3652 | 28.8213 | 29.2665 | 50 | 39.3936 | 205.5928 | 33.9808 | 35.3931 | 110.449 | ON | 17.86 | 112 | 28.6649 | 33.5711 | -1.4948 | 12.9013 | 2.152 | 2.152 | 4.0724 |  | OK | OK | OK | OK | 116.7621 | OK | OK | OK | OK | OK
44811.839 | 1:44 | 95 | 134.0061 | 131.5507 | 144.9139 | 45.0665 | 109.7593 | 109.7593 | 18.7665 | 16.0961 | 29.4154 | 29.7699 | 50 | 39.1733 | 205.4486 | 33.7611 | 35.4029 | 110.3011 | ON | 17.86 | 112 | 27.2065 | 32.9139 | -1.7639 | 13.6738 | 2.2407 | 2.2407 | 4.0864 |  | OK | OK | OK | OK | 116.1461 | OK | OK | OK | OK | OK
44811.8391 | 1:44 | 95 | 133.4339 | 131.0763 | 144.3659 | 43.9792 | 109.5331 | 109.5331 | 18.4956 | 15.8149 | 29.9009 | 30.1864 | 50 | 38.8305 | 204.8365 | 33.7554 | 35.382 | 110.1157 | ON | 16.82 | 110.2 | 27.1592 | 34.1659 | -1.0051 | 14.3715 | 0.6669 | 0.6669 | 4.1011 |  | OK | Low Charge | OK | OK | 116.6139 | OK | OK | OK | OK | OK
44811.8393 | 1:44 | 95 | 132.8547 | 130.5707 | 143.7486 | 43.2624 | 109.3988 | 109.3988 | 18.2674 | 15.5901 | 30.2149 | 30.5014 | 50 | 38.6743 | 204.6096 | 33.7315 | 35.3827 | 109.9722 | ON | 16.82 | 110.2 | 26.4424 | 33.5486 | -1.2299 | 14.9113 | 0.8012 | 0.8012 | 4.1089 |  | OK | Low Charge | OK | OK | 116.0347 | OK | OK | OK | OK | OK
44811.8394 | 1:45 | 95 | 132.3491 | 130.2195 | 143.2072 | 42.5046 | 109.2428 | 109.2428 | 18.0121 | 15.4028 | 30.4763 | 30.7687 | 50 | 38.4885 | 204.1309 | 33.4856 | 35.3388 | 109.8344 | ON | 16.82 | 110.2 | 25.6846 | 33.0072 | -1.4172 | 15.3659 | 0.9572 | 0.9572 | 4.1143 |  | OK | Low Charge | OK | OK | 115.5291 | OK | OK | OK | OK | OK
44811.8395 | 1:45 | 95 | 131.8463 | 129.8347 | 142.7211 | 41.7635 | 108.9519 | 108.9519 | 17.7541 | 15.1193 | 30.6672 | 30.9678 | 50 | 38.2385 | 203.2532 | 33.5156 | 35.3894 | 109.5738 | ON | 16.82 | 110.2 | 24.9435 | 32.5211 | -1.7007 | 15.8485 | 1.2481 | 1.2481 | 4.1171 |  | OK | OK | OK | OK | 115.0263 | OK | OK | OK | OK | OK
44811.8396 | 1:45 | 95 | 131.4319 | 129.3775 | 142.1835 | 41.1719 | 108.7037 | 108.7037 | 17.5395 | 14.8971 | 30.8152 | 31.1243 | 50 | 38.008 | 202.6787 | 33.3711 | 35.3634 | 109.3592 | ON | 16.82 | 110.2 | 24.3519 | 31.9835 | -1.9229 | 16.2273 | 1.4963 | 1.4963 | 4.1242 |  | OK | OK | OK | OK | 114.6119 | OK | OK | OK | OK | OK
44811.8397 | 1:45 | 95 | 131.0937 | 128.9939 | 141.7637 | 40.8584 | 108.6343 | 108.6343 | 17.2754 | 14.6848 | 30.9301 | 31.2298 | 50 | 37.8786 | 202.5393 | 33.3245 | 35.3531 | 109.2492 | ON | 15.76 | 110.2 | 25.0983 | 31.5637 | -1.0752 | 16.545 | 1.5657 | 1.5657 | 4.1317 |  | OK | OK | OK | OK | 115.3337 | OK | OK | OK | OK | OK
44811.8398 | 1:45 | 95 | 130.7312 | 128.7125 | 141.3653 | 40.4689 | 108.4109 | 108.4109 | 17.0853 | 14.5121 | 31.0337 | 31.3369 | 50 | 37.6104 | 201.7422 | 33.2281 | 35.3353 | 109.072 | ON | 15.76 | 110.2 | 24.7089 | 31.1653 | -1.2479 | 16.8248 | 1.7891 | 1.7891 | 4.1376 |  | OK | OK | OK | OK | 114.9712 | OK | OK | OK | OK | OK
44811.8399 | 1:45 | 95 | 130.4673 | 128.3633 | 140.9914 | 40.027 | 108.286 | 108.286 | 16.8138 | 14.2562 | 31.0796 | 31.4362 | 50 | 37.4589 | 201.2919 | 33.2109 | 35.3048 | 108.9458 | ON | 15.76 | 110.2 | 24.267 | 30.7914 | -1.5038 | 17.18 | 1.914 | 1.914 | 4.141 |  | OK | OK | OK | OK | 114.7073 | OK | OK | OK | OK | OK
44811.8401 | 1:46 | 95 | 130.1938 | 128.0736 | 140.7153 | 39.7732 | 108.2619 | 108.2619 | 16.6378 | 14.0761 | 31.1579 | 31.5061 | 50 | 37.31 | 201.5456 | 33.021 | 35.2116 | 108.8803 | ON | 15.76 | 110.2 | 24.0132 | 30.5153 | -1.6839 | 17.43 | 1.9381 | 1.9381 | 4.1578 |  | OK | OK | OK | OK | 114.4338 | OK | OK | OK | OK | OK
44811.8402 | 1:46 | 95 | 130.7289 | 128.4332 | 140.8279 | 39.5466 | 109.9845 | 109.9845 | 14.443 | 13.6565 | 31.1901 | 31.5279 | 50 | 27.9165 | 210.7269 | 32.956 | 35.2379 | 110.5715 | ON | 4.29 | 113.8 | 35.2566 | 27.0279 | 9.3665 | 17.8713 | 3.8155 | 3.8155 | 5.2897 |  | OK | OK | OK | OK | 126.4389 | OK | OK | OK | OK | OK
44811.8403 | 1:46 | 95 | 130.1692 | 128.2734 | 138.9957 | 43.354 | 108.373 | 108.373 | 15.4072 | 15.7016 | 31.2175 | 31.522 | 50 | 19.9013 | 202.3282 | 32.9087 | 35.2192 | 108.7009 | ON | -6.5 | 110.2 | 49.854 | 28.7957 | 22.2016 | 15.8204 | 1.827 | 1.827 | 6.2723 |  | OK | OK | OK | OK | 136.6692 | OK | OK | OK | OK | OK
44811.8404 | 1:46 | 95 | 129.9059 | 127.4331 | 137.2899 | 47.5829 | 105.6302 | 105.6302 | 17.9284 | 18.0402 | 31.2464 | 31.5588 | 50 | 16.7448 | 197.413 | 33.6027 | 35.4224 | 107.037 | ON | -11.06 | 108.3 | 58.6429 | 28.9899 | 29.1002 | 13.5187 | 2.6698 | 2.6698 | 6.7456 |  | OK | OK | OK | OK | 140.9659 | OK | OK | OK | OK | OK
44811.8405 | 1:46 | 95 | 130.0938 | 126.8992 | 136.3357 | 49.8143 | 103.9636 | 103.9636 | 20.655 | 20.2239 | 31.2865 | 31.6194 | 50 | 15.4714 | 194.1557 | 34.2111 | 35.5403 | 106.1343 | ON | -12.65 | 106.4 | 62.4643 | 29.9357 | 32.8739 | 11.3955 | 2.4364 | 2.4364 | 6.9223 |  | OK | OK | OK | OK | 142.7438 | OK | OK | OK | OK | OK
44811.8406 | 1:46 | 95 | 130.5413 | 126.6126 | 135.7878 | 51.1054 | 103.667 | 103.667 | 23.0758 | 22.0535 | 31.3303 | 31.6904 | 50 | 14.8807 | 192.5423 | 34.4705 | 35.6288 | 105.4566 | ON | -14.28 | 106.4 | 65.3854 | 29.3878 | 36.3335 | 9.637 | 2.733 | 2.733 | 7.006 |  | OK | OK | OK | OK | 144.8213 | OK | OK | OK | OK | OK
44811.8408 | 1:47 | 95 | 131.1548 | 126.448 | 135.499 | 53.6187 | 103.0495 | 103.0495 | 25.1576 | 23.6374 | 31.3885 | 31.7961 | 50 | 14.4741 | 191.5863 | 34.8022 | 35.7642 | 104.9765 | ON | -14.28 | 106.4 | 67.8987 | 29.099 | 37.9174 | 8.1587 | 3.3505 | 3.3505 | 7.0709 |  | OK | OK | OK | OK | 145.4348 | OK | OK | OK | OK | OK
44811.8409 | 1:47 | 95 | 131.7214 | 126.4693 | 135.4906 | 56.3287 | 102.395 | 102.395 | 26.8285 | 24.9492 | 31.4148 | 31.9246 | 50 | 13.8076 | 190.512 | 35.0383 | 35.9436 | 104.6055 | ON | -15.96 | 106.4 | 72.2887 | 29.0906 | 40.9092 | 6.9753 | 4.005 | 4.005 | 7.1985 |  | OK | OK | OK | OK | 147.6814 | OK | OK | OK | OK | OK
44811.841 | 1:47 | 95 | 132.3163 | 126.4838 | 135.5985 | 57.3532 | 102.0818 | 102.0818 | 28.1234 | 26.0197 | 31.4533 | 32.0247 | 50 | 13.314 | 189.7854 | 35.4009 | 36.0653 | 104.3616 | ON | -15.96 | 104.4 | 73.3132 | 31.1985 | 41.9797 | 6.005 | 2.3182 | 2.3182 | 7.2994 |  | OK | OK | OK | OK | 148.2763 | OK | OK | OK | OK | OK
44811.8411 | 1:47 | 95 | 132.979 | 126.6787 | 135.7811 | 57.8764 | 101.994 | 101.994 | 29.1055 | 26.8985 | 31.4929 | 32.1671 | 50 | 12.9902 | 189.4657 | 35.6081 | 36.2586 | 104.1919 | ON | -17.69 | 104.4 | 75.5664 | 31.3811 | 44.5885 | 5.2686 | 2.406 | 2.406 | 7.3732 |  | OK | OK | OK | OK | 150.669 | OK | OK | OK | OK | OK
44811.8412 | 1:47 | 95 | 133.7479 | 127.023 | 136.0212 | 58.0638 | 101.9819 | 101.9819 | 29.8265 | 27.5825 | 31.5452 | 32.2766 | 50 | 12.6872 | 189.2877 | 35.6406 | 36.2595 | 104.1976 | ON | -17.69 | 104.4 | 75.7538 | 31.6212 | 45.2725 | 4.6941 | 2.4181 | 2.4181 | 7.4483 |  | OK | OK | OK | OK | 151.4379 | OK | OK | OK | OK | OK
44811.8413 | 1:47 | 95 | 134.3145 | 127.2943 | 136.3108 | 58.0246 | 101.9367 | 101.9367 | 30.3286 | 28.1328 | 31.5631 | 32.3918 | 50 | 12.2667 | 189.1408 | 35.8145 | 36.3575 | 104.0115 | ON | -17.69 | 104.4 | 75.7146 | 31.9108 | 45.8228 | 4.259 | 2.4633 | 2.4633 | 7.559 |  | OK | OK | OK | OK | 152.0045 | OK | OK | OK | OK | OK
44811.8415 | 1:48 | 95 | 134.8717 | 127.5813 | 136.618 | 57.7518 | 101.5214 | 101.5214 | 30.6944 | 28.5398 | 31.5947 | 32.5369 | 50 | 12.1649 | 188.4975 | 35.9312 | 36.4723 | 103.8674 | ON | -17.69 | 104.4 | 75.4418 | 32.218 | 46.2298 | 3.9972 | 2.8786 | 2.8786 | 7.5637 |  | OK | OK | OK | OK | 152.5617 | OK | OK | OK | OK | OK
44811.8416 | 1:48 | 95 | 135.388 | 127.8362 | 136.9393 | 57.2912 | 101.5834 | 101.5834 | 30.9274 | 28.9038 | 31.6284 | 32.6799 | 50 | 11.914 | 188.5037 | 36.0042 | 36.5189 | 103.8024 | ON | -19.46 | 104.4 | 76.7512 | 32.5393 | 48.3638 | 3.7761 | 2.8166 | 2.8166 | 7.6352 |  | OK | OK | OK | OK | 154.848 | OK | OK | OK | OK | OK
44811.8417 | 1:48 | 95 | 135.8426 | 128.237 | 137.3969 | 56.5566 | 101.4876 | 101.4876 | 31.096 | 29.2138 | 31.6179 | 32.8303 | 50 | 11.6346 | 188.341 | 36.2234 | 36.4774 | 103.8099 | ON | -19.46 | 104.4 | 76.0166 | 32.9969 | 48.6738 | 3.6165 | 2.9124 | 2.9124 | 7.71 |  | OK | OK | OK | OK | 155.3026 | OK | OK | OK | OK | OK
44811.8418 | 1:48 | 95 | 136.3914 | 128.5653 | 137.819 | 55.5935 | 101.5248 | 101.5248 | 31.2339 | 29.436 | 31.6433 | 32.949 | 50 | 11.5705 | 188.1378 | 36.1722 | 36.6521 | 103.7501 | ON | -19.46 | 104.4 | 75.0535 | 33.419 | 48.896 | 3.513 | 2.8752 | 2.8752 | 7.7211 |  | OK | OK | OK | OK | 155.8514 | OK | OK | OK | OK | OK
44811.8419 | 1:48 | 95 | 140.7078 | 127.4535 | 136.123 | 59.3156 | 93.8307 | 93.8307 | 25.9209 | 30.3446 | 27.7631 | 33.412 | 50 | 52.1859 | 129.4699 | 36.223 | 36.7514 | 100.1722 | OFF | 30.19 | 77.84 | 29.1256 | 58.283 | 0.15457 | 3.0675 | -15.9907 | -15.9907 | 2.1555
44811.842 | 1:48 | 95 | 140.8165 | 124.6654 | 128.3596 | 72.0172 | 90.0877 | 90.0877 | 31.2629 | 31.2731 | 30.2883 | 33.5338 | 50 | 58.409 | 113.4522 | 36.2442 | 36.7808 | 99.2237 | OFF | 35.28 | 69.9 | 36.7372 | 58.4596 | -4.0069 | 2.2607 | -20.1877 | -20.1877 | 1.7529
44811.8421 | 1:49 | 95 | 139.8461 | 122.9831 | 119.7396 | 83.1713 | 86.7964 | 86.7964 | 31.8325 | 32.9637 | 31.1368 | 33.8837 | 50 | 59.6924 | 101.0469 | 36.3496 | 36.818 | 98.432 | OFF | 36.1 | 64.21 | 47.0713 | 55.5296 | -3.1363 | 0.92005 | -22.5864 | -22.5864 | 1.5559
44811.8423 | 1:49 | 95 | 138.4624 | 121.2497 | 113.601 | 90.3028 | 84.9316 | 84.9316 | 31.8506 | 33.9754 | 31.5097 | 34.31 | 50 | 60.5231 | 87.8485 | 36.5555 | 36.8429 | 97.906 | OFF | 36.91 | 54.95 | 53.3928 | 58.651 | -2.9346 | 0.33467 | -29.9816 | -29.9816 | 1.3633
44811.8424 | 1:49 | 95 | 137.0398 | 119.662 | 109.3936 | 94.6472 | 83.3153 | 83.3153 | 31.8697 | 34.598 | 31.6411 | 34.7326 | 50 | 61.1908 | 80.0091 | 36.5671 | 36.8935 | 97.5312 | OFF | 37.71 | 51.63 | 56.9372 | 57.7636 | -3.112 | 0.13455 | -31.6853 | -31.6853 | 1.248
44811.8425 | 1:49 | 95 | 135.7227 | 118.3054 | 106.7611 | 96.5498 | 82.9434 | 82.9434 | 31.8671 | 34.9817 | 31.6851 | 34.965 | 50 | 61.5714 | 72.7373 | 36.6812 | 37.0548 | 97.2875 | OFF | 37.71 | 44.59 | 58.8398 | 62.1711 | -2.7283 | -0.01675 | -38.3534 | -38.3534 | 1.1464
44811.8426 | 1:49 | 95 | 134.6143 | 117.0577 | 105.3625 | 96.6734 | 83.6988 | 83.6988 | 31.887 | 35.0822 | 31.7052 | 35.0219 | 50 | 61.693 | 67.3876 | 36.8126 | 37.1732 | 97.1316 | OFF | 37.71 | 42.36 | 58.9634 | 63.0025 | -2.6278 | -0.06026 | -41.3388 | -41.3388 | 1.0745
44811.8427 | 1:49 | 95 | 133.4212 | 116.0196 | 104.6453 | 96.2152 | 84.9039 | 84.9039 | 31.9066 | 35.1568 | 31.7395 | 35.0422 | 50 | 61.8359 | 64.6763 | 36.9335 | 37.2603 | 97.034 | OFF | 37.71 | 40.07 | 58.5052 | 64.5753 | -2.5532 | -0.11452 | -44.8339 | -44.8339 | 1.0371
44811.8428 | 1:50 | 95 | 132.3458 | 115.0831 | 104.1793 | 95.5871 | 86.1332 | 86.1332 | 31.9464 | 35.2899 | 31.769 | 35.1013 | 50 | 62.0147 | 62.8047 | 37.0174 | 37.2776 | 96.9668 | OFF | 38.5 | 38.5 | 57.0871 | 65.6793 | -3.2101 | -0.18863 | -47.6332 | -47.6332 | 1.0103
44811.843 | 1:50 | 95 | 131.3264 | 114.2962 | 103.9243 | 95.0347 | 87.4928 | 87.4928 | 31.9753 | 35.3418 | 31.7933 | 35.1654 | 50 | 62.3078 | 61.93 | 37.1899 | 37.3368 | 96.9554 | OFF | 38.5 | 37.71 | 56.5347 | 66.2143 | -3.1582 | -0.17641 | -49.7828 | -49.7828 | 0.99509
44811.8431 | 1:50 | 95 | 130.3858 | 113.6375 | 103.7768 | 94.5776 | 88.8148 | 88.8148 | 32.0225 | 35.4728 | 31.8187 | 35.2549 | 50 | 62.1654 | 61.8712 | 37.1434 | 37.471 | 96.919 | OFF | 38.5 | 37.71 | 56.0776 | 66.0668 | -3.0272 | -0.21782 | -51.1048 | -51.1048 | 0.99617
44811.8432 | 1:50 | 95 | 129.4694 | 113.0787 | 103.6745 | 94.32 | 89.9303 | 89.9303 | 32.0775 | 35.6481 | 31.8417 | 35.4282 | 50 | 62.85 | 62.1319 | 37.2073 | 37.4447 | 96.9577 | OFF | 38.5 | 38.5 | 55.82 | 65.1745 | -2.8519 | -0.21989 | -51.4303 | -51.4303 | 0.99074
44811.8433 | 1:50 | 95 | 128.6292 | 112.5611 | 103.5918 | 94.1571 | 90.857 | 90.857 | 32.1459 | 35.6042 | 31.8629 | 35.7058 | 50 | 63.3311 | 62.5277 | 37.4145 | 37.5556 | 97.0047 | OFF | 39.29 | 38.5 | 54.8671 | 65.0918 | -3.6858 | 0.10161 | -52.357 | -52.357 | 0.9897
44811.8434 | 1:50 | 95 | 127.7866 | 112.0887 | 103.5082 | 93.9605 | 91.6703 | 91.6703 | 32.1997 | 34.6175 | 32.0067 | 36.1478 | 50 | 63.7864 | 62.9886 | 37.5747 | 37.6949 | 97.044 | OFF | 39.29 | 38.5 | 54.6705 | 65.0082 | -4.6725 | 1.5304 | -53.1703 | -53.1703 | 0.98984
44811.8435 | 1:51 | 95 | 126.9697 | 111.7424 | 103.4443 | 93.9237 | 92.3205 | 92.3205 | 32.2828 | 34.1224 | 32.6354 | 36.6326 | 50 | 64.1968 | 63.3468 | 37.6075 | 37.7809 | 97.1046 | OFF | 40.07 | 39.29 | 53.8537 | 64.1543 | -5.9476 | 2.5102 | -53.0305 | -53.0305 | 0.98923
44811.8437 | 1:51 | 95 | 126.2934 | 111.3845 | 103.3388 | 94.141 | 92.8442 | 92.8442 | 32.4048 | 33.9461 | 33.7855 | 37.0661 | 50 | 64.5844 | 63.7203 | 37.8036 | 37.8769 | 97.2306 | OFF | 40.07 | 39.29 | 54.071 | 64.0488 | -6.1239 | 3.1201 | -53.5542 | -53.5542 | 0.9891
44811.8438 | 1:51 | 95 | 125.6553 | 111.0587 | 103.2716 | 94.2135 | 93.2781 | 93.2781 | 32.5249 | 33.9761 | 34.6415 | 37.4681 | 50 | 64.8648 | 64.0207 | 37.9516 | 37.9924 | 97.2464 | OFF | 40.07 | 40.07 | 54.1435 | 63.2016 | -6.0939 | 3.492 | -53.2081 | -53.2081 | 0.98939
44811.8439 | 1:51 | 95 | 125.0155 | 110.8464 | 103.1984 | 94.2255 | 93.6707 | 93.6707 | 32.6626 | 34.0691 | 35.7019 | 37.7581 | 50 | 65.1714 | 64.3247 | 38.1209 | 38.0594 | 97.3442 | OFF | 40.84 | 40.07 | 53.3855 | 63.1284 | -6.7709 | 3.689 | -53.6007 | -53.6007 | 0.9894
44811.844 | 1:51 | 95 | 124.4916 | 110.6048 | 103.1243 | 94.4225 | 93.9983 | 93.9983 | 32.7595 | 34.2179 | 36.5152 | 37.9896 | 50 | 65.4339 | 64.5821 | 38.1635 | 38.171 | 97.4144 | OFF | 40.84 | 40.07 | 53.5825 | 63.0543 | -6.6221 | 3.7717 | -53.9283 | -53.9283 | 0.98937
44811.8441 | 1:51 | 95 | 123.9567 | 110.383 | 103.0837 | 94.6305 | 94.2811 | 94.2811 | 33.0247 | 34.2874 | 37.0045 | 38.2086 | 50 | 65.7568 | 64.8872 | 38.3388 | 38.2315 | 97.5151 | OFF | 40.84 | 40.07 | 53.7905 | 63.0137 | -6.5526 | 3.9212 | -54.2111 | -54.2111 | 0.98919
44811.8442 | 1:52 | 95 | 123.4239 | 110.158 | 103 | 94.8374 | 94.5025 | 94.5025 | 33.3617 | 34.3959 | 37.3287 | 38.448 | 50 | 66.0332 | 65.0644 | 38.5452 | 38.332 | 97.5213 | OFF | 41.6 | 40.84 | 53.2374 | 62.16 | -7.2041 | 4.0521 | -53.6626 | -53.6626 | 0.988
44811.8443 | 1:52 | 95 | 122.9104 | 109.9597 | 102.9452 | 94.9543 | 94.7142 | 94.7142 | 33.8391 | 34.5789 | 37.5729 | 38.5787 | 50 | 66.032 | 65.0179 | 38.6122 | 38.4838 | 97.5669 | OFF | 41.6 | 40.84 | 53.3543 | 62.1052 | -7.0211 | 3.9998 | -53.8742 | -53.8742 | 0.98744
44811.8445 | 1:52 | 95 | 122.4338 | 109.7475 | 102.8768 | 95.1497 | 94.8307 | 94.8307 | 34.4797 | 34.8113 | 37.7777 | 38.7277 | 50 | 66.4599 | 65.3337 | 38.69 | 38.6334 | 97.5375 | OFF | 41.6 | 40.84 | 53.5497 | 62.0368 | -6.7887 | 3.9164 | -53.9907 | -53.9907 | 0.98612
44811.8446 | 1:52 | 95 | 121.9598 | 109.5406 | 102.8103 | 95.3137 | 94.9777 | 94.9777 | 34.8875 | 35.0203 | 38.0182 | 38.8751 | 50 | 66.3998 | 65.6416 | 38.7419 | 38.6725 | 97.5039 | OFF | 41.6 | 40.84 | 53.7137 | 61.9703 | -6.5797 | 3.8548 | -54.1377 | -54.1377 | 0.99065
44811.8447 | 1:52 | 95 | 121.5136 | 109.311 | 102.6998 | 95.4099 | 95.0562 | 95.0562 | 35.2304 | 35.2018 | 38.1598 | 39.0079 | 50 | 66.6572 | 65.8403 | 38.9133 | 38.727 | 97.4198 | OFF | 41.6 | 40.84 | 53.8099 | 61.8598 | -6.3982 | 3.8061 | -54.2162 | -54.2162 | 0.98996
44811.8448 | 1:52 | 95 | 120.9944 | 109.1024 | 102.5905 | 95.4985 | 95.1218 | 95.1218 | 35.5493 | 35.4493 | 38.2836 | 39.1101 | 50 | 66.9161 | 65.9077 | 38.9656 | 38.845 | 97.2347 | OFF | 41.6 | 40.84 | 53.8985 | 61.7505 | -6.1507 | 3.6608 | -54.2818 | -54.2818 | 0.98764
44811.8449 | 1:53 | 95 | 120.5929 | 108.8626 | 102.4503 | 95.5789 | 95.1577 | 95.1577 | 35.8491 | 35.798 | 38.3033 | 39.2155 | 50 | 66.9276 | 65.8244 | 39.1068 | 38.9687 | 97.1328 | OFF | 41.6 | 40.84 | 53.9789 | 61.6103 | -5.802 | 3.4175 | -54.3177 | -54.3177 | 0.98649
44811.845 | 1:53 | 95 | 120.1253 | 108.619 | 102.3006 | 95.6213 | 95.1377 | 95.1377 | 36.153 | 36.1487 | 38.452 | 39.3216 | 50 | 67.0554 | 66.1869 | 39.2316 | 39.0535 | 96.9166 | OFF | 42.36 | 41.6 | 53.2613 | 60.7006 | -6.2113 | 3.1729 | -53.5377 | -53.5377 | 0.98938
44811.8452 | 1:53 | 95 | 119.7087 | 108.3963 | 102.1343 | 95.6302 | 95.1185 | 95.1185 | 36.4707 | 36.4568 | 38.5854 | 39.4295 | 50 | 67.3644 | 66.3577 | 39.3058 | 39.0857 | 96.8076 | OFF | 42.36 | 41.6 | 53.2702 | 60.5343 | -5.9032 | 2.9727 | -53.5185 | -53.5185 | 0.98773
44811.8453 | 1:53 | 95 | 119.3038 | 108.1632 | 102.0047 | 95.6162 | 95.1211 | 95.1211 | 36.7397 | 36.7328 | 38.6737 | 39.5479 | 50 | 67.5841 | 66.5188 | 39.4849 | 39.2054 | 96.6702 | OFF | 42.36 | 41.6 | 53.2562 | 60.4047 | -5.6273 | 2.8151 | -53.5211 | -53.5211 | 0.98705
44811.8454 | 1:53 | 95 | 118.8834 | 107.9706 | 101.8429 | 95.6088 | 95.097 | 95.097 | 36.9905 | 37.0695 | 38.7853 | 39.6631 | 50 | 67.7315 | 66.6431 | 39.5188 | 39.364 | 96.6309 | OFF | 42.36 | 41.6 | 53.2488 | 60.2429 | -5.2905 | 2.5936 | -53.497 | -53.497 | 0.9868
44811.8455 | 1:53 | 95 | 118.4857 | 107.7396 | 101.7208 | 95.5676 | 95.0635 | 95.0635 | 37.2475 | 37.3159 | 38.8849 | 39.7809 | 50 | 67.9341 | 66.8098 | 39.6948 | 39.3728 | 96.4858 | OFF | 42.36 | 41.6 | 53.2076 | 60.1208 | -5.0441 | 2.465 | -53.4635 | -53.4635 | 0.98639
44811.8456 | 1:54 | 95 | 118.1003 | 107.5256 | 101.5518 | 95.539 | 95.0177 | 95.0177 | 37.4577 | 37.393 | 39.005 | 39.9004 | 50 | 68.1061 | 66.9266 | 39.7809 | 39.4397 | 96.3703 | OFF | 43.11 | 41.6 | 52.429 | 59.9518 | -5.717 | 2.5074 | -53.4177 | -53.4177 | 0.98576
44811.8457 | 1:54 | 95 | 119.8879 | 107.9314 | 113.8484 | 81.9583 | 96.2219 | 96.2219 | 36.9224 | 36.872 | 37.223 | 36.5073 | 50 | 62.0481 | 170.1771 | 39.8199 | 39.5425 | 96.8425 | OFF | 38.5 | 98.41 | 43.4583 | 15.4384 | -1.628 | -0.36471 | 2.1881 | 2.1881 | 2.4089
44811.8458 | 1:54 | 95 | 122.7967 | 111.5667 | 131.2155 | 65.4958 | 108.1729 | 108.1729 | 28.4392 | 33.4002 | 31.9147 | 34.2888 | 50 | 41.5604 | 212.7282 | 39.5793 | 39.4126 | 106.8098 | ON | 19.89 | 113.8 | 45.6058 | 17.4155 | 13.5102 | 0.88858 | 5.6271 | 5.6271 | 4.0424 |  | OK | OK | OK | Too Low | 102.9067 | OK | OK | OK | OK | OK
44811.846 | 1:54 | 95 | 121.9583 | 117.5294 | 132.547 | 56.7242 | 109.9342 | 109.9342 | 23.9462 | 33.6253 | 31.7227 | 34.6505 | 50 | 29.7058 | 210.6402 | 39.0818 | 39.334 | 109.1786 | ON | 6.74 | 113.8 | 49.9842 | 18.747 | 26.8853 | 1.0252 | 3.8658 | 3.8658 | 5.0746 |  | OK | OK | OK | Too Low | 115.2183 | OK | OK | OK | OK | OK
44811.8461 | 1:54 | 95 | 121.1015 | 119.2358 | 131.639 | 48.2747 | 108.1793 | 108.1793 | 27.8448 | 34.0295 | 32.5941 | 35.2768 | 50 | 24.3039 | 206.0477 | 39.295 | 39.2981 | 108.3524 | ON | 0.44 | 112 | 47.8347 | 19.639 | 33.5895 | 1.2473 | 3.8207 | 3.8207 | 5.6596 |  | OK | OK | OK | Too Low | 120.6615 | OK | OK | OK | OK | OK
44811.8462 | 1:54 | 95 | 120.6608 | 119.5906 | 130.6864 | 42.7472 | 106.3993 | 106.3993 | 31.1886 | 34.6819 | 33.7212 | 35.8704 | 50 | 20.1762 | 201.6662 | 39.3871 | 39.432 | 107.3011 | ON | -5.06 | 110.2 | 47.8072 | 20.4864 | 39.7419 | 1.1886 | 3.8007 | 3.8007 | 6.2038 |  | OK | OK | OK | OK | 125.7208 | OK | OK | OK | OK | OK
44811.8463 | 1:55 | 95 | 120.8715 | 119.6901 | 129.9055 | 40.025 | 105.0749 | 105.0749 | 33.5912 | 35.3469 | 34.7846 | 36.4076 | 50 | 18.3239 | 198.2577 | 39.7037 | 39.5942 | 106.4063 | ON | -7.99 | 108.3 | 48.015 | 21.6055 | 43.3369 | 1.0608 | 3.2251 | 3.2251 | 6.4486 |  | OK | OK | OK | OK | 128.8615 | OK | OK | OK | OK | OK
44811.8464 | 1:55 | 95 | 120.855 | 119.3017 | 130.1663 | 43.8438 | 102.5243 | 102.5243 | 35.3201 | 35.9997 | 28.7995 | 26.4679 | 50 | 41.7338 | 186.7998 | 39.8732 | 39.6039 | 103.9371 | ON | 19.89 | 104.4 | 23.9538 | 25.7663 | 16.1097 | -9.5318 | 1.8757 | 1.8757 | 3.5705 |  | OK | OK | OK | OK | 100.965 | OK | OK | OK | OK | OK
44811.8465 | 1:55 | 95 | 120.5964 | 119.1387 | 130.9247 | 50.6003 | 100.8145 | 100.8145 | 28.9996 | 36.1421 | 27.2023 | 25.4176 | 50 | 48.9551 | 180.0495 | 39.7027 | 39.2177 | 102.8368 | ON | 26.6 | 102.5 | 24.0003 | 28.4247 | 9.5421 | -10.7246 | 1.6855 | 1.6855 | 3.0594 |  | OK | OK | OK | OK | 93.9964 | OK | OK | OK | OK | OK
44811.8467 | 1:55 | 95 | 120.4272 | 119.1238 | 130.8163 | 55.8988 | 101.0516 | 101.0516 | 27.1788 | 33.7241 | 26.263 | 24.8487 | 50 | 48.3337 | 181.1543 | 39.114 | 38.8339 | 102.8856 | ON | 26.6 | 102.5 | 29.2988 | 28.3163 | 7.1241 | -8.8753 | 1.4484 | 1.4484 | 3.1071 |  | OK | OK | OK | OK | 93.8272 | OK | OK | OK | OK | OK
44811.8468 | 1:55 | 95 | 120.5793 | 119.3568 | 131.0042 | 60.3924 | 101.5669 | 101.5669 | 27.0732 | 33.1535 | 26.0401 | 25.8162 | 50 | 48.6137 | 182.5697 | 38.7679 | 38.6222 | 103.1979 | ON | 26.6 | 102.5 | 33.7923 | 28.5042 | 6.5535 | -7.3373 | 0.9331 | 0.9331 | 3.1158 |  | OK | Low Charge | OK | OK | 93.9793 | OK | OK | OK | OK | OK
44811.8469 | 1:55 | 95 | 121.0246 | 119.7895 | 131.4578 | 64.2695 | 102.3154 | 102.3154 | 27.4635 | 32.8232 | 26.0671 | 26.943 | 50 | 48.5009 | 184.6073 | 38.7066 | 38.4874 | 103.7366 | ON | 26.6 | 102.5 | 37.6695 | 28.9578 | 6.2232 | -5.8801 | 0.1846 | 0.1846 | 3.1536 |  | OK | Low Charge | OK | OK | 94.4246 | OK | OK | OK | OK | OK
44811.847 | 1:56 | 95 | 121.6535 | 120.3058 | 131.9913 | 67.7315 | 102.8295 | 102.8295 | 27.4372 | 32.1779 | 26.0207 | 27.9822 | 50 | 48.9039 | 186.2752 | 38.5516 | 38.4566 | 104.1923 | ON | 26.6 | 104.4 | 41.1315 | 27.5913 | 5.5779 | -4.1956 | 1.5705 | 1.5705 | 3.1598 |  | OK | OK | OK | OK | 95.0535 | OK | OK | OK | OK | OK
44811.8471 | 1:56 | 95 | 122.2983 | 120.9436 | 132.7195 | 69.864 | 103.304 | 103.304 | 27.5822 | 31.5708 | 25.972 | 28.5661 | 50 | 48.7826 | 187.6587 | 38.2516 | 38.4708 | 104.5615 | ON | 26.6 | 104.4 | 43.264 | 28.3195 | 4.9708 | -3.0047 | 1.096 | 1.096 | 3.1876 |  | OK | OK | OK | OK | 95.6983 | OK | OK | OK | OK | OK
44811.8472 | 1:56 | 95 | 122.9718 | 121.5629 | 133.4331 | 71.6601 | 103.6246 | 103.6246 | 27.5143 | 31.0338 | 25.812 | 28.5521 | 50 | 48.6386 | 188.4819 | 38.2039 | 38.2455 | 104.8261 | ON | 26.6 | 104.4 | 45.0601 | 29.0331 | 4.4337 | -2.4816 | 0.7754 | 0.7754 | 3.2079 |  | OK | Low Charge | OK | OK | 96.3718 | OK | OK | OK | OK | OK
44811.8474 | 1:56 | 95 | 123.6645 | 122.1564 | 134.1152 | 73.3413 | 103.7066 | 103.7066 | 27.3398 | 30.2201 | 26.4691 | 28.2757 | 50 | 48.4063 | 188.7771 | 37.9741 | 38.201 | 104.9189 | ON | 26.6 | 104.4 | 46.7413 | 29.7152 | 3.6201 | -1.9444 | 0.6934 | 0.6934 | 3.2244 |  | OK | Low Charge | OK | OK | 97.0645 | OK | OK | OK | OK | OK
44811.8475 | 1:56 | 95 | 124.4413 | 122.6874 | 134.8132 | 74.8971 | 103.6769 | 103.6769 | 27.1442 | 29.3105 | 25.9607 | 27.6423 | 50 | 48.3181 | 188.5861 | 37.8252 | 38.0317 | 104.9098 | ON | 26.6 | 104.4 | 48.2971 | 30.4132 | 2.7105 | -1.6681 | 0.7231 | 0.7231 | 3.2258 |  | OK | Low Charge | OK | OK | 97.8413 | OK | OK | OK | OK | OK
44811.8476 | 1:56 | 95 | 125.0948 | 123.1545 | 135.5049 | 76.2726 | 103.5199 | 103.5199 | 26.959 | 28.1837 | 25.6849 | 27.0545 | 50 | 48.796 | 188.1026 | 37.7053 | 37.9337 | 104.823 | ON | 26.6 | 104.4 | 49.6726 | 31.1049 | 1.5837 | -1.1292 | 0.8801 | 0.8801 | 3.1939 |  | OK | Low Charge | OK | OK | 98.4948 | OK | OK | OK | OK | OK
44811.8477 | 1:57 | 95 | 125.7958 | 123.7399 | 136.258 | 76.1998 | 103.5896 | 103.5896 | 27.0474 | 26.1992 | 25.4424 | 26.6855 | 50 | 48.9144 | 188.6481 | 37.4921 | 37.7403 | 104.8909 | ON | 26.6 | 104.4 | 49.5998 | 31.858 | -0.40079 | 0.48626 | 0.8104 | 0.8104 | 3.1966 |  | OK | Low Charge | OK | OK | 99.1958 | OK | OK | OK | OK | OK
44811.8478 | 1:57 | 95 | 126.4599 | 124.2883 | 136.9283 | 75.2647 | 103.8393 | 103.8393 | 26.9767 | 25.2452 | 25.3581 | 26.4354 | 50 | 49.0041 | 189.176 | 37.3888 | 37.6937 | 105.1507 | ON | 27.51 | 104.4 | 47.7547 | 32.5283 | -2.2648 | 1.1903 | 0.5607 | 0.5607 | 3.2004 |  | OK | Low Charge | OK | OK | 98.9499 | OK | OK | OK | OK | OK
44811.8479 | 1:57 | 95 | 127.1515 | 124.8444 | 137.5798 | 72.8533 | 104.4119 | 104.4119 | 27.111 | 25.2635 | 25.2527 | 26.2833 | 50 | 48.9984 | 190.7311 | 37.2597 | 37.5501 | 105.6159 | ON | 26.6 | 106.4 | 46.2533 | 31.1798 | -1.3365 | 1.0198 | 1.9881 | 1.9881 | 3.2251 |  | OK | OK | OK | OK | 100.5515 | OK | OK | OK | OK | OK
44811.848 | 1:57 | 95 | 127.6724 | 125.2951 | 138.0391 | 70.2967 | 104.9072 | 104.9072 | 27.122 | 25.2379 | 25.0572 | 26.1791 | 50 | 48.9125 | 192.1575 | 37.242 | 37.5388 | 106.0474 | ON | 26.6 | 106.4 | 43.6967 | 31.6391 | -1.3621 | 0.94122 | 1.4928 | 1.4928 | 3.2518 |  | OK | OK | OK | OK | 101.0724 | OK | OK | OK | OK | OK
44811.8482 | 1:57 | 95 | 127.9355 | 125.6854 | 138.3667 | 67.9788 | 105.3159 | 105.3159 | 26.9778 | 25.0435 | 24.7857 | 25.942 | 50 | 48.7409 | 193.2611 | 37.1736 | 37.4009 | 106.4245 | ON | 26.6 | 106.4 | 41.3788 | 31.9667 | -1.5565 | 0.89856 | 1.0841 | 1.0841 | 3.278 |  | OK | OK | OK | OK | 101.3355 | OK | OK | OK | OK | OK
44811.8483 | 1:57 | 95 | 128.0904 | 125.9334 | 138.4937 | 65.7167 | 105.6145 | 105.6145 | 26.8171 | 24.9442 | 24.6023 | 25.6636 | 50 | 48.6742 | 193.7938 | 37.0097 | 37.3307 | 106.67 | ON | 26.6 | 106.4 | 39.1167 | 32.0937 | -1.6558 | 0.71942 | 0.7855 | 0.7855 | 3.2899 |  | OK | Low Charge | OK | OK | 101.4904 | OK | OK | OK | OK | OK
44811.8484 | 1:58 | 95 | 128.1405 | 126.0815 | 138.5713 | 63.6258 | 105.8863 | 105.8863 | 26.5675 | 24.7103 | 24.4347 | 25.4125 | 50 | 48.3996 | 194.2908 | 36.9992 | 37.2905 | 106.9537 | ON | 26.6 | 106.4 | 37.0258 | 32.1713 | -1.8897 | 0.70216 | 0.5137 | 0.5137 | 3.3121 |  | OK | Low Charge | OK | OK | 101.5405 | OK | OK | OK | OK | OK
44811.8485 | 1:58 | 95 | 128.107 | 126.175 | 138.5391 | 62.5007 | 106.1778 | 106.1778 | 26.3163 | 24.4958 | 24.1884 | 25.192 | 50 | 48.1703 | 195.3075 | 36.8149 | 37.2202 | 107.2135 | ON | 26.6 | 108.3 | 35.9007 | 30.2391 | -2.1042 | 0.69617 | 2.1222 | 2.1222 | 3.3403 |  | OK | OK | OK | OK | 101.507 | OK | OK | OK | OK | OK
44811.8486 | 1:58 | 95 | 128.0175 | 126.1782 | 138.4854 | 61.6484 | 106.3286 | 106.3286 | 26.0723 | 24.2812 | 23.8879 | 25.0372 | 50 | 47.8557 | 195.7199 | 36.743 | 37.0606 | 107.3645 | ON | 25.68 | 108.3 | 35.9684 | 30.1854 | -1.3988 | 0.75598 | 1.9714 | 1.9714 | 3.3637 |  | OK | OK | OK | OK | 102.3375 | OK | OK | OK | OK | OK
44811.8487 | 1:58 | 95 | 127.8936 | 126.1304 | 138.3921 | 61.8975 | 106.3879 | 106.3879 | 25.8832 | 24.116 | 23.725 | 25.0045 | 50 | 47.8332 | 195.645 | 36.6227 | 36.9741 | 107.4576 | ON | 25.68 | 108.3 | 36.2175 | 30.0921 | -1.564 | 0.88852 | 1.9121 | 1.9121 | 3.3637 |  | OK | OK | OK | OK | 102.2136 | OK | OK | OK | OK | OK
44811.8489 | 1:58 | 95 | 127.8278 | 126.1428 | 138.2747 | 61.9551 | 106.4808 | 106.4808 | 25.665 | 23.8965 | 23.5062 | 24.9142 | 50 | 47.5764 | 195.8867 | 36.5015 | 36.895 | 107.5496 | ON | 25.68 | 108.3 | 36.2751 | 29.9747 | -1.7835 | 1.0177 | 1.8192 | 1.8192 | 3.3815 |  | OK | OK | OK | OK | 102.1478 | OK | OK | OK | OK | OK
44811.849 | 1:58 | 95 | 127.7616 | 126.1255 | 138.2047 | 62.3169 | 106.5748 | 106.5748 | 25.479 | 23.7606 | 23.3402 | 24.8442 | 50 | 47.3856 | 196.3965 | 36.5014 | 36.8297 | 107.6479 | ON | 25.68 | 108.3 | 36.6369 | 29.9047 | -1.9194 | 1.0836 | 1.7252 | 1.7252 | 3.4001 |  | OK | OK | OK | OK | 102.0816 | OK | OK | OK | OK | OK
44811.8491 | 1:59 | 95 | 127.7333 | 126.1359 | 138.1877 | 62.7496 | 106.6836 | 106.6836 | 25.2987 | 23.6196 | 23.1495 | 24.7554 | 50 | 47.2384 | 196.1514 | 36.4241 | 36.6825 | 107.7407 | ON | 25.68 | 108.3 | 37.0696 | 29.8877 | -2.0604 | 1.1358 | 1.6164 | 1.6164 | 3.4042 |  | OK | OK | OK | OK | 102.0533 | OK | OK | OK | OK | OK
44811.8492 | 1:59 | 95 | 127.7598 | 126.1368 | 138.1838 | 63.1248 | 106.7736 | 106.7736 | 25.0409 | 23.3941 | 23.0252 | 24.6576 | 50 | 47.0352 | 196.5772 | 36.3271 | 36.6037 | 107.8298 | ON | 25.68 | 108.3 | 37.4448 | 29.8838 | -2.2859 | 1.2635 | 1.5264 | 1.5264 | 3.4223 |  | OK | OK | OK | OK | 102.0798 | OK | OK | OK | OK | OK
44811.8493 | 1:59 | 95 | 127.7571 | 126.2211 | 138.2601 | 63.032 | 106.8256 | 106.8256 | 24.9271 | 23.3012 | 22.9149 | 24.5789 | 50 | 46.9464 | 196.3589 | 36.2683 | 36.563 | 107.8939 | ON | 24.74 | 108.3 | 38.2919 | 29.9601 | -1.4388 | 1.2777 | 1.4744 | 1.4744 | 3.4237 |  | OK | OK | OK | OK | 103.0171 | OK | OK | OK | OK | OK
44811.8494 | 1:59 | 95 | 127.8456 | 126.274 | 138.3057 | 62.5702 | 106.9519 | 106.9519 | 24.7661 | 23.1382 | 22.7322 | 24.4944 | 50 | 46.8329 | 196.8129 | 36.2852 | 36.3384 | 108.0115 | ON | 24.74 | 108.3 | 37.8302 | 30.0057 | -1.6018 | 1.3562 | 1.3481 | 1.3481 | 3.4374 |  | OK | OK | OK | OK | 103.1056 | OK | OK | OK | OK | OK
44811.8496 | 1:59 | 95 | 127.9504 | 126.4014 | 138.4295 | 62.5566 | 107.0804 | 107.0804 | 24.5578 | 22.9685 | 22.6042 | 24.3899 | 50 | 46.6472 | 197.1013 | 36.1997 | 36.2876 | 108.1436 | ON | 24.74 | 108.3 | 37.8165 | 30.1295 | -1.7715 | 1.4213 | 1.2196 | 1.2196 | 3.4525 |  | OK | OK | OK | OK | 103.2104 | OK | OK | OK | OK | OK
44811.8497 | 1:59 | 95 | 128.147 | 126.5322 | 138.5522 | 62.7984 | 107.1667 | 107.1667 | 24.4066 | 22.8767 | 22.4741 | 24.3418 | 50 | 46.5507 | 197.5088 | 35.8997 | 36.2694 | 108.1873 | ON | 24.74 | 108.3 | 38.0584 | 30.2522 | -1.8633 | 1.4651 | 1.1333 | 1.1333 | 3.4646 |  | OK | OK | OK | OK | 103.407 | OK | OK | OK | OK | OK
44811.8498 | 2:00 | 95 | 128.328 | 126.6811 | 138.6955 | 63.3278 | 107.2753 | 107.2753 | 24.2437 | 22.6581 | 22.321 | 24.2403 | 50 | 46.1474 | 197.7846 | 36.1437 | 36.2098 | 108.2986 | ON | 24.74 | 108.3 | 38.5879 | 30.3955 | -2.0819 | 1.5822 | 1.0247 | 1.0247 | 3.4921 |  | OK | OK | OK | OK | 103.588 | OK | OK | OK | OK | OK
44811.8499 | 2:00 | 95 | 128.5684 | 126.8077 | 138.8814 | 63.6147 | 107.4387 | 107.4387 | 24.3007 | 22.8282 | 22.3922 | 24.2273 | 50 | 46.8697 | 198.1766 | 35.7822 | 36.0478 | 108.462 | ON | 24.74 | 108.3 | 38.8747 | 30.5814 | -1.9118 | 1.3991 | 0.8613 | 0.8613 | 3.4575 |  | OK | Low Charge | OK | OK | 103.8284 | OK | OK | OK | OK | OK
44811.85 | 2:00 | 95 | 129.0175 | 127.1481 | 139.3353 | 63.8103 | 108.3185 | 108.3185 | 24.5834 | 25.6813 | 22.3864 | 24.2674 | 50 | 46.602 | 200.5769 | 35.9978 | 36.0406 | 109.1129 | ON | 24.74 | 110.2 | 39.0703 | 29.1353 | 0.94128 | -1.4139 | 1.8815 | 1.8815 | 3.5117 |  | OK | OK | OK | OK | 104.2775 | OK | OK | OK | OK | OK
44811.8501 | 2:00 | 95 | 129.4169 | 127.561 | 139.752 | 64.577 | 108.6414 | 108.6414 | 24.5398 | 28.2155 | 22.3129 | 24.2822 | 50 | 46.5791 | 201.5051 | 36.3728 | 35.9573 | 109.4313 | ON | 24.74 | 110.2 | 39.837 | 29.552 | 3.4755 | -3.9334 | 1.5586 | 1.5586 | 3.5282 |  | OK | OK | OK | OK | 104.6769 | OK | OK | OK | OK | OK
44811.8502 | 2:00 | 95 | 129.8005 | 127.85 | 140.1081 | 65.6596 | 108.773 | 108.773 | 24.5465 | 28.716 | 22.2141 | 24.2285 | 50 | 46.602 | 201.6417 | 36.3391 | 35.9135 | 109.5707 | ON | 24.74 | 110.2 | 40.9196 | 29.9081 | 3.976 | -4.4875 | 1.427 | 1.427 | 3.5291 |  | OK | OK | OK | OK | 105.0605 | OK | OK | OK | OK | OK
44811.8504 | 2:00 | 95 | 130.1143 | 128.1785 | 140.5116 | 66.9031 | 108.877 | 108.877 | 26.0425 | 28.5611 | 22.2678 | 24.1959 | 50 | 46.4847 | 202.2877 | 36.194 | 35.7986 | 109.6881 | ON | 24.74 | 110.2 | 42.1631 | 30.3116 | 3.8211 | -4.3652 | 1.323 | 1.323 | 3.5464 |  | OK | OK | OK | OK | 105.3743 | OK | OK | OK | OK | OK
44811.8505 | 2:01 | 95 | 130.509 | 128.4872 | 140.9356 | 67.8324 | 108.9162 | 108.9162 | 27.1618 | 28.2687 | 22.2079 | 24.1568 | 50 | 46.6061 | 202.2069 | 36.1442 | 35.8097 | 109.7266 | ON | 24.74 | 110.2 | 43.0924 | 30.7356 | 3.5287 | -4.1119 | 1.2838 | 1.2838 | 3.5381 |  | OK | OK | OK | OK | 105.769 | OK | OK | OK | OK | OK
44811.8506 | 2:01 | 95 | 130.9381 | 128.9637 | 141.3915 | 68.884 | 109.0361 | 109.0361 | 25.6639 | 28.0665 | 22.1673 | 24.1634 | 50 | 46.4799 | 202.2603 | 36.0076 | 35.8207 | 109.8199 | ON | 24.74 | 110.2 | 44.144 | 31.1915 | 3.3265 | -3.9031 | 1.1639 | 1.1639 | 3.5463 |  | OK | OK | OK | OK | 106.1981 | OK | OK | OK | OK | OK
44811.8507 | 2:01 | 95 | 131.3638 | 129.2933 | 141.8383 | 69.3824 | 109.0026 | 109.0026 | 24.7569 | 27.9316 | 22.0209 | 24.195 | 50 | 46.3683 | 202.1554 | 36.0132 | 35.5747 | 109.8499 | ON | 24.74 | 110.2 | 44.6424 | 31.6383 | 3.1916 | -3.7367 | 1.1974 | 1.1974 | 3.551 |  | OK | OK | OK | OK | 106.6238 | OK | OK | OK | OK | OK
44811.8508 | 2:01 | 95 | 131.7192 | 129.6355 | 142.3124 | 70.4406 | 108.9967 | 108.9967 | 24.5729 | 27.3802 | 22.1106 | 24.2924 | 50 | 46.4295 | 202.3791 | 36.0491 | 35.6187 | 109.8686 | ON | 24.74 | 110.2 | 45.7006 | 32.1124 | 2.6402 | -3.0878 | 1.2033 | 1.2033 | 3.5511 |  | OK | OK | OK | OK | 106.9792 | OK | OK | OK | OK | OK
44811.8509 | 2:01 | 95 | 132.1492 | 129.9153 | 142.8144 | 71.3657 | 108.9968 | 108.9968 | 24.4138 | 26.3411 | 21.7698 | 24.3003 | 50 | 46.2219 | 202.4923 | 35.8984 | 35.5699 | 109.8518 | ON | 24.74 | 110.2 | 46.6257 | 32.6144 | 1.6011 | -2.0409 | 1.2032 | 1.2032 | 3.5651 |  | OK | OK | OK | OK | 107.4092 | OK | OK | OK | OK | OK
44811.8511 | 2:01 | 95 | 132.5009 | 130.267 | 143.2168 | 72.0854 | 108.8328 | 108.8328 | 24.3474 | 23.3418 | 21.7716 | 24.3553 | 50 | 45.8645 | 201.747 | 35.7885 | 35.501 | 109.7182 | ON | 23.8 | 110.2 | 48.2854 | 33.0168 | -0.45822 | 1.0135 | 1.3672 | 1.3672 | 3.5738 |  | OK | OK | OK | OK | 108.7009 | OK | OK | OK | OK | OK
44811.8512 | 2:02 | 95 | 132.888 | 130.5133 | 143.6316 | 72.7989 | 108.6545 | 108.6545 | 24.1238 | 22.568 | 21.6635 | 24.2865 | 50 | 45.8158 | 201.3665 | 35.6897 | 35.4945 | 109.5798 | ON | 23.8 | 110.2 | 48.9989 | 33.4316 | -1.232 | 1.7185 | 1.5455 | 1.5455 | 3.5704 |  | OK | OK | OK | OK | 109.088 | OK | OK | OK | OK | OK
44811.8513 | 2:02 | 95 | 133.2384 | 130.7624 | 143.9426 | 73.0738 | 108.423 | 108.423 | 23.9945 | 22.3516 | 21.5761 | 24.3113 | 50 | 45.7361 | 200.7206 | 35.4967 | 35.4697 | 109.3388 | ON | 23.8 | 110.2 | 49.2737 | 33.7426 | -1.4484 | 1.9597 | 1.777 | 1.777 | 3.5644 |  | OK | OK | OK | OK | 109.4384 | OK | OK | OK | OK | OK
44811.8514 | 2:02 | 95 | 133.4881 | 130.8733 | 144.2421 | 73.1017 | 108.1758 | 108.1758 | 23.8295 | 22.2197 | 21.6099 | 24.3129 | 50 | 45.6512 | 199.7784 | 35.5455 | 35.371 | 109.1586 | ON | 23.8 | 108.3 | 49.3017 | 35.9421 | -1.5803 | 2.0933 | 0.1242 | 0.1242 | 3.5538 |  | OK | Low Charge | OK | OK | 109.6881 | OK | OK | OK | OK | OK
44811.8515 | 2:02 | 95 | 133.6825 | 131.0562 | 144.5175 | 72.6739 | 108.064 | 108.064 | 23.6499 | 22.0704 | 21.402 | 24.2758 | 50 | 45.4704 | 199.2696 | 35.5558 | 35.3488 | 109.0283 | ON | 23.8 | 108.3 | 48.8739 | 36.2175 | -1.7296 | 2.2054 | 0.236 | 0.236 | 3.5561 |  | OK | Low Charge | OK | OK | 109.8825 | OK | OK | OK | OK | OK
44811.8516 | 2:02 | 95 | 133.8896 | 131.2092 | 144.7473 | 72.1708 | 107.9688 | 107.9688 | 23.4739 | 21.9298 | 21.2895 | 24.2418 | 50 | 45.4296 | 199.3926 | 35.391 | 35.2364 | 108.9216 | ON | 23.8 | 108.3 | 48.3708 | 36.4473 | -1.8702 | 2.3121 | 0.3312 | 0.3312 | 3.5605 |  | OK | Low Charge | OK | OK | 110.0896 | OK | OK | OK | OK | OK
44811.8518 | 2:02 | 95 | 134.095 | 131.219 | 144.9474 | 71.6004 | 108.1191 | 108.1191 | 23.3516 | 21.8081 | 21.2257 | 24.1933 | 50 | 45.3686 | 201.5349 | 35.315 | 35.2595 | 108.9625 | ON | 23.8 | 110.2 | 47.8004 | 34.7474 | -1.992 | 2.3853 | 2.0809 | 2.0809 | 3.5998 |  | OK | OK | OK | OK | 110.295 | OK | OK | OK | OK | OK
44811.8519 | 2:03 | 95 | 134.6741 | 131.8238 | 145.5214 | 70.8226 | 109.8179 | 109.8179 | 23.0755 | 21.2077 | 21.3137 | 24.1355 | 50 | 44.5172 | 206.4525 | 35.2364 | 35.04 | 110.2254 | ON | 22.84 | 112 | 47.9826 | 33.5214 | -1.6323 | 2.9279 | 2.1821 | 2.1821 | 3.7346 |  | OK | OK | OK | OK | 111.8341 | OK | OK | OK | OK | OK
44811.852 | 2:03 | 95 | 135.1416 | 132.384 | 146.0421 | 67.9908 | 110.5598 | 110.5598 | 22.8182 | 20.3213 | 22.3692 | 24.4429 | 50 | 42.9417 | 207.8243 | 35.2335 | 34.9881 | 110.7906 | ON | 20.88 | 112 | 47.1108 | 34.0421 | -0.55869 | 4.1216 | 1.4402 | 1.4402 | 3.8605 |  | OK | OK | OK | OK | 114.2616 | OK | OK | OK | OK | OK
44811.8521 | 2:03 | 95 | 135.3168 | 132.5632 | 146.1136 | 58.9274 | 110.6176 | 110.6176 | 22.1982 | 19.4875 | 23.53 | 25.22 | 50 | 42.3435 | 207.7665 | 34.9538 | 35.1234 | 110.9176 | ON | 20.88 | 112 | 38.0474 | 34.1136 | -1.3924 | 5.7324 | 1.3824 | 1.3824 | 3.8999 |  | OK | OK | OK | OK | 114.4368 | OK | OK | OK | OK | OK
44811.8522 | 2:03 | 95 | 135.0553 | 132.4069 | 145.8085 | 50.8867 | 110.6071 | 110.6071 | 21.7635 | 18.9786 | 24.8997 | 26.231 | 50 | 41.8034 | 207.3144 | 34.7069 | 35.301 | 110.9095 | ON | 19.89 | 112 | 30.9967 | 33.8085 | -0.91135 | 7.2523 | 1.3929 | 1.3929 | 3.9292 |  | OK | OK | OK | OK | 115.1653 | OK | OK | OK | OK | OK
44811.8523 | 2:03 | 95 | 134.4074 | 131.944 | 145.1404 | 47.0874 | 110.5029 | 110.5029 | 21.371 | 18.5839 | 26.1705 | 27.1906 | 50 | 41.4761 | 207.2516 | 34.7584 | 35.3329 | 110.8304 | ON | 19.89 | 112 | 27.1974 | 33.1404 | -1.3061 | 8.6067 | 1.4971 | 1.4971 | 3.951 |  | OK | OK | OK | OK | 114.5174 | OK | OK | OK | OK | OK
44811.8524 | 2:03 | 95 | 133.4356 | 131.2601 | 144.274 | 45.2017 | 110.285 | 110.285 | 20.9934 | 18.1628 | 27.3269 | 28.0808 | 50 | 40.9937 | 206.2987 | 34.7165 | 35.4186 | 110.6408 | ON | 18.88 | 112 | 26.3217 | 32.274 | -0.71722 | 9.918 | 1.715 | 1.715 | 3.9681 |  | OK | OK | OK | OK | 114.5556 | OK | OK | OK | OK | OK
44811.8526 | 2:04 | 95 | 132.5202 | 130.6026 | 143.4213 | 43.7759 | 110.1353 | 110.1353 | 20.6984 | 17.8236 | 28.318 | 28.8122 | 50 | 40.688 | 205.9292 | 34.5154 | 35.4708 | 110.5108 | ON | 18.88 | 112 | 24.8959 | 31.4213 | -1.0564 | 10.9886 | 1.8647 | 1.8647 | 3.9833 |  | OK | OK | OK | OK | 113.6402 | OK | OK | OK | OK | OK
44811.8527 | 2:04 | 95 | 131.6438 | 129.8532 | 142.6004 | 41.997 | 109.9504 | 109.9504 | 20.3561 | 17.5498 | 29.0208 | 29.4377 | 50 | 40.32 | 205.5633 | 34.3769 | 35.4716 | 110.3436 | ON | 18.88 | 112 | 23.117 | 30.6004 | -1.3302 | 11.8879 | 2.0496 | 2.0496 | 4.0033 |  | OK | OK | OK | OK | 112.7638 | OK | OK | OK | OK | OK
44811.8528 | 2:04 | 95 | 130.7688 | 129.2591 | 141.7687 | 41.5524 | 109.7178 | 109.7178 | 20.0652 | 17.2561 | 29.5864 | 29.9111 | 50 | 40.156 | 204.8282 | 34.3176 | 35.4862 | 110.1498 | ON | 18.88 | 110.2 | 22.6724 | 31.5687 | -1.6239 | 12.655 | 0.4822 | 0.4822 | 4.0019 |  | OK | Low Charge | OK | OK | 111.8888 | OK | OK | OK | OK | OK
44811.8529 | 2:04 | 95 | 129.9862 | 128.6306 | 140.9597 | 40.9295 | 109.4296 | 109.4296 | 19.7173 | 16.9377 | 30.0409 | 30.3195 | 50 | 39.8477 | 204.1632 | 34.2607 | 35.4933 | 109.8722 | ON | 17.86 | 110.2 | 23.0695 | 30.7597 | -0.9223 | 13.3818 | 0.7704 | 0.7704 | 4.0123 |  | OK | Low Charge | OK | OK | 112.1262 | OK | OK | OK | OK | OK
44811.853 | 2:04 | 95 | 129.3546 | 128.0367 | 140.3077 | 40.2472 | 109.2549 | 109.2549 | 19.4666 | 16.6966 | 30.3777 | 30.6247 | 50 | 39.668 | 203.4801 | 34.0853 | 35.4207 | 109.7317 | ON | 17.86 | 110.2 | 22.3872 | 30.1077 | -1.1634 | 13.9281 | 0.9451 | 0.9451 | 4.013 |  | OK | Low Charge | OK | OK | 111.4946 | OK | OK | OK | OK | OK
44811.8531 | 2:04 | 95 | 128.8466 | 127.5625 | 139.6832 | 39.371 | 109.1335 | 109.1335 | 19.2779 | 16.4631 | 30.605 | 30.8466 | 50 | 39.3165 | 203.3502 | 33.9351 | 35.4205 | 109.6119 | ON | 17.86 | 110.2 | 21.511 | 29.4832 | -1.3969 | 14.3835 | 1.0665 | 1.0665 | 4.0367 |  | OK | OK | OK | OK | 110.9866 | OK | OK | OK | OK | OK
44811.8533 | 2:05 | 95 | 128.4133 | 127.1013 | 139.0987 | 38.9587 | 109.0335 | 109.0335 | 19.0243 | 16.2072 | 30.7857 | 31.0742 | 50 | 39.127 | 203.2149 | 33.9615 | 35.4155 | 109.4878 | ON | 17.86 | 110.2 | 21.0987 | 28.8987 | -1.6528 | 14.8671 | 1.1665 | 1.1665 | 4.0484 |  | OK | OK | OK | OK | 110.5533 | OK | OK | OK | OK | OK
44811.8534 | 2:05 | 95 | 128.0001 | 126.7089 | 138.5786 | 38.3437 | 108.8071 | 108.8071 | 18.7211 | 15.9685 | 30.9392 | 31.2357 | 50 | 38.9447 | 202.6209 | 33.8925 | 35.3968 | 109.3193 | ON | 16.82 | 110.2 | 21.5237 | 28.3786 | -0.85154 | 15.2673 | 1.3929 | 1.3929 | 4.0511 |  | OK | OK | OK | OK | 111.1801 | OK | OK | OK | OK | OK
44811.8535 | 2:05 | 95 | 127.6612 | 126.3806 | 138.1417 | 37.9582 | 108.707 | 108.707 | 18.4984 | 15.7386 | 31.0346 | 31.359 | 50 | 38.6747 | 202.234 | 33.7941 | 35.3707 | 109.2109 | ON | 16.82 | 110.2 | 21.1382 | 27.9417 | -1.0814 | 15.6204 | 1.493 | 1.493 | 4.0644 |  | OK | OK | OK | OK | 110.8412 | OK | OK | OK | OK | OK
44811.8536 | 2:05 | 95 | 127.3511 | 126.0296 | 137.6977 | 37.5826 | 108.5316 | 108.5316 | 18.2317 | 15.5035 | 31.1233 | 31.4712 | 50 | 38.5466 | 201.638 | 33.6137 | 35.3476 | 109.0517 | ON | 16.82 | 110.2 | 20.7626 | 27.4977 | -1.3165 | 15.9678 | 1.6684 | 1.6684 | 4.0629 |  | OK | OK | OK | OK | 110.5311 | OK | OK | OK | OK | OK
44811.8537 | 2:05 | 95 | 127.101 | 125.7151 | 137.2938 | 37.0831 | 108.367 | 108.367 | 18.0106 | 15.3242 | 31.1929 | 31.5766 | 50 | 38.3826 | 201.4288 | 33.5929 | 35.4049 | 108.8649 | ON | 16.82 | 110.2 | 20.2631 | 27.0938 | -1.4958 | 16.2524 | 1.833 | 1.833 | 4.0716 |  | OK | OK | OK | OK | 110.281 | OK | OK | OK | OK | OK
44811.8538 | 2:05 | 95 | 126.8893 | 125.3883 | 137.0319 | 36.744 | 108.3227 | 108.3227 | 17.7828 | 15.057 | 31.2674 | 31.6447 | 50 | 38.0641 | 201.2323 | 33.1565 | 35.4235 | 108.8071 | ON | 16.82 | 110.2 | 19.924 | 26.8319 | -1.763 | 16.5877 | 1.8773 | 1.8773 | 4.0924 |  | OK | OK | OK | OK | 110.0693 | OK | OK | OK | OK | OK
44811.8539 | 2:06 | 95 | 126.7036 | 125.193 | 136.7285 | 36.1877 | 108.1154 | 108.1154 | 17.5688 | 14.8628 | 31.3192 | 31.7138 | 50 | 37.9462 | 200.1452 | 33.532 | 35.3766 | 108.6187 | ON | 15.76 | 110.2 | 20.4277 | 26.5285 | -0.89719 | 16.851 | 2.0846 | 2.0846 | 4.0809 |  | OK | OK | OK | OK | 110.9436 | OK | OK | OK | OK | OK
44811.8541 | 2:06 | 95 | 126.5234 | 124.93 | 136.4709 | 35.7142 | 107.9561 | 107.9561 | 17.3611 | 14.7163 | 31.3491 | 31.7955 | 50 | 37.7449 | 200.3411 | 33.3353 | 35.3273 | 108.482 | ON | 15.76 | 110.2 | 19.9542 | 26.2709 | -1.0437 | 17.0792 | 2.2439 | 2.2439 | 4.1003 |  | OK | OK | OK | OK | 110.7634 | OK | OK | OK | OK | OK
44811.8542 | 2:06 | 95 | 126.3787 | 124.7074 | 136.2238 | 35.2371 | 107.8668 | 107.8668 | 17.1747 | 14.5035 | 31.4116 | 31.8292 | 50 | 37.5245 | 200.1267 | 33.0494 | 35.3025 | 108.3824 | ON | 15.76 | 110.2 | 19.477 | 26.0238 | -1.2566 | 17.3257 | 2.3332 | 2.3332 | 4.1135 |  | OK | OK | OK | OK | 110.6187 | OK | OK | OK | OK | OK
44811.8543 | 2:06 | 95 | 126.4247 | 124.5679 | 136.0866 | 34.7256 | 108.4006 | 108.4006 | 16.7598 | 14.2814 | 31.42 | 31.8756 | 50 | 37.45 | 205.0274 | 33.0278 | 35.2967 | 108.705 | ON | 15.76 | 112 | 18.9656 | 24.0866 | -1.4786 | 17.5942 | 3.5994 | 3.5994 | 4.2134 |  | OK | OK | OK | OK | 110.6647 | OK | OK | OK | OK | OK
44811.8544 | 2:06 | 95 | 126.849 | 125.1378 | 136.142 | 34.5923 | 109.8013 | 109.8013 | 14.7027 | 14.3347 | 31.4499 | 31.841 | 50 | 21.0989 | 206.9313 | 32.8472 | 35.2131 | 109.7962 | ON | -3.64 | 112 | 38.2323 | 24.142 | 17.9747 | 17.5063 | 2.1987 | 2.1987 | 6.191 |  | OK | OK | OK | OK | 130.489 | OK | OK | OK | OK | OK
44811.8545 | 2:06 | 95 | 126.5232 | 124.5658 | 134.2214 | 38.5478 | 106.8208 | 106.8208 | 16.5076 | 16.6315 | 31.4708 | 31.8747 | 50 | 19.1676 | 199.1775 | 33.1078 | 35.2233 | 107.6796 | ON | -6.5 | 108.3 | 45.0478 | 25.9214 | 23.1315 | 15.2432 | 1.4792 | 1.4792 | 6.3151 |  | OK | OK | OK | OK | 133.0232 | OK | OK | OK | OK | OK
44811.8546 | 2:07 | 95 | 126.4535 | 124.0653 | 133.0864 | 42.7459 | 105.0186 | 105.0186 | 19.0581 | 18.9341 | 31.4791 | 31.9227 | 50 | 16.0842 | 196.2 | 33.6729 | 35.4661 | 106.6098 | ON | -11.06 | 108.3 | 53.8059 | 24.7864 | 29.9941 | 12.9887 | 3.2814 | 3.2814 | 6.8509 |  | OK | OK | OK | OK | 137.5135 | OK | OK | OK | OK | OK
44811.8548 | 2:07 | 95 | 126.6889 | 123.9061 | 132.5188 | 45.1753 | 104.0224 | 104.0224 | 21.5987 | 20.9573 | 31.5146 | 31.9679 | 50 | 15.2775 | 193.8185 | 34.1879 | 35.681 | 106.0105 | ON | -12.65 | 106.4 | 57.8253 | 26.1188 | 33.6073 | 11.0106 | 2.3776 | 2.3776 | 6.9558 |  | OK | OK | OK | OK | 139.3389 | OK | OK | OK | OK | OK
44811.8549 | 2:07 | 95 | 127.2543 | 123.9155 | 132.3784 | 47.2726 | 104.0374 | 104.0374 | 23.8903 | 22.7454 | 31.5285 | 32.0691 | 50 | 14.73 | 193.274 | 34.5151 | 35.8165 | 105.6812 | ON | -14.28 | 106.4 | 61.5526 | 25.9784 | 37.0254 | 9.3237 | 2.3626 | 2.3626 | 7.0667 |  | OK | OK | OK | OK | 141.5343 | OK | OK | OK | OK | OK
44811.855 | 2:07 | 95 | 128.1578 | 124.1622 | 132.5213 | 48.6939 | 103.7177 | 103.7177 | 25.8186 | 24.2098 | 31.5707 | 32.1533 | 50 | 14.0009 | 193.1789 | 34.9159 | 35.9144 | 105.5713 | ON | -14.28 | 106.4 | 62.9739 | 26.1213 | 38.4898 | 7.9434 | 2.6823 | 2.6823 | 7.2429 |  | OK | OK | OK | OK | 142.4378 | OK | OK | OK | OK | OK
44811.8551 | 2:07 | 95 | 129.0821 | 124.4871 | 132.8755 | 52.0401 | 103.5405 | 103.5405 | 27.3505 | 25.4556 | 31.5762 | 32.2485 | 50 | 13.7724 | 192.6906 | 35.1592 | 36.11 | 105.4939 | ON | -15.96 | 106.4 | 68.0001 | 26.4755 | 41.4156 | 6.793 | 2.8595 | 2.8595 | 7.2839 |  | OK | OK | OK | OK | 145.0421 | OK | OK | OK | OK | OK
44811.8552 | 2:07 | 95 | 129.9662 | 124.8986 | 133.2758 | 54.3162 | 103.6613 | 103.6613 | 28.5196 | 26.4296 | 31.5864 | 32.3611 | 50 | 13.3959 | 192.6073 | 35.4317 | 36.1721 | 105.4265 | ON | -15.96 | 106.4 | 70.2762 | 26.8758 | 42.3896 | 5.9315 | 2.7387 | 2.7387 | 7.3786 |  | OK | OK | OK | OK | 145.9262 | OK | OK | OK | OK | OK
44811.8553 | 2:08 | 95 | 130.8795 | 125.3314 | 133.7529 | 55.7685 | 103.6213 | 103.6213 | 29.388 | 27.2332 | 31.6114 | 32.4681 | 50 | 13.0718 | 192.9322 | 35.5725 | 36.1716 | 105.4665 | ON | -15.96 | 106.4 | 71.7285 | 27.3529 | 43.1932 | 5.2349 | 2.7787 | 2.7787 | 7.4764 |  | OK | OK | OK | OK | 146.8395 | OK | OK | OK | OK | OK
44811.8555 | 2:08 | 95 | 131.8266 | 125.8187 | 134.2997 | 56.4525 | 103.4851 | 103.4851 | 29.9987 | 27.87 | 31.6187 | 32.5798 | 50 | 12.8348 | 193.0152 | 35.7873 | 36.2326 | 105.5285 | ON | -17.69 | 106.4 | 74.1425 | 27.8997 | 45.56 | 4.7098 | 2.9149 | 2.9149 | 7.5437 |  | OK | OK | OK | OK | 149.5166 | OK | OK | OK | OK | OK
44811.8556 | 2:08 | 95 | 132.5851 | 126.3491 | 134.8971 | 56.6176 | 103.6113 | 103.6113 | 30.4535 | 28.3619 | 31.6338 | 32.7079 | 50 | 12.4571 | 192.6798 | 35.7646 | 36.2762 | 105.5342 | ON | -17.69 | 106.4 | 74.3076 | 28.4971 | 46.0519 | 4.346 | 2.7887 | 2.7887 | 7.6363 |  | OK | OK | OK | OK | 150.2751 | OK | OK | OK | OK | OK
44811.8557 | 2:08 | 95 | 133.3245 | 126.8101 | 135.4504 | 56.4032 | 103.9086 | 103.9086 | 30.7772 | 28.7512 | 31.6579 | 32.8395 | 50 | 12.3807 | 193.2409 | 35.7777 | 36.4171 | 105.5674 | ON | -17.69 | 106.4 | 74.0932 | 29.0504 | 46.4412 | 4.0883 | 2.4914 | 2.4914 | 7.6786 |  | OK | OK | OK | OK | 151.0145 | OK | OK | OK | OK | OK
44811.8558 | 2:08 | 95 | 134.109 | 127.3915 | 136.0585 | 55.7984 | 103.7626 | 103.7626 | 31.0034 | 29.0774 | 31.6549 | 32.9769 | 50 | 12.096 | 193.6059 | 36.1402 | 36.5008 | 105.6807 | ON | -17.69 | 106.4 | 73.4884 | 29.6585 | 46.7674 | 3.8995 | 2.6374 | 2.6374 | 7.7738 |  | OK | OK | OK | OK | 151.799 | OK | OK | OK | OK | OK
44811.8559 | 2:08 | 95 | 134.8802 | 127.8738 | 136.6828 | 55.0744 | 103.6829 | 103.6829 | 31.1394 | 29.3573 | 31.6332 | 33.1188 | 50 | 11.9603 | 193.2697 | 36.2127 | 36.5322 | 105.7441 | ON | -19.46 | 106.4 | 74.5344 | 30.2828 | 48.8173 | 3.7615 | 2.7171 | 2.7171 | 7.8007 |  | OK | OK | OK | OK | 154.3402 | OK | OK | OK | OK | OK
44811.856 | 2:09 | 95 | 135.8677 | 128.2822 | 137.1277 | 54.044 | 99.9981 | 99.9981 | 30.7391 | 29.627 | 27.4998 | 33.473 | 50 | 33.2816 | 166.8679 | 36.1449 | 36.6315 | 104.8483 | OFF | 11.39 | 96.32 | 42.654 | 40.8077 | 18.237 | 3.846 | -3.6781 | -3.6781 | 3.7841
44811.8562 | 2:09 | 95 | 139.6362 | 125.736 | 133.4241 | 62.2781 | 95.0121 | 95.0121 | 28.4714 | 30.322 | 28.5891 | 33.4821 | 50 | 55.0515 | 123.6391 | 35.9626 | 36.6867 | 101.9494 | OFF | 32.77 | 75.27 | 29.5081 | 58.1541 | -2.448 | 3.1601 | -19.7421 | -19.7421 | 1.9833
44811.8563 | 2:09 | 95 | 138.6268 | 123.9014 | 125.8735 | 73.4496 | 92.5512 | 92.5512 | 31.5293 | 31.507 | 30.8454 | 33.4479 | 50 | 58.3619 | 108.5322 | 36.1623 | 36.6881 | 100.9694 | OFF | 35.28 | 67.1 | 38.1696 | 58.7735 | -3.773 | 1.9408 | -25.4512 | -25.4512 | 1.6867
44811.8564 | 2:09 | 95 | 137.4112 | 122.3266 | 119.1562 | 83.1808 | 90.5003 | 90.5003 | 31.8526 | 32.6791 | 31.3581 | 33.6608 | 50 | 59.6611 | 99.2547 | 36.2708 | 36.7244 | 100.3674 | OFF | 36.1 | 61.23 | 47.0808 | 57.9262 | -3.4209 | 0.98165 | -29.2703 | -29.2703 | 1.5325
44811.8565 | 2:09 | 95 | 136.1283 | 120.8474 | 114.1794 | 89.5467 | 89.1884 | 89.1884 | 31.8468 | 33.6529 | 31.6035 | 34.0226 | 50 | 60.5087 | 89.4422 | 36.5095 | 36.7975 | 99.9346 | OFF | 36.91 | 54.95 | 52.6367 | 59.2294 | -3.2572 | 0.36977 | -34.2384 | -34.2384 | 1.3847
44811.8566 | 2:09 | 95 | 134.8205 | 119.5319 | 110.8085 | 93.3372 | 88.2688 | 88.2688 | 31.8408 | 34.2787 | 31.6751 | 34.4104 | 50 | 61.0613 | 82.4698 | 36.7341 | 36.9573 | 99.6181 | OFF | 37.71 | 51.63 | 55.6272 | 59.1785 | -3.4313 | 0.13161 | -36.6388 | -36.6388 | 1.2826
44811.8567 | 2:10 | 95 | 133.6437 | 118.4691 | 108.5427 | 95.6271 | 87.7722 | 87.7722 | 31.8738 | 34.6931 | 31.7067 | 34.7144 | 50 | 61.5486 | 77.3504 | 36.5822 | 36.9353 | 99.4508 | OFF | 37.71 | 48.19 | 57.9171 | 60.3527 | -3.0169 | 0.02124 | -39.5822 | -39.5822 | 1.2072
44811.8568 | 2:10 | 95 | 132.5241 | 117.3844 | 107.0146 | 96.8944 | 88.0055 | 88.0055 | 31.8651 | 35.0264 | 31.73 | 34.9154 | 50 | 61.8419 | 71.5439 | 36.6927 | 37.0994 | 99.2967 | OFF | 37.71 | 44.59 | 59.1844 | 62.4246 | -2.6835 | -0.111 | -43.4155 | -43.4155 | 1.1268
44811.857 | 2:10 | 95 | 131.4651 | 116.4236 | 106.2071 | 97.1413 | 89.0307 | 89.0307 | 31.8638 | 35.107 | 31.7505 | 34.9534 | 50 | 61.874 | 67.2515 | 36.7888 | 37.106 | 99.1039 | OFF | 37.71 | 42.36 | 59.4313 | 63.8471 | -2.603 | -0.15361 | -46.6707 | -46.6707 | 1.0702
44811.8571 | 2:10 | 95 | 130.4911 | 115.5569 | 105.7027 | 96.9652 | 90.238 | 90.238 | 31.9011 | 35.1214 | 31.7696 | 34.9498 | 50 | 61.9686 | 65.633 | 36.8712 | 37.1739 | 98.9977 | OFF | 37.71 | 40.84 | 59.2552 | 64.8627 | -2.5886 | -0.17159 | -49.398 | -49.398 | 1.0478
44811.8572 | 2:10 | 95 | 129.4312 | 114.7772 | 105.3858 | 96.613 | 91.3335 | 91.3335 | 31.925 | 35.2197 | 31.7829 | 35.047 | 50 | 62.1659 | 64.6906 | 37.069 | 37.2393 | 98.7358 | OFF | 38.5 | 40.07 | 58.113 | 65.3158 | -3.2803 | -0.17271 | -51.2635 | -51.2635 | 1.0328
44811.8573 | 2:10 | 95 | 128.4974 | 114.0904 | 105.0905 | 96.4642 | 92.2902 | 92.2902 | 31.9439 | 35.3915 | 31.8189 | 35.1013 | 50 | 62.3704 | 63.8693 | 37.0891 | 37.3604 | 98.4943 | OFF | 38.5 | 39.29 | 57.9642 | 65.8005 | -3.1085 | -0.29022 | -53.0002 | -53.0002 | 1.0194
44811.8574 | 2:11 | 95 | 127.5673 | 113.4424 | 104.8514 | 96.3753 | 93.0831 | 93.0831 | 31.9748 | 35.5463 | 31.8759 | 35.2391 | 50 | 62.6603 | 63.618 | 37.1739 | 37.3987 | 98.3509 | OFF | 38.5 | 39.29 | 57.8753 | 65.5614 | -2.9537 | -0.30726 | -53.7931 | -53.7931 | 1.0124
44811.8575 | 2:11 | 95 | 126.7344 | 112.8488 | 104.6162 | 96.1721 | 93.787 | 93.787 | 32.0342 | 35.7664 | 31.9028 | 35.493 | 50 | 63.0118 | 63.873 | 37.2186 | 37.4486 | 98.1305 | OFF | 39.29 | 39.29 | 56.8821 | 65.3262 | -3.5236 | -0.27339 | -54.4969 | -54.4969 | 1.0111
44811.8577 | 2:11 | 95 | 125.9139 | 112.2872 | 104.3288 | 96.1236 | 94.1746 | 94.1746 | 32.1065 | 36.1669 | 31.9588 | 35.9145 | 50 | 63.5831 | 62.8985 | 37.3063 | 37.5851 | 97.9618 | OFF | 39.29 | 38.5 | 56.8336 | 65.8288 | -3.1231 | -0.25247 | -55.6746 | -55.6746 | 0.99125
44811.8578 | 2:11 | 95 | 125.1098 | 111.7418 | 104.0333 | 95.9314 | 94.5384 | 94.5384 | 32.1944 | 36.4249 | 32.045 | 36.407 | 50 | 63.9991 | 63.0238 | 37.5189 | 37.7375 | 97.7268 | OFF | 39.29 | 39.29 | 56.6414 | 64.7433 | -2.8651 | -0.01781 | -55.2484 | -55.2484 | 0.98761
44811.8579 | 2:11 | 95 | 124.4324 | 111.242 | 103.7694 | 95.7106 | 94.8251 | 94.8251 | 32.2934 | 36.5315 | 32.2223 | 36.8088 | 50 | 64.3556 | 63.4604 | 37.5584 | 37.7605 | 97.5162 | OFF | 40.07 | 39.29 | 55.6406 | 64.4794 | -3.5385 | 0.27736 | -55.5351 | -55.5351 | 0.98868
44811.858 | 2:11 | 95 | 123.727 | 110.7591 | 103.5287 | 95.4502 | 95.0655 | 95.0655 | 32.4812 | 36.5472 | 32.472 | 37.1656 | 50 | 64.7153 | 63.7565 | 37.7019 | 37.9181 | 97.339 | OFF | 40.07 | 39.29 | 55.3802 | 64.2387 | -3.5228 | 0.61834 | -55.7755 | -55.7755 | 0.98793
44811.8581 | 2:12 | 95 | 123.0661 | 110.3454 | 103.2818 | 95.1785 | 95.2001 | 95.2001 | 32.6657 | 36.5261 | 32.8755 | 37.4804 | 50 | 64.9992 | 64.0538 | 37.9347 | 38.067 | 97.1672 | OFF | 40.07 | 40.07 | 55.1085 | 63.2118 | -3.5439 | 0.95433 | -55.1301 | -55.1301 | 0.98814
44811.8582 | 2:12 | 95 | 122.4408 | 109.9325 | 103.0335 | 95.0392 | 95.2947 | 95.2947 | 32.7752 | 36.2296 | 33.4034 | 37.7426 | 50 | 65.2644 | 64.2656 | 37.9821 | 38.0343 | 96.9797 | OFF | 40.84 | 40.07 | 54.1992 | 62.9635 | -4.6104 | 1.513 | -55.2247 | -55.2247 | 0.98751
44811.8583 | 2:12 | 95 | 121.8353 | 109.5748 | 102.786 | 95.0081 | 95.3462 | 95.3462 | 32.9486 | 35.577 | 34.0666 | 37.9572 | 50 | 65.5353 | 64.4817 | 38.1634 | 38.1955 | 96.8598 | OFF | 40.84 | 40.07 | 54.1681 | 62.716 | -5.263 | 2.3802 | -55.2762 | -55.2762 | 0.98687
44811.8585 | 2:12 | 95 | 121.2947 | 109.2429 | 102.5744 | 95.0557 | 95.3625 | 95.3625 | 33.1745 | 35.2037 | 34.6238 | 38.1583 | 50 | 65.5606 | 64.59 | 38.3245 | 38.284 | 96.7476 | OFF | 40.84 | 40.07 | 54.2157 | 62.5044 | -5.6363 | 2.9546 | -55.2925 | -55.2925 | 0.98791
44811.8586 | 2:12 | 95 | 120.7863 | 108.9504 | 102.3564 | 95.0857 | 95.3529 | 95.3529 | 33.5895 | 35.0543 | 35.1471 | 38.3234 | 50 | 65.8838 | 64.7983 | 38.3553 | 38.3252 | 96.6181 | OFF | 40.84 | 40.07 | 54.2457 | 62.2864 | -5.7857 | 3.2692 | -55.2829 | -55.2829 | 0.98653
44811.8587 | 2:12 | 95 | 120.2756 | 108.6168 | 102.1378 | 95.0523 | 95.3319 | 95.3319 | 34.0735 | 35.2542 | 35.5709 | 38.4535 | 50 | 66.0845 | 65.059 | 38.5688 | 38.4224 | 96.4817 | OFF | 41.6 | 40.84 | 53.4523 | 61.2978 | -6.3459 | 3.1993 | -54.4919 | -54.4919 | 0.98731
44811.8588 | 2:13 | 95 | 119.7758 | 108.3148 | 101.9358 | 94.9748 | 95.3026 | 95.3026 | 34.6117 | 35.3188 | 35.9617 | 38.6239 | 50 | 66.3936 | 65.281 | 38.6262 | 38.5384 | 96.3512 | OFF | 41.6 | 40.84 | 53.3748 | 61.0958 | -6.2812 | 3.3051 | -54.4626 | -54.4626 | 0.98628
44811.8589 | 2:13 | 95 | 119.3157 | 108.0262 | 101.7315 | 94.8894 | 95.285 | 95.285 | 34.9689 | 35.3881 | 36.3121 | 38.8026 | 50 | 66.6123 | 65.4021 | 38.745 | 38.6192 | 96.2078 | OFF | 41.6 | 40.84 | 53.2894 | 60.8915 | -6.2119 | 3.4145 | -54.445 | -54.445 | 0.98512
44811.859 | 2:13 | 95 | 118.8779 | 107.7264 | 101.5582 | 94.9269 | 95.2274 | 95.2274 | 35.2582 | 35.5295 | 36.5692 | 38.9243 | 50 | 66.7569 | 65.6752 | 38.8825 | 38.7854 | 96.1062 | OFF | 41.6 | 40.84 | 53.3269 | 60.7182 | -6.0705 | 3.3948 | -54.3874 | -54.3874 | 0.98672
44811.8592 | 2:13 | 95 | 118.4394 | 107.466 | 101.4065 | 94.8997 | 95.1833 | 95.1833 | 35.5687 | 35.817 | 36.7949 | 39.0654 | 50 | 66.9476 | 65.8119 | 38.8802 | 38.8058 | 95.9815 | OFF | 41.6 | 40.84 | 53.2997 | 60.5665 | -5.783 | 3.2484 | -54.3433 | -54.3433 | 0.98609
44811.8593 | 2:13 | 95 | 118.0413 | 107.2536 | 101.2497 | 94.849 | 95.1192 | 95.1192 | 35.6985 | 35.9192 | 37.0268 | 39.1871 | 50 | 67.1744 | 65.977 | 39.0518 | 38.9038 | 95.8446 | OFF | 42.36 | 40.84 | 52.489 | 60.4097 | -6.4408 | 3.2678 | -54.2792 | -54.2792 | 0.98537
44811.8594 | 2:13 | 95 | 117.5173 | 107.0078 | 101.0638 | 94.7018 | 95.0383 | 95.0383 | 35.7731 | 36.0733 | 37.2255 | 39.3056 | 50 | 67.2305 | 66.2516 | 39.1905 | 38.9918 | 95.7159 | OFF | 42.36 | 41.6 | 52.3418 | 59.4638 | -6.2867 | 3.2323 | -53.4383 | -53.4383 | 0.98805
44811.8595 | 2:14 | 95 | 117.1537 | 106.7448 | 100.8758 | 94.7213 | 94.9865 | 94.9865 | 35.8956 | 36.2689 | 37.3765 | 39.4106 | 50 | 67.4655 | 66.4017 | 39.189 | 39.0951 | 95.6353 | OFF | 42.36 | 41.6 | 52.3613 | 59.2758 | -6.0911 | 3.1417 | -53.3865 | -53.3865 | 0.98705
44811.8596 | 2:14 | 95 | 116.8031 | 106.5324 | 100.7159 | 94.6573 | 94.911 | 94.911 | 36.0511 | 36.3297 | 37.5331 | 39.5492 | 50 | 67.4406 | 66.3561 | 39.3229 | 39.1885 | 95.4916 | OFF | 42.36 | 41.6 | 52.2973 | 59.1159 | -6.0303 | 3.2195 | -53.311 | -53.311 | 0.9868
44811.8597 | 2:14 | 95 | 116.4288 | 106.2844 | 100.5364 | 94.5177 | 94.8684 | 94.8684 | 36.2285 | 36.5943 | 37.6731 | 39.6149 | 50 | 67.6456 | 66.547 | 39.3975 | 39.2701 | 95.3982 | OFF | 42.36 | 41.6 | 52.1577 | 58.9364 | -5.7657 | 3.0205 | -53.2683 | -53.2683 | 0.98666
44811.8599 | 2:14 | 95 | 117.6721 | 106.3475 | 110.3636 | 81.7501 | 95.0016 | 95.0016 | 36.3336 | 36.7699 | 36.8623 | 36.8056 | 50 | 62.7762 | 125.4232 | 39.5628 | 39.373 | 95.5857 | OFF | 38.5 | 77.84 | 43.2501 | 32.5236 | -1.7301 | 0.03572 | -17.1616 | -17.1616 | 1.8086
44811.86 | 2:14 | 95 | 119.094 | 107.9835 | 126.7535 | 62.6477 | 97.7171 | 97.7171 | 31.415 | 33.1346 | 31.5525 | 34.5994 | 50 | 53.9902 | 176.9415 | 39.3265 | 39.249 | 99.459 | ON | 31.06 | 100.5 | 31.5877 | 26.2535 | 2.0746 | 1.4648 | 2.7829 | 2.7829 | 2.7899 |  | OK | OK | OK | OK | 88.034 | OK | OK | OK | OK | OK
44811.8601 | 2:14 | 95 | 117.9506 | 112.4809 | 128.1013 | 57.803 | 102.1073 | 102.1073 | 29.8252 | 29.3731 | 29.499 | 33.5056 | 50 | 52.8806 | 186.4849 | 38.6944 | 39.0113 | 102.967 | ON | 30.19 | 104.4 | 27.613 | 23.7013 | -0.81689 | 4.1325 | 2.2927 | 2.2927 | 2.977 |  | OK | OK | OK | OK | 87.7606 | OK | OK | OK | OK | OK
44811.8602 | 2:15 | 95 | 117.2845 | 114.6034 | 127.3636 | 55.2983 | 103.6486 | 103.6486 | 30.016 | 30.5824 | 28.7783 | 31.852 | 50 | 52.5866 | 190.319 | 38.2747 | 38.8287 | 104.3948 | ON | 30.19 | 106.4 | 25.1083 | 20.9636 | 0.3924 | 1.2696 | 2.7514 | 2.7514 | 3.0469 |  | OK | OK | OK | OK | 87.0945 | OK | OK | OK | OK | OK
44811.8603 | 2:15 | 95 | 116.7694 | 115.5071 | 126.9557 | 55.0159 | 104.1608 | 104.1608 | 30.2821 | 28.1629 | 28.2059 | 27.9288 | 50 | 52.1654 | 190.966 | 38.0406 | 38.5145 | 104.9988 | ON | 30.19 | 106.4 | 24.8259 | 20.5557 | -2.0271 | -0.23403 | 2.2392 | 2.2392 | 3.0758 |  | OK | OK | OK | OK | 86.5794 | OK | OK | OK | OK | OK
44811.8604 | 2:15 | 95 | 116.8532 | 116.1936 | 127.1186 | 55.4116 | 104.5766 | 104.5766 | 30.0909 | 27.9049 | 27.6722 | 27.0713 | 50 | 51.8803 | 191.8842 | 37.8857 | 38.3415 | 105.4076 | ON | 29.31 | 106.4 | 26.1016 | 20.7186 | -1.405 | -0.83368 | 1.8234 | 1.8234 | 3.1028 |  | OK | OK | OK | OK | 87.5432 | OK | OK | OK | OK | OK
44811.8605 | 2:15 | 95 | 117.424 | 116.961 | 127.537 | 58.9373 | 104.93 | 104.93 | 29.9997 | 28.8751 | 27.2304 | 26.7155 | 50 | 51.5459 | 193.1399 | 37.8766 | 38.2194 | 105.7827 | ON | 29.31 | 106.4 | 29.6273 | 21.137 | -0.4349 | -2.1596 | 1.47 | 1.47 | 3.1374 |  | OK | OK | OK | OK | 88.114 | OK | OK | OK | OK | OK
44811.8607 | 2:15 | 95 | 118.1974 | 117.7208 | 128.0717 | 61.8985 | 105.1933 | 105.1933 | 29.7007 | 30.3331 | 26.7942 | 26.4476 | 50 | 51.2366 | 193.5213 | 37.7776 | 38.0966 | 106.0647 | ON | 29.31 | 106.4 | 32.5885 | 21.6717 | 1.0231 | -3.8855 | 1.2067 | 1.2067 | 3.1579 |  | OK | OK | OK | OK | 88.8874 | OK | OK | OK | OK | OK
44811.8608 | 2:15 | 95 | 119.0958 | 118.4325 | 128.696 | 63.7068 | 105.523 | 105.523 | 29.0821 | 30.9329 | 26.3856 | 26.196 | 50 | 51.0012 | 194.2059 | 37.9502 | 38.0273 | 106.397 | ON | 29.31 | 106.4 | 34.3968 | 22.296 | 1.6229 | -4.737 | 0.877 | 0.877 | 3.1796 |  | OK | Low Charge | OK | OK | 89.7858 | OK | OK | OK | OK | OK
44811.8609 | 2:16 | 95 | 120.0247 | 119.171 | 129.4073 | 64.9149 | 105.8232 | 105.8232 | 28.5564 | 31.1066 | 26.0021 | 26.1458 | 50 | 50.7827 | 195.1623 | 37.856 | 37.9092 | 106.6972 | ON | 28.42 | 108.3 | 36.4949 | 21.1073 | 2.6866 | -4.9608 | 2.4768 | 2.4768 | 3.2049 |  | OK | OK | OK | OK | 91.6047 | OK | OK | OK | OK | OK
44811.861 | 2:16 | 95 | 120.7987 | 119.8027 | 130.0732 | 65.9449 | 105.9192 | 105.9192 | 28.3718 | 31.0881 | 25.851 | 26.4532 | 50 | 50.5285 | 194.9185 | 37.8026 | 37.9036 | 106.869 | ON | 28.42 | 106.4 | 37.5249 | 23.6732 | 2.6681 | -4.6349 | 0.4808 | 0.4808 | 3.2136 |  | OK | Low Charge | OK | OK | 92.3787 | OK | OK | OK | OK | OK
44811.8611 | 2:16 | 95 | 121.6129 | 120.3767 | 130.7546 | 66.3833 | 105.9492 | 105.9492 | 28.2145 | 30.8716 | 25.7335 | 26.5942 | 50 | 50.5077 | 195.0186 | 37.6651 | 37.8072 | 106.9164 | ON | 28.42 | 108.3 | 37.9633 | 22.4546 | 2.4516 | -4.2774 | 2.3508 | 2.3508 | 3.2162 |  | OK | OK | OK | OK | 93.1929 | OK | OK | OK | OK | OK
44811.8612 | 2:16 | 95 | 122.2289 | 120.9079 | 131.4016 | 67.0936 | 105.9391 | 105.9391 | 28.12 | 30.5785 | 25.5481 | 26.5041 | 50 | 50.3344 | 195.1317 | 37.6382 | 37.703 | 106.9903 | ON | 28.42 | 108.3 | 38.6736 | 23.1016 | 2.1585 | -4.0744 | 2.3609 | 2.3609 | 3.2265 |  | OK | OK | OK | OK | 93.8089 | OK | OK | OK | OK | OK
44811.8614 | 2:16 | 95 | 122.8946 | 121.5023 | 132.0945 | 67.8078 | 106.0412 | 106.0412 | 27.9916 | 30.311 | 25.3062 | 25.5916 | 50 | 50.0162 | 195.2777 | 37.492 | 37.6035 | 107.1082 | ON | 28.42 | 108.3 | 39.3878 | 23.7945 | 1.891 | -4.7195 | 2.2588 | 2.2588 | 3.2446 |  | OK | OK | OK | OK | 94.4746 | OK | OK | OK | OK | OK
44811.8615 | 2:16 | 95 | 123.5322 | 122.014 | 132.8157 | 68.4179 | 106.1285 | 106.1285 | 27.8459 | 29.7374 | 25.0599 | 25.3695 | 50 | 49.824 | 195.3878 | 37.3923 | 37.6066 | 107.2105 | ON | 27.51 | 108.3 | 40.9079 | 24.5157 | 2.2274 | -4.368 | 2.1715 | 2.1715 | 3.256 |  | OK | OK | OK | OK | 96.0222 | OK | OK | OK | OK | OK
44811.8616 | 2:17 | 95 | 124.1393 | 122.536 | 133.4682 | 68.8516 | 106.1887 | 106.1887 | 27.7154 | 27.8809 | 24.8539 | 25.6504 | 50 | 49.5825 | 195.5481 | 37.3212 | 37.394 | 107.2844 | ON | 27.51 | 108.3 | 41.3415 | 25.1682 | 0.37091 | -2.2305 | 2.1113 | 2.1113 | 3.2707 |  | OK | OK | OK | OK | 96.6293 | OK | OK | OK | OK | OK
44811.8617 | 2:17 | 95 | 124.7422 | 123.0677 | 134.1607 | 69.4059 | 106.2323 | 106.2323 | 27.379 | 25.8405 | 24.6198 | 25.868 | 50 | 49.2822 | 195.4074 | 37.1812 | 37.3293 | 107.3474 | ON | 27.51 | 108.3 | 41.8959 | 25.8607 | -1.6695 | 0.02744 | 2.0677 | 2.0677 | 3.2838 |  | OK | OK | OK | OK | 97.2322 | OK | OK | OK | OK | OK
44811.8618 | 2:17 | 95 | 125.3906 | 123.6028 | 134.809 | 69.9472 | 106.2923 | 106.2923 | 27.0504 | 25.3673 | 24.4181 | 25.961 | 50 | 48.9802 | 195.9049 | 36.9595 | 37.2721 | 107.4129 | ON | 26.6 | 108.3 | 43.3472 | 26.509 | -1.2327 | 0.59373 | 2.0077 | 2.0077 | 3.3072 |  | OK | OK | OK | OK | 98.7906 | OK | OK | OK | OK | OK
44811.8619 | 2:17 | 95 | 125.9584 | 124.0498 | 135.4603 | 70.2589 | 106.399 | 106.399 | 26.82 | 25.173 | 24.2798 | 25.9224 | 50 | 49.0868 | 196.1469 | 36.8677 | 37.1803 | 107.5315 | ON | 27.51 | 108.3 | 42.7489 | 27.1603 | -2.337 | 0.74938 | 1.901 | 1.901 | 3.3055 |  | OK | OK | OK | OK | 98.4484 | OK | OK | OK | OK | OK
44811.8621 | 2:17 | 95 | 126.5076 | 124.5693 | 136.1295 | 70.2812 | 106.5099 | 106.5099 | 26.5548 | 24.8908 | 24.1094 | 25.8123 | 50 | 48.5878 | 196.1382 | 36.8961 | 37.0395 | 107.6515 | ON | 26.6 | 108.3 | 43.6812 | 27.8295 | -1.7092 | 0.92149 | 1.7901 | 1.7901 | 3.3314 |  | OK | OK | OK | OK | 99.9076 | OK | OK | OK | OK | OK
44811.8622 | 2:17 | 95 | 127.0377 | 125.0414 | 136.7448 | 70.2919 | 106.6068 | 106.6068 | 26.2747 | 24.66 | 23.928 | 25.6955 | 50 | 48.4481 | 196.3235 | 36.7108 | 36.9373 | 107.7431 | ON | 26.6 | 108.3 | 43.6919 | 28.4448 | -1.94 | 1.0355 | 1.6932 | 1.6932 | 3.3417 |  | OK | OK | OK | OK | 100.4377 | OK | OK | OK | OK | OK
44811.8623 | 2:18 | 95 | 127.4924 | 125.4846 | 137.3275 | 70.2794 | 106.7249 | 106.7249 | 26.0633 | 24.4905 | 23.817 | 25.5521 | 50 | 48.3808 | 196.5984 | 36.5762 | 36.8616 | 107.8992 | ON | 26.6 | 108.3 | 43.6794 | 29.0275 | -2.1095 | 1.0616 | 1.5751 | 1.5751 | 3.3496 |  | OK | OK | OK | OK | 100.8924 | OK | OK | OK | OK | OK
44811.8624 | 2:18 | 95 | 127.979 | 125.8798 | 137.8712 | 70.0659 | 106.9466 | 106.9466 | 25.8126 | 24.2346 | 23.5743 | 25.4147 | 50 | 48.0301 | 197.5792 | 36.5625 | 36.7265 | 108.0444 | ON | 26.6 | 108.3 | 43.4659 | 29.5712 | -2.3654 | 1.1801 | 1.3534 | 1.3534 | 3.384 |  | OK | OK | OK | OK | 101.379 | OK | OK | OK | OK | OK
44811.8625 | 2:18 | 95 | 128.54 | 126.3343 | 138.4028 | 70.1014 | 107.0974 | 107.0974 | 25.5915 | 24.0706 | 23.453 | 25.2584 | 50 | 48.0162 | 197.7803 | 36.4406 | 36.691 | 108.2238 | ON | 26.6 | 108.3 | 43.5014 | 30.1028 | -2.5294 | 1.1878 | 1.2026 | 1.2026 | 3.388 |  | OK | OK | OK | OK | 101.94 | OK | OK | OK | OK | OK
44811.8626 | 2:18 | 95 | 128.9732 | 126.6621 | 138.9048 | 70.1404 | 107.1936 | 107.1936 | 25.3964 | 23.8579 | 23.2908 | 25.1359 | 50 | 47.6822 | 198.3143 | 36.3699 | 36.6269 | 108.313 | ON | 25.68 | 108.3 | 44.4604 | 30.6048 | -1.8221 | 1.278 | 1.1064 | 1.1064 | 3.4147 |  | OK | OK | OK | OK | 103.2932 | OK | OK | OK | OK | OK
44811.8627 | 2:18 | 95 | 129.4712 | 127.0996 | 139.3915 | 70.2125 | 107.3006 | 107.3006 | 25.1944 | 23.7077 | 23.3523 | 25.0185 | 50 | 47.6187 | 198.5079 | 36.2366 | 36.5263 | 108.4313 | ON | 25.68 | 108.3 | 44.5325 | 31.0915 | -1.9723 | 1.3108 | 0.9994 | 0.9994 | 3.4212 |  | OK | Low Charge | OK | OK | 103.7912 | OK | OK | OK | OK | OK
44811.8629 | 2:18 | 95 | 129.8633 | 127.502 | 139.8466 | 70.3682 | 107.4947 | 107.4947 | 25.0415 | 23.6027 | 23.9829 | 25.069 | 50 | 47.4142 | 198.5477 | 36.1163 | 36.4804 | 108.5805 | ON | 25.68 | 108.3 | 44.6882 | 31.5466 | -2.0773 | 1.4663 | 0.8053 | 0.8053 | 3.4332 |  | OK | Low Charge | OK | OK | 104.1833 | OK | OK | OK | OK | OK
44811.863 | 2:19 | 95 | 130.1459 | 127.8553 | 140.3116 | 70.2563 | 107.655 | 107.655 | 24.8508 | 23.41 | 23.5419 | 25.0066 | 50 | 47.1159 | 199.2771 | 36.24 | 36.3417 | 108.7312 | ON | 25.68 | 108.3 | 44.5763 | 32.0116 | -2.27 | 1.5966 | 0.645 | 0.645 | 3.4615 |  | OK | Low Charge | OK | OK | 104.4659 | OK | OK | OK | OK | OK
44811.8631 | 2:19 | 95 | 130.6154 | 128.2329 | 140.812 | 70.3607 | 107.8902 | 107.8902 | 24.8322 | 23.4142 | 23.3625 | 25.2279 | 50 | 47.2456 | 199.715 | 36.1243 | 36.3645 | 108.9487 | ON | 25.68 | 108.3 | 44.6807 | 32.512 | -2.2658 | 1.8136 | 0.4098 | 0.4098 | 3.4613 |  | OK | Low Charge | OK | OK | 104.9354 | OK | OK | OK | OK | OK
44811.8632 | 2:19 | 95 | 130.9905 | 128.533 | 141.2644 | 70.4613 | 108.0948 | 108.0948 | 24.6765 | 23.2951 | 23.1676 | 26.0013 | 50 | 47.1386 | 200.1712 | 35.9709 | 36.3254 | 109.1195 | ON | 25.68 | 110.2 | 44.7813 | 31.0644 | -2.3849 | 2.7063 | 2.1052 | 2.1052 | 3.4747 |  | OK | OK | OK | OK | 105.3105 | OK | OK | OK | OK | OK
44811.8633 | 2:19 | 95 | 131.3476 | 128.919 | 141.7175 | 70.4365 | 108.2807 | 108.2807 | 24.6127 | 23.2364 | 23.1996 | 26.977 | 50 | 47.0195 | 200.7538 | 35.8944 | 36.4245 | 109.2598 | ON | 25.68 | 110.2 | 44.7565 | 31.5175 | -2.4436 | 3.7406 | 1.9193 | 1.9193 | 3.4909 |  | OK | OK | OK | OK | 105.6676 | OK | OK | OK | OK | OK
44811.8634 | 2:19 | 95 | 131.634 | 129.1991 | 142.0558 | 70.2025 | 108.3172 | 108.3172 | 24.3536 | 22.9976 | 23.0968 | 27.5043 | 50 | 46.8705 | 200.8746 | 36.0894 | 36.4108 | 109.3037 | ON | 24.74 | 110.2 | 45.4625 | 31.8558 | -1.7424 | 4.5067 | 1.8828 | 1.8828 | 3.5013 |  | OK | OK | OK | OK | 106.894 | OK | OK | OK | OK | OK
44811.8636 | 2:19 | 95 | 131.9198 | 129.4061 | 142.3295 | 69.9857 | 108.1968 | 108.1968 | 24.2871 | 23.0238 | 23.1062 | 27.6219 | 50 | 46.7436 | 200.473 | 35.8792 | 36.3853 | 109.2222 | ON | 24.74 | 110.2 | 45.2457 | 32.1295 | -1.7162 | 4.5981 | 2.0032 | 2.0032 | 3.502 |  | OK | OK | OK | OK | 107.1798 | OK | OK | OK | OK | OK
44811.8637 | 2:20 | 95 | 132.0357 | 129.5988 | 142.5552 | 69.7567 | 108.0203 | 108.0203 | 24.0847 | 22.8103 | 23.0198 | 27.5314 | 50 | 46.8728 | 199.875 | 35.7793 | 36.3233 | 109.096 | ON | 24.74 | 108.3 | 45.0168 | 34.2552 | -1.9297 | 4.7211 | 0.2797 | 0.2797 | 3.4849 |  | OK | Low Charge | OK | OK | 107.2957 | OK | OK | OK | OK | OK
44811.8638 | 2:20 | 95 | 132.151 | 129.736 | 142.7071 | 69.6985 | 107.8052 | 107.8052 | 24.0161 | 22.7142 | 22.9272 | 27.2803 | 50 | 46.5517 | 199.2278 | 35.7083 | 36.2511 | 108.9174 | ON | 24.74 | 108.3 | 44.9585 | 34.4071 | -2.0258 | 4.5661 | 0.4948 | 0.4948 | 3.4926 |  | OK | Low Charge | OK | OK | 107.411 | OK | OK | OK | OK | OK
44811.8639 | 2:20 | 95 | 132.3573 | 129.7297 | 142.9029 | 69.7208 | 107.7138 | 107.7138 | 23.9209 | 22.6756 | 22.7853 | 26.9904 | 50 | 46.2543 | 199.2425 | 35.6164 | 36.1592 | 108.8041 | ON | 24.74 | 108.3 | 44.9808 | 34.6029 | -2.0644 | 4.3148 | 0.5862 | 0.5862 | 3.5099 |  | OK | Low Charge | OK | OK | 107.6173 | OK | OK | OK | OK | OK
44811.864 | 2:20 | 95 | 132.4228 | 129.7812 | 143.0703 | 69.8518 | 107.574 | 107.574 | 23.7006 | 22.503 | 22.692 | 26.7087 | 50 | 46.382 | 198.7613 | 35.6137 | 36.0921 | 108.6861 | ON | 24.74 | 108.3 | 45.1118 | 34.7703 | -2.237 | 4.2057 | 0.726 | 0.726 | 3.4947 |  | OK | Low Charge | OK | OK | 107.6828 | OK | OK | OK | OK | OK
44811.8641 | 2:20 | 95 | 132.5679 | 129.8674 | 143.1906 | 70.0619 | 107.4773 | 107.4773 | 23.5247 | 22.361 | 22.5688 | 26.4258 | 50 | 46.2763 | 198.4958 | 35.4994 | 35.9785 | 108.5877 | ON | 24.74 | 108.3 | 45.3219 | 34.8906 | -2.379 | 4.0647 | 0.8227 | 0.8227 | 3.4964 |  | OK | Low Charge | OK | OK | 107.8279 | OK | OK | OK | OK | OK
44811.8643 | 2:20 | 95 | 132.6166 | 129.9636 | 143.3371 | 70.0782 | 107.4169 | 107.4169 | 23.522 | 22.3155 | 22.4897 | 26.1864 | 50 | 46.0106 | 198.251 | 35.5451 | 35.983 | 108.5546 | ON | 24.74 | 108.3 | 45.3382 | 35.0371 | -2.4245 | 3.8709 | 0.8831 | 0.8831 | 3.5076 |  | OK | Low Charge | OK | OK | 107.8766 | OK | OK | OK | OK | OK
44811.8644 | 2:21 | 95 | 132.6489 | 130.0527 | 143.4537 | 70.148 | 107.3462 | 107.3462 | 23.33 | 22.2051 | 22.2873 | 25.9273 | 50 | 45.9538 | 198.1648 | 35.5165 | 35.8797 | 108.447 | ON | 23.8 | 108.3 | 46.3481 | 35.1537 | -1.5949 | 3.7222 | 0.9538 | 0.9538 | 3.5095 |  | OK | Low Charge | OK | OK | 108.8489 | OK | OK | OK | OK | OK
44811.8645 | 2:21 | 95 | 132.6508 | 130.0305 | 143.5793 | 70.336 | 107.2635 | 107.2635 | 23.1859 | 22.0222 | 22.1964 | 25.7134 | 50 | 45.8039 | 198.0171 | 35.448 | 35.733 | 108.3876 | ON | 23.8 | 108.3 | 46.536 | 35.2793 | -1.7778 | 3.6911 | 1.0365 | 1.0365 | 3.5158 |  | OK | OK | OK | OK | 108.8508 | OK | OK | OK | OK | OK
44811.8646 | 2:21 | 95 | 132.7663 | 130.1574 | 143.7374 | 70.3814 | 107.2214 | 107.2214 | 23.1105 | 22.0249 | 22.1416 | 25.4703 | 50 | 46.0555 | 197.5625 | 35.1764 | 35.7167 | 108.3363 | ON | 24.74 | 108.3 | 45.6414 | 35.4374 | -2.7151 | 3.4454 | 1.0786 | 1.0786 | 3.4937 |  | OK | OK | OK | OK | 108.0263 | OK | OK | OK | OK | OK
44811.8647 | 2:21 | 95 | 132.7779 | 130.1895 | 143.7836 | 70.3475 | 107.0186 | 107.0186 | 22.91 | 21.8039 | 21.9654 | 25.2567 | 50 | 45.8378 | 197.2769 | 35.035 | 35.6174 | 108.1685 | ON | 23.8 | 108.3 | 46.5475 | 35.4836 | -1.9961 | 3.4527 | 1.2814 | 1.2814 | 3.5016 |  | OK | OK | OK | OK | 108.9779 | OK | OK | OK | OK | OK
44811.8648 | 2:21 | 95 | 132.9182 | 130.1798 | 143.8323 | 70.374 | 106.9391 | 106.9391 | 22.8661 | 21.8085 | 21.9496 | 25.0803 | 50 | 45.5956 | 197.5309 | 35.131 | 35.4871 | 108.0768 | ON | 23.8 | 108.3 | 46.574 | 35.5323 | -1.9915 | 3.2717 | 1.3609 | 1.3609 | 3.5198 |  | OK | OK | OK | OK | 109.1182 | OK | OK | OK | OK | OK
44811.8649 | 2:21 | 95 | 132.9171 | 130.2583 | 143.8995 | 70.4153 | 106.8693 | 106.8693 | 22.7518 | 21.6651 | 21.7291 | 24.9095 | 50 | 45.3683 | 196.7388 | 35.0839 | 35.4354 | 108.0393 | ON | 23.8 | 108.3 | 46.6153 | 35.5995 | -2.1349 | 3.2444 | 1.4307 | 1.4307 | 3.52 |  | OK | OK | OK | OK | 109.1171 | OK | OK | OK | OK | OK
44811.8651 | 2:22 | 95 | 132.9708 | 130.2939 | 144.0472 | 70.5515 | 106.831 | 106.831 | 22.5941 | 21.5788 | 21.7284 | 24.7024 | 50 | 45.2776 | 196.8798 | 35.0487 | 35.3039 | 107.9789 | ON | 23.8 | 108.3 | 46.7515 | 35.7472 | -2.2212 | 3.1236 | 1.469 | 1.469 | 3.5276 |  | OK | OK | OK | OK | 109.1708 | OK | OK | OK | OK | OK
44811.8652 | 2:22 | 95 | 133.0011 | 130.3326 | 144.0924 | 70.5913 | 106.7788 | 106.7788 | 22.4536 | 21.4192 | 21.5172 | 24.5374 | 50 | 45.1593 | 196.403 | 34.9682 | 35.1711 | 107.8936 | ON | 23.8 | 108.3 | 46.7913 | 35.7924 | -2.3808 | 3.1182 | 1.5212 | 1.5212 | 3.5267 |  | OK | OK | OK | OK | 109.2011 | OK | OK | OK | OK | OK
44811.8653 | 2:22 | 95 | 133.0615 | 130.3252 | 144.1461 | 70.6473 | 106.6679 | 106.6679 | 22.3817 | 21.3587 | 21.3742 | 24.3983 | 50 | 45.1397 | 196.4961 | 34.8709 | 35.1497 | 107.7964 | ON | 23.8 | 108.3 | 46.8473 | 35.8461 | -2.4413 | 3.0396 | 1.6321 | 1.6321 | 3.5294 |  | OK | OK | OK | OK | 109.2615 | OK | OK | OK | OK | OK
44811.8654 | 2:22 | 95 | 133.0286 | 130.3382 | 144.2381 | 71.0309 | 106.6202 | 106.6202 | 22.207 | 21.1922 | 21.3706 | 24.2898 | 50 | 44.9151 | 196.1576 | 34.8249 | 35.1256 | 107.7642 | ON | 22.84 | 108.3 | 48.1909 | 35.9381 | -1.6478 | 3.0976 | 1.6798 | 1.6798 | 3.537 |  | OK | OK | OK | OK | 110.1886 | OK | OK | OK | OK | OK
44811.8655 | 2:22 | 95 | 133.057 | 130.3746 | 144.3031 | 71.6196 | 106.5252 | 106.5252 | 22.1209 | 21.111 | 21.2523 | 24.1654 | 50 | 45.1623 | 195.6654 | 34.7722 | 35.0931 | 107.6534 | ON | 23.8 | 108.3 | 47.8195 | 36.0031 | -2.689 | 3.0544 | 1.7748 | 1.7748 | 3.5142 |  | OK | OK | OK | OK | 109.257 | OK | OK | OK | OK | OK
44811.8656 | 2:22 | 95 | 133.1354 | 130.3901 | 144.3131 | 71.7773 | 106.8346 | 106.8346 | 22.0328 | 20.9824 | 21.1456 | 24.073 | 50 | 44.8645 | 198.6969 | 34.5824 | 34.9633 | 107.7816 | ON | 22.84 | 108.3 | 48.9374 | 36.0131 | -1.8576 | 3.0905 | 1.4654 | 1.4654 | 3.5826 |  | OK | OK | OK | OK | 110.2954 | OK | OK | OK | OK | OK
44811.8658 | 2:23 | 95 | 133.4822 | 130.6369 | 144.4963 | 71.8841 | 108.2352 | 108.2352 | 21.8945 | 20.5428 | 21.2953 | 24.0827 | 50 | 43.3794 | 202.2644 | 34.5336 | 34.882 | 108.8508 | ON | 21.87 | 110.2 | 50.0141 | 34.2963 | -1.3272 | 3.5399 | 1.9648 | 1.9648 | 3.7357 |  | OK | OK | OK | OK | 111.6122 | OK | OK | OK | OK | OK
44811.8659 | 2:23 | 95 | 133.6804 | 130.8615 | 144.625 | 70.4072 | 108.6027 | 108.6027 | 21.3941 | 19.4596 | 22.2688 | 24.4978 | 50 | 42.6516 | 202.6977 | 34.5025 | 34.8066 | 109.1278 | ON | 20.88 | 110.2 | 49.5272 | 34.425 | -1.4204 | 5.0383 | 1.5973 | 1.5973 | 3.7906 |  | OK | OK | OK | OK | 112.8004 | OK | OK | OK | OK | OK
44811.866 | 2:23 | 95 | 133.7196 | 130.8914 | 144.601 | 66.136 | 108.5812 | 108.5812 | 21.0738 | 19.044 | 23.4988 | 25.3286 | 50 | 42.1079 | 202.4209 | 34.3462 | 34.9665 | 109.1189 | ON | 20.88 | 110.2 | 45.256 | 34.401 | -1.836 | 6.2846 | 1.6188 | 1.6188 | 3.822 |  | OK | OK | OK | OK | 112.8396 | OK | OK | OK | OK | OK
44811.8661 | 2:23 | 95 | 133.5995 | 130.7464 | 144.385 | 57.4931 | 108.4555 | 108.4555 | 20.7417 | 18.6513 | 24.8859 | 26.3299 | 50 | 41.9492 | 201.7469 | 34.1295 | 35.1133 | 109.0064 | ON | 19.89 | 110.2 | 37.6031 | 34.185 | -1.2387 | 7.6786 | 1.7445 | 1.7445 | 3.8208 |  | OK | OK | OK | OK | 113.7095 | OK | OK | OK | OK | OK
44811.8662 | 2:23 | 95 | 133.124 | 130.2261 | 143.8459 | 51.8011 | 108.3054 | 108.3054 | 20.4544 | 18.3418 | 26.1907 | 27.2725 | 50 | 41.6225 | 201.5685 | 34.0896 | 35.1832 | 108.89 | ON | 19.89 | 110.2 | 31.9111 | 33.6459 | -1.5482 | 8.9307 | 1.8946 | 1.8946 | 3.8398 |  | OK | OK | OK | OK | 113.234 | OK | OK | OK | OK | OK
44811.8663 | 2:23 | 95 | 132.4254 | 129.7287 | 143.1333 | 48.5431 | 108.1876 | 108.1876 | 20.2015 | 18.0169 | 27.2835 | 28.0999 | 50 | 41.2162 | 201.4041 | 34.2381 | 35.2742 | 108.7965 | ON | 19.89 | 110.2 | 28.6531 | 32.9333 | -1.8732 | 10.083 | 2.0124 | 2.0124 | 3.8648 |  | OK | OK | OK | OK | 112.5354 | OK | OK | OK | OK | OK
44811.8664 | 2:24 | 95 | 131.5803 | 129.1673 | 142.5032 | 46.9287 | 108.1746 | 108.1746 | 19.9706 | 17.7995 | 28.226 | 28.8099 | 50 | 41.0437 | 201.2132 | 34.0478 | 35.2965 | 108.7707 | ON | 19.89 | 110.2 | 27.0387 | 32.3032 | -2.0905 | 11.0103 | 2.0254 | 2.0254 | 3.8733 |  | OK | OK | OK | OK | 111.6903 | OK | OK | OK | OK | OK
44811.8666 | 2:24 | 95 | 130.8144 | 128.5086 | 141.6948 | 45.6675 | 107.9848 | 107.9848 | 19.7346 | 17.6203 | 28.9774 | 29.4456 | 50 | 40.8246 | 200.5573 | 34.0409 | 35.3628 | 108.658 | ON | 18.88 | 110.2 | 26.7875 | 31.4948 | -1.2597 | 11.8253 | 2.2152 | 2.2152 | 3.8768 |  | OK | OK | OK | OK | 111.9344 | OK | OK | OK | OK | OK
44811.8667 | 2:24 | 95 | 130.0428 | 127.8648 | 140.9152 | 44.5416 | 107.9557 | 107.9557 | 19.4948 | 17.3136 | 29.5614 | 29.9098 | 50 | 40.5789 | 200.6916 | 33.9557 | 35.2957 | 108.5957 | ON | 18.88 | 110.2 | 25.6616 | 30.7152 | -1.5664 | 12.5962 | 2.2443 | 2.2443 | 3.8964 |  | OK | OK | OK | OK | 111.1628 | OK | OK | OK | OK | OK
44811.8668 | 2:24 | 95 | 129.3376 | 127.3172 | 140.2094 | 43.4408 | 107.9379 | 107.9379 | 19.289 | 17.1281 | 29.9842 | 30.3101 | 50 | 40.4128 | 200.5052 | 33.8861 | 35.3982 | 108.5943 | ON | 18.88 | 110.2 | 24.5608 | 30.0094 | -1.7519 | 13.1821 | 2.2621 | 2.2621 | 3.9048 |  | OK | OK | OK | OK | 110.4576 | OK | OK | OK | OK | OK
44811.8669 | 2:24 | 95 | 128.875 | 126.8926 | 139.6472 | 42.4965 | 108.023 | 108.023 | 19.114 | 16.9648 | 30.3102 | 30.6141 | 50 | 40.2485 | 201.0967 | 33.6447 | 35.3664 | 108.6628 | ON | 18.88 | 110.2 | 23.6165 | 29.4472 | -1.9152 | 13.6493 | 2.177 | 2.177 | 3.9273 |  | OK | OK | OK | OK | 109.995 | OK | OK | OK | OK | OK
44811.867 | 2:24 | 95 | 128.4222 | 126.4906 | 139.0815 | 41.998 | 107.8878 | 107.8878 | 18.8828 | 16.7625 | 30.5644 | 30.8694 | 50 | 40.1171 | 200.6178 | 33.5554 | 35.3158 | 108.5446 | ON | 18.88 | 110.2 | 23.118 | 28.8815 | -2.1175 | 14.1069 | 2.3122 | 2.3122 | 3.9279 |  | OK | OK | OK | OK | 109.5422 | OK | OK | OK | OK | OK
44811.8671 | 2:25 | 95 | 127.8924 | 126.0923 | 138.4742 | 41.5201 | 107.6979 | 107.6979 | 18.6909 | 16.5337 | 30.7433 | 31.0375 | 50 | 39.8015 | 200.004 | 33.617 | 35.3521 | 108.3974 | ON | 17.86 | 110.2 | 23.6601 | 28.2742 | -1.3263 | 14.5038 | 2.5021 | 2.5021 | 3.9394 |  | OK | OK | OK | OK | 110.0324 | OK | OK | OK | OK | OK
44811.8673 | 2:25 | 95 | 127.5424 | 125.7312 | 138.0076 | 41.2475 | 107.5918 | 107.5918 | 18.4862 | 16.3563 | 30.8806 | 31.2032 | 50 | 39.6973 | 199.4613 | 33.4438 | 35.3242 | 108.2871 | ON | 17.86 | 108.3 | 23.3875 | 29.7076 | -1.5037 | 14.8469 | 0.7082 | 0.7082 | 3.937 |  | OK | Low Charge | OK | OK | 109.6824 | OK | OK | OK | OK | OK
44811.8674 | 2:25 | 95 | 127.1914 | 125.4264 | 137.5888 | 40.5045 | 107.6051 | 107.6051 | 18.3355 | 16.1474 | 30.9922 | 31.323 | 50 | 39.4244 | 199.6036 | 33.312 | 35.3441 | 108.3088 | ON | 17.86 | 108.3 | 22.6445 | 29.2888 | -1.7126 | 15.1756 | 0.6949 | 0.6949 | 3.9595 |  | OK | Low Charge | OK | OK | 109.3314 | OK | OK | OK | OK | OK
44811.8675 | 2:25 | 95 | 127.0463 | 125.1542 | 137.255 | 39.9601 | 107.7014 | 107.7014 | 18.1064 | 15.9485 | 31.0856 | 31.4465 | 50 | 39.2293 | 200.1447 | 33.4492 | 35.3118 | 108.3752 | ON | 17.86 | 110.2 | 22.1001 | 27.055 | -1.9115 | 15.498 | 2.4986 | 2.4986 | 3.9838 |  | OK | OK | OK | OK | 109.1863 | OK | OK | OK | OK | OK
44811.8676 | 2:25 | 95 | 126.8226 | 124.9611 | 136.9849 | 39.638 | 107.6747 | 107.6747 | 17.9582 | 15.8219 | 31.1518 | 31.5117 | 50 | 39.1985 | 199.8168 | 33.4477 | 35.2977 | 108.3746 | ON | 17.86 | 108.3 | 21.778 | 28.6849 | -2.0381 | 15.6897 | 0.6253 | 0.6253 | 3.98 |  | OK | Low Charge | OK | OK | 108.9626 | OK | OK | OK | OK | OK
44811.8677 | 2:25 | 95 | 126.6391 | 124.8356 | 136.7432 | 39.2829 | 107.7514 | 107.7514 | 17.7738 | 15.6533 | 31.2249 | 31.5586 | 50 | 39.072 | 200.2106 | 33.2004 | 35.3146 | 108.4465 | ON | 17.86 | 110.2 | 21.423 | 26.5432 | -2.2067 | 15.9053 | 2.4486 | 2.4486 | 3.9967 |  | OK | OK | OK | OK | 108.7791 | OK | OK | OK | OK | OK
44811.8678 | 2:26 | 95 | 127.435 | 125.4891 | 137.2883 | 38.8249 | 110.1526 | 110.1526 | 15.4917 | 14.8429 | 31.2305 | 31.5322 | 50 | 26.7273 | 210.2578 | 32.9383 | 35.222 | 110.5928 | ON | 3.03 | 113.8 | 35.7949 | 23.4883 | 11.8128 | 16.6894 | 3.6474 | 3.6474 | 5.4302 |  | OK | OK | OK | OK | 124.405 | OK | OK | OK | OK | OK
44811.868 | 2:26 | 95 | 127.3546 | 125.6455 | 135.8752 | 43.2873 | 108.4946 | 108.4946 | 16.5714 | 16.8414 | 31.2593 | 31.5736 | 50 | 20.7667 | 203.1641 | 33.0276 | 35.2258 | 109.0287 | ON | -5.06 | 110.2 | 48.3473 | 25.6752 | 21.9014 | 14.7322 | 1.7054 | 1.7054 | 6.1428 |  | OK | OK | OK | OK | 132.4146 | OK | OK | OK | OK | OK
44811.8681 | 2:26 | 95 | 127.4297 | 125.3213 | 134.7617 | 47.3991 | 106.4999 | 106.4999 | 18.9994 | 19.0422 | 31.2866 | 31.6028 | 50 | 16.8763 | 200.0582 | 33.5628 | 35.3794 | 107.9828 | ON | -11.06 | 110.2 | 58.4591 | 24.5617 | 30.1022 | 12.5606 | 3.7001 | 3.7001 | 6.8013 |  | OK | OK | OK | OK | 138.4897 | OK | OK | OK | OK | OK
44811.8682 | 2:26 | 95 | 127.7724 | 125.1848 | 134.0984 | 49.1643 | 105.2616 | 105.2616 | 21.4404 | 21.0127 | 31.3163 | 31.6425 | 50 | 16.2897 | 197.1378 | 34.1997 | 35.5314 | 107.2179 | ON | -11.06 | 108.3 | 60.2243 | 25.7984 | 32.0727 | 10.6298 | 3.0384 | 3.0384 | 6.8357 |  | OK | OK | OK | OK | 138.8324 | OK | OK | OK | OK | OK
44811.8683 | 2:26 | 95 | 128.3606 | 125.1869 | 133.8971 | 50.147 | 105.0507 | 105.0507 | 23.735 | 22.7611 | 31.3566 | 31.7482 | 50 | 15.4452 | 196.0139 | 34.5753 | 35.6607 | 106.7765 | ON | -12.65 | 108.3 | 62.797 | 25.5971 | 35.4111 | 8.9871 | 3.2493 | 3.2493 | 6.99 |  | OK | OK | OK | OK | 141.0106 | OK | OK | OK | OK | OK
44811.8684 | 2:26 | 95 | 129.2825 | 125.4103 | 133.9662 | 52.8884 | 104.6583 | 104.6583 | 25.6412 | 24.2022 | 31.3944 | 31.8536 | 50 | 14.9535 | 195.6509 | 34.7902 | 35.8589 | 106.538 | ON | -14.28 | 108.3 | 67.1685 | 25.6662 | 38.4822 | 7.6514 | 3.6417 | 3.6417 | 7.0936 |  | OK | OK | OK | OK | 143.5625 | OK | OK | OK | OK | OK
44811.8685 | 2:27 | 95 | 130.1375 | 125.7099 | 134.2133 | 54.9143 | 104.3679 | 104.3679 | 27.1782 | 25.4097 | 31.4217 | 31.9596 | 50 | 14.3839 | 195.1333 | 35.1159 | 35.9647 | 106.4267 | ON | -14.28 | 108.3 | 69.1943 | 25.9133 | 39.6897 | 6.5499 | 3.9321 | 3.9321 | 7.2148 |  | OK | OK | OK | OK | 144.4175 | OK | OK | OK | OK | OK
44811.8686 | 2:27 | 95 | 130.9992 | 126.0158 | 134.5764 | 56.6187 | 104.3659 | 104.3659 | 28.4179 | 26.4258 | 31.4712 | 32.0651 | 50 | 14.0367 | 194.8398 | 35.3259 | 36.1388 | 106.323 | ON | -14.28 | 106.4 | 70.8987 | 28.1764 | 40.7058 | 5.6393 | 2.0341 | 2.0341 | 7.2917 |  | OK | OK | OK | OK | 145.2792 | OK | OK | OK | OK | OK
44811.8688 | 2:27 | 95 | 131.7827 | 126.4312 | 134.9949 | 57.7364 | 104.2805 | 104.2805 | 29.3017 | 27.2467 | 31.5053 | 32.1841 | 50 | 13.5679 | 194.6409 | 35.5144 | 36.1712 | 106.2842 | ON | -15.96 | 106.4 | 73.6964 | 28.5949 | 43.2067 | 4.9374 | 2.1195 | 2.1195 | 7.4056 |  | OK | OK | OK | OK | 147.7427 | OK | OK | OK | OK | OK
44811.8689 | 2:27 | 95 | 132.8027 | 126.9436 | 135.4861 | 58.2711 | 104.2511 | 104.2511 | 29.9674 | 27.87 | 31.5218 | 32.322 | 50 | 13.3584 | 194.7273 | 35.6944 | 36.2241 | 106.2726 | ON | -15.96 | 106.4 | 74.2311 | 29.0861 | 43.83 | 4.452 | 2.1489 | 2.1489 | 7.464 |  | OK | OK | OK | OK | 148.7627 | OK | OK | OK | OK | OK
44811.869 | 2:27 | 95 | 133.6762 | 127.3039 | 135.9633 | 58.5868 | 104.2151 | 104.2151 | 30.4306 | 28.405 | 31.5592 | 32.4582 | 50 | 13.0158 | 194.7074 | 35.7809 | 36.2638 | 106.2846 | ON | -15.96 | 106.4 | 74.5468 | 29.5633 | 44.365 | 4.0532 | 2.1849 | 2.1849 | 7.5555 |  | OK | OK | OK | OK | 149.6362 | OK | OK | OK | OK | OK
44811.8691 | 2:27 | 95 | 134.3376 | 127.8222 | 136.5129 | 58.5679 | 104.3693 | 104.3693 | 30.769 | 28.7951 | 31.5838 | 32.586 | 50 | 12.9512 | 194.9627 | 35.8731 | 36.3868 | 106.329 | ON | -17.69 | 106.4 | 76.2579 | 30.1129 | 46.4851 | 3.7909 | 2.0307 | 2.0307 | 7.5824 |  | OK | OK | OK | OK | 152.0276 | OK | OK | OK | OK | OK
44811.8692 | 2:28 | 95 | 135.0471 | 128.295 | 137.1079 | 58.2074 | 104.3953 | 104.3953 | 30.9754 | 29.1169 | 31.5959 | 32.7345 | 50 | 12.8119 | 194.6148 | 36.0703 | 36.4878 | 106.2792 | ON | -17.69 | 106.4 | 75.8974 | 30.7079 | 46.807 | 3.6176 | 2.0047 | 2.0047 | 7.6082 |  | OK | OK | OK | OK | 152.7371 | OK | OK | OK | OK | OK
44811.8693 | 2:28 | 95 | 135.5709 | 128.6827 | 137.6202 | 57.5541 | 104.3722 | 104.3722 | 31.1488 | 29.3955 | 31.622 | 32.8692 | 50 | 12.8144 | 194.491 | 36.0681 | 36.5341 | 106.2118 | ON | -17.69 | 106.4 | 75.2441 | 31.2202 | 47.0855 | 3.4737 | 2.0278 | 2.0278 | 7.603 |  | OK | OK | OK | OK | 153.2609 | OK | OK | OK | OK | OK
44811.8695 | 2:28 | 95 | 135.781 | 128.9181 | 137.7324 | 56.7797 | 103.998 | 103.998 | 31.2933 | 29.6099 | 31.6181 | 33.0355 | 50 | 13.691 | 193.8883 | 36.0418 | 36.5832 | 106.0057 | ON | -15.96 | 106.4 | 72.7397 | 31.3324 | 45.5699 | 3.4256 | 2.402 | 2.402 | 7.347 |  | OK | OK | OK | OK | 151.741 | OK | OK | OK | OK | OK
44811.8696 | 2:28 | 95 | 135.7754 | 128.9692 | 137.7432 | 51.8935 | 103.7428 | 103.7428 | 31.3576 | 29.8023 | 31.655 | 33.1572 | 50 | 15.0185 | 192.8605 | 36.154 | 36.666 | 105.8091 | ON | -12.65 | 106.4 | 64.5435 | 31.3432 | 42.4523 | 3.355 | 2.6572 | 2.6572 | 6.9842 |  | OK | OK | OK | OK | 148.4254 | OK | OK | OK | OK | OK
44811.8697 | 2:28 | 95 | 139.5815 | 127.1448 | 135.3709 | 47.7053 | 95.0569 | 95.0569 | 27.3261 | 30.5209 | 28.5085 | 33.6073 | 50 | 53.1731 | 133.1778 | 36.2033 | 36.6798 | 102.1969 | OFF | 31.06 | 80.35 | 16.6453 | 55.0209 | -0.5391 | 3.0864 | -14.7069 | -14.7069 | 2.1787
44811.8698 | 2:28 | 95 | 139.2564 | 124.7332 | 128.2071 | 57.3866 | 92.248 | 92.248 | 31.2169 | 31.2501 | 31.1099 | 33.6228 | 50 | 58.152 | 113.9326 | 36.2044 | 36.7102 | 101.2992 | OFF | 35.28 | 69.9 | 22.1066 | 58.3071 | -4.03 | 2.3728 | -22.348 | -22.348 | 1.7657
44811.8699 | 2:29 | 95 | 138.218 | 123.1786 | 121.0384 | 72.5007 | 89.9772 | 89.9772 | 31.8805 | 32.5331 | 31.5503 | 33.832 | 50 | 59.5585 | 102.6291 | 36.2374 | 36.7686 | 100.5065 | OFF | 36.1 | 64.21 | 36.4007 | 56.8284 | -3.5669 | 1.299 | -25.7672 | -25.7672 | 1.58
44811.87 | 2:29 | 95 | 136.8083 | 121.5608 | 115.3813 | 83.4329 | 88.2988 | 88.2988 | 31.8686 | 33.6398 | 31.6921 | 34.1694 | 50 | 60.3721 | 91.8715 | 36.4943 | 36.844 | 99.8666 | OFF | 36.91 | 58.13 | 46.5229 | 57.2513 | -3.2702 | 0.52967 | -30.1688 | -30.1688 | 1.4196
44811.8702 | 2:29 | 95 | 135.5538 | 120.1519 | 111.4699 | 89.484 | 87.1627 | 87.1627 | 31.8636 | 34.3182 | 31.7249 | 34.558 | 50 | 61.2182 | 84.349 | 36.466 | 36.8727 | 99.3409 | OFF | 37.71 | 51.63 | 51.774 | 59.8399 | -3.3918 | 0.2398 | -35.5327 | -35.5327 | 1.3047
44811.8703 | 2:29 | 95 | 134.2147 | 118.8494 | 108.7005 | 92.876 | 86.4725 | 86.4725 | 31.8947 | 34.9425 | 31.7768 | 34.9042 | 50 | 61.8068 | 77.7323 | 36.5947 | 37.0244 | 98.9272 | OFF | 37.71 | 48.19 | 55.166 | 60.5105 | -2.7675 | -0.03824 | -38.2826 | -38.2826 | 1.2082
44811.8704 | 2:29 | 95 | 133.0177 | 117.6685 | 106.8981 | 94.6564 | 86.3587 | 86.3587 | 31.8727 | 35.2563 | 31.7723 | 35.1689 | 50 | 62.093 | 72.5139 | 36.6792 | 37.132 | 98.6086 | OFF | 38.5 | 44.59 | 56.1564 | 62.3081 | -3.2437 | -0.08743 | -41.7687 | -41.7687 | 1.1357
44811.8705 | 2:29 | 95 | 131.9031 | 116.541 | 105.7941 | 95.1119 | 87.2176 | 87.2176 | 31.8765 | 35.3908 | 31.789 | 35.2352 | 50 | 62.2263 | 67.1718 | 36.7948 | 37.1802 | 98.3771 | OFF | 38.5 | 42.36 | 56.6119 | 63.4341 | -3.1092 | -0.15565 | -44.8576 | -44.8576 | 1.0643
44811.8706 | 2:30 | 95 | 130.7975 | 115.5372 | 105.2041 | 94.7563 | 88.4789 | 88.4789 | 31.905 | 35.3735 | 31.8108 | 35.2587 | 50 | 61.9171 | 65.3081 | 36.9284 | 37.3315 | 98.1628 | OFF | 37.71 | 40.84 | 57.0463 | 64.3641 | -2.3365 | -0.11478 | -47.6389 | -47.6389 | 1.0443
44811.8707 | 2:30 | 95 | 129.7333 | 114.6756 | 104.8122 | 94.3806 | 89.7133 | 89.7133 | 31.936 | 35.4484 | 31.8163 | 35.282 | 50 | 62.4036 | 64.3357 | 37.0475 | 37.4245 | 97.93 | OFF | 38.5 | 40.07 | 55.8806 | 64.7422 | -3.0516 | -0.16642 | -49.6433 | -49.6433 | 1.0251
44811.8708 | 2:30 | 95 | 128.8638 | 113.9199 | 104.5186 | 94.1888 | 90.832 | 90.832 | 31.9406 | 35.5222 | 31.8595 | 35.3708 | 50 | 62.5256 | 63.8621 | 37.0775 | 37.4942 | 97.7671 | OFF | 38.5 | 39.29 | 55.6888 | 65.2286 | -2.9778 | -0.15141 | -51.5421 | -51.5421 | 1.0173
44811.871 | 2:30 | 95 | 128.0083 | 113.143 | 104.2433 | 94.0708 | 91.6046 | 91.6046 | 31.9693 | 35.7448 | 31.8791 | 35.5076 | 50 | 62.7279 | 62.329 | 37.1252 | 37.4948 | 97.6033 | OFF | 38.5 | 38.5 | 55.5708 | 65.7433 | -2.7553 | -0.2372 | -53.1046 | -53.1046 | 0.99485
44811.8711 | 2:30 | 95 | 127.15 | 112.5019 | 103.9641 | 93.9152 | 92.3799 | 92.3799 | 31.996 | 35.9656 | 31.884 | 35.7522 | 50 | 63.1173 | 62.337 | 37.1476 | 37.5894 | 97.4091 | OFF | 39.29 | 38.5 | 54.6252 | 65.4641 | -3.3244 | -0.21341 | -53.8799 | -53.8799 | 0.98997
44811.8712 | 2:30 | 95 | 126.3755 | 111.9476 | 103.7672 | 93.8817 | 93.0371 | 93.0371 | 32.0654 | 36.2326 | 32.1771 | 36.0544 | 50 | 63.3919 | 62.5481 | 37.2232 | 37.7114 | 97.2645 | OFF | 39.29 | 38.5 | 54.5917 | 65.2672 | -3.0574 | -0.17829 | -54.5371 | -54.5371 | 0.98919
44811.8713 | 2:31 | 95 | 125.5845 | 111.4701 | 103.5157 | 93.7512 | 93.5095 | 93.5095 | 32.128 | 36.5106 | 33.4599 | 36.4216 | 50 | 63.7914 | 62.9714 | 37.5284 | 37.7496 | 97.125 | OFF | 39.29 | 38.5 | 54.4612 | 65.0157 | -2.7794 | -0.08903 | -55.0095 | -55.0095 | 0.98955
44811.8714 | 2:31 | 95 | 124.8192 | 110.9537 | 103.293 | 93.8394 | 93.8798 | 93.8798 | 32.201 | 36.6526 | 34.7288 | 36.841 | 50 | 64.265 | 63.3038 | 37.5276 | 37.8605 | 96.9827 | OFF | 40.07 | 39.29 | 53.7694 | 64.003 | -3.4174 | 0.18837 | -54.5898 | -54.5898 | 0.98783
44811.8715 | 2:31 | 95 | 124.1109 | 110.5182 | 103.0776 | 93.7504 | 94.1657 | 94.1657 | 32.3248 | 36.651 | 35.4764 | 37.2303 | 50 | 64.5087 | 63.6126 | 37.6703 | 37.9055 | 96.8632 | OFF | 40.07 | 39.29 | 53.6804 | 63.7876 | -3.419 | 0.57932 | -54.8757 | -54.8757 | 0.98869
44811.8717 | 2:31 | 95 | 123.4168 | 110.1291 | 102.8488 | 93.804 | 94.3985 | 94.3985 | 32.4705 | 36.671 | 36.4101 | 37.6036 | 50 | 64.791 | 63.792 | 37.9215 | 37.9852 | 96.7427 | OFF | 40.07 | 39.29 | 53.734 | 63.5588 | -3.399 | 0.9326 | -55.1085 | -55.1085 | 0.98743
44811.8718 | 2:31 | 95 | 122.7786 | 109.7469 | 102.6194 | 93.7508 | 94.5393 | 94.5393 | 32.6643 | 36.456 | 36.7338 | 37.8796 | 50 | 65.1182 | 64.3727 | 38.0132 | 38.0542 | 96.6077 | OFF | 40.84 | 40.07 | 52.9108 | 62.5494 | -4.384 | 1.4236 | -54.4693 | -54.4693 | 0.99066
44811.8719 | 2:31 | 95 | 122.1904 | 109.4045 | 102.4132 | 93.6665 | 94.6574 | 94.6574 | 32.7928 | 36.0314 | 37.1253 | 38.0785 | 50 | 65.33 | 64.5108 | 38.0086 | 38.2037 | 96.4623 | OFF | 40.84 | 40.07 | 52.8265 | 62.3432 | -4.8086 | 2.047 | -54.5874 | -54.5874 | 0.98976
44811.872 | 2:32 | 95 | 121.6452 | 109.046 | 102.2151 | 93.7845 | 94.7028 | 94.7028 | 32.8933 | 35.7 | 37.3956 | 38.2512 | 50 | 65.7236 | 64.7172 | 38.1499 | 38.267 | 96.3786 | OFF | 40.84 | 40.07 | 52.9445 | 62.1451 | -5.14 | 2.5511 | -54.6328 | -54.6328 | 0.98749
44811.8721 | 2:32 | 95 | 121.1375 | 108.7774 | 101.9869 | 93.7965 | 94.7644 | 94.7644 | 33.1148 | 35.4276 | 37.6126 | 38.4072 | 50 | 65.7695 | 64.7349 | 38.2395 | 38.4044 | 96.2224 | OFF | 40.84 | 40.07 | 52.9566 | 61.9169 | -5.4124 | 2.9796 | -54.6944 | -54.6944 | 0.98714
44811.8722 | 2:32 | 95 | 120.6106 | 108.4795 | 101.7781 | 93.7573 | 94.7734 | 94.7734 | 33.477 | 35.2785 | 37.7629 | 38.5534 | 50 | 66.0614 | 65.0896 | 38.4124 | 38.444 | 96.0611 | OFF | 41.6 | 40.84 | 52.1573 | 60.9381 | -6.3215 | 3.2749 | -53.9334 | -53.9334 | 0.98797
44811.8724 | 2:32 | 95 | 120.0959 | 108.1506 | 101.573 | 93.7317 | 94.7361 | 94.7361 | 33.9988 | 35.2074 | 37.8681 | 38.6823 | 50 | 66.1362 | 64.9443 | 38.4835 | 38.6404 | 95.8931 | OFF | 41.6 | 40.07 | 52.1317 | 61.503 | -6.3926 | 3.4749 | -54.6661 | -54.6661 | 0.98526
44811.8725 | 2:32 | 95 | 119.5871 | 107.8299 | 101.3966 | 93.7252 | 94.7238 | 94.7238 | 34.4396 | 35.3024 | 38.0078 | 38.8217 | 50 | 66.4199 | 65.3162 | 38.6376 | 38.6372 | 95.7659 | OFF | 41.6 | 40.84 | 52.1252 | 60.5566 | -6.2976 | 3.5193 | -53.8839 | -53.8839 | 0.98639
44811.8726 | 2:32 | 95 | 119.1071 | 107.5527 | 101.2278 | 93.7283 | 94.6729 | 94.6729 | 34.7788 | 35.4183 | 38.1136 | 38.9268 | 50 | 66.5483 | 65.5299 | 38.7544 | 38.7262 | 95.6205 | OFF | 41.6 | 40.84 | 52.1283 | 60.3878 | -6.1817 | 3.5084 | -53.8329 | -53.8329 | 0.98747
44811.8727 | 2:33 | 95 | 118.5878 | 107.2526 | 101.0323 | 93.6643 | 94.6563 | 94.6563 | 35.0534 | 35.5568 | 38.1429 | 39.0332 | 50 | 66.6865 | 65.5372 | 38.8208 | 38.8332 | 95.4874 | OFF | 41.6 | 40.84 | 52.0643 | 60.1923 | -6.0432 | 3.4764 | -53.8163 | -53.8163 | 0.98588
44811.8728 | 2:33 | 95 | 118.1792 | 106.9971 | 100.8295 | 93.5644 | 94.6014 | 94.6014 | 35.3527 | 35.8039 | 38.2144 | 39.1349 | 50 | 66.8093 | 65.8325 | 38.8888 | 38.9339 | 95.3496 | OFF | 41.6 | 40.84 | 51.9644 | 59.9895 | -5.7961 | 3.331 | -53.7614 | -53.7614 | 0.98802
44811.8729 | 2:33 | 95 | 117.7876 | 106.7817 | 100.6557 | 93.4251 | 94.5419 | 94.5419 | 35.6809 | 36.0852 | 38.2741 | 39.2319 | 50 | 67.1632 | 66.0127 | 39.0211 | 39.0016 | 95.2433 | OFF | 42.36 | 41.6 | 51.0651 | 59.0557 | -6.2748 | 3.1467 | -52.9419 | -52.9419 | 0.98595
44811.873 | 2:33 | 95 | 117.3549 | 106.4897 | 100.4696 | 93.4138 | 94.4634 | 94.4634 | 35.9933 | 36.2322 | 38.2946 | 39.3238 | 50 | 67.167 | 66.1662 | 39.2682 | 39.1616 | 95.1505 | OFF | 42.36 | 41.6 | 51.0538 | 58.8696 | -6.1278 | 3.0917 | -52.8634 | -52.8634 | 0.98778
44811.8732 | 2:33 | 95 | 116.9745 | 106.2642 | 100.3083 | 93.465 | 94.4021 | 94.4021 | 36.2769 | 36.3776 | 38.4427 | 39.4332 | 50 | 67.3184 | 66.1341 | 39.2293 | 39.2266 | 95.0553 | OFF | 42.36 | 41.6 | 51.105 | 58.7083 | -5.9824 | 3.0556 | -52.8021 | -52.8021 | 0.98556
44811.8733 | 2:33 | 95 | 116.6301 | 106.1116 | 100.176 | 93.5536 | 94.3356 | 94.3356 | 36.5227 | 36.5496 | 38.3051 | 39.2747 | 50 | 67.6175 | 66.5062 | 39.4182 | 39.3162 | 95.0557 | OFF | 42.36 | 41.6 | 51.1936 | 58.576 | -5.8105 | 2.7251 | -52.7356 | -52.7356 | 0.9865
44811.8734 | 2:34 | 95 | 118.2783 | 106.3723 | 113.7778 | 77.5592 | 94.6878 | 94.6878 | 35.7588 | 35.8851 | 36.4745 | 35.6891 | 50 | 60.4049 | 140.2511 | 39.5269 | 39.4073 | 95.6023 | OFF | 36.91 | 85.18 | 40.6492 | 28.5978 | -1.0249 | -0.19606 | -9.5078 | -9.5078 | 2.0631
44811.8735 | 2:34 | 95 | 119.0123 | 108.8485 | 128.3473 | 63.5496 | 99.0126 | 99.0126 | 30.9881 | 31.6648 | 30.8329 | 34.5975 | 50 | 53.7801 | 179.8534 | 39.1006 | 39.2343 | 100.3844 | ON | 31.06 | 100.5 | 32.4896 | 27.8473 | 0.60481 | 2.9327 | 1.4874 | 1.4874 | 2.841 |  | OK | OK | OK | OK | 87.9523 | OK | OK | OK | OK | OK
44811.8736 | 2:34 | 95 | 118.0812 | 113.1822 | 128.2937 | 59.3613 | 102.4642 | 102.4642 | 29.5265 | 29.6519 | 29.2262 | 33.0901 | 50 | 52.8019 | 187.278 | 38.6796 | 39.0123 | 103.3936 | ON | 30.19 | 104.4 | 29.1713 | 23.8937 | -0.53811 | 3.4382 | 1.9358 | 1.9358 | 2.9922 |  | OK | OK | OK | OK | 87.8912 | OK | OK | OK | OK | OK
44811.8737 | 2:34 | 95 | 117.5063 | 115.0801 | 127.7002 | 57.4191 | 103.9336 | 103.9336 | 29.3557 | 30.4257 | 28.5488 | 30.2165 | 50 | 52.2807 | 190.6925 | 38.2651 | 38.7936 | 104.7504 | ON | 30.19 | 106.4 | 27.2291 | 21.3002 | 0.23574 | -0.20928 | 2.4664 | 2.4664 | 3.0664 |  | OK | OK | OK | OK | 87.3163 | OK | OK | OK | OK | OK
44811.8739 | 2:34 | 95 | 117.2177 | 116.0558 | 127.5729 | 57.0316 | 104.5831 | 104.5831 | 29.2138 | 28.0406 | 27.937 | 27.4448 | 50 | 52.0566 | 192.1619 | 38.0611 | 38.4868 | 105.4122 | ON | 30.19 | 106.4 | 26.8416 | 21.1729 | -2.1494 | -0.59582 | 1.8169 | 1.8169 | 3.0988 |  | OK | OK | OK | OK | 87.0277 | OK | OK | OK | OK | OK
44811.874 | 2:34 | 95 | 117.5354 | 116.8315 | 127.8767 | 57.2385 | 105.1457 | 105.1457 | 29.0853 | 28.659 | 27.4801 | 26.8573 | 50 | 51.7914 | 193.75 | 37.7966 | 38.3254 | 105.9498 | ON | 29.31 | 106.4 | 27.9285 | 21.4767 | -0.65105 | -1.8017 | 1.2543 | 1.2543 | 3.135 |  | OK | OK | OK | OK | 88.2254 | OK | OK | OK | OK | OK
44811.8741 | 2:35 | 95 | 118.2319 | 117.6852 | 128.3587 | 59.8118 | 105.5864 | 105.5864 | 28.977 | 30.3156 | 27.3041 | 26.5823 | 50 | 51.4851 | 194.4795 | 37.8975 | 38.1625 | 106.4366 | ON | 29.31 | 106.4 | 30.5018 | 21.9587 | 1.0056 | -3.7332 | 0.8136 | 0.8136 | 3.1605 |  | OK | Low Charge | OK | OK | 88.9219 | OK | OK | OK | OK | OK
44811.8742 | 2:35 | 95 | 119.0449 | 118.4326 | 128.9156 | 62.5777 | 105.8683 | 105.8683 | 28.8407 | 30.9642 | 27.5254 | 26.4465 | 50 | 51.1563 | 195.3996 | 37.8518 | 38.1756 | 106.7257 | ON | 29.31 | 108.3 | 33.2677 | 20.6156 | 1.6542 | -4.5177 | 2.4317 | 2.4317 | 3.1903 |  | OK | OK | OK | OK | 89.7349 | OK | OK | OK | OK | OK
44811.8743 | 2:35 | 95 | 119.8599 | 119.2061 | 129.4927 | 64.6297 | 106.0881 | 106.0881 | 28.6719 | 31.2503 | 26.8007 | 26.3382 | 50 | 50.9541 | 195.8539 | 37.8954 | 38.0595 | 106.9814 | ON | 28.42 | 108.3 | 36.2097 | 21.1927 | 2.8302 | -4.9121 | 2.2119 | 2.2119 | 3.207 |  | OK | OK | OK | OK | 91.4399 | OK | OK | OK | OK | OK
44811.8744 | 2:35 | 95 | 120.6806 | 119.8775 | 130.1414 | 66.1822 | 106.237 | 106.237 | 28.508 | 31.289 | 26.4245 | 26.6767 | 50 | 50.5668 | 196.2499 | 37.8651 | 38.0467 | 107.1831 | ON | 28.42 | 108.3 | 37.7623 | 21.8414 | 2.869 | -4.6123 | 2.063 | 2.063 | 3.2321 |  | OK | OK | OK | OK | 92.2606 | OK | OK | OK | OK | OK
44811.8746 | 2:35 | 95 | 121.4571 | 120.4751 | 130.7774 | 67.3599 | 106.2922 | 106.2922 | 28.404 | 31.1758 | 26.2257 | 26.9762 | 50 | 50.6329 | 196.1745 | 37.826 | 37.8431 | 107.2919 | ON | 28.42 | 108.3 | 38.94 | 22.4774 | 2.7558 | -4.1997 | 2.0078 | 2.0078 | 3.2277 |  | OK | OK | OK | OK | 93.0371 | OK | OK | OK | OK | OK
44811.8747 | 2:35 | 95 | 122.1707 | 121.0447 | 131.4914 | 68.382 | 106.3839 | 106.3839 | 28.2951 | 30.9274 | 26.0134 | 27.0275 | 50 | 50.4222 | 196.5316 | 37.6959 | 37.816 | 107.3873 | ON | 28.42 | 108.3 | 39.962 | 23.1914 | 2.5074 | -3.8999 | 1.9161 | 1.9161 | 3.2436 |  | OK | OK | OK | OK | 93.7507 | OK | OK | OK | OK | OK
44811.8748 | 2:36 | 95 | 122.9168 | 121.6946 | 132.2268 | 69.3617 | 106.489 | 106.489 | 28.2894 | 30.689 | 25.9369 | 27.0032 | 50 | 50.5932 | 196.7856 | 37.5567 | 37.8261 | 107.539 | ON | 28.42 | 108.3 | 40.9417 | 23.9268 | 2.269 | -3.6858 | 1.811 | 1.811 | 3.239 |  | OK | OK | OK | OK | 94.4968 | OK | OK | OK | OK | OK
44811.8749 | 2:36 | 95 | 123.6879 | 122.2837 | 133.0318 | 70.1292 | 106.921 | 106.921 | 29.6647 | 30.3856 | 25.8806 | 27.0812 | 50 | 50.4149 | 197.9384 | 37.5878 | 37.6934 | 107.9148 | ON | 28.42 | 108.3 | 41.7092 | 24.7318 | 1.9656 | -3.3044 | 1.379 | 1.379 | 3.2656 |  | OK | OK | OK | OK | 95.2679 | OK | OK | OK | OK | OK
44811.875 | 2:36 | 95 | 124.4318 | 122.9969 | 133.8559 | 70.7957 | 107.0252 | 107.0252 | 29.548 | 29.1681 | 25.6766 | 27.5457 | 50 | 50.0138 | 198.0149 | 37.4514 | 37.684 | 108.0748 | ON | 28.42 | 108.3 | 42.3757 | 25.5559 | 0.74812 | -1.6224 | 1.2748 | 1.2748 | 3.287 |  | OK | OK | OK | OK | 96.0118 | OK | OK | OK | OK | OK
44811.8751 | 2:36 | 95 | 125.1865 | 123.5522 | 134.5693 | 71.3552 | 107.1536 | 107.1536 | 29.3556 | 26.746 | 25.6984 | 28.0468 | 50 | 50.2037 | 197.9003 | 37.2834 | 37.6362 | 108.1777 | ON | 28.42 | 108.3 | 42.9352 | 26.2693 | -1.674 | 1.3008 | 1.1464 | 1.1464 | 3.2756 |  | OK | OK | OK | OK | 96.7665 | OK | OK | OK | OK | OK
44811.8752 | 2:36 | 95 | 125.9298 | 124.091 | 135.2894 | 71.7298 | 107.3421 | 107.3421 | 28.6952 | 26.1854 | 25.6108 | 28.4841 | 50 | 50.0012 | 198.6945 | 37.3685 | 37.7051 | 108.3702 | ON | 28.42 | 108.3 | 43.3098 | 26.9894 | -2.2346 | 2.2986 | 0.9579 | 0.9579 | 3.2982 |  | OK | Low Charge | OK | OK | 97.5098 | OK | OK | OK | OK | OK
44811.8754 | 2:36 | 95 | 126.4579 | 124.7265 | 136.0161 | 71.9299 | 107.4234 | 107.4234 | 27.615 | 25.9261 | 25.4285 | 28.686 | 50 | 49.566 | 198.6046 | 37.1685 | 37.593 | 108.483 | ON | 27.51 | 108.3 | 44.4199 | 27.7161 | -1.5839 | 2.7599 | 0.8766 | 0.8766 | 3.3191 |  | OK | Low Charge | OK | OK | 98.9479 | OK | OK | OK | OK | OK
44811.8755 | 2:37 | 95 | 127.0318 | 125.2317 | 136.6575 | 71.9563 | 107.5212 | 107.5212 | 27.3606 | 25.7851 | 25.3327 | 28.6719 | 50 | 49.6276 | 199.0094 | 37.0915 | 37.4846 | 108.5899 | ON | 27.51 | 108.3 | 44.4463 | 28.3575 | -1.7249 | 2.8868 | 0.7788 | 0.7788 | 3.3222 |  | OK | Low Charge | OK | OK | 99.5218 | OK | OK | OK | OK | OK
44811.8756 | 2:37 | 95 | 127.6528 | 125.6568 | 137.2056 | 71.5807 | 107.6029 | 107.6029 | 27.1191 | 25.5278 | 25.2013 | 28.4928 | 50 | 49.1301 | 198.908 | 37.0609 | 37.4556 | 108.6809 | ON | 27.51 | 108.3 | 44.0707 | 28.9056 | -1.9822 | 2.965 | 0.6971 | 0.6971 | 3.3465 |  | OK | Low Charge | OK | OK | 100.1428 | OK | OK | OK | OK | OK
44811.8757 | 2:37 | 95 | 128.1013 | 126.0595 | 137.7981 | 71.2767 | 107.6469 | 107.6469 | 26.8327 | 25.2863 | 25.0305 | 28.2073 | 50 | 49.188 | 199.5564 | 37.0097 | 37.3306 | 108.7486 | ON | 27.51 | 108.3 | 43.7667 | 29.4981 | -2.2237 | 2.9211 | 0.6531 | 0.6531 | 3.3536 |  | OK | Low Charge | OK | OK | 100.5913 | OK | OK | OK | OK | OK
44811.8758 | 2:37 | 95 | 128.5523 | 126.5094 | 138.3185 | 70.926 | 107.7617 | 107.7617 | 26.6492 | 25.1295 | 24.8226 | 27.9042 | 50 | 48.8088 | 199.5884 | 36.9455 | 37.2353 | 108.8772 | ON | 26.6 | 108.3 | 44.326 | 30.0185 | -1.4705 | 2.7747 | 0.5383 | 0.5383 | 3.3742 |  | OK | Low Charge | OK | OK | 101.9523 | OK | OK | OK | OK | OK
44811.8759 | 2:37 | 95 | 128.904 | 126.8366 | 138.7473 | 70.903 | 107.8201 | 107.8201 | 26.3869 | 24.8879 | 24.7259 | 27.5503 | 50 | 48.8551 | 199.7569 | 36.7562 | 37.2709 | 108.9387 | ON | 26.6 | 108.3 | 44.303 | 30.4473 | -1.7121 | 2.6624 | 0.4799 | 0.4799 | 3.3743 |  | OK | Low Charge | OK | OK | 102.304 | OK | OK | OK | OK | OK
44811.8761 | 2:37 | 95 | 129.1988 | 127.1848 | 139.2133 | 71.2197 | 107.8204 | 107.8204 | 26.1392 | 24.6865 | 24.5273 | 27.1965 | 50 | 48.6049 | 199.6224 | 36.6727 | 37.1354 | 108.948 | ON | 26.6 | 108.3 | 44.6197 | 30.9133 | -1.9135 | 2.51 | 0.4796 | 0.4796 | 3.3856 |  | OK | Low Charge | OK | OK | 102.5988 | OK | OK | OK | OK | OK
44811.8762 | 2:38 | 95 | 129.5976 | 127.4835 | 139.6126 | 71.4192 | 107.9304 | 107.9304 | 25.947 | 24.5063 | 24.4546 | 26.9353 | 50 | 48.2822 | 200.0149 | 36.6344 | 37.0469 | 109.0299 | ON | 26.6 | 110.2 | 44.8192 | 29.4126 | -2.0937 | 2.429 | 2.2696 | 2.2696 | 3.4091 |  | OK | OK | OK | OK | 102.9976 | OK | OK | OK | OK | OK
44811.8763 | 2:38 | 95 | 129.9491 | 127.8299 | 140.0974 | 71.4521 | 108.0071 | 108.0071 | 25.7589 | 24.335 | 24.391 | 26.6572 | 50 | 48.6342 | 199.9851 | 36.6057 | 36.9674 | 109.1159 | ON | 26.6 | 108.3 | 44.8521 | 31.7974 | -2.265 | 2.3222 | 0.2929 | 0.2929 | 3.3897 |  | OK | Low Charge | OK | OK | 103.3491 | OK | OK | OK | OK | OK
44811.8764 | 2:38 | 95 | 130.2623 | 128.1042 | 140.4978 | 71.4114 | 108.0896 | 108.0896 | 25.6635 | 24.2667 | 24.0348 | 26.418 | 50 | 48.1071 | 200.4469 | 36.5163 | 36.8769 | 109.1929 | ON | 26.6 | 110.2 | 44.8114 | 30.2978 | -2.3333 | 2.1513 | 2.1104 | 2.1104 | 3.4255 |  | OK | OK | OK | OK | 103.6623 | OK | OK | OK | OK | OK
44811.8765 | 2:38 | 95 | 130.608 | 128.4332 | 140.8219 | 71.689 | 108.0718 | 108.0718 | 25.3324 | 23.9862 | 23.8708 | 26.1704 | 50 | 47.8122 | 200.3017 | 36.3696 | 36.6759 | 109.1732 | ON | 25.68 | 110.2 | 46.009 | 30.6219 | -1.6938 | 2.1842 | 2.1282 | 2.1282 | 3.4394 |  | OK | OK | OK | OK | 104.928 | OK | OK | OK | OK | OK
44811.8766 | 2:38 | 95 | 131.0181 | 128.6125 | 141.1877 | 71.8218 | 108.0164 | 108.0164 | 25.2436 | 23.8279 | 23.7075 | 25.9495 | 50 | 47.6594 | 200.3352 | 36.3907 | 36.6634 | 109.1566 | ON | 25.68 | 110.2 | 46.1418 | 30.9877 | -1.8521 | 2.1215 | 2.1836 | 2.1836 | 3.4483 |  | OK | OK | OK | OK | 105.3381 | OK | OK | OK | OK | OK
44811.8768 | 2:38 | 95 | 131.1006 | 128.7822 | 141.491 | 72.2628 | 107.8286 | 107.8286 | 24.9809 | 23.6413 | 23.5311 | 25.7624 | 50 | 47.7571 | 199.3639 | 36.267 | 36.562 | 108.9391 | ON | 25.68 | 108.3 | 46.5828 | 33.191 | -2.0387 | 2.1211 | 0.4714 | 0.4714 | 3.4274 |  | OK | Low Charge | OK | OK | 105.4206 | OK | OK | OK | OK | OK
44811.8769 | 2:39 | 95 | 131.3592 | 128.9448 | 141.6967 | 72.5251 | 107.6331 | 107.6331 | 24.852 | 23.4764 | 23.346 | 25.6287 | 50 | 47.294 | 198.9612 | 36.1534 | 36.5637 | 108.7742 | ON | 25.68 | 108.3 | 46.8451 | 33.3967 | -2.2037 | 2.1524 | 0.6669 | 0.6669 | 3.4465 |  | OK | Low Charge | OK | OK | 105.6792 | OK | OK | OK | OK | OK
44811.877 | 2:39 | 95 | 131.4851 | 129.0673 | 141.9464 | 72.8375 | 107.4444 | 107.4444 | 24.6878 | 23.3593 | 23.2256 | 25.4758 | 50 | 47.1641 | 198.2606 | 36.1314 | 36.4217 | 108.6335 | ON | 25.68 | 108.3 | 47.1574 | 33.6464 | -2.3207 | 2.1165 | 0.8556 | 0.8556 | 3.4424 |  | OK | Low Charge | OK | OK | 105.8051 | OK | OK | OK | OK | OK
44811.8771 | 2:39 | 95 | 131.6021 | 129.2138 | 142.1868 | 72.9734 | 107.3207 | 107.3207 | 24.5288 | 23.2502 | 23.0927 | 25.3526 | 50 | 47.1908 | 198.2394 | 36.0288 | 36.3392 | 108.4935 | ON | 25.68 | 108.3 | 47.2934 | 33.8868 | -2.4298 | 2.1024 | 0.9793 | 0.9793 | 3.4406 |  | OK | Low Charge | OK | OK | 105.9221 | OK | OK | OK | OK | OK
44811.8772 | 2:39 | 95 | 131.779 | 129.3517 | 142.3931 | 72.8808 | 107.2434 | 107.2434 | 24.3557 | 23.101 | 22.945 | 25.2686 | 50 | 47.0028 | 197.82 | 35.9754 | 36.1876 | 108.4255 | ON | 25.68 | 108.3 | 47.2008 | 34.0931 | -2.579 | 2.1677 | 1.0566 | 1.0566 | 3.4443 |  | OK | OK | OK | OK | 106.099 | OK | OK | OK | OK | OK
44811.8773 | 2:39 | 95 | 131.8674 | 129.4796 | 142.561 | 72.6642 | 107.2385 | 107.2385 | 24.0849 | 22.8497 | 22.7429 | 25.1867 | 50 | 46.6568 | 197.6895 | 35.9318 | 36.2662 | 108.4 | ON | 24.74 | 108.3 | 47.9242 | 34.261 | -1.8903 | 2.337 | 1.0615 | 1.0615 | 3.4615 |  | OK | OK | OK | OK | 107.1274 | OK | OK | OK | OK | OK
44811.8774 | 2:39 | 95 | 131.9621 | 129.5764 | 142.7602 | 72.5997 | 107.2153 | 107.2153 | 24.0502 | 22.7771 | 22.5833 | 25.0679 | 50 | 46.617 | 198.219 | 35.8561 | 36.1872 | 108.346 | ON | 24.74 | 108.3 | 47.8597 | 34.4602 | -1.9629 | 2.2907 | 1.0847 | 1.0847 | 3.4724 |  | OK | OK | OK | OK | 107.2221 | OK | OK | OK | OK | OK
44811.8776 | 2:40 | 95 | 132.1377 | 129.6641 | 142.9285 | 72.4861 | 107.1761 | 107.1761 | 23.8553 | 22.6077 | 22.4287 | 24.9883 | 50 | 46.3419 | 197.5002 | 35.7894 | 36.0331 | 108.3133 | ON | 24.74 | 108.3 | 47.7461 | 34.6285 | -2.1323 | 2.3806 | 1.1239 | 1.1239 | 3.4763 |  | OK | OK | OK | OK | 107.3977 | OK | OK | OK | OK | OK
44811.8777 | 2:40 | 95 | 132.2457 | 129.818 | 143.1311 | 71.9572 | 107.1373 | 107.1373 | 23.7336 | 22.4926 | 22.3896 | 24.8769 | 50 | 46.5048 | 197.7814 | 35.7652 | 35.9689 | 108.2594 | ON | 24.74 | 108.3 | 47.2172 | 34.8311 | -2.2474 | 2.3843 | 1.1627 | 1.1627 | 3.4716 |  | OK | OK | OK | OK | 107.5057 | OK | OK | OK | OK | OK
44811.8778 | 2:40 | 95 | 132.4487 | 129.8661 | 143.2768 | 71.8031 | 107.1178 | 107.1178 | 23.5543 | 22.34 | 22.2195 | 24.8035 | 50 | 46.1048 | 197.7038 | 35.5221 | 35.7432 | 108.2607 | ON | 24.74 | 108.3 | 47.0631 | 34.9768 | -2.4 | 2.4635 | 1.1822 | 1.1822 | 3.4932 |  | OK | OK | OK | OK | 107.7087 | OK | OK | OK | OK | OK
44811.8779 | 2:40 | 95 | 132.6137 | 129.9642 | 143.4413 | 71.5575 | 107.0583 | 107.0583 | 23.3378 | 22.1874 | 22.0822 | 24.7163 | 50 | 46.2176 | 197.4715 | 35.4839 | 35.7298 | 108.1955 | ON | 24.74 | 108.3 | 46.8175 | 35.1413 | -2.5526 | 2.5289 | 1.2417 | 1.2417 | 3.4829 |  | OK | OK | OK | OK | 107.8737 | OK | OK | OK | OK | OK
44811.878 | 2:40 | 95 | 132.6398 | 130.107 | 143.5702 | 71.1861 | 107.0656 | 107.0656 | 23.2642 | 22.1173 | 21.922 | 24.6087 | 50 | 45.927 | 197.2686 | 35.3755 | 35.6701 | 108.1969 | ON | 23.8 | 108.3 | 47.3861 | 35.2702 | -1.6827 | 2.4914 | 1.2344 | 1.2344 | 3.4963 |  | OK | OK | OK | OK | 108.8398 | OK | OK | OK | OK | OK
44811.8781 | 2:40 | 95 | 132.7228 | 130.2084 | 143.7283 | 71.1767 | 107.0382 | 107.0382 | 23.0547 | 21.8956 | 21.7857 | 24.537 | 50 | 45.6846 | 197.5379 | 35.3716 | 35.66 | 108.1756 | ON | 23.8 | 108.3 | 47.3767 | 35.4283 | -1.9044 | 2.6414 | 1.2618 | 1.2618 | 3.5148 |  | OK | OK | OK | OK | 108.9228 | OK | OK | OK | OK | OK
44811.8783 | 2:41 | 95 | 132.9504 | 130.2089 | 143.847 | 71.3294 | 107.0257 | 107.0257 | 22.9659 | 21.8003 | 21.6664 | 24.4335 | 50 | 45.6514 | 197.3832 | 35.1972 | 35.4856 | 108.1235 | ON | 23.8 | 108.3 | 47.5294 | 35.547 | -1.9997 | 2.6332 | 1.2743 | 1.2743 | 3.5141 |  | OK | OK | OK | OK | 109.1504 | OK | OK | OK | OK | OK
44811.8784 | 2:41 | 95 | 133.0298 | 130.2704 | 143.9583 | 71.3285 | 106.9002 | 106.9002 | 22.7719 | 21.6633 | 21.5538 | 24.3603 | 50 | 45.4333 | 196.9431 | 35.3727 | 35.4951 | 108.0273 | ON | 23.8 | 108.3 | 47.5285 | 35.6583 | -2.1367 | 2.697 | 1.3998 | 1.3998 | 3.5196 |  | OK | OK | OK | OK | 109.2298 | OK | OK | OK | OK | OK
44811.8785 | 2:41 | 95 | 133.0541 | 130.337 | 144.1068 | 71.2411 | 106.8496 | 106.8496 | 22.7088 | 21.6226 | 21.455 | 24.2802 | 50 | 45.5181 | 196.8771 | 35.124 | 35.4704 | 107.9712 | ON | 23.8 | 108.3 | 47.4411 | 35.8068 | -2.1774 | 2.6576 | 1.4504 | 1.4504 | 3.5135 |  | OK | OK | OK | OK | 109.2541 | OK | OK | OK | OK | OK
44811.8786 | 2:41 | 95 | 133.0729 | 130.3539 | 144.1776 | 71.1486 | 106.7756 | 106.7756 | 22.5946 | 21.4941 | 21.3417 | 24.1982 | 50 | 45.2978 | 196.9778 | 35.0064 | 35.2753 | 107.8973 | ON | 23.8 | 108.3 | 47.3486 | 35.8776 | -2.3059 | 2.7041 | 1.5244 | 1.5244 | 3.5281 |  | OK | OK | OK | OK | 109.2729 | OK | OK | OK | OK | OK
44811.8787 | 2:41 | 95 | 133.1153 | 130.4264 | 144.2825 | 71.0052 | 106.702 | 106.702 | 22.564 | 21.4501 | 21.2142 | 24.16 | 50 | 45.2905 | 196.357 | 34.9252 | 35.333 | 107.8208 | ON | 23.8 | 108.3 | 47.2052 | 35.9825 | -2.3499 | 2.7098 | 1.598 | 1.598 | 3.5182 |  | OK | OK | OK | OK | 109.3153 | OK | OK | OK | OK | OK
44811.8788 | 2:41 | 95 | 133.1479 | 130.4601 | 144.3317 | 70.8807 | 106.6143 | 106.6143 | 22.3154 | 21.1655 | 21.1371 | 24.1076 | 50 | 44.8387 | 196.0257 | 34.9691 | 35.252 | 107.7359 | ON | 22.84 | 108.3 | 48.0407 | 36.0317 | -1.6745 | 2.9421 | 1.6857 | 1.6857 | 3.5393 |  | OK | OK | OK | OK | 110.3079 | OK | OK | OK | OK | OK
44811.879 | 2:42 | 95 | 133.2018 | 130.5005 | 144.415 | 71.6551 | 106.5588 | 106.5588 | 22.2177 | 21.1719 | 21.112 | 24.0386 | 50 | 44.9733 | 195.8075 | 34.7874 | 35.2458 | 107.6691 | ON | 22.84 | 108.3 | 48.8151 | 36.115 | -1.6681 | 2.8666 | 1.7412 | 1.7412 | 3.5277 |  | OK | OK | OK | OK | 110.3618 | OK | OK | OK | OK | OK
44811.8791 | 2:42 | 95 | 133.2469 | 130.4765 | 144.4635 | 71.9307 | 106.4744 | 106.4744 | 22.1222 | 20.9972 | 20.9376 | 23.9703 | 50 | 44.6154 | 195.5757 | 34.6645 | 35.053 | 107.575 | ON | 22.84 | 108.3 | 49.0907 | 36.1635 | -1.8428 | 2.973 | 1.8256 | 1.8256 | 3.545 |  | OK | OK | OK | OK | 110.4069 | OK | OK | OK | OK | OK
44811.8792 | 2:42 | 95 | 133.5131 | 130.5253 | 144.4573 | 72.1421 | 107.3922 | 107.3922 | 22.0447 | 21.0064 | 21.0176 | 23.9206 | 50 | 44.7096 | 200.4588 | 34.7059 | 34.9885 | 108.1489 | ON | 22.84 | 110.2 | 49.3021 | 34.2573 | -1.8336 | 2.9142 | 2.8078 | 2.8078 | 3.6216 |  | OK | OK | OK | OK | 110.6731 | OK | OK | OK | OK | OK
44811.8793 | 2:42 | 95 | 133.7964 | 130.7348 | 144.6171 | 71.8131 | 108.4096 | 108.4096 | 21.7848 | 19.9929 | 21.6696 | 24.061 | 50 | 42.7503 | 202.5782 | 34.4911 | 34.9055 | 108.8933 | ON | 20.88 | 110.2 | 50.9331 | 34.4171 | -0.88708 | 4.0681 | 1.7904 | 1.7904 | 3.782 |  | OK | OK | OK | OK | 112.9164 | OK | OK | OK | OK | OK
44811.8794 | 2:42 | 95 | 133.8291 | 130.9051 | 144.6846 | 69.4336 | 108.3625 | 108.3625 | 21.349 | 19.3637 | 22.733 | 24.7311 | 50 | 42.5885 | 201.9719 | 34.5575 | 34.9449 | 108.8663 | ON | 20.88 | 110.2 | 48.5536 | 34.4846 | -1.5163 | 5.3673 | 1.8375 | 1.8375 | 3.7821 |  | OK | OK | OK | OK | 112.9491 | OK | OK | OK | OK | OK
44811.8795 | 2:42 | 95 | 133.583 | 130.7916 | 144.5031 | 63.6305 | 108.1955 | 108.1955 | 21.0026 | 18.9433 | 24.08 | 25.6823 | 50 | 42.2249 | 201.5873 | 34.3544 | 35.0876 | 108.7693 | ON | 20.88 | 110.2 | 42.7505 | 34.3031 | -1.9367 | 6.739 | 2.0045 | 2.0045 | 3.7995 |  | OK | OK | OK | OK | 112.703 | OK | OK | OK | OK | OK
44811.8796 | 2:43 | 95 | 133.2747 | 130.4553 | 144.0931 | 54.1407 | 108.1565 | 108.1565 | 20.6636 | 18.5404 | 25.4006 | 26.6519 | 50 | 41.7716 | 201.0709 | 34.3394 | 35.2996 | 108.7286 | ON | 19.89 | 110.2 | 34.2507 | 33.8931 | -1.3496 | 8.1115 | 2.0435 | 2.0435 | 3.8209 |  | OK | OK | OK | OK | 113.3847 | OK | OK | OK | OK | OK
44811.8798 | 2:43 | 95 | 132.7061 | 129.9804 | 143.4921 | 49.3189 | 108.0541 | 108.0541 | 20.4105 | 18.2379 | 26.6527 | 27.6048 | 50 | 41.4667 | 200.5315 | 34.128 | 35.3036 | 108.6811 | ON | 19.89 | 110.2 | 29.4289 | 33.2921 | -1.6521 | 9.3669 | 2.1459 | 2.1459 | 3.832 |  | OK | OK | OK | OK | 112.8161 | OK | OK | OK | OK | OK
44811.8799 | 2:43 | 95 | 131.9574 | 129.414 | 142.7884 | 46.7649 | 108.0833 | 108.0833 | 20.1536 | 17.9461 | 27.7019 | 28.3933 | 50 | 41.1508 | 201.2175 | 34.1726 | 35.3203 | 108.6689 | ON | 19.89 | 110.2 | 26.8749 | 32.5884 | -1.9439 | 10.4472 | 2.1167 | 2.1167 | 3.866 |  | OK | OK | OK | OK | 112.0674 | OK | OK | OK | OK | OK
44811.88 | 2:43 | 95 | 131.1694 | 128.7758 | 141.9672 | 45.5539 | 108.0094 | 108.0094 | 19.9381 | 17.7425 | 28.577 | 29.0665 | 50 | 40.9532 | 201.0715 | 34.0941 | 35.3247 | 108.6363 | ON | 18.88 | 110.2 | 26.6739 | 31.7672 | -1.1375 | 11.324 | 2.1906 | 2.1906 | 3.8771 |  | OK | OK | OK | OK | 112.2894 | OK | OK | OK | OK | OK
44811.8801 | 2:43 | 95 | 130.3542 | 128.1776 | 141.2504 | 44.6633 | 108.0293 | 108.0293 | 19.694 | 17.526 | 29.2741 | 29.6005 | 50 | 40.787 | 200.8126 | 34.0112 | 35.4094 | 108.655 | ON | 18.88 | 110.2 | 25.7833 | 31.0504 | -1.354 | 12.0745 | 2.1707 | 2.1707 | 3.884 |  | OK | OK | OK | OK | 111.4742 | OK | OK | OK | OK | OK
44811.8802 | 2:43 | 95 | 129.644 | 127.6189 | 140.5687 | 43.6775 | 108.0396 | 108.0396 | 19.462 | 17.3011 | 29.7745 | 30.0986 | 50 | 40.6296 | 201.0785 | 34.0719 | 35.4349 | 108.6482 | ON | 18.88 | 110.2 | 24.7975 | 30.3687 | -1.5789 | 12.7975 | 2.1604 | 2.1604 | 3.8999 |  | OK | OK | OK | OK | 110.764 | OK | OK | OK | OK | OK
44811.8803 | 2:44 | 95 | 128.9904 | 127.1616 | 139.8935 | 43.1408 | 108.0057 | 108.0057 | 19.2665 | 17.1023 | 30.1538 | 30.4308 | 50 | 40.383 | 200.9506 | 33.9069 | 35.3665 | 108.6236 | ON | 18.88 | 110.2 | 24.2608 | 29.6935 | -1.7777 | 13.3285 | 2.1943 | 2.1943 | 3.915 |  | OK | OK | OK | OK | 110.1104 | OK | OK | OK | OK | OK
44811.8805 | 2:44 | 95 | 128.4606 | 126.7003 | 139.2999 | 42.6583 | 107.9848 | 107.9848 | 19.0556 | 16.8777 | 30.4332 | 30.7012 | 50 | 40.1472 | 200.8287 | 33.7845 | 35.3238 | 108.6014 | ON | 18.88 | 110.2 | 23.7783 | 29.0999 | -2.0023 | 13.8235 | 2.2152 | 2.2152 | 3.9296 |  | OK | OK | OK | OK | 109.5806 | OK | OK | OK | OK | OK
44811.8806 | 2:44 | 95 | 128.0392 | 126.2924 | 138.7832 | 42.1344 | 107.9868 | 107.9868 | 18.8514 | 16.6932 | 30.6483 | 30.9448 | 50 | 40.0239 | 201.0075 | 33.7996 | 35.388 | 108.6037 | ON | 18.88 | 110.2 | 23.2544 | 28.5832 | -2.1868 | 14.2516 | 2.2132 | 2.2132 | 3.9417 |  | OK | OK | OK | OK | 109.1592 | OK | OK | OK | OK | OK
44811.8807 | 2:44 | 95 | 127.6638 | 125.9852 | 138.2778 | 41.7517 | 107.9324 | 107.9324 | 18.697 | 16.5479 | 30.8263 | 31.1243 | 50 | 39.9162 | 200.5077 | 33.5947 | 35.3672 | 108.5641 | ON | 17.86 | 110.2 | 23.8917 | 28.0778 | -1.3121 | 14.5764 | 2.2676 | 2.2676 | 3.9404 |  | OK | OK | OK | OK | 109.8038 | OK | OK | OK | OK | OK
44811.8808 | 2:44 | 95 | 127.4542 | 125.6892 | 137.8959 | 41.111 | 107.9987 | 107.9987 | 18.4979 | 16.3831 | 30.9461 | 31.2947 | 50 | 39.6889 | 201.007 | 33.5708 | 35.4419 | 108.6206 | ON | 17.86 | 110.2 | 23.251 | 27.6959 | -1.4769 | 14.9116 | 2.2013 | 2.2013 | 3.966 |  | OK | OK | OK | OK | 109.5942 | OK | OK | OK | OK | OK
44811.8809 | 2:44 | 95 | 127.2227 | 125.5357 | 137.5846 | 40.7195 | 108.0598 | 108.0598 | 18.3115 | 16.1932 | 31.0508 | 31.4239 | 50 | 39.4554 | 200.9442 | 33.542 | 35.3342 | 108.6604 | ON | 17.86 | 110.2 | 22.8595 | 27.3846 | -1.6668 | 15.2307 | 2.1402 | 2.1402 | 3.982 |  | OK | OK | OK | OK | 109.3627 | OK | OK | OK | OK | OK
44811.881 | 2:45 | 95 | 127.052 | 125.2638 | 137.2734 | 40.41 | 107.989 | 107.989 | 18.0904 | 15.9626 | 31.1294 | 31.5229 | 50 | 39.3658 | 200.542 | 33.4537 | 35.3055 | 108.6153 | ON | 17.86 | 110.2 | 22.55 | 27.0734 | -1.8974 | 15.5603 | 2.211 | 2.211 | 3.9811 |  | OK | OK | OK | OK | 109.192 | OK | OK | OK | OK | OK
44811.8812 | 2:45 | 95 | 126.872 | 125.116 | 137.0279 | 40.0168 | 107.9307 | 107.9307 | 17.938 | 15.8026 | 31.2023 | 31.5878 | 50 | 39.1349 | 200.367 | 33.4449 | 35.3687 | 108.581 | ON | 17.86 | 110.2 | 22.1567 | 26.8279 | -2.0574 | 15.7852 | 2.2693 | 2.2693 | 3.9949 |  | OK | OK | OK | OK | 109.012 | OK | OK | OK | OK | OK
44811.8813 | 2:45 | 95 | 126.702 | 125.0454 | 136.8426 | 39.6321 | 107.9882 | 107.9882 | 17.7932 | 15.6301 | 31.2539 | 31.6536 | 50 | 39.0714 | 200.7372 | 33.1519 | 35.3802 | 108.6098 | ON | 17.86 | 110.2 | 21.7721 | 26.6426 | -2.2299 | 16.0236 | 2.2118 | 2.2118 | 4.0065 |  | OK | OK | OK | OK | 108.842 | OK | OK | OK | OK | OK
44811.8814 | 2:45 | 95 | 127.3455 | 125.397 | 137.2139 | 39.2626 | 109.6058 | 109.6058 | 16.2685 | 14.7379 | 31.3065 | 31.6736 | 50 | 35.8294 | 211.0314 | 33.234 | 35.2895 | 110.3254 | ON | 13.61 | 113.8 | 25.6526 | 23.4139 | 1.1279 | 16.9357 | 4.1942 | 4.1942 | 4.4673 |  | OK | OK | OK | OK | 113.7355 | OK | OK | OK | OK | OK
44811.8815 | 2:45 | 95 | 127.476 | 126.0038 | 136.5589 | 42.1703 | 109.5325 | 109.5325 | 15.9629 | 16.2822 | 31.3055 | 31.6434 | 50 | 19.1424 | 205.0883 | 33.0459 | 35.2161 | 109.6986 | ON | -6.5 | 112 | 48.6703 | 24.5589 | 22.7822 | 15.3612 | 2.4675 | 2.4675 | 6.4945 |  | OK | OK | OK | OK | 133.976 | OK | OK | OK | OK | OK
44811.8816 | 2:45 | 95 | 127.6258 | 125.6295 | 135.1935 | 46.5734 | 107.0608 | 107.0608 | 18.1187 | 18.4433 | 31.3231 | 31.679 | 50 | 18.273 | 201.3904 | 33.4807 | 35.4348 | 108.3685 | ON | -7.99 | 110.2 | 54.5634 | 24.9935 | 26.4333 | 13.2357 | 3.1392 | 3.1392 | 6.5536 |  | OK | OK | OK | OK | 135.6158 | OK | OK | OK | OK | OK
44811.8817 | 2:46 | 95 | 127.9844 | 125.4614 | 134.4049 | 48.5736 | 105.6403 | 105.6403 | 20.556 | 20.4314 | 31.3423 | 31.7209 | 50 | 16.8294 | 198.3946 | 34.0162 | 35.5552 | 107.5453 | ON | -11.06 | 108.3 | 59.6336 | 26.1049 | 31.4914 | 11.2895 | 2.6597 | 2.6597 | 6.7586 |  | OK | OK | OK | OK | 139.0444 | OK | OK | OK | OK | OK
44811.8818 | 2:46 | 95 | 128.4124 | 125.4796 | 134.1407 | 50.1662 | 105.4293 | 105.4293 | 22.9587 | 22.2395 | 31.3805 | 31.7908 | 50 | 15.7559 | 196.7801 | 34.4126 | 35.6495 | 107.0362 | ON | -12.65 | 108.3 | 62.8162 | 25.8407 | 34.8895 | 9.5513 | 2.8707 | 2.8707 | 6.9438 |  | OK | OK | OK | OK | 141.0624 | OK | OK | OK | OK | OK
44811.882 | 2:46 | 95 | 129.2476 | 125.625 | 134.1889 | 52.9115 | 105.0192 | 105.0192 | 24.949 | 23.7628 | 31.4243 | 31.8864 | 50 | 15.2832 | 196.3947 | 34.8109 | 35.7866 | 106.7622 | ON | -12.65 | 108.3 | 65.5615 | 25.8889 | 36.4128 | 8.1236 | 3.2808 | 3.2808 | 7.0404 |  | OK | OK | OK | OK | 141.8976 | OK | OK | OK | OK | OK
44811.8821 | 2:46 | 95 | 130.2921 | 125.87 | 134.4588 | 55.2267 | 104.7743 | 104.7743 | 26.6349 | 25.0256 | 31.4797 | 31.9841 | 50 | 14.7648 | 196.1667 | 34.9732 | 35.9184 | 106.7029 | ON | -14.28 | 108.3 | 69.5067 | 26.1588 | 39.3056 | 6.9585 | 3.5257 | 3.5257 | 7.1566 |  | OK | OK | OK | OK | 144.5721 | OK | OK | OK | OK | OK
44811.8822 | 2:46 | 95 | 131.2628 | 126.1311 | 134.8111 | 57.4609 | 104.8005 | 104.8005 | 27.9625 | 26.0944 | 31.512 | 32.1133 | 50 | 14.2078 | 195.7749 | 35.3266 | 36.0691 | 106.6296 | ON | -14.28 | 108.3 | 71.7409 | 26.5111 | 40.3744 | 6.0189 | 3.4995 | 3.4995 | 7.2809 |  | OK | OK | OK | OK | 145.5428 | OK | OK | OK | OK | OK
44811.8823 | 2:46 | 95 | 132.1504 | 126.648 | 135.216 | 58.4659 | 104.7437 | 104.7437 | 28.9799 | 26.9974 | 31.5344 | 32.2007 | 50 | 13.6512 | 195.6845 | 35.5091 | 36.1924 | 106.5755 | ON | -15.96 | 108.3 | 74.4259 | 26.916 | 42.9573 | 5.2033 | 3.5563 | 3.5563 | 7.4207 |  | OK | OK | OK | OK | 148.1104 | OK | OK | OK | OK | OK
44811.8824 | 2:47 | 95 | 133.1088 | 127.1247 | 135.6331 | 59.0501 | 104.6325 | 104.6325 | 29.7207 | 27.6858 | 31.5545 | 32.3456 | 50 | 13.3442 | 195.7024 | 35.5419 | 36.2547 | 106.5453 | ON | -15.96 | 108.3 | 75.0101 | 27.3331 | 43.6458 | 4.6598 | 3.6675 | 3.6675 | 7.5025 |  | OK | OK | OK | OK | 149.0688 | OK | OK | OK | OK | OK
44811.8825 | 2:47 | 95 | 133.8955 | 127.5397 | 136.1016 | 59.2021 | 104.5972 | 104.5972 | 30.2457 | 28.2174 | 31.5778 | 32.475 | 50 | 13.0038 | 195.4938 | 35.8053 | 36.353 | 106.5134 | ON | -15.96 | 108.3 | 75.1621 | 27.8016 | 44.1774 | 4.2576 | 3.7028 | 3.7028 | 7.5872 |  | OK | OK | OK | OK | 149.8555 | OK | OK | OK | OK | OK
44811.8827 | 2:47 | 95 | 134.714 | 128.0266 | 136.6089 | 59.2377 | 104.6008 | 104.6008 | 30.6379 | 28.6861 | 31.5815 | 32.6061 | 50 | 13.034 | 195.5969 | 35.9025 | 36.4336 | 106.4866 | ON | -15.96 | 108.3 | 75.1977 | 28.3089 | 44.6461 | 3.92 | 3.6992 | 3.6992 | 7.5826 |  | OK | OK | OK | OK | 150.674 | OK | OK | OK | OK | OK
44811.8828 | 2:47 | 95 | 135.5354 | 128.5174 | 137.1794 | 59.0365 | 104.5838 | 104.5838 | 30.906 | 29.0424 | 31.6135 | 32.7588 | 50 | 12.8141 | 195.6116 | 36.0018 | 36.5116 | 106.5562 | ON | -17.69 | 108.3 | 76.7265 | 28.8794 | 46.7324 | 3.7163 | 3.7162 | 3.7162 | 7.6438 |  | OK | OK | OK | OK | 153.2254 | OK | OK | OK | OK | OK
44811.8829 | 2:47 | 95 | 136.2986 | 129.0395 | 137.7556 | 58.6335 | 104.7593 | 104.7593 | 31.0876 | 29.3193 | 31.6281 | 32.9119 | 50 | 12.7346 | 195.4967 | 36.0035 | 36.5092 | 106.5691 | ON | -17.69 | 108.3 | 76.3235 | 29.4556 | 47.0093 | 3.5927 | 3.5407 | 3.5407 | 7.6617 |  | OK | OK | OK | OK | 153.9886 | OK | OK | OK | OK | OK
44811.883 | 2:47 | 95 | 136.7688 | 129.2976 | 138.0435 | 58.1022 | 104.631 | 104.631 | 31.2347 | 29.5463 | 31.6505 | 33.0351 | 50 | 13.5419 | 195.3827 | 36.2849 | 36.6005 | 106.4296 | ON | -15.96 | 108.3 | 74.0622 | 29.7435 | 45.5063 | 3.4888 | 3.669 | 3.669 | 7.4387 |  | OK | OK | OK | OK | 152.7288 | OK | OK | OK | OK | OK
44811.8831 | 2:48 | 95 | 136.8983 | 129.4285 | 138.09 | 57.318 | 104.1742 | 104.1742 | 31.3376 | 29.7461 | 31.6664 | 33.1791 | 50 | 14.4182 | 193.8183 | 36.2324 | 36.6638 | 106.1332 | ON | -14.28 | 106.4 | 71.598 | 31.69 | 44.0261 | 3.4331 | 2.2258 | 2.2258 | 7.1611 |  | OK | OK | OK | OK | 151.1783 | OK | OK | OK | OK | OK
44811.8832 | 2:48 | 95 | 140.2542 | 128.3316 | 136.6667 | 51.906 | 96.0851 | 96.0851 | 25.9616 | 30.5469 | 28.037 | 33.6282 | 50 | 52.0746 | 139.1479 | 36.3409 | 36.709 | 102.6149 | OFF | 30.19 | 82.79 | 21.716 | 53.8767 | 0.35691 | 3.0813 | -13.2951 | -13.2951 | 2.304
44811.8833 | 2:48 | 95 | 140.6311 | 125.683 | 129.8199 | 63.945 | 92.5444 | 92.5444 | 30.9416 | 31.1306 | 30.3558 | 33.6049 | 50 | 57.8849 | 117.2452 | 36.2578 | 36.7786 | 101.7245 | OFF | 34.45 | 72.62 | 29.495 | 57.1999 | -3.3194 | 2.4743 | -19.9244 | -19.9244 | 1.8178
44811.8835 | 2:48 | 95 | 139.7378 | 124.0793 | 122.1831 | 77.7934 | 89.7747 | 89.7747 | 31.8825 | 32.4638 | 31.242 | 33.7489 | 50 | 59.4516 | 104.5956 | 36.3263 | 36.7831 | 100.9321 | OFF | 36.1 | 64.21 | 41.6934 | 57.9731 | -3.6362 | 1.2851 | -25.5647 | -25.5647 | 1.6088
44811.8836 | 2:48 | 95 | 138.4078 | 122.3497 | 116.2287 | 87.3619 | 87.949 | 87.949 | 31.846 | 33.5868 | 31.5626 | 34.1201 | 50 | 60.4505 | 92.5586 | 36.423 | 36.9396 | 100.2201 | OFF | 36.91 | 58.13 | 50.4519 | 58.0987 | -3.3232 | 0.53335 | -29.819 | -29.819 | 1.4272
44811.8837 | 2:48 | 95 | 136.9998 | 120.7953 | 111.8325 | 93.3218 | 86.2291 | 86.2291 | 31.8906 | 34.4143 | 31.6753 | 34.5873 | 50 | 61.334 | 82.7576 | 36.599 | 37.0046 | 99.6582 | OFF | 37.71 | 51.63 | 55.6118 | 60.2025 | -3.2957 | 0.17302 | -34.599 | -34.599 | 1.2818
44811.8838 | 2:49 | 95 | 135.7275 | 119.462 | 109.0043 | 96.6077 | 85.6786 | 85.6786 | 31.8635 | 34.8615 | 31.7062 | 34.8738 | 50 | 61.6933 | 76.0709 | 36.5793 | 37.0505 | 99.2738 | OFF | 37.71 | 48.19 | 58.8978 | 60.8143 | -2.8485 | 0.01231 | -37.4886 | -37.4886 | 1.1882
44811.8839 | 2:49 | 95 | 134.5983 | 118.2227 | 107.3125 | 97.6593 | 86.1748 | 86.1748 | 31.862 | 35.1063 | 31.7154 | 34.9852 | 50 | 61.8927 | 69.3734 | 36.8166 | 37.1537 | 98.958 | OFF | 37.71 | 43.86 | 59.9493 | 63.4525 | -2.6037 | -0.12116 | -42.3148 | -42.3148 | 1.0977
44811.884 | 2:49 | 95 | 133.3913 | 117.059 | 106.4161 | 97.3462 | 87.4563 | 87.4563 | 31.8693 | 35.0944 | 31.7433 | 35.0035 | 50 | 61.8753 | 66.1815 | 36.8491 | 37.2056 | 98.6445 | OFF | 37.71 | 41.6 | 59.6362 | 64.8161 | -2.6156 | -0.09088 | -45.8563 | -45.8563 | 1.0562
44811.8842 | 2:49 | 95 | 132.3261 | 116.1404 | 105.8866 | 96.7765 | 88.8332 | 88.8332 | 31.883 | 35.0792 | 31.764 | 35.0494 | 50 | 61.9099 | 64.9927 | 36.8432 | 37.3541 | 98.4004 | OFF | 37.71 | 40.07 | 59.0665 | 65.8166 | -2.6308 | -0.02978 | -48.7632 | -48.7632 | 1.0402
44811.8843 | 2:49 | 95 | 131.26 | 115.2731 | 105.4663 | 96.2602 | 90.0985 | 90.0985 | 31.9036 | 35.1743 | 31.7821 | 35.0853 | 50 | 62.0817 | 63.8355 | 36.9457 | 37.3714 | 98.2201 | OFF | 38.5 | 39.29 | 57.7602 | 66.1763 | -3.3257 | -0.08891 | -50.8085 | -50.8085 | 1.0228
44811.8844 | 2:49 | 95 | 130.3904 | 114.4882 | 105.1685 | 95.8584 | 91.1616 | 91.1616 | 31.939 | 35.2732 | 31.8208 | 35.1697 | 50 | 62.2036 | 63.2634 | 37.0601 | 37.4562 | 98.0862 | OFF | 38.5 | 39.29 | 57.3584 | 65.8785 | -3.2269 | -0.10348 | -51.8716 | -51.8716 | 1.0138
44811.8845 | 2:50 | 95 | 129.4122 | 113.7947 | 104.8523 | 95.7255 | 91.9603 | 91.9603 | 31.9642 | 35.5249 | 31.8276 | 35.2892 | 50 | 62.4918 | 61.9934 | 37.1353 | 37.5003 | 97.9531 | OFF | 38.5 | 37.71 | 57.2255 | 67.1423 | -2.9751 | -0.23578 | -54.2503 | -54.2503 | 0.99354
44811.8846 | 2:50 | 95 | 128.4185 | 113.1662 | 104.5311 | 95.5172 | 92.6736 | 92.6736 | 31.9948 | 35.6581 | 31.8379 | 35.4154 | 50 | 62.669 | 61.9158 | 37.1504 | 37.5246 | 97.7646 | OFF | 38.5 | 37.71 | 57.0172 | 66.8211 | -2.8419 | -0.24273 | -54.9635 | -54.9635 | 0.99026
44811.8847 | 2:50 | 95 | 127.6024 | 112.5871 | 104.3157 | 95.3286 | 93.3243 | 93.3243 | 32.0213 | 35.8913 | 31.8661 | 35.6157 | 50 | 62.9911 | 62.1561 | 37.1315 | 37.6563 | 97.6054 | OFF | 38.5 | 38.5 | 56.8286 | 65.8157 | -2.6087 | -0.27557 | -54.8244 | -54.8244 | 0.98925
44811.8849 | 2:50 | 95 | 126.8354 | 112.0689 | 104.0609 | 95.2112 | 93.8107 | 93.8107 | 32.0685 | 36.2061 | 32.0424 | 35.7987 | 50 | 63.3244 | 62.3916 | 37.3139 | 37.6934 | 97.4502 | OFF | 39.29 | 38.5 | 55.9212 | 65.5609 | -3.0839 | -0.40742 | -55.3107 | -55.3107 | 0.98804
44811.885 | 2:50 | 95 | 126.0886 | 111.6016 | 103.8354 | 95.0942 | 94.1777 | 94.1777 | 32.1331 | 36.454 | 32.6065 | 36.1335 | 50 | 63.6502 | 62.7282 | 37.4389 | 37.8084 | 97.3139 | OFF | 39.29 | 38.5 | 55.8042 | 65.3354 | -2.836 | -0.32057 | -55.6777 | -55.6777 | 0.98823
44811.8851 | 2:50 | 95 | 125.3341 | 111.1496 | 103.5986 | 95.0052 | 94.4829 | 94.4829 | 32.1943 | 36.5849 | 34.167 | 36.5474 | 50 | 64.0494 | 63.0902 | 37.5417 | 37.8317 | 97.1497 | OFF | 40.07 | 39.29 | 54.9352 | 64.3086 | -3.4851 | -0.03753 | -55.1929 | -55.1929 | 0.98782
44811.8852 | 2:51 | 95 | 124.6767 | 110.7245 | 103.3678 | 94.9822 | 94.6562 | 94.6562 | 32.2709 | 36.6181 | 34.848 | 36.9584 | 50 | 64.3693 | 63.3935 | 37.5784 | 37.9795 | 97.0135 | OFF | 40.07 | 39.29 | 54.9122 | 64.0778 | -3.4519 | 0.34034 | -55.3662 | -55.3662 | 0.98766
44811.8853 | 2:51 | 95 | 124.0228 | 110.2957 | 103.1138 | 94.951 | 94.7938 | 94.7938 | 32.4105 | 36.4856 | 36.0146 | 37.3072 | 50 | 64.6556 | 63.6731 | 37.7368 | 38.0688 | 96.8998 | OFF | 40.07 | 39.29 | 54.881 | 63.8238 | -3.5844 | 0.82157 | -55.5038 | -55.5038 | 0.98762
44811.8854 | 2:51 | 95 | 123.4101 | 109.9686 | 102.9083 | 94.8788 | 94.8687 | 94.8687 | 32.5778 | 36.467 | 36.41 | 37.5923 | 50 | 64.9172 | 64.0218 | 37.8687 | 38.1638 | 96.7161 | OFF | 40.07 | 40.07 | 54.8088 | 62.8383 | -3.603 | 1.1254 | -54.7987 | -54.7987 | 0.98875
44811.8855 | 2:51 | 95 | 122.8606 | 109.6113 | 102.6733 | 94.9713 | 94.9091 | 94.9091 | 32.7062 | 36.8401 | 36.7298 | 37.8115 | 50 | 65.2206 | 64.1512 | 37.9134 | 38.2041 | 96.5948 | OFF | 40.84 | 40.07 | 54.1313 | 62.6033 | -3.9999 | 0.97142 | -54.8391 | -54.8391 | 0.98662
44811.8857 | 2:51 | 95 | 122.2856 | 109.2816 | 102.4888 | 94.9956 | 94.9533 | 94.9533 | 32.8213 | 36.7858 | 36.9919 | 38.0072 | 50 | 65.4584 | 64.4487 | 38.1297 | 38.3617 | 96.4062 | OFF | 40.84 | 40.07 | 54.1556 | 62.4188 | -4.0542 | 1.2214 | -54.8833 | -54.8833 | 0.9874
44811.8858 | 2:51 | 95 | 121.7511 | 108.9318 | 102.2562 | 94.9789 | 94.9499 | 94.9499 | 32.9998 | 36.6397 | 37.2932 | 38.167 | 50 | 65.6757 | 64.6208 | 38.2451 | 38.3961 | 96.2475 | OFF | 40.84 | 40.07 | 54.1389 | 62.1862 | -4.2003 | 1.5273 | -54.8799 | -54.8799 | 0.98687
44811.8859 | 2:52 | 95 | 121.1851 | 108.6022 | 102.027 | 94.8645 | 94.9182 | 94.9182 | 33.2396 | 36.1403 | 37.4045 | 38.3061 | 50 | 65.8816 | 64.8157 | 38.3113 | 38.5097 | 96.0932 | OFF | 40.84 | 40.07 | 54.0245 | 61.957 | -4.6997 | 2.1658 | -54.8482 | -54.8482 | 0.98677
44811.886 | 2:52 | 95 | 120.6749 | 108.2719 | 101.8349 | 94.8678 | 94.8894 | 94.8894 | 33.6289 | 35.7048 | 37.5837 | 38.4419 | 50 | 66.0959 | 65.0066 | 38.4983 | 38.6675 | 95.8898 | OFF | 41.6 | 40.84 | 53.2678 | 60.9949 | -5.8952 | 2.7371 | -54.0494 | -54.0494 | 0.98652
44811.8861 | 2:52 | 95 | 120.1152 | 107.9568 | 101.5867 | 94.8417 | 94.814 | 94.814 | 34.0765 | 35.4099 | 37.7592 | 38.5588 | 50 | 66.2649 | 65.1581 | 38.5933 | 38.6915 | 95.6991 | OFF | 41.6 | 40.84 | 53.2417 | 60.7467 | -6.1901 | 3.1488 | -53.974 | -53.974 | 0.98633
44811.8862 | 2:52 | 95 | 119.6456 | 107.6591 | 101.3548 | 94.7675 | 94.7128 | 94.7128 | 34.3682 | 35.3205 | 37.7751 | 38.7338 | 50 | 66.4668 | 65.3323 | 38.6028 | 38.7882 | 95.4997 | OFF | 41.6 | 40.84 | 53.1675 | 60.5148 | -6.2796 | 3.4133 | -53.8728 | -53.8728 | 0.98602
44811.8864 | 2:52 | 95 | 119.1245 | 107.3057 | 101.0968 | 94.776 | 94.5853 | 94.5853 | 34.6003 | 35.3511 | 37.9855 | 38.888 | 50 | 66.6882 | 65.568 | 38.7103 | 38.8613 | 95.2538 | OFF | 41.6 | 40.84 | 53.176 | 60.2568 | -6.2489 | 3.5369 | -53.7452 | -53.7452 | 0.98624
44811.8865 | 2:52 | 95 | 118.6282 | 107.0185 | 100.8351 | 94.5817 | 94.4447 | 94.4447 | 34.8421 | 35.5281 | 38.1969 | 38.9993 | 50 | 66.8673 | 65.7305 | 38.7674 | 38.9257 | 95.0638 | OFF | 41.6 | 40.84 | 52.9817 | 59.9951 | -6.072 | 3.4712 | -53.6047 | -53.6047 | 0.98606
44811.8866 | 2:53 | 95 | 118.1877 | 106.8081 | 100.6191 | 94.5606 | 94.3497 | 94.3497 | 35.1035 | 35.6798 | 38.3404 | 39.11 | 50 | 67.014 | 65.8695 | 39.0495 | 38.9879 | 94.9808 | OFF | 42.36 | 40.84 | 52.2007 | 59.7791 | -6.6802 | 3.4302 | -53.5097 | -53.5097 | 0.98599
44811.8867 | 2:53 | 95 | 117.7756 | 106.568 | 100.4599 | 94.7489 | 94.2658 | 94.2658 | 35.3927 | 35.8251 | 38.4789 | 39.1923 | 50 | 67.1305 | 66.0049 | 39.0917 | 39.0729 | 94.9887 | OFF | 42.36 | 41.6 | 52.3888 | 58.8599 | -6.5349 | 3.3672 | -52.6658 | -52.6658 | 0.98624
44811.8868 | 2:53 | 95 | 117.4233 | 106.3938 | 100.3658 | 94.8049 | 94.2615 | 94.2615 | 35.7039 | 36.0504 | 38.5193 | 39.3278 | 50 | 67.3221 | 66.1313 | 39.1117 | 39.1726 | 95.0485 | OFF | 42.36 | 41.6 | 52.4449 | 58.7658 | -6.3096 | 3.2774 | -52.6615 | -52.6615 | 0.98548
44811.8869 | 2:53 | 95 | 118.392 | 106.4536 | 107.7695 | 84.6589 | 94.5281 | 94.5281 | 36.0267 | 36.4381 | 37.3336 | 37.1767 | 50 | 63.9044 | 110.6022 | 39.2124 | 39.2188 | 95.2701 | OFF | 39.29 | 69.9 | 45.3689 | 37.8695 | -2.8519 | 0.73859 | -24.6282 | -24.6282 | 1.5941
44811.8871 | 2:53 | 95 | 120.1074 | 107.8386 | 126.3013 | 62.186 | 97.009 | 97.009 | 31.5846 | 32.6445 | 31.7772 | 34.2156 | 50 | 53.6526 | 174.5519 | 39.2018 | 39.236 | 98.8715 | OFF | 31.06 | 98.41 | 31.126 | 27.8913 | 1.5845 | 1.571 | 1.401 | 1.401 | 2.7688
44811.8872 | 2:53 | 95 | 118.6532 | 112.5448 | 128.9802 | 57.3721 | 102.2267 | 102.2267 | 29.7848 | 28.9734 | 29.4911 | 33.4569 | 50 | 52.9378 | 186.9639 | 38.6004 | 38.9421 | 102.9987 | ON | 30.19 | 104.4 | 27.1821 | 24.5802 | -1.2166 | 4.4835 | 2.1733 | 2.1733 | 2.9815 |  | OK | OK | OK | OK | 88.4632 | OK | OK | OK | OK | OK
44811.8873 | 2:54 | 95 | 117.9847 | 115.0734 | 128.3477 | 55.0372 | 104.0674 | 104.0674 | 29.3761 | 30.1617 | 28.6515 | 31.8694 | 50 | 52.3034 | 191.47 | 38.2385 | 38.7071 | 104.7333 | ON | 30.19 | 106.4 | 24.8472 | 21.9477 | -0.0283 | 1.7077 | 2.3326 | 2.3326 | 3.077 |  | OK | OK | OK | OK | 87.7947 | OK | OK | OK | OK | OK
44811.8874 | 2:54 | 95 | 117.7003 | 116.2632 | 128.184 | 54.9116 | 104.7911 | 104.7911 | 29.3226 | 28.1116 | 28.1314 | 28.0566 | 50 | 52.108 | 192.8344 | 37.9889 | 38.4517 | 105.5088 | ON | 30.19 | 106.4 | 24.7216 | 21.784 | -2.0784 | -0.05499 | 1.6089 | 1.6089 | 3.1064 |  | OK | OK | OK | OK | 87.5103 | OK | OK | OK | OK | OK
44811.8875 | 2:54 | 95 | 118.017 | 117.1666 | 128.5011 | 55.3503 | 105.3704 | 105.3704 | 29.7572 | 29.6761 | 27.5843 | 27.0457 | 50 | 51.8597 | 194.1485 | 37.8822 | 38.3493 | 106.1129 | ON | 29.31 | 106.4 | 26.0403 | 22.1011 | 0.36609 | -2.6304 | 1.0296 | 1.0296 | 3.1378 |  | OK | OK | OK | OK | 88.707 | OK | OK | OK | OK | OK
44811.8876 | 2:54 | 95 | 118.6193 | 118.0199 | 128.9661 | 58.375 | 105.6971 | 105.6971 | 30.1771 | 30.7371 | 27.1347 | 26.6326 | 50 | 51.4993 | 194.8868 | 37.8364 | 38.0869 | 106.4811 | ON | 29.31 | 106.4 | 29.065 | 22.5661 | 1.4271 | -4.1045 | 0.7029 | 0.7029 | 3.166 |  | OK | Low Charge | OK | OK | 89.3093 | OK | OK | OK | OK | OK
44811.8877 | 2:54 | 95 | 119.4488 | 118.8229 | 129.4708 | 61.2601 | 105.9835 | 105.9835 | 30.0269 | 31.1466 | 26.7316 | 26.3537 | 50 | 51.277 | 195.9157 | 37.8703 | 38.0817 | 106.8038 | ON | 29.31 | 108.3 | 31.9501 | 21.1708 | 1.8366 | -4.7929 | 2.3165 | 2.3165 | 3.1923 |  | OK | OK | OK | OK | 90.1388 | OK | OK | OK | OK | OK
44811.8879 | 2:54 | 95 | 120.3601 | 119.6439 | 130.1458 | 63.29 | 106.2691 | 106.2691 | 29.7548 | 31.3695 | 26.3326 | 26.0914 | 50 | 50.9652 | 196.212 | 37.8402 | 37.9981 | 107.1094 | ON | 28.42 | 108.3 | 34.87 | 21.8458 | 2.9495 | -5.2781 | 2.0309 | 2.0309 | 3.2119 |  | OK | OK | OK | OK | 91.9401 | OK | OK | OK | OK | OK
44811.888 | 2:55 | 95 | 121.2017 | 120.3309 | 130.7862 | 64.6531 | 106.4059 | 106.4059 | 29.3928 | 31.3739 | 25.9695 | 25.9393 | 50 | 50.7763 | 196.1857 | 37.6952 | 37.9594 | 107.3267 | ON | 28.42 | 108.3 | 36.2331 | 22.4862 | 2.9539 | -5.4347 | 1.8941 | 1.8941 | 3.2208 |  | OK | OK | OK | OK | 92.7817 | OK | OK | OK | OK | OK
44811.8881 | 2:55 | 95 | 121.949 | 120.9601 | 131.4311 | 65.6679 | 106.5263 | 106.5263 | 28.5555 | 31.279 | 25.7231 | 26.0347 | 50 | 50.5065 | 196.5774 | 37.6907 | 37.8929 | 107.4511 | ON | 28.42 | 108.3 | 37.2479 | 23.1311 | 2.859 | -5.2443 | 1.7737 | 1.7737 | 3.2401 |  | OK | OK | OK | OK | 93.529 | OK | OK | OK | OK | OK
44811.8882 | 2:55 | 95 | 122.6933 | 121.5603 | 132.1009 | 66.7852 | 106.6336 | 106.6336 | 28.1949 | 31.0561 | 25.5003 | 26.22 | 50 | 50.4108 | 196.9013 | 37.6489 | 37.7815 | 107.5917 | ON | 28.42 | 108.3 | 38.3651 | 23.8009 | 2.6361 | -4.8361 | 1.6664 | 1.6664 | 3.2499 |  | OK | OK | OK | OK | 94.2733 | OK | OK | OK | OK | OK
44811.8883 | 2:55 | 95 | 123.4159 | 122.1132 | 132.7556 | 67.828 | 106.7158 | 106.7158 | 28.1503 | 30.8339 | 25.345 | 26.3434 | 50 | 50.0523 | 196.836 | 37.5176 | 37.6105 | 107.7026 | ON | 28.42 | 108.3 | 39.408 | 24.4556 | 2.4139 | -4.4904 | 1.5842 | 1.5842 | 3.2669 |  | OK | OK | OK | OK | 94.9959 | OK | OK | OK | OK | OK
44811.8884 | 2:55 | 95 | 124.1091 | 122.7221 | 133.4921 | 68.6712 | 106.8649 | 106.8649 | 28.0337 | 30.5646 | 25.2533 | 26.2639 | 50 | 50.1414 | 197.2925 | 37.4738 | 37.4898 | 107.8939 | ON | 28.42 | 108.3 | 40.2512 | 25.1921 | 2.1446 | -4.3007 | 1.4351 | 1.4351 | 3.2694 |  | OK | OK | OK | OK | 95.6891 | OK | OK | OK | OK | OK
44811.8886 | 2:55 | 95 | 124.9121 | 123.3311 | 134.2305 | 69.3386 | 107.0369 | 107.0369 | 27.8535 | 30.262 | 25.0544 | 26.1235 | 50 | 50.0459 | 197.7524 | 37.4823 | 37.4248 | 108.0824 | ON | 28.42 | 108.3 | 40.9186 | 25.9305 | 1.842 | -4.1385 | 1.2631 | 1.2631 | 3.2813 |  | OK | OK | OK | OK | 96.4921 | OK | OK | OK | OK | OK
44811.8887 | 2:56 | 95 | 125.5577 | 123.9339 | 134.9841 | 69.8572 | 107.2675 | 107.2675 | 27.7686 | 29.7782 | 24.8865 | 25.9139 | 50 | 49.7113 | 198.3404 | 37.2967 | 37.372 | 108.2417 | ON | 27.51 | 108.3 | 42.3472 | 26.6841 | 2.2682 | -3.8643 | 1.0325 | 1.0325 | 3.3075 |  | OK | OK | OK | OK | 98.0477 | OK | OK | OK | OK | OK
44811.8888 | 2:56 | 95 | 126.1187 | 124.422 | 135.644 | 70.5156 | 107.2181 | 107.2181 | 27.4692 | 28.8812 | 24.5307 | 25.8065 | 50 | 48.8396 | 197.184 | 37.1815 | 37.3033 | 108.2537 | ON | 26.6 | 108.3 | 43.9156 | 27.344 | 2.2812 | -3.0747 | 1.0819 | 1.0819 | 3.3347 |  | OK | OK | OK | OK | 99.5187 | OK | OK | OK | OK | OK
44811.8889 | 2:56 | 95 | 126.8633 | 124.9818 | 136.3615 | 71.2053 | 107.3984 | 107.3984 | 27.4588 | 27.3183 | 24.3273 | 25.8071 | 50 | 49.1564 | 198.7984 | 37.1178 | 37.2807 | 108.4176 | ON | 27.51 | 108.3 | 43.6953 | 28.0615 | -0.1917 | -1.5112 | 0.9016 | 0.9016 | 3.3434 |  | OK | Low Charge | OK | OK | 99.3533 | OK | OK | OK | OK | OK
44811.889 | 2:56 | 95 | 127.5165 | 125.5087 | 137.0594 | 71.9747 | 107.5675 | 107.5675 | 27.1063 | 25.6235 | 24.2665 | 25.8671 | 50 | 49.018 | 199.1797 | 37.0435 | 37.0482 | 108.5935 | ON | 27.51 | 108.3 | 44.4647 | 28.7594 | -1.8865 | 0.24364 | 0.7325 | 0.7325 | 3.3567 |  | OK | Low Charge | OK | OK | 100.0065 | OK | OK | OK | OK | OK
44811.8891 | 2:56 | 95 | 128.0976 | 126.0158 | 137.805 | 72.7115 | 107.6535 | 107.6535 | 26.7858 | 25.2472 | 24.1123 | 25.8693 | 50 | 48.7647 | 199.3454 | 36.9845 | 37.0692 | 108.6993 | ON | 26.6 | 108.3 | 46.1115 | 29.505 | -1.3528 | 0.62211 | 0.6465 | 0.6465 | 3.3727 |  | OK | Low Charge | OK | OK | 101.4976 | OK | OK | OK | OK | OK
44811.8893 | 2:56 | 95 | 128.8238 | 126.602 | 138.5085 | 73.3878 | 107.8715 | 107.8715 | 26.516 | 24.9297 | 23.9046 | 25.756 | 50 | 48.5317 | 200.2692 | 36.825 | 37.0208 | 108.8798 | ON | 26.6 | 110.2 | 46.7878 | 28.3085 | -1.6703 | 0.82633 | 2.3285 | 2.3285 | 3.3997 |  | OK | OK | OK | OK | 102.2238 | OK | OK | OK | OK | OK
44811.8894 | 2:57 | 95 | 129.3809 | 127.1677 | 139.2479 | 73.7952 | 108.1304 | 108.1304 | 26.3218 | 24.7626 | 24.8682 | 25.867 | 50 | 48.4434 | 200.5514 | 36.7361 | 36.8979 | 109.0858 | ON | 26.6 | 110.2 | 47.1952 | 29.0479 | -1.8375 | 1.1045 | 2.0696 | 2.0696 | 3.4089 |  | OK | OK | OK | OK | 102.7809 | OK | OK | OK | OK | OK
44811.8895 | 2:57 | 95 | 130.0364 | 127.7487 | 139.9956 | 74.1659 | 108.2811 | 108.2811 | 26.0868 | 24.5059 | 24.4399 | 25.6583 | 50 | 48.4907 | 200.9917 | 36.7059 | 36.7978 | 109.225 | ON | 26.6 | 110.2 | 47.5659 | 29.7956 | -2.0941 | 1.1523 | 1.9189 | 1.9189 | 3.4133 |  | OK | OK | OK | OK | 103.4364 | OK | OK | OK | OK | OK
44811.8896 | 2:57 | 95 | 130.5916 | 128.2406 | 140.6935 | 74.5001 | 108.4275 | 108.4275 | 25.9453 | 24.4206 | 24.1592 | 25.6137 | 50 | 48.3101 | 201.2782 | 36.5861 | 36.7376 | 109.3716 | ON | 26.6 | 110.2 | 47.9001 | 30.4935 | -2.1794 | 1.1931 | 1.7725 | 1.7725 | 3.4277 |  | OK | OK | OK | OK | 103.9916 | OK | OK | OK | OK | OK
44811.8897 | 2:57 | 95 | 131.1667 | 128.7148 | 141.3639 | 74.6658 | 108.6684 | 108.6684 | 25.8174 | 24.2121 | 23.8838 | 25.9041 | 50 | 47.8458 | 202.0407 | 36.6307 | 36.6648 | 109.5564 | ON | 25.68 | 110.2 | 48.9858 | 31.1639 | -1.4679 | 1.692 | 1.5316 | 1.5316 | 3.4653 |  | OK | OK | OK | OK | 105.4867 | OK | OK | OK | OK | OK
44811.8898 | 2:57 | 95 | 131.5482 | 129.1771 | 141.9453 | 74.9466 | 108.6676 | 108.6676 | 25.6739 | 24.1508 | 23.8015 | 26.679 | 50 | 47.8246 | 201.7333 | 36.4873 | 36.7338 | 109.5425 | ON | 25.68 | 110.2 | 49.2666 | 31.7453 | -1.5292 | 2.5282 | 1.5324 | 1.5324 | 3.4616 |  | OK | OK | OK | OK | 105.8682 | OK | OK | OK | OK | OK
44811.8899 | 2:57 | 95 | 132.1111 | 129.5529 | 142.4281 | 74.9487 | 108.5262 | 108.5262 | 25.475 | 23.9316 | 23.7849 | 27.4042 | 50 | 47.6016 | 201.2645 | 36.331 | 36.7437 | 109.4347 | ON | 25.68 | 110.2 | 49.2687 | 32.2281 | -1.7484 | 3.4726 | 1.6738 | 1.6738 | 3.4664 |  | OK | OK | OK | OK | 106.4311 | OK | OK | OK | OK | OK
44811.8901 | 2:58 | 95 | 132.3758 | 129.84 | 142.8747 | 74.4378 | 108.4416 | 108.4416 | 25.4191 | 23.9773 | 23.7812 | 27.7999 | 50 | 47.9682 | 201.3649 | 36.1918 | 36.7286 | 109.3897 | ON | 25.68 | 110.2 | 48.7578 | 32.6747 | -1.7027 | 3.8227 | 1.7584 | 1.7584 | 3.4478 |  | OK | OK | OK | OK | 106.6958 | OK | OK | OK | OK | OK
44811.8902 | 2:58 | 95 | 132.6942 | 130.1052 | 143.2524 | 73.9111 | 108.3914 | 108.3914 | 25.2024 | 23.701 | 23.6913 | 27.8821 | 50 | 47.6645 | 200.989 | 36.2615 | 36.7272 | 109.2977 | ON | 25.68 | 110.2 | 48.2311 | 33.0524 | -1.979 | 4.1811 | 1.8086 | 1.8086 | 3.4585 |  | OK | OK | OK | OK | 107.0142 | OK | OK | OK | OK | OK
44811.8903 | 2:58 | 95 | 132.8952 | 130.301 | 143.5334 | 73.5194 | 108.2602 | 108.2602 | 25.0876 | 23.6756 | 23.5959 | 27.7543 | 50 | 47.5321 | 200.97 | 36.1465 | 36.7208 | 109.2123 | ON | 25.68 | 110.2 | 47.8394 | 33.3334 | -2.0044 | 4.0787 | 1.9398 | 1.9398 | 3.4656 |  | OK | OK | OK | OK | 107.2152 | OK | OK | OK | OK | OK
44811.8904 | 2:58 | 95 | 133.0626 | 130.5047 | 143.7866 | 73.26 | 108.178 | 108.178 | 24.8531 | 23.4897 | 23.4838 | 27.5091 | 50 | 47.3006 | 200.3175 | 36.1993 | 36.6328 | 109.1269 | ON | 25.68 | 110.2 | 47.58 | 33.5866 | -2.1903 | 4.0195 | 2.022 | 2.022 | 3.468 |  | OK | OK | OK | OK | 107.3826 | OK | OK | OK | OK | OK
44811.8905 | 2:58 | 95 | 133.1678 | 130.5993 | 143.9998 | 72.8006 | 108.1065 | 108.1065 | 24.6909 | 23.3328 | 23.2546 | 27.2311 | 50 | 47.3372 | 200.5998 | 36.0529 | 36.5389 | 109.0323 | ON | 25.68 | 110.2 | 47.1206 | 33.7998 | -2.3472 | 3.8983 | 2.0935 | 2.0935 | 3.4705 |  | OK | OK | OK | OK | 107.4878 | OK | OK | OK | OK | OK
44811.8906 | 2:58 | 95 | 133.2803 | 130.6598 | 144.1341 | 72.4838 | 108.0312 | 108.0312 | 24.5508 | 23.2138 | 23.2108 | 26.9792 | 50 | 47.2129 | 200.1242 | 35.9455 | 36.4218 | 108.9891 | ON | 25.68 | 110.2 | 46.8038 | 33.9341 | -2.4663 | 3.7654 | 2.1688 | 2.1688 | 3.4698 |  | OK | OK | OK | OK | 107.6003 | OK | OK | OK | OK | OK
44811.8908 | 2:59 | 95 | 133.3358 | 130.7936 | 144.2324 | 72.248 | 107.9057 | 107.9057 | 24.3966 | 23.1656 | 23.0437 | 26.7213 | 50 | 47.0048 | 199.8444 | 36.0195 | 36.4004 | 108.8851 | ON | 25.68 | 108.3 | 46.568 | 35.9324 | -2.5144 | 3.5557 | 0.3943 | 0.3943 | 3.4769 |  | OK | Low Charge | OK | OK | 107.6558 | OK | OK | OK | OK | OK
44811.8909 | 2:59 | 95 | 133.3981 | 130.8306 | 144.3554 | 72.1795 | 107.8163 | 107.8163 | 24.221 | 22.9551 | 22.9793 | 26.4236 | 50 | 46.8456 | 199.5317 | 35.9486 | 36.2877 | 108.797 | ON | 24.74 | 108.3 | 47.4395 | 36.0554 | -1.7849 | 3.4685 | 0.4837 | 0.4837 | 3.4809 |  | OK | Low Charge | OK | OK | 108.6581 | OK | OK | OK | OK | OK
44811.891 | 2:59 | 95 | 133.6172 | 130.892 | 144.5161 | 71.9506 | 107.8536 | 107.8536 | 24.0924 | 22.9028 | 22.8068 | 26.2026 | 50 | 46.7985 | 199.7841 | 35.8771 | 36.2095 | 108.8002 | ON | 24.74 | 108.3 | 47.2106 | 36.2161 | -1.8372 | 3.2997 | 0.4464 | 0.4464 | 3.4876 |  | OK | Low Charge | OK | OK | 108.8772 | OK | OK | OK | OK | OK
44811.8911 | 2:59 | 95 | 133.6504 | 130.9343 | 144.5954 | 71.7824 | 107.7233 | 107.7233 | 23.9266 | 22.6671 | 22.6591 | 25.9994 | 50 | 46.5037 | 199.0924 | 35.7587 | 36.1718 | 108.685 | ON | 24.74 | 108.3 | 47.0424 | 36.2954 | -2.0729 | 3.3323 | 0.5767 | 0.5767 | 3.4931 |  | OK | Low Charge | OK | OK | 108.9104 | OK | OK | OK | OK | OK
44811.8912 | 2:59 | 95 | 133.6664 | 130.9089 | 144.6313 | 71.8235 | 107.6285 | 107.6285 | 23.8066 | 22.5688 | 22.5744 | 25.7993 | 50 | 46.6578 | 198.7662 | 35.6862 | 36.1362 | 108.6034 | ON | 24.74 | 108.3 | 47.0835 | 36.3313 | -2.1712 | 3.2305 | 0.6715 | 0.6715 | 3.479 |  | OK | Low Charge | OK | OK | 108.9264 | OK | OK | OK | OK | OK
44811.8913 | 2:59 | 95 | 133.6198 | 130.9741 | 144.7368 | 71.7946 | 107.5768 | 107.5768 | 23.6838 | 22.5185 | 22.5523 | 25.6204 | 50 | 46.4862 | 198.5936 | 35.6501 | 35.9545 | 108.5692 | ON | 24.74 | 108.3 | 47.0546 | 36.4368 | -2.2215 | 3.1019 | 0.7232 | 0.7232 | 3.486 |  | OK | Low Charge | OK | OK | 108.8798 | OK | OK | OK | OK | OK
44811.8914 | 3:00 | 95 | 133.6892 | 130.961 | 144.7622 | 71.7671 | 107.4281 | 107.4281 | 23.5689 | 22.4625 | 22.3447 | 25.44 | 50 | 46.2758 | 198.3321 | 35.6478 | 35.9751 | 108.4198 | ON | 24.74 | 108.3 | 47.0271 | 36.4622 | -2.2776 | 2.9776 | 0.8719 | 0.8719 | 3.4937 |  | OK | Low Charge | OK | OK | 108.9492 | OK | OK | OK | OK | OK
44811.8916 | 3:00 | 95 | 133.6681 | 130.9671 | 144.7629 | 71.9021 | 107.368 | 107.368 | 23.413 | 22.1756 | 22.1751 | 25.2798 | 50 | 46.0481 | 198.1253 | 35.4735 | 35.9443 | 108.3581 | ON | 24.74 | 108.3 | 47.1621 | 36.4629 | -2.5644 | 3.1042 | 0.932 | 0.932 | 3.5034 |  | OK | Low Charge | OK | OK | 108.9281 | OK | OK | OK | OK | OK
44811.8917 | 3:00 | 95 | 133.6531 | 130.9733 | 144.8762 | 72.0584 | 107.3397 | 107.3397 | 23.2834 | 22.2193 | 22.1312 | 25.1322 | 50 | 46.0526 | 198.1881 | 35.4509 | 35.6886 | 108.3621 | ON | 24.74 | 108.3 | 47.3184 | 36.5762 | -2.5207 | 2.9129 | 0.9603 | 0.9603 | 3.5042 |  | OK | Low Charge | OK | OK | 108.9131 | OK | OK | OK | OK | OK
44811.8918 | 3:00 | 95 | 133.6367 | 131.022 | 144.924 | 72.1716 | 107.2504 | 107.2504 | 23.13 | 21.9979 | 21.938 | 24.9811 | 50 | 45.8758 | 197.7287 | 35.4109 | 35.6187 | 108.2363 | ON | 23.8 | 108.3 | 48.3716 | 36.624 | -1.802 | 2.9832 | 1.0496 | 1.0496 | 3.5068 |  | OK | OK | OK | OK | 109.8367 | OK | OK | OK | OK | OK
44811.8919 | 3:00 | 95 | 133.7369 | 131.0178 | 144.9577 | 72.306 | 107.1433 | 107.1433 | 22.9453 | 21.8265 | 21.8452 | 24.8292 | 50 | 45.7073 | 197.4573 | 35.21 | 35.6312 | 108.1173 | ON | 23.8 | 108.3 | 48.506 | 36.6577 | -1.9735 | 3.0027 | 1.1567 | 1.1567 | 3.5121 |  | OK | OK | OK | OK | 109.9369 | OK | OK | OK | OK | OK
44811.892 | 3:00 | 95 | 133.746 | 130.9887 | 144.9792 | 72.2832 | 107.0277 | 107.0277 | 22.8636 | 21.8179 | 21.84 | 24.7081 | 50 | 45.8959 | 197.4446 | 35.0986 | 35.4683 | 108.0166 | ON | 23.8 | 108.3 | 48.4832 | 36.6792 | -1.9821 | 2.8902 | 1.2723 | 1.2723 | 3.501 |  | OK | OK | OK | OK | 109.946 | OK | OK | OK | OK | OK
44811.8921 | 3:01 | 95 | 133.7095 | 130.9964 | 145.0254 | 72.2924 | 106.9006 | 106.9006 | 22.7375 | 21.6475 | 21.6433 | 24.597 | 50 | 45.4834 | 196.8151 | 35.1465 | 35.4522 | 107.8932 | ON | 23.8 | 108.3 | 48.4924 | 36.7254 | -2.1525 | 2.9495 | 1.3994 | 1.3994 | 3.5145 |  | OK | OK | OK | OK | 109.9095 | OK | OK | OK | OK | OK
44811.8923 | 3:01 | 95 | 133.6798 | 130.9838 | 145.0983 | 72.2853 | 106.8644 | 106.8644 | 22.6211 | 21.6046 | 21.522 | 24.5086 | 50 | 45.6788 | 197.0714 | 35.0649 | 35.4101 | 107.8937 | ON | 23.8 | 108.3 | 48.4853 | 36.7983 | -2.1954 | 2.904 | 1.4356 | 1.4356 | 3.5074 |  | OK | OK | OK | OK | 109.8798 | OK | OK | OK | OK | OK
44811.8924 | 3:01 | 95 | 133.7501 | 130.9734 | 145.1505 | 72.2123 | 106.7993 | 106.7993 | 22.5282 | 21.5049 | 21.3954 | 24.4017 | 50 | 45.328 | 196.4588 | 35.0834 | 35.371 | 107.7977 | ON | 23.8 | 108.3 | 48.4123 | 36.8505 | -2.2951 | 2.8968 | 1.5007 | 1.5007 | 3.5177 |  | OK | OK | OK | OK | 109.9501 | OK | OK | OK | OK | OK
44811.8925 | 3:01 | 95 | 133.7187 | 130.9049 | 145.1458 | 72.1428 | 106.6413 | 106.6413 | 22.3895 | 21.2678 | 21.2124 | 24.3231 | 50 | 45.1761 | 196.2195 | 34.9888 | 35.0939 | 107.6471 | ON | 23.8 | 108.3 | 48.3428 | 36.8458 | -2.5322 | 3.0553 | 1.6587 | 1.6587 | 3.5226 |  | OK | OK | OK | OK | 109.9187 | OK | OK | OK | OK | OK
44811.8926 | 3:01 | 95 | 133.6891 | 130.9124 | 145.1349 | 72.18 | 106.5165 | 106.5165 | 22.2201 | 21.1609 | 21.3083 | 24.2231 | 50 | 45.0735 | 196.1345 | 34.9086 | 35.0421 | 107.5155 | ON | 23.8 | 108.3 | 48.38 | 36.8349 | -2.6391 | 3.0623 | 1.7835 | 1.7835 | 3.5272 |  | OK | OK | OK | OK | 109.8891 | OK | OK | OK | OK | OK
44811.8927 | 3:01 | 95 | 133.6288 | 130.875 | 145.1308 | 72.0882 | 106.4241 | 106.4241 | 22.1791 | 21.1676 | 21.0772 | 24.1668 | 50 | 44.9698 | 195.7113 | 34.7511 | 35.0688 | 107.4023 | ON | 22.84 | 108.3 | 49.2482 | 36.8308 | -1.6724 | 2.9991 | 1.8759 | 1.8759 | 3.5263 |  | OK | OK | OK | OK | 110.7888 | OK | OK | OK | OK | OK
44811.8928 | 3:02 | 95 | 133.5946 | 130.7243 | 145.0769 | 71.9573 | 106.225 | 106.225 | 22.0763 | 20.9616 | 20.8875 | 24.0818 | 50 | 44.785 | 194.8658 | 34.5889 | 35.0325 | 107.2334 | ON | 22.84 | 106.4 | 49.1172 | 38.6769 | -1.8784 | 3.1202 | 0.175 | 0.175 | 3.523 |  | OK | Low Charge | OK | OK | 110.7546 | OK | OK | OK | OK | OK
44811.893 | 3:02 | 95 | 133.7968 | 130.7726 | 145.0119 | 71.1315 | 107.4897 | 107.4897 | 21.9995 | 20.9828 | 21.0969 | 24.0857 | 50 | 44.8479 | 200.4016 | 34.7062 | 35.0224 | 108.082 | ON | 22.84 | 110.2 | 48.2915 | 34.8119 | -1.8572 | 3.1029 | 2.7103 | 2.7103 | 3.6122 |  | OK | OK | OK | OK | 110.9568 | OK | OK | OK | OK | OK
44811.8931 | 3:02 | 95 | 133.854 | 131.0122 | 145.1613 | 70.1222 | 108.098 | 108.098 | 21.5944 | 19.6257 | 21.7462 | 24.294 | 50 | 42.8496 | 201.242 | 34.5287 | 34.8885 | 108.4978 | ON | 20.88 | 110.2 | 49.2422 | 34.9613 | -1.2543 | 4.6683 | 2.102 | 2.102 | 3.7523 |  | OK | OK | OK | OK | 112.974 | OK | OK | OK | OK | OK
44811.8932 | 3:02 | 95 | 133.882 | 130.9079 | 145.1122 | 67.2038 | 107.9571 | 107.9571 | 21.1965 | 19.1576 | 22.9221 | 25.0211 | 50 | 42.4135 | 201.0457 | 34.4848 | 35.0185 | 108.4695 | ON | 20.88 | 110.2 | 46.3238 | 34.9122 | -1.7224 | 5.8636 | 2.2429 | 2.2429 | 3.7775 |  | OK | OK | OK | OK | 113.002 | OK | OK | OK | OK | OK
44811.8933 | 3:02 | 95 | 133.7358 | 130.8109 | 144.9118 | 60.5776 | 108.0152 | 108.0152 | 20.856 | 18.7792 | 24.2977 | 25.9677 | 50 | 42.1067 | 200.9299 | 34.3322 | 35.1242 | 108.5438 | ON | 20.88 | 110.2 | 39.6976 | 34.7118 | -2.1008 | 7.1884 | 2.1848 | 2.1848 | 3.7958 |  | OK | OK | OK | OK | 112.8558 | OK | OK | OK | OK | OK
44811.8934 | 3:02 | 95 | 133.4306 | 130.5247 | 144.5101 | 52.3269 | 108.0863 | 108.0863 | 20.5972 | 18.4225 | 25.6198 | 26.9312 | 50 | 41.7548 | 201.1257 | 34.2596 | 35.2315 | 108.6315 | ON | 19.89 | 110.2 | 32.4369 | 34.3101 | -1.4675 | 8.5087 | 2.1137 | 2.1137 | 3.823 |  | OK | OK | OK | OK | 113.5406 | OK | OK | OK | OK | OK
44811.8935 | 3:03 | 95 | 132.9318 | 130.0182 | 143.9369 | 47.6184 | 108.1816 | 108.1816 | 20.2839 | 18.1364 | 26.836 | 27.8168 | 50 | 41.4361 | 201.5048 | 34.0606 | 35.3244 | 108.6682 | ON | 19.89 | 110.2 | 27.7284 | 33.7369 | -1.7536 | 9.6804 | 2.0184 | 2.0184 | 3.8514 |  | OK | OK | OK | OK | 113.0418 | OK | OK | OK | OK | OK
44811.8937 | 3:03 | 95 | 132.2376 | 129.5253 | 143.2689 | 45.6319 | 108.2514 | 108.2514 | 20.0266 | 17.8607 | 27.878 | 28.5922 | 50 | 41.2508 | 201.5883 | 34.2308 | 35.3282 | 108.7464 | ON | 19.89 | 110.2 | 25.7419 | 33.0689 | -2.0293 | 10.7314 | 1.9486 | 1.9486 | 3.8657 |  | OK | OK | OK | OK | 112.3476 | OK | OK | OK | OK | OK
44811.8938 | 3:03 | 95 | 131.5058 | 128.9317 | 142.5649 | 44.4179 | 108.196 | 108.196 | 19.7923 | 17.6226 | 28.6578 | 29.2029 | 50 | 40.949 | 201.2395 | 33.9757 | 35.3766 | 108.7379 | ON | 18.88 | 110.2 | 25.5378 | 32.3649 | -1.2574 | 11.5803 | 2.004 | 2.004 | 3.8804 |  | OK | OK | OK | OK | 112.6258 | OK | OK | OK | OK | OK
44811.8939 | 3:03 | 95 | 130.7557 | 128.3809 | 141.8915 | 43.0602 | 108.1836 | 108.1836 | 19.5937 | 17.4267 | 29.2968 | 29.7217 | 50 | 40.7899 | 201.5595 | 34.0025 | 35.3205 | 108.7111 | ON | 18.88 | 110.2 | 24.1802 | 31.6915 | -1.4533 | 12.295 | 2.0164 | 2.0164 | 3.8973 |  | OK | OK | OK | OK | 111.8757 | OK | OK | OK | OK | OK
44811.894 | 3:03 | 95 | 130.0977 | 127.8863 | 141.2488 | 42.5275 | 108.0657 | 108.0657 | 19.3824 | 17.1897 | 29.7724 | 30.132 | 50 | 40.5586 | 201.0242 | 33.8071 | 35.3704 | 108.633 | ON | 18.88 | 110.2 | 23.6475 | 31.0488 | -1.6903 | 12.9423 | 2.1343 | 2.1343 | 3.9039 |  | OK | OK | OK | OK | 111.2177 | OK | OK | OK | OK | OK
44811.8941 | 3:03 | 95 | 129.5389 | 127.3677 | 140.6634 | 41.9898 | 108.0215 | 108.0215 | 19.1685 | 16.9794 | 30.1311 | 30.4682 | 50 | 40.3676 | 201.0336 | 33.689 | 35.3863 | 108.6503 | ON | 18.88 | 110.2 | 23.1097 | 30.4634 | -1.9006 | 13.4888 | 2.1785 | 2.1785 | 3.9176 |  | OK | OK | OK | OK | 110.6589 | OK | OK | OK | OK | OK
44811.8942 | 3:04 | 95 | 129.1174 | 126.9875 | 140.1061 | 41.3949 | 108.0606 | 108.0606 | 18.9779 | 16.8045 | 30.4214 | 30.7397 | 50 | 40.2082 | 201.3064 | 33.6559 | 35.4108 | 108.6854 | ON | 18.88 | 110.2 | 22.5149 | 29.9061 | -2.0755 | 13.9352 | 2.1394 | 2.1394 | 3.934 |  | OK | OK | OK | OK | 110.2374 | OK | OK | OK | OK | OK
44811.8943 | 3:04 | 95 | 128.749 | 126.7248 | 139.6385 | 40.9566 | 108.2387 | 108.2387 | 18.793 | 16.6369 | 30.6263 | 30.9623 | 50 | 40.0812 | 201.6807 | 33.7005 | 35.3852 | 108.8076 | ON | 18.88 | 110.2 | 22.0766 | 29.4385 | -2.2431 | 14.3253 | 1.9613 | 1.9613 | 3.9499 |  | OK | OK | OK | OK | 109.869 | OK | OK | OK | OK | OK
44811.8945 | 3:04 | 95 | 128.4134 | 126.4176 | 139.1747 | 40.5266 | 108.1287 | 108.1287 | 18.6023 | 16.4882 | 30.7896 | 31.1207 | 50 | 39.898 | 201.075 | 33.6431 | 35.3793 | 108.7399 | ON | 17.86 | 110.2 | 22.6666 | 28.9747 | -1.3718 | 14.6325 | 2.0713 | 2.0713 | 3.9521 |  | OK | OK | OK | OK | 110.5534 | OK | OK | OK | OK | OK
44811.8946 | 3:04 | 95 | 128.1409 | 126.0953 | 138.7963 | 40.0694 | 108.0952 | 108.0952 | 18.4091 | 16.2501 | 30.9266 | 31.2779 | 50 | 39.6662 | 201.3521 | 33.558 | 35.2778 | 108.7001 | ON | 17.86 | 110.2 | 22.2094 | 28.5963 | -1.6099 | 15.0278 | 2.1048 | 2.1048 | 3.974 |  | OK | OK | OK | OK | 110.2809 | OK | OK | OK | OK | OK
44811.8947 | 3:04 | 95 | 127.9409 | 125.9613 | 138.5207 | 39.444 | 108.2094 | 108.2094 | 18.2375 | 16.1696 | 31.0387 | 31.3937 | 50 | 39.6895 | 201.7829 | 33.6067 | 35.2871 | 108.8161 | ON | 17.86 | 110.2 | 21.584 | 28.3207 | -1.6904 | 15.2241 | 1.9906 | 1.9906 | 3.9802 |  | OK | OK | OK | OK | 110.0809 | OK | OK | OK | OK | OK
44811.8948 | 3:04 | 95 | 127.7033 | 125.7846 | 138.2739 | 39.181 | 108.215 | 108.215 | 18.0731 | 15.9535 | 31.1015 | 31.483 | 50 | 39.35 | 201.3408 | 33.3661 | 35.3408 | 108.8396 | ON | 17.86 | 110.2 | 21.321 | 28.0739 | -1.9065 | 15.5295 | 1.985 | 1.985 | 3.9971 |  | OK | OK | OK | OK | 109.8433 | OK | OK | OK | OK | OK
44811.8949 | 3:05 | 95 | 127.6446 | 125.6992 | 138.1215 | 38.9294 | 108.364 | 108.364 | 17.9319 | 15.8014 | 31.1881 | 31.5534 | 50 | 39.2112 | 201.8616 | 33.2944 | 35.3723 | 108.945 | ON | 17.86 | 110.2 | 21.0694 | 27.9215 | -2.0586 | 15.752 | 1.836 | 1.836 | 4.017 |  | OK | OK | OK | OK | 109.7846 | OK | OK | OK | OK | OK
44811.895 | 3:05 | 95 | 127.7998 | 125.6408 | 137.9921 | 38.7343 | 108.856 | 108.856 | 17.5507 | 15.6051 | 31.206 | 31.602 | 50 | 38.9709 | 206.5234 | 33.3311 | 35.351 | 109.3242 | ON | 16.82 | 112 | 21.9143 | 25.9921 | -1.2149 | 15.9969 | 3.144 | 3.144 | 4.1218 |  | OK | OK | OK | OK | 110.9798 | OK | OK | OK | OK | OK
44811.8952 | 3:05 | 95 | 128.5584 | 126.5501 | 138.4671 | 40.335 | 110.8768 | 110.8768 | 15.2863 | 15.2979 | 31.2227 | 31.5655 | 50 | 21.9761 | 210.2635 | 33.1178 | 35.2181 | 111.0127 | ON | -3.64 | 113.8 | 43.975 | 24.6671 | 18.9379 | 16.2676 | 2.9232 | 2.9232 | 6.1338 |  | OK | OK | OK | OK | 132.1984 | OK | OK | OK | OK | OK
44811.8953 | 3:05 | 95 | 128.5075 | 126.4823 | 136.9249 | 45.7637 | 108.711 | 108.711 | 16.8776 | 17.3296 | 31.2622 | 31.5917 | 50 | 20.2957 | 204.2949 | 33.3077 | 35.3499 | 109.3456 | ON | -5.06 | 110.2 | 50.8237 | 26.7249 | 22.3896 | 14.2621 | 1.489 | 1.489 | 6.2578 |  | OK | OK | OK | OK | 133.5675 | OK | OK | OK | OK | OK
44811.8954 | 3:05 | 95 | 128.7287 | 126.2796 | 135.8892 | 49.1042 | 106.7035 | 106.7035 | 19.2899 | 19.4242 | 31.2881 | 31.6395 | 50 | 17.5715 | 200.9769 | 33.8343 | 35.4823 | 108.3049 | ON | -9.5 | 110.2 | 58.6042 | 25.6892 | 28.9242 | 12.2153 | 3.4965 | 3.4965 | 6.6832 |  | OK | OK | OK | OK | 138.2287 | OK | OK | OK | OK | OK
44811.8955 | 3:05 | 95 | 129.2674 | 126.159 | 135.3733 | 49.0789 | 105.9153 | 105.9153 | 21.6875 | 21.2788 | 31.3295 | 31.6968 | 50 | 16.168 | 198.588 | 34.3685 | 35.6332 | 107.6943 | ON | -11.06 | 108.3 | 60.1389 | 27.0733 | 32.3389 | 10.4179 | 2.3847 | 2.3847 | 6.9097 |  | OK | OK | OK | OK | 140.3274 | OK | OK | OK | OK | OK
44811.8956 | 3:06 | 95 | 129.9438 | 126.207 | 135.257 | 53.2128 | 105.7349 | 105.7349 | 23.8245 | 22.8823 | 31.3671 | 31.8112 | 50 | 15.5363 | 197.8644 | 34.6 | 35.8816 | 107.3766 | ON | -12.65 | 108.3 | 65.8628 | 26.957 | 35.5323 | 8.9288 | 2.5651 | 2.5651 | 7.0301 |  | OK | OK | OK | OK | 142.5938 | OK | OK | OK | OK | OK
44811.8957 | 3:06 | 95 | 130.8652 | 126.4638 | 135.4281 | 57.6079 | 105.3781 | 105.3781 | 25.6964 | 24.2972 | 31.4023 | 31.9213 | 50 | 15.1514 | 197.6147 | 35.0338 | 36.0022 | 107.2217 | ON | -12.65 | 108.3 | 70.2579 | 27.1281 | 36.9472 | 7.6241 | 2.9219 | 2.9219 | 7.1124 |  | OK | OK | OK | OK | 143.5152 | OK | OK | OK | OK | OK
44811.8958 | 3:06 | 95 | 131.8209 | 126.7987 | 135.7503 | 60.2142 | 105.4049 | 105.4049 | 27.1777 | 25.4586 | 31.4349 | 32.0437 | 50 | 14.5813 | 197.333 | 35.1217 | 36.0524 | 107.103 | ON | -14.28 | 108.3 | 74.4942 | 27.4503 | 39.7386 | 6.5851 | 2.8951 | 2.8951 | 7.2412 |  | OK | OK | OK | OK | 146.1009 | OK | OK | OK | OK | OK
44811.896 | 3:06 | 95 | 132.8669 | 127.1505 | 136.071 | 61.7573 | 105.0241 | 105.0241 | 28.3746 | 26.4663 | 31.4596 | 32.1724 | 50 | 14.2271 | 196.7458 | 35.4029 | 36.0805 | 106.992 | ON | -14.28 | 108.3 | 76.0373 | 27.771 | 40.7463 | 5.7061 | 3.2759 | 3.2759 | 7.3096 |  | OK | OK | OK | OK | 147.1469 | OK | OK | OK | OK | OK
44811.8961 | 3:06 | 95 | 133.745 | 127.5581 | 136.5013 | 62.8939 | 105.0436 | 105.0436 | 29.2714 | 27.2304 | 31.4846 | 32.3189 | 50 | 13.7008 | 196.5777 | 35.6366 | 36.2699 | 106.8712 | ON | -15.96 | 108.3 | 78.8539 | 28.2013 | 43.1904 | 5.0885 | 3.2564 | 3.2564 | 7.4391 |  | OK | OK | OK | OK | 149.705 | OK | OK | OK | OK | OK
44811.8962 | 3:06 | 95 | 134.6315 | 127.9209 | 136.9346 | 63.6931 | 104.8201 | 104.8201 | 29.9109 | 27.867 | 31.5356 | 32.4365 | 50 | 13.4916 | 196.6626 | 35.6373 | 36.3585 | 106.8617 | ON | -15.96 | 108.3 | 79.6531 | 28.6346 | 43.827 | 4.5695 | 3.4799 | 3.4799 | 7.4974 |  | OK | OK | OK | OK | 150.5915 | OK | OK | OK | OK | OK
44811.8963 | 3:07 | 95 | 135.3721 | 128.412 | 137.4826 | 64.2142 | 104.8869 | 104.8869 | 30.3985 | 28.3687 | 31.5492 | 32.5934 | 50 | 13.1183 | 196.4091 | 35.8663 | 36.3839 | 106.8204 | ON | -15.96 | 108.3 | 80.1742 | 29.1826 | 44.3287 | 4.2247 | 3.4131 | 3.4131 | 7.5889 |  | OK | OK | OK | OK | 151.3321 | OK | OK | OK | OK | OK
44811.8964 | 3:07 | 95 | 136.1382 | 128.8487 | 137.9692 | 64.6867 | 104.8467 | 104.8467 | 30.7233 | 28.7837 | 31.5723 | 32.7227 | 50 | 12.9762 | 195.9135 | 35.9256 | 36.4565 | 106.6495 | ON | -17.69 | 108.3 | 82.3767 | 29.6692 | 46.4737 | 3.939 | 3.4533 | 3.4533 | 7.6099 |  | OK | OK | OK | OK | 153.8282 | OK | OK | OK | OK | OK
44811.8965 | 3:07 | 95 | 136.7572 | 129.2886 | 138.449 | 64.7422 | 104.5494 | 104.5494 | 30.9511 | 29.1149 | 31.5775 | 32.8738 | 50 | 12.5075 | 195.5132 | 36.0391 | 36.5532 | 106.4189 | ON | -17.69 | 108.3 | 82.4322 | 30.149 | 46.8049 | 3.7589 | 3.7506 | 3.7506 | 7.7263 |  | OK | OK | OK | OK | 154.4472 | OK | OK | OK | OK | OK
44811.8967 | 3:07 | 95 | 137.2397 | 129.5853 | 138.7754 | 64.6633 | 103.9838 | 103.9838 | 31.1332 | 29.3876 | 31.5989 | 33.0211 | 50 | 12.4139 | 194.2782 | 36.169 | 36.585 | 106.0963 | ON | -17.69 | 106.4 | 82.3533 | 32.3754 | 47.0776 | 3.6335 | 2.4162 | 2.4162 | 7.7074 |  | OK | OK | OK | OK | 154.9297 | OK | OK | OK | OK | OK
44811.8968 | 3:07 | 95 | 137.7884 | 129.7536 | 139.0851 | 64.3124 | 103.8174 | 103.8174 | 31.2591 | 29.6216 | 31.6156 | 33.1663 | 50 | 12.7473 | 193.5167 | 36.19 | 36.6849 | 105.7989 | ON | -17.69 | 106.4 | 82.0024 | 32.6851 | 47.3116 | 3.5447 | 2.5826 | 2.5826 | 7.5861 |  | OK | OK | OK | OK | 155.4784 | OK | OK | OK | OK | OK
44811.8969 | 3:07 | 95 | 137.9926 | 129.89 | 139.2031 | 63.6988 | 103.4778 | 103.4778 | 31.3673 | 29.8177 | 31.6298 | 33.3274 | 50 | 13.8825 | 192.7171 | 36.346 | 36.7061 | 105.4877 | ON | -15.96 | 106.4 | 79.6588 | 32.8031 | 45.7777 | 3.5097 | 2.9222 | 2.9222 | 7.2568 |  | OK | OK | OK | OK | 153.9526 | OK | OK | OK | OK | OK
44811.897 | 3:08 | 95 | 138.0621 | 129.869 | 139.1466 | 63.0211 | 103.088 | 103.088 | 31.3987 | 29.9913 | 31.6518 | 33.4791 | 50 | 14.8504 | 191.5441 | 36.4548 | 36.739 | 105.1667 | ON | -14.28 | 106.4 | 77.3011 | 32.7466 | 44.2713 | 3.4878 | 3.312 | 3.312 | 6.9794 |  | OK | OK | OK | OK | 152.3421 | OK | OK | OK | OK | OK
44811.8971 | 3:08 | 95 | 141.9567 | 128.1087 | 136.8155 | 66.7483 | 94.6485 | 94.6485 | 27.2121 | 30.6708 | 28.7867 | 33.911 | 50 | 53.9693 | 134.3027 | 36.4483 | 36.8259 | 101.5741 | OFF | 31.06 | 80.35 | 35.6883 | 56.4655 | -0.38922 | 3.2403 | -14.2985 | -14.2985 | 2.1699
44811.8972 | 3:08 | 95 | 141.8477 | 125.7673 | 128.8735 | 78.4343 | 91.0152 | 91.0152 | 31.496 | 31.5505 | 30.9832 | 33.9078 | 50 | 58.814 | 112.6119 | 36.3327 | 36.8655 | 100.6095 | OFF | 35.28 | 69.9 | 43.1543 | 58.9735 | -3.7295 | 2.3573 | -21.1152 | -21.1152 | 1.7318
44811.8974 | 3:08 | 95 | 140.8551 | 124.1494 | 120.7154 | 87.9952 | 88.351 | 88.351 | 31.8397 | 33.0598 | 31.4918 | 34.1263 | 50 | 60.2595 | 101.451 | 36.3988 | 36.9883 | 99.7688 | OFF | 36.91 | 64.21 | 51.0853 | 56.5054 | -3.8502 | 1.0665 | -24.141 | -24.141 | 1.5495
44811.8975 | 3:08 | 95 | 139.407 | 122.4415 | 114.5798 | 94.6447 | 86.5519 | 86.5519 | 31.8359 | 34.1622 | 31.6528 | 34.5393 | 50 | 61.1838 | 89.0202 | 36.5087 | 37.0008 | 99.0724 | OFF | 37.71 | 54.95 | 56.9347 | 59.6298 | -3.5478 | 0.37709 | -31.6019 | -31.6019 | 1.3668
44811.8976 | 3:08 | 95 | 137.9657 | 120.8311 | 110.5053 | 98.2769 | 85.1764 | 85.1764 | 31.8563 | 34.9224 | 31.6932 | 35.0074 | 50 | 62.0339 | 80.8634 | 36.7307 | 37.0824 | 98.6583 | OFF | 38.5 | 51.63 | 59.7769 | 58.8753 | -3.5777 | 0.085 | -33.5464 | -33.5464 | 1.2454
44811.8977 | 3:09 | 95 | 136.5495 | 119.4245 | 107.8253 | 100.1101 | 84.6366 | 84.6366 | 31.8467 | 35.4225 | 31.7035 | 35.2542 | 50 | 62.4015 | 72.6014 | 36.7496 | 37.1754 | 98.2907 | OFF | 38.5 | 44.59 | 61.6101 | 63.2353 | -3.0775 | -0.1683 | -40.0466 | -40.0466 | 1.1323
44811.8978 | 3:09 | 95 | 135.3598 | 118.1369 | 106.3886 | 99.9783 | 85.6312 | 85.6312 | 31.8593 | 35.4602 | 31.7405 | 35.3131 | 50 | 62.4647 | 66.5015 | 36.8106 | 37.2837 | 98.0544 | OFF | 38.5 | 41.6 | 61.4783 | 64.7886 | -3.0398 | -0.14708 | -44.0312 | -44.0312 | 1.0523
44811.8979 | 3:09 | 95 | 134.1995 | 117.049 | 105.6251 | 99.1522 | 86.9304 | 86.9304 | 31.8678 | 35.4942 | 31.7638 | 35.3519 | 50 | 62.3681 | 63.5063 | 36.8459 | 37.3771 | 97.7999 | OFF | 38.5 | 39.29 | 60.6522 | 66.3351 | -3.0058 | -0.14223 | -47.6404 | -47.6404 | 1.0148
44811.898 | 3:09 | 95 | 133.0946 | 116.0403 | 105.1338 | 98.2361 | 88.3683 | 88.3683 | 31.8884 | 35.4995 | 31.7863 | 35.3762 | 50 | 62.565 | 62.3754 | 36.9057 | 37.4428 | 97.6297 | OFF | 38.5 | 38.5 | 59.7361 | 66.6338 | -3.0005 | -0.12337 | -49.8683 | -49.8683 | 0.99755
44811.8982 | 3:09 | 95 | 132.0097 | 115.1613 | 104.795 | 97.3772 | 89.7196 | 89.7196 | 31.8952 | 35.5343 | 31.8117 | 35.4037 | 50 | 62.6329 | 61.9477 | 37.0829 | 37.4958 | 97.4582 | OFF | 38.5 | 37.71 | 58.8772 | 67.085 | -2.9657 | -0.13057 | -52.0096 | -52.0096 | 0.99114
44811.8983 | 3:09 | 95 | 131.0262 | 114.3778 | 104.5823 | 96.5836 | 90.926 | 90.926 | 31.928 | 35.8668 | 31.8306 | 35.5862 | 50 | 63.065 | 62.169 | 36.9913 | 37.6027 | 97.2464 | OFF | 39.29 | 38.5 | 57.2936 | 66.0823 | -3.4232 | -0.28065 | -52.426 | -52.426 | 0.98848
44811.8984 | 3:10 | 95 | 129.9877 | 113.6729 | 104.3462 | 95.9859 | 91.8927 | 91.8927 | 31.9743 | 36.1607 | 31.8348 | 35.7595 | 50 | 63.2933 | 62.3406 | 37.1788 | 37.6632 | 97.0698 | OFF | 39.29 | 38.5 | 56.6959 | 65.8462 | -3.1293 | -0.40111 | -53.3927 | -53.3927 | 0.98778
44811.8985 | 3:10 | 95 | 129.032 | 112.9786 | 104.0883 | 95.6038 | 92.5989 | 92.5989 | 31.9978 | 36.3168 | 31.8563 | 35.9809 | 50 | 63.6469 | 62.6649 | 37.3026 | 37.7346 | 96.9034 | OFF | 39.29 | 38.5 | 56.3138 | 65.5883 | -2.9732 | -0.33591 | -54.0989 | -54.0989 | 0.98747
44811.8986 | 3:10 | 95 | 128.1534 | 112.4256 | 103.8358 | 95.318 | 93.147 | 93.147 | 32.0372 | 36.517 | 31.9015 | 36.1901 | 50 | 63.8559 | 62.9068 | 37.3012 | 37.8157 | 96.7492 | OFF | 39.29 | 38.5 | 56.028 | 65.3358 | -2.773 | -0.32682 | -54.647 | -54.647 | 0.98792
44811.8987 | 3:10 | 95 | 127.3446 | 111.8716 | 103.5375 | 95.109 | 93.5515 | 93.5515 | 32.0858 | 36.6613 | 32.149 | 36.5229 | 50 | 64.2036 | 63.1527 | 37.4372 | 37.8858 | 96.5927 | OFF | 40.07 | 39.29 | 55.039 | 64.2475 | -3.4087 | -0.13845 | -54.2615 | -54.2615 | 0.98668
44811.8989 | 3:10 | 95 | 126.5839 | 111.3794 | 103.2798 | 95.0443 | 93.8731 | 93.8731 | 32.1321 | 36.8847 | 34.0797 | 36.9459 | 50 | 64.5305 | 63.5157 | 37.5672 | 38.0393 | 96.4318 | OFF | 40.07 | 39.29 | 54.9742 | 63.9898 | -3.1852 | 0.06117 | -54.5831 | -54.5831 | 0.98719
44811.899 | 3:10 | 95 | 125.7983 | 110.8816 | 103.0058 | 94.9728 | 94.0862 | 94.0862 | 32.1913 | 37.1033 | 35.2455 | 37.292 | 50 | 64.9125 | 63.8274 | 37.6508 | 38.0725 | 96.3122 | OFF | 40.07 | 39.29 | 54.9028 | 63.7158 | -2.9667 | 0.18874 | -54.7962 | -54.7962 | 0.98637
44811.8991 | 3:11 | 95 | 125.0844 | 110.4462 | 102.7275 | 94.953 | 94.2382 | 94.2382 | 32.3337 | 37.2931 | 36.303 | 37.5746 | 50 | 65.2022 | 64.1783 | 37.8351 | 38.1447 | 96.1313 | OFF | 40.84 | 40.07 | 54.113 | 62.6575 | -3.5469 | 0.28147 | -54.1682 | -54.1682 | 0.98719
44811.8992 | 3:11 | 95 | 124.4544 | 110.0997 | 102.4874 | 94.886 | 94.3359 | 94.3359 | 32.4964 | 37.4841 | 37.0041 | 37.7963 | 50 | 65.4416 | 64.3749 | 37.8921 | 38.2518 | 95.9876 | OFF | 40.84 | 40.07 | 54.046 | 62.4174 | -3.3559 | 0.31219 | -54.2659 | -54.2659 | 0.98669
44811.8993 | 3:11 | 95 | 123.7862 | 109.7319 | 102.2183 | 94.8411 | 94.3651 | 94.3651 | 32.6826 | 37.6907 | 37.3063 | 37.943 | 50 | 65.6712 | 64.6248 | 38.1885 | 38.3697 | 95.8706 | OFF | 40.84 | 40.07 | 54.0011 | 62.1483 | -3.1493 | 0.25233 | -54.2951 | -54.2951 | 0.98698
44811.8994 | 3:11 | 95 | 123.1584 | 109.3263 | 101.9683 | 94.7189 | 94.3867 | 94.3867 | 32.8807 | 37.9207 | 37.5493 | 38.1859 | 50 | 65.9956 | 64.8684 | 38.1178 | 38.3942 | 95.7148 | OFF | 40.84 | 40.07 | 53.8789 | 61.8983 | -2.9193 | 0.2652 | -54.3167 | -54.3167 | 0.98603
44811.8996 | 3:11 | 95 | 122.5084 | 108.9514 | 101.7139 | 94.5572 | 94.3503 | 94.3503 | 33.0521 | 38.1286 | 37.8148 | 38.3583 | 50 | 66.2197 | 65.0762 | 38.2148 | 38.4572 | 95.5037 | OFF | 41.6 | 40.84 | 52.9572 | 60.8739 | -3.4714 | 0.22972 | -53.5103 | -53.5103 | 0.98587
44811.8997 | 3:11 | 95 | 121.9069 | 108.6031 | 101.4491 | 94.4632 | 94.3 | 94.3 | 33.2468 | 38.1614 | 37.9315 | 38.4751 | 50 | 66.3992 | 65.2295 | 38.3403 | 38.6298 | 95.3094 | OFF | 41.6 | 40.84 | 52.8632 | 60.6091 | -3.4386 | 0.31369 | -53.46 | -53.46 | 0.98558
44811.8998 | 3:12 | 95 | 121.287 | 108.319 | 101.2007 | 94.3972 | 94.2297 | 94.2297 | 33.5935 | 38.255 | 38.088 | 38.6441 | 50 | 66.5874 | 65.4625 | 38.5095 | 38.7243 | 95.1395 | OFF | 41.6 | 40.84 | 52.7972 | 60.3607 | -3.345 | 0.38908 | -53.3897 | -53.3897 | 0.98616
44811.8999 | 3:12 | 95 | 120.7844 | 108.0213 | 101.0083 | 94.2847 | 94.1536 | 94.1536 | 34.0858 | 38.3586 | 38.2437 | 38.7905 | 50 | 66.8106 | 65.7431 | 38.6391 | 38.8262 | 95.1008 | OFF | 41.6 | 40.84 | 52.6847 | 60.1683 | -3.2414 | 0.43187 | -53.3137 | -53.3137 | 0.9869
44811.9 | 3:12 | 95 | 120.7428 | 107.7574 | 101.8422 | 93.8696 | 94.1958 | 94.1958 | 34.4652 | 37.581 | 37.7319 | 37.8665 | 50 | 64.5451 | 78.632 | 38.7394 | 38.8736 | 95.119 | OFF | 40.07 | 48.19 | 53.7996 | 53.6522 | -2.4891 | 0.28554 | -46.0058 | -46.0058 | 1.1778
44811.9001 | 3:12 | 95 | 122.5207 | 108.3178 | 121.2189 | 68.5641 | 94.7672 | 94.7672 | 32.9235 | 33.244 | 34.8545 | 35.3577 | 50 | 57.4914 | 160.5364 | 38.698 | 38.8539 | 96.6967 | OFF | 34.45 | 94.19 | 34.1141 | 27.0289 | -1.206 | 2.1137 | -0.57716 | -0.57716 | 2.4274
44811.9002 | 3:12 | 95 | 121.2448 | 111.5503 | 131.7254 | 58.0197 | 100.5717 | 100.5717 | 30.3187 | 29.2614 | 29.8408 | 34.6389 | 50 | 53.0715 | 183.4048 | 38.3892 | 38.7393 | 101.7631 | ON | 31.06 | 102.5 | 26.9597 | 29.2254 | -1.7986 | 5.3775 | 1.9283 | 1.9283 | 2.9231 |  | OK | OK | OK | OK | 90.1848 | OK | OK | OK | OK | OK
44811.9004 | 3:12 | 95 | 119.9098 | 115.2521 | 130.8624 | 57.1998 | 103.3115 | 103.3115 | 29.8078 | 29.7316 | 28.5452 | 32.4847 | 50 | 51.6108 | 189.2166 | 37.8729 | 38.5432 | 104.1284 | ON | 29.31 | 104.4 | 27.8898 | 26.4624 | 0.4216 | 2.7531 | 1.0885 | 1.0885 | 3.0752 |  | OK | OK | OK | OK | 90.5998 | OK | OK | OK | OK | OK
44811.9005 | 3:13 | 95 | 119.441 | 116.9614 | 130.7811 | 56.69 | 103.834 | 103.834 | 30.0782 | 30.7047 | 27.7541 | 27.6043 | 50 | 52.1257 | 190.4994 | 37.7269 | 38.2238 | 104.8038 | ON | 30.19 | 106.4 | 26.5 | 24.3811 | 0.51469 | -3.1004 | 2.566 | 2.566 | 3.0707 |  | OK | OK | OK | OK | 89.251 | OK | OK | OK | OK | OK
44811.9006 | 3:13 | 95 | 119.6901 | 118.1106 | 130.984 | 54.8719 | 104.7919 | 104.7919 | 29.9874 | 31.229 | 27.1913 | 26.6899 | 50 | 51.5353 | 193.042 | 37.6469 | 38.0518 | 105.6978 | ON | 29.31 | 106.4 | 25.5619 | 24.584 | 1.919 | -4.5391 | 1.6081 | 1.6081 | 3.1364 |  | OK | OK | OK | OK | 90.3801 | OK | OK | OK | OK | OK
44811.9007 | 3:13 | 95 | 120.14 | 119.0238 | 131.1774 | 54.935 | 105.3287 | 105.3287 | 29.8313 | 31.4646 | 26.7434 | 26.2537 | 50 | 51.2069 | 194.2449 | 37.6068 | 37.9234 | 106.2551 | ON | 29.31 | 106.4 | 25.625 | 24.7774 | 2.1546 | -5.2109 | 1.0713 | 1.0713 | 3.1703 |  | OK | OK | OK | OK | 90.83 | OK | OK | OK | OK | OK
44811.9008 | 3:13 | 95 | 120.6798 | 119.7261 | 131.4363 | 57.7925 | 105.6843 | 105.6843 | 29.5418 | 31.519 | 26.2906 | 25.9273 | 50 | 50.9674 | 195.0669 | 37.5371 | 37.8592 | 106.6062 | ON | 28.42 | 108.3 | 29.3725 | 23.1363 | 3.099 | -5.5916 | 2.6157 | 2.6157 | 3.1944 |  | OK | OK | OK | OK | 92.2598 | OK | OK | OK | OK | OK
44811.9009 | 3:13 | 95 | 121.3579 | 120.354 | 131.7739 | 61.1532 | 105.8036 | 105.8036 | 28.787 | 31.4007 | 25.9053 | 25.735 | 50 | 50.7265 | 195.3356 | 37.6752 | 37.7356 | 106.7784 | ON | 28.42 | 108.3 | 32.7332 | 23.4739 | 2.9807 | -5.6657 | 2.4964 | 2.4964 | 3.2103 |  | OK | OK | OK | OK | 92.9379 | OK | OK | OK | OK | OK
44811.9011 | 3:13 | 95 | 121.9699 | 120.8754 | 132.1605 | 63.4626 | 105.8688 | 105.8688 | 28.3541 | 31.2313 | 25.5492 | 25.6779 | 50 | 50.3924 | 195.4152 | 37.571 | 37.6988 | 106.9066 | ON | 28.42 | 108.3 | 35.0426 | 23.8605 | 2.8113 | -5.5534 | 2.4312 | 2.4312 | 3.2279 |  | OK | OK | OK | OK | 93.5499 | OK | OK | OK | OK | OK
44811.9012 | 3:14 | 95 | 122.5661 | 121.3899 | 132.6013 | 65.1314 | 105.9952 | 105.9952 | 28.2312 | 31.1005 | 25.4034 | 25.9847 | 50 | 50.3334 | 195.3937 | 37.3964 | 37.6185 | 107.0582 | ON | 28.42 | 108.3 | 36.7114 | 24.3013 | 2.6805 | -5.1158 | 2.3048 | 2.3048 | 3.2306 |  | OK | OK | OK | OK | 94.1461 | OK | OK | OK | OK | OK
44811.9013 | 3:14 | 95 | 123.1562 | 121.863 | 133.1715 | 66.4633 | 106.0821 | 106.0821 | 28.1025 | 31.0134 | 25.2475 | 26.1439 | 50 | 50.1706 | 195.6125 | 37.2513 | 37.3849 | 107.1809 | ON | 28.42 | 108.3 | 38.0433 | 24.8715 | 2.5934 | -4.8696 | 2.2179 | 2.2179 | 3.242 |  | OK | OK | OK | OK | 94.7362 | OK | OK | OK | OK | OK
44811.9014 | 3:14 | 95 | 123.8233 | 122.4128 | 133.7559 | 67.6132 | 106.1474 | 106.1474 | 28.0162 | 30.8327 | 25.1914 | 25.82 | 50 | 50.1543 | 195.6923 | 37.2386 | 37.3867 | 107.2723 | ON | 28.42 | 108.3 | 39.1932 | 25.4559 | 2.4127 | -5.0127 | 2.1526 | 2.1526 | 3.2441 |  | OK | OK | OK | OK | 95.4033 | OK | OK | OK | OK | OK
44811.9015 | 3:14 | 95 | 124.4416 | 122.8612 | 134.3403 | 68.6204 | 106.306 | 106.306 | 27.9314 | 30.5761 | 24.9405 | 25.5696 | 50 | 49.8955 | 196.3707 | 37.2617 | 37.362 | 107.446 | ON | 27.51 | 108.3 | 41.1104 | 26.0403 | 3.0661 | -5.0065 | 1.994 | 1.994 | 3.2676 |  | OK | OK | OK | OK | 96.9316 | OK | OK | OK | OK | OK
44811.9016 | 3:14 | 95 | 125.1299 | 123.3862 | 134.961 | 69.1897 | 106.4107 | 106.4107 | 27.7692 | 30.2301 | 24.7253 | 25.4615 | 50 | 49.7196 | 196.5458 | 37.271 | 37.2841 | 107.5748 | ON | 27.51 | 108.3 | 41.6797 | 26.661 | 2.7201 | -4.7686 | 1.8893 | 1.8893 | 3.2792 |  | OK | OK | OK | OK | 97.6199 | OK | OK | OK | OK | OK
44811.9018 | 3:14 | 95 | 125.8032 | 123.8686 | 135.5828 | 69.5575 | 106.5433 | 106.5433 | 27.5326 | 29.1336 | 24.5474 | 25.5053 | 50 | 49.5339 | 196.6382 | 37.0488 | 37.1966 | 107.7115 | ON | 27.51 | 108.3 | 42.0475 | 27.2828 | 1.6236 | -3.6284 | 1.7567 | 1.7567 | 3.2901 |  | OK | OK | OK | OK | 98.2932 | OK | OK | OK | OK | OK
44811.9019 | 3:15 | 95 | 126.2452 | 124.3108 | 136.1638 | 70.0701 | 106.5207 | 106.5207 | 27.391 | 26.7721 | 24.3383 | 25.6586 | 50 | 49.253 | 196.6604 | 36.9572 | 37.1212 | 107.7166 | ON | 27.51 | 108.3 | 42.5601 | 27.8638 | -0.73789 | -1.1136 | 1.7793 | 1.7793 | 3.3049 |  | OK | OK | OK | OK | 98.7352 | OK | OK | OK | OK | OK
44811.902 | 3:15 | 95 | 126.8231 | 124.8173 | 136.8025 | 70.7064 | 106.6764 | 106.6764 | 27.0763 | 25.4513 | 24.1851 | 25.7408 | 50 | 48.8115 | 197.1027 | 36.9506 | 37.0242 | 107.8531 | ON | 26.6 | 108.3 | 44.1064 | 28.5025 | -1.1487 | 0.28951 | 1.6236 | 1.6236 | 3.3349 |  | OK | OK | OK | OK | 100.2231 | OK | OK | OK | OK | OK
44811.9021 | 3:15 | 95 | 127.4147 | 125.3752 | 137.4343 | 71.062 | 106.7992 | 106.7992 | 26.8112 | 25.0681 | 24.0333 | 25.7114 | 50 | 48.7964 | 197.4528 | 36.8201 | 36.9595 | 107.9982 | ON | 26.6 | 108.3 | 44.462 | 29.1343 | -1.5318 | 0.64325 | 1.5008 | 1.5008 | 3.3412 |  | OK | OK | OK | OK | 100.8147 | OK | OK | OK | OK | OK
44811.9022 | 3:15 | 95 | 128.0816 | 125.8097 | 138.1203 | 71.6219 | 107.0072 | 107.0072 | 26.4634 | 24.8364 | 23.8743 | 25.5937 | 50 | 48.912 | 198.1317 | 36.6931 | 36.806 | 108.1891 | ON | 26.6 | 108.3 | 45.0219 | 29.8203 | -1.7636 | 0.75729 | 1.2928 | 1.2928 | 3.3458 |  | OK | OK | OK | OK | 101.4816 | OK | OK | OK | OK | OK
44811.9023 | 3:15 | 95 | 128.7012 | 126.318 | 138.7677 | 71.5061 | 107.1999 | 107.1999 | 26.3098 | 24.6206 | 23.7533 | 25.5114 | 50 | 48.6004 | 198.3992 | 36.7366 | 36.6758 | 108.3393 | ON | 26.6 | 108.3 | 44.9061 | 30.4677 | -1.9794 | 0.89088 | 1.1001 | 1.1001 | 3.3665 |  | OK | OK | OK | OK | 102.1012 | OK | OK | OK | OK | OK
44811.9024 | 3:15 | 95 | 129.1857 | 126.825 | 139.3611 | 71.6216 | 107.3363 | 107.3363 | 26.0287 | 24.4159 | 23.6592 | 25.3113 | 50 | 48.1163 | 198.7106 | 36.5199 | 36.6969 | 108.5051 | ON | 26.6 | 108.3 | 45.0216 | 31.0611 | -2.1841 | 0.89541 | 0.9637 | 0.9637 | 3.3974 |  | OK | Low Charge | OK | OK | 102.5857 | OK | OK | OK | OK | OK
44811.9026 | 3:16 | 95 | 129.6871 | 127.2921 | 139.9862 | 71.8722 | 107.5458 | 107.5458 | 25.8136 | 24.2487 | 24.5933 | 25.3961 | 50 | 48.2047 | 199.3545 | 36.3944 | 36.4849 | 108.6677 | ON | 26.6 | 108.3 | 45.2722 | 31.6862 | -2.3513 | 1.1474 | 0.7542 | 0.7542 | 3.4028 |  | OK | Low Charge | OK | OK | 103.0871 | OK | OK | OK | OK | OK
44811.9027 | 3:16 | 95 | 130.2747 | 127.7307 | 140.572 | 72.0645 | 107.7354 | 107.7354 | 25.582 | 23.9758 | 23.907 | 25.1368 | 50 | 47.8663 | 199.7215 | 36.4115 | 36.4525 | 108.8486 | ON | 25.68 | 108.3 | 46.3845 | 32.272 | -1.7042 | 1.161 | 0.5646 | 0.5646 | 3.4271 |  | OK | Low Charge | OK | OK | 104.5947 | OK | OK | OK | OK | OK
44811.9028 | 3:16 | 95 | 130.7533 | 128.1889 | 141.1407 | 72.2055 | 107.9254 | 107.9254 | 25.4422 | 23.9908 | 23.8036 | 25.1825 | 50 | 48.1198 | 200.3685 | 36.2367 | 36.4333 | 109.0142 | ON | 26.6 | 110.2 | 45.6055 | 30.9407 | -2.6092 | 1.1917 | 2.2746 | 2.2746 | 3.4236 |  | OK | OK | OK | OK | 104.1533 | OK | OK | OK | OK | OK
44811.9029 | 3:16 | 95 | 131.2491 | 128.7164 | 141.7413 | 72.0545 | 108.2513 | 108.2513 | 25.338 | 23.7907 | 23.5369 | 25.6815 | 50 | 47.534 | 201.1708 | 36.1803 | 36.4107 | 109.2677 | ON | 25.68 | 110.2 | 46.3745 | 31.5413 | -1.8893 | 1.8907 | 1.9487 | 1.9487 | 3.4687 |  | OK | OK | OK | OK | 105.5691 | OK | OK | OK | OK | OK
44811.903 | 3:16 | 95 | 131.682 | 129.1187 | 142.2632 | 71.7553 | 108.356 | 108.356 | 25.21 | 23.6482 | 23.5559 | 26.6288 | 50 | 47.4614 | 200.9495 | 36.0861 | 36.3674 | 109.3777 | ON | 25.68 | 110.2 | 46.0753 | 32.0632 | -2.0318 | 2.9806 | 1.844 | 1.844 | 3.4692 |  | OK | OK | OK | OK | 106.002 | OK | OK | OK | OK | OK
44811.9031 | 3:16 | 95 | 132.1329 | 129.4276 | 142.7384 | 71.5256 | 108.4261 | 108.4261 | 25.0613 | 23.5773 | 23.5313 | 27.2018 | 50 | 47.4564 | 201.2986 | 36.1262 | 36.4153 | 109.461 | ON | 25.68 | 110.2 | 45.8456 | 32.5384 | -2.1027 | 3.6246 | 1.7739 | 1.7739 | 3.4751 |  | OK | OK | OK | OK | 106.4529 | OK | OK | OK | OK | OK
44811.9033 | 3:17 | 95 | 132.4959 | 129.7367 | 143.0817 | 70.9517 | 108.365 | 108.365 | 24.9164 | 23.3883 | 23.3155 | 27.3964 | 50 | 47.0732 | 201.3719 | 36.0686 | 36.4374 | 109.4128 | ON | 25.68 | 110.2 | 45.2717 | 32.8817 | -2.2917 | 4.008 | 1.835 | 1.835 | 3.4978 |  | OK | OK | OK | OK | 106.8159 | OK | OK | OK | OK | OK
44811.9034 | 3:17 | 95 | 132.6594 | 129.8796 | 143.2995 | 70.6162 | 108.1017 | 108.1017 | 24.6937 | 23.2704 | 23.2257 | 27.2981 | 50 | 47.1641 | 200.5624 | 36.0146 | 36.3664 | 109.2059 | ON | 25.68 | 110.2 | 44.9362 | 33.0995 | -2.4096 | 4.0277 | 2.0983 | 2.0983 | 3.4796 |  | OK | OK | OK | OK | 106.9794 | OK | OK | OK | OK | OK
44811.9035 | 3:17 | 95 | 132.6614 | 130.0415 | 143.4888 | 70.4454 | 107.9104 | 107.9104 | 24.5027 | 23.0681 | 23.0628 | 27.1027 | 50 | 46.9616 | 200.071 | 36.0345 | 36.2951 | 109.0313 | ON | 24.74 | 110.2 | 45.7054 | 33.2888 | -1.6719 | 4.0346 | 2.2896 | 2.2896 | 3.4831 |  | OK | OK | OK | OK | 107.9214 | OK | OK | OK | OK | OK
44811.9036 | 3:17 | 95 | 132.7155 | 130.0658 | 143.6286 | 70.3843 | 107.7754 | 107.7754 | 24.3235 | 22.9789 | 22.9013 | 26.8451 | 50 | 47.0624 | 199.5631 | 35.8279 | 36.2013 | 108.9204 | ON | 25.68 | 108.3 | 44.7043 | 35.3286 | -2.7011 | 3.8661 | 0.5246 | 0.5246 | 3.4692 |  | OK | Low Charge | OK | OK | 107.0355 | OK | OK | OK | OK | OK
44811.9037 | 3:17 | 95 | 132.8282 | 130.166 | 143.7878 | 70.0871 | 107.7746 | 107.7746 | 24.202 | 22.8508 | 22.7776 | 26.5898 | 50 | 46.8077 | 199.765 | 35.8202 | 36.219 | 108.8851 | ON | 24.74 | 108.3 | 45.3471 | 35.4878 | -1.8892 | 3.7391 | 0.5254 | 0.5254 | 3.4868 |  | OK | Low Charge | OK | OK | 108.0882 | OK | OK | OK | OK | OK
44811.9038 | 3:17 | 95 | 132.9763 | 130.208 | 143.9287 | 69.9365 | 107.6513 | 107.6513 | 24.0723 | 22.7419 | 22.704 | 26.3243 | 50 | 46.716 | 199.4777 | 35.651 | 36.0767 | 108.7857 | ON | 24.74 | 108.3 | 45.1965 | 35.6287 | -1.9981 | 3.5824 | 0.6487 | 0.6487 | 3.4873 |  | OK | Low Charge | OK | OK | 108.2363 | OK | OK | OK | OK | OK
44811.904 | 3:18 | 95 | 133.0799 | 130.1786 | 144.0052 | 69.6881 | 107.4936 | 107.4936 | 23.9187 | 22.5696 | 22.5984 | 26.0625 | 50 | 46.5388 | 198.5203 | 35.5818 | 36.0308 | 108.6612 | ON | 24.74 | 108.3 | 44.9481 | 35.7052 | -2.1704 | 3.4929 | 0.8064 | 0.8064 | 3.4818 |  | OK | Low Charge | OK | OK | 108.3399 | OK | OK | OK | OK | OK
44811.9041 | 3:18 | 95 | 133.0384 | 130.249 | 144.0652 | 69.5206 | 107.4792 | 107.4792 | 23.748 | 22.508 | 22.4532 | 25.8155 | 50 | 46.6659 | 198.8478 | 35.5403 | 35.8695 | 108.6085 | ON | 24.74 | 108.3 | 44.7806 | 35.7652 | -2.232 | 3.3075 | 0.8208 | 0.8208 | 3.4799 |  | OK | Low Charge | OK | OK | 108.2984 | OK | OK | OK | OK | OK
44811.9042 | 3:18 | 95 | 133.0629 | 130.2764 | 144.1341 | 69.4168 | 107.4205 | 107.4205 | 23.5413 | 22.3271 | 22.3632 | 25.5925 | 50 | 46.4383 | 198.7165 | 35.522 | 35.8092 | 108.5203 | ON | 24.74 | 108.3 | 44.6768 | 35.8341 | -2.4129 | 3.2654 | 0.8795 | 0.8795 | 3.4907 |  | OK | Low Charge | OK | OK | 108.3229 | OK | OK | OK | OK | OK
44811.9043 | 3:18 | 95 | 133.0277 | 130.2391 | 144.1755 | 69.3938 | 107.2649 | 107.2649 | 23.4871 | 22.2787 | 22.2474 | 25.3928 | 50 | 46.0717 | 198.2228 | 35.4878 | 35.8272 | 108.4223 | ON | 24.74 | 108.3 | 44.6538 | 35.8755 | -2.4613 | 3.1141 | 1.0351 | 1.0351 | 3.5037 |  | OK | OK | OK | OK | 108.2877 | OK | OK | OK | OK | OK
44811.9044 | 3:18 | 95 | 133.0125 | 130.265 | 144.2328 | 69.5959 | 107.1947 | 107.1947 | 23.2642 | 22.0457 | 22.0884 | 25.2136 | 50 | 45.9674 | 198.3383 | 35.4148 | 35.6563 | 108.3673 | ON | 23.8 | 108.3 | 45.7959 | 35.9328 | -1.7543 | 3.1678 | 1.1053 | 1.1053 | 3.5116 |  | OK | OK | OK | OK | 109.2125 | OK | OK | OK | OK | OK
44811.9045 | 3:18 | 95 | 133.0264 | 130.3836 | 144.3566 | 69.7207 | 107.2355 | 107.2355 | 23.1662 | 22.0673 | 22.0476 | 25.0506 | 50 | 46.1393 | 197.9476 | 35.3035 | 35.6026 | 108.3607 | ON | 24.74 | 108.3 | 44.9807 | 36.0566 | -2.6727 | 2.9832 | 1.0645 | 1.0645 | 3.4952 |  | OK | OK | OK | OK | 108.2864 | OK | OK | OK | OK | OK
44811.9046 | 3:19 | 95 | 133.1399 | 130.3598 | 144.4346 | 70.5979 | 107.2052 | 107.2052 | 23.0412 | 21.8827 | 21.8125 | 24.8717 | 50 | 45.7886 | 198.0727 | 35.258 | 35.5006 | 108.332 | ON | 23.8 | 108.3 | 46.7979 | 36.1346 | -1.9174 | 2.9891 | 1.0948 | 1.0948 | 3.5176 |  | OK | OK | OK | OK | 109.3399 | OK | OK | OK | OK | OK
44811.9048 | 3:19 | 95 | 133.1816 | 130.3596 | 144.4819 | 70.9435 | 107.117 | 107.117 | 22.8578 | 21.7117 | 21.6879 | 24.6702 | 50 | 45.6535 | 197.678 | 35.2731 | 35.3674 | 108.2424 | ON | 23.8 | 108.3 | 47.1435 | 36.1819 | -2.0883 | 2.9585 | 1.183 | 1.183 | 3.5189 |  | OK | OK | OK | OK | 109.3816 | OK | OK | OK | OK | OK
44811.9049 | 3:19 | 95 | 133.2995 | 130.3715 | 144.5371 | 71.093 | 107.1028 | 107.1028 | 22.7472 | 21.5824 | 21.6265 | 24.5212 | 50 | 45.6204 | 198.0359 | 35.0904 | 35.3719 | 108.207 | ON | 23.8 | 108.3 | 47.293 | 36.2371 | -2.2176 | 2.9388 | 1.1972 | 1.1972 | 3.5268 |  | OK | OK | OK | OK | 109.4995 | OK | OK | OK | OK | OK
44811.905 | 3:19 | 95 | 133.3224 | 130.3891 | 144.5984 | 71.0918 | 106.9604 | 106.9604 | 22.6596 | 21.4822 | 21.4071 | 24.3773 | 50 | 45.3372 | 197.304 | 35.0982 | 35.3233 | 108.091 | ON | 23.8 | 108.3 | 47.2918 | 36.2984 | -2.3178 | 2.8952 | 1.3396 | 1.3396 | 3.5312 |  | OK | OK | OK | OK | 109.5224 | OK | OK | OK | OK | OK
44811.9051 | 3:19 | 95 | 133.3054 | 130.4357 | 144.693 | 71.2212 | 106.8743 | 106.8743 | 22.4641 | 21.4102 | 21.4465 | 24.2608 | 50 | 45.5188 | 197.4774 | 35.107 | 35.3124 | 108.034 | ON | 23.8 | 108.3 | 47.4212 | 36.393 | -2.3898 | 2.8505 | 1.4257 | 1.4257 | 3.5234 |  | OK | OK | OK | OK | 109.5054 | OK | OK | OK | OK | OK
44811.9052 | 3:19 | 95 | 133.3224 | 130.4307 | 144.785 | 71.1601 | 106.8785 | 106.8785 | 22.42 | 21.3571 | 21.2929 | 24.1741 | 50 | 45.2516 | 197.3617 | 34.9537 | 35.1722 | 107.9967 | ON | 23.8 | 108.3 | 47.3601 | 36.485 | -2.443 | 2.817 | 1.4215 | 1.4215 | 3.5372 |  | OK | OK | OK | OK | 109.5224 | OK | OK | OK | OK | OK
44811.9053 | 3:20 | 95 | 133.3825 | 130.455 | 144.8227 | 71.0271 | 106.7062 | 106.7062 | 22.2916 | 21.1664 | 21.1309 | 24.0793 | 50 | 44.8785 | 196.4351 | 34.7945 | 35.0104 | 107.8375 | ON | 22.84 | 108.3 | 48.1871 | 36.5227 | -1.6736 | 2.9129 | 1.5938 | 1.5938 | 3.5438 |  | OK | OK | OK | OK | 110.5425 | OK | OK | OK | OK | OK
44811.9055 | 3:20 | 95 | 133.3803 | 130.4 | 144.8432 | 71.2475 | 106.5203 | 106.5203 | 22.1179 | 21.0232 | 20.9296 | 23.9463 | 50 | 44.9091 | 196.3291 | 34.6729 | 34.9594 | 107.6856 | ON | 22.84 | 108.3 | 48.4075 | 36.5432 | -1.8168 | 2.9231 | 1.7797 | 1.7797 | 3.5402 |  | OK | OK | OK | OK | 110.5403 | OK | OK | OK | OK | OK
44811.9056 | 3:20 | 95 | 133.7016 | 130.4914 | 145.0182 | 71.5595 | 108.1672 | 108.1672 | 22.032 | 21.0237 | 21.1257 | 23.9509 | 50 | 45.046 | 202.7761 | 34.6553 | 34.9372 | 108.8545 | ON | 23.8 | 110.2 | 47.7595 | 34.8182 | -2.7763 | 2.9271 | 2.0328 | 2.0328 | 3.64 |  | OK | OK | OK | OK | 109.9016 | OK | OK | OK | OK | OK
44811.9057 | 3:20 | 95 | 133.9203 | 130.752 | 145.2388 | 70.7308 | 108.8563 | 108.8563 | 21.7057 | 19.7634 | 21.7502 | 24.1731 | 50 | 43.0981 | 203.9292 | 34.7086 | 34.9409 | 109.3386 | ON | 21.87 | 110.2 | 48.8608 | 35.0388 | -2.1066 | 4.4097 | 1.3437 | 1.3437 | 3.7826 |  | OK | OK | OK | OK | 112.0503 | OK | OK | OK | OK | OK
44811.9058 | 3:20 | 95 | 133.9131 | 130.7687 | 145.2981 | 67.763 | 108.699 | 108.699 | 21.2644 | 19.2517 | 23.0101 | 24.9397 | 50 | 42.7105 | 203.3679 | 34.6058 | 35.087 | 109.3288 | ON | 20.88 | 110.2 | 46.883 | 35.0981 | -1.6283 | 5.688 | 1.501 | 1.501 | 3.7984 |  | OK | OK | OK | OK | 113.0331 | OK | OK | OK | OK | OK
44811.9059 | 3:20 | 95 | 133.9102 | 130.6699 | 145.0864 | 60.4901 | 108.6187 | 108.6187 | 20.922 | 18.8673 | 24.3871 | 25.9019 | 50 | 42.1517 | 203.1797 | 34.4513 | 35.16 | 109.2247 | ON | 20.88 | 110.2 | 39.6101 | 34.8864 | -2.0127 | 7.0347 | 1.5813 | 1.5813 | 3.8324 |  | OK | OK | OK | OK | 113.0302 | OK | OK | OK | OK | OK
44811.906 | 3:21 | 95 | 133.5273 | 130.3692 | 144.6917 | 53.1825 | 108.6128 | 108.6128 | 20.6604 | 18.4834 | 25.8184 | 26.8992 | 50 | 41.732 | 203.0159 | 34.3284 | 35.1823 | 109.202 | ON | 19.89 | 110.2 | 33.2925 | 34.4917 | -1.4066 | 8.4159 | 1.5872 | 1.5872 | 3.858 |  | OK | OK | OK | OK | 113.6373 | OK | OK | OK | OK | OK
44811.9061 | 3:21 | 95 | 132.7865 | 129.8364 | 144.0497 | 48.7624 | 108.5086 | 108.5086 | 20.3758 | 18.1792 | 27.1144 | 27.7956 | 50 | 41.484 | 202.7084 | 34.1925 | 35.2342 | 109.0843 | ON | 19.89 | 110.2 | 28.8724 | 33.8497 | -1.7108 | 9.6164 | 1.6914 | 1.6914 | 3.8696 |  | OK | OK | OK | OK | 112.8965 | OK | OK | OK | OK | OK
44811.9063 | 3:21 | 95 | 132.0598 | 129.1845 | 143.2343 | 46.8922 | 108.2289 | 108.2289 | 20.1011 | 17.8977 | 28.1247 | 28.5431 | 50 | 41.1819 | 201.7972 | 34.1614 | 35.2612 | 108.8321 | ON | 19.89 | 110.2 | 27.0022 | 33.0343 | -1.9923 | 10.6454 | 1.9711 | 1.9711 | 3.8742 |  | OK | OK | OK | OK | 112.1698 | OK | OK | OK | OK | OK
44811.9064 | 3:21 | 95 | 131.1213 | 128.4229 | 142.3785 | 45.5505 | 107.8763 | 107.8763 | 19.8241 | 17.6412 | 28.9056 | 29.1944 | 50 | 41.0589 | 200.6975 | 34.0924 | 35.3021 | 108.5146 | ON | 19.89 | 110.2 | 25.6605 | 32.1785 | -2.2488 | 11.5532 | 2.3237 | 2.3237 | 3.863 |  | OK | OK | OK | OK | 111.2313 | OK | OK | OK | OK | OK
44811.9065 | 3:21 | 95 | 130.3302 | 127.7315 | 141.5598 | 44.3971 | 107.6535 | 107.6535 | 19.5606 | 17.4001 | 29.4851 | 29.7139 | 50 | 40.779 | 200.3425 | 33.8962 | 35.3742 | 108.3438 | ON | 18.88 | 110.2 | 25.5171 | 31.3598 | -1.4799 | 12.3138 | 2.5465 | 2.5465 | 3.8761 |  | OK | OK | OK | OK | 111.4502 | OK | OK | OK | OK | OK
44811.9066 | 3:21 | 95 | 129.5522 | 127.1664 | 140.7728 | 43.5623 | 107.5176 | 107.5176 | 19.3331 | 17.2056 | 29.9064 | 30.1304 | 50 | 40.7034 | 200.022 | 33.908 | 35.4545 | 108.1948 | ON | 18.88 | 110.2 | 24.6823 | 30.5728 | -1.6744 | 12.9248 | 2.6824 | 2.6824 | 3.8756 |  | OK | OK | OK | OK | 110.6722 | OK | OK | OK | OK | OK
44811.9067 | 3:22 | 95 | 128.9264 | 126.5264 | 140.0584 | 43.0933 | 107.5183 | 107.5183 | 19.1366 | 16.9577 | 30.2293 | 30.4909 | 50 | 40.4239 | 200.0963 | 33.8458 | 35.4175 | 108.2148 | ON | 18.88 | 110.2 | 24.2133 | 29.8584 | -1.9223 | 13.5332 | 2.6817 | 2.6817 | 3.8966 |  | OK | OK | OK | OK | 110.0464 | OK | OK | OK | OK | OK
44811.9068 | 3:22 | 95 | 128.3013 | 126.1302 | 139.4456 | 42.7171 | 107.5142 | 107.5142 | 18.9218 | 16.8177 | 30.4917 | 30.7489 | 50 | 40.2497 | 200.0045 | 33.7096 | 35.3879 | 108.2049 | ON | 18.88 | 110.2 | 23.8371 | 29.2456 | -2.0623 | 13.9313 | 2.6858 | 2.6858 | 3.9073 |  | OK | OK | OK | OK | 109.4213 | OK | OK | OK | OK | OK
44811.907 | 3:22 | 95 | 127.8428 | 125.7601 | 138.8871 | 42.3368 | 107.5995 | 107.5995 | 18.7628 | 16.5809 | 30.6817 | 30.963 | 50 | 40.0562 | 199.8568 | 33.6804 | 35.3831 | 108.2846 | ON | 18.88 | 108.3 | 23.4568 | 30.5871 | -2.2991 | 14.3821 | 0.7005 | 0.7005 | 3.9184 |  | OK | Low Charge | OK | OK | 108.9628 | OK | OK | OK | OK | OK
44811.9071 | 3:22 | 95 | 127.3932 | 125.3286 | 138.3616 | 41.9263 | 107.5437 | 107.5437 | 18.5459 | 16.4226 | 30.8393 | 31.1216 | 50 | 39.922 | 200.1336 | 33.7837 | 35.3304 | 108.2586 | ON | 17.86 | 110.2 | 24.0663 | 28.1616 | -1.4374 | 14.699 | 2.6563 | 2.6563 | 3.9331 |  | OK | OK | OK | OK | 109.5332 | OK | OK | OK | OK | OK
44811.9072 | 3:22 | 95 | 127.074 | 125.0424 | 137.8919 | 41.4392 | 107.5273 | 107.5273 | 18.3555 | 16.1786 | 30.9318 | 31.2785 | 50 | 39.6935 | 200.1929 | 33.5093 | 35.3609 | 108.2106 | ON | 17.86 | 110.2 | 23.5792 | 27.6919 | -1.6814 | 15.0998 | 2.6727 | 2.6727 | 3.9507 |  | OK | OK | OK | OK | 109.214 | OK | OK | OK | OK | OK
44811.9073 | 3:22 | 95 | 126.8015 | 124.7631 | 137.5337 | 40.9812 | 107.5853 | 107.5853 | 18.1648 | 16.0021 | 31.0675 | 31.3778 | 50 | 39.5397 | 200.2397 | 33.4602 | 35.2884 | 108.3087 | ON | 17.86 | 110.2 | 23.1212 | 27.3337 | -1.8579 | 15.3756 | 2.6147 | 2.6147 | 3.9628 |  | OK | OK | OK | OK | 108.9415 | OK | OK | OK | OK | OK
44811.9074 | 3:23 | 95 | 126.6732 | 124.5731 | 137.2671 | 40.7838 | 107.6873 | 107.6873 | 17.99 | 15.846 | 31.1194 | 31.4375 | 50 | 39.2959 | 200.325 | 33.4368 | 35.2332 | 108.394 | ON | 17.86 | 110.2 | 22.9238 | 27.0671 | -2.014 | 15.5915 | 2.5127 | 2.5127 | 3.9822 |  | OK | OK | OK | OK | 108.8132 | OK | OK | OK | OK | OK
44811.9075 | 3:23 | 95 | 126.4366 | 124.4248 | 136.9489 | 40.4289 | 107.6835 | 107.6835 | 17.7836 | 15.6511 | 31.173 | 31.501 | 50 | 39.2479 | 200.6156 | 33.5029 | 35.2571 | 108.3736 | ON | 17.86 | 110.2 | 22.5689 | 26.7489 | -2.2089 | 15.8499 | 2.5165 | 2.5165 | 3.9912 |  | OK | OK | OK | OK | 108.5766 | OK | OK | OK | OK | OK
44811.9077 | 3:23 | 95 | 126.8516 | 124.6094 | 137.0361 | 39.9257 | 108.8852 | 108.8852 | 16.9292 | 15.0487 | 31.2168 | 31.5275 | 50 | 37.8686 | 209.4519 | 33.3073 | 35.2631 | 109.6588 | ON | 15.76 | 112 | 24.1657 | 25.0361 | -0.71133 | 16.4788 | 3.1148 | 3.1148 | 4.264 |  | OK | OK | OK | OK | 111.0916 | OK | OK | OK | OK | OK
44811.9078 | 3:23 | 95 | 127.1759 | 125.32 | 136.7954 | 41.7533 | 109.4409 | 109.4409 | 15.4849 | 15.6425 | 31.2122 | 31.4723 | 50 | 18.6298 | 205.7848 | 33.0335 | 35.2732 | 109.7513 | ON | -7.99 | 112 | 49.7433 | 24.7954 | 23.6325 | 15.8298 | 2.5591 | 2.5591 | 6.6152 |  | OK | OK | OK | OK | 135.1659 | OK | OK | OK | OK | OK
44811.9079 | 3:23 | 95 | 127.1471 | 124.905 | 135.2292 | 46.471 | 106.8592 | 106.8592 | 17.4624 | 17.822 | 31.2322 | 31.4875 | 50 | 18.553 | 201.1063 | 33.5352 | 35.3492 | 108.1441 | ON | -7.99 | 110.2 | 54.461 | 25.0292 | 25.812 | 13.6655 | 3.3408 | 3.3408 | 6.4898 |  | OK | OK | OK | OK | 135.1371 | OK | OK | OK | OK | OK
44811.908 | 3:23 | 95 | 127.4416 | 124.6045 | 134.3219 | 49.3793 | 105.1269 | 105.1269 | 19.858 | 19.8 | 31.2617 | 31.5401 | 50 | 17.0537 | 197.9494 | 33.941 | 35.5404 | 107.2072 | ON | -9.5 | 108.3 | 58.8793 | 26.0219 | 29.3 | 11.7401 | 3.1731 | 3.1731 | 6.6968 |  | OK | OK | OK | OK | 136.9416 | OK | OK | OK | OK | OK
44811.9081 | 3:24 | 95 | 127.9379 | 124.5029 | 133.9366 | 50.1658 | 104.727 | 104.727 | 22.1645 | 21.6384 | 31.3021 | 31.6251 | 50 | 16.15 | 196.0131 | 34.4133 | 35.6585 | 106.6746 | ON | -11.06 | 108.3 | 61.2258 | 25.6366 | 32.6985 | 9.9866 | 3.573 | 3.573 | 6.8303 |  | OK | OK | OK | OK | 138.9979 | OK | OK | OK | OK | OK
44811.9082 | 3:24 | 95 | 128.6286 | 124.6456 | 133.8831 | 52.7754 | 104.5186 | 104.5186 | 24.2322 | 23.184 | 31.344 | 31.7408 | 50 | 15.1619 | 195.7266 | 34.8278 | 35.8518 | 106.4018 | ON | -12.65 | 108.3 | 65.4254 | 25.5831 | 35.834 | 8.5568 | 3.7814 | 3.7814 | 7.0466 |  | OK | OK | OK | OK | 141.2786 | OK | OK | OK | OK | OK
44811.9083 | 3:24 | 95 | 129.4603 | 124.8717 | 134.0933 | 55.6119 | 104.1243 | 104.1243 | 25.9266 | 24.4946 | 31.3659 | 31.8537 | 50 | 14.5494 | 195.1451 | 34.892 | 35.9724 | 106.2283 | ON | -14.28 | 108.3 | 69.8919 | 25.7933 | 38.7746 | 7.359 | 4.1757 | 4.1757 | 7.1744 |  | OK | OK | OK | OK | 143.7403 | OK | OK | OK | OK | OK
44811.9085 | 3:24 | 95 | 130.3859 | 125.2273 | 134.4292 | 58.4892 | 103.9416 | 103.9416 | 27.3559 | 25.6296 | 31.4145 | 32.0109 | 50 | 14.1639 | 194.814 | 35.204 | 36.0845 | 106.1553 | ON | -14.28 | 106.4 | 72.7692 | 28.0292 | 39.9096 | 6.3813 | 2.4584 | 2.4584 | 7.2587 |  | OK | OK | OK | OK | 144.6659 | OK | OK | OK | OK | OK
44811.9086 | 3:24 | 95 | 131.2365 | 125.5582 | 134.8227 | 61.6994 | 103.94 | 103.94 | 28.4845 | 26.5416 | 31.4439 | 32.169 | 50 | 13.9215 | 194.6589 | 35.5451 | 36.2019 | 106.0837 | ON | -15.96 | 106.4 | 77.6594 | 28.4227 | 42.5016 | 5.6275 | 2.46 | 2.46 | 7.3147 |  | OK | OK | OK | OK | 147.1965 | OK | OK | OK | OK | OK
44811.9087 | 3:24 | 95 | 132.1839 | 125.9801 | 135.2272 | 62.7962 | 103.9851 | 103.9851 | 29.3507 | 27.3088 | 31.4869 | 32.3157 | 50 | 13.4348 | 194.5931 | 35.6838 | 36.2963 | 106.0334 | ON | -15.96 | 106.4 | 78.7562 | 28.8272 | 43.2688 | 5.0069 | 2.4149 | 2.4149 | 7.4389 |  | OK | OK | OK | OK | 148.1439 | OK | OK | OK | OK | OK
44811.9088 | 3:25 | 95 | 132.9874 | 126.4951 | 135.6848 | 63.2745 | 103.8354 | 103.8354 | 30.0094 | 27.9415 | 31.5189 | 32.4451 | 50 | 13.0387 | 194.5885 | 35.7093 | 36.3569 | 106.0195 | ON | -15.96 | 106.4 | 79.2345 | 29.2848 | 43.9015 | 4.5036 | 2.5646 | 2.5646 | 7.545 |  | OK | OK | OK | OK | 148.9474 | OK | OK | OK | OK | OK
44811.9089 | 3:25 | 95 | 133.8786 | 126.9159 | 136.1915 | 63.4757 | 103.8242 | 103.8242 | 30.4264 | 28.4304 | 31.5528 | 32.6127 | 50 | 12.8397 | 194.4777 | 35.8409 | 36.4722 | 106.0514 | ON | -17.69 | 106.4 | 81.1658 | 29.7915 | 46.1204 | 4.1823 | 2.5758 | 2.5758 | 7.5955 |  | OK | OK | OK | OK | 151.5686 | OK | OK | OK | OK | OK
44811.909 | 3:25 | 95 | 134.7369 | 127.4499 | 136.7626 | 63.5354 | 103.9716 | 103.9716 | 30.7674 | 28.8163 | 31.5672 | 32.7534 | 50 | 12.6153 | 194.6916 | 35.9374 | 36.459 | 106.0898 | ON | -17.69 | 106.4 | 81.2254 | 30.3626 | 46.5063 | 3.9371 | 2.4284 | 2.4284 | 7.6657 |  | OK | OK | OK | OK | 152.4269 | OK | OK | OK | OK | OK
44811.9092 | 3:25 | 95 | 135.4799 | 127.993 | 137.3885 | 63.3715 | 103.9267 | 103.9267 | 30.9818 | 29.1174 | 31.5995 | 32.9066 | 50 | 12.5097 | 194.7297 | 36.1092 | 36.6272 | 106.1247 | ON | -17.69 | 106.4 | 81.0615 | 30.9885 | 46.8074 | 3.7893 | 2.4733 | 2.4733 | 7.6969 |  | OK | OK | OK | OK | 153.1699 | OK | OK | OK | OK | OK
44811.9093 | 3:25 | 95 | 136.1188 | 128.4935 | 137.922 | 63.0683 | 104.011 | 104.011 | 31.157 | 29.4083 | 31.6105 | 33.0629 | 50 | 12.6004 | 194.8709 | 36.1316 | 36.6872 | 106.1413 | ON | -17.69 | 106.4 | 80.7583 | 31.522 | 47.0983 | 3.6546 | 2.389 | 2.389 | 7.6765 |  | OK | OK | OK | OK | 153.8088 | OK | OK | OK | OK | OK
44811.9094 | 3:25 | 95 | 136.6585 | 128.7422 | 138.1929 | 62.7763 | 103.853 | 103.853 | 31.2688 | 29.613 | 31.6373 | 33.2213 | 50 | 13.5845 | 194.0998 | 36.262 | 36.6813 | 106.0238 | ON | -15.96 | 106.4 | 78.7363 | 31.7929 | 45.573 | 3.6083 | 2.547 | 2.547 | 7.3821 |  | OK | OK | OK | OK | 152.6185 | OK | OK | OK | OK | OK
44811.9095 | 3:26 | 95 | 136.7973 | 128.8481 | 138.3224 | 62.0282 | 103.8275 | 103.8275 | 31.3404 | 29.8163 | 31.6347 | 33.3754 | 50 | 14.5744 | 193.5116 | 36.2727 | 36.815 | 105.8186 | ON | -14.28 | 106.4 | 76.3082 | 31.9224 | 44.0963 | 3.5591 | 2.5725 | 2.5725 | 7.1124 |  | OK | OK | OK | OK | 151.0773 | OK | OK | OK | OK | OK
44811.9096 | 3:26 | 95 | 140.0863 | 127.1543 | 136.2289 | 60.7133 | 95.3952 | 95.3952 | 26.1977 | 30.5894 | 28.213 | 33.849 | 50 | 52.9622 | 136.1929 | 36.2771 | 36.7985 | 102.3731 | OFF | 30.19 | 82.79 | 30.5233 | 53.4389 | 0.39945 | 3.2596 | -12.6052 | -12.6052 | 2.2301
44811.9097 | 3:26 | 95 | 139.8213 | 124.4366 | 128.3715 | 72.4977 | 92.0397 | 92.0397 | 31.2549 | 31.4525 | 30.4945 | 33.8375 | 50 | 58.4919 | 113.0667 | 36.27 | 36.9151 | 101.2336 | OFF | 35.28 | 69.9 | 37.2178 | 58.4715 | -3.8275 | 2.385 | -22.1397 | -22.1397 | 1.7456
44811.9099 | 3:26 | 95 | 138.7208 | 122.7951 | 120.9176 | 82.1864 | 90.4723 | 90.4723 | 31.8841 | 32.417 | 31.4363 | 33.8961 | 50 | 59.5301 | 103.394 | 36.2908 | 36.8912 | 100.2285 | OFF | 36.1 | 64.21 | 46.0864 | 56.7076 | -3.683 | 1.4791 | -26.2623 | -26.2623 | 1.5909
44811.91 | 3:26 | 95 | 137.3462 | 121.2237 | 115.0894 | 89.5223 | 88.8575 | 88.8575 | 31.8747 | 33.4218 | 31.6435 | 34.0985 | 50 | 60.3702 | 92.0135 | 36.5258 | 37.0935 | 99.5139 | OFF | 36.91 | 58.13 | 52.6123 | 56.9594 | -3.4882 | 0.67672 | -30.7275 | -30.7275 | 1.4215
44811.9101 | 3:26 | 95 | 135.925 | 119.7937 | 111.0845 | 93.5173 | 87.635 | 87.635 | 31.8591 | 34.1296 | 31.6938 | 34.4419 | 50 | 61.0997 | 84.9729 | 36.5068 | 37.0437 | 98.9999 | OFF | 37.71 | 51.63 | 55.8073 | 59.4545 | -3.5804 | 0.31229 | -36.005 | -36.005 | 1.315
44811.9102 | 3:27 | 95 | 134.5182 | 118.4304 | 108.3213 | 95.9036 | 86.9344 | 86.9344 | 31.8636 | 34.732 | 31.7438 | 34.7481 | 50 | 61.5622 | 78.4424 | 36.6748 | 37.1207 | 98.5741 | OFF | 37.71 | 48.19 | 58.1936 | 60.1313 | -2.978 | 0.01606 | -38.7444 | -38.7444 | 1.2213
44811.9103 | 3:27 | 95 | 133.2836 | 117.1859 | 106.494 | 97.1484 | 86.9338 | 86.9338 | 31.8709 | 35.0947 | 31.7835 | 35.001 | 50 | 61.9334 | 72.6562 | 36.7218 | 37.2118 | 98.2449 | OFF | 37.71 | 44.59 | 59.4384 | 61.904 | -2.6153 | -0.0937 | -42.3438 | -42.3438 | 1.1399
44811.9104 | 3:27 | 95 | 132.0826 | 116.085 | 105.3909 | 97.2749 | 87.7049 | 87.7049 | 31.8726 | 35.2159 | 31.7685 | 35.1042 | 50 | 62.0515 | 68.2189 | 36.7952 | 37.3496 | 97.993 | OFF | 38.5 | 43.11 | 58.7749 | 62.2809 | -3.2841 | -0.11169 | -44.5949 | -44.5949 | 1.0804
44811.9105 | 3:27 | 95 | 130.976 | 115.0767 | 104.7594 | 96.8635 | 88.9353 | 88.9353 | 31.8784 | 35.2747 | 31.8041 | 35.138 | 50 | 62.1443 | 66.3327 | 36.841 | 37.3936 | 97.7891 | OFF | 38.5 | 41.6 | 58.3635 | 63.1594 | -3.2253 | -0.13677 | -47.3353 | -47.3353 | 1.0545
44811.9107 | 3:27 | 95 | 129.9217 | 114.1202 | 104.3407 | 97.3977 | 90.0265 | 90.0265 | 31.8962 | 35.3537 | 31.8432 | 35.2538 | 50 | 62.2272 | 65.1258 | 36.88 | 37.518 | 97.6053 | OFF | 38.5 | 40.84 | 58.8977 | 63.5007 | -3.1463 | -0.09994 | -49.1865 | -49.1865 | 1.0377
44811.9108 | 3:27 | 95 | 128.9358 | 113.3735 | 103.9724 | 97.3368 | 90.9894 | 90.9894 | 31.9138 | 35.5115 | 31.8122 | 35.3476 | 50 | 62.4855 | 64.4648 | 36.9276 | 37.4493 | 97.4419 | OFF | 38.5 | 40.07 | 58.8368 | 63.9024 | -2.9885 | -0.16386 | -50.9194 | -50.9194 | 1.0256
44811.9109 | 3:28 | 95 | 127.9296 | 112.6487 | 103.6812 | 97.138 | 91.8624 | 91.8624 | 31.938 | 35.835 | 31.8474 | 35.5253 | 50 | 62.7368 | 63.9571 | 37.115 | 37.5702 | 97.2815 | OFF | 38.5 | 39.29 | 58.638 | 64.3912 | -2.665 | -0.30969 | -52.5724 | -52.5724 | 1.0158
44811.911 | 3:28 | 95 | 127.0214 | 112.1012 | 103.4578 | 96.9667 | 92.6043 | 92.6043 | 31.9599 | 35.9971 | 31.8622 | 35.6502 | 50 | 62.9892 | 63.5307 | 37.1718 | 37.6944 | 97.1606 | OFF | 38.5 | 39.29 | 58.4667 | 64.1678 | -2.5029 | -0.34686 | -53.3143 | -53.3143 | 1.007
44811.9111 | 3:28 | 95 | 126.2264 | 111.5483 | 103.2144 | 96.832 | 93.1256 | 93.1256 | 31.9892 | 36.1568 | 31.9044 | 35.8376 | 50 | 63.4053 | 62.7682 | 37.2982 | 37.8653 | 97.0518 | OFF | 39.29 | 38.5 | 57.542 | 64.7144 | -3.1332 | -0.31924 | -54.6256 | -54.6256 | 0.99184
44811.9112 | 3:28 | 95 | 125.456 | 110.9723 | 102.9509 | 96.7757 | 93.5881 | 93.5881 | 32.0359 | 36.3489 | 31.9327 | 36.0165 | 50 | 63.7222 | 62.8362 | 37.4466 | 37.8033 | 96.9062 | OFF | 39.29 | 38.5 | 57.4857 | 64.4509 | -2.9411 | -0.33241 | -55.0881 | -55.0881 | 0.9887
44811.9114 | 3:28 | 95 | 124.6943 | 110.5834 | 102.7604 | 96.6076 | 93.9836 | 93.9836 | 32.0637 | 36.5778 | 32.0386 | 36.3049 | 50 | 64 | 63.3152 | 37.4506 | 37.8373 | 96.793 | OFF | 40.07 | 39.29 | 56.5376 | 63.4704 | -3.4922 | -0.27298 | -54.6936 | -54.6936 | 0.9913
44811.9115 | 3:28 | 95 | 123.9048 | 110.0721 | 102.5843 | 96.5126 | 94.277 | 94.277 | 32.1021 | 36.7912 | 32.1079 | 36.5771 | 50 | 64.3403 | 63.418 | 37.5364 | 37.9636 | 96.6744 | OFF | 40.07 | 39.29 | 56.4426 | 63.2943 | -3.2788 | -0.21409 | -54.987 | -54.987 | 0.98833
44811.9116 | 3:29 | 95 | 123.2898 | 109.7325 | 102.3556 | 96.4423 | 94.4736 | 94.4736 | 32.1565 | 36.9479 | 32.3063 | 36.901 | 50 | 64.6531 | 63.7079 | 37.7439 | 38.0432 | 96.5639 | OFF | 40.07 | 39.29 | 56.3723 | 63.0656 | -3.1221 | -0.04688 | -55.1836 | -55.1836 | 0.98809
44811.9117 | 3:29 | 95 | 122.6308 | 109.4003 | 102.1733 | 96.3907 | 94.6359 | 94.6359 | 32.2585 | 37.1124 | 32.6314 | 37.1331 | 50 | 64.9392 | 64.0683 | 37.8171 | 38.1403 | 96.4728 | OFF | 40.07 | 40.07 | 56.3207 | 62.1033 | -2.9576 | 0.02066 | -54.5659 | -54.5659 | 0.98906
44811.9118 | 3:29 | 95 | 121.9722 | 109.0645 | 101.9951 | 96.2356 | 94.7525 | 94.7525 | 32.4159 | 37.3351 | 33.0834 | 37.3433 | 50 | 65.2254 | 64.2718 | 37.8476 | 38.2549 | 96.3789 | OFF | 40.84 | 40.07 | 55.3956 | 61.9251 | -3.5049 | 0.00817 | -54.6825 | -54.6825 | 0.98807
44811.9119 | 3:29 | 95 | 121.3866 | 108.7049 | 101.803 | 96.1022 | 94.7947 | 94.7947 | 32.6013 | 37.5552 | 33.6481 | 37.5915 | 50 | 65.4998 | 64.5921 | 37.9728 | 38.3747 | 96.2691 | OFF | 40.84 | 40.07 | 55.2622 | 61.733 | -3.2848 | 0.03628 | -54.7247 | -54.7247 | 0.98868
44811.9121 | 3:29 | 95 | 120.8474 | 108.3855 | 101.6103 | 95.935 | 94.8101 | 94.8101 | 32.8022 | 37.7623 | 34.3113 | 37.8049 | 50 | 65.7392 | 64.7301 | 38.0042 | 38.3711 | 96.1537 | OFF | 40.84 | 40.07 | 55.095 | 61.5403 | -3.0777 | 0.04258 | -54.7401 | -54.7401 | 0.98745
44811.9122 | 3:29 | 95 | 120.2805 | 108.1082 | 101.444 | 95.7816 | 94.8265 | 94.8265 | 33.0456 | 37.9349 | 34.8276 | 37.997 | 50 | 65.9433 | 64.9178 | 38.1307 | 38.493 | 96.0513 | OFF | 40.84 | 40.07 | 54.9416 | 61.374 | -2.9051 | 0.06209 | -54.7565 | -54.7565 | 0.98728
44811.9123 | 3:30 | 95 | 119.7117 | 107.7729 | 101.2545 | 95.6675 | 94.8101 | 94.8101 | 33.3269 | 38.0496 | 35.2271 | 38.1337 | 50 | 66.108 | 65.1374 | 38.2343 | 38.5868 | 95.9293 | OFF | 41.6 | 40.84 | 54.0675 | 60.4145 | -3.5504 | 0.08419 | -53.9701 | -53.9701 | 0.98799
44811.9124 | 3:30 | 95 | 119.2351 | 107.4921 | 101.0698 | 95.617 | 94.7772 | 94.7772 | 33.7536 | 38.1444 | 35.5818 | 38.2728 | 50 | 66.3012 | 65.3149 | 38.318 | 38.6572 | 95.8206 | OFF | 41.6 | 40.84 | 54.017 | 60.2298 | -3.4556 | 0.12842 | -53.9372 | -53.9372 | 0.98782
44811.9125 | 3:30 | 95 | 118.7483 | 107.2359 | 100.8779 | 95.5781 | 94.7522 | 94.7522 | 34.3575 | 38.2417 | 35.9018 | 38.4431 | 50 | 66.5311 | 65.4545 | 38.5083 | 38.7765 | 95.6942 | OFF | 41.6 | 40.84 | 53.9781 | 60.0379 | -3.3583 | 0.20144 | -53.9122 | -53.9122 | 0.98675
44811.9126 | 3:30 | 95 | 118.3029 | 107.0119 | 100.738 | 95.4591 | 94.722 | 94.722 | 34.8087 | 38.3647 | 36.2364 | 38.6085 | 50 | 66.7321 | 65.6779 | 38.5448 | 38.8105 | 95.5513 | OFF | 41.6 | 40.84 | 53.8591 | 59.898 | -3.2353 | 0.24385 | -53.882 | -53.882 | 0.98705
44811.9127 | 3:30 | 95 | 119.6478 | 107.0425 | 112.088 | 79.2975 | 95.0256 | 95.0256 | 34.6116 | 35.1379 | 35.0793 | 36.6092 | 50 | 60.6961 | 125.6312 | 38.6955 | 38.8555 | 96.0013 | OFF | 36.91 | 77.84 | 42.3875 | 34.248 | -1.7721 | 1.4713 | -17.1856 | -17.1856 | 1.8613
44811.9129 | 3:30 | 95 | 120.3026 | 108.4761 | 128.3184 | 61.66 | 98.2052 | 98.2052 | 30.9775 | 29.796 | 30.4739 | 35.9 | 50 | 53.2565 | 178.2291 | 38.466 | 38.7741 | 100.3233 | ON | 31.06 | 100.5 | 30.5999 | 27.8184 | -1.264 | 6.1041 | 2.2948 | 2.2948 | 2.839 |  | OK | OK | OK | OK | 89.2426 | OK | OK | OK | OK | OK
44811.913 | 3:31 | 95 | 118.4536 | 113.0252 | 129.328 | 57.9497 | 102.5055 | 102.5055 | 29.731 | 29.0078 | 28.9376 | 34.0836 | 50 | 52.4954 | 187.5543 | 38.0042 | 38.5278 | 103.4418 | ON | 30.19 | 104.4 | 27.7597 | 24.928 | -1.1822 | 5.0758 | 1.8945 | 1.8945 | 3.0099 |  | OK | OK | OK | OK | 88.2636 | OK | OK | OK | OK | OK
44811.9131 | 3:31 | 95 | 117.7377 | 115.0674 | 128.9568 | 59.1309 | 103.304 | 103.304 | 29.8344 | 30.51 | 27.9237 | 30.736 | 50 | 51.4364 | 189.023 | 37.7307 | 38.3332 | 104.2743 | ON | 29.31 | 104.4 | 29.8209 | 24.5568 | 1.2 | 0.22594 | 1.096 | 1.096 | 3.0803 |  | OK | OK | OK | OK | 88.4277 | OK | OK | OK | OK | OK
44811.9132 | 3:31 | 95 | 117.8605 | 116.2704 | 129.1414 | 56.2215 | 103.963 | 103.963 | 30.0493 | 31.0878 | 27.4276 | 27.0964 | 50 | 51.5949 | 191.0798 | 37.7195 | 38.1488 | 104.9185 | ON | 29.31 | 106.4 | 26.9115 | 22.7414 | 1.7778 | -3.9914 | 2.437 | 2.437 | 3.104 |  | OK | OK | OK | OK | 88.5505 | OK | OK | OK | OK | OK
44811.9133 | 3:31 | 95 | 118.2718 | 117.1639 | 129.3527 | 55.4417 | 104.5418 | 104.5418 | 29.9235 | 31.4112 | 26.9308 | 26.4108 | 50 | 51.3145 | 192.2319 | 37.6319 | 38.0054 | 105.4593 | ON | 29.31 | 106.4 | 26.1317 | 22.9527 | 2.1012 | -5.0004 | 1.8582 | 1.8582 | 3.1346 |  | OK | OK | OK | OK | 88.9618 | OK | OK | OK | OK | OK
44811.9134 | 3:31 | 95 | 118.8192 | 117.9107 | 129.6069 | 56.1684 | 104.8384 | 104.8384 | 29.6891 | 31.5135 | 26.4523 | 26.0793 | 50 | 51.1005 | 193.213 | 37.6419 | 37.9103 | 105.7819 | ON | 29.31 | 106.4 | 26.8584 | 23.2069 | 2.2035 | -5.4342 | 1.5616 | 1.5616 | 3.1597 |  | OK | OK | OK | OK | 89.5092 | OK | OK | OK | OK | OK
44811.9136 | 3:31 | 95 | 119.4758 | 118.5492 | 129.9352 | 59.9831 | 105.0569 | 105.0569 | 29.233 | 31.4545 | 26.0373 | 25.8169 | 50 | 50.8016 | 193.1585 | 37.5618 | 37.8031 | 106.0234 | ON | 28.42 | 106.4 | 31.5631 | 23.5352 | 3.0345 | -5.6376 | 1.3431 | 1.3431 | 3.1733 |  | OK | OK | OK | OK | 91.0558 | OK | OK | OK | OK | OK
44811.9137 | 3:32 | 95 | 120.065 | 119.118 | 130.3677 | 62.9846 | 105.1333 | 105.1333 | 28.5411 | 31.2967 | 25.6915 | 25.6462 | 50 | 50.5391 | 193.7667 | 37.5025 | 37.713 | 106.1613 | ON | 28.42 | 106.4 | 34.5646 | 23.9677 | 2.8767 | -5.6505 | 1.2667 | 1.2667 | 3.1954 |  | OK | OK | OK | OK | 91.645 | OK | OK | OK | OK | OK
44811.9138 | 3:32 | 95 | 120.807 | 119.6788 | 130.9137 | 65.0062 | 105.2932 | 105.2932 | 28.2901 | 31.1515 | 25.4056 | 25.8412 | 50 | 50.3832 | 194.0829 | 37.3161 | 37.7128 | 106.3117 | ON | 28.42 | 106.4 | 36.5862 | 24.5137 | 2.7315 | -5.3103 | 1.1068 | 1.1068 | 3.2079 |  | OK | OK | OK | OK | 92.387 | OK | OK | OK | OK | OK
44811.9139 | 3:32 | 95 | 121.5503 | 120.2075 | 131.4454 | 66.3356 | 105.3312 | 105.3312 | 28.1146 | 31.0466 | 25.2619 | 26.1224 | 50 | 50.2437 | 194.0952 | 37.3664 | 37.5378 | 106.3951 | ON | 28.42 | 106.4 | 37.9156 | 25.0454 | 2.6266 | -4.9242 | 1.0688 | 1.0688 | 3.215 |  | OK | OK | OK | OK | 93.1303 | OK | OK | OK | OK | OK
44811.914 | 3:32 | 95 | 122.2106 | 120.736 | 132.0566 | 67.4147 | 105.4161 | 105.4161 | 28.0267 | 30.9245 | 25.1707 | 26.212 | 50 | 50.1668 | 194.0309 | 37.3787 | 37.4763 | 106.5133 | ON | 28.42 | 106.4 | 38.9947 | 25.6566 | 2.5045 | -4.7125 | 0.9839 | 0.9839 | 3.2178 |  | OK | Low Charge | OK | OK | 93.7906 | OK | OK | OK | OK | OK
44811.9141 | 3:32 | 95 | 122.7852 | 121.2326 | 132.6347 | 68.1515 | 105.5549 | 105.5549 | 27.9607 | 30.7366 | 25.0457 | 26.1589 | 50 | 50.0026 | 194.5925 | 37.1822 | 37.4302 | 106.6436 | ON | 28.42 | 106.4 | 39.7315 | 26.2347 | 2.3166 | -4.5777 | 0.8451 | 0.8451 | 3.2347 |  | OK | Low Charge | OK | OK | 94.3652 | OK | OK | OK | OK | OK
44811.9143 | 3:32 | 95 | 123.365 | 121.713 | 133.2406 | 68.7836 | 105.6032 | 105.6032 | 27.8402 | 30.4901 | 24.8196 | 25.3971 | 50 | 49.9175 | 194.5052 | 37.1279 | 37.3081 | 106.7234 | ON | 27.51 | 106.4 | 41.2736 | 26.8406 | 2.9801 | -5.093 | 0.7968 | 0.7968 | 3.2376 |  | OK | Low Charge | OK | OK | 95.855 | OK | OK | OK | OK | OK
44811.9144 | 3:33 | 95 | 123.982 | 122.2448 | 133.89 | 69.3231 | 105.7185 | 105.7185 | 27.6423 | 29.324 | 24.6167 | 24.9472 | 50 | 49.6982 | 194.7206 | 37.1087 | 37.2443 | 106.8818 | ON | 27.51 | 106.4 | 41.8131 | 27.49 | 1.814 | -4.3769 | 0.6815 | 0.6815 | 3.252 |  | OK | Low Charge | OK | OK | 96.472 | OK | OK | OK | OK | OK
44811.9145 | 3:33 | 95 | 124.5804 | 122.7112 | 134.5164 | 69.8779 | 105.8419 | 105.8419 | 27.4819 | 26.2964 | 24.3894 | 25.0672 | 50 | 49.3451 | 195.3179 | 36.9738 | 37.1012 | 106.955 | ON | 27.51 | 108.3 | 42.3679 | 26.2164 | -1.2136 | -1.2292 | 2.4581 | 2.4581 | 3.2792 |  | OK | OK | OK | OK | 97.0704 | OK | OK | OK | OK | OK
44811.9146 | 3:33 | 95 | 125.1579 | 123.1147 | 135.0798 | 69.9849 | 105.9448 | 105.9448 | 27.1378 | 25.4522 | 25.5794 | 25.4825 | 50 | 49.1223 | 195.4428 | 36.9794 | 36.985 | 107.0975 | ON | 27.51 | 108.3 | 42.4749 | 26.7798 | -2.0578 | 0.0303 | 2.3552 | 2.3552 | 3.2926 |  | OK | OK | OK | OK | 97.6479 | OK | OK | OK | OK | OK
44811.9147 | 3:33 | 95 | 125.72 | 123.5972 | 135.6891 | 70.5175 | 106.1406 | 106.1406 | 26.9093 | 25.1934 | 25.0594 | 25.6723 | 50 | 49.0626 | 195.8378 | 36.7538 | 36.9334 | 107.2601 | ON | 27.51 | 108.3 | 43.0075 | 27.3891 | -2.3166 | 0.47892 | 2.1594 | 2.1594 | 3.3019 |  | OK | OK | OK | OK | 98.21 | OK | OK | OK | OK | OK
44811.9148 | 3:33 | 95 | 126.251 | 124.1114 | 136.4016 | 70.4522 | 106.3359 | 106.3359 | 26.6744 | 24.8378 | 24.4626 | 25.4899 | 50 | 48.4658 | 196.1345 | 36.7 | 36.8117 | 107.4434 | ON | 26.6 | 108.3 | 43.8522 | 28.1016 | -1.7622 | 0.65214 | 1.9641 | 1.9641 | 3.3378 |  | OK | OK | OK | OK | 99.651 | OK | OK | OK | OK | OK
44811.9149 | 3:33 | 95 | 126.8202 | 124.5022 | 136.9521 | 70.5705 | 106.4735 | 106.4735 | 26.435 | 24.6857 | 24.3854 | 25.6147 | 50 | 48.6293 | 196.6863 | 36.6234 | 36.761 | 107.6227 | ON | 26.6 | 108.3 | 43.9705 | 28.6521 | -1.9143 | 0.929 | 1.8265 | 1.8265 | 3.3379 |  | OK | OK | OK | OK | 100.2202 | OK | OK | OK | OK | OK
44811.9151 | 3:34 | 95 | 127.41 | 125.0388 | 137.5962 | 70.821 | 106.7715 | 106.7715 | 26.2637 | 24.5768 | 24.1666 | 25.9571 | 50 | 48.5876 | 197.6214 | 36.5427 | 36.733 | 107.8502 | ON | 26.6 | 108.3 | 44.221 | 29.2962 | -2.0232 | 1.3803 | 1.5285 | 1.5285 | 3.3549 |  | OK | OK | OK | OK | 100.81 | OK | OK | OK | OK | OK
44811.9152 | 3:34 | 95 | 127.8993 | 125.5279 | 138.188 | 70.4349 | 107.0446 | 107.0446 | 26.1061 | 24.4226 | 24.0537 | 26.729 | 50 | 48.5621 | 198.3771 | 36.4619 | 36.7362 | 108.0839 | ON | 26.6 | 108.3 | 43.8349 | 29.888 | -2.1774 | 2.3065 | 1.2554 | 1.2554 | 3.3682 |  | OK | OK | OK | OK | 101.2993 | OK | OK | OK | OK | OK
44811.9153 | 3:34 | 95 | 128.4265 | 125.9858 | 138.7164 | 70.2817 | 107.1721 | 107.1721 | 25.9128 | 24.2809 | 23.962 | 27.3638 | 50 | 48.0498 | 198.6021 | 36.4275 | 36.7484 | 108.24 | ON | 26.6 | 108.3 | 43.6817 | 30.4164 | -2.3191 | 3.0829 | 1.1279 | 1.1279 | 3.3992 |  | OK | OK | OK | OK | 101.8265 | OK | OK | OK | OK | OK
44811.9154 | 3:34 | 95 | 128.7756 | 126.3646 | 139.205 | 70.0783 | 107.2607 | 107.2607 | 25.667 | 24.0797 | 23.869 | 27.5335 | 50 | 48.1931 | 198.84 | 36.3668 | 36.7746 | 108.3545 | ON | 26.6 | 108.3 | 43.4783 | 30.905 | -2.5204 | 3.4539 | 1.0393 | 1.0393 | 3.3953 |  | OK | OK | OK | OK | 102.1756 | OK | OK | OK | OK | OK
44811.9155 | 3:34 | 95 | 129.207 | 126.7263 | 139.6754 | 70.2491 | 107.4357 | 107.4357 | 25.5003 | 23.9329 | 23.6882 | 27.4642 | 50 | 47.6399 | 199.2302 | 36.2311 | 36.6702 | 108.5188 | ON | 25.68 | 108.3 | 44.5691 | 31.3754 | -1.7471 | 3.5313 | 0.8643 | 0.8643 | 3.4317 |  | OK | Low Charge | OK | OK | 103.527 | OK | OK | OK | OK | OK
44811.9156 | 3:34 | 95 | 129.5712 | 127.0596 | 140.0565 | 70.1104 | 107.6184 | 107.6184 | 25.2843 | 23.8089 | 23.635 | 27.2445 | 50 | 47.9381 | 199.7603 | 36.2352 | 36.6342 | 108.6771 | ON | 25.68 | 108.3 | 44.4304 | 31.7565 | -1.8711 | 3.4356 | 0.6816 | 0.6816 | 3.4238 |  | OK | Low Charge | OK | OK | 103.8912 | OK | OK | OK | OK | OK
44811.9158 | 3:35 | 95 | 129.8662 | 127.3237 | 140.3733 | 69.9567 | 107.6791 | 107.6791 | 25.0786 | 23.6146 | 23.3908 | 26.9457 | 50 | 47.7258 | 199.6133 | 36.1277 | 36.5229 | 108.7655 | ON | 25.68 | 108.3 | 44.2767 | 32.0733 | -2.0654 | 3.3311 | 0.6209 | 0.6209 | 3.4331 |  | OK | Low Charge | OK | OK | 104.1862 | OK | OK | OK | OK | OK
44811.9159 | 3:35 | 95 | 130.1667 | 127.5479 | 140.6765 | 69.9569 | 107.7074 | 107.7074 | 24.9823 | 23.4841 | 23.3705 | 26.6457 | 50 | 47.6088 | 199.7263 | 36.117 | 36.4529 | 108.8149 | ON | 25.68 | 108.3 | 44.2769 | 32.3765 | -2.1959 | 3.1616 | 0.5926 | 0.5926 | 3.4414 |  | OK | Low Charge | OK | OK | 104.4867 | OK | OK | OK | OK | OK
44811.916 | 3:35 | 95 | 130.4088 | 127.8512 | 140.9816 | 70.1025 | 107.8433 | 107.8433 | 24.6653 | 23.309 | 23.1852 | 26.3719 | 50 | 47.5129 | 200.3576 | 36.0215 | 36.4334 | 108.9392 | ON | 25.68 | 110.2 | 44.4225 | 30.7816 | -2.371 | 3.0628 | 2.3567 | 2.3567 | 3.4568 |  | OK | OK | OK | OK | 104.7288 | OK | OK | OK | OK | OK
44811.9161 | 3:35 | 95 | 130.5333 | 128.1067 | 141.2964 | 69.3773 | 107.9309 | 107.9309 | 24.5532 | 23.1653 | 23.0759 | 26.0775 | 50 | 47.267 | 200.2971 | 35.9167 | 36.3862 | 109.026 | ON | 25.68 | 110.2 | 43.6973 | 31.0964 | -2.5147 | 2.9122 | 2.2691 | 2.2691 | 3.4695 |  | OK | OK | OK | OK | 104.8533 | OK | OK | OK | OK | OK
44811.9162 | 3:35 | 95 | 130.8693 | 128.3631 | 141.6148 | 70.4712 | 108.0002 | 108.0002 | 24.3695 | 23.0271 | 22.9801 | 25.8351 | 50 | 47.1521 | 200.1403 | 35.8906 | 36.301 | 109.0687 | ON | 25.68 | 110.2 | 44.7912 | 31.4148 | -2.6529 | 2.808 | 2.1998 | 2.1998 | 3.4735 |  | OK | OK | OK | OK | 105.1893 | OK | OK | OK | OK | OK
44811.9163 | 3:35 | 95 | 131.1591 | 128.5604 | 141.904 | 71.029 | 108.0622 | 108.0622 | 24.2788 | 22.9898 | 22.8523 | 25.5996 | 50 | 47.2083 | 200.532 | 35.7785 | 36.1739 | 109.1179 | ON | 25.68 | 110.2 | 45.349 | 31.704 | -2.6902 | 2.6098 | 2.1378 | 2.1378 | 3.4766 |  | OK | OK | OK | OK | 105.4791 | OK | OK | OK | OK | OK
44811.9164 | 3:36 | 95 | 131.4283 | 128.7362 | 142.1837 | 71.3074 | 108.0695 | 108.0695 | 24.0908 | 22.7491 | 22.6342 | 25.3694 | 50 | 46.6959 | 200.3682 | 35.6532 | 36.0351 | 109.1376 | ON | 24.74 | 110.2 | 46.5674 | 31.9837 | -1.9909 | 2.6203 | 2.1305 | 2.1305 | 3.503 |  | OK | OK | OK | OK | 106.6883 | OK | OK | OK | OK | OK
44811.9166 | 3:36 | 95 | 131.6345 | 128.9673 | 142.4821 | 71.5857 | 108.0556 | 108.0556 | 23.8924 | 22.57 | 22.501 | 25.1709 | 50 | 46.6083 | 200.5841 | 35.6719 | 35.9171 | 109.1198 | ON | 24.74 | 110.2 | 46.8457 | 32.2821 | -2.17 | 2.601 | 2.1444 | 2.1444 | 3.5115 |  | OK | OK | OK | OK | 106.8945 | OK | OK | OK | OK | OK
44811.9167 | 3:36 | 95 | 131.8328 | 129.0857 | 142.6963 | 71.8334 | 107.9278 | 107.9278 | 23.7674 | 22.5334 | 22.5078 | 24.9526 | 50 | 46.7562 | 200.1666 | 35.6473 | 35.8092 | 108.9959 | ON | 24.74 | 110.2 | 47.0934 | 32.4963 | -2.2066 | 2.4192 | 2.2722 | 2.2722 | 3.4963 |  | OK | OK | OK | OK | 107.0928 | OK | OK | OK | OK | OK
44811.9168 | 3:36 | 95 | 132.0001 | 129.2 | 142.8685 | 72.0749 | 107.6729 | 107.6729 | 23.5977 | 22.3135 | 22.2933 | 24.7766 | 50 | 46.1919 | 199.351 | 35.5365 | 35.6512 | 108.765 | ON | 24.74 | 108.3 | 47.3349 | 34.5685 | -2.4265 | 2.4631 | 0.6271 | 0.6271 | 3.5153 |  | OK | Low Charge | OK | OK | 107.2601 | OK | OK | OK | OK | OK
44811.9169 | 3:36 | 95 | 132.1057 | 129.1505 | 143.0346 | 72.3832 | 107.4876 | 107.4876 | 23.3799 | 22.095 | 22.0804 | 24.6162 | 50 | 46.5244 | 199.1045 | 35.4142 | 35.6506 | 108.5888 | ON | 24.74 | 108.3 | 47.6432 | 34.7346 | -2.645 | 2.5212 | 0.8124 | 0.8124 | 3.4921 |  | OK | Low Charge | OK | OK | 107.3657 | OK | OK | OK | OK | OK
44811.917 | 3:36 | 95 | 132.0685 | 129.2404 | 143.2229 | 72.4427 | 107.3439 | 107.3439 | 23.2559 | 21.9934 | 21.8577 | 24.5014 | 50 | 45.8815 | 198.7211 | 35.4434 | 35.5531 | 108.4427 | ON | 23.8 | 108.3 | 48.6427 | 34.9229 | -1.8066 | 2.508 | 0.9561 | 0.9561 | 3.5229 |  | OK | Low Charge | OK | OK | 108.2685 | OK | OK | OK | OK | OK
44811.9171 | 3:37 | 95 | 132.24 | 129.3679 | 143.3928 | 72.343 | 107.2783 | 107.2783 | 23.1132 | 21.9516 | 21.7535 | 24.4323 | 50 | 46.0229 | 198.5871 | 35.306 | 35.4944 | 108.3723 | ON | 24.74 | 108.3 | 47.603 | 35.0928 | -2.7884 | 2.4807 | 1.0217 | 1.0217 | 3.5125 |  | OK | OK | OK | OK | 107.5 | OK | OK | OK | OK | OK
44811.9173 | 3:37 | 95 | 132.3442 | 129.4474 | 143.5804 | 72.4061 | 107.229 | 107.229 | 22.9636 | 21.7221 | 21.6344 | 24.3503 | 50 | 45.9179 | 198.3237 | 35.324 | 35.3129 | 108.309 | ON | 23.8 | 108.3 | 48.6061 | 35.2804 | -2.0779 | 2.6282 | 1.071 | 1.071 | 3.5142 |  | OK | OK | OK | OK | 108.5442 | OK | OK | OK | OK | OK
44811.9174 | 3:37 | 95 | 132.3995 | 129.5499 | 143.7117 | 72.5851 | 107.138 | 107.138 | 22.76 | 21.6146 | 21.5184 | 24.2442 | 50 | 45.612 | 197.8888 | 35.1274 | 35.3277 | 108.2205 | ON | 23.8 | 108.3 | 48.7851 | 35.4117 | -2.1854 | 2.6296 | 1.162 | 1.162 | 3.5248 |  | OK | OK | OK | OK | 108.5995 | OK | OK | OK | OK | OK
44811.9175 | 3:37 | 95 | 132.4702 | 129.6185 | 143.8642 | 72.5803 | 107.0585 | 107.0585 | 22.7035 | 21.5524 | 21.4496 | 24.1521 | 50 | 45.5483 | 197.9172 | 35.1097 | 35.2549 | 108.1523 | ON | 23.8 | 108.3 | 48.7803 | 35.5642 | -2.2476 | 2.5997 | 1.2415 | 1.2415 | 3.529 |  | OK | OK | OK | OK | 108.6702 | OK | OK | OK | OK | OK
44811.9176 | 3:37 | 95 | 132.5518 | 129.7462 | 144.0195 | 72.432 | 107.0777 | 107.0777 | 22.5532 | 21.3916 | 21.3309 | 24.0847 | 50 | 45.4616 | 198.357 | 35.0642 | 35.1998 | 108.1331 | ON | 23.8 | 108.3 | 48.632 | 35.7195 | -2.4084 | 2.6931 | 1.2223 | 1.2223 | 3.5414 |  | OK | OK | OK | OK | 108.7518 | OK | OK | OK | OK | OK
44811.9177 | 3:37 | 95 | 132.7585 | 129.7787 | 144.1763 | 72.4039 | 107.0183 | 107.0183 | 22.4576 | 21.324 | 21.1953 | 24.0068 | 50 | 45.3944 | 197.8163 | 34.9762 | 35.1433 | 108.0846 | ON | 23.8 | 108.3 | 48.6039 | 35.8763 | -2.476 | 2.6827 | 1.2817 | 1.2817 | 3.5364 |  | OK | OK | OK | OK | 108.9585 | OK | OK | OK | OK | OK
44811.9178 | 3:38 | 95 | 132.7967 | 129.8529 | 144.2814 | 72.2244 | 106.9438 | 106.9438 | 22.2931 | 21.1611 | 20.967 | 23.888 | 50 | 45.1933 | 197.6157 | 34.7877 | 35.0922 | 107.9835 | ON | 23.8 | 108.3 | 48.4244 | 35.9814 | -2.6389 | 2.7269 | 1.3562 | 1.3562 | 3.5449 |  | OK | OK | OK | OK | 108.9967 | OK | OK | OK | OK | OK
44811.918 | 3:38 | 95 | 132.9189 | 129.9038 | 144.3984 | 72.1336 | 106.8431 | 106.8431 | 22.2244 | 21.121 | 20.9968 | 23.8391 | 50 | 44.9796 | 197.3816 | 34.7683 | 35.0277 | 107.9125 | ON | 22.84 | 108.3 | 49.2936 | 36.0984 | -1.719 | 2.7181 | 1.4569 | 1.4569 | 3.5537 |  | OK | OK | OK | OK | 110.0789 | OK | OK | OK | OK | OK
44811.9181 | 3:38 | 95 | 133.0427 | 129.9382 | 144.528 | 72.0737 | 106.7847 | 106.7847 | 22.0449 | 20.9229 | 20.8435 | 23.7692 | 50 | 44.929 | 197.4221 | 34.6855 | 34.986 | 107.8493 | ON | 22.84 | 108.3 | 49.2337 | 36.228 | -1.9171 | 2.8464 | 1.5153 | 1.5153 | 3.5574 |  | OK | OK | OK | OK | 110.2027 | OK | OK | OK | OK | OK
44811.9182 | 3:38 | 95 | 133.5934 | 130.2062 | 144.6402 | 72.1733 | 108.3559 | 108.3559 | 21.9857 | 20.9157 | 21.0735 | 23.787 | 50 | 44.8694 | 203.6202 | 34.7169 | 34.9118 | 108.9284 | ON | 22.84 | 110.2 | 49.3333 | 34.4402 | -1.9243 | 2.8714 | 1.8441 | 1.8441 | 3.665 |  | OK | OK | OK | OK | 110.7534 | OK | OK | OK | OK | OK
44811.9183 | 3:38 | 95 | 133.8381 | 130.4641 | 144.872 | 71.3247 | 108.9887 | 108.9887 | 21.683 | 19.8156 | 21.7031 | 24.0299 | 50 | 43.0845 | 204.7737 | 34.7192 | 34.771 | 109.4422 | ON | 21.87 | 110.2 | 49.4547 | 34.672 | -2.0544 | 4.2143 | 1.2113 | 1.2113 | 3.7981 |  | OK | OK | OK | OK | 111.9681 | OK | OK | OK | OK | OK
44811.9184 | 3:38 | 95 | 133.8228 | 130.5473 | 144.9656 | 68.2578 | 108.9387 | 108.9387 | 21.2819 | 19.2607 | 22.943 | 24.7829 | 50 | 42.8109 | 204.1583 | 34.3509 | 34.873 | 109.3856 | ON | 20.88 | 110.2 | 47.3778 | 34.7656 | -1.6193 | 5.5222 | 1.2613 | 1.2613 | 3.8055 |  | OK | OK | OK | OK | 112.9428 | OK | OK | OK | OK | OK
44811.9185 | 3:39 | 95 | 133.7241 | 130.5528 | 144.8214 | 60.0374 | 108.9256 | 108.9256 | 20.8862 | 18.8384 | 24.2739 | 25.7684 | 50 | 42.3421 | 204.0291 | 34.3316 | 35.0291 | 109.4015 | ON | 20.88 | 110.2 | 39.1574 | 34.6214 | -2.0416 | 6.93 | 1.2744 | 1.2744 | 3.8345 |  | OK | OK | OK | OK | 112.8441 | OK | OK | OK | OK | OK
44811.9186 | 3:39 | 95 | 133.2634 | 130.2059 | 144.3704 | 52.5823 | 108.7728 | 108.7728 | 20.6316 | 18.5179 | 25.5956 | 26.7404 | 50 | 41.94 | 203.6559 | 34.2588 | 35.1882 | 109.2609 | ON | 19.89 | 110.2 | 32.6923 | 34.1704 | -1.3721 | 8.2225 | 1.4272 | 1.4272 | 3.8552 |  | OK | OK | OK | OK | 113.3734 | OK | OK | OK | OK | OK
44811.9188 | 3:39 | 95 | 132.5677 | 129.6304 | 143.7363 | 48.5406 | 108.6892 | 108.6892 | 20.3591 | 18.1521 | 26.7964 | 27.657 | 50 | 41.5493 | 203.5392 | 34.16 | 35.2247 | 109.2036 | ON | 19.89 | 110.2 | 28.6506 | 33.5363 | -1.7379 | 9.5049 | 1.5108 | 1.5108 | 3.8799 |  | OK | OK | OK | OK | 112.6777 | OK | OK | OK | OK | OK
44811.9189 | 3:39 | 95 | 131.6821 | 129.0426 | 142.9352 | 46.8115 | 108.5062 | 108.5062 | 20.0995 | 17.9335 | 27.8505 | 28.4388 | 50 | 41.3736 | 203.0489 | 34.0543 | 35.3644 | 109.0478 | ON | 19.89 | 110.2 | 26.9215 | 32.7352 | -1.9565 | 10.5053 | 1.6938 | 1.6938 | 3.8833 |  | OK | OK | OK | OK | 111.7921 | OK | OK | OK | OK | OK
44811.919 | 3:39 | 95 | 130.8976 | 128.369 | 142.1431 | 45.406 | 108.3902 | 108.3902 | 19.8345 | 17.6729 | 28.7393 | 29.1239 | 50 | 41.0707 | 202.7087 | 34.0377 | 35.3404 | 108.9324 | ON | 19.89 | 110.2 | 25.516 | 31.9431 | -2.2171 | 11.451 | 1.8098 | 1.8098 | 3.8983 |  | OK | OK | OK | OK | 111.0076 | OK | OK | OK | OK | OK
44811.9191 | 3:39 | 95 | 129.9942 | 127.7012 | 141.3459 | 43.5398 | 108.1872 | 108.1872 | 19.6283 | 17.4232 | 29.3232 | 29.6441 | 50 | 40.9007 | 201.95 | 34.0044 | 35.3594 | 108.7583 | ON | 18.88 | 110.2 | 24.6598 | 31.1459 | -1.4568 | 12.2209 | 2.0128 | 2.0128 | 3.8965 |  | OK | OK | OK | OK | 111.1142 | OK | OK | OK | OK | OK
44811.9192 | 3:40 | 95 | 129.238 | 127.0899 | 140.5969 | 42.5287 | 108.0228 | 108.0228 | 19.401 | 17.2498 | 29.8003 | 30.1131 | 50 | 40.8143 | 201.2559 | 33.9344 | 35.3788 | 108.583 | ON | 18.88 | 110.2 | 23.6487 | 30.3969 | -1.6302 | 12.8633 | 2.1772 | 2.1772 | 3.8901 |  | OK | OK | OK | OK | 110.358 | OK | OK | OK | OK | OK
44811.9193 | 3:40 | 95 | 128.5474 | 126.4778 | 139.8379 | 41.8585 | 107.8429 | 107.8429 | 19.1731 | 17.028 | 30.1464 | 30.4401 | 50 | 40.5505 | 201.0086 | 33.95 | 35.3755 | 108.3918 | ON | 18.88 | 110.2 | 22.9785 | 29.6379 | -1.852 | 13.4122 | 2.3571 | 2.3571 | 3.9042 |  | OK | OK | OK | OK | 109.6674 | OK | OK | OK | OK | OK
44811.9195 | 3:40 | 95 | 127.9334 | 125.9869 | 139.1244 | 41.019 | 107.6259 | 107.6259 | 18.9558 | 16.8069 | 30.4203 | 30.7326 | 50 | 40.3118 | 200.5592 | 33.7505 | 35.3862 | 108.2238 | ON | 18.88 | 110.2 | 22.139 | 28.9244 | -2.0731 | 13.9257 | 2.5741 | 2.5741 | 3.913 |  | OK | OK | OK | OK | 109.0534 | OK | OK | OK | OK | OK
44811.9196 | 3:40 | 95 | 127.3456 | 125.4442 | 138.4613 | 40.2151 | 107.3723 | 107.3723 | 18.7238 | 16.5689 | 30.6597 | 30.9579 | 50 | 40.1349 | 199.751 | 33.8356 | 35.3004 | 108.0019 | ON | 18.88 | 108.3 | 21.3351 | 30.1613 | -2.3111 | 14.389 | 0.9277 | 0.9277 | 3.9109 |  | OK | Low Charge | OK | OK | 108.4656 | OK | OK | OK | OK | OK
44811.9197 | 3:40 | 95 | 126.834 | 124.9969 | 137.8281 | 39.4536 | 107.2062 | 107.2062 | 18.5194 | 16.3585 | 30.835 | 31.1569 | 50 | 39.845 | 199.3357 | 33.5874 | 35.3714 | 107.8453 | ON | 17.86 | 108.3 | 21.5936 | 29.5281 | -1.5015 | 14.7985 | 1.0938 | 1.0938 | 3.924 |  | OK | OK | OK | OK | 108.974 | OK | OK | OK | OK | OK
44811.9198 | 3:40 | 95 | 126.4264 | 124.5385 | 137.2934 | 38.8349 | 107.027 | 107.027 | 18.3213 | 16.1573 | 30.9669 | 31.3034 | 50 | 39.6241 | 198.9627 | 33.5756 | 35.3625 | 107.6785 | ON | 17.86 | 108.3 | 20.9749 | 28.9934 | -1.7027 | 15.1461 | 1.273 | 1.273 | 3.9331 |  | OK | OK | OK | OK | 108.5664 | OK | OK | OK | OK | OK
44811.9199 | 3:41 | 95 | 126.2052 | 124.3738 | 136.6872 | 37.7844 | 107.3212 | 107.3212 | 18.1764 | 15.9725 | 31.0458 | 31.4169 | 50 | 39.2002 | 198.8438 | 33.5662 | 35.3466 | 107.8943 | ON | 17.86 | 108.3 | 19.9244 | 28.3872 | -1.8875 | 15.4444 | 0.9788 | 0.9788 | 3.9618 |  | OK | Low Charge | OK | OK | 108.3452 | OK | OK | OK | OK | OK
44811.92 | 3:41 | 95 | 126.1433 | 124.4425 | 136.239 | 37.0057 | 107.6835 | 107.6835 | 17.9859 | 15.8869 | 31.1298 | 31.5136 | 50 | 39.2008 | 200.0531 | 33.3448 | 35.3273 | 108.1887 | ON | 17.86 | 110.2 | 19.1457 | 26.039 | -1.9731 | 15.6267 | 2.5165 | 2.5165 | 3.9842 |  | OK | OK | OK | OK | 108.2833 | OK | OK | OK | OK | OK
44811.9202 | 3:41 | 95 | 125.9803 | 124.2612 | 135.9917 | 36.7261 | 107.715 | 107.715 | 17.8083 | 15.6976 | 31.1945 | 31.5827 | 50 | 39.1082 | 199.8941 | 33.4349 | 35.2916 | 108.217 | ON | 17.86 | 108.3 | 18.8661 | 27.6917 | -2.1624 | 15.8851 | 0.585 | 0.585 | 3.9881 |  | OK | Low Charge | OK | OK | 108.1203 | OK | OK | OK | OK | OK
44811.9203 | 3:41 | 95 | 126.2838 | 124.358 | 136.074 | 36.584 | 108.821 | 108.821 | 17.0671 | 15.1518 | 31.2262 | 31.6142 | 50 | 37.8327 | 208.6995 | 33.3121 | 35.2927 | 109.3111 | ON | 15.76 | 112 | 20.824 | 24.074 | -0.60818 | 16.4624 | 3.179 | 3.179 | 4.2526 |  | OK | OK | OK | OK | 110.5238 | OK | OK | OK | OK | OK
44811.9204 | 3:41 | 95 | 126.6782 | 125.1539 | 135.9531 | 38.4042 | 109.628 | 109.628 | 15.4084 | 15.4828 | 31.2373 | 31.5503 | 50 | 18.7014 | 205.9343 | 33.0025 | 35.2042 | 109.7421 | ON | -7.99 | 112 | 46.3942 | 23.9531 | 23.4728 | 16.0675 | 2.372 | 2.372 | 6.6055 |  | OK | OK | OK | OK | 134.6682 | OK | OK | OK | OK | OK
44811.9205 | 3:41 | 95 | 126.5778 | 124.8157 | 134.4021 | 43.0016 | 106.8941 | 106.8941 | 17.3058 | 17.6242 | 31.2634 | 31.5646 | 50 | 18.2471 | 200.5412 | 33.3484 | 35.3857 | 108.0274 | ON | -7.99 | 110.2 | 50.9916 | 24.2021 | 25.6142 | 13.9404 | 3.3059 | 3.3059 | 6.5329 |  | OK | OK | OK | OK | 134.5678 | OK | OK | OK | OK | OK
44811.9206 | 3:42 | 95 | 126.7132 | 124.5154 | 133.4282 | 46.8263 | 105.081 | 105.081 | 19.6298 | 19.6081 | 31.2891 | 31.6083 | 50 | 16.7246 | 197.2855 | 34.0232 | 35.6125 | 107.0164 | ON | -11.06 | 108.3 | 57.8863 | 25.1282 | 30.6681 | 12.0002 | 3.219 | 3.219 | 6.7458 |  | OK | OK | OK | OK | 137.7732 | OK | OK | OK | OK | OK
44811.9207 | 3:42 | 95 | 127.1299 | 124.329 | 132.9601 | 47.9616 | 104.335 | 104.335 | 21.8727 | 21.3935 | 31.3145 | 31.6777 | 50 | 15.823 | 194.7858 | 34.4278 | 35.7153 | 106.307 | ON | -12.65 | 106.4 | 60.6116 | 26.5601 | 34.0435 | 10.2842 | 2.065 | 2.065 | 6.8632 |  | OK | OK | OK | OK | 139.7799 | OK | OK | OK | OK | OK
44811.9208 | 3:42 | 95 | 127.7279 | 124.469 | 132.816 | 48.5746 | 103.9449 | 103.9449 | 23.9527 | 22.9705 | 31.3601 | 31.7757 | 50 | 15.0258 | 193.9658 | 34.7866 | 35.8298 | 105.9143 | ON | -12.65 | 106.4 | 61.2246 | 26.416 | 35.6205 | 8.8052 | 2.4551 | 2.4551 | 7.0197 |  | OK | OK | OK | OK | 140.3779 | OK | OK | OK | OK | OK
44811.921 | 3:42 | 95 | 128.6048 | 124.6838 | 132.9895 | 52.1849 | 103.7412 | 103.7412 | 25.6972 | 24.299 | 31.3683 | 31.8961 | 50 | 14.3512 | 193.921 | 34.9838 | 35.9302 | 105.8072 | ON | -14.28 | 106.4 | 66.4649 | 26.5895 | 38.579 | 7.5972 | 2.6588 | 2.6588 | 7.1811 |  | OK | OK | OK | OK | 142.8848 | OK | OK | OK | OK | OK
44811.9211 | 3:42 | 95 | 129.6022 | 124.9985 | 133.3109 | 56.0013 | 103.5733 | 103.5733 | 27.1398 | 25.4528 | 31.4378 | 32.0239 | 50 | 13.9568 | 193.4512 | 35.1795 | 36.0964 | 105.6823 | ON | -15.96 | 106.4 | 71.9613 | 26.9109 | 41.4128 | 6.5711 | 2.8267 | 2.8267 | 7.2636 |  | OK | OK | OK | OK | 145.5622 | OK | OK | OK | OK | OK
44811.9212 | 3:42 | 95 | 130.5167 | 125.2804 | 133.6398 | 58.3413 | 103.4363 | 103.4363 | 28.3031 | 26.4206 | 31.4526 | 32.1835 | 50 | 13.4998 | 192.9378 | 35.4294 | 36.1815 | 105.5515 | ON | -15.96 | 106.4 | 74.3013 | 27.2398 | 42.3806 | 5.7629 | 2.9637 | 2.9637 | 7.3631 |  | OK | OK | OK | OK | 146.4767 | OK | OK | OK | OK | OK
44811.9213 | 3:43 | 95 | 131.3284 | 125.6447 | 134.0566 | 59.4164 | 103.3663 | 103.3663 | 29.1728 | 27.2191 | 31.4803 | 32.3347 | 50 | 13.2401 | 192.7155 | 35.5219 | 36.1803 | 105.386 | ON | -15.96 | 106.4 | 75.3764 | 27.6566 | 43.1791 | 5.1155 | 3.0337 | 3.0337 | 7.4236 |  | OK | OK | OK | OK | 147.2884 | OK | OK | OK | OK | OK
44811.9214 | 3:43 | 95 | 132.0371 | 126.0764 | 134.5396 | 60.0485 | 103.0527 | 103.0527 | 29.8587 | 27.8284 | 31.5161 | 32.4875 | 50 | 12.964 | 192.6524 | 35.7029 | 36.3729 | 105.3901 | ON | -17.69 | 106.4 | 77.7385 | 28.1396 | 45.5184 | 4.6591 | 3.3473 | 3.3473 | 7.4954 |  | OK | OK | OK | OK | 149.7271 | OK | OK | OK | OK | OK
44811.9215 | 3:43 | 95 | 132.7968 | 126.5308 | 135.0056 | 60.4595 | 103.0775 | 103.0775 | 30.32 | 28.3254 | 31.531 | 32.636 | 50 | 12.7366 | 192.3748 | 35.783 | 36.479 | 105.3096 | ON | -17.69 | 106.4 | 78.1495 | 28.6056 | 46.0154 | 4.3105 | 3.3225 | 3.3225 | 7.5474 |  | OK | OK | OK | OK | 150.4868 | OK | OK | OK | OK | OK
44811.9217 | 3:43 | 95 | 133.5549 | 126.9781 | 135.5153 | 60.5521 | 103.0768 | 103.0768 | 30.6699 | 28.7762 | 31.5615 | 32.7893 | 50 | 12.3687 | 192.3914 | 35.9587 | 36.4741 | 105.3027 | ON | -17.69 | 106.4 | 78.2421 | 29.1153 | 46.4662 | 4.013 | 3.3232 | 3.3232 | 7.6506 |  | OK | OK | OK | OK | 151.2449 | OK | OK | OK | OK | OK
44811.9218 | 3:43 | 95 | 134.2379 | 127.4521 | 136.0404 | 60.8482 | 103.077 | 103.077 | 30.9462 | 29.0887 | 31.5912 | 32.9228 | 50 | 12.2916 | 192.4136 | 36.0436 | 36.6546 | 105.3309 | ON | -17.69 | 106.4 | 78.5382 | 29.6404 | 46.7787 | 3.8341 | 3.323 | 3.323 | 7.6733 |  | OK | OK | OK | OK | 151.9279 | OK | OK | OK | OK | OK
44811.9219 | 3:43 | 95 | 134.8308 | 127.9067 | 136.4252 | 61.0298 | 103.1258 | 103.1258 | 31.1219 | 29.3748 | 31.6029 | 33.0812 | 50 | 12.5868 | 192.4642 | 36.1629 | 36.6506 | 105.3431 | ON | -17.69 | 106.4 | 78.7198 | 30.0252 | 47.0648 | 3.7065 | 3.2742 | 3.2742 | 7.5921 |  | OK | OK | OK | OK | 152.5208 | OK | OK | OK | OK | OK
44811.922 | 3:44 | 95 | 135.2976 | 128.1171 | 136.7059 | 60.8584 | 102.9359 | 102.9359 | 31.2587 | 29.5931 | 31.6247 | 33.2482 | 50 | 13.6855 | 191.8542 | 36.1241 | 36.7731 | 105.3071 | ON | -15.96 | 106.4 | 76.8184 | 30.3059 | 45.5531 | 3.655 | 3.4641 | 3.4641 | 7.2768 |  | OK | OK | OK | OK | 151.2576 | OK | OK | OK | OK | OK
44811.9221 | 3:44 | 95 | 135.4352 | 128.249 | 136.8451 | 59.9622 | 103.1475 | 103.1475 | 31.3416 | 29.7935 | 31.1285 | 33.4199 | 50 | 14.6432 | 191.2576 | 36.3669 | 36.8371 | 105.1329 | ON | -14.28 | 106.4 | 74.2421 | 30.4451 | 44.0735 | 3.6265 | 3.2525 | 3.2525 | 7.0189 |  | OK | OK | OK | OK | 149.7152 | OK | OK | OK | OK | OK
44811.9222 | 3:44 | 95 | 139.8162 | 126.2113 | 133.8112 | 65.6112 | 94.3747 | 94.3747 | 27.7944 | 30.5049 | 28.8229 | 33.7593 | 50 | 54.517 | 127.2771 | 36.2534 | 36.8354 | 101.5336 | OFF | 31.92 | 77.84 | 33.6912 | 55.9712 | -1.4151 | 3.2544 | -16.5347 | -16.5347 | 2.0512
Overall |  | minimum | 117.7377 | 93.4197 | 100.738 | 36.584 | 84.6366 | 84.6366 | 15.4084 | 15.0487 | 20.8435 | 23.7692 | 50 | 12.2916 | 61.9477 | 33.0025 | 34.771 | 95.1008 |  | -17.69 | 37.71 | 18.8661 | 22.7414 | -3.8502 | -5.6657 | -55.1836 | -55.1836 | 0.98558
|  | maximum | 141.9567 | 135.4116 | 145.2981 | 100.1101 | 109.628 | 109.628 | 34.8087 | 38.3647 | 38.2437 | 38.7905 | 50 | 66.8106 | 209.4519 | 38.7394 | 38.8736 | 109.7513 | #REF! | 41.6 | 112 | 81.2254 | 67.085 | 47.0983 | 16.4788 | 4.1757 | 4.1757 | 7.6969
|  | average | 128.9564 | 125.0165 | 130.5757 | 69.1987 | 102.7696 | 102.7696 | 26.4438 | 26.6603 | 28.1532 | 30.094 | 50 | 45.7542 | 166.5073 | 36.0325 | 36.6122 | 104.9811 | #REF! | 22.312 | 92.6134 | 46.8867 | 37.9623 | 4.3483 | 3.4338 | -10.1562 | -10.1562 | 3.4649
3 | average | 95 | 128.5954 | 126.3097 | 138.7206 | 71.4935 | 107.1857 | 107.1857 | 26.2979 | 24.6595 | 24.0008 | 25.4859 | 50 | 48.4725 | 198.4104 | 36.6466 | 36.7286 | 108.343 | #REF! | 26.4686 | 108.3 | 45.025 | 30.4206 | -1.809 | 0.8264 | 1.1143 | 1.1143 | 3.3737
2 | average | 95 | 131.688 | 129.0876 | 142.2476 | 71.7785 | 108.3445 | 108.3445 | 25.2031 | 23.6721 | 23.5414 | 26.504 | 50 | 47.4839 | 201.1396 | 36.1309 | 36.3978 | 109.3688 | #REF! | 25.68 | 110.2 | 46.0985 | 32.0476 | -2.0079 | 2.832 | 1.8555 | 1.8555 | 3.471
1 | average | 95 | 132.5856 | 126.2376 | 135.456 | 63.0354 | 103.9103 | 103.9103 | 29.68 | 27.6252 | 31.5029 | 32.3804 | 50 | 13.2368 | 194.5908 | 35.6966 | 36.3266 | 106.0264 | #REF! | -15.96 | 106.4 | 78.9954 | 29.056 | 43.5851 | 4.7553 | 2.4897 | 2.4897 | 7.492
Overall |  | minimum | 0 | 93.4197 | 100.176 | 34.5923 | 80.7595 | 80.7595 | 13.9815 | [6 empty] | 32.8472 |  |  |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0
|  | maximum | 0 | 135.4116 | 150.3208 | 101.221 | 110.8768 | 110.8768 | 38.4008 | [6 empty] | 46.01 |  |  |  | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0
|  | average | #DIV/0! | 124.672 | 133.245 | 70.7963 | 103.3458 | 103.3458 | 26.3483 | [6 empty] | 36.8788 |  |  |  | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Evaporators
3 |  | average | #DIV/0! | 125.0057 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! |  |  |  | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2 |  | average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! |  |  |  | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1 |  | average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! |  |  |  | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
<<< Do not use averages for these cells >>>

## T2
Pull-down 95F System pressures and Temperatures
Fluke DAQ 6.0.4
Time |  | Ch 101 (F) | Ch 102 (F) | Ch 103 (F) | Ch 104 (F) | Ch 105 (F) | Ch 106 (F) | Ch 107 (F) | Ch 108 (F) | Ch 109 (F) | Ch 110 (F) | Ch 111 (F) | Ch 112 (F) | Ch 113 (F) | Ch 114 (F) | Ch 115 (F) | Ch 116 (F) | Ch 117 (F) | Ch 118 (F) | Ch 119 (F) | Ch 120 (F) | Ch 201 (F) | Ch 202 (F) | Ch 203 (F) | Ch 204 (F) | Ch 205 (F) | Ch 206 (F) | Ch 207 (F) | Ch 208 (F) | Ch 209 (F) | Ch 210 (F) | Ch 211 (F) | Ch 212 (F) | Ch 213 (F) | Ch 214 (F) | Ch 215 (F) | Ch 216 (F) | Ch 217 (F) | Ch 218 (F) | Ch 219 (F) | Ch 220 (F) | Ch 301 (F) | Ch 302 (F) | Ch 304 (F) | Ch 305 (F) | Ch 306 (F) | Ch 307 (F) | Ch 308 (F) | Ch 309 (F) | Ch 310 (F) | Ch 311 (F) | Ch 312 (F) | Ch 313 (F) | Ch 314 (F) | Ch 315 (F) | Ch 316 (F) | Ch 317 (F) | Ch 318 (F) | Ch 320 (F) | Ambient L | Ambient Right | Ambient Left
2022-09-07 18:24 | 0:00 | 92.0048 | 91.9984 | 92.9165 | 93.4336 | 92.2081 | 93.2267 | 92.4357 | 93.2031 | 92.5574 | 93.3379 | 92.8284 | 92.71 | 93.4962 | 93.5928 | 93.6337 | 93.3161 | 93.5052 | 93.542 | 93.4583 | 93.5495 | 91.3694 | 89.1489 | 91.2457 | 92.3625 | 91.873 | 91.9339 | 91.5692 | 92.9196 | 92.6506 | 92.0771 | 91.3371 | 92.942 | 92.4896 | 92.2445 | 91.6888 | 92.6849 | 91.5388 | 92.307 | 91.8711 | 91.4675 | 91.5904 | 91.7908 | 91.4523 | 91.5919 | 91.7046 | 91.5781 | 91.3057 | 91.2261 | 91.942 | 91.5753 | 91.4012 | 91.0655 | 92.006 | 92.2084 | 91.0444 | 90.7012 | 92.1169 | 91.263 | 95.3798 | 95.7558 | 94.8449
2022-09-07 18:24 | 0:00 | 92.0164 | 91.9973 | 92.8848 | 93.41 | 92.215 | 93.214 | 92.4634 | 93.1515 | 92.5428 | 93.3224 | 92.8193 | 92.7166 | 93.493 | 93.5545 | 93.6193 | 93.3161 | 93.4915 | 93.5128 | 93.4536 | 93.5545 | 91.3719 | 89.1572 | 91.2668 | 92.2803 | 91.8822 | 91.8991 | 91.605 | 92.8659 | 92.6616 | 92.063 | 91.3351 | 92.9431 | 92.4918 | 92.261 | 91.6993 | 92.6828 | 91.5346 | 92.3305 | 91.8648 | 91.4773 | 91.6236 | 91.7975 | 91.4758 | 91.5848 | 91.7169 | 91.61 | 91.3324 | 91.2332 | 91.9664 | 91.5694 | 91.3986 | 91.0866 | 92.0397 | 92.2334 | 91.0411 | 90.7035 | 92.0847 | 91.3802 | 95.5008 | 95.8349 | 94.8657
2022-09-07 18:24 | 0:00 | 92.0091 | 91.9728 | 92.8732 | 93.3774 | 92.2053 | 93.197 | 92.4338 | 93.173 | 92.5688 | 93.2856 | 92.806 | 92.6995 | 93.4718 | 93.5537 | 93.5627 | 93.3149 | 93.4517 | 93.4895 | 93.428 | 93.5211 | 91.3506 | 89.183 | 91.2644 | 92.309 | 91.8887 | 91.8825 | 91.6086 | 92.8927 | 92.68 | 92.0452 | 91.3318 | 92.9325 | 92.4813 | 92.2822 | 91.6848 | 92.6602 | 91.545 | 92.306 | 91.8322 | 91.4819 | 91.6443 | 91.7943 | 91.4717 | 91.5821 | 91.7002 | 91.5961 | 91.3425 | 91.2804 | 91.9656 | 91.5722 | 91.3784 | 91.0866 | 92.0392 | 92.2166 | 91.0107 | 90.6996 | 92.1276 | 91.4213 | 95.5066 | 95.9106 | 94.9489
2022-09-07 18:25 | 0:00 | 92.0089 | 91.971 | 92.8543 | 93.395 | 92.2052 | 93.1777 | 92.4548 | 93.1444 | 92.5667 | 93.3114 | 92.8003 | 92.71 | 93.4489 | 93.5255 | 93.5654 | 93.2954 | 93.4494 | 93.4781 | 93.4198 | 93.4815 | 91.3384 | 89.198 | 91.2574 | 92.3034 | 91.9018 | 91.849 | 91.5927 | 92.8931 | 92.6272 | 92.1037 | 91.3215 | 92.9362 | 92.4772 | 92.2093 | 91.7215 | 92.6838 | 91.5551 | 92.315 | 91.8263 | 91.5058 | 91.642 | 91.807 | 91.4911 | 91.5845 | 91.7249 | 91.6188 | 91.3604 | 91.2746 | 91.9765 | 91.6096 | 91.4293 | 91.0908 | 92.0064 | 92.2447 | 91.0271 | 90.7774 | 92.0845 | 91.3727 | 95.4951 | 95.8481 | 94.7955
2022-09-07 18:25 | 0:01 | 92.0098 | 91.9557 | 92.8162 | 93.3135 | 92.2285 | 93.1433 | 92.4494 | 93.1196 | 92.5368 | 93.276 | 92.7989 | 92.6838 | 93.4264 | 93.498 | 93.5263 | 93.2788 | 93.4282 | 93.44 | 93.3973 | 93.494 | 91.3329 | 89.1935 | 91.2699 | 92.3207 | 91.9211 | 91.8379 | 91.5904 | 92.87 | 92.6475 | 92.081 | 91.3447 | 92.9382 | 92.4568 | 92.2151 | 91.7443 | 92.6557 | 91.548 | 92.3373 | 91.8833 | 91.4733 | 91.6436 | 91.8155 | 91.505 | 91.5935 | 91.7129 | 91.6506 | 91.3489 | 91.2758 | 91.9912 | 91.5964 | 91.4028 | 91.0775 | 92.0186 | 92.2388 | 91.0392 | 90.7724 | 92.0803 | 91.4634 | 95.2738 | 95.6205 | 94.7287
2022-09-07 18:25 | 0:01 | 92.0237 | 91.9463 | 92.7916 | 93.2934 | 92.2212 | 93.126 | 92.4391 | 93.1122 | 92.5507 | 93.2988 | 92.7745 | 92.6599 | 93.4188 | 93.4744 | 93.5537 | 93.2685 | 93.4162 | 93.4292 | 93.382 | 93.4819 | 91.3222 | 89.2159 | 91.2855 | 92.287 | 91.9088 | 91.9189 | 91.6236 | 92.8564 | 92.6189 | 92.0696 | 91.3614 | 92.9436 | 92.481 | 92.1797 | 91.741 | 92.643 | 91.559 | 92.2793 | 91.8912 | 91.4838 | 91.6408 | 91.811 | 91.509 | 91.6059 | 91.7264 | 91.6294 | 91.3606 | 91.2734 | 91.9917 | 91.5803 | 91.4111 | 91.0935 | 92.0145 | 92.2551 | 91.0428 | 90.7823 | 92.0699 | 91.4346 | 94.9866 | 95.3787 | 94.4418
2022-09-07 18:25 | 0:01 | 92.0054 | 91.9349 | 92.79 | 93.3249 | 92.2338 | 93.1128 | 92.4438 | 93.09 | 92.5315 | 93.2551 | 92.6759 | 92.6705 | 93.4012 | 93.4845 | 93.5486 | 93.2687 | 93.393 | 93.4093 | 93.3781 | 93.5267 | 91.279 | 89.2314 | 91.2838 | 92.2673 | 91.9305 | 91.8482 | 91.6443 | 92.8708 | 92.6193 | 92.1505 | 91.3602 | 92.9233 | 92.4601 | 92.2243 | 91.7871 | 92.6699 | 91.557 | 92.312 | 91.929 | 91.481 | 91.6396 | 91.8414 | 91.507 | 91.6072 | 91.7309 | 91.67 | 91.3513 | 91.2964 | 92.0214 | 91.623 | 91.4109 | 91.1249 | 92.0179 | 92.2529 | 91.0016 | 90.7505 | 92.057 | 91.3649 | 94.7501 | 95.0961 | 94.2621
2022-09-07 18:25 | 0:01 | 92.0181 | 91.921 | 92.7735 | 93.243 | 92.2357 | 93.1074 | 92.4424 | 93.0752 | 92.5225 | 93.2322 | 92.6439 | 92.6719 | 93.3309 | 93.3789 | 93.4796 | 93.2039 | 93.3259 | 93.398 | 93.3088 | 93.4616 | 91.2499 | 89.2174 | 91.2672 | 92.291 | 91.9312 | 91.8932 | 91.642 | 92.8035 | 92.5386 | 92.067 | 91.3821 | 92.9201 | 92.3784 | 92.2171 | 91.7777 | 92.6497 | 91.5558 | 92.2934 | 91.8876 | 91.447 | 91.6374 | 91.844 | 91.508 | 91.6317 | 91.7772 | 91.6549 | 91.4133 | 91.3238 | 92.0759 | 91.6602 | 91.4268 | 91.1459 | 92.1214 | 92.2767 | 91.093 | 90.8259 | 92.189 | 91.4287 | 94.6667 | 94.9759 | 94.3135
2022-09-07 18:25 | 0:01 | 92.0054 | 91.8991 | 92.7314 | 93.2063 | 92.2215 | 93.0745 | 92.4376 | 93.0799 | 92.5232 | 93.1988 | 92.6258 | 92.6559 | 93.2826 | 93.3151 | 93.4375 | 93.1579 | 93.2561 | 93.3582 | 93.2679 | 93.4354 | 91.2264 | 89.2349 | 91.2833 | 92.0454 | 91.9316 | 91.8101 | 91.6436 | 92.7668 | 92.5054 | 91.9797 | 91.4126 | 92.8798 | 92.3689 | 92.1762 | 91.7439 | 92.6048 | 91.484 | 92.1959 | 91.863 | 91.4024 | 91.645 | 91.8488 | 91.5407 | 91.6453 | 91.7385 | 91.6685 | 91.3811 | 91.3595 | 91.9882 | 91.6085 | 91.3886 | 91.1599 | 91.9815 | 92.2065 | 91.0925 | 90.8037 | 92.0857 | 91.3493 | 94.5568 | 94.877 | 94.184
2022-09-07 18:26 | 0:02 | 91.9741 | 91.8703 | 92.6847 | 93.1872 | 92.2512 | 93.0542 | 92.4343 | 93.0176 | 92.5096 | 93.1836 | 92.5822 | 92.6546 | 93.2541 | 93.2986 | 93.4309 | 93.1154 | 93.2354 | 93.3089 | 93.2604 | 93.4338 | 91.1595 | 89.2339 | 91.2724 | 91.944 | 91.9498 | 91.768 | 91.6408 | 92.755 | 92.4598 | 92.0009 | 91.3865 | 92.8491 | 92.3427 | 92.1388 | 91.7496 | 92.5001 | 91.4786 | 92.171 | 91.8308 | 91.3818 | 91.6446 | 91.8541 | 91.5322 | 91.6653 | 91.7111 | 91.6522 | 91.369 | 91.3723 | 91.9535 | 91.6114 | 91.3923 | 91.1605 | 91.9677 | 92.1657 | 91.0909 | 90.7898 | 92.0292 | 91.282 | 94.525 | 94.8073 | 94.2543
2022-09-07 18:26 | 0:02 | 91.9815 | 91.8557 | 92.6562 | 93.0899 | 92.2482 | 93.0342 | 92.4181 | 93.0243 | 92.51 | 93.1741 | 92.5776 | 92.6438 | 93.2406 | 93.2783 | 93.3871 | 93.1193 | 93.2197 | 93.3078 | 93.2203 | 93.3857 | 91.0449 | 89.2521 | 91.2487 | 91.9373 | 91.94 | 91.7334 | 91.6396 | 92.7138 | 92.4022 | 92.0228 | 91.4315 | 92.8674 | 92.3148 | 92.1344 | 91.7425 | 92.4705 | 91.4342 | 92.1386 | 91.8272 | 91.3653 | 91.6389 | 91.8615 | 91.5452 | 91.6991 | 91.7055 | 91.6623 | 91.3699 | 91.3742 | 91.9558 | 91.595 | 91.3715 | 91.161 | 91.9399 | 92.1517 | 91.0903 | 90.7958 | 92.0435 | 91.2786 | 94.4215 | 94.7807 | 94.1878
2022-09-07 18:26 | 0:02 | 91.9564 | 91.8429 | 92.5893 | 93.122 | 92.2409 | 93.02 | 92.4103 | 92.9781 | 92.513 | 93.165 | 92.5739 | 92.6485 | 93.209 | 93.2682 | 93.3875 | 93.0928 | 93.2036 | 93.2713 | 93.2203 | 93.3794 | 90.9209 | 89.2606 | 91.2193 | 91.9079 | 91.944 | 91.7228 | 91.6374 | 92.7137 | 92.3634 | 91.9919 | 91.4276 | 92.8437 | 92.2933 | 92.1468 | 91.7435 | 92.4677 | 91.4301 | 92.151 | 91.8143 | 91.3535 | 91.6286 | 91.8603 | 91.5717 | 91.7328 | 91.7146 | 91.6781 | 91.3949 | 91.3898 | 91.9403 | 91.5724 | 91.3879 | 91.1658 | 91.9137 | 92.1591 | 91.0899 | 90.761 | 92.0124 | 91.2423 | 94.4307 | 94.7323 | 94.187
2022-09-07 18:26 | 0:02 | 91.9431 | 91.8446 | 92.5645 | 93.0811 | 92.2506 | 93.0105 | 92.4001 | 92.9982 | 92.5086 | 93.1325 | 92.5591 | 92.645 | 93.1877 | 93.2151 | 93.338 | 93.0785 | 93.1649 | 93.2601 | 93.1815 | 93.3598 | 90.8483 | 89.2486 | 91.1986 | 91.8698 | 91.9522 | 91.7036 | 91.645 | 92.665 | 92.379 | 91.9909 | 91.4217 | 92.8206 | 92.2887 | 92.1329 | 91.7238 | 92.4863 | 91.4108 | 92.1323 | 91.7901 | 91.33 | 91.6422 | 91.8673 | 91.5573 | 91.7393 | 91.7038 | 91.6647 | 91.3916 | 91.3917 | 91.948 | 91.6087 | 91.3625 | 91.1676 | 91.927 | 92.1639 | 91.0836 | 90.7775 | 91.9992 | 91.2546 | 94.4268 | 94.6899 | 94.1689
2022-09-07 18:26 | 0:02 | 91.9557 | 91.8163 | 92.542 | 93.0878 | 92.2433 | 92.9885 | 92.4131 | 92.9423 | 92.5029 | 93.1258 | 92.519 | 92.6258 | 93.1895 | 93.2201 | 93.3717 | 93.0615 | 93.1372 | 93.216 | 93.1813 | 93.3537 | 90.8022 | 89.2651 | 91.1955 | 91.8735 | 91.972 | 91.7175 | 91.6446 | 92.6728 | 92.3511 | 91.9929 | 91.4241 | 92.8223 | 92.2836 | 92.1502 | 91.7081 | 92.4488 | 91.4163 | 92.1278 | 91.7729 | 91.3454 | 91.6437 | 91.8525 | 91.5804 | 91.7596 | 91.7169 | 91.6787 | 91.4031 | 91.4077 | 91.9851 | 91.593 | 91.4041 | 91.1653 | 91.9309 | 92.1425 | 91.0914 | 90.7908 | 92.013 | 91.2603 | 94.3662 | 94.6166 | 94.067
2022-09-07 18:26 | 0:02 | 91.929 | 91.7961 | 92.5269 | 93.0479 | 92.2473 | 92.9674 | 92.3878 | 92.9394 | 92.4906 | 93.1177 | 92.5404 | 92.613 | 93.188 | 93.165 | 93.3399 | 93.0374 | 93.1564 | 93.2151 | 93.1525 | 93.3342 | 90.7402 | 89.2816 | 91.1756 | 91.8211 | 91.9507 | 91.703 | 91.6389 | 92.618 | 92.3634 | 91.9567 | 91.4187 | 92.8238 | 92.2541 | 92.1518 | 91.7525 | 92.4699 | 91.3806 | 92.1519 | 91.7682 | 91.3175 | 91.6334 | 91.8483 | 91.585 | 91.7741 | 91.6817 | 91.6752 | 91.4234 | 91.3795 | 91.9589 | 91.5956 | 91.3562 | 91.1722 | 91.9285 | 92.1543 | 91.1254 | 90.7813 | 92.0226 | 91.2506 | 94.3258 | 94.5962 | 94.0795
2022-09-07 18:27 | 0:02 | 91.9087 | 91.798 | 92.4905 | 93.0789 | 92.2484 | 92.9344 | 92.3763 | 92.9404 | 92.4933 | 93.1074 | 92.5046 | 92.6208 | 93.1528 | 93.1777 | 93.3594 | 92.9919 | 93.1193 | 93.2018 | 93.1451 | 93.3456 | 90.72 | 89.2799 | 91.1583 | 91.8029 | 91.9647 | 91.7129 | 91.6286 | 92.6201 | 92.3839 | 91.9893 | 91.421 | 92.8118 | 92.2547 | 92.1436 | 91.731 | 92.4209 | 91.388 | 92.1024 | 91.7826 | 91.3041 | 91.636 | 91.854 | 91.5911 | 91.7949 | 91.7017 | 91.6955 | 91.4326 | 91.4128 | 91.9441 | 91.5896 | 91.3826 | 91.1705 | 91.9233 | 92.141 | 91.1266 | 90.8037 | 91.9881 | 91.2387 | 94.2076 | 94.5001 | 93.9867
2022-09-07 18:27 | 0:03 | 91.9118 | 91.7948 | 92.503 | 93.0429 | 92.2431 | 92.9304 | 92.3959 | 92.9084 | 92.4943 | 93.1082 | 92.4865 | 92.6188 | 93.1325 | 93.155 | 93.2975 | 92.994 | 93.0984 | 93.1631 | 93.1288 | 93.3195 | 90.6723 | 89.2899 | 91.1559 | 91.8315 | 91.9561 | 91.6842 | 91.6422 | 92.6266 | 92.3717 | 91.9745 | 91.4249 | 92.7924 | 92.2396 | 92.1469 | 91.7375 | 92.3842 | 91.3592 | 92.1486 | 91.7793 | 91.3158 | 91.6288 | 91.8666 | 91.5901 | 91.8074 | 91.7023 | 91.6936 | 91.4312 | 91.4087 | 91.9537 | 91.6073 | 91.377 | 91.1702 | 91.9222 | 92.1564 | 91.1149 | 90.7969 | 92.0095 | 91.2388 | 94.1228 | 94.4311 | 93.968
2022-09-07 18:27 | 0:03 | 91.8959 | 91.7759 | 92.4862 | 93.0027 | 92.2399 | 92.9334 | 92.3791 | 92.8856 | 92.4788 | 93.111 | 92.4807 | 92.6128 | 93.1258 | 93.1024 | 93.299 | 92.9687 | 93.0833 | 93.1549 | 93.1192 | 93.3038 | 90.6596 | 89.2939 | 91.1361 | 91.8263 | 91.9748 | 91.6885 | 91.6437 | 92.6174 | 92.3536 | 91.989 | 91.4243 | 92.7815 | 92.2286 | 92.1284 | 91.7423 | 92.3538 | 91.3572 | 92.0691 | 91.7721 | 91.3144 | 91.6414 | 91.8654 | 91.6068 | 91.815 | 91.6882 | 91.6848 | 91.4282 | 91.4052 | 91.9571 | 91.5856 | 91.3891 | 91.2025 | 91.9266 | 92.1412 | 91.0909 | 90.8211 | 92.0025 | 91.2742 | 94.0437 | 94.3628 | 93.9269
2022-09-07 18:27 | 0:03 | 91.8858 | 91.7852 | 92.4945 | 93.0335 | 92.251 | 92.9346 | 92.4013 | 92.8948 | 92.4984 | 93.1 | 92.4825 | 92.6049 | 93.116 | 93.125 | 93.2996 | 92.9588 | 93.0616 | 93.1449 | 93.115 | 93.3221 | 90.6459 | 89.3288 | 91.146 | 91.771 | 91.9671 | 91.6932 | 91.6334 | 92.6068 | 92.3602 | 91.9612 | 91.4212 | 92.756 | 92.2193 | 92.1322 | 91.7207 | 92.3646 | 91.3356 | 92.1155 | 91.7527 | 91.3018 | 91.6509 | 91.8738 | 91.6108 | 91.8187 | 91.6996 | 91.6912 | 91.4358 | 91.4008 | 91.9522 | 91.6018 | 91.4025 | 91.1929 | 91.8937 | 92.1358 | 91.0999 | 90.7862 | 92.0105 | 91.2438 | 93.9626 | 94.275 | 93.8224
2022-09-07 18:27 | 0:03 | 91.8865 | 91.7671 | 92.4957 | 93.0211 | 92.2367 | 92.9018 | 92.369 | 92.8901 | 92.4715 | 93.0789 | 92.4671 | 92.6128 | 93.106 | 93.101 | 93.262 | 92.9415 | 93.0404 | 93.1503 | 93.1045 | 93.2661 | 90.6054 | 89.3372 | 91.1355 | 91.7798 | 91.9667 | 91.679 | 91.636 | 92.5735 | 92.3493 | 91.9993 | 91.4331 | 92.7714 | 92.1982 | 92.1486 | 91.7331 | 92.3788 | 91.338 | 92.0842 | 91.7777 | 91.2731 | 91.6584 | 91.8712 | 91.62 | 91.8316 | 91.6852 | 91.6964 | 91.4375 | 91.4136 | 91.9451 | 91.5961 | 91.4078 | 91.1927 | 91.9286 | 92.1542 | 91.093 | 90.8163 | 91.9889 | 91.2575 | 93.9398 | 94.2068 | 93.857
2022-09-07 18:27 | 0:03 | 91.8643 | 91.7611 | 92.4837 | 92.9709 | 92.2483 | 92.8847 | 92.3762 | 92.8749 | 92.456 | 93.0757 | 92.4623 | 92.598 | 93.065 | 93.0874 | 93.2528 | 92.9098 | 93.0198 | 93.1453 | 93.0617 | 93.2714 | 90.5717 | 89.3772 | 91.12 | 91.7782 | 91.9462 | 91.692 | 91.6288 | 92.5562 | 92.3604 | 92.0246 | 91.4235 | 92.7302 | 92.2046 | 92.112 | 91.7428 | 92.3622 | 91.3406 | 92.0928 | 91.7801 | 91.2807 | 91.6432 | 91.8745 | 91.6108 | 91.832 | 91.6846 | 91.682 | 91.4421 | 91.4378 | 91.9581 | 91.5868 | 91.403 | 91.2138 | 91.92 | 92.1382 | 91.1047 | 90.8243 | 91.9758 | 91.2516 | 93.9088 | 94.1027 | 93.8406
2022-09-07 18:28 | 0:04 | 91.8901 | 91.7587 | 92.5112 | 93.0039 | 92.2493 | 92.8585 | 92.3628 | 92.8547 | 92.4728 | 93.0638 | 92.45 | 92.5719 | 93.0755 | 93.0766 | 93.23 | 92.929 | 93.036 | 93.0944 | 93.0465 | 93.2404 | 90.5623 | 89.4127 | 91.129 | 91.8128 | 91.9644 | 91.6856 | 91.6414 | 92.5375 | 92.3236 | 91.9938 | 91.4113 | 92.734 | 92.2035 | 92.1332 | 91.7433 | 92.3785 | 91.3202 | 92.0692 | 91.7496 | 91.2726 | 91.6391 | 91.8739 | 91.6241 | 91.8366 | 91.6905 | 91.6904 | 91.4586 | 91.4199 | 91.9514 | 91.5809 | 91.4038 | 91.2073 | 91.9081 | 92.1191 | 91.1061 | 90.8271 | 92.0015 | 91.2912 | 93.7723 | 94.0565 | 93.6959
2022-09-07 18:28 | 0:04 | 91.8638 | 91.7551 | 92.5102 | 93 | 92.2353 | 92.8779 | 92.3804 | 92.8318 | 92.4536 | 93.047 | 92.4385 | 92.5839 | 93.0393 | 93.0252 | 93.2294 | 92.9012 | 93.012 | 93.0678 | 93.0467 | 93.2169 | 90.5327 | 89.4127 | 91.1084 | 91.7626 | 91.9587 | 91.6726 | 91.6509 | 92.539 | 92.293 | 91.9712 | 91.4249 | 92.7223 | 92.182 | 92.1241 | 91.7273 | 92.3495 | 91.3168 | 92.0648 | 91.7565 | 91.2823 | 91.6459 | 91.8895 | 91.6129 | 91.8552 | 91.6764 | 91.7124 | 91.4513 | 91.409 | 91.9584 | 91.5756 | 91.3868 | 91.1853 | 91.9283 | 92.1443 | 91.1414 | 90.8435 | 91.9936 | 91.2878 | 93.6608 | 93.882 | 93.7069
2022-09-07 18:28 | 0:04 | 91.8649 | 91.7608 | 92.5128 | 92.9835 | 92.2422 | 92.88 | 92.3726 | 92.8031 | 92.4625 | 93.0366 | 92.4111 | 92.5845 | 93.0418 | 93.0347 | 93.199 | 92.8713 | 92.9826 | 93.07 | 93.0155 | 93.2292 | 90.5049 | 89.434 | 91.129 | 91.7344 | 91.9569 | 91.6629 | 91.6584 | 92.5261 | 92.3027 | 91.9974 | 91.4131 | 92.7022 | 92.1615 | 92.1289 | 91.7337 | 92.3406 | 91.3017 | 92.0649 | 91.751 | 91.2804 | 91.6406 | 91.8827 | 91.6313 | 91.8703 | 91.6869 | 91.7187 | 91.4456 | 91.3997 | 91.9673 | 91.5854 | 91.4146 | 91.1991 | 91.9179 | 92.1363 | 91.1214 | 90.8594 | 92.0052 | 91.309 | 93.5355 | 93.7805 | 93.536
2022-09-07 18:28 | 0:04 | 91.8663 | 91.7816 | 92.5278 | 92.8998 | 92.2488 | 92.8576 | 92.3664 | 92.7983 | 92.4377 | 93.0331 | 92.4168 | 92.5699 | 93.0077 | 93.0331 | 93.1831 | 92.8417 | 92.9535 | 93.0378 | 93.0253 | 93.2369 | 90.5017 | 89.4487 | 91.111 | 91.8024 | 91.9633 | 91.6819 | 91.6432 | 92.5045 | 92.2641 | 91.9864 | 91.4332 | 92.6863 | 92.1453 | 92.1222 | 91.7129 | 92.3541 | 91.3183 | 92.0726 | 91.7483 | 91.2681 | 91.644 | 91.8729 | 91.6367 | 91.8623 | 91.6801 | 91.7156 | 91.4674 | 91.4453 | 91.9777 | 91.5772 | 91.4003 | 91.2191 | 91.9084 | 92.1226 | 91.1349 | 90.8497 | 92.016 | 91.3112 | 93.5361 | 93.697 | 93.5768
2022-09-07 18:28 | 0:04 | 91.8661 | 91.7724 | 92.541 | 92.9333 | 92.2553 | 92.8404 | 92.3653 | 92.8278 | 92.4502 | 93.0151 | 92.412 | 92.5702 | 92.9975 | 93.0143 | 93.1895 | 92.8309 | 92.9564 | 93.0491 | 93.0244 | 93.2151 | 90.4624 | 89.4794 | 91.1171 | 91.7703 | 91.9605 | 91.6653 | 91.6391 | 92.4907 | 92.3037 | 91.9426 | 91.4247 | 92.6684 | 92.1476 | 92.11 | 91.7342 | 92.3396 | 91.305 | 92.0828 | 91.7097 | 91.2698 | 91.6512 | 91.8737 | 91.6478 | 91.8853 | 91.6843 | 91.7172 | 91.4573 | 91.4371 | 91.9738 | 91.5828 | 91.4117 | 91.2148 | 91.9231 | 92.1256 | 91.128 | 90.8509 | 91.9885 | 91.2832 | 93.5137 | 93.5741 | 93.5852
2022-09-07 18:28 | 0:04 | 91.8601 | 91.7731 | 92.5317 | 92.9703 | 92.2538 | 92.8203 | 92.3675 | 92.8024 | 92.433 | 93.0114 | 92.421 | 92.5524 | 92.9998 | 93.0291 | 93.1906 | 92.802 | 92.9278 | 93.0481 | 92.9959 | 93.1881 | 90.4569 | 89.521 | 91.1114 | 91.7556 | 91.9665 | 91.6478 | 91.6459 | 92.4863 | 92.2425 | 91.9622 | 91.43 | 92.6506 | 92.1306 | 92.1053 | 91.7306 | 92.3269 | 91.2996 | 92.0672 | 91.719 | 91.2544 | 91.639 | 91.8818 | 91.6432 | 91.8732 | 91.679 | 91.7197 | 91.4727 | 91.4683 | 91.9889 | 91.5907 | 91.4157 | 91.2159 | 91.909 | 92.1339 | 91.1285 | 90.8357 | 91.991 | 91.3053 | 93.4678 | 93.4453 | 93.5629
2022-09-07 18:29 | 0:04 | 91.8514 | 91.7889 | 92.5323 | 92.9334 | 92.2242 | 92.8187 | 92.3504 | 92.7605 | 92.4427 | 93.0067 | 92.4021 | 92.5667 | 92.9807 | 92.9946 | 93.1623 | 92.8346 | 92.9361 | 93.0355 | 92.989 | 93.2256 | 90.4451 | 89.5342 | 91.1049 | 91.7298 | 91.9549 | 91.6686 | 91.6406 | 92.4656 | 92.2045 | 91.9843 | 91.423 | 92.6503 | 92.1322 | 92.0849 | 91.7119 | 92.2574 | 91.27 | 92.0889 | 91.7237 | 91.2436 | 91.6352 | 91.8807 | 91.6606 | 91.8711 | 91.6763 | 91.7033 | 91.4729 | 91.4423 | 91.9806 | 91.5911 | 91.4057 | 91.2373 | 91.9186 | 92.1247 | 91.1366 | 90.8768 | 91.9858 | 91.3053 | 93.2134 | 93.216 | 93.3593
2022-09-07 18:29 | 0:05 | 91.8572 | 91.7715 | 92.5513 | 92.9057 | 92.2676 | 92.8284 | 92.3624 | 92.7541 | 92.4075 | 92.9808 | 92.3896 | 92.5559 | 92.968 | 92.9649 | 93.1711 | 92.7946 | 92.9415 | 93.0096 | 92.9722 | 93.2032 | 90.3971 | 89.5618 | 91.1191 | 91.7562 | 91.966 | 91.6943 | 91.644 | 92.4692 | 92.23 | 91.9651 | 91.4171 | 92.6532 | 92.1167 | 92.0937 | 91.7253 | 92.2713 | 91.2816 | 92.0361 | 91.7294 | 91.251 | 91.6426 | 91.8572 | 91.6677 | 91.8732 | 91.671 | 91.7084 | 91.4922 | 91.4565 | 91.991 | 91.5764 | 91.4387 | 91.2505 | 91.9131 | 92.1186 | 91.1457 | 90.8689 | 91.9827 | 91.3081 | 93.0603 | 93.0441 | 93.2295
2022-09-07 18:29 | 0:05 | 91.8655 | 91.7902 | 92.5387 | 92.951 | 92.2295 | 92.8143 | 92.3552 | 92.765 | 92.4191 | 92.9908 | 92.3881 | 92.5622 | 92.9698 | 92.979 | 93.1603 | 92.7876 | 92.8778 | 93.0228 | 92.94 | 93.2054 | 90.3956 | 89.5829 | 91.1113 | 91.7451 | 91.9724 | 91.6601 | 91.6512 | 92.4341 | 92.2619 | 91.9376 | 91.4122 | 92.6044 | 92.0995 | 92.0873 | 91.7218 | 92.2763 | 91.2922 | 92.0366 | 91.709 | 91.2432 | 91.6346 | 91.8848 | 91.6663 | 91.8822 | 91.674 | 91.7204 | 91.4911 | 91.4583 | 91.9807 | 91.571 | 91.4242 | 91.2551 | 91.9103 | 92.1417 | 91.15 | 90.8751 | 91.987 | 91.2947 | 92.7129 | 92.8033 | 92.9291
2022-09-07 18:29 | 0:05 | 91.8628 | 91.8004 | 92.5407 | 92.8955 | 92.2411 | 92.797 | 92.3527 | 92.7358 | 92.4048 | 92.9705 | 92.4023 | 92.5523 | 92.9677 | 92.9424 | 93.1508 | 92.7752 | 92.8878 | 92.9965 | 92.9551 | 93.1405 | 90.4061 | 89.5996 | 91.1309 | 91.7472 | 91.951 | 91.6512 | 91.639 | 92.4353 | 92.2584 | 91.9555 | 91.4399 | 92.6078 | 92.1017 | 92.1078 | 91.7228 | 92.2554 | 91.2917 | 92.0405 | 91.7051 | 91.2489 | 91.63 | 91.889 | 91.6823 | 91.8911 | 91.6572 | 91.7034 | 91.4885 | 91.4227 | 91.9926 | 91.5772 | 91.4449 | 91.2423 | 91.921 | 92.1083 | 91.1388 | 90.8818 | 91.9873 | 91.3084 | 92.4756 | 92.4932 | 92.6349
2022-09-07 18:29 | 0:05 | 91.861 | 91.8011 | 92.552 | 92.9302 | 92.2341 | 92.7732 | 92.3482 | 92.7398 | 92.3961 | 92.963 | 92.3758 | 92.5509 | 92.9388 | 92.9328 | 93.1154 | 92.7595 | 92.8673 | 92.978 | 92.931 | 93.1499 | 90.3721 | 89.6316 | 91.1282 | 91.7269 | 91.971 | 91.6424 | 91.6352 | 92.435 | 92.239 | 91.9236 | 91.4359 | 92.582 | 92.0999 | 92.0992 | 91.7228 | 92.2602 | 91.2712 | 92.031 | 91.7213 | 91.2442 | 91.6269 | 91.8682 | 91.6831 | 91.9066 | 91.6641 | 91.7191 | 91.5073 | 91.4696 | 91.9898 | 91.5878 | 91.4221 | 91.2544 | 91.929 | 92.107 | 91.143 | 90.8982 | 91.9568 | 91.3142 | 92.1518 | 92.2528 | 92.412
2022-09-07 18:29 | 0:05 | 91.8592 | 91.8118 | 92.565 | 92.9241 | 92.2435 | 92.7725 | 92.3249 | 92.7369 | 92.4038 | 92.9737 | 92.3876 | 92.5305 | 92.9374 | 92.93 | 93.1017 | 92.7177 | 92.8641 | 92.9585 | 92.9035 | 93.1408 | 90.334 | 89.6494 | 91.1188 | 91.7356 | 91.9442 | 91.6523 | 91.6426 | 92.4205 | 92.1871 | 91.9647 | 91.4181 | 92.5841 | 92.0838 | 92.1375 | 91.724 | 92.223 | 91.2508 | 92.0477 | 91.742 | 91.2274 | 91.6297 | 91.8742 | 91.6796 | 91.9045 | 91.6573 | 91.7157 | 91.4826 | 91.4623 | 91.9692 | 91.5881 | 91.425 | 91.247 | 91.9365 | 92.1125 | 91.1641 | 90.9086 | 91.9586 | 91.2896 | 91.9493 | 92.0104 | 92.2815
2022-09-07 18:30 | 0:05 | 91.8835 | 91.8109 | 92.5576 | 92.8779 | 92.2341 | 92.7759 | 92.3537 | 92.7169 | 92.4016 | 92.9541 | 92.3695 | 92.5345 | 92.913 | 92.927 | 93.0741 | 92.7036 | 92.8538 | 92.943 | 92.9179 | 93.1075 | 90.3223 | 89.6761 | 91.1149 | 91.7631 | 91.9493 | 91.6415 | 91.6346 | 92.3999 | 92.178 | 91.964 | 91.415 | 92.5537 | 92.0738 | 92.0803 | 91.7089 | 92.2258 | 91.2944 | 92.0135 | 91.6971 | 91.2333 | 91.5805 | 91.8707 | 91.6968 | 91.8946 | 91.6743 | 91.7151 | 91.4961 | 91.4739 | 91.9724 | 91.5804 | 91.4236 | 91.2702 | 91.9131 | 92.1175 | 91.1462 | 90.9091 | 91.9695 | 91.3393 | 91.9093 | 91.8997 | 92.3204
2022-09-07 18:30 | 0:06 | 91.8756 | 91.8247 | 92.5558 | 92.907 | 92.2332 | 92.7761 | 92.3239 | 92.7293 | 92.3962 | 92.9497 | 92.3638 | 92.5143 | 92.9257 | 92.9125 | 93.0734 | 92.7013 | 92.8688 | 92.9525 | 92.8947 | 93.0918 | 90.3335 | 89.6785 | 91.1144 | 91.7184 | 91.9381 | 91.6292 | 91.63 | 92.3688 | 92.1837 | 91.9385 | 91.4014 | 92.5281 | 92.0595 | 92.072 | 91.6974 | 92.231 | 91.2561 | 91.9998 | 91.7158 | 91.2223 | 91.3993 | 91.8798 | 91.6664 | 91.8893 | 91.6617 | 91.7164 | 91.5032 | 91.4597 | 91.9636 | 91.5712 | 91.4395 | 91.2688 | 91.9327 | 92.1017 | 91.138 | 90.8981 | 91.9713 | 91.3085 | 91.8669 | 91.8381 | 92.3221
2022-09-07 18:30 | 0:06 | 91.879 | 91.8321 | 92.5485 | 92.8605 | 92.2181 | 92.7555 | 92.3353 | 92.7411 | 92.4031 | 92.9414 | 92.3666 | 92.5063 | 92.9044 | 92.8866 | 93.0925 | 92.6787 | 92.8322 | 92.915 | 92.8506 | 93.0885 | 90.3326 | 89.7134 | 91.11 | 91.7538 | 91.9432 | 91.6258 | 91.6269 | 92.3833 | 92.1981 | 91.9596 | 91.4143 | 92.5304 | 92.0497 | 92.0789 | 91.7103 | 92.218 | 91.2501 | 92.0197 | 91.7008 | 91.2295 | 91.2441 | 91.8802 | 91.6917 | 91.8987 | 91.6712 | 91.7165 | 91.5124 | 91.4567 | 91.9536 | 91.585 | 91.4526 | 91.2582 | 91.9215 | 92.1013 | 91.1229 | 90.8935 | 91.9684 | 91.3207 | 91.9506 | 91.9293 | 92.4741
2022-09-07 18:30 | 0:06 | 91.8737 | 91.8277 | 92.5476 | 92.8299 | 92.2255 | 92.7298 | 92.3146 | 92.7257 | 92.3985 | 92.9291 | 92.3551 | 92.5236 | 92.8887 | 92.8765 | 93.054 | 92.6742 | 92.8035 | 92.9095 | 92.8624 | 93.0935 | 90.3135 | 89.7251 | 91.116 | 91.7372 | 91.9302 | 91.6327 | 91.6297 | 92.3777 | 92.1928 | 91.9642 | 91.4211 | 92.4967 | 92.0269 | 92.0759 | 91.7029 | 92.2003 | 91.2656 | 92.0319 | 91.6883 | 91.2313 | 91.0397 | 91.8688 | 91.6839 | 91.9119 | 91.6508 | 91.7168 | 91.5045 | 91.4663 | 91.9694 | 91.5767 | 91.4477 | 91.2864 | 91.9328 | 92.0838 | 91.1617 | 90.8925 | 91.9673 | 91.3388 | 92.1187 | 92.1123 | 92.5684
2022-09-07 18:30 | 0:06 | 91.8546 | 91.1193 | 92.4012 | 92.8772 | 92.2196 | 92.7078 | 92.3093 | 92.7087 | 92.3733 | 92.9082 | 92.3432 | 92.523 | 92.8556 | 92.8387 | 93.0367 | 92.6632 | 92.7935 | 92.8692 | 92.8489 | 93.0742 | 84.6721 | 85.5783 | 88.7887 | 91.7042 | 91.8674 | 91.5847 | 91.5805 | 92.3106 | 92.1664 | 91.8666 | 90.8919 | 92.4875 | 91.9219 | 92.0128 | 91.5089 | 92.1544 | 91.2137 | 91.947 | 91.6877 | 91.1881 | 90.7928 | 91.7465 | 91.5017 | 91.5768 | 91.4227 | 91.6464 | 91.4235 | 91.134 | 91.7543 | 91.4646 | 91.2135 | 91.1208 | 91.766 | 92.0066 | 91.1264 | 90.7335 | 91.8652 | 91.3237 | 92.1832 | 92.2448 | 92.5814
2022-09-07 18:30 | 0:06 | 91.6628 | 81.4238 | 92.0639 | 92.7466 | 92.2144 | 92.5965 | 92.2876 | 92.6561 | 92.3625 | 92.8311 | 92.2838 | 92.4917 | 92.74 | 92.6743 | 92.9458 | 92.6023 | 92.7208 | 92.7455 | 92.7769 | 92.9952 | 84.7469 | 75.5037 | 88.1496 | 91.4169 | 91.7478 | 91.2956 | 91.3993 | 92.2114 | 92.0777 | 91.6442 | 90.5157 | 92.4417 | 91.7741 | 91.7916 | 91.3658 | 92.067 | 91.0595 | 91.7844 | 91.625 | 91.0435 | 90.7053 | 91.5701 | 91.3168 | 91.3034 | 91.1802 | 91.5475 | 91.311 | 90.8453 | 91.4551 | 91.2857 | 91.1927 | 90.957 | 91.538 | 91.9296 | 90.9796 | 90.538 | 91.7195 | 91.251 | 92.3514 | 92.3804 | 92.7262
2022-09-07 18:31 | 0:07 | 89.5209 | 71.7904 | 89.8321 | 92.2298 | 92.106 | 92.1365 | 92.1855 | 92.1976 | 92.2972 | 92.4652 | 91.7759 | 92.4045 | 92.262 | 92.1877 | 92.7387 | 92.4526 | 92.4306 | 92.256 | 92.5998 | 92.7542 | 85.1955 | 71.0992 | 87.6489 | 91.2043 | 91.5966 | 91.0932 | 91.2441 | 91.9313 | 91.8398 | 91.3867 | 90.1394 | 92.3628 | 91.4586 | 91.4897 | 90.9843 | 91.8881 | 90.8933 | 91.5478 | 91.5306 | 90.935 | 90.5441 | 91.4497 | 91.1458 | 91.0381 | 90.9821 | 91.4708 | 91.2091 | 90.5402 | 91.2475 | 91.1649 | 90.9351 | 90.7678 | 91.3384 | 91.7964 | 90.9515 | 90.3837 | 91.6359 | 91.1825 | 92.4484 | 92.5019 | 92.7801
2022-09-07 18:31 | 0:07 | 85.4336 | 74.4591 | 87.0172 | 91.4359 | 91.9133 | 91.3945 | 91.9543 | 91.6395 | 92.1549 | 91.924 | 91.1934 | 92.2707 | 91.7073 | 91.668 | 92.4739 | 92.2994 | 91.9674 | 91.8021 | 92.3338 | 92.4227 | 83.868 | 73.0465 | 86.5124 | 90.8704 | 91.4124 | 90.8206 | 91.0397 | 91.6478 | 91.5341 | 91.0568 | 89.5962 | 92.2071 | 91.1496 | 91.0211 | 90.6581 | 91.6459 | 90.6926 | 91.2154 | 91.4832 | 90.7225 | 90.4245 | 91.2185 | 90.9505 | 90.6312 | 90.7129 | 91.3342 | 91.0188 | 90.2447 | 90.9749 | 90.9298 | 90.7226 | 90.6137 | 91.1118 | 91.7122 | 90.8581 | 90.1658 | 91.4135 | 91.0897 | 92.4695 | 92.5863 | 92.7177
2022-09-07 18:31 | 0:07 | 82.1492 | 75.7648 | 84.7686 | 90.815 | 91.8071 | 91.0051 | 91.8142 | 91.2734 | 92.03 | 91.5523 | 90.7524 | 92.1075 | 91.2591 | 91.1281 | 92.3052 | 92.1118 | 91.5614 | 91.4926 | 92.1813 | 92.2239 | 82.1606 | 73.5494 | 85.3553 | 90.4992 | 91.1103 | 90.5614 | 90.7928 | 91.4263 | 91.2914 | 90.7877 | 89.09 | 92.1344 | 90.8496 | 90.6655 | 90.4056 | 91.4275 | 90.4713 | 90.8864 | 91.3021 | 90.5435 | 90.1997 | 91.015 | 90.7201 | 90.2676 | 90.4327 | 91.1264 | 90.9478 | 89.9355 | 90.6654 | 90.6706 | 90.4222 | 90.4754 | 90.9789 | 91.5121 | 90.7475 | 89.9599 | 91.2487 | 90.9246 | 92.5189 | 92.6762 | 92.8187
2022-09-07 18:31 | 0:07 | 79.346 | 75.2474 | 82.6902 | 90.2792 | 91.5813 | 90.6183 | 91.5944 | 90.9128 | 91.9038 | 91.1773 | 90.4055 | 92.0215 | 90.7731 | 90.8635 | 92.0258 | 91.8666 | 91.261 | 90.9578 | 91.9142 | 91.9857 | 80.5841 | 73.8152 | 84.2835 | 90.2177 | 91.0233 | 90.3537 | 90.7053 | 91.2329 | 90.8874 | 90.4721 | 88.7493 | 92.0472 | 90.5399 | 90.26 | 90.2049 | 91.0976 | 90.2699 | 90.6241 | 91.1955 | 90.3577 | 90.1298 | 90.8034 | 90.5212 | 89.9043 | 90.232 | 91.0303 | 90.7956 | 89.6023 | 90.4557 | 90.4798 | 90.2328 | 90.3467 | 90.7612 | 91.2844 | 90.6656 | 89.7532 | 91.1791 | 90.832 | 92.6199 | 92.7747 | 92.7889
2022-09-07 18:31 | 0:07 | 75.6916 | 74.5091 | 80.7246 | 89.7297 | 91.3422 | 90.442 | 91.4215 | 90.418 | 91.7494 | 90.9629 | 89.7902 | 91.8887 | 90.2412 | 90.3978 | 91.914 | 91.7244 | 90.8822 | 90.64 | 91.5844 | 91.6855 | 79.2924 | 73.6315 | 83.4128 | 89.8398 | 90.8404 | 90.2083 | 90.5441 | 90.9013 | 90.7875 | 90.246 | 88.2965 | 91.8562 | 90.1414 | 89.9119 | 89.9598 | 90.9826 | 90.0121 | 90.3604 | 91.088 | 90.0871 | 89.8192 | 90.6521 | 90.3801 | 89.5897 | 90.017 | 90.9128 | 90.634 | 89.2756 | 90.2419 | 90.3026 | 90.0417 | 90.2458 | 90.5615 | 91.2304 | 90.5957 | 89.5807 | 90.932 | 90.7964 | 92.7562 | 92.9092 | 92.9485
2022-09-07 18:31 | 0:07 | 72.5084 | 73.76 | 79.1603 | 89.2961 | 91.2257 | 89.8884 | 91.0306 | 89.9471 | 91.5622 | 90.5511 | 89.5515 | 91.7788 | 89.9026 | 90.1379 | 91.6225 | 91.4859 | 90.5943 | 90.3546 | 91.3913 | 91.4272 | 78.2867 | 73.31 | 82.6901 | 89.5504 | 90.6564 | 89.9898 | 90.4245 | 90.7533 | 90.5039 | 89.9762 | 88.2169 | 91.725 | 89.8636 | 89.5795 | 89.6677 | 90.5989 | 89.8101 | 90.2049 | 90.879 | 89.9259 | 89.6125 | 90.4554 | 90.2106 | 89.3207 | 89.8157 | 90.7334 | 90.5816 | 89.0201 | 89.9683 | 90.0837 | 89.6689 | 90.0622 | 90.4314 | 91.1334 | 90.4835 | 89.3981 | 90.6993 | 90.6728 | 92.8856 | 93.0753 | 93.0753
2022-09-07 18:32 | 0:07 | 71.5383 | 73.1862 | 78.1146 | 88.9627 | 91.0173 | 89.6409 | 90.7834 | 89.5419 | 91.446 | 90.357 | 89.0265 | 91.7055 | 89.5076 | 89.7864 | 91.3507 | 91.2833 | 90.1995 | 89.8966 | 91.2038 | 91.2661 | 77.3897 | 72.7832 | 81.9607 | 89.3388 | 90.4867 | 89.7681 | 90.1997 | 90.6564 | 90.2547 | 89.7856 | 87.8021 | 91.6826 | 89.6082 | 89.3289 | 89.4837 | 90.4889 | 89.5783 | 89.9228 | 90.7469 | 89.7116 | 89.4431 | 90.293 | 90.0315 | 89.0117 | 89.6725 | 90.6435 | 90.5499 | 88.7141 | 89.7681 | 89.8433 | 89.5749 | 89.8291 | 90.248 | 90.8667 | 90.3719 | 89.2514 | 90.6354 | 90.4732 | 93.0019 | 93.2492 | 93.1351
2022-09-07 18:32 | 0:08 | 70.86 | 72.5829 | 77.2047 | 88.6184 | 90.7453 | 89.4446 | 90.6462 | 89.4024 | 91.326 | 90.1318 | 88.6869 | 91.4501 | 89.3502 | 89.7724 | 91.1741 | 91.0972 | 89.9797 | 89.5108 | 90.9572 | 91.1498 | 76.6094 | 72.2215 | 81.2538 | 88.9996 | 90.2494 | 89.4108 | 90.1298 | 90.3611 | 90.1474 | 89.5306 | 87.4844 | 91.4401 | 89.4324 | 89.0275 | 89.1024 | 90.3828 | 89.4098 | 89.6475 | 90.6332 | 89.5154 | 89.259 | 90.1074 | 89.8249 | 88.7207 | 89.4339 | 90.5253 | 90.3845 | 88.5071 | 89.5293 | 89.7417 | 89.4499 | 89.6666 | 90.0715 | 90.7258 | 90.2434 | 89.0495 | 90.4988 | 90.4179 | 93.1569 | 93.4018 | 93.1863
2022-09-07 18:32 | 0:08 | 70.2917 | 72.0069 | 76.7431 | 88.2239 | 90.5338 | 89.2214 | 90.5503 | 89.0308 | 91.1522 | 89.8667 | 88.4049 | 91.4151 | 88.9588 | 89.6149 | 91.0745 | 90.8712 | 89.71 | 89.3054 | 90.797 | 90.859 | 75.9001 | 71.6734 | 80.6714 | 88.7912 | 90.0017 | 89.3065 | 89.8192 | 90.1941 | 89.6934 | 89.3937 | 87.2604 | 91.4031 | 89.1843 | 88.7567 | 88.8995 | 90.0836 | 89.2471 | 89.4473 | 90.5581 | 89.2951 | 89.1736 | 89.9165 | 89.7791 | 88.4198 | 89.2088 | 90.4302 | 90.2857 | 88.1873 | 89.3517 | 89.5261 | 89.2659 | 89.4274 | 89.9747 | 90.443 | 90.2757 | 88.8404 | 90.2986 | 90.3899 | 93.2856 | 93.5433 | 93.299
2022-09-07 18:32 | 0:08 | 69.7819 | 71.4994 | 76.045 | 88.0155 | 90.3403 | 89.0269 | 90.3202 | 88.7951 | 90.9985 | 89.4637 | 88.0573 | 91.3308 | 88.7846 | 89.2671 | 90.9148 | 90.658 | 89.2921 | 88.8589 | 90.6244 | 90.636 | 75.2856 | 71.1923 | 80.0932 | 88.5062 | 89.8211 | 89.1265 | 89.6125 | 90.1761 | 89.5745 | 89.2556 | 86.881 | 91.2808 | 89.058 | 88.5468 | 88.732 | 90.0318 | 89.0679 | 89.322 | 90.2339 | 89.0576 | 88.923 | 89.7233 | 89.6647 | 88.1769 | 89.1261 | 90.243 | 90.2037 | 87.9348 | 89.1521 | 89.3642 | 89.015 | 89.3387 | 89.8769 | 90.4308 | 90.0232 | 88.6546 | 90.1915 | 90.1898 | 93.4516 | 93.7079 | 93.4334
2022-09-07 18:32 | 0:08 | 69.2364 | 70.9259 | 75.3372 | 87.6439 | 90.0717 | 88.9418 | 90.2184 | 88.4495 | 90.839 | 89.3508 | 87.797 | 91.1446 | 88.4404 | 89.2982 | 90.6065 | 90.4486 | 89.1139 | 88.6811 | 90.3808 | 90.397 | 74.6576 | 70.6413 | 79.5937 | 88.1977 | 89.6632 | 89.0156 | 89.4431 | 89.7939 | 89.4698 | 89.0403 | 86.7072 | 91.0733 | 88.7491 | 88.2658 | 88.211 | 89.7634 | 88.8169 | 89.0668 | 90.2251 | 88.8615 | 88.8916 | 89.5933 | 89.4408 | 87.9148 | 88.9538 | 90.0993 | 90.1415 | 87.6483 | 88.9818 | 89.1978 | 88.8958 | 89.1179 | 89.7812 | 90.2549 | 90.0872 | 88.4411 | 90.0182 | 90.2153 | 93.6099 | 93.8126 | 93.5886
2022-09-07 18:32 | 0:08 | 68.764 | 70.4143 | 74.8175 | 87.1869 | 89.8452 | 88.5279 | 89.8749 | 88.0847 | 90.6914 | 89.2139 | 87.4137 | 91.0633 | 87.9607 | 89.0592 | 90.5294 | 90.2165 | 88.8627 | 88.6253 | 90.2441 | 90.2251 | 74.0983 | 70.1669 | 79.0984 | 88.0029 | 89.3501 | 88.7948 | 89.259 | 89.5645 | 89.1654 | 88.9122 | 86.4117 | 90.9113 | 88.5347 | 88.05 | 87.8693 | 89.6315 | 88.6043 | 88.9019 | 89.8844 | 88.6482 | 88.5674 | 89.3975 | 89.2914 | 87.6566 | 88.7613 | 89.9741 | 89.8855 | 87.4203 | 88.8059 | 88.963 | 88.7013 | 88.916 | 89.5484 | 90.0641 | 90.0105 | 88.3101 | 89.9304 | 90.1189 | 93.7139 | 93.7979 | 93.6982
2022-09-07 18:33 | 0:09 | 68.2495 | 69.8841 | 74.2785 | 86.8602 | 89.6622 | 88.1701 | 89.8678 | 87.5644 | 90.4814 | 88.9452 | 86.9192 | 90.9454 | 87.5859 | 88.6952 | 90.327 | 90.0134 | 88.5632 | 88.1449 | 89.9633 | 89.9463 | 73.5479 | 69.6601 | 78.6307 | 87.7639 | 89.186 | 88.5145 | 89.1736 | 89.4528 | 88.9249 | 88.6189 | 86.068 | 90.7029 | 88.3331 | 87.9171 | 87.6591 | 89.3957 | 88.3863 | 88.7634 | 89.9921 | 88.4836 | 88.4392 | 89.1814 | 89.1328 | 87.3778 | 88.5288 | 89.7557 | 89.8927 | 87.278 | 88.655 | 88.8364 | 88.5318 | 88.7939 | 89.4465 | 89.9933 | 89.668 | 88.1029 | 89.7323 | 89.9987 | 93.7931 | 93.8912 | 93.7005
2022-09-07 18:33 | 0:09 | 67.8051 | 69.3747 | 73.7184 | 86.7427 | 89.3571 | 88.0264 | 89.7352 | 87.1859 | 90.2876 | 88.7582 | 86.7702 | 90.7485 | 87.3844 | 88.375 | 90.0935 | 89.9302 | 88.2953 | 88.0054 | 89.8417 | 89.8209 | 73.0411 | 69.2046 | 78.1446 | 87.5857 | 88.9756 | 88.4346 | 88.923 | 89.2328 | 88.7413 | 88.4193 | 85.718 | 90.622 | 88.0817 | 87.5781 | 87.4078 | 89.3863 | 88.1657 | 88.4032 | 89.7155 | 88.2453 | 88.3557 | 89.0229 | 88.9289 | 87.0982 | 88.4014 | 89.6423 | 89.7497 | 87.004 | 88.3894 | 88.5839 | 88.511 | 88.6585 | 89.3662 | 89.7907 | 89.6947 | 87.9832 | 89.6163 | 89.8221 | 93.9354 | 93.9392 | 93.8173
2022-09-07 18:33 | 0:09 | 67.3474 | 68.8749 | 73.2292 | 86.4321 | 89.1397 | 87.5196 | 89.5402 | 86.9249 | 90.1069 | 88.2597 | 86.4772 | 90.6114 | 87.166 | 87.7597 | 90.0636 | 89.6157 | 88.0265 | 87.9505 | 89.8352 | 89.7203 | 72.5864 | 68.7266 | 77.7413 | 87.3069 | 88.6747 | 88.254 | 88.8916 | 89.1352 | 88.5017 | 88.2886 | 85.4777 | 90.4059 | 87.806 | 87.269 | 87.2678 | 88.7102 | 87.9306 | 88.191 | 89.7043 | 88.0731 | 88.1541 | 88.8755 | 88.7117 | 86.9228 | 88.2354 | 89.5071 | 89.4071 | 86.7219 | 88.1523 | 88.578 | 88.0234 | 88.4029 | 89.0936 | 89.6178 | 89.8906 | 87.8009 | 89.336 | 89.7895 | 94.1123 | 94.0803 | 93.9135
2022-09-07 18:33 | 0:09 | 66.9069 | 68.3939 | 72.7194 | 86.1453 | 88.8885 | 87.6621 | 89.327 | 86.6004 | 89.8986 | 87.9878 | 85.9793 | 90.5317 | 86.7202 | 87.6318 | 89.7115 | 89.3629 | 87.7257 | 87.6725 | 89.5042 | 89.4863 | 72.089 | 68.2896 | 77.253 | 86.995 | 88.4557 | 88.0877 | 88.5674 | 88.8675 | 88.343 | 87.9562 | 85.0466 | 90.1874 | 87.5118 | 87.0803 | 86.9836 | 88.5438 | 87.6895 | 87.9525 | 89.5231 | 87.8485 | 87.881 | 88.6989 | 88.615 | 86.6265 | 88.0599 | 89.2682 | 89.4094 | 86.503 | 88.1151 | 88.3151 | 88.6134 | 88.267 | 89.0823 | 89.4055 | 89.4608 | 87.6265 | 89.3182 | 89.677 | 94.308 | 94.2399 | 94.0581
2022-09-07 18:33 | 0:09 | 66.4417 | 67.8955 | 72.1878 | 85.8592 | 88.7545 | 87.2825 | 89.2343 | 86.6018 | 89.7352 | 87.8099 | 85.7903 | 90.4215 | 86.536 | 87.4739 | 89.5436 | 89.1278 | 87.4396 | 87.242 | 89.2732 | 89.3156 | 71.6179 | 67.8369 | 76.8093 | 86.7228 | 88.2622 | 87.8431 | 88.4392 | 88.689 | 87.9061 | 87.83 | 84.9989 | 90.1428 | 87.2599 | 86.9219 | 86.5916 | 88.4007 | 87.4905 | 87.8042 | 89.5306 | 87.5468 | 87.5993 | 88.495 | 88.4755 | 86.3827 | 87.8255 | 89.0447 | 89.287 | 86.1688 | 87.9685 | 88.0886 | 88.4488 | 88.1439 | 88.8819 | 89.2606 | 89.2973 | 87.4293 | 89.1366 | 89.5318 | 94.4432 | 94.4586 | 94.1567
2022-09-07 18:33 | 0:09 | 66.0166 | 67.4379 | 71.6547 | 85.5685 | 88.4827 | 87.1844 | 88.9559 | 86.0134 | 89.5435 | 87.57 | 85.4106 | 90.2937 | 86.0823 | 87.5256 | 89.3604 | 88.9197 | 87.1994 | 87.0385 | 88.7802 | 88.8125 | 71.1758 | 67.394 | 76.4486 | 86.535 | 88.0629 | 87.6562 | 88.3557 | 88.4196 | 87.7444 | 87.5775 | 84.5137 | 89.9185 | 86.9956 | 86.7401 | 86.3444 | 88.2964 | 87.3031 | 87.7772 | 89.2589 | 87.3707 | 87.4788 | 88.2949 | 88.3247 | 86.1719 | 87.6406 | 88.8903 | 89.2079 | 85.9751 | 87.6967 | 88.0248 | 88.1722 | 87.9717 | 88.7713 | 89.0983 | 89.3429 | 87.2495 | 89.0564 | 89.4397 | 94.5932 | 94.5858 | 94.2852
2022-09-07 18:34 | 0:09 | 65.5278 | 66.9262 | 71.1627 | 85.0868 | 88.2716 | 86.8309 | 88.7062 | 85.8215 | 89.352 | 87.3795 | 85.4059 | 90.1358 | 86.0883 | 87.2974 | 89.0573 | 88.5853 | 86.8429 | 86.6856 | 88.6543 | 88.6201 | 70.7205 | 66.905 | 76.0238 | 86.2369 | 87.764 | 87.4344 | 88.1541 | 88.3203 | 87.4822 | 87.3466 | 84.442 | 89.7164 | 86.7997 | 86.5159 | 85.6935 | 88.2672 | 87.0627 | 87.4701 | 89.1861 | 87.159 | 87.248 | 88.0145 | 88.2823 | 85.8475 | 87.4041 | 88.7601 | 89.142 | 85.6928 | 87.5664 | 87.903 | 87.9664 | 87.9502 | 88.8026 | 88.9516 | 89.2152 | 86.9988 | 88.9104 | 89.4805 | 94.7094 | 94.7974 | 94.3287
2022-09-07 18:34 | 0:10 | 65.104 | 66.4482 | 70.6471 | 84.9926 | 87.9598 | 86.1845 | 88.6662 | 85.5224 | 89.1722 | 87.1762 | 85.3051 | 90.0471 | 85.593 | 87.1633 | 88.9197 | 88.4628 | 86.522 | 86.6937 | 88.5035 | 88.4395 | 70.3151 | 66.4694 | 75.6324 | 86.0567 | 87.5548 | 87.3638 | 87.881 | 87.9948 | 87.0716 | 87.2473 | 84.0594 | 89.4223 | 86.4978 | 86.164 | 85.5371 | 87.7908 | 86.8365 | 87.2496 | 88.995 | 86.9223 | 86.9855 | 87.9477 | 88.0919 | 85.7646 | 87.2591 | 88.5729 | 88.9077 | 85.5418 | 87.3845 | 87.7353 | 87.801 | 87.6588 | 88.5034 | 88.6136 | 88.8974 | 86.8097 | 88.5561 | 89.3269 | 94.8027 | 94.9509 | 94.3678
2022-09-07 18:34 | 0:10 | 64.6692 | 66.0175 | 70.136 | 84.667 | 87.7249 | 85.7886 | 87.9662 | 85.2729 | 88.9339 | 86.8967 | 85.0502 | 89.8886 | 85.2917 | 86.7332 | 88.6787 | 88.2769 | 86.2868 | 86.525 | 88.2173 | 88.1343 | 69.8881 | 66.0931 | 75.2431 | 85.7663 | 87.3651 | 87.3094 | 87.5993 | 87.8577 | 86.9473 | 87.0332 | 83.979 | 89.3361 | 86.5633 | 85.9605 | 85.122 | 87.8074 | 86.5558 | 87.0319 | 88.8523 | 86.6562 | 86.8831 | 87.6982 | 87.9369 | 85.5199 | 87.1429 | 88.3962 | 88.8288 | 85.2977 | 87.1946 | 87.5106 | 87.7155 | 87.4693 | 88.3989 | 88.4605 | 88.9392 | 86.5955 | 88.6276 | 89.2286 | 94.9106 | 95.0638 | 94.439
2022-09-07 18:34 | 0:10 | 64.3093 | 65.5333 | 69.6887 | 84.3881 | 87.6012 | 85.5131 | 88.0798 | 85.0653 | 88.7454 | 86.8961 | 84.5351 | 89.718 | 85.0959 | 86.2776 | 88.4036 | 88.079 | 86.0398 | 86.3279 | 88.0021 | 87.9661 | 69.514 | 65.6464 | 74.8941 | 85.509 | 87.0786 | 87.0126 | 87.4788 | 87.6668 | 86.8363 | 86.7783 | 83.6526 | 89.0177 | 86.2607 | 85.7906 | 84.8805 | 87.6219 | 86.3995 | 86.9498 | 88.4795 | 86.3614 | 86.7905 | 87.5359 | 87.8327 | 85.3791 | 86.9483 | 88.2908 | 88.7201 | 85.105 | 87.0577 | 87.2356 | 87.7648 | 87.2097 | 88.4009 | 88.3047 | 88.7671 | 86.4347 | 88.3585 | 88.9867 | 95.0441 | 95.1261 | 94.5665
2022-09-07 18:34 | 0:10 | 63.891 | 65.0596 | 69.2111 | 84.0406 | 87.2719 | 85.4452 | 87.9209 | 84.6492 | 88.5268 | 86.5295 | 84.411 | 89.5649 | 84.8913 | 85.9487 | 88.2134 | 87.7615 | 85.7619 | 85.8312 | 87.7624 | 88.0438 | 69.1015 | 65.2344 | 74.5461 | 85.3322 | 86.8721 | 86.993 | 87.248 | 87.4903 | 86.2563 | 86.6114 | 83.3597 | 88.9731 | 86.0072 | 85.5066 | 84.5277 | 87.4293 | 86.1444 | 86.6379 | 88.7722 | 86.1897 | 86.3618 | 87.3422 | 87.6579 | 85.082 | 86.7495 | 88.1325 | 88.5627 | 84.8038 | 86.8851 | 87.1793 | 88.0049 | 87.0533 | 88.2114 | 88.0902 | 88.7062 | 86.1716 | 88.228 | 89.0483 | 95.1162 | 95.2247 | 94.6014
2022-09-07 18:34 | 0:10 | 63.4989 | 64.5993 | 68.7581 | 83.7966 | 87.01 | 85.2617 | 87.5477 | 84.3385 | 88.3433 | 86.3122 | 84.0664 | 89.4083 | 84.6247 | 85.6997 | 87.9862 | 87.5405 | 85.4963 | 85.8036 | 87.5208 | 87.7733 | 68.6981 | 64.8031 | 74.2181 | 84.993 | 86.6527 | 86.6777 | 86.9855 | 87.4209 | 86.2313 | 86.4204 | 83.2072 | 88.9024 | 85.7706 | 85.3392 | 84.3672 | 87.4612 | 85.8749 | 86.39 | 88.58 | 85.9078 | 86.1878 | 87.1845 | 87.387 | 84.8622 | 86.5308 | 87.8376 | 88.3837 | 84.5815 | 86.6975 | 86.8513 | 87.4588 | 86.7681 | 88.0939 | 87.9293 | 88.7394 | 86.0097 | 88.012 | 88.8585 | 95.1886 | 95.2731 | 94.6587
2022-09-07 18:35 | 0:11 | 63.1611 | 64.1637 | 68.2947 | 83.5249 | 86.953 | 85.0456 | 87.5461 | 84.0572 | 88.1493 | 85.9567 | 83.5097 | 89.2413 | 83.95 | 85.6342 | 87.6865 | 87.2733 | 85.3021 | 85.2643 | 87.2804 | 87.6649 | 68.3218 | 64.3903 | 73.8293 | 84.8209 | 86.3542 | 86.4578 | 86.8831 | 86.9963 | 85.8781 | 86.2271 | 82.841 | 88.7083 | 85.272 | 85.1334 | 83.7675 | 87.1672 | 85.6567 | 86.2884 | 88.2039 | 85.7862 | 86.0464 | 86.9764 | 87.2169 | 84.5272 | 86.3916 | 87.6474 | 88.3514 | 84.4046 | 86.5286 | 86.7551 | 87.4034 | 86.5784 | 87.7974 | 87.7844 | 88.4916 | 85.7841 | 87.7359 | 88.798 | 95.1048 | 95.2445 | 94.5273
2022-09-07 18:35 | 0:11 | 62.7473 | 63.7516 | 67.912 | 83.2348 | 86.5343 | 84.9936 | 87.3218 | 83.7419 | 87.9109 | 85.7094 | 83.3341 | 89.1589 | 83.7357 | 85.6484 | 87.4568 | 86.9343 | 84.8868 | 85.0973 | 87.0256 | 87.1377 | 67.93 | 64.0159 | 73.4569 | 84.6371 | 86.1343 | 86.372 | 86.7905 | 86.8695 | 85.6713 | 86.0345 | 82.5256 | 88.4104 | 85.0222 | 84.8438 | 83.5414 | 87.0145 | 85.4893 | 86.086 | 88.0138 | 85.4983 | 85.8649 | 86.7681 | 87.0779 | 84.2753 | 86.2674 | 87.4657 | 88.2661 | 84.162 | 86.3886 | 86.63 | 86.8382 | 86.5303 | 87.7158 | 87.5901 | 88.6824 | 85.5557 | 87.5721 | 88.7657 | 94.9256 | 95.1109 | 94.4275
2022-09-07 18:35 | 0:11 | 62.3705 | 63.3363 | 67.4468 | 83.024 | 86.3582 | 84.8072 | 87.3066 | 83.2687 | 87.6601 | 85.5842 | 83.0244 | 88.7491 | 83.632 | 85.1603 | 87.3412 | 86.8262 | 84.7228 | 84.7512 | 86.7307 | 86.9805 | 67.5747 | 63.6095 | 73.131 | 84.2311 | 85.9437 | 86.1425 | 86.3618 | 86.6945 | 85.411 | 85.8239 | 82.2754 | 88.2457 | 84.9068 | 84.5851 | 83.4061 | 86.8073 | 85.2382 | 85.8832 | 88.136 | 85.2664 | 85.631 | 86.6579 | 86.7803 | 84.0424 | 85.946 | 87.3394 | 88.0737 | 83.7622 | 86.1135 | 86.5227 | 87.1923 | 86.1373 | 87.7622 | 87.2591 | 88.4041 | 85.4411 | 87.3273 | 88.5164 | 94.7412 | 94.9179 | 94.2579
2022-09-07 18:35 | 0:11 | 62.0371 | 62.9355 | 67.0907 | 82.7124 | 85.9717 | 84.5419 | 87.103 | 82.8498 | 87.4536 | 85.171 | 82.6478 | 88.6834 | 83.0784 | 85.0276 | 87.1383 | 86.511 | 84.5004 | 84.357 | 86.4666 | 86.8902 | 67.2161 | 63.2362 | 72.8096 | 84.0445 | 85.654 | 85.9087 | 86.1878 | 86.3834 | 85.063 | 85.6331 | 82.2031 | 88.1405 | 84.7649 | 84.4386 | 83.0819 | 86.7259 | 85.0395 | 85.6342 | 87.982 | 85.1072 | 85.5408 | 86.336 | 86.6894 | 83.8516 | 85.8088 | 87.0726 | 87.8581 | 83.5657 | 85.9998 | 86.3472 | 87.4788 | 86.1681 | 87.6154 | 87.0469 | 88.0703 | 85.138 | 87.2619 | 88.4387 | 94.5684 | 94.7482 | 94.1554
2022-09-07 18:35 | 0:11 | 61.8353 | 62.515 | 66.6172 | 82.3707 | 85.7322 | 84.0772 | 86.6656 | 82.6721 | 87.1918 | 84.9844 | 82.5107 | 88.5138 | 82.9038 | 84.9664 | 86.7374 | 86.3085 | 84.2408 | 84.3153 | 86.3563 | 86.4088 | 66.8637 | 62.8758 | 72.5115 | 83.7953 | 85.3972 | 85.673 | 86.0464 | 86.1702 | 84.9718 | 85.4162 | 81.8624 | 87.7926 | 84.4275 | 84.2701 | 82.7116 | 86.245 | 84.8273 | 85.502 | 87.695 | 84.8266 | 85.3632 | 86.1953 | 86.6388 | 83.5723 | 85.6547 | 86.8374 | 87.7321 | 83.3977 | 85.8069 | 86.0845 | 87.2007 | 85.7377 | 87.4761 | 86.7006 | 87.7698 | 84.9904 | 87.0744 | 88.429 | 94.4225 | 94.6374 | 94.158
2022-09-07 18:35 | 0:11 | 61.4995 | 62.1292 | 66.2763 | 82.1932 | 85.4559 | 83.6715 | 86.8165 | 82.3701 | 86.9777 | 84.6304 | 82.2738 | 88.4162 | 82.5105 | 84.37 | 86.6421 | 86.0754 | 83.8607 | 84.3183 | 86.123 | 86.1786 | 66.5021 | 62.513 | 72.1539 | 83.6161 | 85.0445 | 85.5541 | 85.8649 | 85.8444 | 84.7997 | 85.2229 | 81.3562 | 87.704 | 84.2753 | 84.001 | 82.4955 | 86.1213 | 84.591 | 85.261 | 87.3082 | 84.5595 | 85.1465 | 86.0774 | 86.3515 | 83.4071 | 85.3955 | 86.6874 | 87.5309 | 83.2946 | 85.5706 | 85.8156 | 86.8879 | 85.5241 | 87.2076 | 86.6139 | 87.7975 | 84.8027 | 87.1064 | 88.3282 | 94.3386 | 94.5372 | 94.0787
2022-09-07 18:36 | 0:12 | 61.3385 | 61.8166 | 65.9091 | 81.9147 | 85.3499 | 83.3978 | 86.1072 | 82.0715 | 86.7659 | 84.3777 | 81.9213 | 88.3062 | 82.0821 | 84.257 | 86.4756 | 85.7893 | 83.582 | 84.0575 | 85.8162 | 86.28 | 66.1567 | 62.1641 | 71.8222 | 83.3264 | 84.9061 | 85.3655 | 85.631 | 85.5008 | 84.5952 | 85.0513 | 81.3021 | 87.4879 | 84.0026 | 83.734 | 82.3207 | 85.8621 | 84.583 | 84.9435 | 87.4464 | 84.3928 | 84.8189 | 85.8032 | 86.2938 | 83.2174 | 85.3125 | 86.5217 | 87.344 | 82.9562 | 85.3675 | 85.4894 | 86.3157 | 85.3517 | 87.0636 | 86.4189 | 87.8923 | 84.6346 | 86.8264 | 88.123 | 94.2635 | 94.4103 | 94.0448
2022-09-07 18:36 | 0:12 | 61.2244 | 61.4877 | 65.5586 | 81.6448 | 85.0125 | 83.2819 | 86.2382 | 81.6218 | 86.5319 | 84.1796 | 81.938 | 88.032 | 82.0926 | 84.0942 | 86.0819 | 85.6081 | 83.3836 | 83.6614 | 85.5272 | 85.8223 | 65.8544 | 61.8182 | 71.5823 | 83.1491 | 84.607 | 85.1902 | 85.5408 | 85.3594 | 84.1894 | 84.8977 | 80.8847 | 87.2448 | 83.5849 | 83.4403 | 82.1305 | 85.5506 | 84.0957 | 84.7262 | 87.1883 | 84.1733 | 84.5855 | 85.6185 | 86.1109 | 82.9804 | 85.1204 | 86.4036 | 87.2186 | 82.6539 | 85.2822 | 85.4169 | 86.5913 | 85.2488 | 86.9653 | 86.1409 | 87.5449 | 84.406 | 86.5434 | 88.0536 | 94.1636 | 94.3061 | 94.0013
2022-09-07 18:36 | 0:12 | 61.084 | 61.1647 | 65.2496 | 81.3381 | 84.7466 | 82.8607 | 85.7549 | 81.5909 | 86.3978 | 83.9256 | 81.4927 | 87.9102 | 81.6128 | 83.8318 | 85.8381 | 85.3279 | 83.1054 | 83.5841 | 85.2498 | 85.5844 | 65.5548 | 61.5065 | 71.3028 | 82.9031 | 84.3785 | 85.0691 | 85.3632 | 85.2566 | 83.9717 | 84.6657 | 80.5603 | 87.0704 | 83.358 | 83.2723 | 81.585 | 85.3385 | 83.9124 | 84.5386 | 86.9198 | 83.8484 | 84.4555 | 85.3878 | 85.8025 | 82.8406 | 84.8729 | 86.129 | 86.9757 | 82.4797 | 85.0728 | 85.1953 | 86.2983 | 84.9076 | 86.9129 | 85.8575 | 87.6776 | 84.1446 | 86.4448 | 87.715 | 94.1351 | 94.3019 | 94.1062
2022-09-07 18:36 | 0:12 | 60.6607 | 60.8426 | 64.8834 | 80.8678 | 84.5697 | 83.0157 | 86.0039 | 81.1635 | 86.1432 | 83.9169 | 81.327 | 87.8883 | 81.3437 | 83.9157 | 85.6808 | 85.0554 | 82.822 | 83.2831 | 85.1264 | 85.312 | 65.284 | 61.1869 | 71.039 | 82.6791 | 84.094 | 84.7503 | 85.1465 | 84.971 | 83.737 | 84.368 | 80.2144 | 86.9258 | 83.1089 | 83.112 | 81.0291 | 85.3064 | 83.6803 | 84.4396 | 86.7599 | 83.7023 | 84.232 | 85.2655 | 85.7698 | 82.651 | 84.7057 | 85.9142 | 87.0724 | 82.2631 | 84.8751 | 85.0825 | 86.4552 | 84.7019 | 86.6321 | 85.726 | 87.2545 | 83.9557 | 86.1951 | 87.6095 | 94.0862 | 94.1728 | 93.9687
2022-09-07 18:36 | 0:12 | 60.7056 | 60.5496 | 64.5796 | 80.7346 | 84.1967 | 82.7566 | 85.7398 | 81.0686 | 86.0099 | 83.5206 | 81.114 | 87.5633 | 81.183 | 83.7041 | 85.3156 | 84.6976 | 82.6488 | 83.1557 | 84.7937 | 85.0469 | 65.0054 | 60.896 | 70.7699 | 82.4132 | 83.9347 | 84.7452 | 84.8189 | 84.5803 | 83.6035 | 84.2743 | 80.1841 | 86.6606 | 82.8226 | 82.7961 | 80.9162 | 84.8153 | 83.4632 | 84.3202 | 86.2552 | 83.4301 | 83.9987 | 85.0536 | 85.483 | 82.3307 | 84.4929 | 85.5826 | 86.8167 | 82.1529 | 84.6634 | 85.0078 | 86.2584 | 84.5486 | 86.4826 | 85.5936 | 86.5826 | 83.7151 | 86.1847 | 87.5023 | 94.0495 | 94.1007 | 93.9116
2022-09-07 18:36 | 0:12 | 60.6318 | 60.2332 | 64.2447 | 80.4438 | 83.9476 | 82.3314 | 85.3384 | 80.7439 | 85.8047 | 83.2486 | 80.7987 | 87.4834 | 80.9261 | 83.4514 | 85.1248 | 84.4873 | 82.3029 | 82.824 | 84.469 | 84.7593 | 64.732 | 60.5853 | 70.5159 | 82.2176 | 83.6446 | 84.5131 | 84.5855 | 84.6108 | 83.1864 | 84.1518 | 80.0052 | 86.5196 | 82.5712 | 82.5942 | 80.9519 | 84.7473 | 83.3622 | 83.9985 | 85.9506 | 83.087 | 83.8248 | 84.8726 | 85.3441 | 82.0706 | 84.295 | 85.5118 | 86.674 | 81.9345 | 84.5164 | 84.6539 | 85.941 | 84.5213 | 86.4834 | 85.3944 | 86.8034 | 83.5638 | 85.9579 | 87.3024 | 93.9358 | 94.0266 | 93.8438
2022-09-07 18:37 | 0:12 | 60.291 | 59.9823 | 63.9424 | 80.3048 | 83.7868 | 81.7409 | 84.6976 | 80.5104 | 85.5412 | 82.968 | 80.6121 | 87.2402 | 80.5617 | 83.5621 | 84.8532 | 84.301 | 82.0268 | 82.7082 | 84.1912 | 84.4924 | 64.4458 | 60.2876 | 70.1899 | 81.9804 | 83.3923 | 84.2965 | 84.4555 | 84.3393 | 83.0786 | 83.9211 | 79.7191 | 86.3128 | 82.1137 | 82.3429 | 80.5159 | 84.5083 | 83.1045 | 83.7434 | 85.9136 | 82.8689 | 83.614 | 84.6012 | 85.1812 | 81.9312 | 84.0523 | 85.295 | 86.464 | 81.6094 | 84.2711 | 84.4339 | 86.14 | 84.1331 | 86.268 | 85.1916 | 86.691 | 83.2612 | 85.8945 | 87.1097 | 93.8749 | 94.0067 | 93.8387
2022-09-07 18:37 | 0:13 | 60.2561 | 59.6741 | 63.6935 | 80.0381 | 83.3537 | 81.5025 | 84.884 | 80.2247 | 85.3484 | 82.7687 | 80.4642 | 87.0282 | 80.2655 | 83.0971 | 84.7 | 84.0285 | 81.8585 | 82.279 | 84.2303 | 84.4577 | 64.1962 | 60.0051 | 69.9686 | 81.7341 | 83.027 | 84.3066 | 84.232 | 83.9263 | 82.8398 | 83.6577 | 79.4126 | 86.0855 | 81.9848 | 82.1776 | 80.1004 | 84.3962 | 82.9681 | 83.4842 | 85.6808 | 82.6786 | 83.4319 | 84.5952 | 85.157 | 81.7127 | 84.0456 | 85.1946 | 86.3644 | 81.3936 | 84.0438 | 84.3735 | 85.3762 | 84.1539 | 86.1957 | 84.8329 | 86.8431 | 83.0484 | 85.5616 | 87.1065 | 93.7844 | 93.9497 | 93.8069
2022-09-07 18:37 | 0:13 | 59.9612 | 59.4126 | 63.4045 | 79.7342 | 83.2376 | 81.3259 | 84.2591 | 79.8219 | 85.0852 | 82.5782 | 80.1818 | 86.9988 | 79.9197 | 82.8392 | 84.4433 | 83.7934 | 81.5444 | 82.0113 | 83.7546 | 84.2013 | 63.946 | 59.7022 | 69.7403 | 81.5981 | 82.8872 | 84.1234 | 83.9987 | 83.577 | 82.6904 | 83.4246 | 79.2581 | 85.7936 | 81.8868 | 82.136 | 80.0659 | 84.3866 | 82.6191 | 83.6196 | 85.6893 | 82.5693 | 83.0444 | 84.2841 | 84.9498 | 81.5162 | 83.8391 | 84.8575 | 86.1423 | 81.1218 | 84.0614 | 84.0565 | 85.696 | 83.5845 | 85.8222 | 84.8682 | 86.4942 | 82.9128 | 85.4884 | 86.8842 | 93.7384 | 93.8863 | 93.738
2022-09-07 18:37 | 0:13 | 59.7885 | 59.1514 | 63.0946 | 79.4855 | 82.9334 | 81.1701 | 84.1424 | 79.558 | 84.8414 | 82.2098 | 79.7407 | 86.8234 | 79.7773 | 82.8784 | 84.0228 | 83.5485 | 81.2618 | 82.1855 | 83.3926 | 84.1526 | 63.7115 | 59.444 | 69.4501 | 81.3231 | 82.5477 | 83.9821 | 83.8248 | 83.4322 | 82.3837 | 83.2005 | 78.9527 | 85.5383 | 81.5879 | 81.9051 | 79.843 | 83.974 | 82.3939 | 83.2202 | 85.5051 | 82.3533 | 82.9304 | 84.1273 | 84.9887 | 81.3403 | 83.6017 | 84.5953 | 86.04 | 80.8686 | 83.9927 | 84.0511 | 85.5952 | 83.4219 | 85.9112 | 84.5192 | 86.4619 | 82.6302 | 85.2452 | 86.7338 | 93.6239 | 93.7779 | 93.6622
2022-09-07 18:37 | 0:13 | 59.5564 | 58.894 | 62.828 | 79.4555 | 82.8975 | 80.9735 | 84.2119 | 79.272 | 84.724 | 82.1207 | 79.3407 | 86.5549 | 79.4014 | 82.5548 | 83.9953 | 83.2972 | 80.9283 | 82.0771 | 83.4421 | 83.8585 | 63.4796 | 59.1979 | 69.1872 | 81.0606 | 82.4128 | 83.608 | 83.614 | 83.3082 | 82.1432 | 83.0737 | 79.0395 | 85.3335 | 81.3831 | 81.6314 | 79.4072 | 83.7319 | 82.1124 | 83.1299 | 85.2454 | 82.049 | 82.6786 | 83.928 | 84.6003 | 81.1355 | 83.4915 | 84.3992 | 85.8543 | 80.7168 | 83.7351 | 83.7809 | 85.5102 | 83.2682 | 85.8796 | 84.1179 | 86.3368 | 82.5459 | 85.1193 | 86.6476 | 93.5185 | 93.7225 | 93.5492
2022-09-07 18:37 | 0:13 | 59.4886 | 58.6031 | 62.5445 | 79.0874 | 82.5796 | 80.4828 | 84.1886 | 79.0701 | 84.4869 | 81.9184 | 79.2334 | 86.2652 | 79.2123 | 81.783 | 83.7834 | 83.1669 | 80.8376 | 81.3919 | 83.0405 | 83.8757 | 63.2075 | 58.9134 | 68.9675 | 80.8323 | 82.1684 | 83.4625 | 83.4319 | 82.8392 | 81.9267 | 82.8263 | 78.5305 | 85.0793 | 81.2144 | 81.4623 | 79.2437 | 83.7936 | 82.0753 | 82.9562 | 85.1022 | 81.8754 | 82.6446 | 83.8242 | 84.4767 | 81.0032 | 83.2416 | 84.3907 | 85.8039 | 80.4838 | 83.695 | 83.5881 | 85.1963 | 83.0647 | 85.8123 | 83.9362 | 86.0038 | 82.3064 | 84.8124 | 86.5957 | 93.4308 | 93.6429 | 93.5974
2022-09-07 18:38 | 0:14 | 59.3193 | 58.3525 | 62.2701 | 78.8592 | 82.1966 | 80.3431 | 83.9194 | 78.8179 | 84.2767 | 81.486 | 78.823 | 86.2009 | 79.0218 | 81.9312 | 83.4732 | 82.8138 | 80.5384 | 81.0695 | 82.9104 | 83.4105 | 62.9691 | 58.6379 | 68.763 | 80.6525 | 81.8148 | 83.4143 | 83.0444 | 83.0367 | 81.4699 | 82.7084 | 78.1236 | 84.8193 | 80.936 | 81.1922 | 78.9395 | 83.5094 | 81.7772 | 82.7418 | 85.202 | 81.5872 | 82.4152 | 83.4719 | 84.411 | 80.823 | 83.0603 | 84.1449 | 85.6762 | 80.33 | 83.3764 | 83.4258 | 85.227 | 82.74 | 85.6859 | 83.8507 | 86.0883 | 82.0441 | 84.7567 | 86.4344 | 93.3574 | 93.4872 | 93.4661
2022-09-07 18:38 | 0:14 | 58.9976 | 58.1062 | 61.9791 | 78.5172 | 81.9891 | 80.2433 | 83.5686 | 78.5149 | 84.0546 | 81.4352 | 79.1278 | 86.0629 | 78.7697 | 81.8902 | 83.1418 | 82.4786 | 80.2899 | 80.9866 | 82.5879 | 83.2056 | 62.7581 | 58.4144 | 68.5321 | 80.3106 | 81.6861 | 83.1386 | 82.9304 | 82.7254 | 81.5476 | 82.5459 | 77.9081 | 84.6586 | 80.723 | 80.97 | 78.7089 | 83.402 | 81.5092 | 82.653 | 84.5695 | 81.4879 | 82.225 | 83.2463 | 84.2367 | 80.6082 | 82.9519 | 83.9386 | 85.2414 | 80.0746 | 83.3408 | 83.1381 | 85.1311 | 82.5579 | 85.7031 | 83.4949 | 85.5101 | 81.7911 | 84.6895 | 86.2301 | 93.2497 | 93.4202 | 93.42
2022-09-07 18:38 | 0:14 | 58.8528 | 57.8909 | 61.7864 | 78.4732 | 81.8077 | 80.3089 | 83.6712 | 78.3319 | 83.6891 | 81.2122 | 78.2991 | 85.7724 | 78.2297 | 81.6543 | 82.8658 | 82.2167 | 80.0706 | 80.5681 | 82.3864 | 83.2392 | 62.5421 | 58.1686 | 68.3054 | 80.1565 | 81.4333 | 82.834 | 82.6786 | 82.507 | 81.0542 | 82.3463 | 77.9762 | 84.4876 | 80.4121 | 80.8571 | 78.2455 | 83.1441 | 81.344 | 82.421 | 84.1452 | 81.1991 | 81.8812 | 83.1923 | 83.8873 | 80.318 | 82.7171 | 83.7314 | 85.0418 | 79.8343 | 83.1467 | 82.894 | 84.8323 | 82.4049 | 85.4525 | 83.4404 | 86.0058 | 81.6669 | 84.3958 | 86.0626 | 93.1427 | 93.2592 | 93.3255
2022-09-07 18:38 | 0:14 | 58.8125 | 57.6502 | 61.5548 | 78.1415 | 81.4826 | 79.9019 | 83.5433 | 77.9409 | 83.616 | 80.9474 | 78.3226 | 85.6797 | 78.1492 | 81.4486 | 82.6762 | 81.9275 | 79.8342 | 80.7806 | 82.068 | 82.8699 | 62.3403 | 57.9572 | 68.09 | 79.868 | 81.0451 | 82.733 | 82.6446 | 81.8603 | 81.0887 | 81.9874 | 77.4987 | 84.2872 | 80.1633 | 80.4703 | 77.9943 | 82.9375 | 81.1639 | 82.2356 | 84.0119 | 81.0162 | 81.9431 | 82.9009 | 83.914 | 80.1297 | 82.494 | 83.4954 | 84.948 | 79.6386 | 83.0233 | 82.8371 | 85.0269 | 82.2042 | 85.347 | 83.0995 | 85.7421 | 81.414 | 84.0969 | 86.0924 | 92.992 | 93.1643 | 93.2189
2022-09-07 18:38 | 0:14 | 58.7098 | 57.413 | 61.3801 | 77.9631 | 81.3771 | 79.5922 | 82.9892 | 77.7735 | 83.3672 | 80.5523 | 78.0891 | 85.5473 | 77.7838 | 80.7381 | 82.6802 | 81.735 | 79.5421 | 80.1209 | 81.7698 | 82.6687 | 62.1227 | 57.6838 | 67.8649 | 79.7131 | 80.835 | 82.6952 | 82.4152 | 82.1058 | 80.646 | 81.8629 | 77.4153 | 84.0559 | 79.9043 | 80.3416 | 77.9104 | 82.8343 | 80.9083 | 81.8303 | 83.7965 | 80.7458 | 81.6792 | 82.882 | 83.5712 | 79.8183 | 82.3393 | 83.3327 | 84.6288 | 79.524 | 82.8243 | 82.7246 | 84.8149 | 81.893 | 85.1388 | 82.653 | 85.4686 | 81.1883 | 83.9961 | 85.8221 | 92.8667 | 93.0333 | 93.1541
2022-09-07 18:38 | 0:14 | 58.5724 | 57.1754 | 61.1944 | 77.5711 | 81.1253 | 79.1737 | 82.6745 | 77.6471 | 83.2275 | 80.2541 | 78.0617 | 85.3453 | 77.5082 | 80.775 | 82.2986 | 81.5748 | 79.3276 | 80.0008 | 81.5892 | 82.2353 | 61.9114 | 57.4705 | 67.6595 | 79.5458 | 80.5935 | 82.3303 | 82.225 | 81.8617 | 80.4193 | 81.8581 | 77.2998 | 83.8893 | 79.6896 | 80.1624 | 77.642 | 82.5942 | 80.7234 | 81.5932 | 83.9351 | 80.6057 | 81.3968 | 82.5227 | 83.5208 | 79.683 | 82.2873 | 83.075 | 84.4041 | 79.4575 | 82.7411 | 82.381 | 84.8844 | 81.564 | 84.9574 | 82.5631 | 85.5044 | 80.9441 | 83.8315 | 85.6266 | 92.7493 | 92.865 | 93.0964
2022-09-07 18:39 | 0:14 | 58.3841 | 56.9455 | 60.9535 | 77.4817 | 80.9334 | 79.1054 | 82.575 | 77.1778 | 83.0106 | 80.1353 | 77.5399 | 85.1142 | 77.1835 | 80.6944 | 81.9586 | 81.3633 | 79.0682 | 80.0306 | 81.3623 | 81.7252 | 61.7227 | 57.2502 | 67.4635 | 79.2533 | 80.4253 | 82.1548 | 81.8812 | 81.5055 | 80.2386 | 81.4826 | 76.9902 | 83.6957 | 79.3278 | 79.9853 | 77.2961 | 82.3186 | 80.5092 | 81.5316 | 83.643 | 80.3129 | 81.2397 | 82.4776 | 83.4277 | 79.5789 | 82.0275 | 82.9875 | 84.351 | 79.0872 | 82.4976 | 82.2524 | 84.4031 | 81.4003 | 84.8657 | 82.2661 | 85.2355 | 80.8372 | 83.694 | 85.3249 | 92.6386 | 92.7487 | 93.0109
2022-09-07 18:39 | 0:15 | 58.1792 | 56.749 | 60.7691 | 77.2723 | 80.7296 | 78.7836 | 82.6291 | 77.0304 | 82.8072 | 79.7959 | 77.4744 | 84.9655 | 76.8959 | 80.3352 | 81.7482 | 81.143 | 78.8247 | 79.5737 | 81.126 | 81.9072 | 61.5041 | 57.0486 | 67.2356 | 79.0801 | 80.1579 | 82.0202 | 81.9431 | 80.9399 | 79.8905 | 81.2983 | 76.8782 | 83.4657 | 79.2971 | 79.9329 | 76.8172 | 82.3223 | 80.2654 | 81.4141 | 83.7363 | 80.0696 | 81.0085 | 82.2532 | 83.2611 | 79.3431 | 81.884 | 82.8011 | 84.0692 | 78.9583 | 82.2095 | 81.8974 | 84.1887 | 81.4443 | 84.5692 | 82.121 | 84.9036 | 80.6689 | 83.4777 | 85.3376 | 92.4954 | 92.6419 | 92.8583
2022-09-07 18:39 | 0:15 | 58.1152 | 56.5758 | 60.5466 | 77.1559 | 80.509 | 78.5647 | 82.0833 | 76.6094 | 82.6152 | 79.7731 | 77.2116 | 84.8234 | 76.8417 | 79.5755 | 81.6067 | 80.917 | 78.5959 | 79.3859 | 80.9835 | 81.5115 | 61.2978 | 56.8422 | 67.0296 | 78.8426 | 79.911 | 81.9286 | 81.6792 | 81.0827 | 79.6986 | 81.401 | 76.4659 | 83.0856 | 79.187 | 79.5375 | 76.7794 | 82.0239 | 80.1717 | 80.9751 | 83.3946 | 79.9325 | 80.8448 | 81.9441 | 83.0088 | 79.0597 | 81.6508 | 82.5404 | 84.0945 | 78.6008 | 82.2584 | 81.7946 | 84.2293 | 81.1628 | 84.505 | 82.0429 | 84.912 | 80.4102 | 83.3893 | 85.3665 | 92.3256 | 92.4716 | 92.7873
2022-09-07 18:39 | 0:15 | 58.0391 | 56.3562 | 60.4236 | 76.9671 | 80.1351 | 78.2546 | 82.2554 | 76.4599 | 82.3406 | 79.923 | 77.2013 | 84.6419 | 76.7342 | 79.9864 | 81.1866 | 80.6806 | 78.3438 | 79.2506 | 80.6978 | 81.6738 | 61.0613 | 56.6288 | 66.755 | 78.6402 | 79.68 | 81.7488 | 81.3968 | 80.5937 | 79.683 | 81.0478 | 76.1432 | 83.1355 | 78.7085 | 79.2878 | 76.5904 | 81.7903 | 79.9792 | 80.9122 | 83.7917 | 79.6704 | 80.6466 | 81.7713 | 82.8501 | 79.0396 | 81.5257 | 82.295 | 83.8782 | 78.4863 | 82.0537 | 81.4581 | 83.9349 | 80.9126 | 84.2778 | 81.4102 | 84.5005 | 80.1102 | 83.3483 | 85.1193 | 92.1325 | 92.2906 | 92.6984
2022-09-07 18:39 | 0:15 | 57.9735 | 56.1888 | 60.3074 | 76.5652 | 80.0789 | 78.0694 | 82.0815 | 76.2449 | 82.1306 | 79.4147 | 76.9829 | 84.4402 | 76.4364 | 79.975 | 81.075 | 80.4354 | 78.0884 | 78.9792 | 80.5581 | 81.1368 | 60.817 | 56.4435 | 66.5368 | 78.4841 | 79.4559 | 81.6372 | 81.2397 | 80.8303 | 79.4136 | 80.8536 | 75.9742 | 82.8112 | 78.4977 | 79.2192 | 76.4816 | 81.7884 | 79.9591 | 80.831 | 83.4333 | 79.5411 | 80.4265 | 81.5815 | 82.7035 | 78.749 | 81.3477 | 82.1032 | 83.7779 | 78.2396 | 81.7903 | 81.4117 | 83.9752 | 81.0955 | 84.1334 | 81.4782 | 84.7856 | 79.9007 | 83.1312 | 85.0195 | 91.9938 | 92.0668 | 92.5242
2022-09-07 18:39 | 0:15 | 57.9275 | 55.9856 | 60.1231 | 76.2535 | 79.7595 | 78.1873 | 81.723 | 75.9548 | 81.8562 | 79.332 | 76.1694 | 84.1786 | 76.2084 | 79.9258 | 80.9077 | 80.05 | 77.8613 | 78.9663 | 80.284 | 80.8183 | 60.6067 | 56.2472 | 66.3077 | 78.2007 | 79.2294 | 81.6088 | 81.0085 | 80.383 | 79.2214 | 80.5888 | 75.7768 | 82.6853 | 78.3451 | 78.9479 | 76.1926 | 81.6889 | 79.6508 | 80.5009 | 82.35 | 79.3689 | 80.1728 | 81.4437 | 82.5831 | 78.4949 | 81.2668 | 81.9439 | 83.656 | 78.0941 | 81.7099 | 81.2146 | 83.532 | 80.6595 | 83.7928 | 81.4316 | 84.2089 | 79.7967 | 82.9304 | 84.722 | 91.8904 | 91.8295 | 92.3809
2022-09-07 18:40 | 0:16 | 57.8564 | 55.8144 | 59.9932 | 76.2823 | 79.6583 | 77.6031 | 81.4294 | 75.7946 | 81.7481 | 78.8855 | 76.3888 | 83.8561 | 75.8535 | 79.5334 | 80.5838 | 79.8249 | 77.65 | 79.4291 | 80.2438 | 80.7726 | 60.4043 | 56.0622 | 66.1073 | 77.9881 | 78.9429 | 81.3858 | 80.8448 | 80.214 | 78.7429 | 80.5069 | 75.5578 | 82.4091 | 78.1973 | 78.9077 | 75.9022 | 81.2256 | 79.389 | 80.3273 | 82.6098 | 79.0463 | 80.2071 | 81.2345 | 82.5806 | 78.3087 | 80.8997 | 81.7056 | 83.3698 | 77.9767 | 81.4077 | 81.0327 | 82.8443 | 80.5814 | 83.6831 | 81.1639 | 83.975 | 79.5064 | 82.6365 | 84.6 | 91.6674 | 91.6268 | 92.2135
2022-09-07 18:40 | 0:16 | 57.7633 | 55.6061 | 59.8129 | 75.9689 | 79.351 | 77.3681 | 81.2569 | 75.7294 | 81.5747 | 78.815 | 76.4102 | 83.7358 | 75.7473 | 78.9063 | 80.1877 | 79.6864 | 77.4631 | 78.3701 | 79.8284 | 80.825 | 60.1962 | 55.83 | 65.8889 | 77.8944 | 78.7206 | 81.0824 | 80.6466 | 80.2412 | 78.5482 | 80.1716 | 75.1746 | 81.9921 | 78.0078 | 78.7266 | 75.6239 | 80.9989 | 79.2942 | 80.0927 | 82.6026 | 78.8724 | 79.8608 | 81.0775 | 82.267 | 78.0904 | 80.914 | 81.4848 | 83.1105 | 77.6134 | 81.1651 | 80.7695 | 83.1115 | 80.3043 | 83.5626 | 80.9361 | 84.3518 | 79.4254 | 82.4484 | 84.3846 | 91.6965 | 91.6128 | 92.2854
2022-09-07 18:40 | 0:16 | 57.6653 | 55.4404 | 59.5995 | 75.7037 | 79.2472 | 76.9513 | 80.7915 | 75.4693 | 81.3273 | 78.6342 | 75.9771 | 83.6428 | 75.3769 | 78.8656 | 80.1633 | 79.5066 | 77.1751 | 78.4022 | 79.7942 | 80.5379 | 59.9853 | 55.6336 | 65.6719 | 77.6599 | 78.4729 | 80.924 | 80.4265 | 79.8818 | 78.326 | 80.0805 | 74.963 | 81.9908 | 77.7081 | 78.313 | 75.1084 | 80.6274 | 78.9178 | 79.8531 | 82.4968 | 78.6552 | 79.6554 | 80.8962 | 82.1416 | 77.7868 | 80.631 | 81.3585 | 83.0505 | 77.683 | 80.8501 | 80.5835 | 82.8233 | 80.2686 | 83.2814 | 80.849 | 83.7763 | 79.1434 | 82.0455 | 84.2235 | 91.7539 | 91.6742 | 92.4354
2022-09-07 18:40 | 0:16 | 57.5665 | 55.283 | 59.4216 | 75.5548 | 78.9412 | 76.783 | 80.724 | 75.0956 | 81.1288 | 78.452 | 75.7384 | 83.473 | 75.2944 | 78.9885 | 79.9136 | 79.1794 | 76.9794 | 77.9471 | 79.518 | 80.182 | 59.7995 | 55.4439 | 65.5281 | 77.4499 | 78.1762 | 80.7464 | 80.1728 | 79.5858 | 78.0844 | 79.8828 | 74.8847 | 81.6518 | 77.3555 | 78.1575 | 75.1123 | 80.627 | 78.6731 | 79.571 | 82.2118 | 78.4835 | 79.452 | 80.6402 | 81.9128 | 77.718 | 80.4077 | 81.2148 | 83.0092 | 77.2704 | 80.8771 | 80.3808 | 82.9851 | 79.7506 | 83.2707 | 80.4904 | 83.6315 | 78.8978 | 81.9735 | 84.1295 | 91.8268 | 91.808 | 92.5094
2022-09-07 18:40 | 0:16 | 57.4681 | 55.1337 | 59.2421 | 75.3353 | 78.7189 | 76.8713 | 80.388 | 74.9114 | 80.8331 | 78.0367 | 75.6169 | 83.1907 | 75.0129 | 78.6111 | 79.7649 | 78.951 | 76.6941 | 77.9545 | 79.2575 | 79.927 | 59.644 | 55.2993 | 65.3533 | 77.1494 | 77.9721 | 80.5547 | 80.2071 | 78.9861 | 78.0506 | 79.7269 | 74.6969 | 81.5074 | 77.0624 | 78.1492 | 75.0159 | 80.4339 | 78.4838 | 79.4509 | 82.0845 | 78.2001 | 79.4159 | 80.5083 | 81.6146 | 77.5407 | 80.2576 | 81.0019 | 82.5399 | 77.1188 | 80.8192 | 80.326 | 82.7834 | 79.7748 | 82.9665 | 80.2161 | 83.6791 | 78.7557 | 81.7477 | 84.0965 | 91.926 | 91.9307 | 92.462
2022-09-07 18:40 | 0:16 | 57.3396 | 54.9626 | 59.124 | 75.1466 | 78.4206 | 76.5396 | 80.4271 | 74.5797 | 80.6442 | 77.6715 | 75.2682 | 83.0504 | 74.8008 | 78.1924 | 79.5543 | 78.7085 | 76.5513 | 77.6549 | 79.0036 | 79.6895 | 59.4768 | 55.1174 | 65.1592 | 77.0934 | 77.7841 | 80.5467 | 79.8608 | 79.0636 | 77.9508 | 79.5305 | 74.4946 | 81.3966 | 76.8787 | 77.8336 | 74.5392 | 80.2281 | 78.3035 | 79.2619 | 81.9162 | 78.0887 | 79.1654 | 80.229 | 81.5462 | 77.2905 | 80.0331 | 80.8825 | 82.7363 | 76.9053 | 80.6592 | 80.2155 | 82.8231 | 79.5027 | 82.9992 | 80.0897 | 83.5601 | 78.6109 | 81.8781 | 83.5702 | 92.019 | 92.0518 | 92.6661
2022-09-07 18:41 | 0:16 | 57.1598 | 54.8007 | 58.9106 | 74.9587 | 78.3528 | 76.3212 | 80.4577 | 74.2056 | 80.4026 | 77.6714 | 75.1652 | 82.9321 | 74.4771 | 78.2137 | 79.4305 | 78.5016 | 76.3424 | 77.3353 | 78.8661 | 79.207 | 59.3285 | 54.9522 | 64.9803 | 76.7545 | 77.5283 | 80.3256 | 79.6554 | 78.9468 | 77.6885 | 79.4284 | 74.2612 | 81.1796 | 76.8179 | 77.6113 | 74.2763 | 80.2825 | 78.0254 | 79.0134 | 81.9684 | 77.9434 | 79.0703 | 80.0472 | 81.4099 | 77.2509 | 79.8208 | 80.6484 | 82.3985 | 76.7136 | 81.119 | 79.8901 | 82.5585 | 79.0719 | 82.9671 | 79.8315 | 83.4909 | 78.4524 | 81.6397 | 83.7958 | 92.0961 | 92.1789 | 92.6252
2022-09-07 18:41 | 0:17 | 57.031 | 54.6281 | 58.7555 | 74.8289 | 78.0687 | 76.3914 | 80.1669 | 74.0161 | 80.2945 | 77.4055 | 74.7911 | 82.7728 | 74.3452 | 77.8927 | 79.0365 | 78.3021 | 76.0587 | 77.5956 | 78.7549 | 79.4763 | 59.1324 | 54.7684 | 64.8201 | 76.6291 | 77.201 | 80.1635 | 79.452 | 78.8125 | 77.2948 | 79.2331 | 74.1389 | 80.8249 | 76.6427 | 77.4578 | 74.0194 | 79.9703 | 77.7267 | 78.8729 | 81.687 | 77.7039 | 78.9004 | 79.9677 | 81.0631 | 77.0361 | 79.856 | 80.4858 | 82.2785 | 76.6165 | 80.6423 | 79.6172 | 82.5018 | 79.0332 | 82.5349 | 79.802 | 83.1359 | 78.1022 | 81.3479 | 83.426 | 92.2205 | 92.3094 | 92.7179
2022-09-07 18:41 | 0:17 | 56.8482 | 54.4683 | 58.5676 | 74.7161 | 78.0194 | 75.862 | 79.9209 | 73.9476 | 80.0675 | 77.311 | 74.5958 | 82.4561 | 73.9496 | 77.9443 | 78.8615 | 78.0409 | 75.8642 | 77.2731 | 78.5603 | 79.0944 | 58.9559 | 54.5589 | 64.5952 | 76.3181 | 76.9959 | 79.9694 | 79.4159 | 78.5356 | 77.2001 | 78.9507 | 73.7823 | 80.7291 | 76.4109 | 77.1733 | 73.8467 | 79.5368 | 77.6387 | 78.6586 | 81.6242 | 77.4567 | 78.5734 | 79.7172 | 80.8814 | 76.8122 | 79.7183 | 80.2416 | 82.0216 | 76.3211 | 80.4368 | 79.5234 | 82.3119 | 78.6796 | 82.5859 | 79.3444 | 83.07 | 77.9763 | 81.128 | 83.2297 | 92.3024 | 92.4015 | 92.7827
2022-09-07 18:41 | 0:17 | 56.6828 | 54.3311 | 58.394 | 74.3202 | 77.7252 | 75.7879 | 79.9028 | 73.7244 | 79.8846 | 77.0023 | 74.8775 | 82.3189 | 73.9229 | 77.7575 | 78.5154 | 77.7874 | 75.7216 | 76.8864 | 78.1025 | 79.0385 | 58.7886 | 54.4436 | 64.382 | 76.2087 | 76.8428 | 79.7638 | 79.1654 | 77.9599 | 76.5952 | 78.7904 | 73.6556 | 80.5304 | 76.1346 | 77.0164 | 73.7157 | 79.3267 | 77.7197 | 78.4827 | 80.9888 | 77.3441 | 78.3195 | 79.5647 | 80.7456 | 76.5864 | 79.4373 | 80.1173 | 81.8785 | 76.2334 | 80.1664 | 79.3273 | 82.0644 | 78.4003 | 82.4609 | 79.1368 | 82.9073 | 77.645 | 81.1061 | 83.1374 | 92.3823 | 92.4997 | 92.8317
2022-09-07 18:41 | 0:17 | 56.5108 | 54.145 | 58.2086 | 74.2374 | 77.5111 | 75.4397 | 79.6304 | 73.5206 | 79.6223 | 76.7867 | 74.4129 | 82.112 | 73.6713 | 77.6931 | 78.5125 | 77.5873 | 75.582 | 76.7754 | 77.9223 | 78.6935 | 58.6061 | 54.208 | 64.176 | 76.0516 | 76.5949 | 79.5032 | 79.0703 | 77.9282 | 76.4082 | 78.5475 | 73.3656 | 80.3403 | 75.931 | 76.7682 | 73.4401 | 79.0502 | 77.5797 | 78.1307 | 80.9608 | 77.1513 | 78.2301 | 79.4696 | 80.614 | 76.5317 | 79.2656 | 79.798 | 81.5753 | 76.0073 | 79.8278 | 79.1792 | 81.7954 | 78.081 | 82.2954 | 78.8527 | 82.6785 | 77.5605 | 80.9013 | 83.0349 | 92.5484 | 92.601 | 92.8836
2022-09-07 18:41 | 0:17 | 56.3401 | 53.9736 | 58.0645 | 73.9583 | 77.3391 | 75.5252 | 79.3451 | 73.1445 | 79.4327 | 76.3833 | 74.1131 | 82.0737 | 73.3792 | 77.2925 | 78.1793 | 77.338 | 75.3852 | 76.6946 | 77.6022 | 78.5402 | 58.4334 | 54.0541 | 64.0083 | 75.8811 | 76.3427 | 79.468 | 78.9004 | 78.1303 | 76.3452 | 78.4738 | 72.9741 | 79.9083 | 75.725 | 76.6598 | 73.4358 | 78.6847 | 77.553 | 77.9495 | 81.0921 | 77.0169 | 78.0685 | 79.093 | 80.2868 | 76.3695 | 79.1078 | 79.6642 | 81.7382 | 75.7718 | 79.8731 | 78.9047 | 81.8907 | 77.9432 | 82.1559 | 78.6187 | 82.6466 | 77.4011 | 80.7138 | 82.4962 | 92.6028 | 92.6622 | 92.9173
2022-09-07 18:42 | 0:18 | 56.1582 | 53.808 | 57.8792 | 73.9219 | 77.1856 | 75.2938 | 79.5199 | 73.0996 | 79.2425 | 76.2572 | 73.9867 | 81.7203 | 73.3311 | 77.0152 | 77.9338 | 77.2885 | 75.1224 | 76.6153 | 77.4698 | 78.461 | 58.2807 | 53.8615 | 63.864 | 75.7124 | 76.144 | 79.4 | 78.5734 | 77.585 | 76.0935 | 78.2488 | 72.8168 | 79.8092 | 75.5233 | 76.5838 | 73.1247 | 78.6308 | 77.1024 | 78.005 | 80.3754 | 76.7455 | 77.7632 | 79.0852 | 80.5486 | 76.069 | 78.9525 | 79.4254 | 81.3882 | 75.426 | 79.6414 | 78.7179 | 81.6155 | 77.6741 | 81.7902 | 78.4792 | 82.4724 | 77.2458 | 80.5282 | 82.3096 | 92.8477 | 92.7784 | 93.061
2022-09-07 18:42 | 0:18 | 55.9485 | 53.6412 | 57.6977 | 73.71 | 76.9169 | 75.0063 | 79.2507 | 72.6876 | 78.9762 | 76.0749 | 73.4877 | 81.4557 | 72.9444 | 76.9334 | 77.8982 | 76.9596 | 74.9974 | 76.432 | 77.2084 | 78.5289 | 58.0976 | 53.6788 | 63.6629 | 75.5302 | 75.939 | 79.2189 | 78.3195 | 77.563 | 75.9496 | 78.0784 | 72.6358 | 79.6394 | 75.3041 | 76.3277 | 72.9989 | 78.3903 | 76.9169 | 77.7371 | 80.2855 | 76.6309 | 77.656 | 78.9553 | 80.6069 | 75.9176 | 78.7252 | 79.3466 | 81.3558 | 75.4098 | 79.3811 | 78.5583 | 81.2553 | 77.3713 | 81.6173 | 78.4799 | 82.3008 | 76.9064 | 80.2068 | 82.3478 | 92.9025 | 92.9485 | 93.1389
2022-09-07 18:42 | 0:18 | 55.7183 | 53.469 | 57.485 | 73.5791 | 76.7671 | 74.4751 | 78.5353 | 72.6693 | 78.7543 | 75.7991 | 73.7952 | 81.4124 | 72.8847 | 76.4102 | 77.5563 | 76.8801 | 74.6188 | 75.6383 | 77.1357 | 78.2568 | 57.9136 | 53.4977 | 63.4258 | 75.3435 | 75.6393 | 79.1539 | 78.2301 | 77.4523 | 75.5813 | 77.9095 | 72.5518 | 79.4453 | 75.1065 | 76.0393 | 72.7969 | 78.6982 | 76.6389 | 77.4129 | 79.3291 | 76.3227 | 77.4596 | 78.6818 | 80.231 | 75.7259 | 78.516 | 79.2322 | 81.1209 | 75.2699 | 79.4798 | 78.4896 | 81.4552 | 77.4079 | 81.716 | 78.0417 | 82.0909 | 76.6877 | 80.2868 | 82.2274 | 92.9945 | 93.1209 | 93.2201
2022-09-07 18:42 | 0:18 | 55.5417 | 53.3264 | 57.3131 | 73.4209 | 76.6401 | 74.3517 | 78.2572 | 72.3326 | 78.6035 | 75.8351 | 73.1237 | 81.2294 | 72.5918 | 76.0598 | 77.3561 | 76.5922 | 74.5321 | 75.5538 | 76.9303 | 77.7781 | 57.7567 | 53.3603 | 63.2969 | 75.0929 | 75.4002 | 78.9157 | 78.0685 | 77.0677 | 75.3733 | 77.6541 | 72.4976 | 79.2588 | 74.9912 | 75.8205 | 72.5591 | 78.2084 | 76.449 | 77.3965 | 79.7077 | 76.1467 | 77.2603 | 78.4448 | 80.2106 | 75.4735 | 78.3585 | 78.9485 | 81.0642 | 75.013 | 79.1987 | 78.231 | 81.1503 | 77.1244 | 81.4975 | 77.9514 | 81.8965 | 76.5855 | 80.0235 | 82.1852 | 93.16 | 93.2497 | 93.291
2022-09-07 18:42 | 0:18 | 55.3238 | 53.1586 | 57.1589 | 73.0897 | 76.4818 | 73.9116 | 78.2678 | 72.2498 | 78.4154 | 75.6461 | 73.0104 | 81.0652 | 72.4273 | 75.9437 | 77.422 | 76.4109 | 74.3785 | 75.8445 | 76.751 | 77.5909 | 57.5822 | 53.1591 | 63.1209 | 74.876 | 75.2898 | 78.759 | 77.7632 | 77.3411 | 75.3793 | 77.5593 | 72.3787 | 79.0697 | 74.8675 | 75.6191 | 72.0386 | 77.7153 | 76.2164 | 77.2168 | 79.6396 | 75.847 | 77.0366 | 78.2866 | 79.8035 | 75.2667 | 78.2271 | 78.708 | 81.0847 | 74.8861 | 79.0685 | 78.1326 | 81.1759 | 77.0159 | 81.1677 | 77.524 | 81.6462 | 76.4982 | 79.7423 | 82.1012 | 93.4526 | 93.368 | 93.4537
2022-09-07 18:42 | 0:18 | 55.1142 | 52.9232 | 56.9364 | 72.899 | 76.1497 | 74.1326 | 78.408 | 72.0121 | 78.291 | 75.6524 | 73.0423 | 80.8563 | 72.3112 | 76.0774 | 76.8146 | 76.2823 | 74.1442 | 75.5533 | 76.5407 | 77.2734 | 57.3974 | 52.9465 | 62.9102 | 74.7262 | 75.0795 | 78.4048 | 77.656 | 76.9078 | 75.2101 | 77.193 | 71.9314 | 78.8066 | 74.734 | 75.3786 | 72.2326 | 77.6008 | 76.227 | 77.048 | 79.0923 | 75.7231 | 76.7913 | 78.1342 | 79.4872 | 75.0925 | 78.0702 | 78.5031 | 80.6463 | 74.6264 | 78.8842 | 77.9085 | 80.9548 | 76.8568 | 80.7827 | 77.5291 | 81.3824 | 76.3658 | 79.4984 | 81.8883 | 93.5559 | 93.5403 | 93.484
2022-09-07 18:43 | 0:18 | 54.8973 | 52.7616 | 56.7226 | 72.7566 | 76.0065 | 73.8673 | 77.6491 | 71.9148 | 77.9838 | 75.2482 | 72.992 | 80.6228 | 71.898 | 75.5947 | 76.9677 | 76.0923 | 73.8684 | 75.4911 | 76.3372 | 77.5169 | 57.1958 | 52.7907 | 62.6971 | 74.5661 | 74.8266 | 78.3141 | 77.4596 | 76.1792 | 74.9462 | 77.1829 | 71.6941 | 78.5651 | 74.4159 | 75.3075 | 71.8533 | 77.4816 | 75.9657 | 76.834 | 78.9959 | 75.5618 | 76.5656 | 77.9927 | 79.4737 | 75.0662 | 77.9331 | 78.4196 | 80.3446 | 74.3977 | 78.5583 | 77.5847 | 80.7828 | 76.7946 | 80.8325 | 77.2136 | 81.5046 | 76.1009 | 79.4134 | 81.5513 | 93.6132 | 93.6762 | 93.5647
2022-09-07 18:43 | 0:19 | 54.7061 | 52.5924 | 56.5238 | 72.6551 | 75.6677 | 73.8101 | 77.7721 | 71.5933 | 77.8134 | 74.8537 | 72.4703 | 80.467 | 71.8059 | 75.4754 | 76.7571 | 75.9105 | 73.679 | 75.0729 | 75.8606 | 77.0799 | 56.9613 | 52.5742 | 62.4747 | 74.252 | 74.5484 | 78.0523 | 77.2603 | 76.5172 | 74.8666 | 76.9666 | 71.6494 | 78.5465 | 74.2217 | 75.1228 | 71.4189 | 77.5182 | 75.7037 | 76.6207 | 78.9721 | 75.2486 | 76.4984 | 77.8709 | 79.3776 | 74.8167 | 77.7175 | 78.2862 | 80.1135 | 74.172 | 78.466 | 77.5266 | 80.8101 | 76.6208 | 80.7747 | 76.9014 | 81.0197 | 75.797 | 79.1965 | 81.4399 | 93.7895 | 93.7798 | 93.5917
2022-09-07 18:43 | 0:19 | 54.4656 | 52.4183 | 56.3475 | 72.3731 | 75.4511 | 73.4485 | 77.5529 | 71.4289 | 77.6277 | 74.8175 | 72.615 | 80.3312 | 71.6347 | 75.4585 | 76.521 | 75.6231 | 73.5458 | 74.8148 | 75.7523 | 76.8017 | 56.7583 | 52.4112 | 62.2924 | 74.2672 | 74.4294 | 77.8414 | 77.0366 | 76.3675 | 74.5574 | 76.6822 | 71.3026 | 78.102 | 73.8809 | 74.8694 | 71.4294 | 76.9828 | 75.4954 | 76.4833 | 78.9039 | 75.2703 | 76.2789 | 77.5747 | 79.0345 | 74.5433 | 77.5474 | 78.085 | 80.0444 | 74.1837 | 78.2023 | 77.2411 | 80.7105 | 76.2141 | 80.6263 | 76.734 | 80.796 | 75.7447 | 79.173 | 81.3565 | 93.9362 | 93.8947 | 93.6686
2022-09-07 18:43 | 0:19 | 54.2597 | 52.2651 | 56.1441 | 72.2773 | 75.3268 | 73.2398 | 77.2993 | 71.2708 | 77.4363 | 74.49 | 72.2518 | 80.2341 | 71.4579 | 74.9432 | 76.2877 | 75.3748 | 73.3578 | 74.6888 | 75.5776 | 76.6147 | 56.5779 | 52.2336 | 62.0909 | 73.9775 | 74.1644 | 77.8481 | 76.7913 | 76.2251 | 74.322 | 76.597 | 70.9044 | 78.2062 | 73.7176 | 74.7838 | 71.4796 | 77.0034 | 75.4031 | 76.3797 | 78.3759 | 75.0396 | 76.1728 | 77.3378 | 78.8512 | 74.3521 | 77.4079 | 77.8319 | 79.8614 | 73.9433 | 77.8823 | 77.0667 | 80.5141 | 76.4919 | 80.4374 | 76.6555 | 80.6095 | 75.4337 | 78.9262 | 81.038 | 94.0993 | 94.0675 | 93.7579
2022-09-07 18:43 | 0:19 | 54.0714 | 52.0666 | 55.9417 | 71.8386 | 75.1589 | 72.7818 | 77.5829 | 71.0598 | 77.311 | 74.4921 | 72.135 | 80.0598 | 71.1564 | 75.1426 | 76.0945 | 75.1318 | 73.1357 | 74.3175 | 75.364 | 76.4584 | 56.3871 | 52.0613 | 61.9087 | 73.7245 | 73.9385 | 77.6997 | 76.5656 | 76.1705 | 74.1163 | 76.4302 | 70.85 | 77.8458 | 73.7282 | 74.6051 | 70.9351 | 76.7283 | 75.1609 | 76.1325 | 78.5499 | 74.8325 | 75.8754 | 77.1939 | 78.9264 | 74.1667 | 77.3462 | 77.6434 | 79.7612 | 73.6562 | 77.8284 | 76.9475 | 79.9948 | 76.1346 | 80.019 | 76.5319 | 80.7381 | 75.2867 | 78.5062 | 80.9678 | 94.2098 | 94.2733 | 93.8398
2022-09-07 18:43 | 0:19 | 53.8831 | 51.9006 | 55.8043 | 71.6486 | 74.9824 | 72.6105 | 76.9215 | 70.8257 | 77.1459 | 74.257 | 72.0704 | 79.7455 | 71.058 | 74.7545 | 75.8795 | 74.9661 | 72.8424 | 74.3003 | 75.3022 | 76.2561 | 56.1934 | 51.8593 | 61.701 | 73.5512 | 73.7306 | 77.53 | 76.4984 | 75.9109 | 73.8763 | 76.2611 | 70.6988 | 77.4891 | 73.5003 | 74.4169 | 70.9002 | 76.1206 | 75.1111 | 75.8779 | 78.0627 | 74.6677 | 75.889 | 77.0277 | 78.6693 | 74.1141 | 77.1019 | 77.5246 | 79.7474 | 73.5746 | 77.7626 | 76.7174 | 79.9263 | 75.6878 | 80.0591 | 76.2104 | 80.7651 | 75.1119 | 78.5551 | 80.6708 | 94.2352 | 94.4227 | 93.9108
2022-09-07 18:44 | 0:20 | 53.688 | 51.7261 | 55.5701 | 71.5552 | 74.6757 | 72.6934 | 76.6752 | 70.6034 | 76.9637 | 74.0114 | 71.939 | 79.6697 | 70.9885 | 74.5927 | 75.7137 | 74.7877 | 72.6483 | 74.2983 | 75.0781 | 75.8834 | 56.0132 | 51.676 | 61.5007 | 73.3806 | 73.5131 | 77.3327 | 76.2789 | 75.1304 | 73.6557 | 75.9455 | 70.5537 | 77.3588 | 73.2529 | 74.0699 | 70.7138 | 76.3069 | 74.8037 | 75.7567 | 78.0173 | 74.4674 | 75.6823 | 76.8857 | 78.4643 | 73.9606 | 76.8594 | 77.288 | 79.5294 | 73.3405 | 77.7147 | 76.5041 | 79.514 | 75.4107 | 79.8913 | 75.9472 | 80.877 | 74.9768 | 78.4577 | 80.5916 | 94.4038 | 94.5988 | 94.0798
2022-09-07 18:44 | 0:20 | 53.4611 | 51.5388 | 55.3825 | 71.4041 | 74.5289 | 72.6167 | 76.209 | 70.3296 | 76.7339 | 73.7308 | 71.5107 | 79.4546 | 70.7378 | 74.2909 | 75.4834 | 74.6483 | 72.401 | 73.8058 | 74.9606 | 75.993 | 55.8233 | 51.4883 | 61.3081 | 73.2347 | 73.2781 | 77.0474 | 76.1728 | 75.1554 | 73.3325 | 75.8064 | 70.2117 | 77.1842 | 73.0806 | 73.9339 | 70.511 | 76.205 | 74.8359 | 75.4984 | 78.2162 | 74.3227 | 75.5927 | 76.6802 | 78.3287 | 73.7221 | 76.7066 | 77.045 | 79.5054 | 73.118 | 77.5743 | 76.2632 | 79.5049 | 75.2312 | 79.6443 | 75.9714 | 80.2436 | 74.701 | 78.3437 | 80.1582 | 94.6367 | 94.6524 | 94.0896
2022-09-07 18:44 | 0:20 | 53.2525 | 51.3664 | 55.2022 | 71.205 | 74.3754 | 72.1231 | 76.3483 | 70.1636 | 76.634 | 73.8751 | 71.3941 | 79.0966 | 70.4123 | 74.3077 | 75.3582 | 74.4222 | 72.264 | 73.8194 | 74.568 | 75.4578 | 55.6456 | 51.2827 | 61.1437 | 72.9423 | 73.0956 | 76.8979 | 75.8754 | 75.2486 | 73.3401 | 75.6241 | 69.976 | 77.153 | 72.6511 | 73.8084 | 70.3145 | 76.0477 | 74.5906 | 75.3565 | 77.9406 | 74.1847 | 75.1946 | 76.421 | 77.9853 | 73.4895 | 76.5821 | 76.9891 | 79.2705 | 72.9066 | 77.1722 | 76.0967 | 79.3654 | 75.4753 | 79.592 | 75.6809 | 80.1403 | 74.4933 | 77.9543 | 80.282 | 94.7415 | 94.8514 | 94.2406
2022-09-07 18:44 | 0:20 | 53.0515 | 51.1805 | 55.0211 | 71.1413 | 74.1966 | 72.2656 | 76.6089 | 70.0003 | 76.4332 | 73.7621 | 70.8086 | 79.0753 | 70.188 | 74.0542 | 75.0519 | 74.0998 | 72.0934 | 73.5279 | 74.4501 | 75.3629 | 55.4997 | 51.1219 | 60.9929 | 72.8874 | 72.8816 | 76.7953 | 75.889 | 74.9724 | 73.0863 | 75.4668 | 70.0148 | 76.9428 | 72.6105 | 73.54 | 69.8746 | 75.6907 | 74.2022 | 75.0837 | 77.8703 | 73.8042 | 75.0096 | 76.3719 | 77.9332 | 73.3615 | 76.5958 | 76.7446 | 78.7445 | 72.7976 | 76.9831 | 75.9908 | 79.3813 | 75.2152 | 79.504 | 75.4168 | 80.1112 | 74.3677 | 77.9414 | 79.8617 | 94.8576 | 94.91 | 94.2888
2022-09-07 18:44 | 0:20 | 52.8374 | 51.017 | 54.8311 | 70.8883 | 73.9586 | 71.8056 | 76.1213 | 69.8175 | 76.1855 | 73.1476 | 70.8846 | 78.8624 | 70.0534 | 73.9133 | 74.888 | 73.9089 | 71.8654 | 73.4637 | 74.3349 | 75.0216 | 55.3034 | 50.9684 | 60.7356 | 72.6266 | 72.6115 | 76.7516 | 75.6823 | 74.9198 | 72.7845 | 75.2818 | 69.5354 | 76.7835 | 72.311 | 73.3899 | 69.8105 | 75.8419 | 74.1848 | 74.8835 | 77.8395 | 73.7443 | 74.9431 | 76.1302 | 77.8464 | 73.2523 | 76.3319 | 76.5994 | 78.6012 | 72.6821 | 76.9379 | 75.7893 | 79.1307 | 75.0504 | 79.0222 | 75.369 | 79.7471 | 74.0545 | 77.6762 | 79.8446 | 94.9147 | 95.0245 | 94.3703
2022-09-07 18:44 | 0:20 | 52.6708 | 50.8488 | 54.6206 | 70.7931 | 73.7286 | 71.6125 | 75.8218 | 69.5613 | 75.996 | 73.2564 | 70.8094 | 78.6523 | 69.8637 | 73.6749 | 74.5877 | 73.7306 | 71.7163 | 73.2301 | 74.045 | 75.0776 | 55.0699 | 50.7803 | 60.5364 | 72.3944 | 72.2828 | 76.5987 | 75.5927 | 74.5877 | 72.4846 | 75.1878 | 69.578 | 76.4911 | 72.1882 | 73.2319 | 69.5503 | 75.3249 | 73.9803 | 74.6112 | 77.6046 | 73.469 | 74.6358 | 75.7596 | 77.675 | 73.1351 | 76.1277 | 76.5079 | 78.6125 | 72.5766 | 76.8535 | 75.7053 | 79.0624 | 74.8855 | 78.686 | 74.9886 | 79.4195 | 73.9588 | 77.5924 | 79.9441 | 94.9603 | 95.0821 | 94.2858
2022-09-07 18:45 | 0:20 | 52.4893 | 50.6605 | 54.4818 | 70.4655 | 73.6464 | 71.3255 | 75.669 | 69.3119 | 75.7482 | 72.862 | 70.5996 | 78.4731 | 69.5552 | 73.1848 | 74.614 | 73.5711 | 71.5611 | 72.8713 | 73.8833 | 74.8929 | 54.9038 | 50.5961 | 60.3818 | 72.2973 | 72.2079 | 76.3667 | 75.1946 | 74.7471 | 72.3844 | 75.0033 | 69.3142 | 76.3214 | 72.075 | 73.1246 | 69.0299 | 75.8113 | 73.639 | 74.627 | 77.3668 | 73.2725 | 74.4787 | 75.7428 | 77.7111 | 72.9886 | 75.8045 | 76.2154 | 78.4455 | 72.194 | 76.5847 | 75.365 | 79.088 | 74.5176 | 78.8709 | 74.7912 | 79.4126 | 73.7959 | 77.3395 | 79.9385 | 95.072 | 95.1789 | 94.4351
2022-09-07 18:45 | 0:21 | 52.2772 | 50.4597 | 54.2573 | 70.3596 | 73.3507 | 71.463 | 75.6172 | 69.171 | 75.5143 | 72.8675 | 70.418 | 78.3906 | 69.3941 | 73.1042 | 74.21 | 73.4269 | 71.2759 | 72.6732 | 73.6344 | 74.7852 | 54.7541 | 50.4293 | 60.2475 | 72.0874 | 71.9649 | 76.2248 | 75.0096 | 74.2052 | 72.1824 | 74.9313 | 69.1269 | 76.2156 | 71.7828 | 72.9109 | 68.9091 | 75.8277 | 73.5358 | 74.3147 | 77.0982 | 73.1111 | 74.2627 | 75.5857 | 77.2846 | 72.6714 | 75.8349 | 76.0626 | 78.2427 | 72.0722 | 76.55 | 75.156 | 78.9905 | 74.2406 | 78.7516 | 74.6541 | 79.0534 | 73.596 | 77.3284 | 79.6739 | 94.9415 | 95.0337 | 94.357
2022-09-07 18:45 | 0:21 | 52.0497 | 50.2858 | 54.0486 | 70.0341 | 73.3208 | 71.3126 | 75.7027 | 69.0001 | 75.4885 | 72.4271 | 70.3032 | 78.3021 | 69.1569 | 72.4954 | 74.1376 | 73.2002 | 71.1268 | 72.6037 | 73.3963 | 74.6255 | 54.6224 | 50.2353 | 60.0648 | 71.8471 | 71.7704 | 76.1246 | 74.9431 | 73.7361 | 71.9008 | 74.5184 | 68.9415 | 75.9627 | 71.6745 | 72.6944 | 69.2912 | 75.0594 | 73.3311 | 74.1467 | 76.6681 | 72.9853 | 74.1636 | 75.5461 | 77.2221 | 72.5199 | 75.5687 | 75.9008 | 78.1076 | 71.963 | 76.6099 | 75.1588 | 78.8609 | 74.0207 | 78.4444 | 74.5312 | 79.4372 | 73.3879 | 77.1246 | 79.2867 | 94.688 | 94.775 | 94.1445
2022-09-07 18:45 | 0:21 | 51.8323 | 50.0992 | 53.8236 | 70.0502 | 73.1603 | 71.0126 | 75.3286 | 68.647 | 75.1798 | 72.4428 | 69.7267 | 77.9338 | 69.173 | 72.3078 | 73.7643 | 72.9568 | 70.9729 | 72.3617 | 73.2713 | 74.2101 | 54.4582 | 50.0431 | 59.9106 | 71.6983 | 71.5994 | 76.0132 | 74.6358 | 73.956 | 71.7499 | 74.5111 | 68.8016 | 75.7862 | 71.3609 | 72.5573 | 68.6897 | 74.9602 | 73.061 | 73.9533 | 76.713 | 72.7323 | 73.9716 | 75.3777 | 76.7219 | 72.2579 | 75.3136 | 75.7503 | 78.0452 | 71.7528 | 76.1297 | 74.8898 | 78.1842 | 73.9943 | 78.1499 | 74.2579 | 78.6952 | 73.2356 | 76.9334 | 79.1976 | 94.4596 | 94.5806 | 94.0161
2022-09-07 18:45 | 0:21 | 51.5806 | 49.9765 | 53.6703 | 69.6442 | 72.8221 | 70.8094 | 74.8068 | 68.4827 | 74.9529 | 72.2031 | 69.6839 | 77.8819 | 68.9143 | 72.4974 | 73.6393 | 72.8224 | 70.8146 | 71.9518 | 72.9714 | 74.0882 | 54.2551 | 49.8989 | 59.6065 | 71.5925 | 71.4328 | 75.6881 | 74.4787 | 73.7379 | 71.6901 | 74.1629 | 68.6573 | 75.4971 | 71.28 | 72.3647 | 68.5604 | 74.6721 | 72.9964 | 73.914 | 76.2383 | 72.6632 | 73.6332 | 75.1278 | 76.7019 | 72.1697 | 75.2918 | 75.6448 | 77.9685 | 71.6912 | 76.2139 | 74.6076 | 78.2116 | 73.7011 | 77.7213 | 73.9812 | 78.8427 | 72.9829 | 76.7741 | 78.7327 | 94.3206 | 94.4459 | 93.9378
2022-09-07 18:45 | 0:21 | 51.4024 | 49.7694 | 53.4159 | 69.6416 | 72.7978 | 70.4011 | 74.6624 | 68.4146 | 74.8166 | 72.2218 | 69.855 | 77.654 | 68.7231 | 72.4963 | 73.4149 | 72.5884 | 70.5367 | 72.3941 | 72.7022 | 73.791 | 54.0588 | 49.6974 | 59.4313 | 71.465 | 71.1829 | 75.7213 | 74.2627 | 73.4588 | 71.4408 | 74.0366 | 68.3997 | 75.2326 | 70.9498 | 72.1171 | 68.3882 | 74.4627 | 73.1177 | 73.6953 | 75.9791 | 72.4755 | 73.5332 | 74.9189 | 76.4864 | 71.8978 | 75.1309 | 75.2847 | 77.5802 | 71.3906 | 76.2442 | 74.3638 | 78.2253 | 73.3357 | 77.8886 | 73.8656 | 78.6421 | 72.8904 | 76.4365 | 78.5372 | 94.1704 | 94.3441 | 93.8828
2022-09-07 18:46 | 0:22 | 51.2095 | 49.6144 | 53.2751 | 69.2373 | 72.7551 | 70.4194 | 74.3817 | 68.1762 | 74.7088 | 71.8394 | 69.5618 | 77.4489 | 68.5459 | 72.0533 | 73.1332 | 72.4074 | 70.3014 | 71.8039 | 72.5627 | 73.6719 | 53.8772 | 49.5345 | 59.3495 | 71.1929 | 70.9998 | 75.3764 | 74.1636 | 73.3687 | 71.1866 | 74.0239 | 68.2571 | 75.2181 | 70.7223 | 71.8426 | 68.0096 | 74.1763 | 72.4904 | 73.4049 | 75.7955 | 72.1117 | 73.535 | 74.8107 | 76.3662 | 71.7809 | 75.0056 | 75.1588 | 77.6125 | 71.1071 | 76.0837 | 74.2077 | 77.9561 | 73.3787 | 77.5512 | 73.7602 | 78.157 | 72.6006 | 76.5263 | 78.5356 | 94.0811 | 94.2539 | 93.8187
2022-09-07 18:46 | 0:22 | 51.0214 | 49.4397 | 53.057 | 69.1124 | 72.4019 | 70.2589 | 74.3412 | 68.0225 | 74.54 | 71.5211 | 69.3434 | 77.3192 | 68.388 | 71.8687 | 73.0311 | 72.1722 | 70.0156 | 71.4131 | 72.4396 | 73.5488 | 53.7112 | 49.3755 | 59.1253 | 71.0106 | 70.8146 | 75.2508 | 73.9716 | 73.2949 | 70.9954 | 73.7636 | 68.0429 | 75.0543 | 70.7181 | 71.7073 | 67.8377 | 74.1991 | 72.4116 | 73.2991 | 75.3958 | 72.0327 | 73.3837 | 74.7016 | 76.1542 | 71.534 | 74.8383 | 75.007 | 77.2854 | 71.0533 | 75.7183 | 74.1568 | 77.6667 | 73.2837 | 77.6048 | 73.6882 | 78.1122 | 72.4663 | 76.2346 | 78.4979 | 93.9812 | 94.1284 | 93.7667
2022-09-07 18:46 | 0:22 | 50.7718 | 49.2512 | 52.8485 | 69.0541 | 72.2156 | 70.3463 | 74.4727 | 67.8175 | 74.3188 | 71.2708 | 69.0459 | 77.167 | 68.1137 | 71.8905 | 72.7441 | 72.0175 | 69.9432 | 71.4905 | 72.2849 | 73.557 | 53.5168 | 49.1978 | 58.9376 | 70.6717 | 70.5741 | 75.0893 | 73.6332 | 73.0015 | 70.9139 | 73.6305 | 67.7312 | 74.9053 | 70.5381 | 71.6103 | 67.7877 | 74.0712 | 72.1735 | 73.1153 | 75.8669 | 71.7545 | 73.0763 | 74.4476 | 75.9195 | 71.4158 | 74.612 | 74.9111 | 77.222 | 70.8144 | 75.6028 | 74.0195 | 77.7129 | 73.1549 | 77.4682 | 73.5004 | 78.0745 | 72.3033 | 75.8723 | 78.3281 | 94.0093 | 94.0564 | 93.7945
2022-09-07 18:46 | 0:22 | 50.51 | 49.0961 | 52.6217 | 68.918 | 71.9514 | 70.2074 | 74.2281 | 67.6442 | 74.1074 | 71.1594 | 68.9427 | 76.9199 | 67.9517 | 71.5594 | 72.5845 | 71.8862 | 69.7544 | 71.5829 | 72.0893 | 73.451 | 53.3448 | 49.0251 | 58.7189 | 70.675 | 70.3816 | 74.9956 | 73.5332 | 72.8307 | 70.6987 | 73.3435 | 67.6003 | 74.584 | 70.3897 | 71.3449 | 67.6681 | 73.5439 | 72.0697 | 72.8613 | 75.3044 | 71.6197 | 72.9423 | 74.1972 | 75.9905 | 71.3352 | 74.3959 | 74.7372 | 76.8909 | 70.7154 | 75.5653 | 73.8175 | 77.3346 | 72.8779 | 76.9068 | 73.2854 | 78.0681 | 72.0636 | 75.7032 | 77.9382 | 93.8751 | 93.9872 | 93.7346
2022-09-07 18:46 | 0:22 | 50.3935 | 48.9092 | 52.4459 | 68.9074 | 71.8411 | 69.8597 | 73.8054 | 67.4689 | 73.9304 | 71.0012 | 68.7892 | 76.7418 | 67.8201 | 71.3702 | 72.5882 | 71.6182 | 69.5601 | 71.0971 | 71.8715 | 73.1634 | 53.1596 | 48.8441 | 58.5171 | 70.4708 | 70.1319 | 74.8743 | 73.535 | 72.4203 | 70.5161 | 73.436 | 67.3415 | 74.3645 | 70.0745 | 71.2781 | 67.4454 | 73.4029 | 71.8463 | 72.7253 | 75.5896 | 71.4192 | 72.5959 | 74.0508 | 75.8247 | 71.1999 | 74.2672 | 74.521 | 76.7968 | 70.5377 | 75.3091 | 73.6615 | 77.0939 | 72.701 | 76.9033 | 72.9007 | 77.3371 | 71.887 | 75.6282 | 77.9349 | 93.8266 | 93.9369 | 93.7146
2022-09-07 18:46 | 0:22 | 50.3069 | 48.7715 | 52.3165 | 68.6185 | 71.6822 | 69.4625 | 73.8628 | 67.1848 | 73.7184 | 70.7657 | 68.6351 | 76.6024 | 67.5944 | 70.8885 | 72.3745 | 71.4735 | 69.4404 | 70.8738 | 71.7049 | 73.109 | 52.9832 | 48.6886 | 58.3854 | 70.2343 | 69.9662 | 74.6647 | 73.3837 | 71.978 | 70.2552 | 73.102 | 66.997 | 74.1644 | 69.929 | 71.1055 | 67.5099 | 73.1226 | 71.9844 | 72.4505 | 75.4052 | 71.4507 | 72.6775 | 73.9127 | 75.6782 | 71.0887 | 74.1513 | 74.3387 | 76.7027 | 70.357 | 75.2946 | 73.419 | 77.0907 | 72.2931 | 76.9795 | 72.8407 | 77.3262 | 71.7643 | 75.2746 | 77.844 | 93.8031 | 93.9011 | 93.6847
2022-09-07 18:47 | 0:22 | 50.1629 | 48.6096 | 52.163 | 68.4703 | 71.5406 | 69.4917 | 73.406 | 67.0676 | 73.6408 | 70.7992 | 68.3643 | 76.4567 | 67.3193 | 71.0312 | 72.1561 | 71.3266 | 69.1551 | 70.5835 | 71.5057 | 72.6389 | 52.8229 | 48.5171 | 58.1508 | 70.0689 | 69.8193 | 74.5098 | 73.0763 | 71.9295 | 70.1747 | 72.9696 | 66.9427 | 74.0237 | 69.7489 | 70.9441 | 67.1191 | 73.1744 | 71.7665 | 72.2218 | 75.3212 | 71.2185 | 72.5042 | 73.7297 | 75.4744 | 70.766 | 74.0197 | 74.1585 | 76.4854 | 70.1173 | 75.0105 | 73.1334 | 77.0161 | 72.3917 | 76.8269 | 72.8537 | 76.9981 | 71.5194 | 75.1805 | 77.5514 | 93.7543 | 93.8487 | 93.6636
2022-09-07 18:47 | 0:23 | 50.0114 | 48.3999 | 52.0033 | 68.127 | 71.3605 | 69.3603 | 73.4578 | 66.9693 | 73.3498 | 70.483 | 68.0137 | 76.1865 | 67.0184 | 71.1769 | 71.8798 | 71.0511 | 69.0542 | 70.7905 | 71.3001 | 72.3557 | 52.6487 | 48.3761 | 57.9639 | 69.8839 | 69.5624 | 74.3132 | 72.9423 | 71.9968 | 69.8417 | 72.698 | 66.7153 | 73.8095 | 69.6193 | 70.7835 | 66.8028 | 73.0794 | 71.4586 | 72.2676 | 74.9837 | 70.9718 | 72.2581 | 73.5355 | 75.2513 | 70.5174 | 73.7492 | 74.0429 | 76.2963 | 69.9422 | 74.5987 | 73.0124 | 76.6565 | 71.9998 | 76.6139 | 72.5613 | 77.0077 | 71.3644 | 75.1066 | 77.4309 | 93.7055 | 93.848 | 93.592
2022-09-07 18:47 | 0:23 | 49.8108 | 48.2559 | 51.8446 | 68.0376 | 71.139 | 69.2818 | 73.4661 | 66.6928 | 73.1739 | 70.1583 | 67.8347 | 75.9597 | 66.8447 | 70.562 | 71.6518 | 70.8615 | 68.8569 | 70.5146 | 71.0131 | 72.1754 | 52.4797 | 48.2255 | 57.7611 | 69.6547 | 69.3134 | 74.0307 | 72.5959 | 71.4283 | 69.7114 | 72.5609 | 66.6135 | 73.5415 | 69.4502 | 70.5418 | 66.9435 | 72.6963 | 71.3956 | 71.9455 | 74.4072 | 70.8913 | 72.1072 | 73.4997 | 75.1611 | 70.391 | 73.6536 | 73.8365 | 76.3751 | 69.7126 | 74.7305 | 72.8023 | 76.6523 | 72.1433 | 76.6597 | 72.2875 | 77.2936 | 71.2227 | 74.8521 | 77.3806 | 93.5733 | 93.7915 | 93.5489
2022-09-07 18:47 | 0:23 | 49.7064 | 48.0955 | 51.6756 | 67.8911 | 70.8083 | 68.8279 | 73.1162 | 66.5352 | 73.0327 | 69.933 | 67.9307 | 75.8948 | 66.7271 | 70.3607 | 71.4323 | 70.7242 | 68.6016 | 70.1276 | 70.8664 | 71.9853 | 52.3005 | 48.0909 | 57.6095 | 69.5331 | 69.1857 | 73.9259 | 72.6775 | 71.8081 | 69.4304 | 72.4214 | 66.4472 | 73.5366 | 69.1394 | 70.3278 | 66.5722 | 72.4482 | 70.981 | 71.6847 | 74.2841 | 70.4956 | 72.0456 | 73.2848 | 74.6422 | 70.1538 | 73.5124 | 73.6065 | 76.0316 | 69.552 | 74.1677 | 72.5865 | 75.8775 | 72.1764 | 76.2057 | 72.1535 | 76.8289 | 71.0478 | 74.6102 | 77.1692 | 93.51 | 93.6657 | 93.4583
2022-09-07 18:47 | 0:23 | 49.5667 | 47.9626 | 51.5144 | 67.685 | 70.7818 | 68.6067 | 73.1569 | 66.2099 | 72.7637 | 69.7312 | 67.6616 | 75.6621 | 66.5552 | 70.4735 | 71.2336 | 70.3867 | 68.5308 | 70.3888 | 70.7724 | 71.9832 | 52.1262 | 47.938 | 57.3955 | 69.4712 | 69.0157 | 73.8547 | 72.5042 | 71.5697 | 69.3698 | 72.1329 | 66.1013 | 73.2649 | 68.9476 | 70.0812 | 66.3281 | 72.4099 | 71.121 | 71.5739 | 74.2371 | 70.4582 | 71.701 | 73.0502 | 74.6043 | 69.8944 | 73.1786 | 73.5517 | 76.0589 | 69.3281 | 74.0692 | 72.4832 | 75.8094 | 71.6993 | 75.9058 | 72.0105 | 76.608 | 70.8825 | 74.4657 | 76.9197 | 93.39 | 93.5584 | 93.3969
2022-09-07 18:47 | 0:23 | 49.4051 | 47.8026 | 51.3376 | 67.5021 | 70.554 | 68.7208 | 72.749 | 66.1725 | 72.6788 | 69.8334 | 67.3798 | 75.5722 | 66.4595 | 69.9951 | 71.1779 | 70.264 | 68.3391 | 69.9768 | 70.5366 | 71.7975 | 51.9561 | 47.7729 | 57.2104 | 69.3322 | 68.8274 | 73.5055 | 72.2581 | 71.3505 | 69.1136 | 72.0221 | 66.2175 | 73.1266 | 68.9323 | 69.814 | 66.2195 | 72.1424 | 71.1574 | 71.3928 | 74.4899 | 70.4187 | 71.7143 | 72.8372 | 74.5304 | 69.7895 | 73.0523 | 73.1985 | 75.719 | 69.3025 | 73.8161 | 72.382 | 75.8901 | 71.3689 | 75.6954 | 71.7533 | 76.2902 | 70.6743 | 74.3428 | 76.8285 | 93.2796 | 93.3889 | 93.3063
2022-09-07 18:48 | 0:23 | 49.3102 | 47.6977 | 51.2209 | 67.5035 | 70.3984 | 68.6272 | 72.7771 | 65.7732 | 72.538 | 70.0399 | 67.1756 | 75.3907 | 66.1603 | 69.6569 | 70.9235 | 70.0965 | 68.1022 | 69.7424 | 70.3364 | 71.5289 | 51.7912 | 47.6306 | 57.0438 | 69.1536 | 68.6497 | 73.4484 | 72.1072 | 70.8106 | 68.9074 | 71.8739 | 65.8936 | 72.9318 | 68.648 | 69.8253 | 66.4419 | 72.2426 | 70.9753 | 71.3597 | 74.1689 | 70.1683 | 71.4762 | 72.7355 | 74.122 | 69.6052 | 73.0383 | 72.988 | 75.5889 | 69.1183 | 74.1923 | 72.1108 | 75.8752 | 71.177 | 75.7883 | 71.8405 | 76.1192 | 70.4756 | 74.4184 | 76.5961 | 93.1848 | 93.3048 | 93.2959
2022-09-07 18:48 | 0:24 | 49.1474 | 47.5585 | 51.0907 | 67.0942 | 70.3003 | 68.1382 | 72.5953 | 65.8278 | 72.2946 | 69.5195 | 67.5321 | 75.1109 | 66.0864 | 69.781 | 70.7056 | 69.864 | 67.9628 | 69.5739 | 70.2045 | 71.3356 | 51.6329 | 47.4867 | 56.8802 | 68.8557 | 68.4542 | 73.4817 | 72.0456 | 70.5176 | 68.7243 | 71.8111 | 65.5618 | 72.7875 | 68.3807 | 69.7138 | 66.1847 | 72.0829 | 70.6414 | 71.2963 | 74.3132 | 69.9292 | 71.2842 | 72.5905 | 74.0563 | 69.4805 | 72.9642 | 72.8594 | 75.4595 | 68.9063 | 73.583 | 71.9589 | 75.2092 | 71.0495 | 75.56 | 71.532 | 76.2816 | 70.2989 | 74.1364 | 76.4887 | 93.0279 | 93.2028 | 93.2013
2022-09-07 18:48 | 0:24 | 49.0507 | 47.3841 | 50.9472 | 66.8161 | 70.0502 | 68.1443 | 72.4543 | 65.5639 | 72.1614 | 69.2863 | 67.066 | 74.8597 | 65.7635 | 69.6802 | 70.5202 | 69.7157 | 67.826 | 69.5885 | 70.1185 | 71.2115 | 51.5138 | 47.3197 | 56.6881 | 68.6784 | 68.2113 | 73.1696 | 71.701 | 70.3048 | 68.5552 | 71.5642 | 65.328 | 72.647 | 68.1587 | 69.3186 | 65.9353 | 71.8798 | 70.3842 | 70.8974 | 73.2379 | 69.7271 | 71.0008 | 72.4114 | 73.9022 | 69.1703 | 72.6529 | 72.7137 | 75.4142 | 68.7951 | 73.4308 | 71.8569 | 75.4547 | 71.0782 | 75.1547 | 71.043 | 76.27 | 70.2228 | 73.8029 | 76.3859 | 92.9081 | 93.0507 | 93.0977
2022-09-07 18:48 | 0:24 | 48.9059 | 47.2433 | 50.8016 | 66.7119 | 69.9834 | 67.7759 | 72.0591 | 65.4681 | 71.9494 | 68.9814 | 66.9897 | 74.7663 | 65.7643 | 69.2725 | 70.4447 | 69.5517 | 67.6591 | 69.1505 | 69.8273 | 71.0115 | 51.3373 | 47.1617 | 56.5533 | 68.6102 | 68.1697 | 73.2072 | 71.7143 | 70.0363 | 68.4706 | 71.3681 | 65.0869 | 72.2278 | 68.0134 | 69.2593 | 65.5365 | 71.4361 | 70.1484 | 70.7421 | 73.1325 | 69.581 | 70.84 | 72.1567 | 73.8063 | 69.1783 | 72.3983 | 72.6016 | 75.2357 | 68.4968 | 73.7558 | 71.6423 | 75.4376 | 70.8306 | 74.9793 | 70.7988 | 75.9879 | 69.9807 | 73.7943 | 76.2147 | 92.8336 | 92.8974 | 93.0238
2022-09-07 18:48 | 0:24 | 48.7539 | 47.1211 | 50.6567 | 66.646 | 69.8066 | 67.3945 | 71.7339 | 65.3386 | 71.7041 | 68.8848 | 66.7667 | 74.5606 | 65.6112 | 69.0571 | 70.2791 | 69.4146 | 67.4532 | 68.8975 | 69.5658 | 70.971 | 51.184 | 47.0224 | 56.4302 | 68.3899 | 67.8765 | 72.9718 | 71.4762 | 70.0857 | 68.2409 | 71.184 | 65.0376 | 72.1212 | 67.9301 | 69.064 | 65.308 | 71.4719 | 69.9606 | 70.5964 | 73.3819 | 69.4159 | 70.7571 | 72.0039 | 73.8311 | 69.1314 | 72.2836 | 72.4367 | 75.1653 | 68.3602 | 73.575 | 71.4279 | 75.2959 | 70.5722 | 74.7327 | 70.7168 | 75.8012 | 69.7697 | 73.4432 | 76.0965 | 92.6911 | 92.8469 | 92.9554
2022-09-07 18:48 | 0:24 | 48.6215 | 46.9733 | 50.5157 | 66.4926 | 69.7842 | 67.2901 | 71.6492 | 65.303 | 71.6207 | 68.5064 | 66.6376 | 74.5306 | 65.2809 | 69.2658 | 70.0502 | 69.1513 | 67.2322 | 68.9885 | 69.6008 | 70.6433 | 51.0393 | 46.8976 | 56.2651 | 68.1071 | 67.5615 | 72.7101 | 71.2842 | 70.1284 | 67.8407 | 71.1346 | 65.0316 | 72.0293 | 67.616 | 68.8595 | 65.8753 | 71.4816 | 70.2802 | 70.2893 | 72.8118 | 69.4815 | 70.585 | 71.8866 | 73.5944 | 69.1034 | 72.0383 | 72.228 | 74.8087 | 68.2868 | 73.316 | 71.1015 | 75.0105 | 70.6306 | 75.0084 | 70.6547 | 75.3395 | 69.6294 | 73.5426 | 75.981 | 92.5483 | 92.6775 | 92.7906
2022-09-07 18:49 | 0:25 | 48.4627 | 46.8288 | 50.3665 | 66.2616 | 69.5078 | 67.2905 | 71.2935 | 65.046 | 71.4734 | 68.6191 | 66.6187 | 74.3252 | 65.1152 | 69.1719 | 69.8172 | 68.8445 | 67.0214 | 68.5421 | 69.3904 | 70.4306 | 50.8937 | 46.7615 | 56.0458 | 68.0037 | 67.4195 | 72.5064 | 71.0008 | 69.8585 | 67.779 | 71.0908 | 64.7945 | 71.8378 | 67.3527 | 68.7436 | 64.9753 | 71.156 | 69.8613 | 70.1401 | 73.0314 | 69.157 | 70.3195 | 71.7613 | 73.5108 | 68.7955 | 71.9142 | 72.0635 | 74.7672 | 68.1088 | 73.3626 | 71.0168 | 74.6839 | 70.2861 | 74.5728 | 70.2501 | 75.4484 | 69.4241 | 73.1775 | 75.6924 | 92.4486 | 92.5728 | 92.7588
2022-09-07 18:49 | 0:25 | 48.3573 | 46.6887 | 50.23 | 66.2496 | 69.2456 | 67.1326 | 71.1883 | 64.8225 | 71.3535 | 68.2672 | 66.0072 | 74.1841 | 64.9946 | 68.8821 | 69.636 | 68.8071 | 66.9139 | 68.4772 | 69.114 | 70.2797 | 50.7026 | 46.6042 | 55.8869 | 67.8803 | 67.2471 | 72.4556 | 70.84 | 69.9851 | 67.6798 | 70.697 | 64.4233 | 71.7787 | 67.3028 | 68.5861 | 64.9159 | 71.0723 | 69.7926 | 69.9976 | 73.1213 | 68.9862 | 70.2164 | 71.5329 | 73.3829 | 68.6579 | 71.8264 | 71.9547 | 74.2845 | 67.9967 | 73.39 | 70.8989 | 74.8063 | 69.9935 | 74.5364 | 69.9072 | 75.4496 | 69.2201 | 73.0918 | 75.4578 | 92.3573 | 92.4523 | 92.7076
2022-09-07 18:49 | 0:25 | 48.2832 | 46.5763 | 50.0867 | 65.9455 | 69.0958 | 66.8771 | 71.1705 | 64.6855 | 71.1116 | 68.1006 | 65.9508 | 73.9776 | 64.89 | 68.5306 | 69.6556 | 68.5088 | 66.7994 | 68.2028 | 68.9053 | 70.1805 | 50.5577 | 46.4851 | 55.7149 | 67.7158 | 67.0077 | 72.1798 | 70.7571 | 69.8606 | 67.6008 | 70.5279 | 64.2858 | 71.5883 | 67.0451 | 68.4427 | 64.8291 | 70.6666 | 69.1003 | 69.7253 | 72.3818 | 68.7037 | 69.9688 | 71.3031 | 72.8946 | 68.5001 | 71.6205 | 71.694 | 74.1452 | 67.9134 | 72.8508 | 70.7582 | 74.6303 | 70.1529 | 74.391 | 69.9833 | 74.8912 | 68.9961 | 72.8404 | 75.3584 | 92.2565 | 92.3218 | 92.6488
2022-09-07 18:49 | 0:25 | 48.1064 | 46.4507 | 49.9346 | 65.9724 | 68.9733 | 66.776 | 71.194 | 64.4676 | 70.9767 | 67.7395 | 65.7319 | 73.8731 | 64.6791 | 68.3996 | 69.4951 | 68.5141 | 66.5071 | 68.158 | 68.7978 | 70.0097 | 50.3862 | 46.3181 | 55.5502 | 67.549 | 66.9233 | 72.0649 | 70.585 | 69.3217 | 67.2238 | 70.3459 | 64.0578 | 71.3015 | 66.7068 | 68.3676 | 64.5417 | 70.5115 | 69.0712 | 69.6037 | 72.4104 | 68.4498 | 69.9341 | 71.2747 | 73.0507 | 68.2651 | 71.4208 | 71.485 | 74.2418 | 67.4218 | 72.573 | 70.5636 | 74.3263 | 69.8699 | 74.3476 | 69.8743 | 74.6958 | 68.9256 | 72.5825 | 75.287 | 92.1099 | 92.133 | 92.4646
2022-09-07 18:49 | 0:25 | 47.9648 | 46.3273 | 49.8505 | 65.7158 | 68.8326 | 66.4764 | 70.4097 | 64.321 | 70.8323 | 67.7446 | 65.946 | 73.6372 | 64.4579 | 68.2089 | 69.2332 | 68.235 | 66.3749 | 68.1007 | 68.6078 | 69.7836 | 50.2514 | 46.2166 | 55.4107 | 67.2255 | 66.6693 | 71.8673 | 70.3195 | 69.2409 | 67.1449 | 70.1864 | 63.9919 | 71.0174 | 66.5238 | 68.0364 | 64.3429 | 70.019 | 68.9761 | 69.4721 | 72.0979 | 68.4283 | 69.5923 | 71.1496 | 72.6991 | 68.1307 | 71.2736 | 71.4436 | 74.0029 | 67.4639 | 72.1788 | 70.5301 | 74.1528 | 69.5243 | 74.1195 | 69.7172 | 74.4507 | 68.6116 | 72.2479 | 75.1685 | 91.9657 | 91.9853 | 92.4375
2022-09-07 18:49 | 0:25 | 47.8093 | 46.1737 | 49.6827 | 65.507 | 68.6712 | 66.2597 | 70.4216 | 64.0441 | 70.662 | 67.6475 | 65.5084 | 73.5184 | 64.3374 | 68.0687 | 69.1593 | 68.0307 | 66.3007 | 67.9351 | 68.3421 | 69.5707 | 50.1071 | 46.0811 | 55.2463 | 67.1801 | 66.572 | 71.7618 | 70.2164 | 68.7683 | 66.8424 | 70.0804 | 63.646 | 71.0912 | 66.6599 | 67.9581 | 64.3629 | 70.0345 | 69.0951 | 69.2578 | 72.0055 | 68.3544 | 69.5575 | 70.8787 | 72.4925 | 67.9942 | 71.1129 | 71.2767 | 73.8443 | 67.3819 | 72.1711 | 70.2695 | 74.2875 | 69.4085 | 74.0194 | 69.6683 | 74.8068 | 68.4877 | 72.2772 | 74.8961 | 91.8543 | 91.8389 | 92.35
2022-09-07 18:50 | 0:25 | 47.6934 | 46.0563 | 49.5626 | 65.3303 | 68.5388 | 65.9052 | 70.5468 | 63.9998 | 70.5471 | 67.5169 | 65.8555 | 73.3222 | 64.178 | 67.8926 | 68.8431 | 67.8975 | 66.0513 | 67.7875 | 68.2733 | 69.4431 | 49.955 | 45.9559 | 55.0503 | 67.0128 | 66.4329 | 71.5932 | 69.9688 | 68.8338 | 66.6708 | 69.8606 | 63.7163 | 70.86 | 66.4242 | 67.6695 | 63.8922 | 70.1464 | 68.4809 | 69.2401 | 71.807 | 68.0155 | 69.3342 | 70.7554 | 72.3868 | 67.7597 | 70.9905 | 71.0372 | 73.5436 | 67.1026 | 71.8916 | 70.1694 | 73.9924 | 69.3675 | 73.5611 | 69.3086 | 74.4759 | 68.5679 | 72.1602 | 74.7254 | 91.82 | 91.8662 | 92.3533
2022-09-07 18:50 | 0:26 | 47.5921 | 45.9477 | 49.4615 | 65.2241 | 68.2913 | 66.1374 | 70.5822 | 63.8029 | 70.2836 | 67.3218 | 65.1359 | 73.1229 | 63.9997 | 67.5022 | 68.7234 | 67.7771 | 65.7641 | 67.478 | 68.1008 | 69.5107 | 49.8029 | 45.8695 | 54.92 | 66.7775 | 66.1655 | 71.3509 | 69.9341 | 68.5859 | 66.3606 | 69.6428 | 63.4008 | 70.7413 | 66.4622 | 67.5576 | 63.6481 | 69.7912 | 68.4032 | 69.0262 | 71.7703 | 67.8835 | 69.0846 | 70.6403 | 72.3078 | 67.5576 | 70.9197 | 70.868 | 73.3539 | 66.844 | 71.4817 | 69.8309 | 73.8747 | 69.0881 | 73.528 | 69.4756 | 74.0578 | 68.3239 | 71.999 | 74.6232 | 91.8031 | 91.9164 | 92.4504
2022-09-07 18:50 | 0:26 | 47.5228 | 45.818 | 49.3719 | 65.1743 | 68.1672 | 66.1134 | 70.1708 | 63.561 | 70.0239 | 67.0664 | 64.9921 | 72.9087 | 63.8762 | 67.1919 | 68.5407 | 67.5789 | 65.6533 | 67.26 | 67.9639 | 69.3499 | 49.6498 | 45.7408 | 54.8021 | 66.5566 | 66.0032 | 71.3026 | 69.5923 | 68.301 | 66.3688 | 69.4342 | 63.3728 | 70.4917 | 66.1399 | 67.2373 | 63.4368 | 69.5117 | 68.2118 | 68.7027 | 71.3818 | 67.695 | 69.0034 | 70.3584 | 71.9769 | 67.3664 | 70.646 | 70.677 | 73.2528 | 66.8058 | 71.4676 | 69.6819 | 73.6776 | 69.144 | 73.2937 | 69.3168 | 73.911 | 68.0549 | 71.7724 | 74.6682 | 91.8576 | 91.9459 | 92.4982
2022-09-07 18:50 | 0:26 | 47.4891 | 45.7141 | 49.2411 | 64.9767 | 68.0544 | 66.1288 | 70.2998 | 63.3615 | 69.9378 | 67.0675 | 64.9758 | 72.9233 | 63.6174 | 67.5795 | 68.1104 | 67.2795 | 65.5871 | 67.1622 | 67.7439 | 69.2337 | 49.5006 | 45.6303 | 54.6143 | 66.6599 | 65.7731 | 71.282 | 69.5575 | 68.181 | 66.2774 | 69.3551 | 63.2918 | 70.3205 | 65.7189 | 67.1334 | 63.5187 | 69.2685 | 68.0946 | 68.8146 | 71.5088 | 67.5543 | 68.9778 | 70.185 | 71.9162 | 67.0856 | 70.5167 | 70.4518 | 73.2138 | 66.6594 | 71.2503 | 69.5846 | 73.5234 | 68.9476 | 73.2087 | 68.8891 | 74.0797 | 67.9432 | 71.5982 | 74.3344 | 91.9121 | 92.0688 | 92.4994
2022-09-07 18:50 | 0:26 | 47.416 | 45.6383 | 49.1206 | 64.6787 | 67.9315 | 65.6505 | 70.1629 | 63.2285 | 69.7931 | 66.9012 | 64.6421 | 72.603 | 63.5358 | 67.2086 | 67.8895 | 67.2599 | 65.4828 | 67.0005 | 67.4412 | 68.9987 | 49.378 | 45.5518 | 54.5261 | 66.3858 | 65.6266 | 70.9384 | 69.3342 | 68.1404 | 66.0702 | 69.141 | 63.0029 | 70.3079 | 65.6955 | 67.1315 | 63.3875 | 69.511 | 67.7596 | 68.6713 | 71.3336 | 67.3766 | 68.7538 | 70.1314 | 71.8451 | 67.025 | 70.3949 | 70.3924 | 73.0531 | 66.4501 | 71.2887 | 69.3327 | 72.8798 | 68.6711 | 73.033 | 68.6719 | 73.8531 | 67.7969 | 71.5604 | 74.0715 | 92.1514 | 92.1718 | 92.614
2022-09-07 18:50 | 0:26 | 47.3387 | 45.5215 | 49.0604 | 64.6455 | 67.7272 | 65.5617 | 69.7291 | 63.0799 | 69.6699 | 66.6449 | 64.533 | 72.4765 | 63.4125 | 66.9942 | 67.9153 | 67.0849 | 65.3229 | 66.9242 | 67.3535 | 68.7824 | 49.2121 | 45.4015 | 54.4045 | 66.1974 | 65.4532 | 70.7631 | 69.0846 | 68.134 | 65.9121 | 68.9561 | 62.8666 | 69.8983 | 65.582 | 66.8646 | 63.0325 | 69.1636 | 67.7506 | 68.3811 | 71.1784 | 67.191 | 68.5731 | 69.9117 | 71.3826 | 66.8918 | 70.2284 | 70.2791 | 72.925 | 66.3761 | 71.0238 | 69.2404 | 72.9739 | 68.5716 | 73.0363 | 68.4403 | 73.5681 | 67.4258 | 71.6265 | 74.1171 | 92.2836 | 92.2939 | 92.6732
2022-09-07 18:51 | 0:27 | 47.277 | 45.3931 | 48.9143 | 64.487 | 67.4417 | 65.5022 | 69.7709 | 62.8836 | 69.5066 | 66.5054 | 64.2708 | 72.2552 | 63.1766 | 66.908 | 67.7603 | 66.9319 | 65.2089 | 66.5615 | 67.2571 | 68.3351 | 49.1162 | 45.2606 | 54.2303 | 66.0649 | 65.2081 | 70.4742 | 69.0034 | 68.2449 | 65.5974 | 68.8836 | 62.6893 | 69.7145 | 65.3268 | 66.7436 | 62.7966 | 69.0145 | 67.4702 | 68.098 | 71.3302 | 66.9372 | 68.4298 | 69.7144 | 71.4963 | 66.8802 | 70.196 | 70.1465 | 72.6726 | 66.1759 | 71.1532 | 69.0798 | 73.0474 | 68.3484 | 72.576 | 68.2659 | 73.44 | 67.4732 | 71.1993 | 73.9428 | 92.3751 | 92.3579 | 92.7412
2022-09-07 18:51 | 0:27 | 47.1984 | 45.2971 | 48.793 | 64.4251 | 67.4153 | 65.5307 | 69.5204 | 62.7017 | 69.3347 | 66.4904 | 64.048 | 72.1587 | 63.07 | 66.7566 | 67.64 | 66.729 | 64.9718 | 66.8001 | 67.0213 | 68.2197 | 49.0028 | 45.1567 | 54.1279 | 65.9026 | 64.9589 | 70.2822 | 68.9778 | 67.6611 | 65.5147 | 68.6763 | 62.3956 | 69.5454 | 65.383 | 66.6001 | 62.8889 | 68.9504 | 67.425 | 68.1159 | 70.8769 | 66.8544 | 68.2265 | 69.5729 | 71.1661 | 66.6091 | 70.1219 | 69.9158 | 72.7511 | 66.0396 | 70.6539 | 68.819 | 72.9339 | 68.1285 | 72.6183 | 68.2462 | 73.2878 | 67.23 | 71.3062 | 73.4243 | 92.4683 | 92.4592 | 92.8363
2022-09-07 18:51 | 0:27 | 47.1793 | 45.1911 | 48.6454 | 64.2796 | 67.2 | 64.9847 | 69.4068 | 62.5956 | 69.1859 | 66.3277 | 64.1048 | 71.9408 | 62.9157 | 66.5545 | 67.5374 | 66.5696 | 64.8019 | 66.6296 | 66.9398 | 68.2188 | 48.8788 | 45.0626 | 53.9685 | 65.6248 | 64.7932 | 70.2946 | 68.7538 | 67.5854 | 65.3841 | 68.5223 | 62.1868 | 69.4716 | 65.0586 | 66.289 | 62.5407 | 68.7055 | 67.1434 | 67.8698 | 70.908 | 66.6622 | 68.2785 | 69.3782 | 70.924 | 66.6388 | 69.7769 | 69.7528 | 72.2875 | 65.8386 | 70.6939 | 68.7831 | 72.1683 | 68.0029 | 72.3542 | 67.9195 | 72.8438 | 66.9655 | 70.9254 | 73.3933 | 92.5156 | 92.5596 | 92.8385
2022-09-07 18:51 | 0:27 | 47.0698 | 45.0683 | 48.5615 | 64.0763 | 67.0781 | 64.8807 | 69.187 | 62.3417 | 68.9984 | 66.3343 | 63.9035 | 71.8232 | 62.6639 | 66.4835 | 67.3939 | 66.3519 | 64.5931 | 66.1607 | 66.6363 | 67.9977 | 48.7801 | 44.9473 | 53.8519 | 65.4893 | 64.7137 | 70.0831 | 68.5731 | 66.7514 | 65.1039 | 68.3702 | 62.0365 | 69.2592 | 64.7234 | 66.2255 | 62.4669 | 68.5732 | 67.23 | 67.7804 | 70.7757 | 66.5669 | 67.8596 | 69.3465 | 70.9511 | 66.3979 | 69.7331 | 69.5907 | 72.0458 | 65.5685 | 70.3863 | 68.5497 | 72.6166 | 67.9479 | 72.18 | 67.9966 | 72.4388 | 67.0086 | 70.6999 | 73.3313 | 92.5935 | 92.6264 | 92.8333
2022-09-07 18:51 | 0:27 | 47.009 | 44.9845 | 48.4419 | 64.0575 | 66.8695 | 64.8679 | 68.9985 | 62.3205 | 68.8176 | 65.944 | 64.1017 | 71.672 | 62.5669 | 65.8124 | 67.2045 | 66.2105 | 64.4445 | 65.7926 | 66.4712 | 68.0868 | 48.6572 | 44.8247 | 53.7163 | 65.4019 | 64.5997 | 69.9982 | 68.4298 | 66.831 | 64.9245 | 68.2679 | 61.8304 | 69.2038 | 64.6262 | 65.9933 | 62.3878 | 68.3702 | 67.1339 | 67.4549 | 70.2825 | 66.3864 | 67.6737 | 69.2011 | 70.6723 | 66.0983 | 69.6962 | 69.4078 | 72.1226 | 65.4739 | 70.4919 | 68.2689 | 72.3892 | 67.605 | 71.966 | 68.0001 | 72.6956 | 66.7354 | 70.5422 | 73.2865 | 92.7027 | 92.6742 | 92.8491
2022-09-07 18:51 | 0:27 | 46.8463 | 44.8723 | 48.3256 | 63.6612 | 66.7925 | 64.5035 | 68.767 | 62.2546 | 68.5885 | 65.6917 | 64.0113 | 71.483 | 62.3803 | 66.036 | 67.0518 | 66.0942 | 64.2713 | 65.6304 | 66.3249 | 67.9727 | 48.5585 | 44.7121 | 53.5666 | 65.2185 | 64.4271 | 69.989 | 68.2265 | 66.9251 | 64.9624 | 68.0286 | 61.7048 | 69.0666 | 64.4164 | 65.9868 | 62.1679 | 68.0341 | 66.8638 | 67.3567 | 69.8944 | 66.1962 | 67.615 | 68.8231 | 70.6522 | 66.1409 | 69.3813 | 69.3945 | 72.0144 | 65.3406 | 70.3873 | 68.1841 | 72.1237 | 67.5365 | 71.8615 | 67.7231 | 72.5794 | 66.5596 | 70.4618 | 72.9943 | 92.7883 | 92.7508 | 92.9035
2022-09-07 18:52 | 0:27 | 46.7122 | 44.7756 | 48.2251 | 63.577 | 66.4491 | 63.985 | 68.6819 | 62.2043 | 68.4676 | 65.5351 | 63.8049 | 71.4685 | 62.1804 | 66.1062 | 67.0156 | 65.7669 | 64.1394 | 65.7322 | 66.1138 | 67.6382 | 48.4461 | 44.6067 | 53.3852 | 65.2339 | 64.1844 | 69.8268 | 68.2785 | 66.9698 | 64.6686 | 67.9074 | 61.7244 | 68.8987 | 64.2365 | 65.7332 | 61.8625 | 67.981 | 66.9287 | 67.124 | 70.0171 | 66.1197 | 67.3953 | 68.7155 | 70.6034 | 65.9549 | 69.1957 | 69.2633 | 71.7821 | 65.2289 | 70.2373 | 68.1018 | 72.1378 | 67.4782 | 71.6587 | 67.336 | 72.787 | 66.428 | 70.3688 | 72.8521 | 92.8521 | 92.8098 | 92.9679
2022-09-07 18:52 | 0:28 | 46.6122 | 44.6902 | 48.14 | 63.3815 | 66.5788 | 63.966 | 68.1066 | 61.9258 | 68.2995 | 65.3713 | 63.511 | 71.2384 | 62.0908 | 66.0117 | 66.624 | 65.7076 | 63.9482 | 65.8732 | 66.1699 | 67.4562 | 48.3198 | 44.4953 | 53.3143 | 64.993 | 63.9567 | 69.6031 | 67.8596 | 66.5502 | 64.4041 | 67.8367 | 61.7531 | 68.5672 | 64.2344 | 65.5467 | 61.8102 | 67.8426 | 66.5256 | 66.833 | 70.4084 | 65.9783 | 67.1768 | 68.6859 | 70.353 | 65.8765 | 69.1368 | 69.073 | 71.7997 | 65.2106 | 69.8132 | 67.8738 | 71.7896 | 67.1793 | 71.2017 | 67.2177 | 72.5502 | 66.274 | 70.1506 | 72.6884 | 92.9404 | 92.9763 | 93.0584
2022-09-07 18:52 | 0:28 | 46.5295 | 44.5718 | 47.9987 | 63.3462 | 66.3236 | 63.7382 | 68.2839 | 61.7341 | 68.2512 | 65.1328 | 63.1495 | 71.0005 | 61.8115 | 65.7549 | 66.4448 | 65.6431 | 63.8409 | 65.5089 | 65.8526 | 67.1131 | 48.1787 | 44.3726 | 53.1639 | 64.862 | 63.8965 | 69.5527 | 67.6737 | 66.256 | 64.3723 | 67.5504 | 61.5216 | 68.4938 | 64.2963 | 65.3567 | 61.5433 | 67.7561 | 66.2427 | 66.9891 | 70.011 | 65.8205 | 67.0734 | 68.5479 | 70.3373 | 65.554 | 69.0277 | 68.8845 | 71.308 | 64.8774 | 69.7764 | 67.6655 | 71.6526 | 67.0591 | 71.189 | 66.9369 | 72.1794 | 66.0141 | 69.9605 | 72.5037 | 93.0813 | 93.0977 | 93.1324
2022-09-07 18:52 | 0:28 | 46.4111 | 44.4668 | 47.8836 | 63.1145 | 66.1259 | 63.9259 | 68.2514 | 61.6427 | 68.1035 | 65.1144 | 63.1907 | 70.8398 | 61.7045 | 65.4834 | 66.2621 | 65.4527 | 63.6457 | 65.5348 | 65.7439 | 67.0929 | 48.0577 | 44.2536 | 53.0219 | 64.6729 | 63.6431 | 69.2271 | 67.615 | 66.2737 | 64.2634 | 67.4359 | 61.3736 | 68.2339 | 63.8948 | 65.096 | 61.2814 | 67.7294 | 66.2675 | 66.7757 | 69.9593 | 65.6075 | 66.9627 | 68.4049 | 70.2959 | 65.4364 | 68.8164 | 68.7589 | 71.2951 | 64.6741 | 69.4823 | 67.4134 | 71.7042 | 66.4956 | 71.0734 | 66.8581 | 71.9175 | 65.7827 | 69.7486 | 72.256 | 93.1858 | 93.1704 | 93.191
2022-09-07 18:52 | 0:28 | 46.2812 | 44.3629 | 47.778 | 62.8349 | 65.976 | 63.5671 | 68.0228 | 61.4361 | 67.9239 | 64.9119 | 63.3604 | 70.7208 | 61.7237 | 65.3243 | 66.0121 | 65.299 | 63.4635 | 65.3376 | 65.5972 | 67.0491 | 47.9415 | 44.1268 | 52.8959 | 64.6239 | 63.4644 | 68.9317 | 67.3953 | 66.3819 | 63.922 | 67.207 | 61.0971 | 68.163 | 63.7335 | 65.0776 | 61.405 | 67.3412 | 66.0895 | 66.7291 | 69.5704 | 65.5643 | 66.7531 | 68.2862 | 69.9899 | 65.3875 | 68.5993 | 68.5416 | 71.3488 | 64.6105 | 69.8739 | 67.4048 | 71.3072 | 66.4005 | 71.0156 | 66.674 | 71.9042 | 65.7544 | 69.8406 | 72.2581 | 93.2943 | 93.362 | 93.2651
2022-09-07 18:52 | 0:28 | 46.1212 | 44.2385 | 47.6532 | 62.7837 | 65.8637 | 63.4401 | 67.7145 | 61.3245 | 67.7834 | 64.8385 | 63.2651 | 70.5014 | 61.4653 | 65.1419 | 66.1077 | 65.1746 | 63.4268 | 65.007 | 65.5622 | 66.8304 | 47.8229 | 44.0185 | 52.762 | 64.3226 | 63.3616 | 68.8508 | 67.1768 | 66.006 | 63.7429 | 67.1641 | 60.9282 | 67.9729 | 63.6618 | 64.9972 | 61.2405 | 67.2137 | 65.6975 | 66.4262 | 69.2426 | 65.256 | 66.6526 | 68.0445 | 69.695 | 65.1333 | 68.517 | 68.3895 | 70.9314 | 64.4852 | 69.5076 | 67.3487 | 71.1426 | 66.3594 | 70.8792 | 66.6752 | 71.6306 | 65.5558 | 69.535 | 71.8603 | 93.4001 | 93.4349 | 93.3312
2022-09-07 18:53 | 0:29 | 45.9697 | 44.1379 | 47.5431 | 62.7929 | 65.7006 | 63.0847 | 67.6517 | 61.1409 | 67.5911 | 64.563 | 62.931 | 70.4769 | 61.309 | 65.2895 | 65.9446 | 64.919 | 63.1375 | 65.0827 | 65.2404 | 66.6066 | 47.7147 | 43.8701 | 52.6941 | 64.1844 | 63.1409 | 68.8001 | 67.0734 | 66.1455 | 63.6745 | 67.0412 | 60.8128 | 67.8108 | 63.3478 | 64.9504 | 60.6445 | 67.0293 | 65.7119 | 66.2454 | 69.2212 | 65.1351 | 66.5908 | 67.9855 | 69.5756 | 65.0777 | 68.3369 | 68.2201 | 71.0116 | 64.2871 | 69.1191 | 67.1851 | 71.234 | 66.2654 | 70.7232 | 66.5375 | 71.5063 | 65.365 | 69.6552 | 71.6598 | 93.5161 | 93.5751 | 93.4023
2022-09-07 18:53 | 0:29 | 45.8123 | 44.0337 | 47.3832 | 62.6857 | 65.5096 | 63.2103 | 67.6388 | 60.9051 | 67.4782 | 64.5744 | 62.6943 | 70.283 | 61.1337 | 64.951 | 65.5509 | 64.7799 | 63.1305 | 64.5804 | 65.0115 | 66.5367 | 47.6111 | 43.7551 | 52.559 | 64.0166 | 63.0198 | 68.8807 | 66.9627 | 65.8169 | 63.5359 | 66.8676 | 60.6474 | 67.6074 | 63.4105 | 64.7453 | 60.1327 | 67.0506 | 65.4546 | 66.2005 | 69.5598 | 64.976 | 66.5096 | 67.7433 | 69.3328 | 64.9991 | 68.2214 | 68.1362 | 70.6031 | 64.0146 | 68.8308 | 67.0702 | 70.4393 | 66.3599 | 70.3836 | 66.2835 | 71.5821 | 65.2806 | 69.2021 | 71.5518 | 93.5504 | 93.6627 | 93.4566
2022-09-07 18:53 | 0:29 | 45.6135 | 43.9275 | 47.2807 | 62.4672 | 65.3786 | 63.2314 | 67.8155 | 60.758 | 67.2997 | 64.4129 | 62.277 | 70.1398 | 61.144 | 64.6707 | 65.659 | 64.7323 | 62.9851 | 64.2925 | 65.0288 | 66.3979 | 47.5319 | 43.6764 | 52.4565 | 63.8242 | 62.8658 | 68.528 | 66.7531 | 65.3722 | 63.6039 | 66.7179 | 60.4684 | 67.4173 | 63.2389 | 64.5432 | 59.9349 | 66.5892 | 65.4256 | 65.9599 | 68.8258 | 64.9159 | 66.1392 | 67.6107 | 69.2909 | 64.8155 | 68.1239 | 67.992 | 70.8251 | 63.9957 | 68.7252 | 66.8143 | 70.1349 | 66.2784 | 70.3339 | 66.2047 | 71.2592 | 65.2524 | 69.1673 | 71.6688 | 93.7064 | 93.7968 | 93.4232
2022-09-07 18:53 | 0:29 | 45.4849 | 43.8069 | 47.1557 | 62.467 | 65.3949 | 63.0361 | 67.5202 | 60.6627 | 67.1231 | 64.2619 | 62.3575 | 69.969 | 60.9919 | 64.5446 | 65.3607 | 64.4571 | 62.7717 | 64.2749 | 64.7931 | 66.4564 | 47.4055 | 43.556 | 52.3241 | 63.7578 | 62.6977 | 68.3759 | 66.6526 | 64.9834 | 63.3225 | 66.4937 | 60.3482 | 67.2211 | 63.1942 | 64.4927 | 59.5761 | 66.7218 | 65.1828 | 65.9186 | 68.4498 | 64.7063 | 66.1802 | 67.5381 | 68.9412 | 64.5963 | 67.9826 | 67.8243 | 70.5267 | 63.8568 | 68.6137 | 66.5682 | 70.5511 | 66.1686 | 70.3044 | 65.7385 | 71.2977 | 64.9428 | 69.0848 | 71.4495 | 94.0112 | 93.963 | 93.7023
2022-09-07 18:53 | 0:29 | 45.3321 | 43.7181 | 47.0122 | 62.057 | 65.1479 | 62.9072 | 67.408 | 60.5931 | 67.0841 | 64.1405 | 62.2189 | 69.8945 | 60.8091 | 64.5798 | 65.4692 | 64.3325 | 62.672 | 64.3678 | 64.5517 | 66.0185 | 47.2915 | 43.425 | 52.1842 | 63.5995 | 62.5819 | 68.3368 | 66.5908 | 65.2115 | 63.2654 | 66.3781 | 60.282 | 67.1976 | 62.8819 | 64.2227 | 59.5644 | 66.442 | 65.2758 | 65.7275 | 68.6561 | 64.5756 | 66.0323 | 67.3538 | 68.8578 | 64.4783 | 67.6939 | 67.6359 | 70.5178 | 63.758 | 68.4981 | 66.5282 | 70.4461 | 65.8866 | 70.1054 | 65.4929 | 71.0388 | 64.7681 | 68.9088 | 71.1379 | 94.1146 | 94.2381 | 93.7709
2022-09-07 18:53 | 0:29 | 45.1272 | 43.5558 | 46.8819 | 61.9705 | 64.9917 | 62.981 | 67.0665 | 60.4347 | 66.8703 | 63.764 | 62.1583 | 69.6675 | 60.6812 | 64.3896 | 65.0928 | 64.1481 | 62.5224 | 64.1362 | 64.47 | 65.9456 | 47.1706 | 43.2745 | 52.0159 | 63.4269 | 62.4023 | 68.1338 | 66.5096 | 65.1404 | 63.033 | 66.2631 | 60.2107 | 66.7478 | 62.7546 | 63.9031 | 59.3625 | 66.1329 | 65.2098 | 65.48 | 68.6539 | 64.5479 | 65.803 | 67.2007 | 68.6958 | 64.2803 | 67.6233 | 67.5062 | 70.1274 | 63.5435 | 68.2631 | 66.306 | 70.085 | 65.6608 | 70.0016 | 65.2801 | 70.7586 | 64.642 | 68.5587 | 70.847 | 94.3483 | 94.3723 | 93.9994
2022-09-07 18:54 | 0:29 | 45.0382 | 43.4513 | 46.7443 | 61.9597 | 64.9176 | 62.6568 | 67.0336 | 60.2182 | 66.7072 | 63.8991 | 62.0983 | 69.4853 | 60.4078 | 64.2147 | 64.9179 | 64.0054 | 62.2518 | 63.8432 | 64.2567 | 65.8042 | 47.0804 | 43.1596 | 51.9552 | 63.299 | 62.2303 | 67.9944 | 66.1392 | 64.7927 | 62.8105 | 66.1064 | 59.8672 | 66.7426 | 62.7642 | 63.8809 | 59.1809 | 66.1423 | 65.017 | 65.4073 | 68.3484 | 64.3026 | 65.5352 | 67.0045 | 68.4384 | 64.1264 | 67.5354 | 67.354 | 70.0756 | 63.3439 | 68.2492 | 66.3135 | 70.0908 | 65.3598 | 69.8667 | 65.1803 | 70.7378 | 64.48 | 68.4838 | 70.8917 | 94.4972 | 94.4775 | 94.0191
2022-09-07 18:54 | 0:30 | 44.9059 | 43.3169 | 46.5992 | 61.6976 | 64.6924 | 62.429 | 66.8427 | 60.2056 | 66.6399 | 63.6499 | 62.1094 | 69.1514 | 60.293 | 63.8267 | 64.7035 | 63.9004 | 62.1519 | 63.8732 | 64.0954 | 65.7879 | 46.9616 | 43.0624 | 51.8344 | 63.0703 | 62.1418 | 67.8372 | 66.1802 | 64.4385 | 62.6798 | 65.984 | 59.7436 | 66.5845 | 62.5053 | 63.5615 | 59.1667 | 65.8695 | 64.9523 | 65.1971 | 68.3161 | 64.1987 | 65.4817 | 66.9598 | 68.3534 | 63.9668 | 67.3897 | 67.1819 | 69.8638 | 63.2605 | 68.2494 | 66.0745 | 69.74 | 65.1817 | 69.6299 | 65.2982 | 70.4127 | 64.3511 | 68.3769 | 70.8384 | 94.6309 | 94.6513 | 94.1356
2022-09-07 18:54 | 0:30 | 44.7699 | 43.1933 | 46.468 | 61.5165 | 64.5901 | 62.3837 | 66.7681 | 59.9161 | 66.4813 | 63.575 | 61.7733 | 69.056 | 60.1838 | 63.9047 | 64.5176 | 63.7142 | 61.9905 | 64.0094 | 63.9688 | 65.6805 | 46.8308 | 42.9356 | 51.6865 | 63.0768 | 61.8525 | 67.7237 | 66.0323 | 64.1366 | 62.5695 | 65.6949 | 59.7248 | 66.5072 | 62.3705 | 63.6011 | 58.9121 | 65.7972 | 64.5518 | 65.1882 | 67.6428 | 63.9903 | 65.3436 | 66.7241 | 68.1235 | 63.9174 | 67.2017 | 67.0725 | 69.6508 | 63.0448 | 67.9777 | 65.9265 | 69.4038 | 65.1789 | 69.4245 | 65.1685 | 70.526 | 64.2976 | 68.1346 | 70.5804 | 94.7203 | 94.8701 | 94.2457
2022-09-07 18:54 | 0:30 | 44.6446 | 43.0635 | 46.3621 | 61.5118 | 64.4518 | 62.2214 | 66.3913 | 59.8702 | 66.3485 | 63.3722 | 61.5795 | 69.0366 | 59.9311 | 64.0155 | 64.4287 | 63.5727 | 61.8125 | 63.7432 | 63.8899 | 65.5962 | 46.7255 | 42.792 | 51.5605 | 62.9559 | 61.716 | 67.5628 | 65.803 | 64.4238 | 62.3156 | 65.7304 | 59.3556 | 66.4471 | 62.137 | 63.5287 | 58.8922 | 65.7267 | 64.451 | 64.8741 | 67.2733 | 63.8145 | 65.214 | 66.6594 | 68.1313 | 63.7267 | 67.2467 | 66.9124 | 69.7069 | 62.8923 | 68.045 | 65.8085 | 69.5644 | 64.8811 | 69.1055 | 64.9424 | 70.0993 | 64.0378 | 67.8868 | 70.433 | 94.9227 | 95.0677 | 94.4245
2022-09-07 18:54 | 0:30 | 44.4785 | 43.001 | 46.19 | 61.2666 | 64.4106 | 61.9072 | 66.1555 | 59.8477 | 66.2693 | 63.1013 | 61.6248 | 68.7476 | 59.791 | 63.8595 | 64.2859 | 63.389 | 61.6531 | 63.8222 | 63.6656 | 65.2568 | 46.6016 | 42.6917 | 51.4726 | 62.7875 | 61.5829 | 67.3448 | 65.5352 | 64.1795 | 62.1274 | 65.3892 | 59.2002 | 66.2585 | 61.942 | 63.346 | 59.3716 | 65.7009 | 64.2021 | 64.8111 | 67.4897 | 63.6527 | 65.1128 | 66.4684 | 67.9782 | 63.5358 | 66.9786 | 66.695 | 69.6409 | 62.7587 | 67.7684 | 65.6692 | 69.2196 | 65.0393 | 68.9372 | 65.0137 | 70.0532 | 63.9018 | 67.684 | 70.3473 | 94.9921 | 95.0504 | 94.3205
2022-09-07 18:54 | 0:30 | 44.2586 | 42.8416 | 46.0081 | 60.9896 | 64.1239 | 61.7741 | 66.3773 | 59.5183 | 66.1163 | 62.9484 | 61.4181 | 68.6803 | 59.7207 | 63.5956 | 64.1992 | 63.206 | 61.4974 | 63.1359 | 63.6256 | 65.044 | 46.4666 | 42.5534 | 51.3007 | 62.6125 | 61.4004 | 67.2588 | 65.4817 | 64.2442 | 62.0083 | 65.2828 | 58.9774 | 66.0233 | 61.8986 | 63.0965 | 59.2135 | 65.5726 | 63.9761 | 64.6403 | 67.44 | 63.4509 | 64.8822 | 66.3193 | 68.0129 | 63.3274 | 66.8893 | 66.551 | 69.1976 | 62.7439 | 67.3091 | 65.4934 | 69.4443 | 64.6092 | 69.1071 | 64.671 | 69.9866 | 63.8394 | 67.7743 | 70.1504 | 95.0901 | 95.1191 | 94.412
2022-09-07 18:55 | 0:31 | 44.0448 | 42.7143 | 45.8232 | 61.135 | 64.0309 | 61.8435 | 65.9615 | 59.3934 | 65.888 | 62.8928 | 61.0832 | 68.5825 | 59.5868 | 63.3594 | 64.145 | 63.0475 | 61.3873 | 62.7432 | 63.449 | 65.1207 | 46.3666 | 42.4217 | 51.1304 | 62.4075 | 61.2367 | 67.3802 | 65.3436 | 64.2005 | 61.7707 | 65.197 | 58.9278 | 65.9681 | 61.7414 | 62.9351 | 59.2132 | 65.3752 | 64.1081 | 64.2837 | 66.9886 | 63.4216 | 64.7075 | 66.2218 | 67.8851 | 63.2376 | 66.7447 | 66.4512 | 69.1977 | 62.6242 | 67.3951 | 65.251 | 69.2798 | 64.5807 | 68.9064 | 64.441 | 69.7294 | 63.6507 | 67.3821 | 69.8462 | 94.9664 | 95.0766 | 94.3813
2022-09-07 18:55 | 0:31 | 43.9208 | 42.5886 | 45.7276 | 60.9588 | 63.9152 | 61.7161 | 65.6596 | 59.2304 | 65.7044 | 62.6848 | 60.8391 | 68.44 | 59.3562 | 63.1136 | 63.8279 | 62.9332 | 61.2987 | 62.9011 | 63.1707 | 64.7614 | 46.2538 | 42.2782 | 51.0534 | 62.2268 | 61.0833 | 67.1656 | 65.214 | 63.6861 | 61.7138 | 64.9882 | 58.8577 | 65.8806 | 61.5334 | 62.9367 | 59.0947 | 65.5121 | 64.0991 | 64.3231 | 67.1431 | 63.3161 | 64.6139 | 65.9283 | 67.7544 | 63.1855 | 66.5946 | 66.3557 | 69.0172 | 62.4676 | 67.3431 | 65.1638 | 69.3198 | 64.6279 | 68.7677 | 64.3723 | 69.2078 | 63.379 | 67.4535 | 69.9674 | 94.7539 | 94.9562 | 94.1828
2022-09-07 18:55 | 0:31 | 43.6828 | 42.4775 | 45.5259 | 60.9363 | 63.6868 | 61.7359 | 65.8229 | 59.1724 | 65.5934 | 62.4946 | 60.7298 | 68.2789 | 59.2776 | 62.9571 | 63.6778 | 62.7254 | 61.1506 | 62.6675 | 63.0092 | 64.8748 | 46.1334 | 42.191 | 50.931 | 62.0886 | 60.9496 | 66.9856 | 65.1128 | 63.715 | 61.6343 | 64.9641 | 58.6816 | 65.6795 | 61.428 | 62.7376 | 58.8445 | 65.0575 | 63.9394 | 64.1592 | 67.0754 | 63.1429 | 64.414 | 65.9039 | 67.561 | 62.8676 | 66.4206 | 66.0895 | 68.8239 | 62.3163 | 66.9833 | 65.1343 | 68.6187 | 64.0822 | 68.4589 | 64.3122 | 69.5821 | 63.3312 | 67.1817 | 69.7841 | 94.5682 | 94.7711 | 94.0674
2022-09-07 18:55 | 0:31 | 43.513 | 42.3558 | 45.3522 | 60.6796 | 63.6375 | 61.3233 | 65.4868 | 59.0837 | 65.5212 | 62.5816 | 61.0053 | 68.158 | 59.1711 | 62.5814 | 63.5191 | 62.647 | 60.9731 | 62.6687 | 62.9806 | 64.4809 | 46.0207 | 42.0757 | 50.7765 | 62.073 | 60.7661 | 66.6015 | 64.8822 | 63.276 | 61.4896 | 64.6249 | 58.4561 | 65.4145 | 61.0963 | 62.5049 | 58.7473 | 64.9275 | 63.6917 | 63.9977 | 67.0575 | 62.9145 | 64.3204 | 65.8655 | 67.3291 | 62.699 | 66.2614 | 65.9349 | 68.7416 | 62.1888 | 66.6921 | 64.9204 | 68.8691 | 63.967 | 68.514 | 64.0799 | 69.5445 | 63.1891 | 66.9997 | 69.3983 | 94.3692 | 94.5317 | 93.8777
2022-09-07 18:55 | 0:31 | 43.4039 | 42.2063 | 45.2507 | 60.4751 | 63.5897 | 61.2143 | 65.4412 | 58.9644 | 65.3334 | 62.271 | 60.6232 | 68.0503 | 58.9657 | 62.6056 | 63.4033 | 62.4748 | 60.8832 | 62.2861 | 62.7273 | 64.2192 | 45.864 | 41.9418 | 50.6833 | 61.9007 | 60.6396 | 66.4737 | 64.7075 | 63.6189 | 61.3469 | 64.5916 | 58.5379 | 65.431 | 60.9229 | 62.3204 | 58.6605 | 64.8075 | 63.3387 | 63.8419 | 66.8627 | 62.7714 | 64.1579 | 65.6001 | 67.1096 | 62.4425 | 66.1242 | 65.8729 | 68.3728 | 62.0556 | 66.6474 | 64.6744 | 68.1407 | 63.7677 | 68.3782 | 63.8442 | 69.2765 | 63.0612 | 66.7192 | 69.1493 | 94.1578 | 94.3857 | 93.8356
2022-09-07 18:55 | 0:31 | 43.1818 | 42.0976 | 45.057 | 60.3581 | 63.4624 | 61.0745 | 65.2817 | 58.8115 | 65.1674 | 62.154 | 60.4563 | 67.8518 | 58.9197 | 62.669 | 63.0996 | 62.3225 | 60.7488 | 62.4996 | 62.6506 | 64.1625 | 45.7532 | 41.8188 | 50.5276 | 61.726 | 60.4393 | 66.3187 | 64.6139 | 63.1691 | 61.151 | 64.3931 | 58.28 | 65.2122 | 60.8713 | 62.1816 | 58.557 | 64.605 | 63.1766 | 63.7383 | 66.5466 | 62.6418 | 64.1572 | 65.4563 | 66.8463 | 62.4794 | 65.9308 | 65.7143 | 68.4416 | 61.8952 | 66.6811 | 64.5104 | 68.183 | 63.7675 | 68.324 | 63.8302 | 68.7131 | 62.8248 | 66.5637 | 69.0987 | 94.0425 | 94.2106 | 93.7735
2022-09-07 18:56 | 0:31 | 43.0442 | 41.963 | 44.9098 | 60.2383 | 63.1218 | 60.9143 | 65.3143 | 58.6521 | 65.0707 | 62.1977 | 60.4013 | 67.7929 | 58.659 | 62.4852 | 63.1843 | 62.1736 | 60.5828 | 61.9339 | 62.4606 | 64.1887 | 45.5941 | 41.7112 | 50.3919 | 61.6175 | 60.2948 | 66.3332 | 64.414 | 63.2087 | 61.0623 | 64.3181 | 58.1609 | 65.0727 | 60.7237 | 62.1531 | 58.4113 | 64.3454 | 63.2316 | 63.6292 | 66.1098 | 62.5799 | 64.0376 | 65.3255 | 66.8078 | 62.3982 | 65.7321 | 65.6072 | 68.4057 | 61.6602 | 66.3819 | 64.3005 | 68.0961 | 63.5816 | 67.8857 | 63.5843 | 68.8409 | 62.6928 | 66.5382 | 68.943 | 93.9146 | 94.1979 | 93.7653
2022-09-07 18:56 | 0:32 | 43.0214 | 41.8616 | 44.8162 | 60.1041 | 63.0736 | 60.5735 | 65.2034 | 58.3708 | 64.8893 | 61.9504 | 60.312 | 67.5156 | 58.5617 | 62.2266 | 63.103 | 62.044 | 60.4168 | 62.0091 | 62.3569 | 63.8931 | 45.4564 | 41.5962 | 50.2497 | 61.3246 | 60.1859 | 66.282 | 64.3204 | 63.0864 | 60.8555 | 64.1279 | 58.0839 | 64.8447 | 60.5039 | 62.0236 | 58.1437 | 64.3287 | 63.0865 | 63.4318 | 66.4346 | 62.3287 | 63.7588 | 65.1239 | 66.7315 | 62.1423 | 65.7144 | 65.4016 | 68.3588 | 61.5623 | 66.3704 | 64.2008 | 67.7825 | 63.5009 | 67.8904 | 63.4045 | 68.4547 | 62.6218 | 66.5109 | 68.8602 | 93.8559 | 94.0992 | 93.7189
2022-09-07 18:56 | 0:32 | 42.9881 | 41.7229 | 44.7287 | 59.7733 | 63.0348 | 60.4461 | 64.9347 | 58.2108 | 64.7881 | 61.8945 | 60.1937 | 67.5964 | 58.4134 | 62.0446 | 62.9011 | 61.8747 | 60.3192 | 61.7525 | 62.098 | 63.5797 | 45.3441 | 41.4451 | 50.1361 | 61.3655 | 59.989 | 66.1848 | 64.1579 | 62.8521 | 60.6027 | 64.0744 | 57.8077 | 64.6998 | 60.4758 | 61.924 | 58.182 | 64.0153 | 62.7725 | 63.3125 | 66.0654 | 62.1754 | 63.5743 | 64.8995 | 66.6361 | 62.2782 | 65.5016 | 65.3703 | 68.0998 | 61.4033 | 66.2687 | 63.8398 | 67.6489 | 63.5515 | 67.8022 | 63.2725 | 68.4135 | 62.3387 | 66.4208 | 68.6374 | 93.849 | 94.0527 | 93.6806
2022-09-07 18:56 | 0:32 | 42.8332 | 41.5899 | 44.5674 | 59.8253 | 62.7728 | 60.2627 | 64.8544 | 58.1922 | 64.6904 | 61.6541 | 60.0914 | 67.4185 | 58.3159 | 61.8175 | 62.8154 | 61.7269 | 60.1813 | 61.7378 | 62.1385 | 63.4558 | 45.2195 | 41.317 | 50.0572 | 61.0686 | 59.8709 | 66.0713 | 64.1572 | 62.4513 | 60.5367 | 63.9894 | 57.6324 | 64.5618 | 60.2565 | 61.737 | 58.1489 | 63.8461 | 62.9624 | 63.0732 | 66.0666 | 62.2049 | 63.6016 | 64.7345 | 66.6128 | 62.1457 | 65.4818 | 65.1556 | 67.6782 | 61.3391 | 66.4093 | 63.7712 | 67.6673 | 63.2588 | 67.5024 | 63.2283 | 68.6634 | 62.1854 | 66.0643 | 68.6485 | 93.8144 | 94.0243 | 93.6494
2022-09-07 18:56 | 0:32 | 42.6168 | 41.4489 | 44.3991 | 59.7077 | 62.71 | 60.0345 | 64.7264 | 58.0512 | 64.4943 | 61.7236 | 59.9685 | 67.1263 | 58.1119 | 61.7979 | 62.4042 | 61.5531 | 59.9722 | 61.8177 | 61.9597 | 63.6598 | 45.1292 | 41.1774 | 49.9447 | 61.0904 | 59.7477 | 65.8312 | 64.0376 | 62.4557 | 60.4395 | 63.849 | 57.4264 | 64.4498 | 60.2042 | 61.6617 | 57.8674 | 63.9121 | 62.72 | 62.9729 | 65.9634 | 62.0246 | 63.4144 | 64.6316 | 66.3442 | 61.9565 | 65.2771 | 65.1001 | 67.7126 | 61.1878 | 66.16 | 63.626 | 67.5608 | 63.1036 | 67.5245 | 62.8821 | 68.1272 | 62.139 | 65.9779 | 68.2433 | 93.7233 | 94.032 | 93.6318
2022-09-07 18:56 | 0:32 | 42.3938 | 41.3443 | 44.2101 | 59.4363 | 62.6881 | 60.2056 | 64.4428 | 58.0373 | 64.3153 | 61.7387 | 59.8955 | 66.984 | 57.9236 | 61.5221 | 62.3274 | 61.5135 | 59.8533 | 61.3501 | 61.8266 | 63.4494 | 45.0297 | 41.0687 | 49.8041 | 60.8932 | 59.4911 | 65.638 | 63.7588 | 62.1588 | 60.1826 | 63.6838 | 57.3111 | 64.2736 | 59.9952 | 61.4336 | 57.7579 | 63.6307 | 62.5965 | 62.8527 | 65.4606 | 61.8723 | 63.1362 | 64.4947 | 66.4795 | 61.7379 | 65.1492 | 64.872 | 67.538 | 60.9769 | 65.9468 | 63.6564 | 67.6796 | 62.8179 | 67.3066 | 62.6775 | 68.3544 | 62.0148 | 65.9556 | 68.3545 | 93.6954 | 93.9363 | 93.5803
2022-09-07 18:57 | 0:32 | 42.1623 | 41.1771 | 44.1353 | 59.3521 | 62.23 | 60.1073 | 64.341 | 57.7796 | 64.1906 | 61.7195 | 59.5065 | 67.002 | 57.7709 | 61.5009 | 62.164 | 61.3112 | 59.7239 | 61.5579 | 61.6575 | 63.2871 | 44.8931 | 40.9393 | 49.6876 | 60.886 | 59.4894 | 65.1917 | 63.5743 | 62.3057 | 60.2177 | 63.3789 | 56.9462 | 64.1373 | 60.0358 | 61.3031 | 57.6692 | 63.5776 | 62.2071 | 62.7297 | 65.0593 | 61.7126 | 63.2687 | 64.2996 | 66.1076 | 61.6993 | 64.9812 | 64.7926 | 67.4322 | 60.8472 | 66.1644 | 63.4322 | 67.5639 | 62.6047 | 67.0556 | 62.6246 | 67.9745 | 61.8563 | 65.8672 | 68.1697 | 93.614 | 93.8149 | 93.5452
2022-09-07 18:57 | 0:33 | 42.0139 | 41.0794 | 43.9742 | 59.3386 | 62.2942 | 59.8882 | 64.3927 | 57.6887 | 64.0749 | 61.2941 | 59.6242 | 66.8684 | 57.6745 | 61.6024 | 61.8957 | 61.1853 | 59.5615 | 61.321 | 61.5178 | 63.0917 | 44.7712 | 40.8107 | 49.4984 | 60.6331 | 59.271 | 65.2997 | 63.6016 | 62.1148 | 59.9189 | 63.3009 | 57.2587 | 64.0049 | 59.6991 | 61.1403 | 57.4948 | 63.3317 | 62.3663 | 62.5792 | 65.4138 | 61.643 | 63.1202 | 64.2393 | 65.7635 | 61.5857 | 64.7374 | 64.5666 | 67.303 | 60.788 | 65.7379 | 63.2853 | 67.4089 | 62.5768 | 67.1379 | 62.4901 | 67.8101 | 61.6804 | 65.7378 | 67.7608 | 93.5506 | 93.7273 | 93.5098
2022-09-07 18:57 | 0:33 | 41.8603 | 40.9228 | 43.8358 | 59.122 | 62.1843 | 59.776 | 64.1334 | 57.4805 | 63.9371 | 61.3221 | 59.217 | 66.6278 | 57.5813 | 61.3505 | 61.9801 | 61.0454 | 59.458 | 61.2237 | 61.3154 | 62.8745 | 44.6234 | 40.6804 | 49.3986 | 60.52 | 59.1295 | 65.239 | 63.4144 | 61.8445 | 59.8096 | 63.0513 | 57.1134 | 63.8976 | 59.5374 | 60.9661 | 57.424 | 63.1803 | 62.1981 | 62.4849 | 65.3544 | 61.3788 | 62.9049 | 64.1041 | 65.4798 | 61.4108 | 64.6447 | 64.4332 | 67.0516 | 60.58 | 65.4466 | 63.129 | 67.0166 | 62.3783 | 66.7337 | 62.4699 | 67.7695 | 61.6014 | 65.34 | 67.6631 | 93.5221 | 93.6657 | 93.4624
2022-09-07 18:57 | 0:33 | 41.7214 | 40.8178 | 43.7264 | 59.0682 | 62.0806 | 59.8868 | 64.1805 | 57.3617 | 63.786 | 60.8158 | 59.0675 | 66.4863 | 57.3355 | 61.2282 | 61.6858 | 60.9198 | 59.2338 | 61.2991 | 61.0979 | 62.7377 | 44.4888 | 40.5476 | 49.2343 | 60.2737 | 58.9761 | 65.1078 | 63.1362 | 61.6116 | 59.6998 | 63.0038 | 56.8766 | 63.6541 | 59.4185 | 60.9025 | 57.0765 | 63.1392 | 61.9815 | 62.3054 | 65.1015 | 61.2676 | 62.6747 | 64.0916 | 65.5971 | 61.2708 | 64.7233 | 64.3038 | 67.1265 | 60.5282 | 65.4918 | 63.0078 | 66.9485 | 62.2224 | 66.305 | 62.3378 | 67.6743 | 61.3969 | 65.2876 | 67.6774 | 93.4703 | 93.536 | 93.4105
2022-09-07 18:57 | 0:33 | 41.662 | 40.7079 | 43.5807 | 58.8862 | 61.8375 | 59.5227 | 63.9108 | 57.1471 | 63.6385 | 60.7651 | 59.3295 | 66.4209 | 57.1711 | 61.0457 | 61.5684 | 60.8297 | 59.1288 | 61.0678 | 61.0292 | 62.5775 | 44.3601 | 40.4397 | 49.1318 | 60.1356 | 58.8487 | 64.9687 | 63.2687 | 61.7135 | 59.6435 | 62.8367 | 56.7313 | 63.5484 | 59.3743 | 60.7156 | 57.0423 | 62.9496 | 61.9255 | 62.0662 | 64.8616 | 61.1686 | 62.6462 | 63.8453 | 65.6331 | 61.3734 | 64.5551 | 64.2697 | 66.9449 | 60.3152 | 65.7246 | 62.7857 | 66.725 | 62.3099 | 66.0404 | 62.0947 | 67.6949 | 61.2699 | 65.3598 | 67.4163 | 93.3942 | 93.3949 | 93.3505
2022-09-07 18:57 | 0:33 | 41.6075 | 40.5479 | 43.4745 | 58.6004 | 61.7357 | 59.4211 | 63.6835 | 57.0001 | 63.5205 | 60.551 | 58.7344 | 66.1895 | 57.1297 | 60.8092 | 61.504 | 60.6686 | 59.0587 | 60.5493 | 60.8165 | 62.3883 | 44.206 | 40.3144 | 48.9491 | 60.0661 | 58.7407 | 65.1214 | 63.1202 | 61.663 | 59.53 | 62.7283 | 56.5774 | 63.452 | 59.1594 | 60.6375 | 56.8837 | 62.9545 | 61.5166 | 62.021 | 65.0366 | 60.9712 | 62.4489 | 63.7861 | 65.7507 | 61.1323 | 64.3695 | 64.1627 | 66.661 | 60.141 | 65.2419 | 62.6519 | 66.6725 | 61.8854 | 66.1637 | 61.7884 | 67.4692 | 61.1365 | 65.2195 | 67.387 | 93.3452 | 93.2574 | 93.2698
2022-09-07 18:58 | 0:34 | 41.4567 | 40.448 | 43.3022 | 58.6509 | 61.5961 | 59.2582 | 63.3989 | 56.9007 | 63.4061 | 60.5939 | 58.8046 | 66.0557 | 56.9713 | 60.7547 | 61.2748 | 60.4995 | 58.8927 | 60.5587 | 60.7876 | 62.6637 | 44.0784 | 40.2186 | 48.8319 | 60.0665 | 58.5641 | 64.8393 | 62.9049 | 61.1217 | 59.4116 | 62.4771 | 56.5412 | 63.4066 | 58.9327 | 60.4281 | 56.5771 | 62.9443 | 61.6484 | 61.8696 | 64.9227 | 60.8884 | 62.3081 | 63.5395 | 65.565 | 60.8194 | 64.0923 | 63.9711 | 66.8029 | 60.013 | 65.0349 | 62.6546 | 66.4695 | 61.8882 | 66.1578 | 61.6892 | 67.4073 | 60.9933 | 64.9342 | 67.2258 | 93.2048 | 93.2051 | 93.2682
2022-09-07 18:58 | 0:34 | 41.2903 | 40.309 | 43.1594 | 58.5444 | 61.5319 | 58.9674 | 63.4988 | 56.7454 | 63.2462 | 60.2306 | 58.7251 | 65.6584 | 56.8748 | 60.6904 | 61.1725 | 60.298 | 58.7748 | 60.6204 | 60.6191 | 62.2617 | 43.9152 | 40.0759 | 48.7437 | 59.7763 | 58.3662 | 64.4629 | 62.6747 | 61.0128 | 59.2151 | 62.46 | 56.2737 | 63.1877 | 58.914 | 60.2462 | 56.418 | 62.847 | 61.2853 | 61.6899 | 64.7308 | 60.5774 | 61.9651 | 63.3628 | 65.1747 | 60.7679 | 64.0389 | 63.8085 | 66.5438 | 59.8831 | 64.8534 | 62.2345 | 66.2471 | 61.7053 | 65.9609 | 61.5289 | 67.1473 | 60.8069 | 64.8841 | 67.113 | 93.0257 | 93.1346 | 93.0979
2022-09-07 18:58 | 0:34 | 41.1339 | 40.1952 | 43.0509 | 58.416 | 61.391 | 58.838 | 63.2506 | 56.5438 | 63.1617 | 60.1412 | 58.3101 | 65.6384 | 56.7533 | 60.7295 | 60.9836 | 60.1741 | 58.5228 | 60.3184 | 60.5821 | 62.1143 | 43.8145 | 39.9721 | 48.5837 | 59.6317 | 58.3483 | 64.4987 | 62.6462 | 61.0283 | 59.0289 | 62.3469 | 56.0898 | 63.0057 | 58.7423 | 60.1726 | 56.4602 | 62.5467 | 61.1639 | 61.5889 | 64.0168 | 60.54 | 61.9874 | 63.4081 | 64.9114 | 60.5792 | 63.8163 | 63.6813 | 66.57 | 59.7581 | 64.6237 | 62.2374 | 65.9609 | 61.4909 | 66.2093 | 61.3906 | 66.926 | 60.74 | 64.6598 | 66.9583 | 92.8971 | 92.9761 | 93.0739
2022-09-07 18:58 | 0:34 | 41.0886 | 40.0944 | 42.9842 | 58.3244 | 61.2132 | 58.9128 | 62.9854 | 56.4848 | 62.9221 | 60.1333 | 58.3885 | 65.634 | 56.6386 | 60.3834 | 60.7205 | 60.0744 | 58.4531 | 60.2356 | 60.3193 | 62.0906 | 43.6992 | 39.8589 | 48.4909 | 59.4446 | 58.1254 | 64.5546 | 62.4489 | 61.1104 | 58.8256 | 62.1616 | 55.9758 | 62.82 | 58.6106 | 60.0619 | 56.1746 | 62.4406 | 60.9402 | 61.3577 | 64.2039 | 60.27 | 61.7546 | 63.1404 | 64.6603 | 60.5131 | 63.6658 | 63.4825 | 66.3606 | 59.6515 | 64.5345 | 62.0005 | 66.1937 | 61.5009 | 65.7854 | 61.1844 | 66.9359 | 60.5585 | 64.5447 | 66.7886 | 92.77 | 92.8281 | 92.961
2022-09-07 18:58 | 0:34 | 41.0617 | 39.9699 | 42.9029 | 58.2514 | 61.1593 | 58.5931 | 62.9245 | 56.3639 | 62.7886 | 59.8864 | 58.3695 | 65.5613 | 56.4256 | 60.0673 | 60.9111 | 59.9588 | 58.2596 | 60.2904 | 60.1767 | 62.1051 | 43.5909 | 39.7529 | 48.3599 | 59.4457 | 57.9674 | 64.2311 | 62.3081 | 60.5777 | 58.6776 | 61.9039 | 55.943 | 62.6961 | 58.4319 | 59.9719 | 56.2821 | 62.2798 | 61.0313 | 61.2468 | 63.6979 | 60.3093 | 61.6349 | 63.0807 | 64.7168 | 60.3372 | 63.6933 | 63.3279 | 66.053 | 59.5057 | 64.2845 | 61.9622 | 65.965 | 61.5604 | 65.5344 | 61.0082 | 66.627 | 60.4609 | 64.2779 | 66.365 | 92.6351 | 92.6933 | 92.9494
2022-09-07 18:58 | 0:34 | 41.0795 | 39.8503 | 42.7778 | 58.0861 | 60.9647 | 58.4188 | 62.9189 | 56.268 | 62.7001 | 59.7885 | 58.0197 | 65.3586 | 56.3916 | 59.9131 | 60.6551 | 59.7399 | 58.1586 | 59.7075 | 60.0906 | 61.8636 | 43.4803 | 39.6407 | 48.221 | 59.3819 | 57.8237 | 63.9711 | 61.9651 | 60.5841 | 58.6766 | 61.8824 | 55.7355 | 62.4509 | 58.232 | 59.8175 | 56.0463 | 62.0552 | 60.4317 | 61.0258 | 63.8967 | 59.9923 | 61.4837 | 62.9881 | 64.5098 | 60.1077 | 63.6125 | 63.0773 | 66.1477 | 59.2694 | 64.2636 | 61.9308 | 65.813 | 61.302 | 65.7507 | 60.9798 | 66.5299 | 60.3252 | 64.3539 | 66.048 | 92.5431 | 92.5714 | 92.8156
2022-09-07 18:59 | 0:34 | 41.0623 | 39.7865 | 42.7121 | 57.985 | 60.9 | 58.2312 | 62.4568 | 56.0279 | 62.565 | 59.7553 | 57.8163 | 65.1739 | 56.1512 | 59.7384 | 60.5669 | 59.6461 | 58.1147 | 59.5036 | 59.8702 | 61.7403 | 43.3781 | 39.581 | 48.1117 | 59.1855 | 57.6799 | 63.7409 | 61.9874 | 60.1123 | 58.3944 | 61.7239 | 55.6085 | 62.3953 | 58.093 | 59.6469 | 55.8109 | 61.6891 | 60.4695 | 61.0741 | 63.8722 | 59.874 | 61.4002 | 62.8405 | 64.3617 | 60.1453 | 63.2997 | 63.0498 | 65.769 | 59.1388 | 63.9735 | 61.6447 | 65.7999 | 60.9859 | 65.4172 | 61.0611 | 66.2527 | 60.108 | 64.205 | 66.1386 | 92.4107 | 92.4016 | 92.7169
2022-09-07 18:59 | 0:35 | 41.0162 | 39.6648 | 42.6151 | 57.7693 | 60.7469 | 58.0332 | 62.422 | 56.0151 | 62.3563 | 59.5908 | 57.9068 | 64.9844 | 56.0969 | 59.6288 | 60.5704 | 59.5289 | 57.9107 | 59.5035 | 59.8076 | 61.5603 | 43.2592 | 39.4669 | 48.0225 | 59.0927 | 57.5862 | 63.5612 | 61.7546 | 60.2873 | 58.2162 | 61.6056 | 55.5681 | 62.3092 | 58.054 | 59.5587 | 55.7013 | 61.6618 | 60.4828 | 60.9481 | 63.6436 | 59.7517 | 61.1416 | 62.68 | 64.2569 | 59.907 | 63.3235 | 62.7989 | 65.7368 | 59.0934 | 63.8324 | 61.53 | 65.7512 | 60.9512 | 65.2913 | 60.9316 | 65.6363 | 59.9181 | 64.0354 | 66.1974 | 92.2474 | 92.2614 | 92.6152
2022-09-07 18:59 | 0:35 | 40.9789 | 39.5495 | 42.5872 | 57.4227 | 60.5702 | 58.0522 | 62.385 | 55.8679 | 62.2921 | 59.2618 | 57.9256 | 65.0367 | 55.9704 | 59.6687 | 60.3324 | 59.3633 | 57.8212 | 59.4248 | 59.7094 | 61.4834 | 43.1495 | 39.3303 | 47.8923 | 58.8454 | 57.4425 | 63.6193 | 61.6349 | 60.5271 | 58.0859 | 61.5488 | 55.4644 | 62.0812 | 57.9873 | 59.3803 | 55.7791 | 61.3024 | 60.2893 | 60.8413 | 63.6384 | 59.6892 | 61.0138 | 62.6809 | 63.9057 | 59.7536 | 63.1927 | 62.6955 | 65.6882 | 58.9917 | 63.8975 | 61.4316 | 65.4289 | 60.7029 | 65.3582 | 60.7975 | 65.6484 | 59.9154 | 63.7348 | 66.2341 | 92.1231 | 92.129 | 92.5136
2022-09-07 18:59 | 0:35 | 40.9132 | 39.4736 | 42.5117 | 57.3331 | 60.6266 | 57.86 | 62.3656 | 55.7926 | 62.0972 | 59.1642 | 57.7619 | 64.8943 | 55.806 | 59.357 | 60.1346 | 59.2026 | 57.614 | 59.1861 | 59.6082 | 61.0956 | 43.0622 | 39.2165 | 47.7622 | 58.7397 | 57.2522 | 63.4485 | 61.4837 | 59.9337 | 57.963 | 61.3745 | 55.3132 | 62.0244 | 57.8999 | 59.1662 | 55.6744 | 61.2336 | 60.3883 | 60.6114 | 63.3697 | 59.5957 | 60.883 | 62.5094 | 63.9789 | 59.5704 | 63.0495 | 62.5757 | 65.4463 | 58.801 | 63.4516 | 61.1763 | 65.4204 | 60.6485 | 65.1772 | 60.6865 | 65.6501 | 59.8533 | 63.6618 | 66.053 | 91.9793 | 92.0648 | 92.4386
2022-09-07 18:59 | 0:35 | 40.634 | 39.3508 | 42.2896 | 57.2458 | 60.3554 | 57.9466 | 62.2252 | 55.6385 | 62.0587 | 59.0584 | 57.5407 | 64.8031 | 55.6004 | 59.563 | 60.0881 | 59.0572 | 57.4996 | 59.1447 | 59.4196 | 61.1709 | 43.0025 | 39.093 | 47.7244 | 58.6341 | 57.1234 | 63.2821 | 61.4002 | 60.207 | 57.8511 | 61.3151 | 55.1766 | 61.7937 | 57.8846 | 59.1122 | 55.4411 | 61.2928 | 60.0572 | 60.4541 | 63.1324 | 59.4228 | 60.7589 | 62.3198 | 63.7567 | 59.543 | 62.8266 | 62.5343 | 65.2817 | 58.7022 | 63.3419 | 61.0858 | 65.1458 | 60.3189 | 64.958 | 60.4848 | 65.6527 | 59.6055 | 63.4591 | 65.9432 | 91.8684 | 91.8755 | 92.363
2022-09-07 18:59 | 0:35 | 40.4189 | 39.2717 | 42.1494 | 57.0646 | 60.2592 | 57.8661 | 62.3217 | 55.4918 | 61.8931 | 59.1764 | 57.4773 | 64.693 | 55.5476 | 59.2347 | 59.9009 | 58.8774 | 57.4773 | 59.3464 | 59.1767 | 60.9172 | 42.8969 | 39.0148 | 47.6368 | 58.5508 | 57.0456 | 62.9766 | 61.1416 | 59.4658 | 57.6325 | 61.1743 | 54.8612 | 61.6731 | 57.5072 | 58.974 | 55.1813 | 61.1994 | 59.9649 | 60.4167 | 62.9601 | 59.326 | 60.7113 | 62.1974 | 63.684 | 59.4251 | 62.6653 | 62.274 | 65.2879 | 58.563 | 63.3402 | 60.9592 | 64.9416 | 60.308 | 64.6997 | 60.2389 | 65.5259 | 59.4081 | 63.3243 | 65.7417 | 91.814 | 91.7443 | 92.2976
2022-09-07 19:00 | 0:36 | 40.231 | 39.1784 | 42.0448 | 57.1101 | 60.1983 | 57.5871 | 61.8541 | 55.395 | 61.6712 | 58.7797 | 57.1753 | 64.4102 | 55.4536 | 59.1039 | 59.7765 | 58.8706 | 57.3446 | 59.3052 | 59.0637 | 60.6326 | 42.809 | 38.8904 | 47.5293 | 58.5023 | 56.9266 | 62.9357 | 61.0138 | 59.3948 | 57.4772 | 60.9747 | 54.7619 | 61.5151 | 57.3084 | 58.8096 | 54.7984 | 61.0653 | 59.6313 | 60.2296 | 62.4396 | 59.0196 | 60.5067 | 62.0379 | 63.6859 | 59.2246 | 62.6144 | 62.1796 | 65.0554 | 58.4496 | 63.116 | 60.9423 | 64.6894 | 60.1674 | 64.7139 | 60.2089 | 65.3947 | 59.2843 | 63.1238 | 65.5774 | 91.8701 | 91.7268 | 92.3239
2022-09-07 19:00 | 0:36 | 40.0544 | 39.0922 | 41.9448 | 56.9227 | 59.9577 | 57.6297 | 61.6312 | 55.2798 | 61.5907 | 58.5942 | 57.1961 | 64.2256 | 55.1837 | 58.9822 | 59.4728 | 58.7344 | 57.1981 | 58.7601 | 59.025 | 60.6056 | 42.7305 | 38.8101 | 47.4132 | 58.2195 | 56.7428 | 62.7354 | 60.883 | 59.2676 | 57.5242 | 60.8859 | 54.7324 | 61.4529 | 57.1052 | 58.5767 | 54.9523 | 61.027 | 59.5236 | 60.0284 | 62.5082 | 59.0244 | 60.4439 | 61.8501 | 63.4692 | 58.9823 | 62.4987 | 61.9907 | 64.8722 | 58.2174 | 63.0853 | 60.7899 | 64.6616 | 60.057 | 64.4907 | 60.1711 | 64.9949 | 59.2637 | 63.044 | 65.4902 | 91.8946 | 91.7933 | 92.3355
2022-09-07 19:00 | 0:36 | 39.9582 | 38.9462 | 41.822 | 56.7926 | 59.9095 | 57.1367 | 61.6806 | 55.1434 | 61.4947 | 58.5594 | 57.0391 | 64.217 | 55.1214 | 58.9804 | 59.5316 | 58.6269 | 57.0249 | 58.4478 | 58.7426 | 60.7127 | 42.6033 | 38.6879 | 47.3175 | 58.212 | 56.5845 | 62.5967 | 60.7589 | 58.9487 | 57.176 | 60.6245 | 54.6255 | 61.244 | 56.8791 | 58.514 | 54.6604 | 60.8271 | 59.4987 | 60.1525 | 62.208 | 58.937 | 60.2067 | 61.7991 | 63.2368 | 58.927 | 62.3154 | 61.8712 | 64.8241 | 58.1564 | 63.0741 | 60.5644 | 64.4222 | 59.6189 | 64.2805 | 59.8785 | 64.9245 | 59.1369 | 62.9195 | 65.3018 | 91.9174 | 91.9263 | 92.3157
2022-09-07 19:00 | 0:36 | 39.8628 | 38.8368 | 41.661 | 56.6539 | 59.8374 | 57.0042 | 61.4625 | 54.9589 | 61.399 | 58.5498 | 57.0302 | 64.1361 | 54.9962 | 58.8335 | 59.5245 | 58.4074 | 56.9971 | 58.4042 | 58.6441 | 60.4364 | 42.5096 | 38.5801 | 47.231 | 58.0127 | 56.3833 | 62.4971 | 60.7113 | 58.8255 | 57.1403 | 60.5952 | 54.2336 | 61.0827 | 56.8098 | 58.2285 | 54.6983 | 60.4621 | 59.3128 | 59.8051 | 62.1077 | 58.7759 | 60.0266 | 61.7269 | 62.9824 | 58.9205 | 62.1605 | 61.7762 | 64.5803 | 58.0841 | 62.9533 | 60.4339 | 64.3322 | 59.789 | 64.2853 | 59.6559 | 64.6141 | 58.9251 | 62.8253 | 65.0116 | 92.0174 | 92.1141 | 92.4049
2022-09-07 19:00 | 0:36 | 39.7966 | 38.7818 | 41.571 | 56.5592 | 59.6018 | 57.0987 | 61.2711 | 54.8819 | 61.3312 | 58.3571 | 57.1058 | 63.9701 | 54.9002 | 58.6162 | 59.416 | 58.2826 | 56.7573 | 58.1559 | 58.6638 | 60.206 | 42.4044 | 38.5168 | 47.0818 | 57.8711 | 56.301 | 62.5003 | 60.5067 | 59.0003 | 57.0711 | 60.4954 | 54.1993 | 61.0446 | 56.8285 | 58.2009 | 54.5164 | 60.5594 | 59.4303 | 59.5981 | 62.0192 | 58.7488 | 60.0169 | 61.5486 | 62.9756 | 58.7889 | 62.0717 | 61.6364 | 64.3824 | 57.9358 | 62.7448 | 60.3087 | 64.0636 | 59.5887 | 63.7762 | 59.5517 | 64.8517 | 58.8171 | 62.5949 | 65.0351 | 92.2597 | 92.3041 | 92.6522
2022-09-07 19:00 | 0:36 | 39.7826 | 38.6763 | 41.5141 | 56.258 | 59.5882 | 56.835 | 61.4721 | 54.6906 | 61.136 | 58.0985 | 56.8485 | 63.7469 | 54.7741 | 58.4513 | 59.0777 | 58.0941 | 56.6619 | 58.4447 | 58.5012 | 59.9298 | 42.2815 | 38.3968 | 47.0159 | 57.7169 | 56.1396 | 62.5781 | 60.4439 | 58.7704 | 56.8636 | 60.2384 | 54.076 | 60.9631 | 56.5874 | 58.0811 | 54.5379 | 60.5645 | 59.4785 | 59.4405 | 62.5078 | 58.7103 | 60.0075 | 61.3712 | 62.8428 | 58.7317 | 61.9313 | 61.5272 | 64.3303 | 57.7702 | 62.7134 | 60.0915 | 64.1632 | 59.2573 | 63.6941 | 59.3782 | 64.6307 | 58.5746 | 62.6678 | 64.8106 | 92.3804 | 92.4689 | 92.6376
2022-09-07 19:01 | 0:36 | 39.6335 | 38.581 | 41.3864 | 56.4846 | 59.6187 | 56.6396 | 61.1056 | 54.5633 | 61.0081 | 58.203 | 56.6235 | 63.6021 | 54.6275 | 58.2529 | 59.1223 | 57.9617 | 56.5848 | 58.2384 | 58.3 | 59.9568 | 42.1973 | 38.306 | 46.8554 | 57.6548 | 56.0846 | 62.2762 | 60.2067 | 58.4916 | 56.8757 | 60.2341 | 54.2634 | 60.7961 | 56.6372 | 57.9494 | 54.2748 | 60.2744 | 58.8564 | 59.5137 | 62.2048 | 58.3942 | 59.8334 | 61.2794 | 62.8078 | 58.4694 | 61.8593 | 61.3212 | 64.1883 | 57.6422 | 62.3819 | 60.1292 | 63.9867 | 59.3081 | 63.6629 | 59.2426 | 64.5186 | 58.5237 | 62.4988 | 64.6491 | 92.4647 | 92.614 | 92.6657
2022-09-07 19:01 | 0:37 | 39.5787 | 38.4719 | 41.3343 | 56.2408 | 59.3435 | 56.3807 | 60.9498 | 54.5228 | 60.9001 | 57.8864 | 56.5017 | 63.5923 | 54.5275 | 58.0034 | 58.8896 | 57.8471 | 56.3976 | 57.8891 | 58.2332 | 60.2314 | 42.085 | 38.2138 | 46.684 | 57.4593 | 55.8772 | 62.1527 | 60.0266 | 58.3819 | 56.6876 | 60.109 | 53.9462 | 60.6009 | 56.3008 | 57.824 | 54.2711 | 60.0622 | 58.92 | 59.1686 | 61.7717 | 58.2484 | 59.6782 | 61.1647 | 62.5503 | 58.3325 | 61.742 | 61.1859 | 64.187 | 57.4931 | 62.1148 | 59.9951 | 64.1543 | 59.2796 | 63.5519 | 59.1695 | 64.4817 | 58.4152 | 62.4185 | 64.3838 | 92.5864 | 92.7261 | 92.7101
2022-09-07 19:01 | 0:37 | 39.5634 | 38.365 | 41.1497 | 56.1283 | 59.1829 | 56.4716 | 60.9125 | 54.3152 | 60.7872 | 57.6626 | 56.3868 | 63.2285 | 54.4048 | 58.0635 | 58.7894 | 57.7205 | 56.2483 | 57.7936 | 57.9499 | 59.9209 | 41.9605 | 38.1287 | 46.6121 | 57.3314 | 55.8169 | 62.0851 | 60.0169 | 58.0864 | 56.5411 | 59.879 | 53.7658 | 60.5741 | 56.1446 | 57.7283 | 54.0387 | 60.1798 | 58.8654 | 59.057 | 61.5514 | 58.079 | 59.5186 | 61.0271 | 62.4769 | 58.2084 | 61.5132 | 61.1122 | 63.9804 | 57.3513 | 62.0636 | 59.738 | 64.1206 | 58.9145 | 63.6899 | 59.103 | 64.3573 | 58.2028 | 62.3006 | 64.4072 | 92.6686 | 92.841 | 92.7459
2022-09-07 19:01 | 0:37 | 39.6096 | 38.3175 | 41.1869 | 56.0225 | 59.0953 | 56.5992 | 60.86 | 54.1164 | 60.6635 | 57.8017 | 56.2493 | 63.1324 | 54.336 | 58.0139 | 58.6327 | 57.5911 | 56.1231 | 57.9979 | 57.9314 | 59.8578 | 41.8624 | 38.0424 | 46.5034 | 57.3057 | 55.7111 | 61.9471 | 60.0075 | 58.2596 | 56.5038 | 59.779 | 53.6018 | 60.3343 | 56.0614 | 57.6367 | 53.8868 | 59.7413 | 58.5849 | 59.0181 | 61.5705 | 57.9481 | 59.3899 | 60.8326 | 62.3297 | 57.9942 | 61.3676 | 61.0359 | 63.9657 | 57.1496 | 62.1741 | 59.5866 | 63.3201 | 58.9226 | 63.5758 | 58.9331 | 64.2453 | 58.1469 | 62.1137 | 64.3884 | 92.7732 | 92.9512 | 92.8133
2022-09-07 19:01 | 0:37 | 39.5758 | 38.2242 | 41.1299 | 55.8071 | 59.1309 | 56.4358 | 60.8097 | 54.1297 | 60.4422 | 57.8123 | 56.1108 | 63.0262 | 54.2209 | 57.9775 | 58.5802 | 57.4872 | 56.022 | 57.6512 | 57.7002 | 59.7032 | 41.7719 | 37.9508 | 46.3873 | 57.2282 | 55.5177 | 61.6827 | 59.8334 | 58.1303 | 56.1242 | 59.6367 | 53.5128 | 60.2528 | 55.9529 | 57.3827 | 53.907 | 59.719 | 58.6309 | 58.8432 | 61.4813 | 57.8143 | 59.1892 | 60.7774 | 62.4723 | 58.0696 | 61.3802 | 60.8738 | 63.6852 | 57.1128 | 62.0796 | 59.4035 | 63.3538 | 58.9351 | 63.2774 | 58.7426 | 63.9434 | 58.0184 | 61.915 | 64.2811 | 92.8258 | 93.0075 | 92.9119
2022-09-07 19:01 | 0:37 | 39.5773 | 38.1699 | 41.0721 | 55.7489 | 58.9063 | 56.048 | 60.2578 | 53.9917 | 60.4247 | 57.4367 | 56.1094 | 62.897 | 54.1309 | 57.5072 | 58.4656 | 57.331 | 55.8527 | 57.6178 | 57.6452 | 59.3203 | 41.6895 | 37.8523 | 46.2947 | 56.9623 | 55.4281 | 61.5831 | 59.6782 | 58.1773 | 56.111 | 59.644 | 53.2382 | 60.0882 | 55.8973 | 57.3313 | 53.68 | 59.4034 | 58.5478 | 58.6528 | 61.023 | 57.7936 | 59.1182 | 60.6483 | 62.1294 | 57.9455 | 61.1199 | 60.7757 | 63.568 | 57.038 | 61.7631 | 59.3094 | 62.8056 | 58.72 | 62.8814 | 58.6109 | 64.1008 | 57.859 | 61.7982 | 64.1627 | 92.9373 | 93.1259 | 92.9286
2022-09-07 19:02 | 0:38 | 39.5502 | 38.0505 | 41.0341 | 55.5833 | 58.9349 | 56.2618 | 60.3594 | 53.8548 | 60.2674 | 57.5607 | 55.9101 | 62.8937 | 53.9794 | 57.383 | 58.3501 | 57.2 | 55.7702 | 57.2736 | 57.5985 | 59.3813 | 41.5428 | 37.7795 | 46.1687 | 56.7583 | 55.3075 | 61.6405 | 59.5186 | 57.838 | 56.123 | 59.3364 | 53.2146 | 60.0003 | 55.9061 | 57.1542 | 53.5786 | 59.3706 | 58.564 | 58.556 | 61.277 | 57.642 | 59.0161 | 60.4175 | 61.9463 | 57.7293 | 60.9576 | 60.6472 | 63.4097 | 56.8938 | 61.7267 | 59.1996 | 62.6057 | 58.3954 | 62.5675 | 58.3934 | 63.8117 | 57.6959 | 61.6628 | 64.0544 | 93.0514 | 93.2703 | 93.0452
2022-09-07 19:02 | 0:38 | 39.4501 | 38.0006 | 40.9437 | 55.3831 | 58.7637 | 55.8586 | 60.3686 | 53.7221 | 60.117 | 57.4909 | 55.7662 | 62.6478 | 53.8116 | 57.6467 | 58.1279 | 57.1043 | 55.7114 | 57.1014 | 57.4376 | 59.2183 | 41.4756 | 37.6769 | 46.1033 | 56.7929 | 55.1945 | 61.536 | 59.3899 | 58.01 | 55.9979 | 59.2157 | 53.103 | 59.7684 | 55.6511 | 57.0717 | 53.2113 | 59.4167 | 58.2122 | 58.5628 | 61.1769 | 57.4483 | 58.7708 | 60.2797 | 62.0048 | 57.6482 | 60.8015 | 60.4729 | 63.3525 | 56.8717 | 61.5994 | 59.0316 | 62.9046 | 58.1456 | 62.8007 | 58.3741 | 63.8348 | 57.5279 | 61.4913 | 63.7321 | 93.1861 | 93.4258 | 93.071
2022-09-07 19:02 | 0:38 | 39.3776 | 37.8977 | 40.8704 | 55.3657 | 58.5851 | 55.917 | 60.1578 | 53.7927 | 60.0443 | 57.1032 | 55.777 | 62.5329 | 53.625 | 57.5112 | 58.0129 | 56.9779 | 55.5625 | 57.3945 | 57.321 | 59.2004 | 41.3695 | 37.5791 | 46.0024 | 56.6863 | 55.0781 | 61.2692 | 59.1892 | 57.3503 | 55.7038 | 59.0941 | 53.0723 | 59.5846 | 55.5003 | 56.9607 | 53.176 | 59.1509 | 58.1346 | 58.4346 | 61.0684 | 57.298 | 58.7781 | 60.2247 | 61.8914 | 57.5633 | 60.7079 | 60.3066 | 62.98 | 56.563 | 61.7773 | 58.8234 | 62.6619 | 58.1806 | 62.8605 | 58.2986 | 63.217 | 57.3109 | 61.436 | 63.6467 | 93.2958 | 93.55 | 93.1801
2022-09-07 19:02 | 0:38 | 39.2843 | 37.8485 | 40.8137 | 55.3364 | 58.498 | 55.9053 | 60.0458 | 53.4955 | 59.9494 | 57.0241 | 55.5933 | 62.4916 | 53.5538 | 57.1327 | 57.8322 | 56.8783 | 55.4761 | 56.9656 | 57.1979 | 59.1594 | 41.3293 | 37.4928 | 45.9392 | 56.5578 | 54.8758 | 61.092 | 59.1182 | 57.2038 | 55.655 | 58.8979 | 52.755 | 59.5724 | 55.3737 | 56.832 | 53.1503 | 59.1858 | 58.0795 | 58.2119 | 61.1285 | 57.2599 | 58.7045 | 60.0967 | 61.4429 | 57.4592 | 60.8035 | 60.2026 | 62.8183 | 56.4878 | 61.403 | 58.8046 | 62.3257 | 58.275 | 62.4821 | 58.1051 | 63.4942 | 57.3797 | 61.2105 | 63.5712 | 93.4112 | 93.665 | 93.2938
2022-09-07 19:02 | 0:38 | 39.242 | 37.7737 | 40.741 | 55.1307 | 58.3243 | 55.6802 | 59.8591 | 53.4209 | 59.8542 | 57.0221 | 55.5045 | 62.2369 | 53.328 | 57.2898 | 57.65 | 56.683 | 55.2474 | 57.0623 | 57.0887 | 58.8962 | 41.221 | 37.3925 | 45.8616 | 56.3612 | 54.7052 | 60.8404 | 59.0161 | 57.3155 | 55.4341 | 58.822 | 52.7188 | 59.4594 | 55.1671 | 56.772 | 53.0362 | 59.0234 | 57.6242 | 58.1733 | 60.9329 | 57.0067 | 58.3817 | 59.9481 | 61.3327 | 57.264 | 60.6522 | 60.111 | 62.8185 | 56.4113 | 61.3691 | 58.6066 | 62.4537 | 58.1078 | 62.2186 | 58.0006 | 62.8472 | 57.3455 | 61.0463 | 63.6178 | 93.5058 | 93.7794 | 93.3024
2022-09-07 19:02 | 0:38 | 39.1554 | 37.7173 | 40.6758 | 55.1127 | 58.2624 | 55.6435 | 59.8845 | 53.2631 | 59.7766 | 56.9289 | 55.4561 | 62.3233 | 53.2883 | 57.0564 | 57.4142 | 56.6114 | 55.1915 | 56.986 | 56.929 | 58.7833 | 41.1765 | 37.3373 | 45.7665 | 56.2311 | 54.6115 | 60.8963 | 58.7708 | 57.1001 | 55.2928 | 58.7934 | 52.7846 | 59.1978 | 55.0926 | 56.5493 | 52.902 | 58.7476 | 57.5628 | 57.9846 | 60.4996 | 56.9294 | 58.3809 | 59.8659 | 61.3201 | 57.0462 | 60.4204 | 59.9248 | 62.4772 | 56.3215 | 61.0898 | 58.5601 | 62.5141 | 58.0936 | 62.3989 | 57.7902 | 62.6893 | 57.212 | 61.0822 | 63.5727 | 93.6273 | 93.921 | 93.441
2022-09-07 19:03 | 0:38 | 39.0876 | 37.6378 | 40.5941 | 55.0627 | 58.1504 | 55.5465 | 59.5813 | 53.143 | 59.5449 | 56.8653 | 55.1917 | 62.133 | 53.2386 | 56.9457 | 57.4892 | 56.4661 | 55.1335 | 56.8053 | 56.8055 | 58.5421 | 41.088 | 37.2372 | 45.6729 | 56.1173 | 54.5055 | 60.9723 | 58.7781 | 56.8111 | 55.3155 | 58.5638 | 52.3032 | 59.1138 | 55.0885 | 56.4747 | 52.6229 | 58.5265 | 57.3646 | 57.9082 | 60.5389 | 56.8302 | 58.2424 | 59.7214 | 61.2702 | 56.9826 | 60.3589 | 59.8486 | 62.3566 | 56.1712 | 60.9488 | 58.4159 | 62.0853 | 57.9506 | 62.3856 | 57.9333 | 62.7725 | 57.0035 | 61.1347 | 63.0627 | 93.7035 | 94.0383 | 93.5044
2022-09-07 19:03 | 0:39 | 39.0259 | 37.5666 | 40.5 | 54.8584 | 57.9867 | 55.3274 | 59.5861 | 53.2359 | 59.3754 | 56.4839 | 55.2618 | 61.988 | 53.0481 | 56.8302 | 57.2451 | 56.3241 | 54.9299 | 56.4929 | 56.6774 | 58.5195 | 41.0019 | 37.1583 | 45.5931 | 56.0954 | 54.4296 | 60.7767 | 58.7045 | 56.7279 | 55.2482 | 58.4265 | 52.4452 | 58.9428 | 54.8707 | 56.2633 | 52.5879 | 58.5001 | 57.4771 | 57.8469 | 60.5872 | 56.7212 | 58.1908 | 59.5571 | 60.9164 | 56.8614 | 60.1532 | 59.6223 | 62.3892 | 56.0529 | 60.7163 | 58.3167 | 61.7037 | 57.7269 | 61.9066 | 57.6412 | 62.4319 | 56.8716 | 60.7021 | 62.9941 | 93.8757 | 94.2302 | 93.5675
2022-09-07 19:03 | 0:39 | 38.9932 | 37.4832 | 40.431 | 54.7056 | 57.8107 | 54.9221 | 59.5124 | 53.066 | 59.3155 | 56.5366 | 55.0055 | 61.7767 | 53.0635 | 56.6382 | 57.2135 | 56.0969 | 54.905 | 56.2974 | 56.6265 | 58.6125 | 40.9424 | 37.064 | 45.5128 | 55.9477 | 54.2479 | 60.6953 | 58.3817 | 56.6639 | 55.1375 | 58.2596 | 52.1718 | 58.7217 | 54.7371 | 56.3041 | 52.4977 | 58.4644 | 57.3862 | 57.6738 | 60.5157 | 56.5923 | 58.1848 | 59.3505 | 60.8062 | 56.6584 | 60.0369 | 59.49 | 62.3179 | 55.8994 | 60.7235 | 58.1737 | 61.8469 | 57.6487 | 61.9886 | 57.4684 | 62.6375 | 56.7697 | 60.7032 | 62.9702 | 94.1091 | 94.4262 | 93.7582
2022-09-07 19:03 | 0:39 | 38.8815 | 37.3854 | 40.3312 | 54.5041 | 57.6701 | 55.0663 | 59.2671 | 53.032 | 59.2205 | 56.3105 | 55.0525 | 61.6415 | 52.8457 | 56.4792 | 56.929 | 56.102 | 54.7589 | 56.2245 | 56.3439 | 58.1308 | 40.8922 | 37.0126 | 45.4822 | 55.8995 | 54.1346 | 60.4534 | 58.3809 | 56.9575 | 55.0305 | 58.3479 | 52.1783 | 58.7862 | 54.7531 | 56.036 | 52.4379 | 58.4689 | 57.2875 | 57.5025 | 60.3481 | 56.4624 | 57.8878 | 59.2309 | 60.6461 | 56.569 | 59.8391 | 59.4083 | 62.0924 | 55.7799 | 60.4494 | 58.079 | 61.6512 | 57.4208 | 61.8043 | 57.2698 | 62.4296 | 56.5969 | 60.375 | 62.726 | 94.3104 | 94.611 | 93.8841
2022-09-07 19:03 | 0:39 | 38.7214 | 37.309 | 40.216 | 54.3735 | 57.6519 | 55.0646 | 59.1947 | 52.7867 | 59.0735 | 56.3407 | 54.7146 | 61.6242 | 52.7699 | 56.5444 | 56.8647 | 55.9655 | 54.549 | 56.1548 | 56.2634 | 57.8825 | 40.8409 | 36.9225 | 45.44 | 55.7482 | 54.0459 | 60.3073 | 58.2424 | 56.4892 | 54.6131 | 58.1802 | 52.1551 | 58.6076 | 54.5683 | 55.8956 | 52.3166 | 58.2349 | 57.1429 | 57.4351 | 60.2658 | 56.3335 | 57.7283 | 59.0987 | 60.6239 | 56.6018 | 59.7896 | 59.3627 | 62.0565 | 55.6509 | 60.8145 | 57.9732 | 61.9857 | 57.3573 | 61.5916 | 57.193 | 62.3454 | 56.4318 | 60.6407 | 62.4947 | 94.4863 | 94.7891 | 93.9491
2022-09-07 19:03 | 0:39 | 38.56 | 37.2315 | 40.0776 | 54.367 | 57.5243 | 54.8541 | 58.9162 | 52.6754 | 58.9841 | 56.0326 | 54.7234 | 61.428 | 52.6467 | 56.1006 | 56.7668 | 55.8613 | 54.4844 | 55.9777 | 56.1945 | 57.8669 | 40.7769 | 36.8318 | 45.3358 | 55.5016 | 53.9099 | 60.3464 | 58.1908 | 56.5789 | 54.5207 | 58.0862 | 52.0326 | 58.414 | 54.5472 | 55.8913 | 52.3271 | 57.907 | 56.956 | 57.2578 | 60.2935 | 56.2255 | 57.606 | 59.0843 | 60.5548 | 56.5687 | 59.7962 | 59.2157 | 61.8661 | 55.5319 | 60.3927 | 57.7489 | 61.636 | 57.3576 | 61.4788 | 57.2181 | 62.0707 | 56.332 | 60.2904 | 62.4364 | 94.604 | 94.9826 | 93.977
2022-09-07 19:04 | 0:40 | 38.4416 | 37.1512 | 39.9615 | 54.2446 | 57.3648 | 54.7667 | 59.1646 | 52.5149 | 58.8739 | 56.0812 | 54.6887 | 61.3775 | 52.3151 | 56.1411 | 56.6456 | 55.7913 | 54.3398 | 55.9101 | 55.9938 | 57.8871 | 40.6765 | 36.75 | 45.2466 | 55.3158 | 53.807 | 60.0963 | 58.1848 | 56.4728 | 54.5332 | 57.8994 | 51.8885 | 58.5272 | 54.4503 | 55.7633 | 52.2358 | 57.8658 | 56.8293 | 57.1566 | 59.932 | 56.1895 | 57.5629 | 58.8765 | 60.3593 | 56.3711 | 59.5616 | 59.0899 | 61.7419 | 55.5305 | 60.1935 | 57.6172 | 61.7957 | 57.1992 | 61.5377 | 56.9883 | 62.1085 | 56.2234 | 60.3335 | 62.3653 | 94.707 | 95.1372 | 94.1811
2022-09-07 19:04 | 0:40 | 38.3213 | 37.0867 | 39.8956 | 54.1919 | 57.347 | 54.4485 | 58.8842 | 52.4908 | 58.7749 | 56.0326 | 54.7092 | 61.0792 | 52.3643 | 56.0522 | 56.5814 | 55.6448 | 54.3139 | 55.8515 | 55.9257 | 57.8935 | 40.5814 | 36.6737 | 45.1272 | 55.2039 | 53.6781 | 60.1371 | 57.8878 | 56.3882 | 54.3912 | 57.9016 | 51.8434 | 58.219 | 54.3008 | 55.48 | 52.0158 | 57.8572 | 56.5881 | 56.9163 | 59.7543 | 55.98 | 57.4962 | 58.9336 | 60.1607 | 56.1708 | 59.5729 | 58.924 | 61.4855 | 55.4087 | 60.0062 | 57.5722 | 61.3606 | 56.9761 | 61.1869 | 56.9349 | 61.9072 | 56.062 | 60.1767 | 62.1828 | 94.9235 | 95.3172 | 94.2848
2022-09-07 19:04 | 0:40 | 38.2195 | 36.9997 | 39.7609 | 54.0997 | 57.2177 | 54.6745 | 58.6031 | 52.2591 | 58.603 | 55.8114 | 54.2695 | 61.0831 | 52.3153 | 55.9217 | 56.4597 | 55.5313 | 54.116 | 55.9778 | 55.7605 | 57.4564 | 40.4849 | 36.5819 | 45.023 | 55.1621 | 53.5472 | 59.6664 | 57.7283 | 56.4492 | 54.3413 | 57.6541 | 51.7964 | 58.2149 | 54.2094 | 55.4954 | 51.7124 | 57.771 | 56.2191 | 56.8394 | 59.5936 | 55.91 | 57.5019 | 58.8184 | 59.9579 | 55.994 | 59.3984 | 58.8021 | 61.6232 | 55.3409 | 59.7287 | 57.4913 | 61.5041 | 56.9067 | 61.1824 | 56.8894 | 61.8996 | 55.9428 | 59.9527 | 62.0707 | 94.9692 | 95.4948 | 94.4261
2022-09-07 19:04 | 0:40 | 38.0935 | 36.8849 | 39.6398 | 54.0451 | 57.2017 | 54.2972 | 58.8332 | 52.1899 | 58.4896 | 55.6121 | 54.1931 | 60.998 | 52.1757 | 55.8722 | 56.3191 | 55.4245 | 54.0451 | 55.8252 | 55.7784 | 57.4402 | 40.4078 | 36.459 | 44.9302 | 55.116 | 53.4372 | 59.6794 | 57.606 | 55.9925 | 54.2178 | 57.5103 | 51.6379 | 57.996 | 54.0731 | 55.3379 | 51.7428 | 57.7452 | 56.3273 | 56.7071 | 59.3751 | 55.67 | 57.1499 | 58.5844 | 60.0011 | 55.9563 | 59.2684 | 58.6227 | 61.5943 | 55.2463 | 59.8672 | 57.2926 | 61.1165 | 56.5661 | 60.9704 | 56.6321 | 61.7546 | 55.8881 | 59.8308 | 62.038 | 95.0606 | 95.5702 | 94.4453
2022-09-07 19:04 | 0:40 | 37.8935 | 36.7768 | 39.5143 | 53.8143 | 57.0589 | 54.0916 | 58.4437 | 52.1799 | 58.4149 | 55.479 | 54.3864 | 60.8554 | 52.0058 | 55.6435 | 56.4388 | 55.3508 | 53.9287 | 55.4762 | 55.5738 | 57.1683 | 40.3099 | 36.3714 | 44.8498 | 54.9141 | 53.3258 | 59.49 | 57.5629 | 55.934 | 54.1058 | 57.4102 | 51.6037 | 57.8457 | 53.9248 | 55.1454 | 51.5861 | 57.4788 | 56.1902 | 56.6247 | 59.4451 | 55.5754 | 56.9452 | 58.5181 | 59.9635 | 55.7914 | 59.1157 | 58.5791 | 61.5244 | 54.9974 | 59.8158 | 57.016 | 61.126 | 56.5339 | 60.9268 | 56.4602 | 61.3533 | 55.7747 | 59.803 | 61.863 | 95.1345 | 95.6429 | 94.4722
2022-09-07 19:04 | 0:40 | 37.7236 | 36.6767 | 39.4089 | 53.6863 | 56.8783 | 54.0776 | 58.3252 | 51.9433 | 58.2695 | 55.4293 | 54.2344 | 60.609 | 51.9153 | 55.4661 | 56.1627 | 55.1351 | 53.7801 | 55.5447 | 55.3991 | 57.4132 | 40.2355 | 36.2739 | 44.777 | 54.817 | 53.1635 | 59.6928 | 57.4962 | 55.9248 | 53.9979 | 57.2259 | 51.4492 | 57.6581 | 53.7686 | 55.1667 | 51.6939 | 57.1999 | 56.2041 | 56.6343 | 58.9774 | 55.5978 | 57.0608 | 58.4469 | 59.8717 | 55.7959 | 59.0947 | 58.5361 | 61.2524 | 54.9296 | 59.9188 | 56.955 | 60.797 | 56.4017 | 60.6682 | 56.3292 | 61.3873 | 55.6652 | 59.6096 | 61.6967 | 95.1359 | 95.6378 | 94.5449
2022-09-07 19:05 | 0:40 | 37.56 | 36.592 | 39.267 | 53.7943 | 56.663 | 53.9986 | 58.3466 | 51.8605 | 58.1974 | 55.2944 | 53.965 | 60.5617 | 51.8491 | 55.3123 | 56.0396 | 55.0878 | 53.5973 | 55.2082 | 55.4032 | 57.3828 | 40.1467 | 36.1686 | 44.711 | 54.6658 | 53.0306 | 59.6107 | 57.5019 | 55.4149 | 53.7612 | 57.1413 | 51.286 | 57.5954 | 53.631 | 55.0535 | 51.2593 | 57.0211 | 56.0411 | 56.4595 | 58.8937 | 55.5225 | 56.8549 | 58.1948 | 59.7734 | 55.7425 | 58.8883 | 58.4325 | 60.9171 | 54.8729 | 59.6076 | 56.8958 | 60.8894 | 56.4769 | 60.4679 | 56.3155 | 61.5207 | 55.525 | 59.5889 | 61.3822 | 94.9092 | 95.4216 | 94.295
2022-09-07 19:05 | 0:41 | 37.3759 | 36.5275 | 39.1704 | 53.4216 | 56.6475 | 53.8358 | 58.1743 | 51.8591 | 58.0824 | 55.0919 | 53.9981 | 60.5904 | 51.7677 | 55.4252 | 55.7499 | 54.9703 | 53.4844 | 55.3423 | 55.2151 | 57.2845 | 40.0868 | 36.1353 | 44.6149 | 54.5947 | 52.9443 | 59.2264 | 57.1499 | 55.4648 | 53.8208 | 56.8824 | 51.3002 | 57.5336 | 53.4097 | 54.8406 | 50.9971 | 57.0803 | 56.2466 | 56.3357 | 58.7916 | 55.4801 | 56.7899 | 58.0125 | 59.6088 | 55.6262 | 58.7738 | 58.3139 | 60.9836 | 54.6449 | 59.5414 | 56.6776 | 60.8162 | 56.0416 | 60.1719 | 55.9258 | 61.5197 | 55.3437 | 59.377 | 61.336 | 94.6693 | 95.0965 | 94.1278
2022-09-07 19:05 | 0:41 | 37.2425 | 36.4181 | 39.0688 | 53.2802 | 56.5958 | 53.6405 | 58.0496 | 51.6805 | 57.9717 | 55.0946 | 53.8058 | 60.3809 | 51.667 | 55.3208 | 55.7577 | 54.9383 | 53.4839 | 55.4508 | 55.2055 | 56.9716 | 39.9861 | 36.0192 | 44.5027 | 54.5752 | 52.8884 | 59.093 | 56.9452 | 55.706 | 53.77 | 56.8871 | 51.1671 | 57.4045 | 53.216 | 54.7328 | 50.6704 | 56.7784 | 55.8037 | 56.2483 | 58.5582 | 55.1986 | 56.5765 | 57.9435 | 59.4008 | 55.5441 | 58.5632 | 58.2374 | 60.8499 | 54.5888 | 59.5251 | 56.7029 | 60.2715 | 56.1597 | 60.1722 | 56.0549 | 61.0062 | 55.2804 | 59.3042 | 61.148 | 94.4347 | 94.8395 | 93.974
2022-09-07 19:05 | 0:41 | 37.1878 | 36.3144 | 38.9759 | 53.4169 | 56.5189 | 53.4365 | 57.5568 | 51.6032 | 57.8216 | 54.692 | 53.6166 | 60.3083 | 51.5585 | 55.0018 | 55.6243 | 54.7315 | 53.3463 | 54.9711 | 55.0719 | 56.7659 | 39.8787 | 35.8928 | 44.4071 | 54.457 | 52.7036 | 59.1342 | 57.0608 | 55.1803 | 53.5841 | 56.7253 | 51 | 57.3161 | 53.302 | 54.6036 | 50.4055 | 56.8802 | 55.7659 | 56.1106 | 58.6898 | 55.1625 | 56.4329 | 57.885 | 59.3996 | 55.4064 | 58.5485 | 58.0847 | 60.7602 | 54.4588 | 59.532 | 56.5539 | 60.5776 | 56.1694 | 60.2413 | 55.8281 | 61.2703 | 55.1372 | 59.0582 | 61.1081 | 94.2909 | 94.7011 | 93.8985
2022-09-07 19:05 | 0:41 | 37.1318 | 36.1919 | 38.8419 | 53.304 | 56.3838 | 53.2987 | 57.6664 | 51.3349 | 57.6666 | 54.6588 | 53.6226 | 60.1215 | 51.4894 | 54.9247 | 55.603 | 54.5975 | 53.2569 | 54.9485 | 54.7567 | 56.8375 | 39.8104 | 35.7946 | 44.3475 | 54.3302 | 52.6271 | 59.0216 | 56.8549 | 55.0969 | 53.4687 | 56.7368 | 50.9605 | 57.1883 | 53.1698 | 54.4208 | 50.2677 | 56.8218 | 55.4646 | 55.951 | 58.7568 | 54.9387 | 56.492 | 57.7641 | 59.181 | 55.267 | 58.3487 | 57.9639 | 60.7836 | 54.3404 | 58.94 | 56.3113 | 60.5306 | 55.8563 | 60.0106 | 55.7969 | 60.9528 | 55.0899 | 58.9518 | 61.1392 | 94.2335 | 94.553 | 93.7988
2022-09-07 19:05 | 0:41 | 36.9705 | 36.0841 | 38.7725 | 53.2824 | 56.2735 | 53.299 | 57.5507 | 51.2943 | 57.6301 | 54.5504 | 53.6449 | 60.0623 | 51.4465 | 54.8021 | 55.4359 | 54.4774 | 53.13 | 54.6609 | 54.8331 | 56.6923 | 39.6975 | 35.7253 | 44.2385 | 54.0412 | 52.5213 | 58.728 | 56.7899 | 54.9637 | 53.349 | 56.5389 | 50.9537 | 57.1179 | 53.0484 | 54.4548 | 50.1723 | 56.84 | 55.3538 | 55.8788 | 58.6631 | 54.8711 | 56.3221 | 57.6529 | 59.008 | 55.1738 | 58.2595 | 57.9241 | 60.5938 | 54.2073 | 58.9576 | 56.1681 | 60.284 | 55.6401 | 59.9449 | 55.5446 | 60.8212 | 54.7827 | 59.168 | 60.9706 | 94.1562 | 94.4709 | 93.8011
2022-09-07 19:06 | 0:41 | 36.8417 | 36.0023 | 38.6379 | 53.1355 | 56.1696 | 53.2339 | 57.4211 | 51.1795 | 57.4119 | 54.4068 | 53.1453 | 59.8943 | 51.2585 | 54.5945 | 55.2508 | 54.4256 | 53.0072 | 54.2682 | 54.78 | 56.7736 | 39.6212 | 35.6313 | 44.1248 | 53.9809 | 52.4241 | 58.6263 | 56.5765 | 54.9874 | 53.2333 | 56.3304 | 50.7597 | 56.9523 | 53.0374 | 54.2538 | 49.9129 | 56.8274 | 55.3023 | 55.6184 | 58.6895 | 54.6545 | 56.1118 | 57.5385 | 58.9522 | 55.0995 | 58.2149 | 57.7481 | 60.5548 | 54.1393 | 58.8901 | 56.0683 | 60.3176 | 55.6917 | 59.7189 | 55.4982 | 60.7676 | 54.7516 | 58.985 | 60.6485 | 94.074 | 94.3961 | 93.8098
2022-09-07 19:06 | 0:42 | 36.6455 | 35.8941 | 38.5404 | 52.9523 | 56.0985 | 53.2576 | 57.4425 | 51.0422 | 57.3808 | 54.2956 | 53.3301 | 59.7867 | 51.1605 | 54.7718 | 54.9893 | 54.3179 | 52.8828 | 54.5568 | 54.4835 | 56.5994 | 39.5137 | 35.547 | 44.0206 | 53.8448 | 52.307 | 58.5363 | 56.4329 | 54.7724 | 53.2286 | 56.1589 | 50.5946 | 56.9105 | 52.8429 | 54.2538 | 49.7982 | 56.8145 | 55.3662 | 55.6554 | 58.3698 | 54.6428 | 56.0611 | 57.4203 | 58.9243 | 54.976 | 58.0782 | 57.624 | 60.4525 | 53.9732 | 58.7332 | 55.995 | 60.0526 | 55.5174 | 59.7309 | 55.3859 | 60.6597 | 54.6911 | 58.8477 | 60.6555 | 94.0466 | 94.3535 | 93.7458
2022-09-07 19:06 | 0:42 | 36.5879 | 35.8073 | 38.4505 | 52.685 | 55.9724 | 53.1452 | 57.3699 | 51.012 | 57.3398 | 54.2003 | 52.9293 | 59.7045 | 51.0524 | 54.6472 | 54.9592 | 54.1906 | 52.854 | 54.5245 | 54.4326 | 56.3817 | 39.3754 | 35.4001 | 43.859 | 53.8486 | 52.1142 | 58.4708 | 56.492 | 55.0138 | 53.0278 | 56.2025 | 50.6257 | 56.7104 | 52.7252 | 54.1144 | 49.85 | 56.509 | 55.1244 | 55.6553 | 58.0935 | 54.4111 | 55.9048 | 57.2666 | 58.615 | 54.7398 | 57.9558 | 57.4734 | 60.217 | 53.8944 | 58.7394 | 55.8205 | 59.99 | 55.5354 | 59.4953 | 55.41 | 60.4031 | 54.6689 | 58.8022 | 60.4552 | 93.9989 | 94.2842 | 93.645
2022-09-07 19:06 | 0:42 | 36.5247 | 35.7229 | 38.3117 | 52.5798 | 55.8579 | 53.0771 | 57.4449 | 50.8602 | 57.1369 | 53.941 | 53.1044 | 59.5779 | 50.8821 | 54.5336 | 54.8401 | 54.0139 | 52.6651 | 54.6945 | 54.3744 | 56.1848 | 39.2563 | 35.3248 | 43.7522 | 53.7453 | 52.0028 | 58.4434 | 56.3221 | 54.7854 | 52.8175 | 56.0787 | 50.4686 | 56.556 | 52.6408 | 54.0188 | 49.6906 | 56.1422 | 55.0574 | 55.3875 | 57.6524 | 54.3286 | 55.8743 | 57.2337 | 58.5681 | 54.5237 | 57.9733 | 57.2563 | 60.1301 | 53.6812 | 58.3632 | 55.8049 | 59.7702 | 55.5531 | 59.812 | 55.0473 | 60.2983 | 54.4378 | 58.4438 | 60.2824 | 93.9648 | 94.2483 | 93.6832
2022-09-07 19:06 | 0:42 | 36.4321 | 35.624 | 38.2451 | 52.5598 | 55.7676 | 53.0175 | 57.1766 | 50.8402 | 57.0908 | 53.9057 | 53.0821 | 59.4466 | 50.7642 | 54.2647 | 54.7386 | 53.8609 | 52.6029 | 54.212 | 54.3006 | 55.9595 | 39.1564 | 35.2382 | 43.649 | 53.5943 | 51.885 | 58.0997 | 56.1118 | 54.3828 | 52.6624 | 55.8896 | 50.0632 | 56.4237 | 52.4555 | 53.7894 | 49.7961 | 56.0302 | 54.7605 | 55.2424 | 57.7484 | 54.1745 | 55.6085 | 57.0979 | 58.3325 | 54.4828 | 57.6241 | 57.113 | 59.9428 | 53.6452 | 58.1663 | 55.6919 | 59.6942 | 55.4543 | 59.5086 | 55.135 | 60.0731 | 54.4286 | 58.6379 | 60.3676 | 93.8979 | 94.1872 | 93.5878
2022-09-07 19:06 | 0:42 | 36.3566 | 35.5386 | 38.1999 | 52.335 | 55.6165 | 52.6855 | 57.1822 | 50.6502 | 56.9533 | 53.7568 | 53.0866 | 59.4533 | 50.6149 | 54.0287 | 54.5973 | 53.7869 | 52.4224 | 53.822 | 54.1966 | 55.9158 | 39.0902 | 35.1247 | 43.5663 | 53.4552 | 51.8408 | 58.2624 | 56.0611 | 54.1915 | 52.523 | 55.8499 | 49.9757 | 56.3873 | 52.4464 | 53.7252 | 49.5838 | 56.0758 | 54.736 | 55.2218 | 57.3878 | 54.1599 | 55.3383 | 56.9021 | 58.169 | 54.4694 | 57.633 | 57.1024 | 59.7683 | 53.5102 | 58.3097 | 55.4729 | 59.6011 | 55.1454 | 59.2233 | 54.9127 | 60.0083 | 54.2599 | 58.3805 | 60.2318 | 93.8255 | 94.0874 | 93.617
2022-09-07 19:07 | 0:43 | 36.2625 | 35.4259 | 38.0842 | 52.449 | 55.5109 | 52.7026 | 56.8746 | 50.5845 | 56.8465 | 53.7768 | 52.6368 | 59.2547 | 50.4836 | 53.956 | 54.4807 | 53.6691 | 52.3036 | 54 | 54.0371 | 55.6278 | 39.0111 | 35.0708 | 43.5126 | 53.3791 | 51.6879 | 58.1493 | 55.9048 | 54.0749 | 52.4102 | 55.7301 | 49.8564 | 56.1463 | 52.1785 | 53.6912 | 49.4709 | 56.2087 | 54.6124 | 55.0752 | 57.7024 | 54.05 | 55.4414 | 56.9195 | 58.2788 | 54.4012 | 57.7055 | 56.9681 | 59.4646 | 53.3642 | 58.1886 | 55.4468 | 59.5341 | 55.1125 | 59.1828 | 54.8342 | 59.6449 | 54.2705 | 58.2965 | 60.1933 | 93.7184 | 94.0335 | 93.5172
2022-09-07 19:07 | 0:43 | 36.1773 | 35.3468 | 37.9802 | 52.0337 | 55.441 | 52.6511 | 56.6577 | 50.5217 | 56.716 | 53.6874 | 52.7486 | 59.1028 | 50.4134 | 54.0027 | 54.4367 | 53.5308 | 52.1736 | 53.7563 | 53.7981 | 55.6783 | 38.9295 | 34.9626 | 43.4269 | 53.1765 | 51.6111 | 57.9055 | 55.8743 | 54.1688 | 52.4143 | 55.5523 | 49.7952 | 56.0936 | 52.1297 | 53.4963 | 49.278 | 55.9672 | 54.4524 | 55.0299 | 57.6364 | 53.9303 | 55.2728 | 56.7795 | 58.1944 | 54.0662 | 57.3376 | 56.7675 | 59.4587 | 53.2507 | 57.9351 | 55.3644 | 59.1832 | 55.1114 | 59.0001 | 54.7235 | 59.8269 | 54.1511 | 58.0943 | 60.0727 | 93.6403 | 93.9665 | 93.4921
2022-09-07 19:07 | 0:43 | 36.0284 | 35.2242 | 37.8479 | 52.1375 | 55.3628 | 52.5641 | 56.5782 | 50.3666 | 56.6058 | 53.5932 | 52.2619 | 58.9461 | 50.3537 | 54.0294 | 54.2794 | 53.3744 | 52.1157 | 53.7667 | 53.8124 | 55.4921 | 38.8386 | 34.8652 | 43.345 | 53.151 | 51.5134 | 58.0116 | 55.6085 | 53.9546 | 52.3301 | 55.5117 | 49.7963 | 56.0012 | 52.0771 | 53.315 | 49.1179 | 55.7956 | 54.4799 | 54.8157 | 57.4564 | 53.8486 | 55.1342 | 56.6941 | 57.9575 | 53.9501 | 57.2718 | 56.696 | 59.589 | 53.2341 | 57.8725 | 55.2767 | 59.4632 | 54.7987 | 58.8955 | 54.4669 | 59.719 | 54.0157 | 57.8065 | 59.9106 | 93.5847 | 93.8518 | 93.4873
2022-09-07 19:07 | 0:43 | 35.9895 | 35.1513 | 37.7194 | 52.0316 | 55.0502 | 52.2103 | 56.7065 | 50.2489 | 56.4636 | 53.4576 | 52.4175 | 58.7876 | 50.1522 | 53.8987 | 54.2271 | 53.412 | 52.0873 | 54.1181 | 53.7102 | 55.4161 | 38.755 | 34.7858 | 43.2352 | 53.0602 | 51.3023 | 57.5911 | 55.3383 | 54.1275 | 52.2622 | 55.3408 | 49.8218 | 55.74 | 52.137 | 53.3115 | 49.0128 | 55.508 | 54.2177 | 54.7204 | 57.3233 | 53.6284 | 55.1067 | 56.4988 | 57.8727 | 53.8596 | 57.1916 | 56.5192 | 59.3016 | 53.0206 | 57.8071 | 55.0912 | 59.0754 | 54.5689 | 58.7475 | 54.6309 | 59.6761 | 53.8397 | 57.8029 | 59.6445 | 93.4987 | 93.733 | 93.3657
2022-09-07 19:07 | 0:43 | 35.8205 | 35.0881 | 37.6493 | 51.8608 | 55.2159 | 52.2511 | 56.5333 | 50.0188 | 56.3506 | 53.3795 | 52.1917 | 58.7651 | 50.0963 | 53.6267 | 54.1304 | 53.2328 | 52.0363 | 53.9324 | 53.6437 | 55.2984 | 38.6683 | 34.6958 | 43.176 | 52.9129 | 51.2946 | 57.6724 | 55.4414 | 53.7209 | 52.131 | 55.4012 | 49.7114 | 55.7899 | 51.9846 | 53.2032 | 49.0497 | 55.4049 | 54.2786 | 54.608 | 57.2758 | 53.6178 | 55.0962 | 56.4323 | 57.6498 | 53.7739 | 57.0632 | 56.5033 | 59.3212 | 52.9527 | 57.8735 | 54.8933 | 58.8961 | 54.3007 | 58.7495 | 54.3121 | 59.4771 | 53.6434 | 57.6479 | 59.7425 | 93.348 | 93.6165 | 93.2219
2022-09-07 19:07 | 0:43 | 35.6895 | 34.9681 | 37.5617 | 51.7819 | 55.0546 | 52.3828 | 56.4267 | 49.9464 | 56.2852 | 53.282 | 51.9652 | 58.6164 | 50.0166 | 53.607 | 54.0436 | 53.1241 | 51.7906 | 53.7655 | 53.3937 | 55.1829 | 38.601 | 34.5895 | 43.075 | 52.8798 | 51.1789 | 57.5348 | 55.2728 | 53.4484 | 52.0409 | 55.2093 | 49.4267 | 55.6075 | 51.7609 | 52.9679 | 48.8742 | 55.1522 | 53.9439 | 54.4813 | 57.3395 | 53.4531 | 54.8835 | 56.3805 | 57.5124 | 53.8307 | 56.9895 | 56.3916 | 59.0659 | 52.8838 | 57.7509 | 54.8406 | 58.8445 | 54.2603 | 58.5118 | 54.2051 | 58.9973 | 53.5423 | 57.6581 | 59.4083 | 93.2625 | 93.539 | 93.2194
2022-09-07 19:08 | 0:43 | 35.5776 | 34.8974 | 37.4194 | 51.6283 | 55.0136 | 52.0876 | 56.3299 | 49.9169 | 56.2458 | 53.0804 | 52.2446 | 58.4494 | 49.9217 | 53.3501 | 53.9446 | 53.0447 | 51.687 | 53.0979 | 53.3526 | 55.2628 | 38.5477 | 34.5213 | 42.9739 | 52.602 | 51.0404 | 57.2656 | 55.1342 | 53.2817 | 51.9272 | 54.968 | 49.4826 | 55.5607 | 51.6686 | 52.8637 | 48.6995 | 54.9502 | 53.7726 | 54.2854 | 56.9551 | 53.2737 | 54.7779 | 56.1379 | 57.5305 | 53.6942 | 56.7934 | 56.2797 | 59.1438 | 52.7813 | 57.4703 | 54.9043 | 58.9968 | 54.1959 | 58.5324 | 53.9203 | 59.1737 | 53.4742 | 57.6191 | 59.5387 | 93.2454 | 93.4502 | 93.1474
2022-09-07 19:08 | 0:44 | 35.4105 | 34.7863 | 37.3215 | 51.5528 | 54.8558 | 52.1565 | 56.3051 | 49.7749 | 56.0832 | 52.9617 | 51.6585 | 58.5242 | 49.7161 | 53.3718 | 53.911 | 52.9312 | 51.5232 | 53.0067 | 53.3106 | 55.1513 | 38.4603 | 34.4441 | 42.9097 | 52.6393 | 50.937 | 57.1834 | 55.1067 | 53.4047 | 51.8067 | 54.8313 | 49.2238 | 55.3499 | 51.4621 | 52.8409 | 48.7212 | 54.9375 | 53.9157 | 54.1964 | 56.5211 | 53.2326 | 54.5765 | 56.058 | 57.4975 | 53.5041 | 56.719 | 56.1525 | 58.8412 | 52.6332 | 57.5793 | 54.7137 | 58.5824 | 54.0311 | 58.0877 | 53.9459 | 59.1651 | 53.4212 | 57.2304 | 59.331 | 93.1295 | 93.3803 | 93.0555
2022-09-07 19:08 | 0:44 | 35.3625 | 34.6977 | 37.2754 | 51.6313 | 54.8273 | 52.0739 | 55.9922 | 49.6902 | 55.9669 | 52.9164 | 51.7537 | 58.3802 | 49.708 | 53.365 | 53.8138 | 52.7551 | 51.5062 | 52.9468 | 53.1257 | 55.053 | 38.3887 | 34.3432 | 42.8061 | 52.5727 | 50.8263 | 57.1685 | 55.0962 | 53.1327 | 51.5796 | 54.6835 | 49.0052 | 55.2477 | 51.4073 | 52.7299 | 48.5887 | 54.8945 | 53.7245 | 54.0734 | 56.6392 | 53.0703 | 54.5054 | 55.9836 | 57.465 | 53.5299 | 56.559 | 56.0473 | 58.8302 | 52.5164 | 57.3501 | 54.6507 | 58.5441 | 54.0914 | 58.062 | 53.8161 | 59.0025 | 53.1913 | 57.0975 | 59.28 | 93.0452 | 93.2529 | 93.0518
2022-09-07 19:08 | 0:44 | 35.3587 | 34.6256 | 37.1641 | 51.4316 | 54.6943 | 51.7193 | 56.1368 | 49.819 | 55.8229 | 52.8362 | 52.1128 | 58.2579 | 49.5818 | 52.9504 | 53.6272 | 52.6775 | 51.39 | 53.0148 | 52.8928 | 55.0286 | 38.3232 | 34.2642 | 42.7655 | 52.3565 | 50.6915 | 56.977 | 54.8835 | 53.1006 | 51.5093 | 54.7197 | 49.0222 | 55.2373 | 51.3456 | 52.5505 | 48.4324 | 54.8358 | 53.6067 | 53.9219 | 56.7533 | 52.9633 | 54.4007 | 55.8263 | 57.389 | 53.369 | 56.444 | 55.942 | 58.9147 | 52.4898 | 57.3984 | 54.3831 | 58.5844 | 53.932 | 58.1569 | 53.6221 | 58.7631 | 53.0407 | 57.1625 | 59.0966 | 92.9379 | 93.097 | 92.9031
2022-09-07 19:08 | 0:44 | 35.1048 | 34.5457 | 37.0465 | 51.2704 | 54.4658 | 51.8548 | 56.0189 | 49.4736 | 55.7573 | 52.7729 | 51.7326 | 58.1021 | 49.4924 | 52.8866 | 53.408 | 52.5164 | 51.2654 | 52.7806 | 52.8541 | 54.8413 | 38.23 | 34.1705 | 42.6532 | 52.2483 | 50.5513 | 56.8227 | 54.7779 | 52.8967 | 51.3208 | 54.5301 | 48.944 | 55.1383 | 51.1974 | 52.5179 | 48.4419 | 54.9644 | 53.5104 | 53.8151 | 56.6962 | 52.8915 | 54.3195 | 55.6876 | 57.1464 | 53.1412 | 56.3158 | 55.8192 | 58.6399 | 52.3484 | 57.1691 | 54.4939 | 58.109 | 53.8286 | 58.0691 | 53.6888 | 58.4761 | 53.0025 | 57.1095 | 59.0287 | 92.8095 | 92.9758 | 92.8561
2022-09-07 19:08 | 0:44 | 34.8642 | 34.4648 | 36.9368 | 51.2314 | 54.4944 | 51.6763 | 55.8163 | 49.4483 | 55.5579 | 52.8055 | 51.7253 | 58.0917 | 49.3466 | 52.8502 | 53.2696 | 52.4594 | 51.2163 | 52.5687 | 52.7454 | 54.8128 | 38.1511 | 34.0909 | 42.5541 | 52.199 | 50.5053 | 56.6274 | 54.5765 | 52.8181 | 51.2142 | 54.3773 | 48.9202 | 55.0215 | 51.1541 | 52.5517 | 48.3505 | 54.6415 | 53.5193 | 53.9441 | 56.5801 | 52.8819 | 54.0632 | 55.7506 | 56.9798 | 53.2128 | 56.3182 | 55.6786 | 58.5642 | 52.3087 | 57.0646 | 54.1579 | 58.0335 | 53.6459 | 57.8488 | 53.4133 | 58.6512 | 52.8643 | 56.8005 | 58.5355 | 92.6634 | 92.8523 | 92.7395
2022-09-07 19:09 | 0:45 | 34.7715 | 34.3309 | 36.8446 | 50.9495 | 54.3677 | 51.5028 | 55.8436 | 49.3704 | 55.5258 | 52.7888 | 51.793 | 58.0641 | 49.1775 | 52.8715 | 53.2698 | 52.3931 | 50.9804 | 52.7657 | 52.6796 | 54.47 | 38.0621 | 34.0047 | 42.4852 | 52.1295 | 50.4121 | 56.6202 | 54.5054 | 52.5453 | 51.1779 | 54.2276 | 48.926 | 54.916 | 50.9104 | 52.3212 | 48.2129 | 54.7014 | 53.3106 | 53.6266 | 56.4172 | 52.7461 | 54.108 | 55.6596 | 56.8994 | 52.879 | 56.1684 | 55.5698 | 58.4594 | 52.1067 | 56.8054 | 54.2394 | 57.8236 | 53.646 | 57.8482 | 53.6254 | 58.4339 | 52.7963 | 56.7152 | 58.7079 | 92.5112 | 92.6946 | 92.605
2022-09-07 19:09 | 0:45 | 34.5434 | 34.237 | 36.6661 | 50.9699 | 54.202 | 51.2326 | 55.4125 | 49.2472 | 55.4108 | 52.6277 | 51.4976 | 57.8718 | 49.1582 | 52.7166 | 53.0787 | 52.2938 | 50.9574 | 52.668 | 52.5997 | 54.532 | 37.9723 | 33.9183 | 42.4095 | 52.0549 | 50.2674 | 56.6665 | 54.4007 | 52.7489 | 51.133 | 54.1811 | 48.7097 | 54.7191 | 50.9534 | 52.1564 | 48.1402 | 54.4834 | 53.2372 | 53.5204 | 56.2631 | 52.6145 | 54.0377 | 55.5003 | 56.8245 | 52.7737 | 56.1206 | 55.443 | 58.1763 | 51.9615 | 56.7369 | 54.0516 | 57.862 | 53.4965 | 57.7167 | 53.3842 | 58.2507 | 52.7744 | 56.74 | 58.5251 | 92.3405 | 92.532 | 92.4996
2022-09-07 19:09 | 0:45 | 34.582 | 34.1405 | 36.582 | 50.833 | 54.1191 | 51.266 | 55.4198 | 49.172 | 55.278 | 52.5575 | 51.4129 | 57.7456 | 48.9834 | 52.4004 | 53.1135 | 52.165 | 50.8231 | 52.421 | 52.6328 | 54.5173 | 37.9011 | 33.8293 | 42.3012 | 52.0485 | 50.1748 | 56.408 | 54.3195 | 52.7127 | 50.8065 | 54.2272 | 48.5412 | 54.5493 | 50.7643 | 52.1016 | 48.0532 | 54.4572 | 52.9079 | 53.4856 | 56.0448 | 52.3788 | 53.8894 | 55.3408 | 56.57 | 52.7142 | 55.8971 | 55.3596 | 57.9072 | 51.7958 | 56.6668 | 53.9661 | 57.7675 | 53.5072 | 57.482 | 53.1139 | 58.2454 | 52.6092 | 56.444 | 58.4766 | 92.1605 | 92.3114 | 92.3301
2022-09-07 19:09 | 0:45 | 34.4302 | 34.0228 | 36.4503 | 50.9229 | 54.0134 | 51.2466 | 55.2766 | 48.9079 | 55.2197 | 52.3164 | 51.0235 | 57.6751 | 48.8868 | 52.3147 | 52.9677 | 52.0988 | 50.6806 | 52.2991 | 52.4061 | 54.2516 | 37.7862 | 33.7377 | 42.1957 | 51.8287 | 50.0875 | 56.2356 | 54.0632 | 52.5745 | 50.9113 | 54.0084 | 48.4034 | 54.4938 | 50.7486 | 51.9856 | 48.2158 | 54.0499 | 53.0879 | 53.2561 | 56.1057 | 52.4373 | 53.7771 | 55.1735 | 56.47 | 52.5566 | 55.8323 | 55.2321 | 58.0426 | 51.781 | 56.2904 | 53.7953 | 57.8432 | 53.421 | 57.2628 | 52.9891 | 58.2227 | 52.4904 | 56.4456 | 58.4425 | 91.9231 | 92.095 | 92.1145
2022-09-07 19:09 | 0:45 | 34.492 | 33.9337 | 36.4173 | 50.8274 | 53.9123 | 51.0136 | 54.9201 | 48.8724 | 55.0387 | 52.038 | 51.0376 | 57.4765 | 48.855 | 52.4006 | 52.7051 | 51.9785 | 50.6226 | 51.9425 | 52.2983 | 54.2501 | 37.6632 | 33.6158 | 42.0887 | 51.7074 | 49.9914 | 56.3536 | 54.108 | 52.5954 | 50.7127 | 53.9188 | 48.1846 | 54.4363 | 50.5366 | 51.8944 | 47.9207 | 53.8381 | 52.9947 | 53.2951 | 56.0089 | 52.3192 | 53.645 | 54.9971 | 56.5738 | 52.648 | 55.7242 | 55.203 | 57.7584 | 51.6187 | 56.484 | 53.752 | 57.7391 | 52.9823 | 57.3384 | 52.8709 | 58.2693 | 52.3222 | 56.3394 | 58.2433 | 91.7524 | 91.8942 | 91.9741
2022-09-07 19:09 | 0:45 | 34.3648 | 33.8423 | 36.3305 | 50.7326 | 53.8485 | 50.713 | 54.9398 | 48.8646 | 55.0161 | 51.9447 | 51.0027 | 57.2862 | 48.7661 | 52.2083 | 52.759 | 51.8641 | 50.5034 | 51.9209 | 52.1405 | 54.2498 | 37.5843 | 33.559 | 42.0476 | 51.5082 | 49.8413 | 56.2009 | 54.0377 | 52.4517 | 50.6332 | 53.793 | 48.2106 | 54.2535 | 50.4284 | 51.8158 | 47.6705 | 54.0188 | 52.7413 | 53.1215 | 56.0197 | 52.1987 | 53.5571 | 54.9883 | 56.402 | 52.5927 | 55.5376 | 55.0933 | 57.8906 | 51.6259 | 56.8859 | 53.5562 | 57.7001 | 52.7089 | 57.1211 | 52.7508 | 57.8668 | 52.1891 | 56.2155 | 58.0033 | 91.7076 | 91.8105 | 92.0212
2022-09-07 19:10 | 0:45 | 34.1929 | 33.7998 | 36.2285 | 50.5139 | 53.884 | 50.6981 | 54.8177 | 48.6669 | 54.885 | 51.8948 | 51.0297 | 57.1897 | 48.6218 | 52.0867 | 52.7411 | 51.7275 | 50.4488 | 51.775 | 51.9991 | 53.9156 | 37.4934 | 33.4653 | 41.9268 | 51.5044 | 49.7297 | 56.1075 | 53.8894 | 52.1502 | 50.603 | 53.7358 | 48.0431 | 54.0484 | 50.1897 | 51.6456 | 47.591 | 53.9795 | 52.5866 | 52.9044 | 55.9563 | 51.9951 | 53.3013 | 54.8919 | 56.3987 | 52.5024 | 55.5787 | 54.9222 | 57.8221 | 51.4698 | 56.1956 | 53.5697 | 57.3511 | 52.7422 | 57.1322 | 52.6367 | 57.9965 | 52.1465 | 55.912 | 57.9168 | 91.7873 | 91.8974 | 92.2506
2022-09-07 19:10 | 0:46 | 34.152 | 33.6702 | 36.1469 | 50.476 | 53.7557 | 50.883 | 54.9026 | 48.5464 | 54.7817 | 51.9142 | 50.6364 | 57.1679 | 48.4545 | 52.0391 | 52.5517 | 51.5985 | 50.387 | 51.9593 | 51.9389 | 53.9402 | 37.3995 | 33.358 | 41.8381 | 51.4192 | 49.6613 | 55.9997 | 53.7771 | 51.9426 | 50.3576 | 53.5381 | 47.9216 | 54.1851 | 50.1804 | 51.4889 | 47.5451 | 53.8928 | 52.5739 | 52.8321 | 55.7846 | 51.9333 | 53.2972 | 54.8794 | 56.1123 | 52.2719 | 55.3271 | 54.7667 | 57.3959 | 51.3554 | 56.0614 | 53.4149 | 57.0855 | 52.649 | 56.9955 | 52.6766 | 57.6097 | 52.0302 | 55.9422 | 57.746 | 91.9743 | 92.0733 | 92.3986
2022-09-07 19:10 | 0:46 | 34.1451 | 33.5632 | 36.0458 | 50.2766 | 53.6677 | 50.6572 | 54.7567 | 48.4683 | 54.6689 | 51.9681 | 50.8854 | 56.9344 | 48.4524 | 52.0807 | 52.4599 | 51.5023 | 50.2298 | 51.7683 | 51.8139 | 53.6569 | 37.2892 | 33.2647 | 41.7306 | 51.2889 | 49.4943 | 55.8035 | 53.645 | 52.1909 | 50.2435 | 53.4349 | 47.8337 | 53.9688 | 50.0073 | 51.3678 | 47.4118 | 53.5443 | 52.4106 | 52.6566 | 55.4396 | 51.8269 | 53.1688 | 54.6734 | 56.0166 | 52.2259 | 55.199 | 54.6831 | 57.2644 | 51.2321 | 55.8427 | 53.2086 | 56.7251 | 52.4692 | 56.8946 | 52.5026 | 57.4615 | 51.8978 | 56.1249 | 57.6602 | 92.1084 | 92.1816 | 92.3221
2022-09-07 19:10 | 0:46 | 34.0351 | 33.5219 | 36.0023 | 50.2936 | 53.4684 | 50.5309 | 54.7279 | 48.4688 | 54.5028 | 51.8454 | 50.7567 | 56.8909 | 48.2315 | 51.6026 | 52.3443 | 51.4592 | 50.0464 | 51.546 | 51.7325 | 53.7192 | 37.1862 | 33.1972 | 41.5931 | 51.3636 | 49.4323 | 55.7328 | 53.5571 | 51.9294 | 50.1336 | 53.3138 | 47.6682 | 53.9021 | 50.0028 | 51.2652 | 47.3128 | 53.423 | 52.2211 | 52.7025 | 55.0914 | 51.6897 | 53.129 | 54.4915 | 56.0018 | 51.9968 | 55.2067 | 54.5198 | 57.0707 | 51.0753 | 55.6971 | 53.1433 | 56.7226 | 52.7286 | 56.8089 | 52.5598 | 57.3812 | 51.8093 | 55.7266 | 57.8748 | 92.1714 | 92.2876 | 92.4669
2022-09-07 19:10 | 0:46 | 33.9418 | 33.4626 | 35.8966 | 50.0833 | 53.4538 | 50.2198 | 54.4693 | 48.3554 | 54.4656 | 51.6059 | 50.675 | 56.8435 | 48.2485 | 51.7225 | 52.25 | 51.314 | 49.9643 | 51.7297 | 51.6646 | 53.3949 | 37.1036 | 33.1414 | 41.5481 | 51.0284 | 49.3131 | 55.4928 | 53.3013 | 51.7698 | 50.0997 | 53.1818 | 47.4952 | 53.7419 | 49.855 | 51.1866 | 47.301 | 53.4618 | 52.3485 | 52.5101 | 54.9853 | 51.6401 | 53.0052 | 54.4204 | 55.6614 | 52.0025 | 55.0734 | 54.4809 | 56.95 | 50.9608 | 55.6547 | 52.9299 | 56.6779 | 52.6132 | 56.4796 | 52.387 | 57.089 | 51.7542 | 55.6154 | 57.7179 | 92.2671 | 92.4317 | 92.4917
2022-09-07 19:10 | 0:46 | 33.9597 | 33.3473 | 35.8415 | 50.137 | 53.3767 | 50.204 | 54.6259 | 48.1648 | 54.433 | 51.5237 | 50.484 | 56.6154 | 48.0991 | 51.6082 | 51.9974 | 51.1582 | 49.865 | 51.3786 | 51.5859 | 53.381 | 37.0225 | 33.0388 | 41.4539 | 50.9348 | 49.2218 | 55.6259 | 53.2972 | 51.8545 | 49.9933 | 53.0903 | 47.4428 | 53.6738 | 49.8306 | 51.0303 | 47.1616 | 53.0075 | 52.2029 | 52.3117 | 55.2112 | 51.5771 | 52.943 | 54.2466 | 55.7867 | 51.9292 | 54.952 | 54.4448 | 56.9374 | 50.8883 | 55.8878 | 52.7092 | 56.8906 | 52.4083 | 56.4368 | 52.2432 | 57.3185 | 51.5873 | 55.7536 | 57.3035 | 92.3479 | 92.5461 | 92.5475
2022-09-07 19:11 | 0:47 | 34.013 | 33.2731 | 35.7497 | 49.8332 | 53.2741 | 50.3252 | 54.626 | 47.9698 | 54.3118 | 51.4375 | 49.9397 | 56.6956 | 47.9578 | 51.4811 | 51.9855 | 50.9879 | 49.7023 | 51.3614 | 51.4274 | 53.3351 | 36.9076 | 32.9391 | 41.3643 | 50.724 | 49.1862 | 55.3491 | 53.1688 | 51.7232 | 50.0147 | 53.041 | 47.5375 | 53.4715 | 49.8078 | 50.9495 | 46.9193 | 53.2926 | 52.1084 | 52.3993 | 55.2408 | 51.4743 | 52.7521 | 54.1768 | 55.5611 | 51.8083 | 54.7792 | 54.3183 | 56.8485 | 50.8551 | 55.7356 | 52.7555 | 56.8274 | 52.1872 | 56.4099 | 52.0753 | 57.1448 | 51.4894 | 55.5436 | 57.0778 | 92.4876 | 92.6707 | 92.685
2022-09-07 19:11 | 0:47 | 33.8038 | 33.1844 | 35.6624 | 49.9062 | 53.1733 | 50.2302 | 54.4236 | 47.8091 | 54.1747 | 51.7102 | 49.915 | 56.4842 | 47.9943 | 51.3185 | 51.8864 | 50.9868 | 49.6696 | 51.3442 | 51.2971 | 53.1421 | 36.8435 | 32.847 | 41.2793 | 50.7623 | 48.983 | 55.41 | 53.129 | 51.3826 | 49.8335 | 52.979 | 47.4356 | 53.4224 | 49.5855 | 50.8792 | 46.9901 | 52.7987 | 51.8389 | 52.2389 | 55.2325 | 51.2963 | 52.6675 | 54.0747 | 55.3956 | 51.7376 | 54.5617 | 54.214 | 56.7905 | 50.7131 | 55.8253 | 52.7254 | 56.7806 | 52.1244 | 56.1082 | 51.9069 | 57.2904 | 51.2561 | 55.3963 | 57.2237 | 92.5542 | 92.7496 | 92.6809
2022-09-07 19:11 | 0:47 | 33.6422 | 33.1261 | 35.5695 | 49.8367 | 52.9328 | 50.035 | 54.2752 | 47.8455 | 54.0956 | 51.202 | 50.1041 | 56.4235 | 47.7953 | 51.1219 | 51.851 | 50.8132 | 49.5758 | 51.1589 | 51.2408 | 53.116 | 36.7407 | 32.7877 | 41.1889 | 50.6689 | 48.9335 | 55.1463 | 53.0052 | 51.1877 | 49.605 | 52.7957 | 47.2359 | 53.3432 | 49.5364 | 50.7542 | 46.8295 | 53.0412 | 51.747 | 52.1157 | 54.678 | 51.1607 | 52.4892 | 54.0776 | 55.1953 | 51.4828 | 54.5873 | 54.0297 | 56.7697 | 50.582 | 55.2423 | 52.6144 | 56.7838 | 52.0116 | 56.2454 | 51.8478 | 56.7868 | 51.3019 | 55.3321 | 57.0351 | 92.6043 | 92.8108 | 92.7498
2022-09-07 19:11 | 0:47 | 33.5077 | 33.048 | 35.4857 | 49.6196 | 52.9112 | 49.7011 | 53.7035 | 47.6979 | 53.934 | 51.0775 | 49.8995 | 56.3912 | 47.6906 | 51.0734 | 51.7531 | 50.728 | 49.4109 | 50.8574 | 51.0755 | 52.9207 | 36.687 | 32.7022 | 41.0935 | 50.5451 | 48.8165 | 55.0861 | 52.943 | 51.0851 | 49.6167 | 52.638 | 47.2109 | 53.076 | 49.2562 | 50.6924 | 46.6931 | 52.794 | 51.7743 | 52.0123 | 54.631 | 51.2621 | 52.4422 | 54.046 | 55.0921 | 51.3921 | 54.5047 | 53.855 | 56.7346 | 50.4811 | 54.9552 | 52.4596 | 55.8319 | 52.0044 | 56.0254 | 52.0418 | 56.5777 | 51.2807 | 55.0765 | 56.9731 | 92.7407 | 92.9522 | 92.8291
2022-09-07 19:11 | 0:47 | 33.5582 | 32.9699 | 35.4422 | 49.5424 | 52.8438 | 49.8874 | 54.1659 | 47.6323 | 53.8425 | 50.9545 | 49.8189 | 56.1791 | 47.641 | 51.0921 | 51.6031 | 50.6438 | 49.3374 | 51.0185 | 50.9786 | 52.881 | 36.5969 | 32.6195 | 40.9963 | 50.5185 | 48.6676 | 54.998 | 52.7521 | 51.1409 | 49.2434 | 52.5898 | 47.0389 | 53.0275 | 49.0986 | 50.5516 | 47.4548 | 52.6501 | 51.9203 | 51.862 | 54.5671 | 51.2056 | 52.4434 | 53.8641 | 55.0655 | 51.3702 | 54.4018 | 53.7076 | 56.5708 | 50.3584 | 55.1801 | 52.2349 | 56.0059 | 51.6962 | 56.1562 | 51.8846 | 56.7833 | 51.0197 | 54.9748 | 56.7494 | 92.881 | 93.0918 | 92.9029
2022-09-07 19:11 | 0:47 | 33.4863 | 32.9304 | 35.3633 | 49.5416 | 52.7147 | 49.7929 | 53.9503 | 47.6116 | 53.691 | 50.9257 | 49.6342 | 56.0085 | 47.5822 | 50.7896 | 51.5025 | 50.4057 | 49.3051 | 50.6388 | 50.8702 | 52.8848 | 36.5054 | 32.5595 | 40.9275 | 50.5151 | 48.6384 | 54.9224 | 52.6675 | 51.1312 | 49.0653 | 52.6325 | 46.7537 | 52.8943 | 49.1584 | 50.5286 | 47.1738 | 52.4249 | 51.5284 | 51.9318 | 54.4149 | 50.9365 | 52.3788 | 53.7494 | 54.9762 | 51.2933 | 54.2959 | 53.6351 | 56.4603 | 50.3419 | 54.8925 | 52.2747 | 56.0797 | 51.7857 | 56.0752 | 51.8013 | 56.5211 | 50.9084 | 54.816 | 56.8576 | 93.0016 | 93.2384 | 93.0324
2022-09-07 19:12 | 0:47 | 33.4121 | 32.8443 | 35.2567 | 49.4061 | 52.5321 | 49.6265 | 53.8549 | 47.4951 | 53.6597 | 50.8481 | 49.6524 | 56.0536 | 47.4847 | 50.9529 | 51.4057 | 50.4672 | 49.145 | 50.5568 | 50.7779 | 52.7704 | 36.4162 | 32.4832 | 40.8303 | 50.3241 | 48.4873 | 54.8276 | 52.4892 | 50.8333 | 49.1594 | 52.4078 | 46.7948 | 52.8848 | 49.0065 | 50.2924 | 46.9996 | 52.319 | 51.3558 | 51.7582 | 53.9887 | 50.7834 | 52.2577 | 53.6061 | 54.7865 | 51.1899 | 54.2203 | 53.5661 | 56.2661 | 50.1501 | 54.8101 | 52.1537 | 55.907 | 51.7557 | 55.7427 | 51.6562 | 56.498 | 50.8593 | 54.7533 | 56.586 | 93.1614 | 93.3963 | 93.0805
2022-09-07 19:12 | 0:48 | 33.5027 | 32.7675 | 35.1072 | 49.3999 | 52.537 | 49.6909 | 53.8188 | 47.4819 | 53.5759 | 50.8661 | 49.5722 | 55.8019 | 47.2293 | 50.7097 | 51.3384 | 50.302 | 49.0169 | 50.5493 | 50.6804 | 52.4508 | 36.3248 | 32.4126 | 40.7318 | 50.1334 | 48.3949 | 54.7186 | 52.4422 | 50.6333 | 49.1147 | 52.3821 | 46.5762 | 52.7272 | 49.0245 | 50.2196 | 46.7993 | 52.2196 | 51.2165 | 51.5303 | 54.144 | 50.6478 | 52.032 | 53.4578 | 54.8879 | 51.1784 | 54.0583 | 53.4972 | 56.0537 | 50.0216 | 54.7892 | 51.9541 | 56.1238 | 51.6125 | 55.4235 | 51.3496 | 56.4719 | 50.8169 | 54.7239 | 56.3042 | 93.2905 | 93.5537 | 93.1415
2022-09-07 19:12 | 0:48 | 33.5904 | 32.7061 | 35.1253 | 49.21 | 52.4118 | 49.5467 | 53.4613 | 47.3056 | 53.4939 | 50.4477 | 49.57 | 55.7561 | 47.2129 | 50.5656 | 51.1068 | 50.2104 | 48.9582 | 50.1326 | 50.6207 | 52.5484 | 36.2519 | 32.3192 | 40.6145 | 50.1386 | 48.2576 | 54.5731 | 52.4434 | 50.4412 | 49.0037 | 52.1527 | 46.5172 | 52.6062 | 48.8302 | 50.18 | 46.8633 | 51.9569 | 51.3393 | 51.5793 | 54.088 | 50.6081 | 51.9311 | 53.4387 | 54.6076 | 50.9628 | 53.9302 | 53.3808 | 55.9338 | 50.0651 | 54.6709 | 51.8933 | 55.6356 | 51.416 | 55.3255 | 51.3164 | 56.3128 | 50.5382 | 54.4648 | 56.3599 | 93.4185 | 93.7197 | 93.2966
2022-09-07 19:12 | 0:48 | 33.5119 | 32.67 | 35.1106 | 49.1324 | 52.3111 | 49.4471 | 53.4511 | 47.2351 | 53.3117 | 50.5075 | 49.6741 | 55.6495 | 47.1051 | 50.585 | 51.0165 | 50.1647 | 48.8529 | 50.2697 | 50.4713 | 52.399 | 36.1758 | 32.2734 | 40.5608 | 49.9774 | 48.1964 | 54.2795 | 52.3788 | 50.1669 | 48.8665 | 52.0455 | 46.347 | 52.562 | 48.5876 | 50.2112 | 46.7776 | 52.1053 | 51.2714 | 51.3831 | 54.0656 | 50.5728 | 51.8825 | 53.2835 | 54.6379 | 51.0424 | 53.8643 | 53.32 | 55.7388 | 50.0137 | 54.6896 | 51.6728 | 55.7766 | 51.3982 | 55.3445 | 51.2012 | 56.1434 | 50.39 | 54.3595 | 56.4476 | 93.5633 | 93.8525 | 93.3984
2022-09-07 19:12 | 0:48 | 33.4615 | 32.5849 | 35.0118 | 48.9912 | 52.2197 | 49.2204 | 53.4892 | 47.1275 | 53.2422 | 50.3117 | 49.4318 | 55.4859 | 46.8606 | 50.3147 | 51.0042 | 50.016 | 48.7867 | 50.0695 | 50.3229 | 52.2103 | 36.1455 | 32.2144 | 40.5396 | 49.9372 | 48.0534 | 54.3813 | 52.2577 | 50.3248 | 48.7662 | 52.0058 | 46.1599 | 52.4486 | 48.6539 | 49.8837 | 46.6686 | 51.884 | 50.8793 | 51.1221 | 53.9742 | 50.388 | 51.7214 | 53.2537 | 54.4856 | 50.7328 | 53.6821 | 53.2338 | 55.7612 | 49.869 | 54.6086 | 51.5095 | 55.7312 | 51.2921 | 55.3518 | 51.2426 | 56.3052 | 50.5768 | 54.3465 | 56.3687 | 93.6867 | 93.9723 | 93.4405
2022-09-07 19:12 | 0:48 | 33.3628 | 32.5306 | 34.9948 | 48.6154 | 52.1022 | 49.009 | 53.2117 | 47.1415 | 53.1753 | 50.2726 | 49.3709 | 55.5382 | 46.8453 | 50.3043 | 50.8777 | 49.9477 | 48.6831 | 49.9642 | 50.2125 | 52.0658 | 36.048 | 32.118 | 40.4635 | 49.6267 | 47.9895 | 54.4213 | 52.032 | 50.0686 | 48.626 | 51.9549 | 46.1914 | 52.3166 | 48.4612 | 49.825 | 46.3518 | 51.8725 | 50.9684 | 51.0883 | 53.8331 | 50.3795 | 51.5987 | 53.0662 | 54.5358 | 50.7662 | 53.746 | 53.1241 | 55.7235 | 49.8093 | 54.5059 | 51.3787 | 55.6674 | 51.1678 | 55.1223 | 51.1051 | 55.7257 | 50.4451 | 54.3769 | 56.0862 | 93.8349 | 94.1624 | 93.5832
2022-09-07 19:13 | 0:49 | 33.2587 | 32.4638 | 34.9014 | 48.6689 | 51.9808 | 48.9243 | 53.1573 | 47.065 | 53.1133 | 50.4125 | 49.1263 | 55.2936 | 46.8324 | 50.4537 | 50.9601 | 49.8474 | 48.5538 | 50.1714 | 50.1635 | 52.0798 | 35.9793 | 32.0638 | 40.352 | 49.4668 | 47.9242 | 54.2924 | 51.9311 | 49.8372 | 48.6242 | 51.8105 | 46.1163 | 52.2545 | 48.4127 | 49.6547 | 45.9051 | 51.8791 | 50.7798 | 51.0807 | 53.891 | 50.2221 | 51.4663 | 52.9604 | 54.4002 | 50.6091 | 53.4578 | 53.007 | 55.5846 | 49.6406 | 54.4024 | 51.511 | 55.4075 | 50.7988 | 55.0669 | 50.9052 | 55.6689 | 50.2525 | 54.2705 | 55.9834 | 93.9511 | 94.3211 | 93.6105
2022-09-07 19:13 | 0:49 | 33.2104 | 32.391 | 34.8664 | 48.6408 | 52.0176 | 48.7374 | 53.0005 | 46.8981 | 53.0432 | 50.2569 | 49.3431 | 55.2231 | 46.7338 | 50.3043 | 50.7585 | 49.7538 | 48.4797 | 50.04 | 49.9196 | 52.0709 | 35.9504 | 31.9869 | 40.2871 | 49.4158 | 47.8351 | 54.0757 | 51.8825 | 50.0111 | 48.6243 | 51.626 | 46.1421 | 52.0922 | 48.3395 | 49.6135 | 45.9025 | 51.8236 | 50.8178 | 51.0053 | 53.715 | 50.1681 | 51.3361 | 52.8969 | 54.2111 | 50.5171 | 53.3493 | 52.9069 | 55.4651 | 49.5007 | 54.0865 | 51.3961 | 55.3828 | 50.8617 | 54.9361 | 50.727 | 55.8152 | 50.1078 | 53.9613 | 55.8516 | 94.1129 | 94.482 | 93.7771
2022-09-07 19:13 | 0:49 | 33.1795 | 32.3432 | 34.8006 | 48.578 | 51.9408 | 48.6504 | 53.1241 | 46.8592 | 52.9251 | 50.0768 | 49.0634 | 55.1796 | 46.7448 | 50.2524 | 50.5699 | 49.6643 | 48.4241 | 50.0297 | 49.8404 | 51.7443 | 35.8736 | 31.9313 | 40.2074 | 49.4695 | 47.7182 | 53.7475 | 51.7214 | 50.1547 | 48.5237 | 51.6423 | 46.0729 | 52.0528 | 48.0688 | 49.5109 | 45.7196 | 51.8417 | 50.8458 | 50.8291 | 53.6368 | 50.1214 | 51.3193 | 52.7987 | 54.068 | 50.3187 | 53.289 | 52.7254 | 55.5053 | 49.3941 | 53.7832 | 51.265 | 55.5802 | 50.7294 | 55.1312 | 50.5797 | 55.5787 | 49.937 | 53.861 | 55.9972 | 94.289 | 94.6626 | 93.9134
2022-09-07 19:13 | 0:49 | 33.1617 | 32.3126 | 34.7471 | 48.6128 | 51.7372 | 48.8521 | 52.9739 | 46.696 | 52.8365 | 50.0188 | 48.7841 | 54.9878 | 46.6758 | 49.9739 | 50.5677 | 49.5106 | 48.3436 | 49.7683 | 49.8301 | 51.6791 | 35.8162 | 31.832 | 40.13 | 49.3677 | 47.6091 | 53.7027 | 51.5987 | 50.0651 | 48.3514 | 51.5939 | 45.8911 | 51.9274 | 48.1684 | 49.4784 | 45.9387 | 51.7559 | 50.7335 | 50.7865 | 53.4519 | 49.9284 | 51.1087 | 52.6071 | 54.0091 | 50.2607 | 53.3134 | 52.5889 | 55.4129 | 49.3685 | 53.5468 | 51.1151 | 55.3667 | 50.6944 | 55.0474 | 50.4999 | 55.4294 | 49.7932 | 53.769 | 55.6449 | 94.4723 | 94.8508 | 94.0226
2022-09-07 19:13 | 0:49 | 33.1369 | 32.2056 | 34.6691 | 48.2674 | 51.7488 | 48.6109 | 52.6909 | 46.5624 | 52.6955 | 49.8655 | 48.8195 | 55.0761 | 46.3735 | 49.9516 | 50.2809 | 49.4098 | 48.1668 | 49.737 | 49.6883 | 51.6743 | 35.7494 | 31.7863 | 40.029 | 49.2966 | 47.5073 | 53.8388 | 51.4663 | 50.0588 | 48.3422 | 51.4797 | 45.8085 | 51.7326 | 48.1509 | 49.3714 | 45.9979 | 51.4761 | 50.345 | 50.7629 | 53.4 | 49.8643 | 51.0818 | 52.5735 | 53.88 | 50.085 | 53.0707 | 52.5167 | 55.167 | 49.2113 | 53.5535 | 51.0276 | 55.2579 | 50.5745 | 54.8239 | 50.4175 | 55.2469 | 49.8392 | 53.7796 | 55.7586 | 94.6008 | 95.0102 | 94.1418
2022-09-07 19:13 | 0:49 | 33.0166 | 32.1373 | 34.5847 | 48.2231 | 51.6447 | 48.5688 | 52.5764 | 46.5992 | 52.5712 | 49.7663 | 48.7487 | 54.8238 | 46.4388 | 49.5588 | 50.1747 | 49.3134 | 48.1479 | 49.4791 | 49.7013 | 51.9041 | 35.7179 | 31.6977 | 39.9894 | 49.2088 | 47.3864 | 53.7109 | 51.3361 | 49.7328 | 48.2295 | 51.2192 | 45.8215 | 51.5668 | 48.115 | 49.2966 | 45.9007 | 51.3305 | 50.3297 | 50.6022 | 53.1276 | 49.6581 | 51.0422 | 52.3583 | 53.8171 | 50.0943 | 52.8874 | 52.4372 | 55.1076 | 49.0931 | 53.7062 | 50.9113 | 54.8086 | 50.4152 | 54.8883 | 50.3884 | 55.187 | 49.7316 | 53.4725 | 55.6149 | 94.7653 | 95.1939 | 94.2409
2022-09-07 19:14 | 0:50 | 32.9113 | 32.0987 | 34.5421 | 48.3168 | 51.5357 | 48.4577 | 52.6796 | 46.446 | 52.6152 | 49.5425 | 48.5418 | 54.6843 | 46.3352 | 49.6629 | 50.164 | 49.2844 | 48.0259 | 49.4265 | 49.5787 | 51.4339 | 35.682 | 31.6704 | 39.9494 | 49.2099 | 47.3309 | 53.7026 | 51.3193 | 50.0321 | 48.1039 | 51.2356 | 45.6384 | 51.521 | 48.0821 | 49.1327 | 45.8965 | 51.2615 | 50.0149 | 50.4075 | 52.9618 | 49.5924 | 50.9354 | 52.3217 | 53.6626 | 49.9314 | 52.9992 | 52.2737 | 54.9032 | 48.9771 | 53.4677 | 50.7901 | 54.427 | 50.3065 | 54.4151 | 50.223 | 55.1593 | 49.6647 | 53.3402 | 55.4926 | 94.8825 | 95.3431 | 94.2982
2022-09-07 19:14 | 0:50 | 32.8191 | 32.0027 | 34.4564 | 48.325 | 51.4381 | 48.5777 | 52.6191 | 46.27 | 52.3924 | 49.6602 | 48.3757 | 54.8144 | 46.1177 | 49.6446 | 50.1265 | 49.1518 | 47.8914 | 49.4667 | 49.4619 | 51.3254 | 35.6312 | 31.5886 | 39.8874 | 49.0257 | 47.2801 | 53.6802 | 51.1087 | 49.6406 | 48.1409 | 51.1172 | 45.5762 | 51.5211 | 47.8038 | 48.973 | 45.6688 | 51.1004 | 49.9894 | 50.3359 | 52.8799 | 49.4754 | 50.8414 | 52.2346 | 53.4569 | 49.7484 | 52.7136 | 52.1558 | 54.8276 | 48.8953 | 53.4126 | 50.5875 | 54.4883 | 50.3531 | 54.3056 | 50.2664 | 55.0717 | 49.5853 | 53.3434 | 55.2574 | 95.0065 | 95.4454 | 94.4391
2022-09-07 19:14 | 0:50 | 32.7522 | 31.9835 | 34.3587 | 48.1235 | 51.3362 | 48.2888 | 52.4681 | 46.2195 | 52.3178 | 49.5993 | 48.6578 | 54.6843 | 46.0797 | 49.4571 | 50.0852 | 49.0028 | 47.9173 | 49.3451 | 49.3643 | 51.2672 | 35.5706 | 31.5209 | 39.8325 | 49.0769 | 47.1523 | 53.38 | 51.0818 | 49.5542 | 47.8055 | 50.9908 | 45.4982 | 51.3203 | 47.7033 | 49.1258 | 45.6568 | 51.1414 | 49.8148 | 50.3783 | 52.7035 | 49.3086 | 50.7163 | 52.1401 | 53.4663 | 49.647 | 52.7811 | 52.1523 | 54.8317 | 48.7475 | 53.0207 | 50.6957 | 54.5278 | 50.4538 | 54.3007 | 50.1377 | 54.9141 | 49.4482 | 53.1246 | 55.2325 | 95.1693 | 95.5565 | 94.6031
2022-09-07 19:14 | 0:50 | 32.7231 | 31.9062 | 34.3455 | 47.9558 | 51.2951 | 48.1015 | 52.3458 | 46.1751 | 52.2591 | 49.2262 | 48.2723 | 54.493 | 46.0687 | 49.3051 | 49.8729 | 48.9315 | 47.7333 | 49.4251 | 49.2709 | 51.2352 | 35.504 | 31.4434 | 39.7274 | 48.8302 | 47.0468 | 53.3256 | 51.0422 | 49.4538 | 47.7147 | 50.9269 | 45.245 | 51.322 | 47.4942 | 48.9228 | 45.7328 | 50.7807 | 49.9025 | 50.083 | 52.7949 | 49.3361 | 50.7343 | 52.0163 | 53.3164 | 49.5704 | 52.8283 | 52.0134 | 54.7729 | 48.6641 | 53.163 | 50.4909 | 54.4501 | 50.2235 | 54.2579 | 50.149 | 54.55 | 49.3644 | 53.0086 | 55.0118 | 95.1372 | 95.6261 | 94.5738
2022-09-07 19:14 | 0:50 | 32.571 | 31.8237 | 34.2265 | 47.9556 | 51.0582 | 48.102 | 52.2697 | 46.0756 | 52.1444 | 49.2527 | 48.2132 | 54.3147 | 45.9109 | 49.3623 | 49.8451 | 48.8771 | 47.613 | 49.333 | 49.2301 | 51.1978 | 35.456 | 31.3759 | 39.6704 | 48.7628 | 46.9541 | 53.339 | 50.9354 | 49.2011 | 47.5582 | 50.7743 | 45.3135 | 51.1347 | 47.3664 | 48.9127 | 45.5361 | 50.9 | 49.7045 | 50.0786 | 52.7853 | 49.1653 | 50.5549 | 51.9293 | 53.3226 | 49.5772 | 52.6234 | 51.8629 | 54.4782 | 48.6441 | 53.2737 | 50.3906 | 53.8913 | 50.0973 | 54.0911 | 50.0161 | 54.5148 | 49.2926 | 52.9335 | 54.9986 | 95.0692 | 95.6012 | 94.4762
2022-09-07 19:14 | 0:50 | 32.4218 | 31.78 | 34.1393 | 47.9469 | 51.036 | 48.0965 | 52.2806 | 45.8617 | 52.0211 | 49.071 | 47.9634 | 54.2063 | 45.7385 | 49.0484 | 49.723 | 48.7948 | 47.548 | 49.0494 | 49.1187 | 50.9395 | 35.4047 | 31.3047 | 39.6184 | 48.8038 | 46.8944 | 53.2003 | 50.8414 | 49.1056 | 47.6224 | 50.7802 | 45.2815 | 51.1219 | 47.3734 | 48.7824 | 45.5491 | 50.9152 | 49.7034 | 50.1459 | 52.5831 | 49.2066 | 50.4834 | 51.7296 | 52.9345 | 49.3538 | 52.426 | 51.7593 | 54.3419 | 48.4903 | 53.1942 | 50.2293 | 53.8527 | 50.0082 | 53.9702 | 49.8153 | 54.3087 | 49.2872 | 53.0094 | 54.7399 | 94.8726 | 95.3875 | 94.2826
2022-09-07 19:15 | 0:50 | 32.2599 | 31.6961 | 34.0497 | 47.6792 | 50.9689 | 48.1119 | 52.0011 | 45.8357 | 51.9265 | 49.2184 | 48.2416 | 54.1779 | 45.6722 | 49.0142 | 49.518 | 48.7129 | 47.5427 | 48.8705 | 48.9119 | 50.8156 | 35.3313 | 31.2359 | 39.552 | 48.537 | 46.7412 | 52.9421 | 50.7163 | 49.5052 | 47.3927 | 50.7011 | 45.1101 | 51.0692 | 47.3352 | 48.6447 | 45.5083 | 50.7208 | 49.8576 | 49.8856 | 52.7985 | 49.2242 | 50.3209 | 51.725 | 52.9563 | 49.4053 | 52.4448 | 51.7122 | 54.3593 | 48.4766 | 52.905 | 50.0729 | 54.0421 | 49.8892 | 54.045 | 49.5828 | 54.6751 | 49.0302 | 52.9986 | 54.5544 | 94.799 | 95.1789 | 94.2344
2022-09-07 19:15 | 0:51 | 32.1284 | 31.6199 | 33.9647 | 47.6636 | 50.8951 | 47.8931 | 52.0975 | 45.7767 | 51.8561 | 49.1954 | 47.8866 | 54.0243 | 45.5917 | 49.2032 | 49.4958 | 48.6144 | 47.424 | 48.7773 | 48.9396 | 50.8198 | 35.2501 | 31.1594 | 39.484 | 48.5167 | 46.5978 | 52.7674 | 50.7343 | 49.0294 | 47.442 | 50.4857 | 45.046 | 50.9904 | 47.1601 | 48.5533 | 45.1813 | 50.5397 | 49.5858 | 49.7727 | 52.622 | 48.933 | 50.1778 | 51.5747 | 53.0439 | 49.3255 | 52.309 | 51.6704 | 54.124 | 48.3958 | 53.2879 | 49.8941 | 53.965 | 49.7964 | 53.8287 | 49.6129 | 54.4451 | 48.9012 | 52.8155 | 54.6142 | 94.5127 | 94.9045 | 94.0157
2022-09-07 19:15 | 0:51 | 32.0158 | 31.5601 | 33.8615 | 47.7142 | 50.9067 | 47.6429 | 51.9315 | 45.6067 | 51.7399 | 48.9988 | 47.9448 | 53.9249 | 45.4772 | 48.9397 | 49.547 | 48.5437 | 47.2844 | 48.8322 | 48.7415 | 50.8031 | 35.1851 | 31.1182 | 39.4228 | 48.4493 | 46.5936 | 52.8634 | 50.5549 | 49.1017 | 47.3941 | 50.3737 | 45.0134 | 50.8555 | 47.1103 | 48.4312 | 45.1831 | 50.6689 | 49.3207 | 49.7424 | 52.3525 | 48.8301 | 50.1098 | 51.5153 | 52.9147 | 49.2996 | 52.1554 | 51.5327 | 54.2644 | 48.2863 | 53.184 | 49.9001 | 53.9212 | 49.8707 | 53.6455 | 49.6752 | 54.4679 | 48.858 | 52.6228 | 54.5797 | 94.3559 | 94.7151 | 93.8929
2022-09-07 19:15 | 0:51 | 31.9783 | 31.4499 | 33.7049 | 47.3137 | 50.649 | 47.4106 | 51.8278 | 45.6949 | 51.7016 | 48.6792 | 48.3096 | 53.8863 | 45.4969 | 48.9032 | 49.4719 | 48.4053 | 47.2447 | 48.5658 | 48.8106 | 50.7026 | 35.1124 | 31.0082 | 39.3537 | 48.2995 | 46.4665 | 52.7608 | 50.4834 | 48.7106 | 47.2824 | 50.3854 | 44.7792 | 50.7536 | 46.8668 | 48.3193 | 45.1304 | 50.658 | 49.4005 | 49.5397 | 52.3133 | 48.7569 | 50.0209 | 51.4775 | 52.71 | 48.8586 | 52.2101 | 51.3591 | 54.054 | 48.1987 | 52.9131 | 49.8196 | 53.9339 | 49.6386 | 53.6095 | 49.4662 | 54.2538 | 48.7367 | 52.466 | 54.423 | 94.2732 | 94.6158 | 93.9215
2022-09-07 19:15 | 0:51 | 32.024 | 31.3898 | 33.7152 | 47.4888 | 50.609 | 47.6963 | 51.8946 | 45.5211 | 51.5395 | 48.9012 | 47.7142 | 53.8193 | 45.358 | 48.9039 | 49.2711 | 48.2495 | 47.1165 | 48.4907 | 48.7587 | 50.5887 | 35.0693 | 30.9563 | 39.2265 | 48.2375 | 46.392 | 52.7785 | 50.3209 | 48.6672 | 47.1725 | 50.2618 | 44.7096 | 50.671 | 46.8493 | 48.2749 | 45.0053 | 50.4679 | 49.2271 | 49.3951 | 52.3088 | 48.7296 | 50.0464 | 51.3235 | 52.6414 | 49.0802 | 52.0896 | 51.2993 | 54.0061 | 48.0662 | 52.7871 | 49.7769 | 53.8051 | 49.5061 | 53.3609 | 49.1886 | 54.3216 | 48.6532 | 52.3542 | 54.1815 | 94.2041 | 94.5169 | 93.9227
2022-09-07 19:15 | 0:51 | 31.9477 | 31.3262 | 33.6017 | 47.3587 | 50.5628 | 47.6569 | 51.6271 | 45.4786 | 51.4792 | 48.5335 | 47.8428 | 53.7177 | 45.3374 | 48.8088 | 49.1018 | 48.1802 | 47.0327 | 48.3344 | 48.6036 | 50.6217 | 35.0209 | 30.909 | 39.2424 | 48.1391 | 46.2641 | 52.6269 | 50.1778 | 48.732 | 46.9504 | 50.2082 | 44.6236 | 50.4944 | 46.6336 | 48.1844 | 44.9785 | 50.2532 | 49.2723 | 49.3227 | 52.1241 | 48.6636 | 49.9935 | 51.3333 | 52.5573 | 48.9076 | 51.8656 | 51.2134 | 53.7402 | 47.9864 | 52.4312 | 49.6473 | 53.8667 | 49.3776 | 53.3957 | 49.1947 | 53.9644 | 48.4798 | 52.3409 | 54.1661 | 94.1534 | 94.4735 | 93.9135
2022-09-07 19:16 | 0:52 | 31.5813 | 31.2364 | 33.5274 | 47.1878 | 50.5598 | 47.6741 | 51.5973 | 45.3971 | 51.3486 | 48.5665 | 47.5538 | 53.6242 | 45.1859 | 48.4878 | 48.9753 | 48.0851 | 46.9006 | 48.3136 | 48.4713 | 50.4542 | 34.9828 | 30.8048 | 39.2252 | 48.0459 | 46.1931 | 52.3098 | 50.1098 | 48.382 | 46.9112 | 49.9305 | 44.721 | 50.3774 | 46.6208 | 48.021 | 44.8414 | 50.3447 | 49.1434 | 49.3628 | 51.9569 | 48.5828 | 49.8802 | 51.1755 | 52.4945 | 48.7575 | 51.9805 | 51.0864 | 53.6841 | 47.9464 | 52.3541 | 49.6009 | 53.5868 | 49.2505 | 53.2019 | 49.0716 | 54.0161 | 48.4247 | 52.2655 | 54.1823 | 94.0269 | 94.3911 | 93.7653
2022-09-07 19:16 | 0:52 | 31.3925 | 31.1381 | 33.4485 | 47.0742 | 50.4644 | 47.4266 | 51.471 | 45.2992 | 51.2709 | 48.4909 | 47.5425 | 53.5806 | 45.0308 | 48.5693 | 48.7989 | 48.0108 | 46.799 | 48.4883 | 48.2266 | 50.2785 | 34.9225 | 30.7072 | 39.1707 | 47.9011 | 46.1165 | 52.2391 | 50.0209 | 48.3912 | 46.8898 | 49.9124 | 44.5603 | 50.2975 | 46.6081 | 47.954 | 45.0356 | 50.117 | 49.2057 | 49.2225 | 51.9565 | 48.5912 | 49.7387 | 51.0568 | 52.4372 | 48.6305 | 51.9352 | 50.9871 | 53.7893 | 47.7591 | 52.1505 | 49.5243 | 52.8364 | 49.1432 | 53.2366 | 49.1025 | 53.923 | 48.3588 | 52.0489 | 53.9664 | 93.9816 | 94.3111 | 93.7554
2022-09-07 19:16 | 0:52 | 31.3443 | 31.0495 | 33.3533 | 46.7989 | 50.3056 | 47.3627 | 51.4378 | 45.2537 | 51.2405 | 48.1476 | 47.5647 | 53.5575 | 45.0335 | 48.3996 | 48.7396 | 47.8071 | 46.7857 | 48.0399 | 48.1136 | 50.1475 | 34.8621 | 30.6512 | 39.1589 | 47.9355 | 46.0209 | 52.2849 | 50.0464 | 48.353 | 46.7657 | 49.8414 | 44.3537 | 50.1969 | 46.5772 | 47.9333 | 45.0349 | 50.0042 | 49.2487 | 49.116 | 51.954 | 48.5812 | 49.6807 | 50.9871 | 52.272 | 48.5526 | 51.8871 | 50.8623 | 53.702 | 47.6679 | 51.862 | 49.3079 | 52.8415 | 49.1617 | 53.0468 | 49.0321 | 53.571 | 48.3001 | 51.9641 | 53.7994 | 93.9678 | 94.2641 | 93.7446
2022-09-07 19:16 | 0:52 | 31.0768 | 31.0019 | 33.2629 | 46.7097 | 50.319 | 47.2002 | 51.2542 | 45.1575 | 51.1453 | 48.2106 | 47.6477 | 53.4221 | 44.8998 | 48.3802 | 48.717 | 47.8404 | 46.6582 | 47.883 | 48.0833 | 49.9549 | 34.8082 | 30.572 | 39.0273 | 47.7675 | 45.9544 | 52.193 | 49.9935 | 48.2792 | 46.7076 | 49.6694 | 44.3552 | 50.1215 | 46.5283 | 47.7252 | 44.7898 | 49.762 | 49.0436 | 49.0049 | 51.8291 | 48.4012 | 49.4733 | 51.0118 | 52.2196 | 48.3933 | 51.6734 | 50.8286 | 53.4441 | 47.6158 | 52.0017 | 49.2619 | 52.6432 | 48.9671 | 52.9443 | 48.8067 | 53.7079 | 48.2572 | 51.9141 | 53.7099 | 93.8921 | 94.162 | 93.721
2022-09-07 19:16 | 0:52 | 30.701 | 30.914 | 33.1409 | 46.6938 | 50.2929 | 46.8666 | 51.1947 | 44.9805 | 51.0724 | 47.986 | 47.4578 | 53.2898 | 44.7427 | 48.2961 | 48.6414 | 47.7661 | 46.5627 | 47.9544 | 47.9728 | 49.9584 | 34.7139 | 30.5178 | 38.9675 | 47.7001 | 45.848 | 52.0613 | 49.8802 | 48.3758 | 46.6016 | 49.6605 | 44.2615 | 49.9213 | 46.3775 | 47.6534 | 44.5526 | 49.7902 | 48.7756 | 48.982 | 51.5126 | 48.2005 | 49.348 | 50.7997 | 52.1146 | 48.3763 | 51.4531 | 50.7418 | 53.2182 | 47.5685 | 51.9936 | 49.2709 | 52.7614 | 48.9308 | 52.6102 | 48.8801 | 53.6985 | 48.0999 | 51.9572 | 53.4802 | 93.8761 | 94.1339 | 93.7118
2022-09-07 19:16 | 0:52 | 30.8842 | 30.7993 | 33.0573 | 46.6834 | 50.1437 | 46.9709 | 51.2422 | 44.8915 | 51.0248 | 48.0125 | 47.0655 | 53.2602 | 44.7285 | 48.18 | 48.4831 | 47.6384 | 46.5221 | 48.0129 | 47.8272 | 49.9021 | 34.6469 | 30.4398 | 38.8527 | 47.543 | 45.7515 | 51.9947 | 49.7387 | 48.1177 | 46.464 | 49.5987 | 44.305 | 49.9931 | 46.2129 | 47.6384 | 44.4273 | 49.7472 | 48.6986 | 49.0258 | 51.4583 | 48.1543 | 49.2615 | 50.6915 | 52.1925 | 48.4092 | 51.5064 | 50.597 | 53.2189 | 47.481 | 52.2319 | 49.1365 | 52.9448 | 48.7305 | 52.6718 | 48.5995 | 53.445 | 47.9615 | 51.7226 | 53.498 | 93.7746 | 94.0674 | 93.5659
2022-09-07 19:17 | 0:52 | 30.853 | 30.6995 | 33.0181 | 46.6649 | 50.0243 | 46.7542 | 51.0183 | 44.7856 | 50.8917 | 48.0233 | 47.0032 | 52.9881 | 44.5662 | 48.0108 | 48.4725 | 47.5724 | 46.4055 | 48.0002 | 47.7045 | 49.6199 | 34.5448 | 30.3277 | 38.7639 | 47.5715 | 45.6055 | 51.779 | 49.6807 | 47.7859 | 46.2991 | 49.5535 | 44.1675 | 49.8682 | 46.1299 | 47.6104 | 44.2423 | 49.7204 | 48.4497 | 48.8586 | 51.4963 | 47.9527 | 49.1787 | 50.7478 | 51.7923 | 48.1352 | 51.3079 | 50.506 | 53.1375 | 47.2209 | 51.8599 | 49.0942 | 52.8314 | 48.6971 | 52.5514 | 48.5645 | 53.2314 | 47.9569 | 51.8074 | 53.5266 | 93.6924 | 93.9621 | 93.582
2022-09-07 19:17 | 0:53 | 31.1374 | 30.6043 | 32.9583 | 46.5219 | 49.928 | 46.711 | 51.0007 | 44.6865 | 50.8397 | 47.966 | 47.0315 | 53.003 | 44.5977 | 47.9607 | 48.2501 | 47.4706 | 46.3195 | 48.1106 | 47.7937 | 49.677 | 34.437 | 30.2589 | 38.6705 | 47.4049 | 45.552 | 51.7354 | 49.4733 | 48.006 | 46.241 | 49.486 | 43.9392 | 49.789 | 46.0194 | 47.4881 | 44.5242 | 49.4499 | 48.6115 | 48.803 | 50.9223 | 47.9841 | 48.9834 | 50.5375 | 51.7235 | 48.1395 | 51.1668 | 50.3692 | 52.9829 | 47.2072 | 51.7727 | 48.9946 | 52.803 | 48.7138 | 52.492 | 48.426 | 53.2286 | 47.9285 | 51.7071 | 53.4808 | 93.7118 | 93.9112 | 93.6498
2022-09-07 19:17 | 0:53 | 30.9703 | 30.5375 | 32.8539 | 46.4345 | 49.7989 | 46.7958 | 50.9612 | 44.6701 | 50.6688 | 47.7573 | 47.0623 | 52.8763 | 44.3855 | 47.8126 | 48.2338 | 47.4158 | 46.2668 | 47.6334 | 47.7206 | 49.669 | 34.3851 | 30.1653 | 38.5947 | 47.3028 | 45.4456 | 51.5617 | 49.348 | 47.8993 | 46.2161 | 49.2431 | 43.8424 | 49.6499 | 45.8785 | 47.3688 | 44.2197 | 49.3236 | 48.3463 | 48.5677 | 50.8775 | 47.7732 | 49.0712 | 50.4731 | 51.5627 | 47.9439 | 51.0686 | 50.2903 | 52.8609 | 47.1728 | 51.7605 | 48.7755 | 52.6205 | 48.6958 | 52.4195 | 48.2791 | 53.1713 | 47.6597 | 51.4722 | 53.2991 | 93.6989 | 93.8372 | 93.6443
2022-09-07 19:17 | 0:53 | 30.392 | 30.4414 | 32.7254 | 46.3912 | 49.7669 | 46.4311 | 50.7185 | 44.6368 | 50.6778 | 47.6756 | 47.1615 | 52.785 | 44.308 | 47.9857 | 48.4135 | 47.2877 | 46.1482 | 47.6914 | 47.5637 | 49.5842 | 34.2904 | 30.097 | 38.5101 | 47.2021 | 45.3273 | 51.812 | 49.2615 | 47.7167 | 46.1182 | 49.2529 | 43.7991 | 49.5312 | 45.9892 | 47.296 | 44.0084 | 49.1333 | 48.1356 | 48.5505 | 51.0759 | 47.6841 | 49.0529 | 50.3932 | 51.5324 | 47.8751 | 50.9468 | 50.2526 | 52.9624 | 47.0784 | 51.697 | 48.7296 | 52.2002 | 48.4475 | 52.2175 | 48.203 | 53.0688 | 47.6002 | 51.1885 | 53.1979 | 93.5467 | 93.7642 | 93.4263
2022-09-07 19:17 | 0:53 | 30.5555 | 30.3803 | 32.6319 | 46.1761 | 49.6271 | 46.4347 | 50.5987 | 44.5353 | 50.5703 | 47.8381 | 46.9588 | 52.6527 | 44.3019 | 47.8307 | 48.1749 | 47.2195 | 46.1157 | 47.7912 | 47.5289 | 49.5401 | 34.2384 | 30.0409 | 38.4734 | 47.0722 | 45.3039 | 51.5517 | 49.1787 | 47.6769 | 46.0671 | 49.0663 | 43.7881 | 49.4906 | 46.0137 | 47.1639 | 44.0099 | 49.0671 | 48.1387 | 48.4493 | 50.8856 | 47.5913 | 48.9761 | 50.3292 | 51.3683 | 47.7311 | 50.7886 | 50.0909 | 52.6893 | 46.9445 | 51.3749 | 48.7894 | 51.9788 | 48.4887 | 52.2139 | 48.1121 | 52.9943 | 47.5595 | 51.305 | 53.0137 | 93.4372 | 93.6623 | 93.3013
2022-09-07 19:17 | 0:53 | 30.1865 | 30.2977 | 32.5371 | 46.2106 | 49.5449 | 46.2197 | 50.4147 | 44.4464 | 50.5006 | 47.5591 | 46.658 | 52.4972 | 44.2054 | 47.694 | 48.1212 | 47.2105 | 45.9767 | 47.3754 | 47.4054 | 49.2182 | 34.1686 | 29.9772 | 38.4155 | 47.1649 | 45.2341 | 51.3884 | 48.9834 | 47.6199 | 45.9697 | 48.9498 | 43.8043 | 49.3474 | 45.9413 | 47.0455 | 43.8754 | 48.9222 | 48.1725 | 48.4283 | 50.4663 | 47.5571 | 48.792 | 50.1688 | 51.4368 | 47.6374 | 50.8053 | 50.0344 | 52.564 | 46.8461 | 51.5682 | 48.5562 | 52.1415 | 48.1875 | 52.1976 | 48.2047 | 52.7321 | 47.4613 | 51.2689 | 53.1045 | 93.2639 | 93.4997 | 93.2372
2022-09-07 19:18 | 0:54 | 29.8778 | 30.2337 | 32.4887 | 45.9908 | 49.4669 | 46.2394 | 50.4234 | 44.4115 | 50.3477 | 47.5397 | 46.7194 | 52.5772 | 44.1707 | 47.616 | 47.9176 | 47.0934 | 45.8822 | 47.6262 | 47.3157 | 49.4139 | 34.0909 | 29.89 | 38.2907 | 46.8841 | 45.1382 | 51.273 | 49.0712 | 47.6404 | 45.9325 | 48.8477 | 43.4857 | 49.1597 | 45.7655 | 46.9737 | 44.0088 | 48.9156 | 48.2456 | 48.2384 | 50.8392 | 47.5137 | 48.5942 | 50.061 | 51.2279 | 47.5879 | 50.7299 | 49.9703 | 52.4828 | 46.752 | 51.4134 | 48.5097 | 52.418 | 48.3021 | 52.0804 | 47.9639 | 52.5326 | 47.3499 | 51.1113 | 52.7986 | 93.1489 | 93.3809 | 93.139
2022-09-07 19:18 | 0:54 | 30.402 | 30.0868 | 32.412 | 46.01 | 49.446 | 45.9161 | 50.3109 | 44.3461 | 50.3212 | 47.2339 | 46.7456 | 52.5084 | 44.0324 | 47.4211 | 47.7973 | 46.9722 | 45.7871 | 47.509 | 47.229 | 49.2769 | 33.9999 | 29.777 | 38.2127 | 46.9304 | 45.0165 | 51.3626 | 49.0529 | 47.4555 | 45.7321 | 48.8156 | 43.4341 | 49.1663 | 45.6367 | 46.797 | 43.8966 | 48.9467 | 48.1016 | 48.0692 | 50.5326 | 47.464 | 48.4448 | 49.8071 | 51.1602 | 47.6048 | 50.6224 | 49.8957 | 52.4118 | 46.6816 | 51.3904 | 48.2479 | 52.1275 | 47.9246 | 51.9284 | 47.9185 | 52.615 | 47.2942 | 50.9867 | 52.8149 | 93.0889 | 93.2694 | 93.1342
2022-09-07 19:18 | 0:54 | 30.6056 | 30.0341 | 32.3278 | 45.9648 | 49.2644 | 46.0699 | 50.3162 | 44.1458 | 50.1887 | 47.4184 | 46.6335 | 52.3626 | 44.0666 | 47.0313 | 47.7252 | 46.8761 | 45.7082 | 47.2371 | 47.1281 | 49.4448 | 33.9084 | 29.7151 | 38.1426 | 46.7462 | 44.9247 | 51.269 | 48.9761 | 47.4202 | 45.6175 | 48.7086 | 43.3789 | 48.8464 | 45.4055 | 46.7553 | 43.7351 | 48.6554 | 47.8373 | 47.9476 | 50.4024 | 47.2608 | 48.4362 | 49.7901 | 51.1233 | 47.5799 | 50.3961 | 49.7637 | 52.4525 | 46.5938 | 51.0741 | 48.2867 | 52.1222 | 47.8331 | 51.9562 | 48.096 | 52.4357 | 47.0807 | 51.0053 | 52.6704 | 93.0876 | 93.1898 | 93.1722
2022-09-07 19:18 | 0:54 | 30.4599 | 29.9549 | 32.2256 | 45.8378 | 49.2889 | 46.2682 | 50.2888 | 44.0572 | 50.0732 | 47.2365 | 46.5061 | 52.1897 | 43.8569 | 47.1865 | 47.5902 | 46.7296 | 45.4975 | 47.126 | 47.0988 | 49.171 | 33.8539 | 29.6275 | 38.1346 | 46.5841 | 44.8726 | 50.9887 | 48.792 | 46.9239 | 45.6009 | 48.6041 | 43.1719 | 48.9273 | 45.302 | 46.6732 | 43.5644 | 48.529 | 47.9215 | 47.8839 | 50.5072 | 47.2821 | 48.3259 | 49.7304 | 50.9883 | 47.4478 | 50.3912 | 49.6075 | 52.3555 | 46.543 | 51.077 | 48.0638 | 51.8865 | 47.673 | 52.0491 | 47.7904 | 52.5887 | 46.9664 | 50.9925 | 52.6725 | 92.9315 | 93.0553 | 93.0625
2022-09-07 19:18 | 0:54 | 30.2946 | 29.8752 | 32.1214 | 45.742 | 49.1758 | 45.8128 | 50.2815 | 44.0688 | 50.0643 | 47.0043 | 46.4793 | 52.2769 | 43.7296 | 47.0934 | 47.5411 | 46.7052 | 45.5247 | 46.9701 | 46.8458 | 48.9913 | 33.7999 | 29.572 | 38.0414 | 46.6134 | 44.7553 | 50.8287 | 48.5942 | 47.065 | 45.4784 | 48.5604 | 43.0204 | 48.7404 | 45.2587 | 46.5733 | 43.5718 | 48.431 | 47.552 | 47.8322 | 50.5864 | 47.089 | 48.3233 | 49.7009 | 50.9143 | 47.3675 | 50.434 | 49.4799 | 52.2728 | 46.4404 | 51.0477 | 47.9616 | 51.8049 | 47.6737 | 51.7804 | 47.7146 | 52.7051 | 46.9695 | 50.9461 | 52.5034 | 92.8881 | 92.9271 | 92.8741
2022-09-07 19:18 | 0:54 | 30.1633 | 29.8251 | 32.054 | 45.6755 | 49.0186 | 45.8817 | 50.0997 | 43.9616 | 49.9659 | 47.0333 | 46.357 | 52.2047 | 43.726 | 46.8172 | 47.5078 | 46.6106 | 45.408 | 46.7453 | 46.8196 | 48.9708 | 33.7199 | 29.4578 | 38.012 | 46.4276 | 44.6623 | 50.8727 | 48.4448 | 47.0313 | 45.3925 | 48.4331 | 43.0653 | 48.6923 | 45.09 | 46.4996 | 43.3146 | 48.4377 | 47.5009 | 47.7166 | 50.2472 | 47.0133 | 48.2823 | 49.5961 | 50.8316 | 47.2174 | 50.26 | 49.4559 | 52.0603 | 46.364 | 51.1311 | 47.9327 | 51.4062 | 47.5494 | 51.6133 | 47.4996 | 52.1037 | 46.8518 | 50.5359 | 52.4166 | 92.6633 | 92.754 | 92.6839
2022-09-07 19:19 | 0:54 | 29.7767 | 29.7713 | 31.9967 | 45.584 | 49.0608 | 45.7358 | 49.8059 | 43.8078 | 49.906 | 46.9152 | 46.5049 | 51.9855 | 43.5572 | 46.9671 | 47.3299 | 46.4851 | 45.3004 | 46.7567 | 46.7334 | 48.9233 | 33.6758 | 29.4464 | 37.9665 | 46.4453 | 44.5822 | 50.709 | 48.4362 | 46.8042 | 45.3068 | 48.3059 | 43.0217 | 48.6198 | 45.0654 | 46.3869 | 43.3328 | 48.2486 | 47.2176 | 47.5596 | 50.1981 | 46.7984 | 48.2285 | 49.4692 | 50.8609 | 47.2468 | 50.2664 | 49.3674 | 51.9847 | 46.3022 | 50.8056 | 47.9527 | 51.6949 | 47.6255 | 51.5566 | 47.5041 | 52.1719 | 46.7078 | 50.4217 | 52.3484 | 92.5233 | 92.6327 | 92.6387
2022-09-07 19:19 | 0:55 | 29.6928 | 29.6406 | 31.9101 | 45.6414 | 48.884 | 45.4903 | 49.9471 | 43.7321 | 49.7928 | 46.893 | 46.1415 | 51.8295 | 43.4534 | 46.8216 | 47.3641 | 46.3147 | 45.227 | 46.8219 | 46.6261 | 48.6374 | 33.604 | 29.3314 | 37.9297 | 46.4034 | 44.5208 | 50.5928 | 48.3259 | 46.9053 | 45.3349 | 48.329 | 42.9498 | 48.6504 | 45.0561 | 46.3145 | 43.2955 | 48.2694 | 47.3308 | 47.5488 | 49.9266 | 46.6791 | 48.055 | 49.2647 | 50.7186 | 47.0358 | 50.0296 | 49.3004 | 51.7931 | 46.1776 | 50.8062 | 47.7585 | 50.718 | 47.5124 | 51.3843 | 47.352 | 51.7668 | 46.7416 | 50.8102 | 52.18 | 92.3812 | 92.4867 | 92.5155
2022-09-07 19:19 | 0:55 | 30.0776 | 29.6068 | 31.7949 | 45.4006 | 48.9018 | 45.7523 | 49.7619 | 43.4763 | 49.663 | 46.8157 | 45.8777 | 51.891 | 43.4191 | 46.7495 | 47.1583 | 46.3278 | 45.2252 | 46.6288 | 46.5649 | 48.4673 | 33.5253 | 29.2847 | 37.793 | 46.2092 | 44.434 | 50.5727 | 48.3233 | 46.5815 | 45.2321 | 48.1084 | 42.7808 | 48.5781 | 45.0081 | 46.2604 | 43.2127 | 48.3294 | 47.1979 | 47.4438 | 49.9966 | 46.716 | 47.9808 | 49.173 | 50.5152 | 46.9855 | 49.9286 | 49.1995 | 51.6662 | 46.1328 | 50.7851 | 47.6152 | 51.1823 | 47.2676 | 51.3758 | 47.2856 | 51.9584 | 46.635 | 50.4142 | 51.9634 | 92.1885 | 92.3254 | 92.3166
2022-09-07 19:19 | 0:55 | 29.4626 | 29.4986 | 31.7318 | 45.3029 | 48.7326 | 45.6558 | 49.696 | 43.5349 | 49.5228 | 46.4744 | 46.0299 | 51.7189 | 43.2674 | 46.6453 | 46.9788 | 46.1624 | 45.0866 | 46.5363 | 46.5053 | 48.7045 | 33.4374 | 29.1667 | 37.7261 | 46.2241 | 44.3505 | 50.618 | 48.2823 | 46.4624 | 45.03 | 48.043 | 42.8199 | 48.2348 | 44.8942 | 46.1364 | 42.9977 | 47.984 | 47.0143 | 47.4264 | 50.0017 | 46.6136 | 47.8107 | 49.1415 | 50.4039 | 46.8777 | 49.7786 | 49.1278 | 51.79 | 45.9911 | 50.4998 | 47.5237 | 50.8282 | 47.2747 | 51.0967 | 47.2606 | 51.9414 | 46.5753 | 50.1732 | 52.0166 | 91.9408 | 92.1311 | 92.2281
2022-09-07 19:19 | 0:55 | 29.7148 | 29.4174 | 31.6942 | 45.3508 | 48.6664 | 45.5153 | 49.5182 | 43.5219 | 49.509 | 46.468 | 45.8568 | 51.8204 | 43.2292 | 46.6183 | 46.8801 | 46.1476 | 45.0607 | 46.2965 | 46.4095 | 48.4548 | 33.3845 | 29.1071 | 37.7213 | 46.1607 | 44.2826 | 50.5232 | 48.2285 | 46.1519 | 44.961 | 47.9348 | 42.7534 | 48.2564 | 44.6494 | 46.0063 | 43.032 | 47.9383 | 46.9785 | 47.3791 | 49.8802 | 46.5311 | 47.7543 | 49.0714 | 50.3105 | 46.772 | 49.7963 | 49.0029 | 51.6974 | 45.9836 | 50.5572 | 47.5465 | 50.9268 | 47.0104 | 51.1816 | 47.0646 | 51.6838 | 46.4625 | 50.2852 | 51.9959 | 91.9198 | 91.9958 | 92.251
2022-09-07 19:19 | 0:55 | 29.1009 | 29.3896 | 31.6143 | 45.1373 | 48.5245 | 45.3773 | 49.4756 | 43.3468 | 49.3867 | 46.4606 | 45.8771 | 51.6947 | 43.1456 | 46.5397 | 46.7428 | 46.0245 | 44.8297 | 46.2158 | 46.2895 | 48.3855 | 33.3228 | 29.0626 | 37.6549 | 46.1262 | 44.171 | 50.3218 | 48.055 | 46.1953 | 44.8418 | 47.9025 | 42.6898 | 48.235 | 44.7129 | 45.9378 | 42.8119 | 47.8373 | 46.9346 | 47.1737 | 49.573 | 46.4347 | 47.7464 | 48.9512 | 50.3194 | 46.6975 | 49.7152 | 48.8417 | 51.5134 | 45.8013 | 50.4209 | 47.4904 | 51.0967 | 46.984 | 51.126 | 47.0766 | 51.7669 | 46.3657 | 50.1837 | 51.7886 | 91.996 | 92.1063 | 92.4083
2022-09-07 19:20 | 0:56 | 28.7397 | 29.2756 | 31.4889 | 45.2258 | 48.4463 | 45.3204 | 49.5238 | 43.3048 | 49.3727 | 46.4087 | 45.81 | 51.4319 | 43.1274 | 46.3885 | 46.8885 | 45.9415 | 44.7879 | 46.0818 | 46.258 | 48.3735 | 33.2577 | 28.9843 | 37.6073 | 45.9881 | 44.1345 | 50.432 | 47.9808 | 46.3941 | 44.8039 | 47.6999 | 42.4356 | 48.0625 | 44.5027 | 45.8206 | 42.7546 | 47.8206 | 46.7299 | 47.0761 | 49.4337 | 46.268 | 47.6216 | 48.9391 | 50.0361 | 46.5419 | 49.8048 | 48.7549 | 51.3225 | 45.7312 | 50.1494 | 47.3688 | 50.5955 | 47.0755 | 50.9145 | 47.1261 | 51.518 | 46.2601 | 49.8864 | 51.8591 | 92.0198 | 92.1436 | 92.356
2022-09-07 19:20 | 0:56 | 29.4626 | 29.1816 | 31.4718 | 45.0344 | 48.4711 | 45.1444 | 49.4745 | 43.2403 | 49.254 | 46.2745 | 45.4963 | 51.2381 | 42.9557 | 46.3918 | 46.7182 | 45.89 | 44.729 | 46.4283 | 46.134 | 48.2699 | 33.1953 | 28.8784 | 37.5635 | 45.8797 | 44.037 | 50.0657 | 47.8107 | 46.2078 | 44.5585 | 47.6523 | 42.422 | 48.1881 | 44.4364 | 45.8188 | 42.8281 | 47.948 | 46.9069 | 47.0048 | 49.5975 | 46.3207 | 47.5286 | 48.7992 | 49.9817 | 46.4981 | 49.4809 | 48.6516 | 51.134 | 45.6012 | 50.1677 | 47.1573 | 50.8646 | 47.0384 | 50.7445 | 46.9606 | 51.4242 | 46.1676 | 49.878 | 51.5629 | 92.1384 | 92.251 | 92.4292
2022-09-07 19:20 | 0:56 | 29.0571 | 29.088 | 31.363 | 44.8142 | 48.2938 | 44.9153 | 49.111 | 43.131 | 49.2215 | 46.1886 | 45.535 | 51.2356 | 42.8955 | 46.4215 | 46.7262 | 45.8235 | 44.6122 | 46.3876 | 46.049 | 48.129 | 33.0912 | 28.819 | 37.4855 | 45.7397 | 43.9608 | 50.0781 | 47.7543 | 46.044 | 44.7004 | 47.5964 | 42.1991 | 47.9997 | 44.5286 | 45.6496 | 42.7094 | 47.8413 | 46.8211 | 47.0821 | 49.3582 | 46.2939 | 47.3189 | 48.7248 | 50.0106 | 46.325 | 49.4343 | 48.5983 | 51.2395 | 45.5299 | 50.0252 | 47.1024 | 50.9284 | 46.9632 | 50.6248 | 46.8747 | 51.3308 | 46.1135 | 49.6399 | 51.6598 | 92.2285 | 92.3518 | 92.6
2022-09-07 19:20 | 0:56 | 28.8951 | 29.0515 | 31.2946 | 44.8854 | 48.2465 | 45.1144 | 49.2399 | 43.009 | 49.1645 | 46.1694 | 45.2475 | 51.265 | 42.8076 | 46.3354 | 46.493 | 45.705 | 44.5475 | 46.3695 | 45.9454 | 47.8893 | 33.0131 | 28.7423 | 37.366 | 45.7809 | 43.8584 | 50.0014 | 47.7464 | 46.1914 | 44.4644 | 47.5427 | 42.1891 | 47.857 | 44.3623 | 45.6911 | 42.6427 | 47.5688 | 46.7283 | 46.8814 | 49.343 | 46.1847 | 47.2802 | 48.5796 | 49.8734 | 46.3906 | 49.3291 | 48.5379 | 50.9151 | 45.5379 | 49.8925 | 47.0882 | 50.7777 | 46.8547 | 50.7266 | 46.7006 | 51.5367 | 46.0005 | 49.726 | 51.2204 | 92.3836 | 92.5016 | 92.6912
2022-09-07 19:20 | 0:56 | 28.531 | 28.9764 | 31.2128 | 44.7868 | 48.1495 | 44.9014 | 49.0868 | 42.9812 | 49.0924 | 46.1764 | 45.4495 | 51.2014 | 42.7506 | 46.1849 | 46.3783 | 45.6587 | 44.4455 | 46.0654 | 45.8768 | 47.9828 | 32.9554 | 28.6687 | 37.2518 | 45.6444 | 43.8098 | 49.7317 | 47.6216 | 46.064 | 44.4618 | 47.4579 | 42.107 | 47.8354 | 44.312 | 45.4733 | 42.4577 | 47.5744 | 46.4642 | 46.8151 | 49.2088 | 46.079 | 47.2028 | 48.557 | 49.8304 | 46.3851 | 49.267 | 48.4135 | 51.0428 | 45.4465 | 49.7773 | 46.9376 | 50.4159 | 46.6744 | 50.5068 | 46.6022 | 51.2033 | 45.922 | 49.5587 | 51.4141 | 92.4929 | 92.6282 | 92.6749
2022-09-07 19:20 | 0:56 | 28.9395 | 28.8732 | 31.1539 | 44.6921 | 48.1113 | 44.8288 | 48.9124 | 42.8821 | 48.9733 | 46.0292 | 45.3594 | 51.0386 | 42.6692 | 46.0847 | 46.3336 | 45.558 | 44.3331 | 45.8636 | 45.9002 | 47.9629 | 32.8864 | 28.6265 | 37.18 | 45.4946 | 43.6795 | 49.818 | 47.5286 | 45.5866 | 44.3569 | 47.3482 | 42.0027 | 47.626 | 44.239 | 45.4096 | 42.4158 | 47.5288 | 46.2068 | 46.7049 | 49.4594 | 45.7972 | 47.1618 | 48.4714 | 49.709 | 46.188 | 49.1022 | 48.2599 | 51.0031 | 45.327 | 49.6908 | 46.8583 | 50.3413 | 46.751 | 50.3533 | 46.5176 | 51.1146 | 45.8047 | 49.5458 | 51.1863 | 92.5884 | 92.7513 | 92.7967
2022-09-07 19:21 | 0:56 | 28.403 | 28.8162 | 31.0175 | 44.4068 | 48.1271 | 44.7365 | 49.1306 | 42.7961 | 48.896 | 46.2097 | 45.1902 | 51.0922 | 42.5971 | 45.9317 | 46.3199 | 45.4922 | 44.3424 | 45.9064 | 45.6612 | 47.6516 | 32.7851 | 28.5435 | 37.1077 | 45.4535 | 43.5772 | 49.5785 | 47.3189 | 45.8452 | 44.2749 | 47.1547 | 41.9589 | 47.5113 | 44.215 | 45.2679 | 42.3247 | 47.3721 | 46.3429 | 46.6262 | 49.0932 | 45.7213 | 47.022 | 48.4534 | 49.5419 | 46.1375 | 49.2449 | 48.1917 | 50.9152 | 45.2559 | 49.5497 | 46.6962 | 49.8659 | 46.5647 | 50.4043 | 46.7518 | 50.9104 | 45.8337 | 49.3003 | 51.3719 | 92.6456 | 92.8175 | 92.8032
2022-09-07 19:21 | 0:57 | 28.5439 | 28.7324 | 30.9509 | 44.5 | 48.089 | 44.8387 | 49.0244 | 42.7 | 48.7769 | 46.1197 | 45.0774 | 50.817 | 42.5134 | 45.9269 | 46.1088 | 45.3682 | 44.2231 | 45.9507 | 45.6899 | 47.4163 | 32.7326 | 28.4602 | 37.0255 | 45.3253 | 43.5202 | 49.4193 | 47.2802 | 45.8248 | 44.2856 | 47.2078 | 41.8443 | 47.4989 | 44.047 | 45.3177 | 42.2962 | 47.2737 | 46.3134 | 46.5962 | 49.0069 | 45.6851 | 46.8946 | 48.2754 | 49.5354 | 46.1111 | 48.9127 | 48.1849 | 50.8913 | 45.1801 | 49.7869 | 46.4726 | 50.23 | 46.4353 | 50.1698 | 46.3857 | 50.9495 | 45.641 | 49.3548 | 51.1891 | 92.6989 | 92.8822 | 92.8363
2022-09-07 19:21 | 0:57 | 28.6313 | 28.6898 | 30.9262 | 44.5462 | 47.9221 | 44.7888 | 48.8754 | 42.6372 | 48.7216 | 45.9636 | 45.0207 | 50.8501 | 42.3614 | 45.7108 | 46.0395 | 45.266 | 44.1592 | 45.3528 | 45.5731 | 47.4411 | 32.6288 | 28.4026 | 36.8975 | 45.2891 | 43.4462 | 49.6137 | 47.2028 | 45.7149 | 44.2163 | 47.0253 | 41.7852 | 47.6146 | 43.9325 | 45.208 | 42.1971 | 47.2865 | 46.1729 | 46.488 | 48.7604 | 45.5958 | 46.8337 | 48.1671 | 49.4776 | 45.9861 | 48.8165 | 48.09 | 50.6581 | 45.0107 | 49.7294 | 46.5456 | 50.2476 | 46.376 | 50.2103 | 46.2891 | 50.9243 | 45.6191 | 49.2249 | 51.0918 | 92.7146 | 92.9373 | 92.8068
2022-09-07 19:21 | 0:57 | 28.4388 | 28.6079 | 30.8787 | 44.3313 | 47.8251 | 44.4367 | 48.8651 | 42.5765 | 48.6317 | 45.5971 | 45.0744 | 50.8349 | 42.4302 | 45.6604 | 46.1211 | 45.1343 | 44.1158 | 45.476 | 45.4637 | 47.3687 | 32.5285 | 28.3527 | 36.7462 | 45.2313 | 43.3477 | 49.3509 | 47.1618 | 45.7096 | 44.2199 | 47.0676 | 41.7563 | 47.2747 | 43.9539 | 45.1054 | 42.2006 | 47.1108 | 46.3304 | 46.304 | 48.958 | 45.6382 | 46.7959 | 48.16 | 49.291 | 45.8179 | 48.7051 | 48.0397 | 50.3592 | 44.9629 | 49.5 | 46.4521 | 50.0338 | 46.2536 | 50.0592 | 46.194 | 50.8056 | 45.4891 | 49.2107 | 50.8473 | 92.8019 | 93.0383 | 92.8786
2022-09-07 19:21 | 0:57 | 28.6243 | 28.4959 | 30.7726 | 44.36 | 47.7177 | 44.4346 | 48.803 | 42.4982 | 48.6177 | 45.6687 | 44.9049 | 50.7338 | 42.2514 | 45.5658 | 46.0177 | 45.0845 | 44.0343 | 45.4537 | 45.1911 | 47.1914 | 32.4642 | 28.2165 | 36.6976 | 45.0703 | 43.2588 | 49.3554 | 47.022 | 45.6593 | 43.9944 | 46.9398 | 41.7804 | 47.2144 | 43.8394 | 44.9473 | 42.3662 | 46.9542 | 46.3506 | 46.2401 | 48.7335 | 45.8178 | 46.7794 | 48.0345 | 49.0701 | 45.6865 | 48.5459 | 47.8979 | 50.3793 | 44.8135 | 49.2768 | 46.2813 | 49.8696 | 46.2913 | 50.1259 | 46.1239 | 50.4692 | 45.3571 | 48.903 | 50.8064 | 92.9597 | 93.1576 | 92.9713
2022-09-07 19:21 | 0:57 | 29.0079 | 28.4343 | 30.7395 | 44.1262 | 47.6278 | 44.5254 | 48.6882 | 42.3008 | 48.4477 | 45.3618 | 44.6362 | 50.6032 | 42.2038 | 45.592 | 45.8437 | 45.0134 | 43.9364 | 45.6234 | 45.1511 | 46.9228 | 32.3647 | 28.1607 | 36.6083 | 44.9427 | 43.1461 | 49.2533 | 46.8946 | 45.4197 | 43.7918 | 46.867 | 41.5347 | 47.0927 | 43.7955 | 44.9681 | 42.1358 | 46.855 | 46.289 | 46.1642 | 48.9251 | 45.7178 | 46.6263 | 47.9714 | 48.9814 | 45.6634 | 48.5686 | 47.8037 | 50.5877 | 44.7341 | 49.3524 | 46.1923 | 49.976 | 46.1155 | 50.039 | 45.8932 | 50.5055 | 45.3091 | 48.8229 | 50.9146 | 93.0562 | 93.2997 | 93.0808
2022-09-07 19:22 | 0:58 | 29.0241 | 28.4126 | 30.7099 | 44.0341 | 47.6562 | 44.374 | 48.5027 | 42.312 | 48.3641 | 45.395 | 44.7255 | 50.3404 | 42.1092 | 45.5579 | 45.7142 | 44.9571 | 43.8261 | 45.2968 | 45.1738 | 47.0393 | 32.3191 | 28.1424 | 36.6418 | 44.8979 | 43.1075 | 49.1829 | 46.8337 | 45.2984 | 43.7943 | 46.7758 | 41.4242 | 47.0373 | 43.5575 | 44.8195 | 41.9407 | 46.7707 | 46.038 | 45.973 | 48.6212 | 45.4627 | 46.4994 | 47.8254 | 49.2174 | 45.7101 | 48.5089 | 47.7143 | 50.4719 | 44.6552 | 49.3125 | 46.1509 | 49.8246 | 45.9209 | 50.005 | 45.8958 | 50.5025 | 45.1309 | 48.9929 | 50.4301 | 93.1465 | 93.4419 | 93.1079
2022-09-07 19:22 | 0:58 | 28.4535 | 28.4062 | 30.6358 | 44.0822 | 47.5855 | 44.2181 | 48.239 | 42.2472 | 48.2935 | 45.3448 | 44.5712 | 50.3177 | 42.0556 | 45.1974 | 45.6536 | 44.8724 | 43.8212 | 45.1171 | 45.054 | 47.2787 | 32.2555 | 28.0923 | 36.6161 | 44.8596 | 43.0018 | 49.3536 | 46.7959 | 45.1654 | 43.727 | 46.6313 | 41.3678 | 46.9148 | 43.3183 | 44.7829 | 41.8397 | 46.4536 | 45.8228 | 45.9897 | 48.6038 | 45.3298 | 46.5281 | 47.7169 | 49.0521 | 45.6099 | 48.3367 | 47.6423 | 50.1381 | 44.6382 | 49.0981 | 46.0742 | 49.8105 | 45.8556 | 49.956 | 45.8498 | 50.3445 | 45.1023 | 48.8064 | 50.5476 | 93.3117 | 93.623 | 93.2725
2022-09-07 19:22 | 0:58 | 28.2388 | 28.3306 | 30.5709 | 44.0112 | 47.4538 | 44.0291 | 48.2916 | 42.2281 | 48.1993 | 45.2463 | 44.7176 | 50.2145 | 41.861 | 45.1761 | 45.7599 | 44.8123 | 43.69 | 45.1645 | 44.9973 | 46.9283 | 32.2042 | 28.0088 | 36.5163 | 44.7254 | 42.9331 | 49.1385 | 46.7794 | 45.1965 | 43.5431 | 46.5815 | 41.3205 | 46.7698 | 43.3156 | 44.6318 | 41.7019 | 46.4186 | 45.7469 | 45.9717 | 48.625 | 45.2008 | 46.4054 | 47.5886 | 48.7929 | 45.4937 | 48.2266 | 47.5645 | 49.9365 | 44.5555 | 49.0111 | 45.9297 | 49.8966 | 45.727 | 49.8241 | 45.7144 | 50.1618 | 44.9987 | 48.6757 | 50.5235 | 93.4278 | 93.713 | 93.3641
2022-09-07 19:22 | 0:58 | 28.5558 | 28.2691 | 30.5158 | 43.8695 | 47.3594 | 43.9409 | 48.1177 | 42.1829 | 48.117 | 45.1925 | 44.6583 | 50.125 | 41.8113 | 45.1485 | 45.4531 | 44.7206 | 43.5444 | 44.8589 | 44.9712 | 47.0466 | 32.1361 | 27.9516 | 36.3813 | 44.6766 | 42.8565 | 48.8689 | 46.6263 | 45.083 | 43.5307 | 46.417 | 41.3195 | 46.8083 | 43.3507 | 44.5647 | 41.5981 | 46.6345 | 45.5783 | 45.8207 | 48.2009 | 45.0677 | 46.2184 | 47.5581 | 48.7512 | 45.3812 | 48.1931 | 47.4787 | 49.9615 | 44.4114 | 48.8178 | 45.8307 | 49.5563 | 45.7036 | 49.7908 | 45.904 | 50.0312 | 44.9554 | 48.4594 | 50.6494 | 93.5553 | 93.8338 | 93.4309
2022-09-07 19:22 | 0:58 | 28.1476 | 28.2267 | 30.4367 | 43.7239 | 47.3513 | 43.7267 | 48.0521 | 42.0409 | 48.0494 | 45.1328 | 44.4777 | 49.9821 | 41.7423 | 45.0769 | 45.3864 | 44.6596 | 43.4718 | 45.1249 | 44.8671 | 46.9732 | 32.0767 | 27.911 | 36.2831 | 44.6283 | 42.7696 | 48.7777 | 46.4994 | 45.2402 | 43.3986 | 46.3108 | 41.148 | 46.7356 | 43.1539 | 44.4637 | 41.5497 | 46.4862 | 45.6265 | 45.6301 | 48.1368 | 45.0671 | 46.0759 | 47.5418 | 48.7823 | 45.3083 | 48.1059 | 47.3801 | 49.8796 | 44.3533 | 48.8076 | 45.8991 | 49.6543 | 45.8784 | 49.5326 | 45.8415 | 50.0778 | 44.8634 | 48.5488 | 50.5086 | 93.6974 | 93.9276 | 93.4555
2022-09-07 19:22 | 0:58 | 28.5731 | 28.1414 | 30.4311 | 43.8204 | 47.1844 | 43.8619 | 48.1798 | 41.998 | 47.9267 | 44.9915 | 44.3435 | 49.9499 | 41.6702 | 44.8441 | 45.2763 | 44.5628 | 43.4131 | 44.7218 | 44.5858 | 46.7866 | 31.9893 | 27.8746 | 36.1425 | 44.6151 | 42.7478 | 48.727 | 46.5281 | 45.0989 | 43.3415 | 46.3614 | 41.2345 | 46.6029 | 43.1042 | 44.3587 | 41.5308 | 46.1811 | 45.4719 | 45.6631 | 48.0869 | 44.9344 | 46.0778 | 47.4152 | 48.7248 | 45.2544 | 48.1518 | 47.2487 | 49.7762 | 44.3252 | 48.6915 | 45.7516 | 49.791 | 45.613 | 49.4363 | 45.5571 | 49.9497 | 44.8445 | 48.3856 | 50.2239 | 93.6782 | 93.8755 | 93.4668
2022-09-07 19:23 | 0:58 | 28.8356 | 28.0958 | 30.3885 | 43.7227 | 47.2615 | 43.7499 | 48.0674 | 41.8539 | 47.8726 | 44.8506 | 44.409 | 49.9051 | 41.546 | 44.9958 | 45.3818 | 44.4448 | 43.3276 | 44.8661 | 44.5891 | 46.6429 | 31.8916 | 27.7905 | 36.051 | 44.4891 | 42.6283 | 48.6905 | 46.4054 | 44.9542 | 43.2941 | 46.2294 | 41.0731 | 46.5301 | 43.0233 | 44.3122 | 41.3773 | 46.2523 | 45.3878 | 45.6377 | 47.8807 | 44.8398 | 46.0278 | 47.3208 | 48.458 | 45.0758 | 48.0021 | 47.1773 | 49.6159 | 44.1185 | 48.6407 | 45.6656 | 49.4213 | 45.3269 | 49.4196 | 45.4068 | 49.6959 | 44.7043 | 48.2795 | 50.2102 | 93.7795 | 93.9195 | 93.599
2022-09-07 19:23 | 0:59 | 28.8094 | 28.0721 | 30.3381 | 43.5362 | 47.1078 | 43.7865 | 47.8565 | 41.8571 | 47.7902 | 45.0216 | 44.2447 | 49.8307 | 41.554 | 44.7406 | 45.1206 | 44.3291 | 43.2437 | 44.4411 | 44.694 | 46.792 | 31.8212 | 27.7196 | 35.9516 | 44.3406 | 42.5451 | 48.5265 | 46.2184 | 44.7286 | 43.2035 | 46.1575 | 40.9227 | 46.4381 | 42.9704 | 44.2615 | 41.3054 | 46.0387 | 45.2595 | 45.4887 | 48.1448 | 44.6886 | 45.9353 | 47.3017 | 48.383 | 45.1018 | 48.0142 | 47.0515 | 49.5606 | 44.1215 | 48.4578 | 45.5731 | 49.392 | 45.4254 | 49.3437 | 45.3226 | 49.8932 | 44.614 | 48.0874 | 49.9887 | 93.9135 | 93.9835 | 93.6269
2022-09-07 19:23 | 0:59 | 28.7125 | 28.0084 | 30.3246 | 43.6131 | 47.0017 | 43.6688 | 47.7568 | 41.6973 | 47.7593 | 44.8111 | 44.0296 | 49.8154 | 41.5635 | 44.6765 | 45.1099 | 44.23 | 43.2198 | 44.3878 | 44.5225 | 46.602 | 31.7476 | 27.6358 | 35.8802 | 44.2977 | 42.4207 | 48.6696 | 46.0759 | 44.4208 | 43.1218 | 45.9343 | 40.7097 | 46.3749 | 42.9685 | 44.1602 | 41.165 | 46.0958 | 45.2694 | 45.5045 | 48.0875 | 44.6608 | 45.9291 | 47.158 | 48.45 | 45.005 | 47.7465 | 47.0405 | 49.3572 | 43.976 | 48.4763 | 45.438 | 49.1172 | 45.4296 | 49.1671 | 45.379 | 49.6453 | 44.5744 | 47.9413 | 50.0829 | 94.0597 | 93.9888 | 93.7914
2022-09-07 19:23 | 0:59 | 28.7174 | 27.9722 | 30.2738 | 43.4634 | 46.9767 | 43.6314 | 47.7628 | 41.7216 | 47.6645 | 44.6882 | 44.1991 | 49.6565 | 41.4241 | 44.7637 | 45.0258 | 44.1396 | 43.104 | 44.6666 | 44.5227 | 46.432 | 31.6965 | 27.6008 | 35.8232 | 44.1471 | 42.3324 | 48.2289 | 46.0778 | 44.2142 | 43.0402 | 45.8865 | 40.6887 | 46.1363 | 42.8766 | 43.9601 | 41.1136 | 45.939 | 45.3287 | 45.3127 | 48.0996 | 44.712 | 45.7537 | 47.0573 | 48.3421 | 44.8678 | 47.6474 | 46.9062 | 49.487 | 43.9329 | 48.4301 | 45.2869 | 49.1561 | 45.1946 | 48.9499 | 45.256 | 49.7232 | 44.4117 | 48.2047 | 49.706 | 94.181 | 94.0964 | 93.8354
2022-09-07 19:23 | 0:59 | 28.66 | 27.9295 | 30.1945 | 43.3929 | 46.813 | 43.5155 | 47.741 | 41.6502 | 47.5346 | 44.6458 | 44.1666 | 49.7104 | 41.3014 | 44.8034 | 44.828 | 44.1177 | 42.9772 | 44.6023 | 44.3343 | 46.4373 | 31.6407 | 27.5302 | 35.7688 | 44.128 | 42.2714 | 48.3548 | 46.0278 | 44.4056 | 42.9645 | 45.8047 | 40.5636 | 46.1242 | 42.7864 | 43.9455 | 41.0736 | 46.1609 | 45.2565 | 45.2349 | 47.9871 | 44.7576 | 45.5765 | 46.9631 | 48.1382 | 44.7567 | 47.5452 | 46.8666 | 49.1638 | 43.9365 | 48.1755 | 45.2082 | 49.0816 | 45.4006 | 48.9912 | 44.9345 | 49.3322 | 44.3321 | 47.7587 | 49.8232 | 94.2561 | 94.2053 | 93.9213
2022-09-07 19:23 | 0:59 | 28.5608 | 27.8708 | 30.1575 | 43.2591 | 46.8312 | 43.4253 | 47.3056 | 41.5632 | 47.5623 | 44.4272 | 43.8621 | 49.6942 | 41.2426 | 44.4902 | 44.6211 | 44.0191 | 42.8873 | 44.1675 | 44.2267 | 46.3626 | 31.5746 | 27.5015 | 35.6948 | 44.1127 | 42.1811 | 48.1021 | 45.9353 | 44.1212 | 42.8649 | 45.8175 | 40.5776 | 46.041 | 42.6695 | 43.8095 | 40.9704 | 45.8194 | 44.9227 | 45.1917 | 47.9207 | 44.5243 | 45.6136 | 46.7823 | 48.0299 | 44.6921 | 47.5047 | 46.7403 | 49.1463 | 43.8489 | 48.2471 | 45.2139 | 49.2215 | 45.0598 | 48.9634 | 44.9871 | 49.4068 | 44.3504 | 47.9278 | 49.7379 | 94.4324 | 94.3677 | 94.0469
2022-09-07 19:24 | 0:59 | 28.4192 | 27.863 | 30.0928 | 43.2671 | 46.6543 | 43.2751 | 47.618 | 41.4722 | 47.4658 | 44.4826 | 44.0838 | 49.5489 | 41.16 | 44.3915 | 44.7825 | 43.9027 | 42.9015 | 44.2639 | 44.2709 | 46.2029 | 31.5135 | 27.4496 | 35.6413 | 43.9711 | 42.0986 | 47.9628 | 45.9291 | 44.4739 | 42.8036 | 45.7447 | 40.4699 | 45.9303 | 42.6539 | 43.8035 | 40.797 | 45.5978 | 44.8246 | 45.1374 | 47.6715 | 44.3824 | 45.4308 | 46.7369 | 48.0815 | 44.5614 | 47.3085 | 46.6705 | 49.0197 | 43.7766 | 48.1433 | 44.9224 | 49.1489 | 45.0577 | 48.8895 | 44.9164 | 49.3275 | 44.2341 | 47.9545 | 49.2857 | 94.5744 | 94.4497 | 94.0927
2022-09-07 19:24 | 1:00 | 28.3565 | 27.8329 | 30.0248 | 43.1578 | 46.6284 | 43.1478 | 47.4534 | 41.4034 | 47.3933 | 44.5441 | 44.0791 | 49.4892 | 41.1059 | 44.1544 | 44.5325 | 43.8234 | 42.842 | 43.9798 | 44.0847 | 46.3469 | 31.4568 | 27.4302 | 35.6024 | 43.8255 | 42.0262 | 47.8726 | 45.7537 | 44.648 | 42.7937 | 45.6015 | 40.5063 | 45.7392 | 42.4821 | 43.6943 | 40.7168 | 45.6437 | 44.6638 | 44.9667 | 47.6282 | 44.2387 | 45.4914 | 46.7279 | 47.9824 | 44.5817 | 47.2549 | 46.589 | 49.0506 | 43.5965 | 47.9177 | 44.965 | 48.8506 | 44.9336 | 48.9031 | 44.8889 | 49.3457 | 44.0505 | 47.7715 | 49.3492 | 94.7036 | 94.5883 | 94.1264
2022-09-07 19:24 | 1:00 | 28.3175 | 27.7878 | 29.9397 | 43.0006 | 46.5945 | 43.1576 | 47.3682 | 41.4313 | 47.2543 | 44.6339 | 43.8573 | 49.5176 | 40.999 | 44.3203 | 44.6601 | 43.7585 | 42.7041 | 44.1222 | 44.111 | 46.3227 | 31.4142 | 27.3263 | 35.5137 | 43.7615 | 41.9153 | 47.7185 | 45.5765 | 44.4049 | 42.7064 | 45.5607 | 40.4597 | 45.764 | 42.4479 | 43.6639 | 40.5628 | 45.5535 | 44.7297 | 44.9367 | 47.6639 | 44.2088 | 45.4219 | 46.5371 | 48.0283 | 44.5044 | 47.1332 | 46.4706 | 49.0285 | 43.4882 | 47.8834 | 44.862 | 48.9129 | 44.8592 | 48.5107 | 44.5432 | 49.3161 | 43.9723 | 47.5766 | 49.3934 | 94.7749 | 94.6995 | 94.2177
2022-09-07 19:24 | 1:00 | 28.3351 | 27.7052 | 29.9215 | 43.0181 | 46.5623 | 43.1001 | 47.2666 | 41.2955 | 47.1665 | 44.3131 | 44.0132 | 49.3949 | 40.8733 | 44.1127 | 44.5522 | 43.6578 | 42.6809 | 44.2247 | 44.025 | 46.0967 | 31.3524 | 27.2615 | 35.5106 | 43.7273 | 41.8687 | 47.7891 | 45.6136 | 44.0829 | 42.5638 | 45.5033 | 40.4108 | 45.8119 | 42.4261 | 43.5672 | 40.6422 | 45.4653 | 44.8272 | 44.911 | 47.5005 | 44.1407 | 45.2017 | 46.5581 | 47.7646 | 44.4302 | 47.1714 | 46.4771 | 48.8488 | 43.4754 | 47.8663 | 44.8859 | 48.6726 | 44.6613 | 48.4121 | 44.7493 | 48.9951 | 43.8807 | 47.3655 | 49.2733 | 94.7975 | 94.8152 | 94.2501
2022-09-07 19:24 | 1:00 | 28.3569 | 27.667 | 29.892 | 42.9854 | 46.4534 | 42.8212 | 47.2864 | 41.0573 | 47.1174 | 44.3586 | 43.6936 | 49.1479 | 40.8434 | 44.2246 | 44.4549 | 43.6223 | 42.5909 | 44.1039 | 44.0338 | 45.9035 | 31.3168 | 27.2411 | 35.4714 | 43.7392 | 41.8268 | 47.6367 | 45.4308 | 43.7393 | 42.4873 | 45.3209 | 40.2119 | 45.6961 | 42.3446 | 43.488 | 40.6205 | 45.4279 | 44.6641 | 44.7236 | 47.3332 | 44.059 | 45.1399 | 46.5159 | 47.7204 | 44.3629 | 47.1106 | 46.3504 | 48.8501 | 43.4762 | 47.7348 | 44.8055 | 48.6204 | 44.7039 | 48.6267 | 44.535 | 48.6852 | 43.7771 | 47.5375 | 49.4483 | 94.8813 | 94.9129 | 94.2111
2022-09-07 19:24 | 1:00 | 28.3171 | 27.6189 | 29.8437 | 42.7377 | 46.3674 | 42.8404 | 47.1495 | 41.0633 | 47.0854 | 44.3043 | 43.6974 | 49.1878 | 40.7456 | 44.1675 | 44.3387 | 43.5414 | 42.5195 | 43.9006 | 43.8481 | 45.9627 | 31.2644 | 27.175 | 35.3868 | 43.5256 | 41.7327 | 47.6594 | 45.4914 | 43.7086 | 42.3976 | 45.2115 | 40.2335 | 45.6481 | 42.1951 | 43.4709 | 40.578 | 45.6196 | 44.4631 | 44.632 | 47.1844 | 43.9803 | 45.1004 | 46.3988 | 47.5845 | 44.281 | 47.0466 | 46.2411 | 48.692 | 43.2709 | 47.6119 | 44.7696 | 48.6412 | 44.6677 | 48.4284 | 44.4087 | 48.8507 | 43.7525 | 47.3141 | 49.1387 | 94.851 | 94.9056 | 94.2442
2022-09-07 19:25 | 1:01 | 28.0358 | 27.5692 | 29.7982 | 42.7616 | 46.2589 | 42.813 | 46.9425 | 41.1117 | 46.9266 | 43.9378 | 43.7679 | 49.0561 | 40.6822 | 43.9796 | 44.1365 | 43.4465 | 42.4508 | 43.807 | 43.7926 | 46.0057 | 31.1957 | 27.1327 | 35.323 | 43.6181 | 41.6048 | 47.568 | 45.4219 | 44.0731 | 42.3517 | 45.2679 | 40.0519 | 45.5085 | 42.0585 | 43.3542 | 40.4939 | 45.3471 | 44.3309 | 44.5875 | 47.3036 | 43.8732 | 45.0272 | 46.2892 | 47.6581 | 44.1373 | 46.8363 | 46.1125 | 48.7599 | 43.2106 | 47.6307 | 44.5514 | 48.538 | 44.583 | 48.2785 | 44.2408 | 49.0091 | 43.6623 | 47.3878 | 48.9957 | 94.7123 | 94.8051 | 94.1356
2022-09-07 19:25 | 1:01 | 28.0106 | 27.5503 | 29.708 | 42.8145 | 46.144 | 42.7807 | 47.2232 | 41.0317 | 46.904 | 44.0249 | 43.5634 | 48.9408 | 40.6569 | 43.9013 | 44.2549 | 43.4198 | 42.3285 | 43.9088 | 43.672 | 45.7115 | 31.1635 | 27.0806 | 35.2706 | 43.4897 | 41.5385 | 47.5148 | 45.2017 | 43.8205 | 42.2389 | 45.1192 | 40.0348 | 45.4661 | 42.0223 | 43.257 | 40.3542 | 45.2495 | 44.295 | 44.5111 | 46.8984 | 43.8366 | 44.9357 | 46.3307 | 47.4305 | 44.0517 | 46.8492 | 46.0086 | 48.5883 | 43.2116 | 47.4435 | 44.6271 | 48.4487 | 44.2631 | 48.2482 | 44.1486 | 48.921 | 43.5434 | 47.33 | 48.9189 | 94.4889 | 94.6172 | 93.973
2022-09-07 19:25 | 1:01 | 28.014 | 27.6363 | 29.7123 | 42.6532 | 46.0913 | 42.7904 | 47.1364 | 40.863 | 46.7967 | 43.8584 | 43.2432 | 48.8693 | 40.6257 | 43.9265 | 44.0746 | 43.3592 | 42.2658 | 43.6208 | 43.6842 | 45.5352 | 31.1255 | 27.0572 | 35.1814 | 43.3504 | 41.4482 | 47.49 | 45.1399 | 43.6106 | 42.099 | 45.1012 | 39.8926 | 45.3049 | 41.7871 | 43.1416 | 40.1979 | 45.276 | 44.2722 | 44.3839 | 46.8334 | 43.7704 | 44.7951 | 46.1871 | 47.4064 | 44.091 | 46.8243 | 46.0247 | 48.4074 | 43.1116 | 47.2224 | 44.376 | 48.4531 | 44.2598 | 48.131 | 44.0517 | 48.7388 | 43.5335 | 47.3002 | 48.7979 | 94.2741 | 94.3993 | 93.7765
2022-09-07 19:25 | 1:01 | 27.9121 | 29.2563 | 29.6764 | 42.5029 | 46.0693 | 42.6062 | 47.0153 | 40.7707 | 46.738 | 43.8088 | 43.2158 | 48.8829 | 40.5337 | 43.7185 | 43.988 | 43.293 | 42.1934 | 43.6391 | 43.5542 | 45.5564 | 31.0364 | 26.9533 | 35.1088 | 43.2947 | 41.3912 | 47.5532 | 45.1004 | 43.5755 | 42.0831 | 44.9357 | 39.8134 | 45.3034 | 41.898 | 43.1203 | 40.2611 | 45.1011 | 44.2774 | 44.2803 | 46.7034 | 43.6952 | 44.7709 | 46.1074 | 47.3451 | 43.8697 | 46.6608 | 45.8751 | 48.6257 | 43.0273 | 47.2873 | 44.3835 | 48.3452 | 44.2323 | 48.1257 | 44.0269 | 48.7135 | 43.4537 | 47.095 | 48.7522 | 94.0135 | 94.2109 | 93.6467
2022-09-07 19:25 | 1:01 | 27.9494 | 29.0048 | 29.587 | 42.5878 | 46.0921 | 42.7213 | 46.7068 | 40.68 | 46.6435 | 43.6858 | 42.9738 | 48.6416 | 40.4497 | 43.4616 | 43.9658 | 43.1682 | 42.1131 | 43.4574 | 43.4819 | 45.398 | 31.0028 | 26.9313 | 35.0654 | 43.2197 | 41.3193 | 47.3468 | 45.0272 | 43.5179 | 42.0134 | 44.8656 | 39.6326 | 44.9951 | 41.7654 | 42.99 | 40.0363 | 45.048 | 44.1007 | 44.2015 | 46.9381 | 43.5523 | 44.6869 | 45.9904 | 47.072 | 43.7788 | 46.5997 | 45.8295 | 48.3026 | 42.9659 | 47.1541 | 44.3526 | 48.3447 | 44.0695 | 48.252 | 43.9738 | 48.5181 | 43.3899 | 47.0948 | 48.9129 | 93.9252 | 94.0634 | 93.6351
2022-09-07 19:25 | 1:01 | 27.6461 | 28.4157 | 29.4251 | 42.416 | 45.9857 | 42.4827 | 46.765 | 40.7528 | 46.5836 | 43.7994 | 43.1439 | 48.6917 | 40.3634 | 43.5385 | 43.8972 | 43.1496 | 42.068 | 43.2621 | 43.4088 | 45.2625 | 30.9491 | 26.8466 | 35.0406 | 43.145 | 41.2857 | 47.2616 | 44.9357 | 43.2856 | 41.9226 | 44.7259 | 39.7037 | 45.1374 | 41.881 | 42.9238 | 40.0091 | 44.9684 | 43.9115 | 44.2362 | 46.7159 | 43.4939 | 44.597 | 45.913 | 46.9945 | 43.8276 | 46.5761 | 45.753 | 48.1962 | 42.882 | 47.2698 | 44.1663 | 47.9682 | 44.034 | 48.1326 | 44.0042 | 48.3263 | 43.3275 | 46.8456 | 48.6505 | 93.8287 | 93.9403 | 93.5588
2022-09-07 19:26 | 1:01 | 27.625 | 27.3781 | 29.3834 | 42.405 | 45.8429 | 42.3631 | 46.7317 | 40.6421 | 46.5198 | 43.5682 | 43.2244 | 48.4749 | 40.3955 | 43.3719 | 43.7525 | 43.0945 | 42.0258 | 43.1898 | 43.3222 | 45.1577 | 30.9023 | 26.7931 | 35.047 | 43.046 | 41.2164 | 47.0464 | 44.7951 | 43.3154 | 41.8888 | 44.6947 | 39.6991 | 44.9513 | 41.7536 | 42.8455 | 39.9111 | 44.8127 | 43.9103 | 44.1043 | 46.5834 | 43.4529 | 44.4246 | 45.8771 | 46.9596 | 43.6684 | 46.4874 | 45.6729 | 48.153 | 42.7559 | 47.3743 | 44.1193 | 47.7882 | 43.9186 | 48.0082 | 43.7368 | 48.3434 | 43.236 | 46.8939 | 48.3856 | 93.759 | 93.8357 | 93.5453
2022-09-07 19:26 | 1:02 | 27.1053 | 27.2534 | 29.3534 | 42.2222 | 45.8195 | 42.3854 | 46.5578 | 40.5688 | 46.485 | 43.5735 | 43.1768 | 48.5517 | 40.3306 | 43.4911 | 43.6525 | 42.9816 | 41.9313 | 43.1551 | 43.2103 | 45.2251 | 30.8311 | 26.7436 | 34.9713 | 43.0151 | 41.1357 | 46.9952 | 44.7709 | 43.1599 | 41.8242 | 44.6735 | 39.5357 | 45.0644 | 41.7459 | 42.8518 | 39.9504 | 44.7637 | 43.7862 | 44.1675 | 46.474 | 43.3488 | 44.4464 | 45.7736 | 47.0057 | 43.6343 | 46.3733 | 45.5433 | 47.8989 | 42.7268 | 47.4787 | 44.0581 | 48.0291 | 43.8149 | 47.8621 | 43.6031 | 48.1794 | 43.1069 | 46.8744 | 48.5064 | 93.6805 | 93.7639 | 93.5341
2022-09-07 19:26 | 1:02 | 27.2747 | 27.1627 | 29.303 | 42.3088 | 45.7872 | 42.3324 | 46.5137 | 40.3426 | 46.3803 | 43.3506 | 42.8946 | 48.4386 | 40.1747 | 43.4313 | 43.6666 | 42.8977 | 41.9212 | 43.2938 | 43.1244 | 45.2295 | 30.807 | 26.6947 | 34.9656 | 42.9215 | 41.0648 | 46.8163 | 44.6869 | 43.1075 | 41.6685 | 44.6029 | 39.4733 | 44.835 | 41.618 | 42.7787 | 39.892 | 44.7441 | 43.8392 | 43.9395 | 46.6785 | 43.3768 | 44.3193 | 45.6484 | 47.0144 | 43.6385 | 46.2565 | 45.5254 | 48.0381 | 42.5957 | 47.133 | 43.8488 | 47.9629 | 43.7627 | 47.7573 | 43.7431 | 48.2086 | 43.0611 | 46.6553 | 48.5625 | 93.6028 | 93.6843 | 93.44
2022-09-07 19:26 | 1:02 | 27.0642 | 27.1559 | 29.2328 | 42.1162 | 45.6561 | 42.2772 | 46.4917 | 40.4154 | 46.3442 | 43.6577 | 42.9549 | 48.295 | 40.1489 | 42.9995 | 43.4721 | 42.8216 | 41.7961 | 43.2303 | 43.0857 | 45.1862 | 30.7675 | 26.638 | 34.9071 | 42.8109 | 40.9583 | 46.7295 | 44.597 | 42.906 | 41.5963 | 44.4986 | 39.4581 | 44.873 | 41.4399 | 42.601 | 39.734 | 44.7632 | 43.6427 | 43.8982 | 46.6151 | 43.183 | 44.3147 | 45.5352 | 46.6942 | 43.475 | 46.1264 | 45.3765 | 48.1756 | 42.6333 | 46.8355 | 43.8593 | 47.8602 | 43.5838 | 47.6057 | 43.5737 | 48.1258 | 43.0424 | 46.5076 | 48.0755 | 93.5491 | 93.65 | 93.4133
2022-09-07 19:26 | 1:02 | 26.7208 | 27.0963 | 29.1674 | 42.1585 | 45.6762 | 42.1183 | 46.5337 | 40.2681 | 46.2924 | 43.2536 | 42.7461 | 48.3613 | 40.0145 | 43.0276 | 43.4958 | 42.7765 | 41.7304 | 43.1104 | 43.0323 | 45.2582 | 30.7223 | 26.5798 | 34.855 | 42.6585 | 40.8484 | 46.8351 | 44.4246 | 42.8507 | 41.5782 | 44.3507 | 39.2669 | 44.7234 | 41.3721 | 42.5657 | 39.5727 | 44.6585 | 43.3512 | 43.8883 | 46.3789 | 43.0968 | 44.3005 | 45.568 | 46.5975 | 43.3765 | 46.2987 | 45.2818 | 47.9229 | 42.5242 | 46.6842 | 43.76 | 47.7693 | 43.443 | 47.7075 | 43.5147 | 48.0238 | 42.9685 | 46.3359 | 48.3101 | 93.4847 | 93.6085 | 93.3902
2022-09-07 19:26 | 1:02 | 26.6685 | 27.0087 | 29.119 | 42.1207 | 45.5421 | 41.9748 | 46.2292 | 40.2561 | 46.187 | 43.2372 | 42.8531 | 48.2647 | 39.916 | 43.1224 | 43.5094 | 42.7101 | 41.6533 | 43.0656 | 42.922 | 44.986 | 30.6417 | 26.5149 | 34.8145 | 42.6109 | 40.8463 | 46.7604 | 44.4464 | 42.9968 | 41.4962 | 44.3259 | 39.2826 | 44.7882 | 41.3053 | 42.4087 | 39.5492 | 44.5793 | 43.4422 | 43.7477 | 46.2616 | 43.0115 | 44.1696 | 45.5001 | 46.4094 | 43.2713 | 46.0687 | 45.2084 | 47.966 | 42.4693 | 46.6283 | 43.8237 | 47.8373 | 43.4901 | 47.3967 | 43.5293 | 47.7803 | 42.9435 | 46.4116 | 48.2197 | 93.396 | 93.5136 | 93.3314
2022-09-07 19:27 | 1:03 | 26.6568 | 26.908 | 29.0421 | 42.0059 | 45.4382 | 41.8845 | 46.2501 | 40.1183 | 46.0423 | 43.2241 | 42.6826 | 48.1859 | 39.956 | 43.073 | 43.5888 | 42.6149 | 41.6374 | 42.8625 | 42.8227 | 44.9545 | 30.6033 | 26.4731 | 34.7214 | 42.561 | 40.7106 | 46.7251 | 44.3193 | 43.0083 | 41.4305 | 44.2429 | 39.0844 | 44.6649 | 41.1237 | 42.3486 | 39.7794 | 44.5557 | 43.6287 | 43.7276 | 46.214 | 43.0848 | 44.1446 | 45.395 | 46.463 | 43.1078 | 46.0042 | 45.12 | 47.6888 | 42.2804 | 46.3851 | 43.6495 | 47.5587 | 43.3738 | 47.3996 | 43.4194 | 47.7558 | 42.7256 | 46.3051 | 48.0786 | 93.3525 | 93.4557 | 93.3248
2022-09-07 19:27 | 1:03 | 26.5068 | 26.8513 | 28.9545 | 41.9203 | 45.4578 | 42.018 | 46.1302 | 40.1087 | 45.9624 | 43.1603 | 42.5664 | 48.0989 | 39.8124 | 43.084 | 43.3323 | 42.5592 | 41.5262 | 42.7751 | 42.7862 | 44.912 | 30.524 | 26.355 | 34.6776 | 42.4803 | 40.6553 | 46.6899 | 44.3147 | 42.8245 | 41.3567 | 44.1228 | 39.0521 | 44.5034 | 41.0744 | 42.3182 | 39.7027 | 44.3901 | 43.5479 | 43.6468 | 46.1893 | 43.047 | 44.0283 | 45.2357 | 46.6139 | 43.1174 | 45.8835 | 45.0871 | 47.6373 | 42.2421 | 46.3984 | 43.4852 | 47.2944 | 43.358 | 47.3654 | 43.4336 | 47.8638 | 42.6966 | 46.0895 | 48.0603 | 93.2812 | 93.431 | 93.3345
2022-09-07 19:27 | 1:03 | 26.2409 | 26.7621 | 28.8268 | 41.7777 | 45.4 | 41.6921 | 45.9453 | 40.2175 | 45.9376 | 42.9386 | 42.8285 | 48.0887 | 39.7102 | 42.7327 | 43.2436 | 42.4358 | 41.4806 | 43.0352 | 42.7023 | 44.7687 | 30.4837 | 26.2852 | 34.695 | 42.4275 | 40.5935 | 46.6175 | 44.3005 | 42.813 | 41.2427 | 44.022 | 39.0289 | 44.3445 | 41.073 | 42.2525 | 39.4516 | 44.134 | 43.3648 | 43.6232 | 45.8239 | 42.8777 | 43.9615 | 45.2307 | 46.3691 | 43.004 | 45.8112 | 44.9577 | 47.5342 | 42.2314 | 46.4719 | 43.5663 | 47.5262 | 43.4074 | 47.2435 | 43.2194 | 47.6193 | 42.615 | 46.0757 | 48.0701 | 93.1779 | 93.3649 | 93.2523
2022-09-07 19:27 | 1:03 | 26.271 | 26.682 | 28.774 | 41.6041 | 45.1893 | 41.8005 | 46.0913 | 40.063 | 45.9289 | 43.0132 | 42.5605 | 48.0512 | 39.5926 | 42.7766 | 43.0701 | 42.3925 | 41.3253 | 42.7772 | 42.62 | 44.604 | 30.4584 | 26.2229 | 34.6748 | 42.4331 | 40.5677 | 46.4828 | 44.1696 | 42.6881 | 41.2731 | 44.0709 | 38.9625 | 44.2735 | 41.0927 | 42.2232 | 39.395 | 44.1572 | 43.414 | 43.48 | 46.018 | 42.8167 | 43.8337 | 45.1713 | 46.2956 | 42.902 | 45.6331 | 44.9245 | 47.518 | 42.0783 | 46.3057 | 43.4438 | 47.3788 | 43.2074 | 47.0978 | 43.0767 | 47.6792 | 42.4987 | 46.0197 | 47.9469 | 93.1446 | 93.2735 | 93.1741
2022-09-07 19:27 | 1:03 | 26.3398 | 26.5979 | 28.7051 | 41.7801 | 45.1724 | 41.6829 | 46.0689 | 39.9217 | 45.8139 | 42.9681 | 42.503 | 47.9651 | 39.5724 | 42.904 | 43.0349 | 42.2888 | 41.2249 | 42.5798 | 42.5525 | 44.6606 | 30.3822 | 26.152 | 34.6028 | 42.3134 | 40.4952 | 46.6273 | 44.1446 | 42.5093 | 41.188 | 44.0056 | 38.8815 | 44.2279 | 41.1761 | 42.1309 | 39.4233 | 44.0689 | 43.3977 | 43.398 | 45.9009 | 42.7913 | 43.6469 | 45.0463 | 46.0012 | 42.7604 | 45.5973 | 44.807 | 47.3587 | 42.0069 | 46.0429 | 43.3592 | 47.1011 | 43.1091 | 46.8784 | 43.0643 | 47.4587 | 42.4338 | 45.9147 | 47.6006 | 93.0473 | 93.1623 | 93.1173
2022-09-07 19:27 | 1:03 | 26.13 | 26.5273 | 28.6392 | 41.6946 | 45.1607 | 41.6239 | 46.0123 | 39.8266 | 45.7744 | 42.6256 | 42.2114 | 47.9198 | 39.5309 | 42.6216 | 42.956 | 42.2504 | 41.188 | 42.3578 | 42.4874 | 44.7415 | 30.3275 | 26.0773 | 34.5602 | 42.283 | 40.3956 | 46.4954 | 44.0283 | 42.4355 | 41.0473 | 43.8218 | 38.8916 | 44.127 | 40.8985 | 42.0547 | 39.3246 | 43.885 | 43.1704 | 43.2804 | 45.9014 | 42.6725 | 43.6412 | 44.9796 | 46.0926 | 42.8104 | 45.5033 | 44.7164 | 47.2543 | 42.0088 | 46.1483 | 43.2407 | 47.0806 | 43.0436 | 47.1562 | 42.8782 | 47.4558 | 42.4318 | 45.9934 | 47.6675 | 92.9155 | 93.0546 | 93.0524
2022-09-07 19:28 | 1:03 | 26.1979 | 26.3948 | 28.5321 | 41.688 | 45.0598 | 41.6399 | 45.6973 | 39.805 | 45.6798 | 42.5299 | 42.1522 | 47.7258 | 39.5094 | 42.4866 | 42.9629 | 42.2223 | 41.1251 | 42.4712 | 42.4905 | 44.4465 | 30.245 | 25.9914 | 34.461 | 42.2396 | 40.2993 | 46.2658 | 43.9615 | 42.4306 | 40.954 | 43.8951 | 38.7651 | 44.1583 | 40.7566 | 41.9363 | 39.1614 | 44.0576 | 43.1385 | 43.1997 | 45.9818 | 42.613 | 43.56 | 44.9093 | 46.0489 | 42.7423 | 45.5561 | 44.6644 | 47.3332 | 41.8802 | 46.2085 | 43.2521 | 46.3675 | 43.0933 | 46.9992 | 42.9391 | 47.3443 | 42.3212 | 45.8866 | 47.5365 | 92.821 | 92.9335 | 92.9317
2022-09-07 19:28 | 1:04 | 26.0044 | 26.3558 | 28.477 | 41.3369 | 44.9453 | 41.5183 | 45.6651 | 39.7951 | 45.6649 | 42.5222 | 42.5088 | 47.7454 | 39.3398 | 42.5933 | 42.7495 | 42.0701 | 41.1016 | 42.4587 | 42.353 | 44.2519 | 30.196 | 25.9341 | 34.4393 | 42.1098 | 40.2343 | 46.1611 | 43.8337 | 42.1807 | 40.8623 | 43.7882 | 38.5773 | 43.9669 | 40.7397 | 41.8104 | 39.222 | 43.8156 | 43.1768 | 43.032 | 45.7729 | 42.6415 | 43.5665 | 44.8291 | 46.057 | 42.636 | 45.5794 | 44.5917 | 47.2909 | 41.7236 | 45.8056 | 43.1357 | 46.869 | 42.8681 | 46.8354 | 42.865 | 47.1068 | 42.2503 | 45.7812 | 47.2589 | 92.7031 | 92.873 | 92.8648
2022-09-07 19:28 | 1:04 | 25.8269 | 26.259 | 28.347 | 41.3838 | 44.8997 | 41.4149 | 45.5239 | 39.7593 | 45.5717 | 42.6446 | 42.1655 | 47.6097 | 39.2793 | 42.5408 | 42.6792 | 41.9677 | 40.9319 | 42.5101 | 42.2735 | 44.2842 | 30.1213 | 25.8318 | 34.3396 | 42.0091 | 40.1588 | 46.1494 | 43.6469 | 42.1517 | 40.8163 | 43.7217 | 38.5565 | 43.8967 | 40.6616 | 41.7373 | 38.9646 | 43.8948 | 42.8528 | 43.0878 | 45.7594 | 42.3344 | 43.5259 | 44.8101 | 45.9107 | 42.526 | 45.4044 | 44.457 | 47.2049 | 41.7479 | 45.848 | 43.0988 | 46.6679 | 42.9389 | 46.7328 | 42.7819 | 46.9764 | 42.1723 | 45.6944 | 47.2534 | 92.542 | 92.7078 | 92.8204
2022-09-07 19:28 | 1:04 | 25.9324 | 26.1865 | 28.2431 | 41.3991 | 44.8864 | 41.2415 | 45.5746 | 39.536 | 45.5052 | 42.5068 | 42.081 | 47.4313 | 39.2485 | 42.4418 | 42.6227 | 41.9059 | 40.9316 | 42.331 | 42.2195 | 44.1578 | 30.0586 | 25.7931 | 34.2973 | 41.9511 | 40.0948 | 46.041 | 43.6412 | 42.047 | 40.7668 | 43.5465 | 38.5146 | 43.8883 | 40.6223 | 41.7354 | 38.9691 | 43.7886 | 42.6195 | 43.0319 | 45.5036 | 42.2788 | 43.3344 | 44.6248 | 45.6835 | 42.4353 | 45.2036 | 44.3965 | 47.2079 | 41.6442 | 45.6889 | 43.0253 | 46.528 | 42.9352 | 46.5802 | 42.7148 | 47.2561 | 42.1361 | 45.572 | 47.183 | 92.4685 | 92.5882 | 92.7607
2022-09-07 19:28 | 1:04 | 25.658 | 26.2429 | 28.2063 | 41.2927 | 44.837 | 41.086 | 45.4671 | 39.4913 | 45.4004 | 42.3879 | 42.0856 | 47.3208 | 39.12 | 42.356 | 42.5119 | 41.8324 | 40.8937 | 42.2356 | 42.0853 | 44.0491 | 29.9853 | 25.7351 | 34.218 | 41.8631 | 40.0102 | 45.8951 | 43.56 | 42.1522 | 40.6888 | 43.5447 | 38.467 | 43.7041 | 40.453 | 41.5853 | 38.7709 | 43.565 | 42.6732 | 42.8638 | 45.4635 | 42.2061 | 43.3937 | 44.5846 | 45.7206 | 42.4663 | 45.3673 | 44.3597 | 46.9858 | 41.6154 | 45.9093 | 42.9105 | 46.6407 | 42.8863 | 46.6738 | 42.7557 | 47.1826 | 42.107 | 45.5283 | 47.1105 | 92.3659 | 92.511 | 92.6769
2022-09-07 19:28 | 1:04 | 25.6483 | 26.1027 | 28.1801 | 41.2253 | 44.706 | 41.1017 | 45.514 | 39.5591 | 45.3785 | 42.5712 | 42.1944 | 47.2872 | 39.0714 | 42.1163 | 42.4749 | 41.7725 | 40.7438 | 41.8647 | 42.0064 | 43.9345 | 29.9107 | 25.6775 | 34.1395 | 41.8838 | 39.9451 | 45.9502 | 43.5665 | 42.0751 | 40.7266 | 43.3969 | 38.4114 | 43.7296 | 40.6108 | 41.4656 | 38.6326 | 43.5857 | 42.8094 | 42.8234 | 45.2784 | 42.1595 | 43.2103 | 44.5518 | 45.6224 | 42.269 | 45.2023 | 44.2336 | 46.8942 | 41.6044 | 45.7059 | 42.7986 | 46.7494 | 42.8582 | 46.5622 | 42.6013 | 46.9824 | 41.9158 | 45.5224 | 47.0958 | 92.2053 | 92.3517 | 92.557
2022-09-07 19:29 | 1:05 | 26.1991 | 26.303 | 28.3197 | 41.0683 | 44.675 | 41.1029 | 45.4949 | 39.5187 | 45.2953 | 42.301 | 42.0687 | 47.321 | 39.0282 | 42.2772 | 42.4179 | 41.7209 | 40.7145 | 41.9583 | 41.9779 | 43.9267 | 29.8745 | 25.6266 | 34.0929 | 41.6926 | 39.8961 | 45.7706 | 43.5259 | 42.1745 | 40.5817 | 43.3567 | 38.3764 | 43.7243 | 40.3817 | 41.4132 | 38.7529 | 43.4926 | 42.4467 | 42.7335 | 45.1437 | 41.9987 | 43.2217 | 44.4269 | 45.5517 | 42.3988 | 45.2086 | 44.23 | 46.8479 | 41.4529 | 45.7905 | 42.6554 | 46.7132 | 42.7278 | 46.1972 | 42.4372 | 46.6667 | 41.9161 | 45.3098 | 46.9025 | 92.0668 | 92.1925 | 92.5162
2022-09-07 19:29 | 1:05 | 27.919 | 26.1109 | 28.6807 | 41.0761 | 44.6192 | 41.0258 | 45.2629 | 39.3815 | 45.2257 | 42.1731 | 41.9697 | 47.3839 | 38.9907 | 42.0598 | 42.3361 | 41.6794 | 40.632 | 42.0703 | 41.9271 | 43.8937 | 29.8038 | 25.571 | 33.9793 | 41.6118 | 39.8313 | 45.7468 | 43.3344 | 42.1138 | 40.5187 | 43.2525 | 38.2937 | 43.6454 | 40.3963 | 41.4193 | 38.6295 | 43.4702 | 42.3594 | 42.7923 | 45.315 | 41.8785 | 43.1292 | 44.3909 | 45.4023 | 42.3115 | 45.0259 | 44.1033 | 46.8663 | 41.4068 | 45.5656 | 42.6293 | 46.381 | 42.5586 | 46.3892 | 42.4522 | 46.4569 | 41.838 | 45.1215 | 47.011 | 91.8745 | 92.0628 | 92.2928
2022-09-07 19:29 | 1:05 | 28.7673 | 26.1061 | 28.9094 | 41.0017 | 44.5646 | 40.7855 | 45.3127 | 39.4385 | 45.185 | 41.9908 | 41.9621 | 47.2832 | 38.8934 | 42.1113 | 42.4554 | 41.6326 | 40.6051 | 42.0726 | 42.0624 | 43.8756 | 29.7425 | 25.5551 | 33.8311 | 41.5764 | 39.7315 | 45.7794 | 43.3937 | 41.7154 | 40.3779 | 43.4218 | 38.3436 | 43.5801 | 40.4567 | 41.3673 | 38.5403 | 43.1936 | 42.3752 | 42.7128 | 45.0728 | 41.916 | 43.0546 | 44.2983 | 45.4833 | 42.2424 | 45.0416 | 44.0679 | 46.7821 | 41.2877 | 45.5962 | 42.5073 | 45.9523 | 42.2855 | 45.9674 | 42.2777 | 46.4511 | 41.7034 | 45.3665 | 46.7225 | 91.8042 | 91.9501 | 92.2961
2022-09-07 19:29 | 1:05 | 28.9603 | 26.3233 | 29.5562 | 41.1916 | 44.5973 | 40.7589 | 45.2551 | 39.4689 | 45.1414 | 41.9893 | 42.1305 | 47.1914 | 38.9254 | 42.0299 | 42.2082 | 41.5569 | 40.5628 | 42.1393 | 41.898 | 43.8557 | 29.6747 | 25.6391 | 33.6838 | 41.6125 | 39.6926 | 45.6032 | 43.2103 | 41.802 | 40.404 | 43.164 | 38.2475 | 43.4333 | 40.3278 | 41.2786 | 38.4017 | 43.2218 | 42.2585 | 42.6212 | 44.9638 | 41.7904 | 43.046 | 44.2299 | 45.2763 | 42.0534 | 44.8558 | 43.9806 | 46.4741 | 41.2222 | 45.3429 | 42.5462 | 46.1842 | 42.4208 | 45.9941 | 42.2541 | 46.3663 | 41.6407 | 45.1279 | 46.6363 | 91.6727 | 91.8154 | 92.2752
2022-09-07 19:29 | 1:05 | 29.5161 | 26.4858 | 30.7068 | 41.1792 | 44.6088 | 40.7936 | 45.2596 | 39.3958 | 45.0739 | 42.1772 | 42.0055 | 47.2301 | 39.0399 | 42.0836 | 42.3262 | 41.495 | 40.5993 | 42.0105 | 41.8534 | 43.9182 | 29.6061 | 25.6231 | 33.5803 | 41.4712 | 39.6332 | 45.5201 | 43.2217 | 41.5613 | 40.3563 | 43.1431 | 38.1607 | 43.3794 | 40.2679 | 41.2394 | 38.4083 | 43.539 | 42.1238 | 42.4785 | 45.1362 | 41.7652 | 42.9259 | 44.2114 | 45.3651 | 41.9839 | 44.7871 | 43.9103 | 46.3361 | 41.1947 | 45.3053 | 42.4875 | 46.2795 | 42.3233 | 46.0762 | 42.1741 | 46.6174 | 41.6311 | 45.1337 | 46.7334 | 91.5668 | 91.7633 | 92.2211
2022-09-07 19:29 | 1:05 | 30.2574 | 26.4988 | 31.0011 | 41.3845 | 44.5472 | 40.9065 | 45.327 | 39.3313 | 45.0608 | 42.2327 | 42.0797 | 47.1302 | 39.152 | 41.9326 | 42.3727 | 41.5249 | 40.6251 | 41.9321 | 41.8596 | 43.9073 | 29.5566 | 25.5819 | 33.4702 | 41.3476 | 39.5438 | 45.3024 | 43.1292 | 41.5399 | 40.3559 | 43.0457 | 38.0693 | 43.3176 | 40.2378 | 41.2765 | 38.383 | 43.4764 | 42.3809 | 42.5485 | 45.0748 | 41.8665 | 42.6726 | 44.1401 | 45.3253 | 41.9829 | 44.8222 | 43.8251 | 46.2324 | 41.1456 | 45.3372 | 42.3567 | 46.0964 | 42.1024 | 46.0108 | 41.9829 | 46.4611 | 41.5594 | 45.0076 | 46.7715 | 91.6771 | 91.7692 | 92.2088
2022-09-07 19:30 | 1:05 | 30.4543 | 26.5501 | 30.9459 | 41.3197 | 44.5397 | 41.0285 | 45.244 | 39.33 | 45.011 | 42.3285 | 42.0108 | 47.0787 | 39.0564 | 41.8977 | 42.2704 | 41.5038 | 40.5958 | 41.9203 | 41.8461 | 43.8179 | 29.4923 | 25.527 | 33.4114 | 41.3984 | 39.4801 | 45.2766 | 43.0546 | 41.4313 | 40.2758 | 42.9643 | 38.0748 | 43.4183 | 40.1327 | 41.2888 | 38.3752 | 43.2345 | 42.1236 | 42.5445 | 45.0016 | 41.7251 | 42.7157 | 44.0245 | 45.0374 | 41.8914 | 44.5235 | 43.7344 | 46.3147 | 41.0556 | 45.0266 | 42.2853 | 45.4409 | 42.1866 | 45.9535 | 42.1443 | 46.1908 | 41.5111 | 45.0666 | 46.6362 | 91.7593 | 91.8487 | 92.2949
2022-09-07 19:30 | 1:06 | 30.4211 | 26.5341 | 30.6178 | 41.2621 | 44.5113 | 40.8487 | 45.2179 | 39.2732 | 44.9734 | 42.075 | 41.8284 | 46.8531 | 39.0067 | 41.865 | 42.1852 | 41.4263 | 40.5734 | 41.9628 | 41.7394 | 43.8559 | 29.5 | 25.5342 | 33.3746 | 41.3146 | 39.4216 | 45.3351 | 43.046 | 41.4121 | 40.1477 | 42.9115 | 37.9605 | 43.2982 | 40.1702 | 41.2746 | 38.2652 | 43.1249 | 42.1129 | 42.4287 | 44.8773 | 41.6393 | 42.6535 | 44.0051 | 45.0309 | 41.8894 | 44.4923 | 43.6274 | 46.4436 | 41.0379 | 45.1326 | 42.2253 | 45.8316 | 41.9627 | 45.9385 | 42.0739 | 46.1129 | 41.4279 | 44.995 | 46.3796 | 91.8404 | 91.9351 | 92.3404
2022-09-07 19:30 | 1:06 | 30.2651 | 26.549 | 30.4307 | 41.137 | 44.4448 | 40.7703 | 45.121 | 39.1946 | 44.8655 | 41.921 | 41.9299 | 46.8732 | 38.9175 | 41.8101 | 42.0617 | 41.3789 | 40.5147 | 41.8554 | 41.737 | 43.5557 | 29.456 | 25.4741 | 33.3438 | 41.2871 | 39.3884 | 45.2213 | 42.9259 | 41.4943 | 40.1174 | 42.7972 | 37.8852 | 43.2572 | 40.1914 | 41.1588 | 38.137 | 43.0984 | 42.0796 | 42.3597 | 44.8233 | 41.6219 | 42.6035 | 43.8727 | 45.035 | 41.7723 | 44.4873 | 43.5869 | 46.2186 | 40.9095 | 44.8239 | 42.2607 | 45.3807 | 42.0029 | 45.8302 | 42.0825 | 46.2145 | 41.4042 | 44.8856 | 46.4361 | 91.9381 | 92.0649 | 92.3863
2022-09-07 19:30 | 1:06 | 30.1727 | 26.5675 | 30.5131 | 41.0737 | 44.3971 | 40.7946 | 45.1673 | 39.1801 | 44.8248 | 41.8373 | 41.5345 | 46.7859 | 38.9526 | 41.9265 | 42.0497 | 41.318 | 40.4579 | 41.8131 | 41.6449 | 43.7028 | 29.4636 | 25.5239 | 33.3555 | 41.2471 | 39.3142 | 45.4128 | 42.6726 | 41.6247 | 40.0167 | 42.7465 | 37.7388 | 43.0798 | 39.9635 | 41.087 | 38.0934 | 43.0294 | 42.0015 | 42.246 | 44.7835 | 41.5367 | 42.5779 | 43.8234 | 44.9286 | 41.6555 | 44.3815 | 43.5243 | 46.056 | 40.7882 | 44.9339 | 42.0635 | 45.8811 | 41.8443 | 45.7711 | 41.9001 | 46.2354 | 41.3629 | 44.6949 | 46.4648 | 92.0624 | 92.1388 | 92.4454
2022-09-07 19:30 | 1:06 | 30.0202 | 26.6338 | 30.425 | 41.0054 | 44.3827 | 40.6606 | 45.166 | 39.1564 | 44.8274 | 41.8355 | 42.0938 | 46.8461 | 38.8467 | 41.8285 | 42.0479 | 41.2634 | 40.4131 | 41.5719 | 41.6667 | 43.5012 | 29.4503 | 25.6819 | 33.2969 | 41.2376 | 39.2892 | 45.0262 | 42.7157 | 41.6284 | 39.8865 | 42.7386 | 37.8149 | 43.113 | 39.8252 | 41.0367 | 38.0367 | 43.0026 | 41.935 | 42.218 | 44.699 | 41.5281 | 42.5667 | 43.7839 | 44.8908 | 41.6339 | 44.2733 | 43.446 | 46.1277 | 40.7978 | 44.8083 | 41.963 | 45.6838 | 41.8663 | 45.7564 | 41.9173 | 46.2652 | 41.2113 | 44.5285 | 46.4046 | 92.1519 | 92.1927 | 92.484
2022-09-07 19:30 | 1:06 | 29.8274 | 26.6151 | 30.2613 | 40.9382 | 44.4079 | 40.6859 | 44.9202 | 39.1478 | 44.742 | 41.7466 | 41.6521 | 46.7407 | 38.7739 | 41.7346 | 41.945 | 41.2399 | 40.3165 | 41.6436 | 41.5757 | 43.5423 | 29.4738 | 25.6113 | 33.3941 | 41.1236 | 39.2637 | 44.9558 | 42.6535 | 41.3682 | 39.8925 | 42.6237 | 37.7167 | 43.0318 | 39.8102 | 40.96 | 38.0012 | 43.1217 | 42.1093 | 42.163 | 44.7775 | 41.5242 | 42.4889 | 43.7415 | 44.8888 | 41.5374 | 44.1782 | 43.3793 | 46.0641 | 40.7927 | 44.9632 | 41.8913 | 45.609 | 41.7436 | 45.5647 | 41.7999 | 46.1587 | 41.1027 | 44.4956 | 46.4832 | 92.3157 | 92.3436 | 92.637
2022-09-07 19:31 | 1:07 | 29.6127 | 26.6089 | 30.0923 | 40.991 | 44.2522 | 40.5319 | 44.9813 | 39.0909 | 44.716 | 41.6518 | 41.5876 | 46.7615 | 38.7161 | 41.7073 | 41.8313 | 41.1966 | 40.2839 | 41.7562 | 41.41 | 43.498 | 29.5099 | 25.6143 | 33.4761 | 41.0769 | 39.1982 | 44.8975 | 42.6035 | 41.2711 | 39.9082 | 42.6369 | 37.7133 | 42.8223 | 39.7757 | 40.9159 | 38.0066 | 42.99 | 41.7325 | 42.0758 | 44.3783 | 41.3755 | 42.259 | 43.6211 | 44.7979 | 41.5528 | 44.2426 | 43.2825 | 45.9702 | 40.7376 | 44.8815 | 41.8094 | 45.513 | 41.7989 | 45.6532 | 41.699 | 46.1692 | 41.0632 | 44.7571 | 46.1754 | 92.4639 | 92.5173 | 92.7449
2022-09-07 19:31 | 1:07 | 29.3464 | 26.6342 | 29.9753 | 40.8881 | 44.1984 | 40.558 | 44.7555 | 39.024 | 44.7181 | 41.5619 | 41.503 | 46.5602 | 38.6992 | 41.5179 | 41.8651 | 41.076 | 40.2352 | 41.5696 | 41.407 | 43.504 | 29.5542 | 25.6729 | 33.4885 | 40.9391 | 39.1339 | 44.8783 | 42.5779 | 41.0996 | 39.7621 | 42.5582 | 37.6348 | 42.7404 | 39.802 | 40.7967 | 37.8514 | 42.8151 | 41.9118 | 42.1328 | 44.4706 | 41.3117 | 42.3123 | 43.6148 | 44.6397 | 41.4421 | 44.0674 | 43.2527 | 45.8964 | 40.6555 | 44.9659 | 41.821 | 45.5705 | 41.6915 | 45.3274 | 41.6707 | 46.0197 | 41.0609 | 44.4369 | 46.0628 | 92.588 | 92.6463 | 92.7619
2022-09-07 19:31 | 1:07 | 29.0521 | 26.5885 | 29.6944 | 40.6719 | 44.253 | 40.3396 | 44.8529 | 38.9371 | 44.6294 | 41.6536 | 41.7006 | 46.5592 | 38.6225 | 41.5599 | 41.7409 | 41.0638 | 40.2271 | 41.4833 | 41.3848 | 43.2956 | 29.51 | 25.7567 | 33.4629 | 40.9951 | 39.0746 | 44.8181 | 42.5667 | 41.2023 | 39.7923 | 42.5959 | 37.4988 | 42.6075 | 39.6005 | 40.8184 | 37.7993 | 42.8225 | 41.8839 | 42.0014 | 44.5171 | 41.3198 | 42.2153 | 43.4871 | 44.5824 | 41.447 | 43.999 | 43.1785 | 45.6716 | 40.6686 | 44.8773 | 41.7292 | 45.1162 | 41.5806 | 45.3233 | 41.5907 | 45.7415 | 40.9631 | 44.4187 | 45.9307 | 92.6243 | 92.7327 | 92.8046
2022-09-07 19:31 | 1:07 | 28.745 | 26.5804 | 29.3945 | 40.6822 | 44.1713 | 40.3167 | 44.8173 | 38.9429 | 44.6035 | 41.3074 | 41.5323 | 46.586 | 38.58 | 41.525 | 41.6955 | 41.0369 | 40.176 | 41.5722 | 41.2687 | 43.0819 | 29.5548 | 26.0247 | 33.3777 | 40.9064 | 39.0159 | 44.5002 | 42.4889 | 41.1691 | 39.7078 | 42.4434 | 37.6058 | 42.5116 | 39.6864 | 40.6405 | 37.7337 | 42.6842 | 41.7686 | 41.8346 | 44.4137 | 41.3746 | 42.1875 | 43.4263 | 44.4519 | 41.3867 | 44.0575 | 43.1245 | 45.5609 | 40.6105 | 44.6546 | 41.6216 | 45.3146 | 41.4396 | 45.3354 | 41.5245 | 45.7259 | 40.9026 | 44.3969 | 46.0483 | 92.7605 | 92.7877 | 92.8167
2022-09-07 19:31 | 1:07 | 28.3582 | 26.455 | 29.1284 | 40.5773 | 44.0894 | 40.3167 | 44.8251 | 38.9502 | 44.5372 | 41.4482 | 41.7185 | 46.6028 | 38.5696 | 41.3308 | 41.5833 | 40.9649 | 40.127 | 41.3372 | 41.2244 | 43.2347 | 29.4705 | 25.5046 | 33.3734 | 40.8829 | 38.9386 | 44.5617 | 42.259 | 41.0666 | 39.7631 | 42.3266 | 37.5719 | 42.5506 | 39.5444 | 40.6165 | 37.7333 | 42.6833 | 41.8474 | 41.7817 | 44.2552 | 41.2348 | 41.9916 | 43.4173 | 44.4087 | 41.3264 | 43.8208 | 43.0802 | 45.4205 | 40.5143 | 44.6848 | 41.5485 | 45.4098 | 41.371 | 45.331 | 41.469 | 45.6024 | 40.8134 | 44.2968 | 45.8576 | 92.8662 | 92.8498 | 92.9367
2022-09-07 19:31 | 1:07 | 27.3156 | 26.4184 | 28.7508 | 40.4667 | 43.9543 | 40.302 | 44.6529 | 38.8412 | 44.4585 | 41.4655 | 41.5551 | 46.4924 | 38.446 | 41.1507 | 41.6298 | 40.8986 | 39.9389 | 41.2481 | 41.1429 | 43.2173 | 29.4692 | 25.3871 | 33.4482 | 40.8342 | 38.8981 | 44.4562 | 42.3123 | 40.9087 | 39.6627 | 42.3263 | 37.4635 | 42.5817 | 39.5096 | 40.4958 | 37.6765 | 42.5646 | 41.5195 | 41.7604 | 44.0762 | 41.1055 | 41.9999 | 43.4051 | 44.4393 | 41.3127 | 43.7804 | 42.9656 | 45.4178 | 40.4571 | 44.4998 | 41.5323 | 45.1613 | 41.4313 | 45.1264 | 41.3789 | 45.4624 | 40.8221 | 44.187 | 45.7422 | 92.9333 | 93.0349 | 92.931
2022-09-07 19:32 | 1:08 | 26.2636 | 26.3138 | 28.4187 | 40.4101 | 43.9419 | 40.1621 | 44.5693 | 38.7321 | 44.3767 | 41.5536 | 41.3407 | 46.2889 | 38.3039 | 41.4123 | 41.6246 | 40.8417 | 39.9433 | 41.293 | 41.0993 | 43.0088 | 29.5371 | 25.367 | 33.4955 | 40.6443 | 38.8359 | 44.404 | 42.2153 | 40.8486 | 39.587 | 42.167 | 37.4228 | 42.5807 | 39.5297 | 40.4462 | 37.6236 | 42.3456 | 41.4632 | 41.7374 | 43.9862 | 40.9646 | 41.9904 | 43.3103 | 44.3002 | 41.186 | 43.8977 | 42.8768 | 45.4204 | 40.4593 | 44.359 | 41.5359 | 45.0035 | 41.4484 | 45.0269 | 41.2038 | 45.4349 | 40.7881 | 44.0063 | 45.7921 | 93.0374 | 93.1129 | 93.0449
2022-09-07 19:32 | 1:08 | 25.4931 | 26.2179 | 28.1568 | 40.4977 | 43.9185 | 40.1421 | 44.3854 | 38.6579 | 44.3273 | 41.3582 | 41.2548 | 46.2804 | 38.2001 | 41.3088 | 41.5726 | 40.7703 | 39.8546 | 40.9326 | 41.0497 | 42.9128 | 29.585 | 25.2158 | 33.5069 | 40.7024 | 38.8023 | 44.5229 | 42.1875 | 40.8592 | 39.5743 | 42.1315 | 37.5144 | 42.5888 | 39.5104 | 40.3423 | 37.5247 | 42.4144 | 41.4335 | 41.815 | 44.0757 | 40.9347 | 41.9996 | 43.2594 | 44.3849 | 41.0578 | 43.7919 | 42.796 | 45.5309 | 40.3735 | 44.2022 | 41.5054 | 44.4797 | 41.4796 | 44.9632 | 41.1843 | 45.1423 | 40.6873 | 43.9396 | 45.8624 | 93.1891 | 93.2764 | 93.0265
2022-09-07 19:32 | 1:08 | 25.16 | 26.0749 | 28.0633 | 40.2106 | 43.8137 | 39.9781 | 44.3796 | 38.6825 | 44.2895 | 41.394 | 41.0726 | 46.1062 | 38.1877 | 41.1655 | 41.3812 | 40.6919 | 39.8306 | 41.0474 | 41.0655 | 42.6881 | 29.5766 | 25.1439 | 33.4242 | 40.7268 | 38.7412 | 44.4242 | 41.9916 | 40.6897 | 39.5226 | 42.0591 | 37.2607 | 42.4488 | 39.3243 | 40.3041 | 37.4777 | 42.142 | 41.3641 | 41.5657 | 43.8561 | 40.8807 | 41.9303 | 43.2071 | 44.1689 | 41.0428 | 43.8044 | 42.6888 | 45.4447 | 40.231 | 44.0476 | 41.3456 | 44.9625 | 41.5639 | 44.9306 | 41.3263 | 45.3171 | 40.7382 | 43.8004 | 45.7726 | 93.3284 | 93.3307 | 93.2179
2022-09-07 19:32 | 1:08 | 25.0207 | 25.9045 | 27.9246 | 40.3015 | 43.7669 | 39.7914 | 44.3071 | 38.5372 | 44.215 | 41.2791 | 40.9667 | 46.1769 | 38.1366 | 40.8181 | 41.4318 | 40.6545 | 39.7223 | 40.5874 | 40.9083 | 42.9371 | 29.5137 | 25.0478 | 33.395 | 40.5425 | 38.6681 | 44.2708 | 41.9999 | 40.9352 | 39.4108 | 41.989 | 37.1421 | 42.4085 | 39.2495 | 40.308 | 37.5315 | 42.1085 | 41.5495 | 41.5671 | 43.7598 | 40.9719 | 41.8053 | 43.1402 | 44.1942 | 41.0245 | 43.6273 | 42.6639 | 45.2768 | 40.1647 | 44.3055 | 41.1414 | 45.2197 | 41.3316 | 44.9599 | 41.1643 | 45.3274 | 40.7036 | 43.8792 | 45.5593 | 93.4837 | 93.5272 | 93.2984
2022-09-07 19:32 | 1:08 | 24.9633 | 25.8148 | 27.7265 | 40.1163 | 43.6508 | 39.8875 | 44.2455 | 38.5834 | 44.131 | 41.2591 | 41.191 | 46.0716 | 38.0651 | 40.8529 | 41.2659 | 40.5546 | 39.6912 | 40.7334 | 40.7997 | 42.8367 | 29.4554 | 24.976 | 33.306 | 40.538 | 38.6386 | 44.4279 | 41.9904 | 40.7465 | 39.3367 | 41.923 | 37.1838 | 42.2863 | 39.2231 | 40.1787 | 37.3817 | 42.074 | 41.2993 | 41.3803 | 43.6859 | 40.7483 | 41.7425 | 43.0487 | 44.0688 | 40.9464 | 43.6056 | 42.6254 | 45.2984 | 40.18 | 44.112 | 41.2765 | 44.7799 | 41.3272 | 44.983 | 41.1402 | 45.2181 | 40.5572 | 43.8156 | 45.6281 | 93.6167 | 93.6711 | 93.4313
2022-09-07 19:32 | 1:08 | 24.7904 | 25.6979 | 27.5804 | 40.1461 | 43.6271 | 39.9965 | 44.1384 | 38.3969 | 44.0448 | 41.2051 | 40.9118 | 45.9112 | 37.932 | 40.7546 | 41.2812 | 40.5051 | 39.5341 | 40.6544 | 40.715 | 42.8069 | 29.3394 | 24.9309 | 33.2332 | 40.3911 | 38.5498 | 44.5084 | 41.9996 | 40.3645 | 39.2678 | 41.8895 | 36.931 | 42.2271 | 39.0917 | 40.1325 | 37.3842 | 42.0319 | 41.207 | 41.3143 | 43.4183 | 40.7621 | 41.5142 | 42.9247 | 43.866 | 40.9092 | 43.462 | 42.5827 | 45.2189 | 40.0875 | 44.216 | 41.0425 | 44.9547 | 41.1894 | 44.888 | 41.0807 | 45.2125 | 40.5052 | 43.8247 | 45.2343 | 93.749 | 93.8738 | 93.474
2022-09-07 19:33 | 1:08 | 24.7252 | 25.5979 | 27.5873 | 39.9871 | 43.5606 | 39.9566 | 44.1498 | 38.3851 | 44.0262 | 41.0179 | 40.8418 | 45.9096 | 37.8983 | 40.7851 | 41.122 | 40.393 | 39.5115 | 40.6661 | 40.6564 | 42.6166 | 29.2781 | 24.8992 | 33.1624 | 40.4134 | 38.5172 | 44.2624 | 41.9303 | 40.4982 | 39.2561 | 41.8473 | 36.937 | 42.2175 | 39.166 | 40.0421 | 37.3254 | 41.8394 | 41.0607 | 41.3218 | 43.6405 | 40.6502 | 41.5299 | 42.8729 | 43.9128 | 40.9111 | 43.569 | 42.4821 | 45.0692 | 40.052 | 44.017 | 41.1465 | 44.8964 | 40.9919 | 44.8081 | 40.9878 | 45.2871 | 40.4205 | 43.7791 | 45.1942 | 93.8613 | 93.9989 | 93.5081
2022-09-07 19:33 | 1:09 | 24.6848 | 25.4808 | 27.535 | 39.8305 | 43.4984 | 39.7095 | 43.9214 | 38.3153 | 43.9635 | 40.9454 | 40.8821 | 45.9607 | 37.8911 | 40.9299 | 41.0265 | 40.369 | 39.4908 | 40.8443 | 40.5926 | 42.5123 | 29.1501 | 24.8488 | 33.0641 | 40.3045 | 38.4469 | 44.1189 | 41.8053 | 40.4037 | 39.1596 | 41.8824 | 36.9306 | 41.9444 | 39.0053 | 40.0491 | 37.2675 | 41.6679 | 41.1228 | 41.2146 | 43.411 | 40.6081 | 41.529 | 42.8216 | 43.968 | 40.7824 | 43.5245 | 42.3879 | 44.9331 | 39.9882 | 43.8195 | 40.9842 | 44.366 | 41.0125 | 44.7734 | 40.9166 | 45.1788 | 40.3258 | 43.5304 | 45.2851 | 94.0638 | 94.1462 | 93.5181
2022-09-07 19:33 | 1:09 | 24.9518 | 25.3978 | 27.4347 | 39.8475 | 43.4869 | 39.7675 | 44.0763 | 38.2721 | 43.9212 | 40.9489 | 40.993 | 45.7652 | 37.768 | 40.6037 | 41.0446 | 40.3294 | 39.3816 | 40.5999 | 40.6297 | 42.5235 | 29.0641 | 24.8976 | 32.9934 | 40.2725 | 38.3787 | 44.0521 | 41.7425 | 40.2702 | 39.026 | 41.6649 | 36.932 | 41.9929 | 38.9203 | 39.9149 | 37.2787 | 41.7051 | 41.03 | 41.1519 | 43.4399 | 40.5411 | 41.5065 | 42.7876 | 43.8306 | 40.7178 | 43.3539 | 42.3338 | 44.954 | 39.9256 | 43.9062 | 40.926 | 44.3641 | 41.0878 | 44.5833 | 40.9867 | 44.9144 | 40.3038 | 43.4935 | 45.2429 | 94.2646 | 94.3738 | 93.7868
2022-09-07 19:33 | 1:09 | 24.7498 | 25.315 | 27.3732 | 39.8435 | 43.3993 | 39.7981 | 44.0021 | 38.0627 | 43.7963 | 40.7514 | 40.6599 | 45.7889 | 37.6629 | 40.7457 | 40.9186 | 40.2705 | 39.2868 | 40.5053 | 40.5048 | 42.5043 | 29.0801 | 24.7717 | 33.0352 | 40.1476 | 38.3322 | 43.959 | 41.5142 | 40.3273 | 39.0007 | 41.6835 | 37.1164 | 42.0341 | 38.8917 | 39.9166 | 37.1064 | 41.791 | 40.8801 | 41.15 | 43.4715 | 40.4445 | 41.4528 | 42.6706 | 43.7456 | 40.7274 | 43.3038 | 42.3364 | 44.7402 | 40.015 | 43.7767 | 40.874 | 44.3315 | 40.9759 | 44.6561 | 40.6905 | 44.8769 | 40.2533 | 43.6128 | 45.201 | 94.4493 | 94.448 | 93.9416
2022-09-07 19:33 | 1:09 | 25.0074 | 25.2858 | 27.3268 | 39.7908 | 43.3446 | 39.6176 | 43.9293 | 38.0855 | 43.791 | 40.6833 | 40.8755 | 45.6434 | 37.618 | 40.6053 | 40.87 | 40.1267 | 39.2014 | 40.4005 | 40.4385 | 42.3631 | 29.2587 | 24.7864 | 33.289 | 40.1297 | 38.3125 | 43.8583 | 41.5299 | 40.1539 | 39.0302 | 41.5131 | 36.9397 | 41.9768 | 38.8256 | 39.8725 | 37.1308 | 41.8741 | 40.9656 | 41.0841 | 43.5029 | 40.4203 | 41.4461 | 42.7215 | 43.7386 | 40.6463 | 43.2866 | 42.2418 | 44.7289 | 39.8908 | 43.7927 | 40.9893 | 44.2374 | 40.8596 | 44.4798 | 40.8032 | 44.9231 | 40.3037 | 43.5538 | 45.0907 | 94.5992 | 94.6079 | 93.9865
2022-09-07 19:33 | 1:09 | 24.5052 | 25.131 | 27.2116 | 39.7488 | 43.3678 | 39.3311 | 43.7471 | 38.015 | 43.6869 | 40.7763 | 40.5742 | 45.645 | 37.5316 | 40.4419 | 40.9329 | 40.0641 | 39.2033 | 40.446 | 40.3736 | 42.423 | 29.6012 | 24.9691 | 33.7206 | 40.1453 | 38.2788 | 43.8206 | 41.529 | 40.0606 | 39.0337 | 41.4452 | 36.9296 | 41.911 | 38.8903 | 39.7877 | 37.158 | 41.6038 | 40.9449 | 41.1142 | 43.4183 | 40.3611 | 41.3352 | 42.6782 | 43.6188 | 40.7782 | 43.1573 | 42.1952 | 44.7343 | 39.8963 | 44.049 | 40.7424 | 44.3641 | 40.7888 | 44.438 | 40.6733 | 45.013 | 40.2354 | 43.598 | 44.9519 | 94.7267 | 94.7527 | 94.0782
2022-09-07 19:34 | 1:10 | 25.0543 | 25.1882 | 27.2081 | 39.7071 | 43.2829 | 39.5285 | 43.6544 | 37.9093 | 43.6092 | 40.6794 | 40.5739 | 45.5384 | 37.5204 | 40.517 | 40.7078 | 40.0165 | 39.0786 | 40.2556 | 40.3987 | 42.2762 | 29.8973 | 25.0189 | 33.8503 | 40.2166 | 38.2149 | 43.924 | 41.5065 | 40.1818 | 38.9129 | 41.4689 | 37.0827 | 41.7416 | 38.7163 | 39.7917 | 37.1611 | 41.6453 | 40.8636 | 40.9916 | 43.4022 | 40.3498 | 41.3098 | 42.6801 | 43.5423 | 40.6765 | 43.1629 | 42.1515 | 44.67 | 39.8409 | 43.6302 | 40.8315 | 43.9081 | 40.7359 | 44.3063 | 40.6472 | 44.9568 | 40.143 | 43.4307 | 44.9951 | 94.7996 | 94.8515 | 94.1068
2022-09-07 19:34 | 1:10 | 24.44 | 25.0514 | 27.1104 | 39.6213 | 43.2672 | 39.329 | 43.5901 | 37.8343 | 43.5684 | 40.7555 | 40.5176 | 45.5766 | 37.4138 | 40.5168 | 40.7167 | 39.9941 | 39.0741 | 40.2866 | 40.2727 | 42.4162 | 30.1059 | 24.9579 | 33.8433 | 40.1681 | 38.1751 | 43.955 | 41.4528 | 40.059 | 38.9491 | 41.4072 | 37.0045 | 41.6917 | 38.6574 | 39.7328 | 37.1068 | 41.5859 | 40.785 | 40.9119 | 43.1282 | 40.2867 | 41.3163 | 42.6245 | 43.5762 | 40.4723 | 43.1438 | 42.062 | 44.6682 | 39.8041 | 43.5155 | 40.8409 | 43.9263 | 40.6368 | 44.4677 | 40.6647 | 44.7998 | 40.1916 | 43.5839 | 44.8788 | 94.8342 | 94.9806 | 94.1943
2022-09-07 19:34 | 1:10 | 24.4702 | 25.0562 | 27.0664 | 39.5858 | 43.1388 | 39.2726 | 43.3118 | 37.8688 | 43.5231 | 40.4024 | 40.4695 | 45.4504 | 37.3937 | 40.5135 | 40.6615 | 39.9001 | 38.9974 | 40.1344 | 40.2316 | 42.1032 | 30.1389 | 24.8278 | 33.8039 | 40.1465 | 38.1359 | 44.098 | 41.4461 | 39.8789 | 38.8928 | 41.3206 | 36.906 | 41.6161 | 38.6667 | 39.7204 | 37.0918 | 41.5514 | 40.6771 | 40.9117 | 43.0472 | 40.2174 | 41.2694 | 42.6012 | 43.587 | 40.414 | 43.1883 | 41.9822 | 44.6007 | 39.8512 | 43.5136 | 40.8222 | 43.7882 | 40.8261 | 44.4006 | 40.6037 | 44.7317 | 40.0997 | 43.5825 | 44.6658 | 94.9079 | 95.0412 | 94.2373
2022-09-07 19:34 | 1:10 | 24.4199 | 25.001 | 27.0204 | 39.5248 | 43.1005 | 39.2871 | 43.4951 | 37.7275 | 43.4318 | 40.2963 | 40.3509 | 45.3747 | 37.3269 | 40.5037 | 40.6783 | 39.885 | 38.9618 | 40.3538 | 40.0632 | 42.11 | 30.0556 | 24.8201 | 33.5479 | 40.0003 | 38.0988 | 44.1007 | 41.3352 | 39.9112 | 38.74 | 41.2723 | 36.7174 | 41.6112 | 38.5914 | 39.6424 | 37.0644 | 41.4076 | 40.7836 | 40.8445 | 43.0011 | 40.2255 | 41.1955 | 42.4358 | 43.5536 | 40.3867 | 43.1319 | 41.9201 | 44.5679 | 39.6346 | 43.4633 | 40.6888 | 43.8047 | 40.8186 | 44.227 | 40.6616 | 44.5136 | 40.1109 | 43.5103 | 44.7619 | 94.8881 | 94.9695 | 94.2044
2022-09-07 19:34 | 1:10 | 24.45 | 24.9437 | 26.9827 | 39.3224 | 43.0457 | 38.9644 | 43.4461 | 37.7062 | 43.4321 | 40.1657 | 40.1657 | 45.379 | 37.2872 | 40.2355 | 40.7289 | 39.7986 | 38.8655 | 40.1188 | 40.0874 | 42.0007 | 29.9274 | 24.7507 | 33.3692 | 39.9305 | 38.0343 | 43.7612 | 41.3098 | 39.8437 | 38.6414 | 41.2139 | 36.6055 | 41.4816 | 38.608 | 39.5825 | 37.2416 | 41.2233 | 40.8886 | 40.7741 | 43.251 | 40.4257 | 41.1122 | 42.3731 | 43.4512 | 40.3358 | 43.0728 | 41.9239 | 44.4365 | 39.6388 | 43.3989 | 40.561 | 43.6515 | 40.8921 | 44.0982 | 40.6438 | 44.3523 | 40.0612 | 43.4342 | 44.8079 | 94.6622 | 94.8202 | 94.0444
2022-09-07 19:34 | 1:10 | 24.4702 | 24.9027 | 26.928 | 39.4427 | 43.0662 | 38.6644 | 43.5278 | 37.6689 | 43.3287 | 40.1759 | 40.3112 | 45.2931 | 37.2044 | 40.0994 | 40.6163 | 39.7447 | 38.819 | 39.9733 | 39.9662 | 41.9333 | 29.763 | 24.7678 | 33.2039 | 39.8961 | 37.9523 | 43.7004 | 41.3163 | 39.9214 | 38.5714 | 41.1666 | 36.4865 | 41.484 | 38.5129 | 39.5769 | 37.0136 | 41.3458 | 40.7846 | 40.7829 | 42.8928 | 40.3295 | 40.9528 | 42.2904 | 43.2925 | 40.2468 | 42.9124 | 41.8477 | 44.4275 | 39.6527 | 43.4462 | 40.5321 | 43.8944 | 40.7734 | 43.9491 | 40.3651 | 44.4269 | 39.9354 | 43.345 | 44.6245 | 94.3845 | 94.6779 | 93.8529
2022-09-07 19:35 | 1:10 | 24.5142 | 24.8518 | 26.8868 | 39.2122 | 42.9569 | 39.0001 | 43.4473 | 37.5893 | 43.3342 | 40.2481 | 40.2362 | 45.1452 | 37.0701 | 40.1371 | 40.386 | 39.6961 | 38.7244 | 39.8514 | 39.8747 | 41.8992 | 29.5825 | 24.6749 | 33.1153 | 39.8362 | 37.8931 | 43.6704 | 41.2694 | 39.7743 | 38.5646 | 41.1627 | 36.5046 | 41.364 | 38.3226 | 39.466 | 36.9942 | 41.2308 | 40.6896 | 40.6266 | 42.9976 | 40.2353 | 40.8311 | 42.236 | 43.2323 | 40.2689 | 42.7735 | 41.747 | 44.2358 | 39.5174 | 43.4575 | 40.3949 | 44.0098 | 40.6579 | 43.947 | 40.3817 | 44.484 | 39.912 | 43.175 | 44.5635 | 94.211 | 94.4721 | 93.7172
2022-09-07 19:35 | 1:11 | 24.8927 | 24.8264 | 26.908 | 39.2838 | 42.9074 | 39.0995 | 43.324 | 37.4333 | 43.2104 | 39.9641 | 39.9721 | 44.9769 | 37.1406 | 40.0309 | 40.3285 | 39.6538 | 38.6755 | 39.794 | 39.8962 | 41.7859 | 29.4123 | 24.7218 | 32.9764 | 39.7773 | 37.8517 | 43.3769 | 41.1955 | 39.8896 | 38.5067 | 41.0827 | 36.497 | 41.2604 | 38.4025 | 39.4082 | 36.8753 | 41.0942 | 40.6365 | 40.6065 | 42.7362 | 40.1653 | 40.8151 | 42.2099 | 43.1547 | 40.1962 | 42.7896 | 41.7706 | 44.2652 | 39.4983 | 43.3695 | 40.3774 | 43.6627 | 40.6543 | 44.1051 | 40.2584 | 44.3748 | 39.7931 | 43.2286 | 44.3478 | 94.0536 | 94.2639 | 93.6406
2022-09-07 19:35 | 1:11 | 24.936 | 24.7192 | 26.8801 | 39.054 | 42.7111 | 38.9512 | 43.3719 | 37.5561 | 43.1985 | 39.9535 | 40.2255 | 44.9937 | 37.0612 | 39.9273 | 40.2064 | 39.5942 | 38.625 | 39.7937 | 39.7874 | 41.9576 | 29.2383 | 24.5793 | 32.8884 | 39.6602 | 37.8036 | 43.2951 | 41.1122 | 39.486 | 38.3993 | 40.9616 | 36.3796 | 41.2495 | 38.274 | 39.3035 | 36.6731 | 40.88 | 40.4262 | 40.522 | 42.5354 | 40.018 | 40.8094 | 42.2407 | 43.0633 | 40.1731 | 42.8019 | 41.6337 | 44.1567 | 39.4362 | 43.136 | 40.3521 | 43.3052 | 40.4014 | 43.8541 | 40.1835 | 44.2955 | 39.8334 | 43.0616 | 44.3963 | 93.9465 | 94.0648 | 93.5624
2022-09-07 19:35 | 1:11 | 25.1631 | 24.7319 | 26.8236 | 39.1943 | 42.7492 | 38.9595 | 43.178 | 37.3387 | 43.0891 | 39.9244 | 39.8934 | 44.9485 | 37.0037 | 39.8615 | 40.2004 | 39.567 | 38.6289 | 39.6383 | 39.7468 | 41.7142 | 29.1093 | 24.5606 | 32.8126 | 39.695 | 37.7327 | 43.3246 | 40.9528 | 39.703 | 38.3341 | 40.9418 | 36.2732 | 41.205 | 38.2253 | 39.2437 | 36.6948 | 40.935 | 40.4144 | 40.4603 | 42.5944 | 40.0049 | 40.7039 | 42.0713 | 42.9669 | 39.9481 | 42.6559 | 41.5828 | 44.1706 | 39.351 | 43.0606 | 40.2118 | 43.0978 | 40.4598 | 43.755 | 40.0688 | 44.2708 | 39.7681 | 42.9078 | 44.4028 | 93.8655 | 93.9334 | 93.5535
2022-09-07 19:35 | 1:11 | 25.0366 | 24.7136 | 26.6846 | 39.0227 | 42.6519 | 38.8733 | 43.1664 | 37.3171 | 43.0682 | 40.0864 | 40.0211 | 44.9276 | 36.911 | 39.8205 | 40.2241 | 39.4565 | 38.5129 | 39.8006 | 39.6518 | 41.6639 | 28.9244 | 24.5186 | 32.7135 | 39.5186 | 37.6649 | 43.308 | 40.8311 | 39.59 | 38.2607 | 40.8912 | 36.193 | 41.1346 | 38.1711 | 39.1034 | 36.8213 | 40.8319 | 40.4624 | 40.3516 | 42.3688 | 40.0287 | 40.6606 | 41.9662 | 42.973 | 39.9037 | 42.6458 | 41.4904 | 43.8887 | 39.2357 | 42.8322 | 40.1745 | 43.1681 | 40.464 | 43.691 | 40.117 | 44.2675 | 39.6581 | 42.9288 | 44.3274 | 93.7711 | 93.9317 | 93.5575
2022-09-07 19:35 | 1:11 | 24.7741 | 24.6547 | 26.688 | 39.0435 | 42.5562 | 38.8414 | 42.9479 | 37.2855 | 43.0041 | 40.0143 | 39.8155 | 44.8959 | 36.8516 | 39.6486 | 40.2122 | 39.4178 | 38.463 | 39.6058 | 39.5953 | 41.6972 | 28.7941 | 24.4213 | 32.6395 | 39.4847 | 37.6265 | 43.2604 | 40.8151 | 39.6576 | 38.1302 | 40.843 | 36.1534 | 41.0466 | 38.0618 | 39.1715 | 36.6454 | 40.9298 | 40.2657 | 40.4279 | 42.6506 | 39.8481 | 40.586 | 41.916 | 42.865 | 39.8462 | 42.4881 | 41.4214 | 43.8198 | 39.1826 | 42.8772 | 40.1373 | 43.4788 | 40.2072 | 43.5365 | 39.9092 | 44.0475 | 39.5529 | 42.8145 | 44.2938 | 93.6789 | 93.7875 | 93.4445
2022-09-07 19:36 | 1:12 | 24.8883 | 24.5803 | 26.6543 | 38.9109 | 42.511 | 38.6625 | 42.9804 | 37.2877 | 42.9054 | 39.862 | 39.7963 | 44.8969 | 36.8251 | 39.7066 | 40.1765 | 39.3201 | 38.3552 | 39.5082 | 39.6572 | 41.5349 | 28.6527 | 24.3721 | 32.5032 | 39.4298 | 37.5178 | 43.1713 | 40.8094 | 39.5014 | 38.0667 | 40.666 | 36.0107 | 40.8497 | 38.0645 | 39.0274 | 36.5268 | 40.6861 | 40.1266 | 40.2279 | 42.3257 | 39.7387 | 40.532 | 41.8116 | 42.7631 | 39.8553 | 42.4582 | 41.4219 | 43.9631 | 39.0835 | 42.876 | 40.1945 | 43.7118 | 40.1734 | 43.7039 | 39.983 | 43.9732 | 39.4716 | 42.7091 | 44.122 | 93.58 | 93.7271 | 93.4151
2022-09-07 19:36 | 1:12 | 25.0111 | 24.5405 | 26.6173 | 38.8836 | 42.5104 | 38.5561 | 42.8676 | 37.1785 | 42.9265 | 39.7048 | 39.8568 | 44.8205 | 36.6845 | 39.6609 | 40.0033 | 39.2753 | 38.3905 | 39.4223 | 39.5076 | 41.3905 | 28.5419 | 24.2791 | 32.42 | 39.4517 | 37.4962 | 42.9882 | 40.7039 | 39.3528 | 38.0701 | 40.6326 | 35.9554 | 40.9137 | 38.0347 | 38.9974 | 36.3797 | 40.914 | 40.136 | 40.1891 | 42.4039 | 39.6703 | 40.5665 | 41.7139 | 42.7713 | 39.6957 | 42.4001 | 41.3185 | 43.703 | 39.0169 | 42.9054 | 40.0134 | 43.3231 | 40.1819 | 43.5975 | 39.8978 | 43.8726 | 39.4095 | 42.4886 | 44.1997 | 93.526 | 93.6891 | 93.3401
2022-09-07 19:36 | 1:12 | 25.0661 | 24.4888 | 26.5857 | 38.7605 | 42.5253 | 38.4962 | 42.8321 | 37.0899 | 42.9058 | 39.5845 | 40.005 | 44.716 | 36.7057 | 39.6484 | 40.0014 | 39.2217 | 38.3275 | 39.4188 | 39.5667 | 41.2782 | 28.4376 | 24.2309 | 32.3567 | 39.297 | 37.4249 | 43.0582 | 40.6606 | 39.2418 | 38.025 | 40.6395 | 35.9515 | 40.7096 | 37.9734 | 38.886 | 36.4301 | 40.5441 | 40.1375 | 40.1204 | 42.3519 | 39.6099 | 40.4818 | 41.6773 | 42.7049 | 39.5427 | 42.2779 | 41.2623 | 43.7263 | 39.0181 | 42.6103 | 39.9622 | 43.0764 | 40.1383 | 43.5474 | 39.8037 | 43.8023 | 39.4352 | 42.59 | 44.069 | 93.525 | 93.6999 | 93.3949
2022-09-07 19:36 | 1:12 | 24.805 | 24.4682 | 26.5181 | 38.8962 | 42.4867 | 38.5904 | 42.9221 | 36.9897 | 42.7999 | 39.6366 | 39.6476 | 44.8122 | 36.6636 | 39.4596 | 39.8858 | 39.1739 | 38.2903 | 39.3812 | 39.3722 | 41.3338 | 28.3163 | 24.2054 | 32.2671 | 39.1794 | 37.3513 | 42.8247 | 40.586 | 39.088 | 38.0627 | 40.4539 | 35.8105 | 40.7801 | 37.939 | 38.8466 | 36.2403 | 40.6798 | 39.8765 | 39.9562 | 42.3041 | 39.4774 | 40.3278 | 41.5987 | 42.5267 | 39.6346 | 42.1621 | 41.153 | 43.6744 | 38.9288 | 42.6127 | 39.8681 | 43.246 | 40.0444 | 43.3195 | 39.802 | 43.9164 | 39.3225 | 42.4107 | 43.9093 | 93.366 | 93.6603 | 93.192
2022-09-07 19:36 | 1:12 | 24.4189 | 24.4123 | 26.4649 | 38.672 | 42.301 | 38.5962 | 42.8775 | 37.0749 | 42.7874 | 39.6106 | 39.8211 | 44.6839 | 36.6014 | 39.5563 | 39.7554 | 39.1276 | 38.2116 | 39.5639 | 39.4018 | 41.1011 | 28.2195 | 24.1175 | 32.1916 | 39.1353 | 37.2978 | 42.8946 | 40.532 | 39.0013 | 37.9933 | 40.3987 | 35.8054 | 40.7616 | 37.8366 | 38.7441 | 36.2852 | 40.726 | 39.8097 | 39.8848 | 42.4839 | 39.4063 | 40.3152 | 41.5505 | 42.6861 | 39.5497 | 42.1944 | 41.1472 | 43.5165 | 38.7906 | 42.6615 | 39.7728 | 43.3951 | 40.097 | 43.3329 | 39.6477 | 43.6328 | 39.2638 | 42.4312 | 43.9657 | 93.3062 | 93.5447 | 93.2639
2022-09-07 19:36 | 1:12 | 24.3738 | 24.3511 | 26.3829 | 38.6126 | 42.2731 | 38.4849 | 42.7238 | 36.9475 | 42.6918 | 39.5187 | 39.6275 | 44.7329 | 36.5359 | 39.4844 | 39.7126 | 39.1108 | 38.1164 | 39.1786 | 39.2733 | 41.1873 | 28.0828 | 24.0411 | 32.0911 | 39.0557 | 37.2194 | 43.0129 | 40.5665 | 38.9208 | 37.8777 | 40.4018 | 35.7511 | 40.6817 | 37.7634 | 38.7152 | 36.1151 | 40.6618 | 39.697 | 39.8202 | 42.3277 | 39.3568 | 40.2148 | 41.5136 | 42.5325 | 39.5638 | 42.0889 | 41.0654 | 43.7731 | 38.781 | 42.4003 | 39.6822 | 43.5248 | 39.8427 | 43.3727 | 39.5434 | 43.6767 | 39.0487 | 42.4136 | 43.8832 | 93.2831 | 93.514 | 93.178
2022-09-07 19:37 | 1:12 | 24.2299 | 24.3498 | 26.3328 | 38.659 | 42.2013 | 38.3624 | 42.7082 | 36.9033 | 42.6342 | 39.668 | 39.3544 | 44.4438 | 36.4452 | 39.2385 | 39.7681 | 39.0262 | 38.1052 | 39.2087 | 39.2331 | 41.096 | 28.0117 | 24.0378 | 31.9983 | 39.0395 | 37.2151 | 42.8468 | 40.4818 | 39.0018 | 37.8969 | 40.281 | 35.6387 | 40.6791 | 37.671 | 38.6353 | 36.0655 | 40.4143 | 39.7308 | 39.8002 | 42.1857 | 39.3795 | 40.1599 | 41.4171 | 42.4668 | 39.464 | 42.1913 | 41.0038 | 43.7565 | 38.6582 | 42.3431 | 39.6283 | 43.2547 | 39.8532 | 43.0826 | 39.4389 | 43.7172 | 39.0735 | 42.4174 | 43.7733 | 93.2516 | 93.3971 | 93.1601
2022-09-07 19:37 | 1:13 | 23.8383 | 24.2105 | 26.2662 | 38.4411 | 42.2223 | 38.3428 | 42.6142 | 36.8554 | 42.5321 | 39.547 | 39.5915 | 44.396 | 36.4502 | 39.3029 | 39.6412 | 38.9455 | 38.0374 | 39.1273 | 39.2676 | 41.0087 | 27.9039 | 23.8723 | 31.907 | 39.1438 | 37.1314 | 42.8201 | 40.3278 | 38.882 | 37.7824 | 40.2895 | 35.6581 | 40.6178 | 37.6176 | 38.5626 | 36.0183 | 40.509 | 39.6876 | 39.8684 | 42.065 | 39.3374 | 40.0717 | 41.3999 | 42.4628 | 39.4039 | 42.0824 | 40.9108 | 43.3816 | 38.5291 | 42.3496 | 39.584 | 43.0139 | 39.8238 | 43.1058 | 39.4837 | 43.6675 | 39.0828 | 42.1318 | 43.8233 | 93.215 | 93.2988 | 93.2014
2022-09-07 19:37 | 1:13 | 23.9471 | 24.1946 | 26.2183 | 38.4468 | 42.0921 | 38.1464 | 42.4589 | 36.8948 | 42.4887 | 39.3301 | 39.5205 | 44.2444 | 36.3983 | 39.2119 | 39.5738 | 38.904 | 37.9818 | 39.1388 | 39.1609 | 40.9929 | 27.7956 | 23.8148 | 31.8374 | 38.9259 | 37.0842 | 42.5907 | 40.3152 | 38.9332 | 37.6608 | 40.1169 | 35.4792 | 40.5516 | 37.5067 | 38.4934 | 36.0679 | 40.4418 | 39.4372 | 39.619 | 41.8738 | 39.1806 | 40.0672 | 41.281 | 42.2617 | 39.2381 | 41.8767 | 40.8584 | 43.4099 | 38.5002 | 42.2583 | 39.5347 | 42.9026 | 39.7185 | 42.9839 | 39.376 | 43.4002 | 38.9954 | 42.1019 | 43.8953 | 93.1 | 93.2519 | 93.147
2022-09-07 19:37 | 1:13 | 23.6874 | 24.1137 | 26.1361 | 38.4508 | 41.991 | 38.094 | 42.6324 | 36.7651 | 42.4162 | 39.1941 | 39.2859 | 44.2566 | 36.311 | 39.1579 | 39.4695 | 38.8023 | 37.84 | 39.0731 | 39.2542 | 40.956 | 27.7327 | 23.8067 | 31.6941 | 38.8118 | 37.0222 | 42.6991 | 40.2148 | 38.9433 | 37.5952 | 40.1907 | 35.3978 | 40.4103 | 37.4872 | 38.4122 | 35.7954 | 40.2598 | 39.3353 | 39.5412 | 41.8551 | 39.0784 | 39.9543 | 41.2465 | 42.2178 | 39.2317 | 41.8572 | 40.7679 | 43.6015 | 38.4159 | 42.0071 | 39.4624 | 42.9259 | 39.6799 | 43.1797 | 39.4171 | 43.153 | 38.9263 | 41.9581 | 43.8918 | 92.9336 | 93.1233 | 92.9756
2022-09-07 19:37 | 1:13 | 23.7134 | 24.065 | 26.0879 | 38.3712 | 41.9881 | 38.0403 | 42.5602 | 36.6962 | 42.4083 | 39.2433 | 39.4674 | 44.1866 | 36.2749 | 39.1046 | 39.3872 | 38.7762 | 37.8518 | 39.0863 | 39.0136 | 40.7517 | 27.6151 | 23.7329 | 31.5403 | 38.8173 | 36.9477 | 42.688 | 40.1599 | 38.7181 | 37.4866 | 40.119 | 35.4306 | 40.3688 | 37.3797 | 38.3675 | 35.7517 | 40.2043 | 39.2644 | 39.564 | 41.7681 | 39.0155 | 39.9106 | 41.131 | 42.0987 | 39.1348 | 41.7409 | 40.6889 | 43.3975 | 38.4154 | 42.1371 | 39.4144 | 42.9967 | 39.7589 | 43.0076 | 39.2916 | 43.2243 | 38.832 | 41.8353 | 43.5977 | 92.8467 | 92.976 | 92.8797
2022-09-07 19:37 | 1:13 | 23.5401 | 24.0038 | 25.9184 | 38.3935 | 41.9265 | 37.9781 | 42.4854 | 36.6345 | 42.3638 | 39.2257 | 39.4498 | 44.1255 | 36.2541 | 39.0301 | 39.3609 | 38.6924 | 37.7275 | 38.7419 | 38.9278 | 40.7897 | 27.5035 | 23.6307 | 31.4563 | 38.6934 | 36.9187 | 42.6023 | 40.0717 | 38.6079 | 37.4415 | 39.8828 | 35.3161 | 40.3277 | 37.407 | 38.2867 | 35.763 | 40.1287 | 39.4562 | 39.6036 | 41.6667 | 38.9476 | 39.8188 | 41.0583 | 42.135 | 39.0655 | 41.697 | 40.6378 | 43.197 | 38.361 | 41.8957 | 39.2907 | 42.9233 | 39.5525 | 42.9572 | 39.2215 | 43.3051 | 38.7828 | 41.8815 | 43.3789 | 92.6821 | 92.8473 | 92.8179
2022-09-07 19:38 | 1:14 | 23.4299 | 23.9218 | 25.8087 | 38.2189 | 41.922 | 37.9245 | 42.4892 | 36.5914 | 42.2852 | 39.1202 | 39.261 | 44.1987 | 36.1377 | 38.978 | 39.3774 | 38.6484 | 37.6902 | 38.8233 | 38.8009 | 40.6916 | 27.4205 | 23.5241 | 31.3697 | 38.6287 | 36.7894 | 42.4094 | 40.0672 | 38.6424 | 37.3967 | 39.8243 | 35.2571 | 40.3218 | 37.2401 | 38.2608 | 35.6568 | 40.0267 | 39.4061 | 39.4911 | 41.6494 | 38.938 | 39.7973 | 40.9574 | 42.0625 | 39.0117 | 41.5675 | 40.6113 | 43.1618 | 38.3425 | 41.9991 | 39.3476 | 42.7258 | 39.3997 | 42.8023 | 39.2339 | 43.1689 | 38.679 | 41.6943 | 43.2758 | 92.5338 | 92.7221 | 92.743
2022-09-07 19:38 | 1:14 | 23.4457 | 23.8471 | 25.7354 | 38.1618 | 41.8405 | 37.8333 | 42.3735 | 36.5391 | 42.191 | 39.1348 | 39.2038 | 44.0985 | 36.1053 | 38.9118 | 39.3738 | 38.5339 | 37.6722 | 38.5819 | 38.8239 | 40.7706 | 27.3663 | 23.4783 | 31.3072 | 38.5478 | 36.7492 | 42.1658 | 39.9543 | 38.5468 | 37.3426 | 39.7792 | 35.2543 | 40.2857 | 37.2161 | 38.1004 | 35.7468 | 40.0904 | 39.4856 | 39.3817 | 41.611 | 38.9621 | 39.6442 | 40.9109 | 41.9435 | 38.9051 | 41.4207 | 40.5525 | 43.1701 | 38.1922 | 41.8645 | 39.1049 | 42.5288 | 39.478 | 42.6595 | 38.9574 | 43.0753 | 38.5595 | 41.6282 | 43.2343 | 92.4055 | 92.5719 | 92.6135
2022-09-07 19:38 | 1:14 | 23.5039 | 23.776 | 25.7439 | 38.0559 | 41.7752 | 37.7707 | 42.3408 | 36.5291 | 42.1636 | 38.9282 | 38.9409 | 44.0185 | 36.0464 | 38.934 | 39.1005 | 38.4918 | 37.6546 | 38.6927 | 38.7026 | 40.6114 | 27.2836 | 23.3525 | 31.2104 | 38.4918 | 36.6805 | 42.2127 | 39.9106 | 38.3662 | 37.2719 | 39.7371 | 35.1839 | 40.0485 | 37.1509 | 38.0543 | 35.6143 | 40.0438 | 39.4065 | 39.2932 | 41.624 | 38.8154 | 39.5688 | 40.9488 | 41.9002 | 38.7794 | 41.5814 | 40.4476 | 43.0356 | 38.1337 | 41.8433 | 39.2004 | 42.2219 | 39.3876 | 42.5937 | 39.0558 | 42.947 | 38.5795 | 41.6075 | 43.3122 | 92.2658 | 92.4606 | 92.4963
2022-09-07 19:38 | 1:14 | 23.2992 | 23.6976 | 25.69 | 37.9617 | 41.8083 | 37.7439 | 42.2328 | 36.4305 | 42.0395 | 38.8487 | 38.9104 | 43.9676 | 35.8931 | 38.8604 | 39.1494 | 38.466 | 37.5268 | 38.6898 | 38.6776 | 40.4421 | 27.2208 | 23.2823 | 31.149 | 38.4043 | 36.6285 | 42.1248 | 39.8188 | 38.2766 | 37.1972 | 39.6612 | 35.0001 | 40.0066 | 37.0949 | 38.0447 | 35.5378 | 39.9635 | 39.2582 | 39.2338 | 41.394 | 38.8308 | 39.6009 | 40.7828 | 41.9351 | 38.8265 | 41.3531 | 40.4141 | 42.9584 | 38.142 | 41.9184 | 39.1029 | 42.2216 | 39.2077 | 42.629 | 38.9423 | 42.9873 | 38.4408 | 41.7189 | 43.1872 | 92.1709 | 92.3184 | 92.4734
2022-09-07 19:38 | 1:14 | 23.19 | 23.6417 | 25.6291 | 37.982 | 41.5907 | 37.778 | 42.2072 | 36.3 | 41.9638 | 38.7911 | 38.8732 | 43.8297 | 35.8244 | 38.7774 | 39.186 | 38.3935 | 37.4753 | 38.6086 | 38.5298 | 40.6415 | 27.137 | 23.1667 | 31.1337 | 38.4321 | 36.5286 | 41.9585 | 39.7973 | 38.1357 | 37.1822 | 39.6281 | 35.0116 | 39.945 | 37.0627 | 38.003 | 35.3623 | 39.6747 | 39.0896 | 39.1368 | 41.4429 | 38.715 | 39.5031 | 40.7608 | 41.8212 | 38.8389 | 41.5394 | 40.3351 | 42.8347 | 38.0346 | 41.7171 | 38.9916 | 42.5397 | 39.0064 | 42.5792 | 38.91 | 42.9625 | 38.344 | 41.6859 | 43.0103 | 91.9989 | 92.1614 | 92.3558
2022-09-07 19:38 | 1:14 | 23.0507 | 23.52 | 25.5338 | 37.8707 | 41.6024 | 37.6541 | 41.9892 | 36.2948 | 41.9845 | 38.8948 | 39.1323 | 43.9096 | 35.8145 | 38.6416 | 38.9874 | 38.3124 | 37.4755 | 38.3405 | 38.4916 | 40.4141 | 27.0438 | 23.0823 | 31.0637 | 38.3299 | 36.4964 | 41.7655 | 39.6442 | 38.1663 | 37.1021 | 39.3875 | 34.9721 | 39.9059 | 37.0957 | 37.8724 | 35.3788 | 39.7695 | 39.2408 | 39.0739 | 41.429 | 38.6421 | 39.5383 | 40.6245 | 41.9347 | 38.6867 | 41.3034 | 40.221 | 42.8527 | 37.956 | 41.8344 | 38.9633 | 42.4959 | 39.1312 | 42.4492 | 39.0465 | 42.7457 | 38.3775 | 41.4747 | 43.1297 | 91.8811 | 91.9965 | 92.2481
2022-09-07 19:39 | 1:14 | 23.0053 | 23.439 | 25.4227 | 37.7352 | 41.5971 | 37.6749 | 42.0382 | 36.2189 | 41.9002 | 38.7314 | 38.7954 | 43.8863 | 35.7667 | 38.6076 | 39.0214 | 38.2994 | 37.3847 | 38.3583 | 38.5461 | 40.3698 | 26.985 | 22.9632 | 31.0396 | 38.2404 | 36.4474 | 41.7645 | 39.5688 | 38.4234 | 37.1711 | 39.4183 | 34.8334 | 39.9875 | 37.0445 | 37.8442 | 35.332 | 39.9091 | 39.1121 | 39.0631 | 41.5585 | 38.6212 | 39.4353 | 40.6013 | 41.8008 | 38.6581 | 41.1934 | 40.2109 | 42.6589 | 37.9044 | 41.8111 | 38.8428 | 42.3971 | 39.0225 | 42.4505 | 38.8034 | 42.7545 | 38.2786 | 41.3265 | 42.9463 | 91.7592 | 91.8585 | 92.2193
2022-09-07 19:39 | 1:15 | 22.8276 | 23.3534 | 25.3177 | 37.4512 | 41.5668 | 37.7583 | 42.0008 | 36.0227 | 41.8066 | 38.8803 | 38.3122 | 43.7144 | 35.6955 | 38.6408 | 38.9426 | 38.1958 | 37.3164 | 38.4699 | 38.5156 | 40.2761 | 26.9406 | 22.8998 | 30.9724 | 38.1318 | 36.3385 | 42.0693 | 39.6009 | 38.3675 | 37.1189 | 39.4973 | 34.821 | 39.8424 | 36.9553 | 37.8391 | 35.2369 | 39.8692 | 38.7956 | 39.0697 | 41.514 | 38.4541 | 39.3644 | 40.5302 | 41.7248 | 38.6065 | 41.0353 | 40.1361 | 42.6975 | 37.8498 | 41.6287 | 38.7637 | 42.2826 | 39.0053 | 42.2376 | 38.7101 | 42.8036 | 38.179 | 41.3744 | 42.9873 | 91.6555 | 91.7669 | 92.0892
2022-09-07 19:39 | 1:15 | 22.7131 | 23.2757 | 25.2852 | 37.7023 | 41.5235 | 37.6733 | 41.9833 | 35.959 | 41.759 | 38.6104 | 38.5097 | 43.6371 | 35.6555 | 38.6885 | 38.9044 | 38.1158 | 37.3015 | 38.4414 | 38.3227 | 40.2097 | 26.8809 | 22.8338 | 30.9542 | 38.0421 | 36.3103 | 41.9935 | 39.5031 | 38.1823 | 36.9692 | 39.3096 | 34.6962 | 39.7234 | 36.8544 | 37.7368 | 35.1964 | 39.8034 | 38.9178 | 38.9203 | 41.2948 | 38.4844 | 39.2615 | 40.446 | 41.6158 | 38.4769 | 41.051 | 40.0692 | 42.7037 | 37.7569 | 41.6418 | 38.7457 | 42.1758 | 38.6578 | 42.288 | 38.6106 | 42.5043 | 38.1103 | 41.3026 | 42.9603 | 91.5824 | 91.6504 | 91.9883
2022-09-07 19:39 | 1:15 | 22.7122 | 23.1923 | 25.2232 | 37.616 | 41.3875 | 37.394 | 41.971 | 35.9683 | 41.674 | 38.471 | 38.4728 | 43.4866 | 35.6351 | 38.4669 | 38.862 | 38.0413 | 37.213 | 38.3034 | 38.3489 | 40.1189 | 26.8068 | 22.7628 | 30.8975 | 37.9708 | 36.2397 | 42.0979 | 39.5383 | 37.9637 | 36.9133 | 39.3045 | 34.7681 | 39.6385 | 36.762 | 37.6023 | 35.1398 | 39.5774 | 38.863 | 38.8995 | 41.1318 | 38.4158 | 39.246 | 40.3816 | 41.5163 | 38.4595 | 40.9184 | 40.0129 | 42.3639 | 37.6754 | 41.5803 | 38.6646 | 42.2022 | 38.6062 | 42.2487 | 38.4858 | 42.4567 | 38.0885 | 41.2504 | 42.8365 | 91.5631 | 91.6645 | 92.0606
2022-09-07 19:39 | 1:15 | 22.5271 | 23.0914 | 25.1135 | 37.5572 | 41.3291 | 37.3728 | 41.7434 | 35.9123 | 41.7298 | 38.5224 | 38.6202 | 43.4137 | 35.4992 | 38.3293 | 38.7743 | 38.0372 | 37.1328 | 38.2212 | 38.1105 | 40.0267 | 26.7602 | 22.6716 | 30.8677 | 37.9495 | 36.1909 | 41.8903 | 39.4353 | 37.8489 | 36.8268 | 39.2204 | 34.6208 | 39.5512 | 36.8164 | 37.5678 | 35.1668 | 39.5099 | 38.863 | 38.8683 | 41.1777 | 38.3768 | 39.144 | 40.3263 | 41.4031 | 38.3951 | 40.8609 | 39.9388 | 42.4755 | 37.5583 | 41.5444 | 38.657 | 42.2011 | 38.8124 | 42.0005 | 38.5543 | 42.5295 | 38.1573 | 41.1987 | 42.8961 | 91.5854 | 91.7257 | 92.0921
2022-09-07 19:39 | 1:15 | 22.5955 | 22.9965 | 25.0686 | 37.4964 | 41.1663 | 37.093 | 41.6543 | 35.778 | 41.563 | 38.4358 | 38.1261 | 43.3588 | 35.4111 | 38.3898 | 38.7368 | 37.9632 | 37.0567 | 38.2378 | 38.1511 | 39.9711 | 26.7351 | 22.5721 | 30.8032 | 37.8588 | 36.1779 | 41.7673 | 39.3644 | 37.8192 | 36.8065 | 39.1157 | 34.523 | 39.6056 | 36.7474 | 37.4494 | 35.0791 | 39.421 | 38.5875 | 38.7937 | 41.1255 | 38.2204 | 39.1068 | 40.3021 | 41.3733 | 38.2953 | 40.8533 | 39.8691 | 42.428 | 37.5883 | 41.3489 | 38.5347 | 41.4777 | 38.5698 | 41.8567 | 38.4263 | 42.4665 | 37.9307 | 41.3273 | 42.5903 | 91.6396 | 91.7982 | 92.1034
2022-09-07 19:40 | 1:15 | 22.4123 | 22.9423 | 24.9907 | 37.5136 | 41.2636 | 37.1452 | 41.5549 | 35.7269 | 41.5093 | 38.3641 | 38.2865 | 43.2917 | 35.3555 | 38.3143 | 38.6404 | 37.887 | 36.9474 | 38.0685 | 38.1803 | 39.926 | 26.668 | 22.5428 | 30.7077 | 37.8513 | 36.0709 | 41.5883 | 39.2615 | 37.9201 | 36.7397 | 39.0174 | 34.4487 | 39.5819 | 36.6378 | 37.4879 | 34.932 | 39.4611 | 38.5921 | 38.7666 | 41.0807 | 38.1334 | 39.0245 | 40.2275 | 41.2698 | 38.2728 | 40.7036 | 39.7979 | 42.2229 | 37.5751 | 41.4457 | 38.5245 | 41.8829 | 38.5229 | 41.9633 | 38.4891 | 42.3231 | 37.866 | 41.2001 | 42.5893 | 91.6527 | 91.8994 | 92.012
2022-09-07 19:40 | 1:16 | 22.2568 | 22.8692 | 24.8709 | 37.2768 | 41.1354 | 37.1262 | 41.6301 | 35.8039 | 41.4868 | 38.3991 | 38.4876 | 43.283 | 35.3293 | 38.161 | 38.5346 | 37.8282 | 36.9611 | 37.8062 | 38.0621 | 39.9514 | 26.5907 | 22.4679 | 30.653 | 37.7749 | 35.9882 | 41.6297 | 39.246 | 37.6487 | 36.6398 | 39.0833 | 34.3384 | 39.2631 | 36.5584 | 37.3768 | 34.8777 | 39.4422 | 38.5774 | 38.5675 | 41.0301 | 38.151 | 38.9471 | 40.1188 | 41.2663 | 38.1145 | 40.795 | 39.7331 | 42.1415 | 37.4644 | 41.2343 | 38.3758 | 41.7936 | 38.4231 | 41.8399 | 38.3574 | 42.4327 | 37.8129 | 41.0838 | 42.7338 | 91.8026 | 91.9689 | 92.1821
2022-09-07 19:40 | 1:16 | 22.2427 | 22.844 | 24.7524 | 37.3324 | 41.0405 | 37.1889 | 41.4464 | 35.6772 | 41.4757 | 38.2882 | 38.2175 | 43.2137 | 35.2653 | 38.0497 | 38.5082 | 37.7927 | 36.8779 | 37.9199 | 37.9678 | 40.0363 | 26.529 | 22.4401 | 30.5653 | 37.6344 | 35.9494 | 41.6547 | 39.144 | 37.7224 | 36.555 | 38.9815 | 34.3353 | 39.3934 | 36.4653 | 37.375 | 34.7518 | 39.5815 | 38.5548 | 38.6459 | 40.9821 | 38.0529 | 38.9597 | 40.1042 | 41.1871 | 38.1573 | 40.8005 | 39.6788 | 42.1957 | 37.356 | 41.1631 | 38.306 | 41.9263 | 38.6148 | 41.8498 | 38.3068 | 42.1101 | 37.7759 | 40.8614 | 42.5805 | 91.9076 | 92.0491 | 92.2772
2022-09-07 19:40 | 1:16 | 22.1896 | 22.7218 | 24.6523 | 37.2837 | 41.0366 | 37.1961 | 41.419 | 35.6766 | 41.3317 | 38.2413 | 38.1944 | 43.3467 | 35.1984 | 38.0252 | 38.3814 | 37.7449 | 36.7632 | 37.6813 | 37.9038 | 39.6169 | 26.4373 | 22.2958 | 30.5027 | 37.6979 | 35.9212 | 41.4422 | 39.1068 | 37.7073 | 36.4945 | 38.9637 | 34.3267 | 39.3458 | 36.3992 | 37.2806 | 34.7578 | 39.2674 | 38.5168 | 38.4511 | 40.7781 | 38.0557 | 38.9226 | 39.9966 | 41.0744 | 38.1795 | 40.5262 | 39.5935 | 42.2238 | 37.3521 | 41.2874 | 38.2564 | 42.0229 | 38.4492 | 41.7616 | 38.2187 | 42.2616 | 37.7465 | 40.9432 | 42.687 | 92.0354 | 92.1557 | 92.2909
2022-09-07 19:40 | 1:16 | 22.2025 | 22.6016 | 24.6383 | 37.0725 | 40.9482 | 36.9586 | 41.326 | 35.6732 | 41.2944 | 38.342 | 38.3828 | 43.1636 | 35.1149 | 37.8885 | 38.2061 | 37.6624 | 36.7561 | 37.692 | 37.7267 | 39.7945 | 26.3681 | 22.24 | 30.4329 | 37.5956 | 35.8319 | 41.1998 | 39.0245 | 37.7324 | 36.4592 | 38.8718 | 34.3032 | 39.3267 | 36.4276 | 37.1805 | 34.742 | 39.3559 | 38.2883 | 38.3579 | 40.7752 | 37.8618 | 38.7278 | 39.9276 | 40.9991 | 38.028 | 40.5714 | 39.5515 | 42.2132 | 37.2616 | 40.9467 | 38.2884 | 41.2922 | 38.3655 | 41.6512 | 38.1515 | 42.0607 | 37.6234 | 40.7697 | 42.5853 | 92.1314 | 92.2677 | 92.4321
2022-09-07 19:40 | 1:16 | 22.0927 | 22.5715 | 24.538 | 37.1745 | 40.8927 | 36.7347 | 41.2364 | 35.5903 | 41.2147 | 38.112 | 37.9945 | 43.1443 | 35.0754 | 37.873 | 38.3166 | 37.6067 | 36.705 | 37.8427 | 37.6953 | 39.5612 | 26.3134 | 22.1881 | 30.4051 | 37.6032 | 35.7567 | 41.3009 | 38.9471 | 37.5529 | 36.4329 | 38.8009 | 34.1262 | 39.0417 | 36.3325 | 37.1058 | 34.6948 | 39.1119 | 38.2653 | 38.3749 | 40.7494 | 37.8447 | 38.7269 | 39.8759 | 40.9213 | 37.9531 | 40.4539 | 39.4565 | 42.1482 | 37.0881 | 40.7777 | 38.1618 | 41.4606 | 38.3183 | 41.6446 | 38.0867 | 42.1999 | 37.6206 | 40.7674 | 42.3229 | 92.2246 | 92.3492 | 92.4632
2022-09-07 19:41 | 1:16 | 22.0096 | 22.5625 | 24.5397 | 37.0978 | 40.8512 | 36.8995 | 41.2976 | 35.5289 | 41.2011 | 38.086 | 38.1953 | 43.1018 | 35.0125 | 37.9109 | 38.271 | 37.506 | 36.6159 | 37.6415 | 37.726 | 39.6485 | 26.2584 | 22.1673 | 30.3207 | 37.3772 | 35.6962 | 41.3341 | 38.9597 | 37.4606 | 36.2849 | 38.7199 | 34.203 | 39.1519 | 36.2373 | 37.0544 | 34.5947 | 38.9172 | 38.2979 | 38.3252 | 40.4507 | 37.7739 | 38.6132 | 39.8062 | 40.935 | 37.8204 | 40.3574 | 39.4338 | 41.9749 | 37.1317 | 40.9361 | 38.1226 | 41.5149 | 38.1104 | 41.6812 | 37.9741 | 41.9705 | 37.537 | 40.7642 | 42.1741 | 92.3496 | 92.4675 | 92.5658
2022-09-07 19:41 | 1:17 | 21.9057 | 22.4823 | 24.4548 | 36.901 | 40.6948 | 36.914 | 41.2695 | 35.4041 | 41.16 | 37.9198 | 38.1557 | 43.0635 | 34.8696 | 37.9239 | 38.1387 | 37.413 | 36.5562 | 37.8206 | 37.6948 | 39.4986 | 26.1924 | 22.0734 | 30.282 | 37.3487 | 35.6196 | 41.3077 | 38.9226 | 37.4342 | 36.2794 | 38.6241 | 34.0465 | 39.1345 | 36.1073 | 37.0207 | 34.4138 | 38.9758 | 38.1623 | 38.2214 | 40.535 | 37.6992 | 38.5841 | 39.7971 | 40.9448 | 37.8044 | 40.2517 | 39.4022 | 41.8034 | 37.1257 | 40.8828 | 38.1422 | 41.4113 | 38.1611 | 41.4902 | 37.9622 | 41.8012 | 37.4453 | 40.6472 | 41.935 | 92.4207 | 92.5564 | 92.5433
2022-09-07 19:41 | 1:17 | 22.1221 | 22.3458 | 24.4447 | 36.9293 | 40.7259 | 36.8606 | 41.0832 | 35.231 | 41.1024 | 38.0087 | 38.0451 | 42.9483 | 34.9331 | 37.7236 | 38.2004 | 37.3698 | 36.485 | 37.5838 | 37.7887 | 39.2469 | 26.1327 | 21.9931 | 30.1939 | 37.336 | 35.5629 | 41.1282 | 38.7278 | 37.581 | 36.1923 | 38.4612 | 34.0225 | 39.2226 | 36.0281 | 36.9822 | 34.3703 | 38.8784 | 38.0138 | 38.194 | 40.5781 | 37.5581 | 38.463 | 39.7162 | 40.7623 | 37.8127 | 40.3565 | 39.336 | 41.8708 | 36.9946 | 40.6564 | 38.0532 | 41.606 | 38.0439 | 41.5955 | 37.943 | 41.7724 | 37.412 | 40.6668 | 41.9488 | 92.4728 | 92.6254 | 92.5848
2022-09-07 19:41 | 1:17 | 21.8808 | 22.3096 | 24.2873 | 36.8007 | 40.7201 | 36.8639 | 41.1891 | 35.2312 | 40.9635 | 37.7959 | 37.7666 | 42.8862 | 34.8165 | 37.6566 | 38.0451 | 37.3421 | 36.4449 | 37.5849 | 37.5628 | 39.3782 | 26.0696 | 21.9296 | 30.156 | 37.2398 | 35.507 | 40.9349 | 38.7269 | 37.274 | 36.0707 | 38.5014 | 33.963 | 39.0192 | 35.9372 | 36.905 | 34.4584 | 38.8585 | 37.9709 | 38.1579 | 40.4062 | 37.5806 | 38.4432 | 39.6467 | 40.8369 | 37.6595 | 40.3456 | 39.2588 | 41.7793 | 36.8876 | 40.8831 | 37.8844 | 41.2197 | 37.9509 | 41.3883 | 37.8498 | 41.8914 | 37.3688 | 40.5151 | 42.0234 | 92.6022 | 92.7169 | 92.6432
2022-09-07 19:41 | 1:17 | 21.7845 | 22.2465 | 24.1827 | 36.7578 | 40.5726 | 36.6278 | 41.0558 | 35.2608 | 40.9969 | 37.6428 | 37.7231 | 42.7655 | 34.7968 | 37.522 | 38.0745 | 37.2999 | 36.4207 | 37.3235 | 37.5207 | 39.3574 | 26.0147 | 21.8938 | 30.106 | 37.2942 | 35.458 | 41.0748 | 38.6132 | 37.3006 | 36.0534 | 38.4087 | 33.7988 | 38.8775 | 35.977 | 36.8407 | 34.2859 | 38.779 | 37.8889 | 38.2633 | 40.2748 | 37.5166 | 38.3798 | 39.5748 | 40.5614 | 37.6836 | 40.2063 | 39.2135 | 41.8692 | 36.848 | 40.6336 | 37.8371 | 41.0416 | 37.8104 | 41.3553 | 37.8644 | 41.8659 | 37.2486 | 40.5811 | 41.8274 | 92.7411 | 92.875 | 92.7417
2022-09-07 19:41 | 1:17 | 21.8132 | 22.1531 | 24.1122 | 36.7098 | 40.4409 | 36.7142 | 40.9628 | 35.1183 | 40.8731 | 37.7477 | 37.8325 | 42.6646 | 34.6762 | 37.48 | 37.932 | 37.2079 | 36.2824 | 37.2301 | 37.3685 | 39.2848 | 25.9514 | 21.8717 | 30.0121 | 37.1385 | 35.3674 | 40.9593 | 38.5841 | 37.4789 | 36.0762 | 38.3655 | 33.7858 | 38.7428 | 35.8875 | 36.7605 | 34.346 | 38.847 | 37.7868 | 37.9856 | 40.4019 | 37.4438 | 38.2852 | 39.5284 | 40.6289 | 37.594 | 40.1854 | 39.0974 | 41.7474 | 36.7693 | 40.5277 | 37.811 | 41.3353 | 37.8605 | 41.3708 | 37.7139 | 41.6811 | 37.2431 | 40.325 | 41.8453 | 92.9348 | 93.0071 | 92.8649
2022-09-07 19:42 | 1:17 | 22.0058 | 22.1755 | 24.0875 | 36.7403 | 40.5029 | 36.4417 | 41.0757 | 35.029 | 40.7987 | 37.7479 | 37.8299 | 42.6583 | 34.6307 | 37.3481 | 37.9708 | 37.1606 | 36.2718 | 37.3556 | 37.2516 | 39.336 | 25.8666 | 21.8279 | 29.9468 | 37.0865 | 35.3022 | 40.9057 | 38.463 | 37.3528 | 35.9531 | 38.3238 | 33.7473 | 38.8617 | 35.8209 | 36.71 | 34.1206 | 38.6798 | 37.9499 | 38.0124 | 40.371 | 37.6131 | 38.2175 | 39.5064 | 40.454 | 37.5364 | 40.0108 | 39.0276 | 41.3799 | 36.786 | 40.3694 | 37.6458 | 40.991 | 37.8873 | 41.3214 | 37.5292 | 41.7193 | 37.1155 | 40.2171 | 41.7223 | 93.0455 | 93.1731 | 92.9806
2022-09-07 19:42 | 1:18 | 21.7343 | 22.139 | 24.0904 | 36.6242 | 40.454 | 36.4199 | 40.8467 | 35.0997 | 40.7717 | 37.5998 | 37.7988 | 42.615 | 34.5491 | 37.3926 | 37.8331 | 37.094 | 36.1154 | 37.4186 | 37.283 | 39.0999 | 25.8032 | 21.7737 | 29.8961 | 37.1026 | 35.2388 | 40.7783 | 38.4432 | 37.2211 | 35.8759 | 38.1856 | 33.6272 | 38.8028 | 35.807 | 36.6516 | 34.1193 | 38.7783 | 37.8921 | 37.9804 | 40.3314 | 37.3916 | 38.2132 | 39.3227 | 40.488 | 37.4939 | 39.9645 | 39.0062 | 41.5119 | 36.6738 | 40.4278 | 37.4685 | 41.1932 | 37.8179 | 41.2719 | 37.4904 | 41.51 | 37.1823 | 40.2451 | 41.7796 | 93.22 | 93.3668 | 93.0364
2022-09-07 19:42 | 1:18 | 21.5875 | 22.0372 | 24.0298 | 36.4761 | 40.3943 | 36.3735 | 40.8778 | 34.938 | 40.6972 | 37.7366 | 37.4718 | 42.5688 | 34.4078 | 37.4222 | 37.7972 | 37.0699 | 36.1326 | 37.3223 | 37.1823 | 39.1604 | 25.7625 | 21.656 | 29.8434 | 36.8853 | 35.1723 | 40.6886 | 38.3798 | 36.9586 | 35.7442 | 38.2161 | 33.5719 | 38.7074 | 35.7722 | 36.5626 | 34.088 | 38.6775 | 37.772 | 37.8486 | 40.2279 | 37.2707 | 38.1318 | 39.3845 | 40.399 | 37.4644 | 39.8811 | 38.9201 | 41.4622 | 36.7103 | 40.4259 | 37.4806 | 41.3742 | 37.7597 | 41.2418 | 37.6011 | 41.5263 | 37.0881 | 40.2381 | 41.8236 | 93.4174 | 93.5152 | 93.2141
2022-09-07 19:42 | 1:18 | 21.6619 | 21.9584 | 24.0205 | 36.344 | 40.3652 | 36.4086 | 40.4642 | 34.886 | 40.6287 | 37.44 | 37.4786 | 42.5307 | 34.4665 | 37.3713 | 37.6118 | 36.9987 | 36.0446 | 37.15 | 37.0996 | 39.1322 | 25.6798 | 21.634 | 29.7944 | 36.9275 | 35.1458 | 40.6324 | 38.2852 | 36.9037 | 35.782 | 38.0683 | 33.5863 | 38.6304 | 35.6635 | 36.4932 | 33.9528 | 38.3586 | 37.7628 | 37.7837 | 40.1702 | 37.248 | 38.0637 | 39.3801 | 40.2551 | 37.3398 | 39.9124 | 38.8776 | 41.2352 | 36.5778 | 40.1782 | 37.5672 | 41.0799 | 37.7213 | 41.1429 | 37.4725 | 41.4973 | 37.006 | 40.0595 | 41.7001 | 93.5356 | 93.6477 | 93.2483
2022-09-07 19:42 | 1:18 | 21.5311 | 21.9314 | 23.975 | 36.5293 | 40.1873 | 36.3571 | 40.6049 | 34.9012 | 40.6272 | 37.3061 | 37.4279 | 42.4751 | 34.3783 | 37.3646 | 37.5464 | 36.8926 | 35.9939 | 37.0827 | 37.1786 | 39.0403 | 25.6378 | 21.5752 | 29.6966 | 36.7363 | 35.0781 | 40.4659 | 38.2175 | 36.7078 | 35.7692 | 38.0138 | 33.5275 | 38.3845 | 35.63 | 36.4146 | 33.8855 | 38.5308 | 37.697 | 37.6808 | 40.1847 | 37.2142 | 37.8661 | 39.2655 | 40.2954 | 37.2145 | 39.7366 | 38.7765 | 41.1312 | 36.4825 | 40.309 | 37.42 | 41.0986 | 37.6453 | 41.1239 | 37.3298 | 41.4561 | 36.912 | 39.8952 | 41.6847 | 93.6621 | 93.846 | 93.2611
2022-09-07 19:42 | 1:18 | 21.4807 | 21.9276 | 23.9347 | 36.4074 | 40.198 | 36.254 | 40.4866 | 34.7312 | 40.5477 | 37.4074 | 37.45 | 42.3613 | 34.2901 | 37.1961 | 37.7169 | 36.8727 | 35.9664 | 36.9396 | 37.1291 | 39.0875 | 25.5927 | 21.5316 | 29.6403 | 36.6699 | 35.0228 | 40.5991 | 38.2132 | 36.8832 | 35.6296 | 38.0062 | 33.4306 | 38.4468 | 35.5392 | 36.4026 | 33.9695 | 38.4654 | 37.6484 | 37.6339 | 40.1167 | 37.2222 | 37.805 | 39.0891 | 40.2135 | 37.2974 | 39.8992 | 38.7364 | 41.1107 | 36.4543 | 40.1795 | 37.3754 | 40.8582 | 37.5559 | 40.9936 | 37.2482 | 41.2783 | 36.7871 | 40.0232 | 41.7404 | 93.8924 | 94.0508 | 93.4243
2022-09-07 19:43 | 1:19 | 21.6217 | 21.861 | 23.9066 | 36.2769 | 40.1578 | 36.1495 | 40.6303 | 34.8038 | 40.4906 | 37.4731 | 37.4457 | 42.3636 | 34.2818 | 37.2138 | 37.5095 | 36.7927 | 35.9294 | 37.1054 | 36.954 | 38.9308 | 25.5339 | 21.4589 | 29.5868 | 36.7168 | 34.9778 | 40.5392 | 38.1318 | 36.8055 | 35.5958 | 37.9172 | 33.4643 | 38.3308 | 35.509 | 36.2633 | 33.8074 | 38.2707 | 37.6478 | 37.5605 | 40.007 | 37.0599 | 37.8238 | 39.1626 | 40.2663 | 37.1589 | 39.6842 | 38.6675 | 41.2051 | 36.3559 | 40.024 | 37.3376 | 40.6193 | 37.3751 | 40.8125 | 37.2808 | 41.3177 | 36.7245 | 39.9808 | 41.7539 | 94.0164 | 94.1591 | 93.5149
2022-09-07 19:43 | 1:19 | 21.5739 | 21.7962 | 23.8503 | 36.3104 | 40.0689 | 36.1191 | 40.597 | 34.6022 | 40.4059 | 37.2669 | 37.4494 | 42.276 | 34.244 | 37.1411 | 37.4549 | 36.6882 | 35.854 | 37.0188 | 36.9756 | 38.8283 | 25.4705 | 21.3967 | 29.5373 | 36.628 | 34.916 | 40.7044 | 38.0637 | 36.6775 | 35.5969 | 37.8104 | 33.4112 | 38.436 | 35.3643 | 36.2201 | 33.8163 | 38.2689 | 37.514 | 37.5124 | 39.945 | 36.9742 | 37.7436 | 39.0669 | 40.1197 | 37.1584 | 39.538 | 38.6359 | 41.0352 | 36.3139 | 40.1288 | 37.305 | 40.4669 | 37.3 | 40.6746 | 37.1762 | 41.1972 | 36.7326 | 39.6902 | 41.4908 | 94.2499 | 94.297 | 93.6508
2022-09-07 19:43 | 1:19 | 21.6892 | 21.7041 | 23.8044 | 36.1969 | 40.0012 | 36.0188 | 40.4325 | 34.5867 | 40.4477 | 37.1036 | 37.5142 | 42.2895 | 34.1069 | 37.0907 | 37.4017 | 36.6553 | 35.7619 | 36.9573 | 36.8482 | 38.7278 | 25.4356 | 21.3888 | 29.5105 | 36.5421 | 34.8739 | 40.2741 | 37.8661 | 36.6335 | 35.4996 | 37.7445 | 33.3942 | 38.2469 | 35.3025 | 36.1424 | 33.7824 | 38.0962 | 37.5018 | 37.549 | 39.9849 | 36.9322 | 37.7939 | 39.0123 | 40.041 | 37.0919 | 39.5378 | 38.5518 | 40.9821 | 36.1872 | 40.0277 | 37.2093 | 40.7242 | 37.2331 | 40.5853 | 37.1973 | 41.0051 | 36.6466 | 39.8054 | 41.4424 | 94.478 | 94.4172 | 93.8177
2022-09-07 19:43 | 1:19 | 21.6615 | 21.6624 | 23.6997 | 36.1924 | 39.9901 | 35.9308 | 40.2294 | 34.5755 | 40.4146 | 37.1876 | 37.2589 | 42.2328 | 34.1122 | 37.0445 | 37.3865 | 36.5686 | 35.7275 | 36.8929 | 36.824 | 38.6701 | 25.3457 | 21.1936 | 29.4694 | 36.5715 | 34.7489 | 40.1337 | 37.805 | 36.8692 | 35.4276 | 37.7069 | 33.2382 | 38.2234 | 35.3095 | 36.1574 | 33.6253 | 38.1044 | 37.4447 | 37.3337 | 40.0425 | 36.9073 | 37.6078 | 38.9303 | 39.9719 | 36.9931 | 39.4814 | 38.4661 | 40.9406 | 36.1899 | 40.1641 | 37.2047 | 40.4615 | 37.1587 | 40.6886 | 37.0331 | 41.0994 | 36.5901 | 39.7149 | 41.452 | 94.5236 | 94.5709 | 93.9196
2022-09-07 19:43 | 1:19 | 21.4227 | 21.5773 | 23.5557 | 36.1123 | 39.9253 | 35.9243 | 40.2492 | 34.4498 | 40.3065 | 36.9155 | 37.1318 | 41.9949 | 34.0264 | 37.0566 | 37.3402 | 36.579 | 35.7142 | 37.0237 | 36.7154 | 38.6191 | 25.2987 | 21.1648 | 29.3772 | 36.4649 | 34.7307 | 40.2617 | 37.8238 | 36.5894 | 35.3458 | 37.8312 | 33.0718 | 38.0524 | 35.2002 | 36.0992 | 33.7657 | 38.0554 | 37.5407 | 37.3527 | 39.7533 | 37.0076 | 37.602 | 38.8716 | 39.824 | 36.9932 | 39.4492 | 38.4179 | 40.914 | 36.0784 | 39.8833 | 37.0311 | 40.4025 | 37.0799 | 40.6316 | 37.0122 | 41.0993 | 36.5239 | 39.59 | 41.3339 | 94.6387 | 94.6927 | 93.876
2022-09-07 19:43 | 1:19 | 21.2923 | 21.5491 | 23.5009 | 35.9349 | 39.8422 | 35.6573 | 40.1955 | 34.5071 | 40.2142 | 37.0509 | 37.3385 | 42.0308 | 33.9958 | 36.9374 | 37.2645 | 36.4886 | 35.6192 | 36.9762 | 36.7056 | 38.7326 | 25.2469 | 21.1295 | 29.343 | 36.3806 | 34.6465 | 40.0319 | 37.7436 | 36.4202 | 35.272 | 37.569 | 32.9889 | 37.9915 | 35.1602 | 36.0199 | 33.6134 | 37.8721 | 37.3736 | 37.1982 | 39.8634 | 36.9253 | 37.4781 | 38.7615 | 39.9245 | 36.7374 | 39.3649 | 38.3196 | 40.7593 | 35.9762 | 39.6967 | 36.9691 | 40.2463 | 37.1382 | 40.5172 | 36.9674 | 40.9167 | 36.5038 | 39.5818 | 41.202 | 94.7593 | 94.8117 | 94.0178
2022-09-07 19:44 | 1:19 | 21.7804 | 21.575 | 23.5452 | 35.953 | 39.8688 | 35.7865 | 40.0778 | 34.4112 | 40.2473 | 36.9742 | 36.9377 | 41.9517 | 33.9682 | 36.6939 | 37.1079 | 36.4398 | 35.5626 | 36.9744 | 36.64 | 38.6642 | 25.2027 | 21.128 | 29.3203 | 36.3504 | 34.6043 | 40.1565 | 37.7939 | 36.4352 | 35.2943 | 37.6639 | 32.9646 | 38.0329 | 35.1502 | 36.071 | 33.4671 | 37.9523 | 37.2362 | 37.251 | 39.6349 | 36.7904 | 37.3473 | 38.7567 | 39.7852 | 36.8152 | 39.2923 | 38.2816 | 40.8153 | 36.0846 | 40.0182 | 36.9352 | 40.4722 | 37.0902 | 40.2373 | 36.8734 | 40.8843 | 36.3818 | 39.7007 | 41.0842 | 94.8734 | 94.9276 | 94.0152
2022-09-07 19:44 | 1:20 | 21.1571 | 21.5227 | 23.4519 | 35.9037 | 39.7885 | 35.6622 | 40.3354 | 34.3117 | 40.0907 | 37.002 | 37.0632 | 41.8152 | 33.8565 | 36.7577 | 36.9206 | 36.4098 | 35.5007 | 36.6979 | 36.5361 | 38.5307 | 25.1657 | 21.1092 | 29.2239 | 36.2761 | 34.5299 | 39.9899 | 37.6078 | 36.3167 | 35.1914 | 37.5319 | 32.9956 | 38.0395 | 35.1319 | 35.9289 | 33.3463 | 37.8571 | 37.1275 | 37.1876 | 39.6149 | 36.613 | 37.2784 | 38.6759 | 39.753 | 36.7289 | 39.1617 | 38.2012 | 40.6293 | 36.0197 | 39.8661 | 36.8695 | 40.0406 | 37.1527 | 40.3554 | 36.8214 | 40.768 | 36.2162 | 39.4379 | 41.2366 | 94.8381 | 94.9826 | 94.0591
2022-09-07 19:44 | 1:20 | 21.4443 | 21.5449 | 23.5253 | 35.933 | 39.704 | 35.6017 | 39.9906 | 34.2499 | 40.0784 | 36.9467 | 36.8689 | 41.7876 | 33.8291 | 36.6212 | 37.0656 | 36.3203 | 35.421 | 36.5935 | 36.4029 | 38.6306 | 25.1052 | 21.1398 | 29.1001 | 36.2831 | 34.4671 | 39.9599 | 37.602 | 36.4865 | 35.0861 | 37.4417 | 32.9961 | 38.0236 | 35.0306 | 35.8181 | 33.4132 | 37.854 | 37.0926 | 37.1745 | 39.3087 | 36.6046 | 37.2191 | 38.6371 | 39.6053 | 36.6754 | 39.136 | 38.1146 | 40.7194 | 35.8742 | 39.6684 | 36.7702 | 40.0963 | 37.0669 | 40.3806 | 36.7781 | 40.5804 | 36.2147 | 39.4274 | 41.1464 | 94.7858 | 94.9714 | 94.0811
2022-09-07 19:44 | 1:20 | 21.4328 | 21.5406 | 23.5378 | 35.9153 | 39.6692 | 35.3664 | 39.9444 | 34.2723 | 39.9811 | 36.691 | 36.7944 | 41.8286 | 33.7621 | 36.6273 | 37.0469 | 36.2859 | 35.3251 | 36.6601 | 36.3501 | 38.3521 | 25.038 | 21.0415 | 29.0094 | 36.2728 | 34.4295 | 39.7659 | 37.4781 | 36.2185 | 35.0317 | 37.2701 | 32.9595 | 37.6614 | 34.9765 | 35.7777 | 33.2603 | 37.6604 | 37.0033 | 37.1448 | 39.0933 | 36.4926 | 37.1752 | 38.5268 | 39.638 | 36.6476 | 39.0204 | 38.0823 | 40.4838 | 35.8164 | 39.784 | 36.6097 | 40.1845 | 36.7187 | 40.2806 | 36.6958 | 40.4753 | 36.1236 | 39.3071 | 41.024 | 94.5538 | 94.7968 | 93.8816
2022-09-07 19:44 | 1:20 | 21.5767 | 21.4683 | 23.4584 | 35.7457 | 39.6099 | 35.4958 | 39.9868 | 34.1651 | 39.895 | 36.7006 | 36.7341 | 41.8108 | 33.6848 | 36.4841 | 36.936 | 36.2272 | 35.2424 | 36.5039 | 36.3089 | 38.464 | 24.958 | 21.0289 | 28.9392 | 36.1818 | 34.3439 | 39.6202 | 37.3473 | 36.3145 | 34.9448 | 37.2089 | 32.8789 | 37.6812 | 34.9115 | 35.6708 | 33.1415 | 37.5664 | 36.9728 | 36.9912 | 39.3196 | 36.4836 | 37.1224 | 38.4597 | 39.4822 | 36.5548 | 38.9586 | 38.0617 | 40.6536 | 35.7449 | 39.6869 | 36.6066 | 39.9196 | 36.7774 | 40.3027 | 36.7335 | 40.6122 | 36.124 | 39.184 | 41.0832 | 94.3677 | 94.5502 | 93.7678
2022-09-07 19:44 | 1:20 | 21.7126 | 21.4721 | 23.3992 | 35.8223 | 39.6054 | 35.4054 | 40.0774 | 34.0828 | 39.7991 | 36.6698 | 36.654 | 41.7403 | 33.6871 | 36.3074 | 36.9108 | 36.1625 | 35.2508 | 36.31 | 36.2978 | 38.3711 | 24.8767 | 20.9641 | 28.8616 | 36.0154 | 34.2775 | 39.592 | 37.2784 | 36.1417 | 34.9271 | 37.2383 | 32.824 | 37.756 | 34.794 | 35.6081 | 33.1682 | 37.6336 | 37.0583 | 36.9862 | 39.3871 | 36.4856 | 37.1185 | 38.4012 | 39.3877 | 36.4956 | 39.0363 | 37.9426 | 40.3924 | 35.6972 | 39.5505 | 36.6463 | 39.9207 | 36.7566 | 40.2578 | 36.7235 | 40.501 | 36.0968 | 39.0793 | 40.9436 | 94.1555 | 94.3463 | 93.6467
2022-09-07 19:45 | 1:21 | 21.4408 | 21.4387 | 23.3985 | 35.6787 | 39.4843 | 35.1523 | 39.8606 | 34.0835 | 39.8021 | 36.8758 | 36.762 | 41.729 | 33.5776 | 36.2764 | 36.7279 | 36.0991 | 35.1754 | 36.3495 | 36.1434 | 38.2387 | 24.8471 | 20.9505 | 28.8212 | 35.9918 | 34.2056 | 39.6479 | 37.2191 | 35.98 | 34.7608 | 37.1415 | 32.7083 | 37.5624 | 34.769 | 35.5667 | 33.0915 | 37.5823 | 36.8809 | 36.8769 | 39.1642 | 36.3937 | 37.0303 | 38.4036 | 39.4287 | 36.4596 | 38.9286 | 37.8989 | 40.383 | 35.6663 | 39.4943 | 36.5559 | 40.1579 | 36.5799 | 40.1214 | 36.4855 | 40.4782 | 35.9725 | 39.2737 | 40.7724 | 93.9857 | 94.2174 | 93.521
2022-09-07 19:45 | 1:21 | 21.394 | 21.387 | 23.324 | 35.7495 | 39.4506 | 35.206 | 39.9499 | 34.0512 | 39.8133 | 36.6788 | 36.9511 | 41.5631 | 33.5483 | 36.354 | 36.6942 | 36.0411 | 35.1707 | 36.1975 | 36.2354 | 38.2116 | 24.809 | 20.8944 | 28.7393 | 35.9116 | 34.1604 | 39.4726 | 37.1752 | 36.068 | 34.706 | 37.1509 | 32.6005 | 37.6294 | 34.7289 | 35.6033 | 33.0064 | 37.581 | 36.8013 | 36.9045 | 39.0866 | 36.3524 | 37.0003 | 38.3148 | 39.2552 | 36.3615 | 38.8021 | 37.8211 | 40.3208 | 35.5423 | 39.4689 | 36.4607 | 40.0944 | 36.5455 | 40.0755 | 36.4282 | 40.3934 | 35.9113 | 38.9631 | 40.692 | 93.8036 | 94.0601 | 93.3695
2022-09-07 19:45 | 1:21 | 21.7962 | 21.3458 | 23.2634 | 35.4903 | 39.4177 | 35.1352 | 39.7901 | 33.9779 | 39.7524 | 36.4875 | 36.693 | 41.45 | 33.4375 | 36.2926 | 36.8307 | 35.9912 | 35.0661 | 36.1683 | 36.1653 | 38.1828 | 24.7586 | 20.8801 | 28.7066 | 35.8862 | 34.1101 | 39.4537 | 37.1224 | 35.8699 | 34.7813 | 37.0262 | 32.4929 | 37.5601 | 34.7095 | 35.5359 | 32.9453 | 37.6073 | 36.7193 | 36.6592 | 39.1262 | 36.2243 | 36.9496 | 38.2493 | 39.2304 | 36.2195 | 38.9582 | 37.787 | 40.2442 | 35.497 | 39.3456 | 36.4273 | 39.7424 | 36.4541 | 39.9769 | 36.4672 | 40.4021 | 35.8801 | 39.0201 | 40.6278 | 93.731 | 93.9907 | 93.3881
2022-09-07 19:45 | 1:21 | 21.9128 | 21.2975 | 23.2334 | 35.4533 | 39.3189 | 35.2092 | 39.8403 | 33.7811 | 39.6951 | 36.4391 | 36.6112 | 41.4624 | 33.4166 | 36.327 | 36.5719 | 35.9304 | 35.073 | 36.1518 | 36.1138 | 38.1098 | 24.7353 | 20.8014 | 28.7369 | 35.7004 | 34.0433 | 39.4029 | 37.1185 | 35.9768 | 34.6936 | 37.0687 | 32.4897 | 37.507 | 34.6242 | 35.4881 | 32.9188 | 37.3365 | 36.764 | 36.6326 | 39.1682 | 36.2051 | 36.877 | 38.1384 | 39.2739 | 36.1409 | 38.7861 | 37.7205 | 40.307 | 35.4372 | 39.3767 | 36.3446 | 39.8462 | 36.5896 | 39.887 | 36.4892 | 40.3227 | 35.9461 | 39.0445 | 40.5136 | 93.5435 | 93.8666 | 93.2066
2022-09-07 19:45 | 1:21 | 21.6749 | 21.3231 | 23.2588 | 35.4188 | 39.3452 | 35.1172 | 39.8094 | 33.7962 | 39.6136 | 36.4575 | 36.5733 | 41.4327 | 33.4558 | 36.2193 | 36.4935 | 35.8647 | 34.9633 | 35.9862 | 36.1233 | 37.9844 | 24.6956 | 20.7528 | 28.664 | 35.7613 | 33.9701 | 39.4027 | 37.0303 | 35.7331 | 34.6891 | 36.969 | 32.4738 | 37.4702 | 34.4982 | 35.3634 | 32.8425 | 37.2855 | 36.518 | 36.5421 | 38.9425 | 36.0757 | 36.785 | 38.0342 | 39.2705 | 36.1666 | 38.6188 | 37.6604 | 40.1262 | 35.4181 | 39.0983 | 36.4052 | 39.8357 | 36.4481 | 39.9108 | 36.1641 | 39.99 | 35.7972 | 38.9409 | 40.5888 | 93.5801 | 93.9196 | 93.3031
2022-09-07 19:45 | 1:21 | 21.2382 | 21.3019 | 23.2475 | 35.5186 | 39.3167 | 35.1087 | 39.768 | 33.8516 | 39.5553 | 36.3543 | 36.4778 | 41.3171 | 33.3693 | 36.184 | 36.4544 | 35.8121 | 34.9168 | 35.9826 | 35.989 | 37.87 | 24.6703 | 20.7537 | 28.6577 | 35.6796 | 33.9242 | 39.356 | 37.0003 | 35.8899 | 34.6332 | 36.9786 | 32.4301 | 37.302 | 34.5753 | 35.2485 | 32.8597 | 37.4638 | 36.6152 | 36.4122 | 39.0968 | 36.1021 | 36.7582 | 37.9397 | 39.1025 | 36.0501 | 38.5581 | 37.5892 | 40.1982 | 35.3158 | 39.0738 | 36.1337 | 39.5293 | 36.4446 | 39.8201 | 36.3294 | 40.1113 | 35.7082 | 38.8788 | 40.3779 | 93.5241 | 93.7536 | 93.25
2022-09-07 19:46 | 1:21 | 21.0934 | 21.2809 | 23.1657 | 35.4301 | 39.2019 | 34.8907 | 39.6377 | 33.9195 | 39.5414 | 36.2398 | 36.5498 | 41.2392 | 33.2612 | 36.2974 | 36.4341 | 35.7961 | 34.8795 | 35.9952 | 35.9462 | 37.8755 | 24.6361 | 20.7112 | 28.625 | 35.6123 | 33.855 | 39.4508 | 36.9496 | 35.6176 | 34.5311 | 36.8291 | 32.2379 | 37.3771 | 34.4501 | 35.2069 | 32.7163 | 37.2275 | 36.4832 | 36.4686 | 38.8399 | 35.9671 | 36.7401 | 37.9197 | 39.0656 | 35.9169 | 38.5341 | 37.4572 | 39.995 | 35.243 | 39.0635 | 36.1819 | 39.5087 | 36.3835 | 39.729 | 36.3125 | 40.0825 | 35.6704 | 38.8576 | 40.2194 | 93.5269 | 93.6683 | 93.2321
2022-09-07 19:46 | 1:22 | 21.2892 | 21.2218 | 23.1192 | 35.4337 | 39.2092 | 34.9353 | 39.4371 | 33.8227 | 39.4549 | 36.2156 | 36.4036 | 41.2484 | 33.272 | 36.0955 | 36.5139 | 35.7296 | 34.7987 | 35.8882 | 36.1194 | 37.941 | 24.6107 | 20.6108 | 28.5867 | 35.5589 | 33.8055 | 39.2236 | 36.877 | 35.6268 | 34.4621 | 36.7897 | 32.1141 | 37.2735 | 34.4568 | 35.1626 | 32.7337 | 37.0414 | 36.1749 | 36.3789 | 38.5826 | 35.7949 | 36.7508 | 37.8926 | 39.0545 | 35.9322 | 38.4926 | 37.4557 | 39.8518 | 35.2766 | 39.1441 | 36.2874 | 39.8045 | 36.335 | 39.7834 | 36.0742 | 40.1083 | 35.6664 | 38.7822 | 40.2084 | 93.4863 | 93.6051 | 93.2737
2022-09-07 19:46 | 1:22 | 21.4028 | 21.1606 | 23.1086 | 35.2492 | 39.1096 | 34.7541 | 39.5524 | 33.7719 | 39.4521 | 36.0692 | 36.3434 | 41.2439 | 33.2097 | 36.1406 | 36.339 | 35.7178 | 34.8427 | 36.0775 | 35.8775 | 37.7111 | 24.5598 | 20.5509 | 28.5077 | 35.545 | 33.7467 | 39.2879 | 36.785 | 35.5419 | 34.4673 | 36.6761 | 32.0809 | 37.2201 | 34.3625 | 35.1297 | 32.7274 | 37.1889 | 36.338 | 36.3997 | 38.5048 | 35.7865 | 36.586 | 37.775 | 38.9313 | 35.8274 | 38.3762 | 37.425 | 39.8235 | 35.2042 | 38.9153 | 36.0903 | 39.7784 | 36.3832 | 39.3687 | 35.9278 | 39.8454 | 35.5699 | 38.6079 | 40.3113 | 93.4844 | 93.5324 | 93.2763
2022-09-07 19:46 | 1:22 | 21.6731 | 21.1828 | 23.1238 | 35.2176 | 39.1282 | 34.8256 | 39.519 | 33.6879 | 39.3471 | 36.2683 | 36.4253 | 41.1197 | 33.1661 | 36.0872 | 36.2236 | 35.6019 | 34.7694 | 35.8175 | 35.8256 | 37.7654 | 24.5263 | 20.5689 | 28.5135 | 35.4792 | 33.7048 | 39.2402 | 36.7582 | 35.4791 | 34.3304 | 36.7144 | 32.1142 | 37.1439 | 34.2989 | 35.0857 | 32.6081 | 37.1342 | 36.3544 | 36.3268 | 38.3615 | 35.7924 | 36.5872 | 37.8036 | 38.919 | 35.9564 | 38.3278 | 37.3696 | 39.674 | 35.1273 | 38.9277 | 36.0485 | 39.599 | 36.2355 | 39.4418 | 35.9205 | 39.9304 | 35.4755 | 38.5281 | 40.1909 | 93.4102 | 93.4288 | 93.2417
2022-09-07 19:46 | 1:22 | 21.0381 | 21.168 | 23.0392 | 35.3331 | 39.0908 | 34.7893 | 39.4925 | 33.585 | 39.3 | 36.1157 | 36.1594 | 41.0075 | 33.0371 | 35.8443 | 36.3039 | 35.5094 | 34.6468 | 35.7174 | 35.747 | 37.8767 | 24.5098 | 20.4723 | 28.5302 | 35.4369 | 33.6319 | 39.1671 | 36.7401 | 35.5363 | 34.2445 | 36.7113 | 32.138 | 37.0546 | 34.28 | 34.9468 | 32.4759 | 37.0056 | 36.2976 | 36.285 | 38.196 | 35.7371 | 36.5551 | 37.7564 | 38.7613 | 35.9509 | 38.292 | 37.3038 | 39.696 | 35.1145 | 38.8442 | 35.9727 | 39.7231 | 36.0951 | 39.4346 | 35.8738 | 39.8809 | 35.4193 | 38.5611 | 40.2436 | 93.242 | 93.3039 | 93.1187
2022-09-07 19:46 | 1:22 | 20.7342 | 21.1149 | 22.9596 | 35.0504 | 38.9694 | 34.8558 | 39.45 | 33.4458 | 39.2159 | 35.9441 | 36.1035 | 40.966 | 33.0374 | 35.9073 | 36.1302 | 35.4651 | 34.6437 | 35.5656 | 35.703 | 37.5365 | 24.4529 | 20.3968 | 28.46 | 35.3575 | 33.6298 | 39.2966 | 36.7508 | 35.3763 | 34.2214 | 36.547 | 32.1577 | 36.9305 | 34.2356 | 34.996 | 32.4926 | 36.9977 | 36.1039 | 36.2627 | 38.456 | 35.6936 | 36.5874 | 37.6739 | 38.7106 | 35.9258 | 38.2438 | 37.2566 | 39.6749 | 35.0928 | 38.7903 | 35.9301 | 39.6474 | 36.0735 | 39.4901 | 35.892 | 39.8646 | 35.3321 | 38.4517 | 40.3088 | 93.1982 | 93.2149 | 93.0662
2022-09-07 19:47 | 1:23 | 20.4314 | 20.8912 | 22.8531 | 35.0315 | 38.9354 | 34.7699 | 39.1975 | 33.446 | 39.1902 | 36.0072 | 36.149 | 40.9601 | 33.0465 | 35.8147 | 36.081 | 35.4479 | 34.5909 | 35.6749 | 35.6068 | 37.508 | 24.4098 | 20.0842 | 28.4343 | 35.3161 | 33.5741 | 39.1411 | 36.586 | 35.4807 | 34.2755 | 36.4492 | 32.0972 | 36.868 | 34.157 | 34.8645 | 32.463 | 36.6825 | 36.257 | 36.0992 | 38.6427 | 35.7314 | 36.7052 | 37.5791 | 38.5941 | 35.8385 | 38.2231 | 37.2036 | 39.7255 | 34.9985 | 38.7555 | 35.9342 | 39.5839 | 35.9214 | 39.2434 | 35.8478 | 39.7806 | 35.3251 | 38.1862 | 40.0696 | 93.1241 | 93.1737 | 93.0533
2022-09-07 19:47 | 1:23 | 18.193 | 20.2048 | 22.0931 | 34.9374 | 38.8694 | 34.8393 | 39.132 | 33.3506 | 39.1748 | 35.9859 | 36.2076 | 40.9248 | 32.9117 | 35.712 | 35.9944 | 35.3794 | 34.5786 | 35.5401 | 35.5021 | 37.4016 | 24.5582 | 20.8465 | 29.0266 | 35.2973 | 33.5598 | 39.1011 | 36.5872 | 35.4614 | 34.2011 | 36.441 | 32.1977 | 36.9504 | 34.0356 | 34.8691 | 32.5991 | 36.6601 | 36.2114 | 36.0759 | 38.1783 | 35.7548 | 36.8117 | 37.683 | 38.6761 | 35.9099 | 38.3661 | 37.1444 | 39.7682 | 35.1783 | 38.6764 | 35.8871 | 39.5638 | 35.9818 | 39.2076 | 35.7398 | 39.721 | 35.4071 | 38.3882 | 40.0451 | 93.032 | 93.1422 | 92.9154
2022-09-07 19:47 | 1:23 | 17.5695 | 19.8668 | 21.6065 | 34.7311 | 38.8287 | 34.6006 | 39.1755 | 33.1721 | 39.0249 | 35.7944 | 35.9305 | 40.8449 | 32.74 | 35.6597 | 35.908 | 35.2248 | 34.368 | 35.2078 | 35.4206 | 37.2862 | 25.2045 | 22.1493 | 30.0963 | 35.4272 | 33.6056 | 39.294 | 36.5551 | 35.509 | 34.2856 | 36.5886 | 32.5792 | 36.8171 | 33.946 | 34.8964 | 32.7189 | 36.6509 | 36.1032 | 36.1028 | 38.2558 | 35.6353 | 36.8324 | 37.8349 | 38.8604 | 35.9898 | 38.3749 | 37.1262 | 39.7069 | 35.302 | 38.8384 | 35.9546 | 38.8724 | 36.1155 | 39.1917 | 35.7517 | 39.8187 | 35.5956 | 38.4817 | 39.9927 | 93.0458 | 93.102 | 92.9171
2022-09-07 19:47 | 1:23 | 17.1993 | 19.5532 | 21.2051 | 34.637 | 38.5658 | 34.3916 | 38.8583 | 33.1255 | 38.9793 | 35.839 | 35.7046 | 40.8248 | 32.6598 | 35.417 | 35.9244 | 35.157 | 34.3419 | 35.3824 | 35.3016 | 37.4516 | 26.0161 | 23.596 | 31.0481 | 35.477 | 33.6716 | 39.3232 | 36.5874 | 35.3923 | 34.2625 | 36.5554 | 32.8616 | 36.8315 | 33.931 | 34.9443 | 32.8311 | 36.7933 | 35.9604 | 36.0639 | 38.1825 | 35.5861 | 36.8745 | 37.9221 | 38.8462 | 36.0695 | 38.6528 | 37.0854 | 39.733 | 35.5448 | 38.8549 | 36.0926 | 38.4642 | 36.261 | 39.3085 | 35.8579 | 39.7888 | 35.7492 | 38.9137 | 39.9808 | 92.9882 | 93.0041 | 92.8781
2022-09-07 19:47 | 1:23 | 16.8094 | 19.2519 | 20.8483 | 34.4655 | 38.5466 | 34.4919 | 38.9099 | 33.0132 | 38.9226 | 35.7545 | 35.4366 | 40.7368 | 32.5206 | 35.2922 | 35.7319 | 35.1005 | 34.1712 | 35.1335 | 35.2079 | 37.1328 | 26.8712 | 24.9752 | 31.733 | 35.6212 | 33.7404 | 39.3115 | 36.7052 | 35.3002 | 34.2437 | 36.7111 | 33.0481 | 36.6854 | 33.8761 | 35.0535 | 33.0434 | 36.6857 | 35.9199 | 36.0442 | 38.0804 | 35.6443 | 36.9298 | 37.9898 | 38.9891 | 36.2188 | 38.6527 | 37.0524 | 39.686 | 35.6933 | 38.8167 | 36.2064 | 38.8275 | 36.4838 | 39.4676 | 35.9612 | 39.8821 | 35.8707 | 38.9308 | 40.0412 | 92.8685 | 92.945 | 92.7481
2022-09-07 19:47 | 1:23 | 16.4865 | 18.9168 | 20.6219 | 34.5824 | 38.4516 | 34.2813 | 38.678 | 32.9066 | 38.8181 | 35.6094 | 35.356 | 40.5713 | 32.4705 | 35.324 | 35.5713 | 35.0762 | 34.1485 | 35.2111 | 35.0347 | 37.196 | 27.6733 | 26.1871 | 32.2249 | 35.5734 | 33.7707 | 39.5433 | 36.8117 | 35.2436 | 34.2999 | 36.6842 | 33.2409 | 36.7087 | 33.8717 | 35.1343 | 33.0787 | 36.7219 | 35.8554 | 36.1651 | 37.9474 | 35.5637 | 36.8568 | 38.0437 | 39.1619 | 36.38 | 38.942 | 37.1051 | 39.8965 | 35.7812 | 38.93 | 36.219 | 38.8691 | 36.4827 | 39.5078 | 35.976 | 39.9996 | 35.9132 | 38.9297 | 40.0446 | 92.7596 | 92.8869 | 92.731
2022-09-07 19:48 | 1:23 | 16.1733 | 18.6553 | 20.3027 | 34.53 | 38.2991 | 34.1612 | 38.5455 | 32.7816 | 38.7584 | 35.6919 | 35.0736 | 40.4092 | 32.2972 | 35.2067 | 35.517 | 34.9263 | 33.8932 | 34.9051 | 35.0005 | 37.0909 | 28.361 | 27.1633 | 32.5595 | 35.724 | 33.7994 | 39.7029 | 36.8324 | 35.1297 | 34.1955 | 36.8765 | 33.398 | 36.7421 | 33.8387 | 35.1028 | 33.2255 | 36.6169 | 35.8088 | 36.0968 | 38.0422 | 35.563 | 36.9831 | 38.0934 | 39.1628 | 36.4765 | 38.9479 | 37.0874 | 39.8351 | 35.9263 | 38.9993 | 36.2221 | 38.8473 | 36.6184 | 39.5494 | 35.9896 | 39.8059 | 36.0219 | 39.0623 | 39.9839 | 92.6902 | 92.7724 | 92.7093
2022-09-07 19:48 | 1:24 | 15.808 | 18.3185 | 20.0976 | 34.2677 | 38.0865 | 34.0998 | 38.3642 | 32.5973 | 38.6659 | 35.5964 | 35.1829 | 40.4155 | 32.1887 | 35.1544 | 35.5346 | 34.9011 | 33.8923 | 34.7668 | 34.8776 | 37.1695 | 28.9762 | 27.9608 | 32.8054 | 35.6109 | 33.8355 | 39.6909 | 36.8745 | 35.2268 | 34.2877 | 36.8002 | 33.4848 | 36.7257 | 33.7972 | 35.2326 | 33.3275 | 36.6586 | 35.7893 | 36.1042 | 37.8268 | 35.5733 | 37.0136 | 38.1509 | 39.1142 | 36.5104 | 38.8632 | 37.0845 | 39.8305 | 35.9213 | 39.059 | 36.2543 | 38.716 | 36.7065 | 39.4862 | 35.9493 | 39.8564 | 36.0628 | 39.0164 | 40.0831 | 92.5517 | 92.6654 | 92.5706
2022-09-07 19:48 | 1:24 | 15.5557 | 18.1277 | 19.7784 | 34.0997 | 38.0374 | 34.1894 | 38.3099 | 32.5942 | 38.5936 | 35.5416 | 34.8984 | 40.31 | 32.0944 | 35.1808 | 35.4206 | 34.7775 | 33.8818 | 34.8071 | 34.8122 | 37.0086 | 29.4861 | 28.5769 | 33.0007 | 35.6538 | 33.8571 | 39.7632 | 36.9298 | 35.2851 | 34.2418 | 36.8389 | 33.5936 | 36.4706 | 33.6704 | 35.1638 | 33.35 | 36.6034 | 35.6988 | 35.988 | 38.0268 | 35.5707 | 36.9981 | 38.2091 | 39.1613 | 36.6042 | 39.0142 | 37.1009 | 39.7489 | 35.9974 | 39.0365 | 36.2766 | 38.5591 | 36.7206 | 39.6343 | 35.9488 | 39.8289 | 36.094 | 39.0667 | 40.0102 | 92.4312 | 92.5335 | 92.5013
2022-09-07 19:48 | 1:24 | 15.3148 | 17.8282 | 19.5049 | 33.9511 | 37.9036 | 34.1005 | 38.1834 | 32.4069 | 38.4907 | 35.3732 | 34.7501 | 40.2229 | 31.9196 | 34.992 | 35.6272 | 34.6639 | 33.7785 | 34.5847 | 34.8775 | 36.866 | 29.9161 | 29.0415 | 33.1253 | 35.658 | 33.9449 | 39.9091 | 36.8568 | 35.1117 | 34.1429 | 36.7403 | 33.6404 | 36.4973 | 33.6894 | 35.1728 | 33.4102 | 36.8321 | 35.6282 | 36.0405 | 37.9707 | 35.5397 | 36.9829 | 38.2517 | 39.1531 | 36.6197 | 38.9747 | 37.0836 | 39.838 | 36.0924 | 39.041 | 36.3046 | 38.5277 | 36.8344 | 39.4971 | 35.9745 | 39.6484 | 36.1283 | 39.1193 | 39.919 | 92.3538 | 92.4269 | 92.4117
2022-09-07 19:48 | 1:24 | 15.0649 | 17.5848 | 19.354 | 34.0176 | 37.9099 | 33.9328 | 38.0327 | 32.2865 | 38.4333 | 35.5564 | 34.5868 | 40.1316 | 31.9029 | 34.7604 | 35.6045 | 34.6546 | 33.6251 | 34.5808 | 34.6888 | 36.9295 | 30.3148 | 29.3941 | 33.2619 | 35.6665 | 33.9143 | 39.7457 | 36.9831 | 34.9851 | 34.0692 | 36.7983 | 33.692 | 36.3804 | 33.5673 | 35.1688 | 33.483 | 36.6839 | 35.672 | 35.9637 | 37.6701 | 35.5323 | 36.975 | 38.2026 | 39.2505 | 36.687 | 39.1258 | 37.0789 | 39.7364 | 36.1937 | 39.0274 | 36.3211 | 38.4429 | 36.8491 | 39.4885 | 35.9099 | 39.8342 | 36.2026 | 39.0008 | 39.9347 | 92.2499 | 92.3235 | 92.3347
2022-09-07 19:48 | 1:24 | 14.9025 | 17.3714 | 19.1686 | 33.8929 | 37.672 | 33.9288 | 37.7307 | 32.1153 | 38.3667 | 35.2174 | 34.739 | 39.8229 | 31.8016 | 34.7398 | 35.3457 | 34.5783 | 33.5573 | 34.5274 | 34.6176 | 36.7516 | 30.5954 | 29.6726 | 33.3321 | 35.6977 | 33.9387 | 40.044 | 37.0136 | 35.1568 | 34.1459 | 36.9546 | 33.7296 | 36.2131 | 33.6665 | 35.1914 | 33.5733 | 36.7196 | 35.6741 | 35.8756 | 37.711 | 35.5357 | 37.0598 | 38.26 | 39.3011 | 36.7107 | 39.1884 | 37.0751 | 39.8756 | 36.1638 | 39.0619 | 36.4173 | 38.4316 | 36.9254 | 39.4526 | 36.0052 | 39.7875 | 36.2352 | 39.1257 | 40.0127 | 92.1829 | 92.1744 | 92.3334
2022-09-07 19:49 | 1:24 | 14.5532 | 17.0847 | 18.9547 | 33.8397 | 37.5029 | 33.8081 | 37.8736 | 32.1077 | 38.197 | 35.2963 | 34.2068 | 39.8338 | 31.6739 | 34.6878 | 35.2441 | 34.4812 | 33.3701 | 34.4972 | 34.4923 | 36.6597 | 30.869 | 29.8937 | 33.4158 | 35.7711 | 33.9721 | 39.9224 | 36.9981 | 35.3834 | 34.1232 | 36.805 | 33.8227 | 36.2624 | 33.5558 | 35.2868 | 33.5879 | 36.6601 | 35.5057 | 35.9426 | 37.8012 | 35.4761 | 37.0866 | 38.2129 | 39.3385 | 36.7282 | 39.2016 | 37.0958 | 39.8256 | 36.2248 | 39.0937 | 36.3536 | 38.512 | 36.8797 | 39.4775 | 36.018 | 39.9672 | 36.2881 | 39.0635 | 40.0006 | 91.9741 | 92.0597 | 92.084
2022-09-07 19:49 | 1:25 | 14.4178 | 16.8795 | 18.768 | 33.7274 | 37.3601 | 33.617 | 37.6068 | 31.9271 | 38.1813 | 35.1883 | 34.3124 | 39.806 | 31.4774 | 34.6428 | 35.193 | 34.3766 | 33.3167 | 34.3634 | 34.3514 | 36.81 | 31.0951 | 30.0554 | 33.4954 | 35.752 | 33.9533 | 39.8765 | 36.9829 | 35.0827 | 34.0962 | 36.7542 | 33.868 | 36.1898 | 33.4378 | 35.2048 | 33.6567 | 36.6961 | 35.4938 | 35.9211 | 37.8277 | 35.4391 | 37.0742 | 38.2803 | 39.2549 | 36.7762 | 39.2454 | 37.0461 | 39.8289 | 36.3158 | 39.1701 | 36.3947 | 38.3289 | 36.9549 | 39.3778 | 36.0339 | 40.0128 | 36.2877 | 39.0791 | 39.9898 | 91.8837 | 91.9941 | 92.0841
2022-09-07 19:49 | 1:25 | 14.218 | 16.6786 | 18.5595 | 33.5149 | 37.3052 | 33.5174 | 37.5047 | 31.8036 | 38.1218 | 35.1613 | 34.3174 | 39.7761 | 31.4634 | 34.3539 | 35.2146 | 34.261 | 33.2599 | 34.1531 | 34.2343 | 36.6295 | 31.2817 | 30.1901 | 33.5672 | 35.7178 | 33.9852 | 40.0226 | 36.975 | 34.9793 | 34.1252 | 36.8369 | 33.9072 | 36.0932 | 33.37 | 35.1956 | 33.7295 | 36.4915 | 35.4541 | 36.0435 | 37.4838 | 35.3859 | 37.0947 | 38.3349 | 39.2833 | 36.8383 | 39.1581 | 37.1459 | 39.8171 | 36.3999 | 39.1722 | 36.4913 | 38.3388 | 37.0418 | 39.4439 | 36.0522 | 39.9048 | 36.3607 | 39.1834 | 39.9227 | 91.8968 | 92.0274 | 92.1593
2022-09-07 19:49 | 1:25 | 13.9895 | 16.4444 | 18.3489 | 33.5348 | 37.2287 | 33.3435 | 37.5146 | 31.6051 | 37.9715 | 35.0371 | 33.9219 | 39.6393 | 31.3542 | 34.3628 | 35.1025 | 34.2365 | 33.1831 | 33.8221 | 34.0846 | 36.6948 | 31.4592 | 30.3163 | 33.62 | 35.7298 | 34.0733 | 40.0971 | 37.0598 | 34.8779 | 33.9498 | 36.9806 | 33.9379 | 36.1277 | 33.323 | 35.159 | 33.7968 | 36.6633 | 35.4201 | 35.8919 | 37.3998 | 35.4024 | 37.0639 | 38.3293 | 39.3475 | 36.8489 | 39.2033 | 37.1054 | 39.8029 | 36.365 | 39.1268 | 36.4862 | 38.4096 | 37.0907 | 39.4463 | 36.1719 | 39.9669 | 36.4269 | 39.2271 | 39.9217 | 91.9408 | 92.078 | 92.1452
2022-09-07 19:49 | 1:25 | 13.7981 | 16.2485 | 18.1435 | 33.4066 | 37.1341 | 33.2749 | 37.4632 | 31.7174 | 37.88 | 35.1654 | 33.9829 | 39.4751 | 31.2193 | 34.098 | 35.0911 | 34.1505 | 33.0177 | 33.7759 | 33.9908 | 36.602 | 31.5876 | 30.3958 | 33.6655 | 35.5802 | 34.0525 | 39.9571 | 37.0866 | 34.934 | 34.0225 | 36.8689 | 33.9872 | 35.9438 | 33.3005 | 35.1987 | 33.812 | 36.6828 | 35.3522 | 35.8992 | 37.5016 | 35.3749 | 37.1564 | 38.4058 | 39.3855 | 36.891 | 39.2067 | 37.1517 | 39.8888 | 36.4564 | 39.2314 | 36.4592 | 38.443 | 37.0703 | 39.4573 | 36.1057 | 40.057 | 36.4499 | 39.2975 | 39.9232 | 92.1562 | 92.2395 | 92.3995
2022-09-07 19:49 | 1:25 | 13.6232 | 16.0242 | 17.8185 | 33.4751 | 37.0493 | 33.3154 | 37.3479 | 31.4069 | 37.8148 | 35.0589 | 33.7166 | 39.298 | 31.1249 | 34.032 | 34.9941 | 34.0365 | 32.9454 | 33.9341 | 33.9186 | 36.5154 | 31.7079 | 30.4301 | 33.7167 | 35.5465 | 34.0252 | 39.8271 | 37.0742 | 35.0613 | 34.0601 | 36.9473 | 34.0067 | 35.8402 | 33.3715 | 35.1091 | 33.8761 | 36.3461 | 35.2718 | 35.8657 | 37.7082 | 35.2942 | 37.1579 | 38.4132 | 39.4591 | 36.974 | 39.2629 | 37.1419 | 39.7463 | 36.4881 | 39.296 | 36.4664 | 38.5084 | 37.1675 | 39.3753 | 36.2311 | 39.979 | 36.4928 | 39.3403 | 39.8496 | 92.2616 | 92.3366 | 92.3769
2022-09-07 19:50 | 1:26 | 13.4014 | 15.8276 | 17.5916 | 33.3231 | 36.8624 | 33.6376 | 37.3511 | 31.3376 | 37.6839 | 35.0463 | 33.645 | 39.3259 | 31.159 | 33.6858 | 34.7097 | 33.9021 | 32.9041 | 33.5479 | 33.8249 | 36.3806 | 31.8142 | 30.5187 | 33.7557 | 35.5114 | 34.0518 | 39.7976 | 37.0947 | 34.8496 | 34.0208 | 36.8354 | 34.059 | 35.9604 | 33.334 | 35.2011 | 33.9073 | 36.252 | 35.2964 | 35.8133 | 37.3866 | 35.2856 | 37.1913 | 38.4507 | 39.3698 | 37.0298 | 39.2213 | 37.1791 | 39.9153 | 36.5739 | 39.2697 | 36.5186 | 38.4965 | 37.1982 | 39.3019 | 36.3024 | 40.0605 | 36.5873 | 39.4292 | 39.8359 | 92.2657 | 92.4284 | 92.3677
2022-09-07 19:50 | 1:26 | 13.2522 | 15.6474 | 17.4764 | 33.0477 | 36.7894 | 33.2142 | 36.9066 | 31.2094 | 37.4949 | 35.0026 | 33.6471 | 39.3042 | 30.8449 | 33.821 | 34.7661 | 33.8977 | 32.8402 | 33.7749 | 33.7901 | 36.4792 | 31.9069 | 30.5556 | 33.7743 | 35.5521 | 34.0972 | 39.7877 | 37.0639 | 34.9102 | 34.1617 | 36.913 | 34.0934 | 35.7946 | 33.2998 | 35.2725 | 33.9329 | 36.4001 | 35.3485 | 35.9371 | 37.1076 | 35.2902 | 37.217 | 38.4475 | 39.3993 | 37.0751 | 39.3743 | 37.1523 | 39.8525 | 36.6076 | 39.2373 | 36.5964 | 38.6447 | 37.225 | 39.4387 | 36.2607 | 40.0613 | 36.6146 | 39.3622 | 39.8409 | 92.3186 | 92.5389 | 92.3937
2022-09-07 19:50 | 1:26 | 12.8748 | 14.6331 | 17.2345 | 33.1341 | 36.7506 | 33.061 | 36.8597 | 31.1031 | 37.3954 | 34.9428 | 33.4136 | 39.1409 | 30.8505 | 33.6279 | 34.5926 | 33.7935 | 32.7925 | 33.5725 | 33.6378 | 36.2586 | 31.9663 | 30.5751 | 33.8108 | 35.4822 | 34.1383 | 39.8021 | 37.1564 | 34.8465 | 34.1194 | 36.8605 | 34.1569 | 35.6516 | 33.1988 | 35.1958 | 33.9948 | 36.2364 | 35.373 | 35.8475 | 36.9971 | 35.2438 | 37.2324 | 38.4693 | 39.4355 | 37.1002 | 39.3261 | 37.1547 | 39.7913 | 36.6829 | 39.2824 | 36.5691 | 38.6082 | 37.2653 | 39.4608 | 36.3006 | 40.1257 | 36.6968 | 39.5198 | 39.9241 | 92.4617 | 92.6633 | 92.4497
2022-09-07 19:50 | 1:26 | 13.9516 | 13.9815 | 18.5401 | 33.0317 | 36.5742 | 32.9708 | 36.955 | 30.9554 | 37.3061 | 34.6076 | 33.2206 | 38.9802 | 30.7774 | 33.5266 | 34.5549 | 33.7144 | 32.5686 | 33.6223 | 33.5199 | 36.2216 | 31.956 | 30.5895 | 33.8065 | 35.4507 | 34.1435 | 39.9176 | 37.1579 | 34.9022 | 34.1469 | 37.0244 | 34.2203 | 35.6467 | 33.2813 | 35.3126 | 34.0107 | 36.2015 | 35.216 | 35.8038 | 37.045 | 35.2112 | 37.2938 | 38.5639 | 39.4554 | 37.1886 | 39.2504 | 37.2339 | 39.7053 | 36.7383 | 39.3403 | 36.6794 | 38.6866 | 37.2972 | 39.716 | 36.3384 | 40.1 | 36.7649 | 39.5847 | 39.8587 | 92.549 | 92.7989 | 92.5982
2022-09-07 19:50 | 1:26 | 16.4165 | 16.502 | 21.9793 | 33.498 | 36.5664 | 32.9803 | 36.7842 | 31.2133 | 37.2654 | 34.7151 | 33.4486 | 39.0736 | 31.1844 | 33.8166 | 34.9835 | 33.7148 | 32.7788 | 33.8845 | 33.7899 | 36.4408 | 32.0113 | 30.6275 | 33.8788 | 35.7012 | 34.1688 | 39.8844 | 37.1913 | 34.7457 | 34.153 | 36.9918 | 34.2332 | 35.6014 | 33.4623 | 35.3167 | 34.082 | 36.3703 | 35.3248 | 35.8583 | 37.4959 | 35.2264 | 37.3627 | 38.6003 | 39.5844 | 37.2714 | 39.3753 | 37.2959 | 39.8014 | 36.8074 | 39.501 | 36.6762 | 38.7417 | 37.368 | 39.533 | 36.3506 | 40.0564 | 36.8069 | 39.4922 | 39.9005 | 92.6913 | 92.9306 | 92.7004
2022-09-07 19:50 | 1:26 | 18.7425 | 19.339 | 24.6914 | 34.1247 | 36.6213 | 33.2724 | 36.8562 | 31.6075 | 37.2847 | 35.0741 | 33.9748 | 39.1673 | 31.5675 | 34.2135 | 35.0272 | 33.7702 | 32.9671 | 34.2145 | 33.8687 | 36.5636 | 32.1184 | 30.7032 | 33.9523 | 35.8299 | 34.2516 | 39.7838 | 37.217 | 34.8089 | 34.1654 | 36.9218 | 34.2983 | 35.7199 | 33.6857 | 35.3919 | 34.1556 | 36.3377 | 35.4007 | 36.0205 | 37.466 | 35.31 | 37.3479 | 38.6394 | 39.6047 | 37.3566 | 39.4039 | 37.3177 | 39.7403 | 36.9149 | 39.4398 | 36.7941 | 38.7245 | 37.5003 | 39.4562 | 36.5518 | 40.0733 | 36.8734 | 39.4173 | 39.9902 | 92.7656 | 93.038 | 92.74
2022-09-07 19:51 | 1:26 | 20.7696 | 21.9606 | 26.6266 | 34.656 | 36.6547 | 33.4914 | 36.9879 | 31.8822 | 37.3378 | 35.188 | 34.3989 | 39.0697 | 31.9497 | 34.3299 | 35.2264 | 33.819 | 33.2911 | 34.4596 | 34.0582 | 36.823 | 32.197 | 30.826 | 34.0678 | 36.0279 | 34.3024 | 39.7417 | 37.2324 | 34.8009 | 34.09 | 36.9301 | 34.3686 | 35.7859 | 33.7744 | 35.5111 | 34.2456 | 36.5844 | 35.4692 | 36.1319 | 37.6856 | 35.3796 | 37.3804 | 38.66 | 39.6504 | 37.4657 | 39.383 | 37.3457 | 39.7809 | 36.9939 | 39.4336 | 36.8197 | 38.6954 | 37.5111 | 39.557 | 36.5825 | 40.0578 | 36.9334 | 39.5857 | 39.9368 | 92.8941 | 93.1358 | 92.8547
2022-09-07 19:51 | 1:27 | 22.5314 | 24.2752 | 28.4542 | 35.0022 | 36.6493 | 33.6742 | 37.1168 | 32.2118 | 37.3518 | 35.3296 | 34.585 | 39.2807 | 32.2408 | 34.5604 | 35.1893 | 33.9092 | 33.491 | 34.659 | 34.2068 | 36.8802 | 32.3034 | 30.9588 | 34.2019 | 36.1761 | 34.3772 | 40.0244 | 37.2938 | 34.8531 | 34.1003 | 37.1305 | 34.4186 | 35.8166 | 33.8596 | 35.5705 | 34.3275 | 36.5539 | 35.5378 | 36.2008 | 37.8271 | 35.4192 | 37.4406 | 38.6799 | 39.7026 | 37.5904 | 39.4937 | 37.4096 | 39.8671 | 37.0742 | 39.5111 | 36.8293 | 38.8484 | 37.6335 | 39.5894 | 36.6163 | 40.0351 | 36.9858 | 39.644 | 39.9849 | 93.0051 | 93.2445 | 92.9013
2022-09-07 19:51 | 1:27 | 23.9792 | 26.1045 | 29.3315 | 35.4155 | 36.6974 | 33.8923 | 37.4611 | 32.392 | 37.3454 | 35.3961 | 34.764 | 39.2432 | 32.5059 | 34.6985 | 35.2454 | 33.9679 | 33.6733 | 34.9582 | 34.3365 | 37.0752 | 32.4214 | 31.0769 | 34.3311 | 36.3611 | 34.421 | 40.2483 | 37.3627 | 34.8633 | 34.3303 | 37.0508 | 34.5239 | 35.8468 | 34.0078 | 35.6788 | 34.3975 | 36.5706 | 35.6281 | 36.2599 | 37.9965 | 35.4995 | 37.5428 | 38.7564 | 39.7133 | 37.6509 | 39.655 | 37.4583 | 39.8631 | 37.1793 | 39.5846 | 36.9218 | 38.8525 | 37.6599 | 39.5677 | 36.6073 | 40.0096 | 37.0763 | 39.709 | 40.0101 | 93.1904 | 93.3945 | 93.0653
2022-09-07 19:51 | 1:27 | 25.2043 | 27.5497 | 29.7978 | 35.773 | 36.7515 | 33.9718 | 37.4545 | 32.5546 | 37.3079 | 35.5468 | 34.9594 | 39.1376 | 32.6556 | 34.7384 | 35.5294 | 34.0367 | 33.8111 | 35.0298 | 34.4025 | 37.1296 | 32.5235 | 31.1946 | 34.4729 | 36.4647 | 34.4746 | 39.9704 | 37.3479 | 35.1701 | 34.3666 | 37.0841 | 34.5806 | 35.9878 | 34.1376 | 35.8115 | 34.4749 | 36.7116 | 35.6703 | 36.4008 | 38.0661 | 35.5406 | 37.5095 | 38.7868 | 39.8536 | 37.7344 | 39.9037 | 37.4612 | 39.9096 | 37.2811 | 39.5639 | 36.9921 | 38.8438 | 37.7991 | 39.551 | 36.6761 | 40.0625 | 37.1365 | 39.6951 | 40.0442 | 93.3464 | 93.5387 | 93.1396
2022-09-07 19:51 | 1:27 | 26.1804 | 28.6816 | 30.2321 | 35.8218 | 36.8181 | 34.0311 | 37.4004 | 32.7892 | 37.3745 | 35.6153 | 35.1868 | 39.1931 | 32.8394 | 34.9193 | 35.6476 | 34.0771 | 33.9781 | 35.1675 | 34.4767 | 37.28 | 32.6314 | 31.2847 | 34.6286 | 36.4436 | 34.5462 | 40.1436 | 37.3804 | 35.1182 | 34.5886 | 37.1473 | 34.6529 | 35.9943 | 34.2078 | 35.8882 | 34.5136 | 36.7065 | 35.6978 | 36.4788 | 38.0589 | 35.6079 | 37.521 | 38.8081 | 39.8378 | 37.8292 | 39.761 | 37.5023 | 39.9293 | 37.3289 | 39.5618 | 37.0891 | 38.8238 | 37.8109 | 39.7683 | 36.8231 | 40.1446 | 37.2247 | 39.6898 | 40.1516 | 93.5342 | 93.7935 | 93.2776
2022-09-07 19:51 | 1:27 | 26.9771 | 29.4914 | 30.4845 | 36.0716 | 36.889 | 34.2224 | 37.6182 | 32.9521 | 37.401 | 35.692 | 35.323 | 39.2088 | 32.9902 | 35.0197 | 35.5211 | 34.136 | 34.0935 | 35.2789 | 34.5501 | 37.3147 | 32.778 | 31.3681 | 34.82 | 36.5515 | 34.6151 | 40.1524 | 37.4406 | 35.1663 | 34.5286 | 37.2791 | 34.69 | 36.064 | 34.339 | 36.0403 | 34.6301 | 36.767 | 35.739 | 36.5541 | 38.0866 | 35.6701 | 37.5689 | 38.8418 | 39.8522 | 37.9097 | 39.7036 | 37.5164 | 39.8441 | 37.4071 | 39.7435 | 37.1295 | 38.9388 | 37.931 | 39.622 | 36.9563 | 40.2583 | 37.2707 | 39.7276 | 40.1864 | 93.6299 | 93.9345 | 93.404
2022-09-07 19:52 | 1:28 | 27.5648 | 30.0756 | 30.7579 | 36.2138 | 36.8907 | 34.3012 | 37.671 | 33.0975 | 37.4371 | 35.6732 | 35.4478 | 39.4393 | 33.0975 | 35.1178 | 35.6355 | 34.1561 | 34.1825 | 35.3595 | 34.6274 | 37.3265 | 32.9195 | 31.4245 | 34.9872 | 36.6682 | 34.7277 | 40.2159 | 37.5428 | 35.2512 | 34.5163 | 37.2595 | 34.7944 | 36.1208 | 34.44 | 36.0461 | 34.693 | 36.8051 | 35.8158 | 36.5292 | 38.1624 | 35.7151 | 37.6293 | 38.9868 | 39.8789 | 38.0198 | 39.85 | 37.5513 | 39.9547 | 37.5274 | 39.7682 | 37.1624 | 39.0185 | 37.9213 | 39.7495 | 37.0459 | 40.1904 | 37.3712 | 39.8004 | 40.1613 | 93.774 | 94.0878 | 93.4741
2022-09-07 19:52 | 1:28 | 28.0727 | 30.4811 | 30.876 | 36.4189 | 36.9268 | 34.4265 | 37.5348 | 33.1544 | 37.4328 | 35.7433 | 35.4064 | 39.3883 | 33.1628 | 35.172 | 35.7215 | 34.1659 | 34.3475 | 35.3407 | 34.7011 | 37.396 | 33.0484 | 31.4676 | 35.143 | 36.7565 | 34.784 | 40.1097 | 37.5095 | 35.2384 | 34.6407 | 37.312 | 34.8523 | 36.0634 | 34.5086 | 36.1133 | 34.7169 | 36.7743 | 35.9139 | 36.6296 | 38.0318 | 35.775 | 37.6789 | 39.0425 | 40.0051 | 38.113 | 39.8348 | 37.6569 | 40.0166 | 37.604 | 39.8215 | 37.2162 | 38.9419 | 37.959 | 39.7649 | 37.0898 | 40.2247 | 37.4645 | 39.7587 | 40.2176 | 93.9844 | 94.2521 | 93.4815
2022-09-07 19:52 | 1:28 | 28.4908 | 30.7674 | 31.0512 | 36.3261 | 36.902 | 34.5408 | 37.6408 | 33.3006 | 37.416 | 35.8892 | 35.4708 | 39.2988 | 33.3038 | 35.2137 | 35.8431 | 34.2341 | 34.4176 | 35.4645 | 34.7579 | 37.4447 | 33.1944 | 31.524 | 35.3147 | 36.822 | 34.8698 | 40.1793 | 37.521 | 35.5588 | 34.7206 | 37.3573 | 34.9453 | 36.2132 | 34.6175 | 36.2064 | 34.8591 | 36.7845 | 35.9907 | 36.7285 | 38.0374 | 35.8333 | 37.7213 | 39.0266 | 40.0283 | 38.2167 | 39.8329 | 37.6666 | 40.0067 | 37.6585 | 39.8614 | 37.2829 | 38.9945 | 38.0405 | 39.8292 | 37.1381 | 40.2242 | 37.5186 | 39.8054 | 40.1981 | 94.1084 | 94.4426 | 93.6176
2022-09-07 19:52 | 1:28 | 28.8152 | 30.9846 | 31.1205 | 36.5188 | 36.9031 | 34.592 | 37.6696 | 33.4558 | 37.4679 | 35.9333 | 35.6807 | 39.3612 | 33.3779 | 35.2905 | 35.9042 | 34.2853 | 34.4881 | 35.5442 | 34.8005 | 37.5242 | 33.3404 | 31.5423 | 35.4763 | 36.8596 | 34.942 | 40.3113 | 37.5689 | 35.5635 | 34.6516 | 37.4783 | 35.0503 | 36.1646 | 34.692 | 36.2991 | 34.9081 | 36.8205 | 35.9918 | 36.7168 | 38.0675 | 35.8885 | 37.7514 | 39.1359 | 40.1027 | 38.2927 | 39.89 | 37.7479 | 39.9611 | 37.7498 | 40.0297 | 37.3836 | 39.0611 | 38.0433 | 39.8557 | 37.1391 | 40.2165 | 37.591 | 39.9538 | 40.2045 | 94.2657 | 94.67 | 93.7919
2022-09-07 19:52 | 1:28 | 29.0902 | 31.1384 | 31.2535 | 36.6857 | 36.9371 | 34.6612 | 37.6748 | 33.5177 | 37.485 | 36.0583 | 35.6757 | 39.2834 | 33.4877 | 35.3992 | 35.8425 | 34.3199 | 34.5872 | 35.5985 | 34.8534 | 37.5703 | 33.4674 | 31.5896 | 35.6042 | 36.989 | 35.034 | 40.3288 | 37.6293 | 35.4571 | 34.7996 | 37.4252 | 35.0994 | 36.2975 | 34.8089 | 36.3392 | 34.9851 | 36.946 | 36.0516 | 36.7809 | 38.0973 | 35.9093 | 37.7595 | 39.1791 | 40.1385 | 38.3425 | 39.8883 | 37.7293 | 39.994 | 37.8055 | 40.0523 | 37.3953 | 39.114 | 38.1219 | 39.8625 | 37.2041 | 40.254 | 37.6245 | 40.0487 | 40.1794 | 94.476 | 94.8567 | 93.935
2022-09-07 19:52 | 1:28 | 29.3359 | 31.2569 | 31.3919 | 36.7626 | 36.9535 | 34.7477 | 37.6666 | 33.653 | 37.4696 | 36.0407 | 35.7637 | 39.2604 | 33.5938 | 35.4498 | 35.9227 | 34.3456 | 34.6432 | 35.6685 | 34.9215 | 37.6074 | 33.6251 | 31.5942 | 35.7614 | 37.0894 | 35.1132 | 40.4658 | 37.6789 | 35.4517 | 34.7765 | 37.5859 | 35.1769 | 36.2079 | 34.8534 | 36.3362 | 35.0782 | 36.9764 | 36.0731 | 36.8084 | 38.1466 | 35.998 | 37.6557 | 39.1802 | 40.2129 | 38.4361 | 40.034 | 37.776 | 40.1365 | 37.9074 | 39.9669 | 37.4222 | 39.2016 | 38.2012 | 39.8317 | 37.296 | 40.2877 | 37.6925 | 40.0661 | 40.1827 | 94.5847 | 94.9768 | 94.0045
2022-09-07 19:53 | 1:28 | 29.5911 | 31.3562 | 31.4138 | 36.8179 | 36.9785 | 34.8044 | 37.7062 | 33.7482 | 37.536 | 36.07 | 35.7595 | 39.3354 | 33.6649 | 35.468 | 35.9896 | 34.3831 | 34.7538 | 35.718 | 34.9711 | 37.6954 | 33.7745 | 31.6254 | 35.8982 | 37.1939 | 35.1275 | 40.6419 | 37.7213 | 35.4941 | 34.9606 | 37.6516 | 35.2865 | 36.354 | 34.9034 | 36.4014 | 35.1813 | 37.0199 | 36.2095 | 36.9193 | 38.1779 | 35.9913 | 37.7402 | 39.2685 | 40.2232 | 38.4985 | 39.9887 | 37.8416 | 40.1229 | 38.0015 | 40.0515 | 37.457 | 39.182 | 38.2756 | 40.0038 | 37.4078 | 40.2816 | 37.7829 | 40.0985 | 40.3065 | 94.7234 | 95.128 | 94.094
2022-09-07 19:53 | 1:29 | 30.438 | 25.429 | 31.0909 | 36.8681 | 36.9583 | 34.8324 | 37.7603 | 33.7192 | 37.5497 | 36.0353 | 35.8987 | 39.3391 | 33.6945 | 35.4817 | 36.0527 | 34.4322 | 34.8277 | 35.7233 | 35.0624 | 37.7519 | 34.2771 | 27.8295 | 35.6324 | 37.328 | 35.2174 | 40.4968 | 37.7514 | 35.5651 | 34.8818 | 37.7222 | 35.1929 | 36.3667 | 34.9268 | 36.4122 | 35.1646 | 37.0207 | 36.2998 | 36.8907 | 38.2597 | 36.0445 | 37.7643 | 39.2276 | 40.2057 | 38.3851 | 40.0224 | 37.8246 | 40.1416 | 37.8286 | 40.039 | 37.4159 | 39.0509 | 38.1968 | 39.9438 | 37.332 | 40.3219 | 37.6812 | 40.0978 | 40.3977 | 94.7564 | 95.272 | 94.2243
2022-09-07 19:53 | 1:29 | 30.4617 | 28.811 | 31.0783 | 36.7404 | 36.9758 | 34.8075 | 37.7436 | 33.7625 | 37.5847 | 36.0987 | 35.9711 | 39.3274 | 33.7741 | 35.6262 | 36.0932 | 34.4656 | 34.8733 | 35.7754 | 35.073 | 37.5856 | 34.1552 | 29.375 | 35.0008 | 37.297 | 35.1095 | 40.3717 | 37.7595 | 35.6083 | 34.8691 | 37.5032 | 35.0785 | 36.3026 | 35.0055 | 36.4124 | 35.1379 | 37.0445 | 36.387 | 36.8763 | 38.3001 | 36.1247 | 37.8244 | 39.1908 | 40.1121 | 38.3105 | 39.8091 | 37.8128 | 40.0808 | 37.7632 | 39.8726 | 37.3384 | 39.078 | 38.2049 | 39.7906 | 37.364 | 40.3599 | 37.6414 | 39.9947 | 40.4103 | 94.8501 | 95.403 | 94.2691
2022-09-07 19:53 | 1:29 | 31.0583 | 29.588 | 31.3802 | 36.8731 | 37.0634 | 34.9067 | 37.821 | 33.8812 | 37.6064 | 36.1156 | 35.961 | 39.4241 | 33.8918 | 35.5628 | 36.2144 | 34.4884 | 34.9839 | 35.8432 | 35.1289 | 37.6958 | 34.0898 | 30.7022 | 35.1193 | 37.3624 | 35.2168 | 40.2139 | 37.6557 | 35.7762 | 34.9876 | 37.5729 | 35.1318 | 36.4088 | 35.0181 | 36.4617 | 35.1869 | 37.0376 | 36.4022 | 36.9637 | 38.3623 | 36.1848 | 37.9122 | 39.1807 | 40.1485 | 38.2867 | 39.8177 | 37.8702 | 40.1219 | 37.8278 | 39.9175 | 37.408 | 39.0798 | 38.2771 | 39.9415 | 37.3239 | 40.3641 | 37.7269 | 39.7971 | 40.5957 | 94.9987 | 95.4843 | 94.2842
2022-09-07 19:53 | 1:29 | 31.5872 | 30.5195 | 31.6082 | 36.9374 | 37.0823 | 35.0253 | 37.8675 | 34.0533 | 37.6413 | 36.1208 | 36.2613 | 39.3916 | 33.9696 | 35.7085 | 36.1529 | 34.5466 | 35.0686 | 35.8755 | 35.2244 | 37.7807 | 34.1561 | 31.3674 | 35.4707 | 37.3546 | 35.3184 | 40.224 | 37.7402 | 35.7546 | 35.0402 | 37.6223 | 35.2687 | 36.4881 | 35.1253 | 36.502 | 35.2901 | 37.07 | 36.412 | 36.9635 | 38.25 | 36.2445 | 37.979 | 39.2424 | 40.2093 | 38.405 | 39.908 | 37.9364 | 40.1386 | 37.9345 | 39.9884 | 37.5216 | 39.0902 | 38.3035 | 39.9001 | 37.3972 | 40.4212 | 37.8323 | 39.8789 | 40.4087 | 95.1274 | 95.567 | 94.4542
2022-09-07 19:53 | 1:29 | 32.0434 | 31.0028 | 31.7651 | 37.1253 | 37.1265 | 35.1176 | 38.0146 | 34.0989 | 37.6953 | 36.331 | 36.2054 | 39.3742 | 34.0826 | 35.7812 | 36.3094 | 34.6497 | 35.16 | 35.9215 | 35.2634 | 37.871 | 34.3198 | 31.6697 | 35.8086 | 37.4654 | 35.3873 | 40.316 | 37.7643 | 35.9017 | 35.1358 | 37.7033 | 35.3841 | 36.7292 | 35.2769 | 36.6046 | 35.3691 | 37.1582 | 36.4942 | 37.0649 | 38.3606 | 36.3157 | 38.0307 | 39.3039 | 40.3348 | 38.5286 | 40.0377 | 37.9898 | 40.1545 | 38.0707 | 40.1064 | 37.6099 | 39.1499 | 38.4069 | 40.0741 | 37.5356 | 40.4206 | 37.9348 | 40.0952 | 40.4497 | 95.0774 | 95.5197 | 94.3864
2022-09-07 19:54 | 1:30 | 32.6781 | 31.4805 | 31.8748 | 37.1317 | 37.1739 | 35.2054 | 37.965 | 34.179 | 37.748 | 36.4113 | 36.2909 | 39.4185 | 34.2083 | 35.9306 | 36.2444 | 34.7064 | 35.2293 | 36.0135 | 35.3542 | 37.895 | 34.4639 | 31.7449 | 36.0525 | 37.5742 | 35.4962 | 40.4474 | 37.8244 | 35.9636 | 35.2308 | 37.8205 | 35.5156 | 36.5187 | 35.3615 | 36.6618 | 35.4502 | 37.1202 | 36.5147 | 37.1579 | 38.368 | 36.3775 | 38.1072 | 39.4245 | 40.399 | 38.6624 | 40.0495 | 38.0275 | 40.1837 | 38.1859 | 40.1936 | 37.6824 | 39.2324 | 38.4552 | 40.1375 | 37.6397 | 40.5633 | 38.0283 | 40.124 | 40.5608 | 94.949 | 95.3393 | 94.255
2022-09-07 19:54 | 1:30 | 33.651 | 31.8472 | 32.0883 | 37.2187 | 37.1825 | 35.2704 | 37.9122 | 34.3085 | 37.7604 | 36.3753 | 36.5446 | 39.4992 | 34.3292 | 35.9253 | 36.5206 | 34.796 | 35.3114 | 36.0508 | 35.4258 | 37.9929 | 34.7955 | 31.8004 | 36.176 | 37.6382 | 35.5683 | 40.4253 | 37.9122 | 35.9316 | 35.3247 | 37.8026 | 35.6156 | 36.5201 | 35.4506 | 36.7611 | 35.5664 | 37.1261 | 36.5686 | 37.171 | 38.41 | 36.4423 | 38.1639 | 39.4847 | 40.4342 | 38.7663 | 40.1856 | 38.0853 | 40.3106 | 38.2356 | 40.2165 | 37.7923 | 39.281 | 38.5394 | 40.0897 | 37.682 | 40.5537 | 38.0936 | 40.2499 | 40.5084 | 94.663 | 95.0755 | 93.9899
2022-09-07 19:54 | 1:30 | 34.7034 | 31.8884 | 32.5778 | 37.3677 | 37.2346 | 35.3608 | 37.9555 | 34.409 | 37.7935 | 36.4203 | 36.5276 | 39.3688 | 34.4366 | 36.0125 | 36.4634 | 34.8483 | 35.4087 | 36.1551 | 35.4927 | 38.0676 | 35.2792 | 31.7837 | 36.3734 | 37.6796 | 35.7021 | 40.5619 | 37.979 | 35.9203 | 35.4061 | 37.8957 | 35.7897 | 36.6382 | 35.5647 | 36.8408 | 35.6578 | 37.283 | 36.6788 | 37.2557 | 38.3928 | 36.514 | 38.3398 | 39.5311 | 40.4922 | 38.8479 | 40.2612 | 38.0843 | 40.3867 | 38.3478 | 40.3255 | 37.8645 | 39.3947 | 38.6506 | 40.0737 | 37.7501 | 40.571 | 38.2124 | 40.1887 | 40.5439 | 94.4639 | 94.8793 | 93.8399
2022-09-07 19:54 | 1:30 | 35.662 | 31.8984 | 33.4614 | 37.6907 | 37.2766 | 35.4752 | 37.8265 | 34.5038 | 37.8258 | 36.5608 | 36.6245 | 39.4312 | 34.5294 | 36.0518 | 36.5772 | 34.8931 | 35.5022 | 36.2691 | 35.6318 | 38.2012 | 35.9306 | 31.7843 | 36.6408 | 37.7626 | 35.7985 | 40.6827 | 38.0307 | 36.0884 | 35.6241 | 38.0531 | 35.9645 | 36.6265 | 35.753 | 36.949 | 35.7524 | 37.325 | 36.7968 | 37.3722 | 38.5325 | 36.6475 | 38.3543 | 39.5844 | 40.6111 | 38.9423 | 40.3196 | 38.1699 | 40.3888 | 38.4478 | 40.3737 | 37.9198 | 39.3754 | 38.6776 | 40.0781 | 37.8636 | 40.5541 | 38.2581 | 40.239 | 40.6156 | 94.3319 | 94.7121 | 93.8315
2022-09-07 19:54 | 1:30 | 36.6269 | 31.9478 | 34.4759 | 37.7588 | 37.3659 | 35.6021 | 38.1275 | 34.6714 | 37.8812 | 36.5873 | 36.8198 | 39.4176 | 34.7308 | 36.1736 | 36.811 | 35.0291 | 35.6257 | 36.4209 | 35.7625 | 38.3708 | 36.7075 | 31.9496 | 37.0681 | 37.9668 | 35.9216 | 40.6766 | 38.1072 | 36.2219 | 35.6533 | 38.1011 | 36.1447 | 36.7431 | 35.8822 | 37.1069 | 35.9329 | 37.3783 | 36.8573 | 37.4809 | 38.5812 | 36.7293 | 38.377 | 39.6564 | 40.6501 | 39.0493 | 40.2748 | 38.2351 | 40.4012 | 38.5342 | 40.4335 | 38.035 | 39.5145 | 38.7733 | 40.1244 | 37.9714 | 40.6569 | 38.3791 | 40.3095 | 40.6667 | 94.188 | 94.5494 | 93.7265
2022-09-07 19:54 | 1:30 | 37.1085 | 32.0089 | 35.2903 | 37.8127 | 37.4588 | 35.7492 | 38.145 | 34.8231 | 37.9227 | 36.7266 | 36.97 | 39.464 | 35.0158 | 36.4076 | 36.8915 | 35.0913 | 35.8171 | 36.5661 | 35.9642 | 38.5462 | 37.0948 | 31.8894 | 37.4226 | 38.0664 | 36.0866 | 40.814 | 38.1639 | 36.4373 | 35.7377 | 38.2954 | 36.3186 | 36.9401 | 36.047 | 37.2642 | 36.071 | 37.5017 | 36.9311 | 37.6215 | 38.6169 | 36.8436 | 38.4058 | 39.7158 | 40.6823 | 39.1689 | 40.3372 | 38.2828 | 40.5279 | 38.6487 | 40.5837 | 38.132 | 39.614 | 38.8471 | 40.208 | 38.0956 | 40.7018 | 38.4297 | 40.3981 | 40.7049 | 94.0528 | 94.4194 | 93.7097
2022-09-07 19:55 | 1:30 | 37.3238 | 32.1588 | 35.6562 | 38.1575 | 37.5282 | 35.9309 | 38.2932 | 35.0389 | 38.0016 | 36.8435 | 37.0794 | 39.415 | 35.1726 | 36.5036 | 37.1227 | 35.2527 | 35.987 | 36.7182 | 36.0564 | 38.5755 | 37.3622 | 31.9275 | 37.6441 | 38.2173 | 36.1726 | 40.9466 | 38.3398 | 36.5724 | 35.7701 | 38.4976 | 36.4816 | 36.9829 | 36.1646 | 37.4037 | 36.2126 | 37.5571 | 37.057 | 37.7766 | 38.671 | 36.9578 | 38.5475 | 39.8011 | 40.7016 | 39.2749 | 40.4248 | 38.3419 | 40.5403 | 38.7267 | 40.5954 | 38.1557 | 39.6791 | 38.9329 | 40.288 | 38.1543 | 40.7132 | 38.5406 | 40.376 | 40.7103 | 93.9702 | 94.3281 | 93.6301
2022-09-07 19:55 | 1:31 | 37.4904 | 32.3685 | 35.8525 | 38.3177 | 37.6081 | 36.1502 | 38.3876 | 35.2982 | 38.0806 | 36.9894 | 37.2033 | 39.4812 | 35.3988 | 36.6693 | 37.0389 | 35.3286 | 36.1674 | 36.855 | 36.1447 | 38.7414 | 37.5845 | 32.1838 | 37.8498 | 38.3991 | 36.2767 | 41.0064 | 38.3543 | 36.5836 | 35.951 | 38.4245 | 36.6049 | 37.0098 | 36.3091 | 37.4911 | 36.3341 | 37.6462 | 37.1308 | 37.8488 | 38.7212 | 37.0825 | 38.5936 | 39.8656 | 40.8307 | 39.4037 | 40.4962 | 38.3859 | 40.5898 | 38.8351 | 40.6884 | 38.2555 | 39.7673 | 39.0023 | 40.3425 | 38.2205 | 40.7522 | 38.614 | 40.4978 | 40.8404 | 93.9216 | 94.2244 | 93.6269
2022-09-07 19:55 | 1:31 | 37.6519 | 32.5829 | 36.1263 | 38.551 | 37.6968 | 36.283 | 38.4066 | 35.5068 | 38.1481 | 37.0964 | 37.4003 | 39.5586 | 35.5583 | 36.7576 | 37.0413 | 35.4086 | 36.2701 | 36.9917 | 36.2983 | 38.8171 | 37.7875 | 32.2441 | 38.0148 | 38.4662 | 36.3593 | 40.9684 | 38.377 | 36.6422 | 36.1129 | 38.5452 | 36.7328 | 37.1199 | 36.448 | 37.6256 | 36.3942 | 37.7458 | 37.2252 | 37.9374 | 38.755 | 37.162 | 38.6899 | 39.9275 | 40.874 | 39.4409 | 40.5623 | 38.4662 | 40.6004 | 38.941 | 40.8036 | 38.3498 | 39.7522 | 39.0789 | 40.4897 | 38.3445 | 40.7656 | 38.6962 | 40.5334 | 40.8175 | 93.9195 | 94.1596 | 93.7238
2022-09-07 19:55 | 1:31 | 37.966 | 32.8055 | 36.4038 | 38.8078 | 37.7642 | 36.3979 | 38.5389 | 35.6414 | 38.2317 | 37.2672 | 37.4878 | 39.6978 | 35.7027 | 36.985 | 37.3109 | 35.5901 | 36.4257 | 37.0876 | 36.3824 | 38.8671 | 38.0384 | 32.4949 | 38.2121 | 38.5531 | 36.4265 | 40.9508 | 38.4058 | 36.8071 | 36.2269 | 38.6191 | 36.8673 | 37.1492 | 36.573 | 37.7231 | 36.6545 | 37.8055 | 37.2855 | 38.0207 | 38.8283 | 37.2468 | 38.7621 | 39.99 | 40.9627 | 39.5449 | 40.688 | 38.5224 | 40.6465 | 39.0186 | 40.8183 | 38.424 | 39.8316 | 39.175 | 40.4793 | 38.43 | 40.7792 | 38.7655 | 40.5756 | 40.8714 | 93.8677 | 94.0956 | 93.6104
2022-09-07 19:55 | 1:31 | 38.1291 | 33.1924 | 36.6756 | 38.8591 | 37.833 | 36.6072 | 38.6645 | 35.8148 | 38.2844 | 37.3498 | 37.5922 | 39.6804 | 35.9392 | 37.0806 | 37.3507 | 35.6406 | 36.5394 | 37.1813 | 36.5372 | 39.1036 | 38.2584 | 33.2686 | 38.382 | 38.6144 | 36.5851 | 41.1618 | 38.5475 | 36.8572 | 36.3406 | 38.6984 | 36.9836 | 37.1872 | 36.6691 | 37.8101 | 36.7167 | 37.9107 | 37.3893 | 38.1269 | 38.9359 | 37.3282 | 38.8931 | 40.0815 | 40.9748 | 39.6197 | 40.6796 | 38.6087 | 40.6544 | 39.0984 | 40.8211 | 38.4842 | 39.855 | 39.2661 | 40.4564 | 38.4786 | 40.8793 | 38.8178 | 40.5244 | 41.018 | 93.7926 | 94.0224 | 93.5228
2022-09-07 19:55 | 1:31 | 38.3176 | 33.5857 | 36.8511 | 38.8899 | 37.9288 | 36.7182 | 38.6842 | 36.0236 | 38.3472 | 37.4678 | 37.7456 | 39.7825 | 36.0612 | 37.2146 | 37.3873 | 35.7826 | 36.6663 | 37.2791 | 36.6522 | 39.1057 | 38.4879 | 33.9405 | 38.57 | 38.7833 | 36.7732 | 41.1345 | 38.5936 | 36.929 | 36.4977 | 38.6481 | 37.0694 | 37.3366 | 36.8647 | 37.9014 | 36.86 | 37.9896 | 37.4705 | 38.1902 | 38.9636 | 37.4155 | 38.9698 | 40.1221 | 41.0299 | 39.7096 | 40.6913 | 38.6458 | 40.7048 | 39.183 | 40.9001 | 38.5615 | 39.9653 | 39.3529 | 40.5915 | 38.631 | 40.8752 | 38.9309 | 40.6773 | 41.0822 | 93.7554 | 93.9975 | 93.5692
2022-09-07 19:56 | 1:32 | 38.4601 | 34.3663 | 37.0048 | 39.0603 | 38.0362 | 36.842 | 38.8079 | 36.1565 | 38.4166 | 37.5797 | 37.9144 | 39.7864 | 36.2372 | 37.2891 | 37.4977 | 35.9023 | 36.818 | 37.4148 | 36.7215 | 39.1866 | 38.7019 | 34.7811 | 38.7267 | 38.9123 | 36.8166 | 41.2981 | 38.6899 | 37.0721 | 36.6289 | 38.8948 | 37.2029 | 37.3914 | 36.9546 | 37.9941 | 36.9804 | 38.0517 | 37.5337 | 38.2866 | 39.0263 | 37.5485 | 38.9762 | 40.1511 | 41.0716 | 39.8067 | 40.7867 | 38.7265 | 40.7405 | 39.2585 | 40.9286 | 38.583 | 39.9884 | 39.3951 | 40.6021 | 38.7543 | 40.9498 | 39.0118 | 40.6701 | 41.0299 | 93.7148 | 93.9336 | 93.5278
2022-09-07 19:56 | 1:32 | 38.6712 | 35.4761 | 37.1783 | 39.2738 | 38.0988 | 36.9508 | 38.8135 | 36.3934 | 38.4835 | 37.6881 | 38.0257 | 39.8679 | 36.3558 | 37.3524 | 37.708 | 35.9672 | 36.9479 | 37.5238 | 36.8683 | 39.312 | 38.8976 | 35.5187 | 38.8651 | 38.9838 | 36.9597 | 41.2835 | 38.7621 | 37.0623 | 36.7456 | 38.8579 | 37.3171 | 37.5055 | 37.0803 | 38.0684 | 37.0971 | 38.0906 | 37.6311 | 38.3853 | 39.1257 | 37.6276 | 38.9979 | 40.2222 | 41.1514 | 39.8786 | 40.8572 | 38.7822 | 40.8303 | 39.3702 | 40.9498 | 38.6692 | 40.037 | 39.4753 | 40.6661 | 38.7874 | 40.9845 | 39.0845 | 40.6628 | 41.0538 | 93.6777 | 93.8734 | 93.5623
2022-09-07 19:56 | 1:32 | 38.8039 | 36.253 | 37.4502 | 39.3849 | 38.1886 | 37.0869 | 38.8827 | 36.4978 | 38.5848 | 37.8211 | 38.1078 | 39.9695 | 36.4651 | 37.4835 | 37.7762 | 36.069 | 37.0705 | 37.5896 | 36.9669 | 39.3643 | 39.0249 | 36.0656 | 39.0178 | 39.092 | 37.0635 | 41.4654 | 38.8931 | 37.2096 | 36.961 | 38.9499 | 37.4269 | 37.6493 | 37.2084 | 38.1913 | 37.2177 | 38.1911 | 37.7341 | 38.4687 | 39.2188 | 37.7207 | 39.1218 | 40.2736 | 41.197 | 39.9709 | 40.864 | 38.8718 | 40.8509 | 39.4328 | 41.0231 | 38.7383 | 40.1358 | 39.5556 | 40.7292 | 38.9104 | 40.9693 | 39.1585 | 40.8262 | 41.086 | 93.641 | 93.8098 | 93.5375
2022-09-07 19:56 | 1:32 | 38.7759 | 36.7263 | 37.4601 | 39.563 | 38.2546 | 37.2048 | 38.9356 | 36.6379 | 38.66 | 37.931 | 38.2652 | 40.0012 | 36.6009 | 37.5801 | 37.9253 | 36.1982 | 37.2307 | 37.7936 | 37.0528 | 39.4562 | 39.1806 | 36.4572 | 39.1499 | 39.2079 | 37.1812 | 41.5179 | 38.9698 | 37.3224 | 37.1171 | 39.0712 | 37.5229 | 37.6389 | 37.3434 | 38.2714 | 37.3929 | 38.2946 | 37.7914 | 38.5259 | 39.2118 | 37.8415 | 39.1581 | 40.3432 | 41.224 | 40.0539 | 40.9315 | 38.9342 | 40.9174 | 39.5368 | 41.1136 | 38.8466 | 40.2106 | 39.6171 | 40.6632 | 38.9053 | 40.9972 | 39.2219 | 40.9131 | 41.1598 | 93.5052 | 93.7067 | 93.3644
2022-09-07 19:56 | 1:32 | 38.8055 | 37.0752 | 37.6092 | 39.6072 | 38.3351 | 37.3177 | 39.0384 | 36.7699 | 38.7204 | 38.0093 | 38.3856 | 40.0514 | 36.7615 | 37.7538 | 38.1238 | 36.3637 | 37.3669 | 37.8421 | 37.16 | 39.5057 | 39.3174 | 36.789 | 39.2687 | 39.3172 | 37.2923 | 41.636 | 38.9762 | 37.5128 | 37.1609 | 39.104 | 37.6631 | 37.801 | 37.4815 | 38.3999 | 37.4511 | 38.343 | 37.8977 | 38.612 | 39.2953 | 37.9165 | 39.2728 | 40.4261 | 41.2999 | 40.1585 | 40.9789 | 38.9674 | 40.9506 | 39.6283 | 41.1959 | 38.9057 | 40.2813 | 39.6791 | 40.8382 | 39.081 | 41.0071 | 39.3266 | 41.0108 | 41.1144 | 93.3878 | 93.6075 | 93.1921
2022-09-07 19:56 | 1:32 | 38.8522 | 37.3428 | 37.7619 | 39.6754 | 38.3877 | 37.4516 | 39.2311 | 36.9681 | 38.7938 | 38.1365 | 38.4613 | 40.0069 | 36.9584 | 37.8369 | 38.15 | 36.4351 | 37.4586 | 37.9532 | 37.2641 | 39.5655 | 39.467 | 37.0619 | 39.3696 | 39.4373 | 37.4267 | 41.6351 | 38.9979 | 37.5824 | 37.185 | 39.1862 | 37.7785 | 37.8332 | 37.5871 | 38.4843 | 37.5621 | 38.4386 | 37.9804 | 38.6891 | 39.3766 | 38.0149 | 39.309 | 40.5044 | 41.3336 | 40.2407 | 41.0321 | 39.0614 | 41.0269 | 39.6936 | 41.301 | 38.979 | 40.3147 | 39.7501 | 40.8419 | 39.1305 | 41.1204 | 39.4038 | 41.0923 | 41.1928 | 93.3128 | 93.5102 | 93.1649
2022-09-07 19:57 | 1:32 | 38.8221 | 37.5692 | 37.9126 | 39.8329 | 38.5037 | 37.5872 | 39.2376 | 37.094 | 38.863 | 38.1877 | 38.5268 | 39.9779 | 37.0817 | 38.0131 | 38.1865 | 36.5948 | 37.607 | 38.0481 | 37.4243 | 39.6934 | 39.5889 | 37.3074 | 39.5181 | 39.5415 | 37.5713 | 41.7 | 39.1218 | 37.6628 | 37.3541 | 39.2437 | 37.8596 | 37.999 | 37.7221 | 38.5869 | 37.7345 | 38.5295 | 38.0806 | 38.7781 | 39.3939 | 38.1122 | 39.4134 | 40.5643 | 41.4234 | 40.3263 | 41.2131 | 39.1118 | 41.1224 | 39.7822 | 41.3464 | 39.1359 | 40.3942 | 39.8471 | 40.8458 | 39.1663 | 41.1736 | 39.487 | 41.1377 | 41.2961 | 93.2002 | 93.3952 | 93.0995
2022-09-07 19:57 | 1:33 | 39.1802 | 37.7489 | 38.0736 | 39.8888 | 38.5999 | 37.6749 | 39.2277 | 37.221 | 38.9452 | 38.3398 | 38.6912 | 40.1173 | 37.26 | 38.0607 | 38.3968 | 36.7008 | 37.7357 | 38.1537 | 37.5599 | 39.8511 | 39.7314 | 37.5619 | 39.6354 | 39.6302 | 37.6925 | 41.7394 | 39.1581 | 37.7741 | 37.4389 | 39.3529 | 37.9786 | 38.0072 | 37.8471 | 38.6878 | 37.8281 | 38.6006 | 38.1623 | 38.8676 | 39.4503 | 38.2162 | 39.4338 | 40.6095 | 41.4457 | 40.4171 | 41.1987 | 39.1973 | 41.1233 | 39.8683 | 41.3636 | 39.1648 | 40.4485 | 39.9318 | 40.9832 | 39.2359 | 41.2244 | 39.5545 | 41.1454 | 41.3434 | 93.1049 | 93.3222 | 93.1126
2022-09-07 19:57 | 1:33 | 39.671 | 37.9435 | 38.2402 | 40.0885 | 38.6623 | 37.8162 | 39.2891 | 37.3939 | 39.0289 | 38.4602 | 38.745 | 40.2227 | 37.4272 | 38.2455 | 38.4164 | 36.8208 | 37.8443 | 38.2453 | 37.6244 | 39.8958 | 39.8939 | 37.8021 | 39.7702 | 39.7134 | 37.8782 | 41.716 | 39.2728 | 37.8169 | 37.5988 | 39.4296 | 38.0938 | 38.101 | 37.9568 | 38.7372 | 37.9198 | 38.6424 | 38.2825 | 38.9518 | 39.5042 | 38.2777 | 39.4647 | 40.7179 | 41.5025 | 40.4704 | 41.2294 | 39.2251 | 41.1861 | 39.9494 | 41.4369 | 39.2126 | 40.4848 | 39.9907 | 41.0065 | 39.3201 | 41.2215 | 39.6506 | 41.2193 | 41.4192 | 93.0905 | 93.2159 | 93.2028
2022-09-07 19:57 | 1:33 | 39.8312 | 38.1456 | 38.5031 | 40.1422 | 38.7496 | 37.9594 | 39.3889 | 37.5116 | 39.0996 | 38.5506 | 38.9503 | 40.2889 | 37.5147 | 38.2839 | 38.5234 | 36.9162 | 38.0146 | 38.3727 | 37.736 | 39.9865 | 39.9802 | 38.0142 | 39.8887 | 39.7811 | 37.9105 | 41.7485 | 39.309 | 37.976 | 37.7538 | 39.4517 | 38.1941 | 38.1918 | 38.0817 | 38.8371 | 38.0418 | 38.7365 | 38.3656 | 38.9981 | 39.5267 | 38.3804 | 39.3459 | 40.782 | 41.5407 | 40.5363 | 41.3429 | 39.2829 | 41.2874 | 40.0204 | 41.4965 | 39.2923 | 40.5577 | 40.0604 | 41.1196 | 39.4021 | 41.3314 | 39.7312 | 41.2083 | 41.5636 | 93.0495 | 93.1179 | 93.1106
2022-09-07 19:57 | 1:33 | 39.352 | 38.3069 | 38.5733 | 40.2151 | 38.8507 | 38.1169 | 39.4564 | 37.6452 | 39.1657 | 38.648 | 39.0405 | 40.3078 | 37.6673 | 38.4409 | 38.6654 | 37.0035 | 38.0977 | 38.4871 | 37.809 | 40.0594 | 40.0586 | 38.1322 | 39.9657 | 39.8506 | 38.0097 | 41.8273 | 39.4134 | 37.9973 | 37.8003 | 39.4965 | 38.312 | 38.2371 | 38.1826 | 38.9209 | 38.1739 | 38.81 | 38.446 | 39.0971 | 39.6801 | 38.5127 | 39.1668 | 40.8177 | 41.5895 | 40.6501 | 41.449 | 39.3541 | 41.3528 | 40.099 | 41.5246 | 39.4012 | 40.6313 | 40.1189 | 41.1282 | 39.4898 | 41.4425 | 39.8031 | 41.2332 | 41.5646 | 92.874 | 92.9915 | 92.8907
2022-09-07 19:57 | 1:33 | 38.9501 | 38.4008 | 38.668 | 40.3458 | 38.9088 | 38.2253 | 39.5434 | 37.8174 | 39.2491 | 38.7343 | 39.1478 | 40.3293 | 37.7567 | 38.5008 | 38.774 | 37.1551 | 38.1745 | 38.4863 | 37.9644 | 40.0629 | 40.1326 | 38.2834 | 40.0535 | 39.9672 | 38.1668 | 42.0474 | 39.4338 | 38.1903 | 37.8395 | 39.6468 | 38.3877 | 38.4206 | 38.2955 | 39.0252 | 38.3198 | 38.8512 | 38.5436 | 39.1766 | 39.7219 | 38.6081 | 38.9365 | 40.8513 | 41.6091 | 40.7318 | 41.4784 | 39.4126 | 41.3702 | 40.1679 | 41.5036 | 39.4247 | 40.7072 | 40.1851 | 41.1695 | 39.61 | 41.3827 | 39.8672 | 41.3924 | 41.546 | 92.7361 | 92.8852 | 92.7189
2022-09-07 19:58 | 1:33 | 37.6813 | 37.4999 | 38.274 | 40.3846 | 39.0069 | 38.2548 | 39.6095 | 37.9048 | 39.3191 | 38.8294 | 39.2004 | 40.3449 | 37.8287 | 38.5877 | 38.7768 | 37.2836 | 38.2637 | 38.6181 | 38.0933 | 40.1292 | 37.3032 | 37.3318 | 39.2643 | 40.0513 | 38.138 | 41.9042 | 39.4647 | 38.2539 | 38.0197 | 39.6289 | 38.209 | 38.4406 | 38.2917 | 39.0762 | 38.3317 | 38.978 | 38.5955 | 39.2424 | 39.785 | 38.639 | 38.7809 | 40.9274 | 41.5689 | 40.6094 | 41.4269 | 39.4683 | 41.3506 | 40.0818 | 41.5721 | 39.4567 | 40.6503 | 40.1797 | 41.3086 | 39.6558 | 41.405 | 39.8569 | 41.4021 | 41.5901 | 92.6119 | 92.7332 | 92.6637
2022-09-07 19:58 | 1:34 | 32.5149 | 32.8541 | 35.1547 | 40.2084 | 38.9847 | 38.1153 | 39.5468 | 37.681 | 39.3645 | 38.752 | 39.0652 | 40.4723 | 37.4755 | 38.2619 | 38.7409 | 37.2205 | 38.1722 | 38.2933 | 37.9209 | 39.9554 | 34.0212 | 32.2026 | 37.5538 | 39.887 | 37.9266 | 41.7138 | 39.3459 | 38.0108 | 37.8144 | 39.3935 | 37.6866 | 38.4984 | 37.9983 | 38.8163 | 38.111 | 38.8872 | 38.5264 | 39.0533 | 39.6547 | 38.5372 | 38.7196 | 40.727 | 41.3765 | 40.2649 | 41.1604 | 39.4563 | 41.2471 | 39.7786 | 41.3715 | 39.2284 | 40.437 | 40.028 | 41.19 | 39.5063 | 41.4218 | 39.5967 | 41.207 | 41.7326 | 92.4928 | 92.6687 | 92.6122
2022-09-07 19:58 | 1:34 | 29.281 | 30.897 | 32.7168 | 39.5589 | 38.9124 | 37.8354 | 39.4841 | 37.3043 | 39.3165 | 38.4172 | 38.6625 | 40.4586 | 37.1097 | 38.0009 | 38.5216 | 37.1064 | 37.8949 | 37.9325 | 37.6676 | 39.8069 | 30.7884 | 30.3616 | 35.2022 | 39.6411 | 37.5951 | 41.4451 | 39.1668 | 37.9115 | 37.4861 | 39.1187 | 36.9474 | 38.4113 | 37.7004 | 38.4402 | 37.845 | 38.6743 | 38.4053 | 38.7803 | 39.4569 | 38.3962 | 38.6701 | 40.4548 | 41.1491 | 39.7554 | 40.8842 | 39.276 | 41.1262 | 39.2498 | 40.9345 | 38.9302 | 40.2584 | 39.7523 | 40.736 | 39.3146 | 41.3317 | 39.2199 | 40.9963 | 41.5793 | 92.3663 | 92.5049 | 92.506
2022-09-07 19:58 | 1:34 | 28.6386 | 29.9593 | 31.7627 | 39.1178 | 38.9177 | 37.681 | 39.4541 | 37.0041 | 39.3166 | 38.2419 | 38.5513 | 40.411 | 36.8487 | 37.8872 | 38.5015 | 36.9918 | 37.7126 | 37.7582 | 37.4728 | 39.5001 | 28.3149 | 29.0621 | 33.8484 | 39.3452 | 37.3578 | 41.161 | 38.9365 | 37.7292 | 37.2308 | 38.7937 | 36.4162 | 38.3114 | 37.4368 | 38.1546 | 37.5159 | 38.4888 | 38.2771 | 38.6432 | 39.3154 | 38.2479 | 38.5704 | 40.2328 | 40.9102 | 39.2854 | 40.6087 | 39.1588 | 40.9896 | 38.9693 | 40.7113 | 38.6322 | 40.0664 | 39.539 | 40.6876 | 39.0607 | 40.9246 | 39.0521 | 40.7331 | 41.4457 | 92.2198 | 92.3505 | 92.3408
2022-09-07 19:58 | 1:34 | 27.9732 | 29.4666 | 31.1298 | 38.8242 | 38.9638 | 37.4988 | 39.3932 | 36.8895 | 39.3295 | 38.199 | 38.4651 | 40.3367 | 36.6757 | 37.7363 | 38.436 | 36.9011 | 37.5613 | 37.6678 | 37.3236 | 39.4179 | 27.3343 | 28.1224 | 32.9489 | 39.1067 | 37.2401 | 40.7176 | 38.7809 | 37.6165 | 37.0398 | 38.6138 | 36.1606 | 38.1356 | 37.288 | 37.9009 | 37.2195 | 38.3606 | 38.1676 | 38.4744 | 39.2808 | 38.0624 | 38.5475 | 40.0523 | 40.8865 | 38.9429 | 40.3895 | 39.1041 | 40.8786 | 38.6931 | 40.4728 | 38.5312 | 39.7094 | 39.321 | 40.6265 | 38.9612 | 41.0395 | 38.9497 | 40.6345 | 41.4313 | 92.0543 | 92.1907 | 92.3048
2022-09-07 19:58 | 1:34 | 27.5642 | 29.1824 | 30.6843 | 38.6394 | 38.9747 | 37.3184 | 39.3888 | 36.8009 | 39.3228 | 38.0426 | 38.4994 | 40.4211 | 36.5751 | 37.6949 | 38.3719 | 36.8315 | 37.4731 | 37.4865 | 37.2532 | 39.3015 | 26.8088 | 27.5219 | 32.4085 | 38.9643 | 37.1058 | 40.716 | 38.7196 | 37.5999 | 36.9161 | 38.5746 | 35.8794 | 38.1372 | 37.1277 | 37.737 | 37.0366 | 38.109 | 38.0661 | 38.3272 | 39.1829 | 37.9607 | 38.4916 | 39.9981 | 40.7416 | 38.757 | 40.2352 | 39.068 | 40.8244 | 38.567 | 40.4285 | 38.4492 | 39.672 | 39.2414 | 40.5827 | 38.8526 | 41.0018 | 38.8488 | 40.4702 | 41.3039 | 92.0823 | 92.1378 | 92.4428
2022-09-07 19:59 | 1:34 | 27.2164 | 28.9283 | 30.3568 | 38.5164 | 39.0235 | 37.2083 | 39.2552 | 36.7103 | 39.3443 | 37.8745 | 38.4586 | 40.484 | 36.4493 | 37.6551 | 38.3457 | 36.748 | 37.3231 | 37.4184 | 37.2035 | 39.2944 | 26.42 | 27.0038 | 31.981 | 38.726 | 37.0371 | 40.4665 | 38.6701 | 37.5228 | 36.8948 | 38.4776 | 35.6007 | 38.174 | 36.9445 | 37.6221 | 36.8295 | 38.0392 | 38.1324 | 38.1764 | 39.2291 | 37.982 | 38.4101 | 39.9131 | 40.6874 | 38.6598 | 40.1969 | 38.9508 | 40.7786 | 38.4008 | 40.3255 | 38.3947 | 39.5748 | 39.2356 | 40.5808 | 38.7642 | 41.0938 | 38.8064 | 40.3443 | 41.4372 | 92.101 | 92.0739 | 92.384
2022-09-07 19:59 | 1:35 | 26.8875 | 28.5912 | 30.0324 | 38.1917 | 39.0429 | 37.2096 | 39.3263 | 36.6193 | 39.3549 | 37.8388 | 38.4113 | 40.4248 | 36.3701 | 37.5448 | 38.2664 | 36.7315 | 37.2442 | 37.3632 | 37.1351 | 39.1285 | 26.1316 | 26.5396 | 31.6352 | 38.67 | 36.9416 | 40.3138 | 38.5704 | 37.4999 | 36.8432 | 38.4242 | 35.3764 | 38.1776 | 36.9547 | 37.4668 | 36.7214 | 38.0018 | 37.9755 | 38.0992 | 39.1817 | 37.8502 | 38.3525 | 39.8446 | 40.638 | 38.4983 | 40.0511 | 38.9836 | 40.7516 | 38.2243 | 40.1891 | 38.327 | 39.6738 | 39.158 | 40.4813 | 38.8549 | 40.8813 | 38.6836 | 40.3637 | 41.2964 | 92.168 | 92.1474 | 92.4434
2022-09-07 19:59 | 1:35 | 26.5332 | 28.2947 | 29.6831 | 38.0092 | 39.0487 | 36.9716 | 39.2494 | 36.5641 | 39.3557 | 37.7609 | 38.3418 | 40.5496 | 36.2354 | 37.522 | 38.0921 | 36.6978 | 37.1668 | 37.2897 | 37.1243 | 39.1718 | 26.177 | 26.151 | 31.3882 | 38.4448 | 36.8689 | 40.3341 | 38.5475 | 37.3912 | 36.8288 | 38.3271 | 35.2361 | 38.116 | 36.8799 | 37.3705 | 36.5568 | 38.0513 | 37.9128 | 37.9907 | 39.1932 | 37.8089 | 38.2194 | 39.788 | 40.5633 | 38.4154 | 39.9366 | 38.96 | 40.5116 | 38.1076 | 40.0735 | 38.2324 | 39.8671 | 39.2456 | 40.443 | 38.7278 | 40.8462 | 38.6156 | 40.2807 | 41.4645 | 92.15 | 92.1942 | 92.3596
2022-09-07 19:59 | 1:35 | 26.1943 | 27.9561 | 29.3471 | 38.0884 | 39.0723 | 37.0618 | 39.1918 | 36.3702 | 39.3665 | 37.681 | 38.0427 | 40.4566 | 36.1026 | 37.374 | 38.1162 | 36.6564 | 37.0409 | 37.1834 | 37.0525 | 39.1518 | 26.5484 | 25.8513 | 31.2001 | 38.3023 | 36.7966 | 40.3178 | 38.4916 | 37.4537 | 36.7481 | 38.2885 | 35.1044 | 38.2413 | 36.8349 | 37.2616 | 36.4515 | 38.0006 | 37.977 | 37.977 | 39.2514 | 37.7997 | 38.2362 | 39.695 | 40.4698 | 38.231 | 39.9225 | 38.9126 | 40.5768 | 38.0282 | 40.2509 | 38.1439 | 39.5611 | 39.1362 | 40.2443 | 38.6506 | 40.7959 | 38.4989 | 40.1152 | 41.2469 | 92.304 | 92.3458 | 92.4902
2022-09-07 19:59 | 1:35 | 26.0437 | 27.7188 | 29.0736 | 37.8969 | 39.0824 | 36.8553 | 39.2867 | 36.2455 | 39.3858 | 37.6305 | 37.9762 | 40.4163 | 36.0213 | 37.3641 | 38.2528 | 36.6378 | 37.0022 | 37.1954 | 37.0663 | 39.1734 | 26.7272 | 25.6867 | 30.9836 | 38.2324 | 36.722 | 40.1525 | 38.4101 | 37.3656 | 36.6958 | 38.1404 | 34.9713 | 38.0485 | 36.7603 | 37.2103 | 36.4583 | 37.8816 | 37.9813 | 37.9401 | 39.1106 | 37.7456 | 38.0896 | 39.6212 | 40.4309 | 38.1636 | 39.8581 | 38.8393 | 40.5929 | 37.9277 | 39.9701 | 38.0879 | 39.4415 | 38.9611 | 40.2465 | 38.5923 | 40.8769 | 38.4131 | 40.0703 | 41.2373 | 92.3134 | 92.4079 | 92.4972
2022-09-07 19:59 | 1:35 | 25.772 | 27.4473 | 28.8581 | 37.8259 | 39.0781 | 36.8744 | 39.2848 | 36.0642 | 39.3699 | 37.4741 | 37.8903 | 40.4356 | 35.912 | 37.3207 | 38.0636 | 36.6061 | 36.9171 | 37.0995 | 37.0552 | 38.9619 | 26.6389 | 25.4281 | 30.7758 | 38.2119 | 36.6324 | 40.1727 | 38.3525 | 37.4653 | 36.6356 | 38.1106 | 34.8914 | 38.128 | 36.6705 | 37.1561 | 36.3865 | 37.9558 | 37.9406 | 37.9115 | 39.0491 | 37.7365 | 38.1669 | 39.5259 | 40.4053 | 38.0798 | 39.7709 | 38.7704 | 40.4448 | 37.7827 | 39.9431 | 38.0368 | 39.603 | 38.9075 | 40.2472 | 38.5365 | 40.6092 | 38.334 | 39.9777 | 41.1375 | 92.4066 | 92.5214 | 92.5994
2022-09-07 20:00 | 1:35 | 25.5814 | 27.2327 | 28.6349 | 37.6694 | 39.1165 | 36.6999 | 39.2013 | 35.9768 | 39.3636 | 37.5294 | 38.0045 | 40.4765 | 35.8136 | 37.2083 | 38.0688 | 36.6133 | 36.8484 | 37.1019 | 36.9674 | 38.859 | 26.4737 | 25.2377 | 30.5468 | 38.0982 | 36.5579 | 40.0322 | 38.2194 | 37.4301 | 36.5128 | 38.0361 | 34.7342 | 38.034 | 36.6003 | 36.9818 | 36.2068 | 37.8686 | 37.901 | 37.8252 | 38.9578 | 37.6332 | 37.9871 | 39.4071 | 40.3634 | 38.0024 | 39.6788 | 38.7833 | 40.4668 | 37.6687 | 39.8902 | 38.017 | 39.7651 | 38.7895 | 40.3053 | 38.5445 | 40.7234 | 38.3023 | 39.9629 | 41.0893 | 92.4777 | 92.6683 | 92.6578
2022-09-07 20:00 | 1:36 | 25.4061 | 26.9864 | 28.3749 | 37.5089 | 39.088 | 36.6698 | 39.2195 | 35.8958 | 39.3557 | 37.4918 | 37.7736 | 40.4032 | 35.698 | 37.1879 | 37.9233 | 36.5951 | 36.8059 | 37.0312 | 37.0035 | 38.8937 | 26.3417 | 25.0802 | 30.379 | 37.9329 | 36.5079 | 39.9242 | 38.2362 | 37.2207 | 36.487 | 37.9814 | 34.6812 | 38.058 | 36.6352 | 36.9312 | 36.0792 | 37.7606 | 37.7795 | 37.7921 | 39.1134 | 37.5848 | 38 | 39.3968 | 40.3075 | 37.888 | 39.65 | 38.709 | 40.365 | 37.5259 | 39.8239 | 37.9353 | 39.4597 | 38.7355 | 40.2121 | 38.5388 | 40.4488 | 38.1523 | 39.8939 | 41.0836 | 92.5566 | 92.7668 | 92.7441
2022-09-07 20:00 | 1:36 | 25.2073 | 26.7344 | 28.1569 | 37.3647 | 39.1263 | 36.5326 | 39.0945 | 35.8505 | 39.3675 | 37.3373 | 37.8585 | 40.4964 | 35.6265 | 37.1957 | 38.0734 | 36.5799 | 36.7409 | 37.013 | 36.965 | 38.8894 | 26.1989 | 24.9036 | 30.2069 | 37.8141 | 36.4372 | 39.985 | 38.0896 | 37.1394 | 36.4511 | 37.9456 | 34.5425 | 37.9952 | 36.5883 | 36.853 | 36.0454 | 37.7415 | 37.6884 | 37.6961 | 38.8517 | 37.5555 | 37.9554 | 39.2978 | 40.2416 | 37.8358 | 39.473 | 38.6746 | 40.2879 | 37.4225 | 39.6032 | 37.9199 | 39.0653 | 38.7075 | 40.127 | 38.5648 | 40.5848 | 38.1387 | 39.8324 | 41.1508 | 92.7036 | 92.8628 | 92.8082
2022-09-07 20:00 | 1:36 | 25.0403 | 26.5302 | 27.9819 | 37.2534 | 39.1387 | 36.5451 | 39.1748 | 35.9041 | 39.3717 | 37.2783 | 37.9532 | 40.3445 | 35.5494 | 37.0059 | 37.8563 | 36.5763 | 36.6624 | 36.8456 | 36.9174 | 38.8795 | 26.0182 | 24.7668 | 30.0596 | 37.867 | 36.3826 | 39.9051 | 38.1669 | 37.2402 | 36.3126 | 37.8717 | 34.4962 | 38.0663 | 36.5744 | 36.7867 | 35.9343 | 37.7526 | 37.6879 | 37.6258 | 38.9547 | 37.4561 | 37.8395 | 39.2799 | 40.2116 | 37.6123 | 39.5381 | 38.6255 | 40.4281 | 37.361 | 39.6111 | 37.8488 | 39.1861 | 38.6918 | 40.1045 | 38.3324 | 40.5773 | 38.0143 | 39.8124 | 41.1346 | 92.8197 | 92.9866 | 92.8878
2022-09-07 20:00 | 1:36 | 24.7862 | 26.3031 | 27.7871 | 37.2758 | 39.1215 | 36.5444 | 39.1194 | 35.7837 | 39.2961 | 37.1642 | 37.7323 | 40.3653 | 35.5241 | 36.9609 | 37.8591 | 36.5565 | 36.6367 | 36.8871 | 36.9132 | 38.6827 | 25.8584 | 24.5086 | 29.8694 | 37.6761 | 36.3199 | 39.7689 | 37.9871 | 37.1078 | 36.3346 | 37.8291 | 34.3546 | 38.0103 | 36.4954 | 36.7225 | 35.7276 | 37.755 | 37.6779 | 37.6527 | 38.9395 | 37.3616 | 37.7871 | 39.1438 | 40.136 | 37.6488 | 39.3962 | 38.5712 | 40.2466 | 37.2759 | 39.5834 | 37.7914 | 39.5656 | 38.548 | 40.0868 | 38.291 | 40.5323 | 37.935 | 39.6105 | 41.1944 | 92.9218 | 93.0844 | 92.8446
2022-09-07 20:00 | 1:36 | 24.6133 | 26.119 | 27.6503 | 37.0689 | 39.1466 | 36.6044 | 39.0662 | 35.6824 | 39.2711 | 37.1636 | 37.6838 | 40.3311 | 35.4129 | 37.0663 | 37.854 | 36.5389 | 36.5343 | 36.7514 | 36.9184 | 38.5294 | 25.7731 | 24.3487 | 29.773 | 37.5684 | 36.2113 | 39.9532 | 38 | 37.2214 | 36.3258 | 37.7276 | 34.245 | 37.9887 | 36.4203 | 36.6476 | 35.6378 | 37.6892 | 37.585 | 37.6154 | 38.8864 | 37.2741 | 37.7517 | 39.0693 | 40.083 | 37.5102 | 39.2088 | 38.5138 | 40.3071 | 37.0739 | 39.5343 | 37.6732 | 39.4304 | 38.392 | 40.0896 | 38.3244 | 40.5856 | 37.8383 | 39.7839 | 41.1814 | 93.0441 | 93.2134 | 92.9923
2022-09-07 20:01 | 1:37 | 24.4017 | 25.8803 | 27.4297 | 37.0286 | 39.1004 | 36.2547 | 38.9716 | 35.6469 | 39.2812 | 37.1894 | 37.6641 | 40.422 | 35.2754 | 37.0361 | 37.7049 | 36.5346 | 36.5207 | 36.8018 | 36.8491 | 38.4838 | 25.6544 | 24.1662 | 29.6236 | 37.499 | 36.1773 | 39.8343 | 37.9554 | 36.9096 | 36.2944 | 37.5931 | 34.1373 | 37.9735 | 36.3362 | 36.5891 | 35.5606 | 37.6027 | 37.6603 | 37.4524 | 38.9789 | 37.2429 | 37.6668 | 39.0277 | 39.9918 | 37.4679 | 39.1822 | 38.4786 | 40.3145 | 36.9566 | 39.4808 | 37.6633 | 39.3712 | 38.3326 | 39.9516 | 38.2768 | 40.505 | 37.7681 | 39.5377 | 41.156 | 93.0497 | 93.331 | 92.995
2022-09-07 20:01 | 1:37 | 24.1987 | 25.6533 | 27.2772 | 36.9205 | 39.0754 | 36.341 | 38.9181 | 35.4866 | 39.2983 | 37.1013 | 37.3117 | 40.3953 | 35.2902 | 36.8356 | 37.6707 | 36.508 | 36.4017 | 36.857 | 36.834 | 38.4669 | 25.5745 | 23.9835 | 29.5123 | 37.3828 | 36.0613 | 39.5451 | 37.8395 | 36.9121 | 36.2173 | 37.5794 | 34.0715 | 37.7303 | 36.2944 | 36.5051 | 35.3794 | 37.583 | 37.4305 | 37.434 | 38.8796 | 37.1456 | 37.517 | 38.9374 | 39.9021 | 37.3877 | 39.2184 | 38.3484 | 40.1858 | 36.9175 | 39.373 | 37.5428 | 39.4949 | 38.3133 | 39.9148 | 38.1853 | 40.3631 | 37.6593 | 39.424 | 41.1757 | 93.1613 | 93.4309 | 93.0774
2022-09-07 20:01 | 1:37 | 24.027 | 25.4696 | 27.092 | 36.8827 | 39.0083 | 36.2243 | 38.9724 | 35.4626 | 39.245 | 37.0187 | 37.3961 | 40.3727 | 35.1748 | 36.8994 | 37.6285 | 36.5033 | 36.3578 | 36.692 | 36.7971 | 38.4108 | 25.4603 | 23.7822 | 29.387 | 37.1573 | 36.0054 | 39.6668 | 37.7871 | 36.7405 | 36.1459 | 37.5551 | 33.8781 | 37.8219 | 36.1441 | 36.4859 | 35.3991 | 37.4908 | 37.583 | 37.372 | 38.8543 | 37.1787 | 37.5345 | 38.8069 | 39.8394 | 37.3178 | 39.106 | 38.3352 | 40.2306 | 36.8705 | 39.4625 | 37.5181 | 39.5654 | 37.9036 | 39.802 | 37.9732 | 40.3986 | 37.5407 | 39.4085 | 41.0189 | 93.3707 | 93.6109 | 93.1722
2022-09-07 20:01 | 1:37 | 23.9049 | 25.247 | 26.9636 | 36.686 | 39.0386 | 36.2355 | 38.922 | 35.4138 | 39.2559 | 36.968 | 37.3922 | 40.4399 | 35.0877 | 36.8165 | 37.5752 | 36.4768 | 36.2516 | 36.6075 | 36.8019 | 38.5254 | 25.3816 | 23.6581 | 29.2376 | 37.1796 | 35.9126 | 39.6173 | 37.7517 | 36.866 | 36.099 | 37.4526 | 33.8014 | 37.8902 | 36.0454 | 36.3677 | 35.1476 | 37.5968 | 37.3859 | 37.3795 | 38.8987 | 37.1188 | 37.4117 | 38.7214 | 39.8406 | 37.2801 | 39.1113 | 38.2655 | 40.0518 | 36.7689 | 39.1998 | 37.4448 | 39.7015 | 37.9361 | 39.8597 | 37.8331 | 40.497 | 37.4659 | 39.5238 | 40.9911 | 93.4603 | 93.7361 | 93.3205
2022-09-07 20:01 | 1:37 | 23.7339 | 25.1023 | 26.8054 | 36.6524 | 38.9977 | 36.1551 | 38.8187 | 35.2761 | 39.2167 | 36.8347 | 37.2847 | 40.3937 | 35.0318 | 36.6801 | 37.5995 | 36.4606 | 36.2241 | 36.591 | 36.7614 | 38.3179 | 25.29 | 23.4168 | 29.1505 | 37.1035 | 35.8474 | 39.648 | 37.6668 | 36.8305 | 36.0345 | 37.3551 | 33.7754 | 37.7619 | 35.9716 | 36.2744 | 35.0849 | 37.4937 | 37.3505 | 37.2201 | 38.9072 | 37.0019 | 37.3829 | 38.7275 | 39.8177 | 37.1578 | 38.9451 | 38.1888 | 40.1029 | 36.6354 | 39.1957 | 37.3996 | 39.1128 | 37.9777 | 39.7558 | 37.9395 | 40.5047 | 37.4132 | 39.3905 | 40.9513 | 93.5777 | 93.8858 | 93.4009
2022-09-07 20:01 | 1:37 | 23.3999 | 24.8274 | 26.5719 | 36.5538 | 38.9538 | 36.0211 | 38.7727 | 35.2614 | 39.1666 | 36.8453 | 37.108 | 40.4409 | 35.0061 | 36.6403 | 37.6348 | 36.4231 | 36.1339 | 36.4595 | 36.7415 | 38.3101 | 25.2145 | 23.2435 | 29.0229 | 37.0136 | 35.7677 | 39.361 | 37.517 | 36.6875 | 36.0032 | 37.2985 | 33.6532 | 37.8159 | 35.9875 | 36.1619 | 35.0863 | 37.5146 | 37.2925 | 37.0933 | 38.7692 | 36.9933 | 37.3756 | 38.7236 | 39.7744 | 37.0304 | 39.0354 | 38.1448 | 39.9723 | 36.5433 | 39.2644 | 37.2506 | 39.0924 | 38.0283 | 39.8032 | 37.929 | 40.5412 | 37.3558 | 39.334 | 41.0186 | 93.6914 | 94.0523 | 93.5185
2022-09-07 20:02 | 1:37 | 23.3166 | 24.7074 | 26.3939 | 36.4605 | 38.9557 | 35.8784 | 38.7965 | 35.2666 | 39.1852 | 36.8062 | 37.2505 | 40.2803 | 34.9564 | 36.4732 | 37.5646 | 36.3738 | 36.0431 | 36.3735 | 36.6582 | 38.3026 | 25.1273 | 23.0624 | 28.8996 | 36.9097 | 35.672 | 39.414 | 37.5345 | 36.545 | 35.8996 | 37.221 | 33.5362 | 37.6642 | 35.9574 | 36.0945 | 34.9679 | 37.4111 | 37.4558 | 37.1029 | 38.8179 | 36.9199 | 37.2835 | 38.5954 | 39.7453 | 36.9532 | 38.8302 | 38.0425 | 39.997 | 36.4179 | 39.0902 | 37.2404 | 39.0283 | 37.9495 | 39.5224 | 37.7506 | 40.2609 | 37.3014 | 39.1638 | 40.8966 | 93.8972 | 94.2348 | 93.6463
2022-09-07 20:02 | 1:38 | 23.1101 | 24.5032 | 26.2139 | 36.4181 | 38.984 | 35.8289 | 38.7758 | 35.1907 | 39.1899 | 36.9202 | 37.145 | 40.3758 | 34.8959 | 36.4649 | 37.488 | 36.3391 | 36.0165 | 36.368 | 36.5565 | 38.3005 | 25.051 | 22.8573 | 28.7815 | 36.8852 | 35.5792 | 39.343 | 37.4117 | 36.5975 | 35.8197 | 37.1889 | 33.4288 | 37.7244 | 35.8765 | 36.0309 | 34.8286 | 37.417 | 37.2716 | 36.9805 | 38.6039 | 36.8595 | 37.233 | 38.4443 | 39.6346 | 36.9276 | 38.8679 | 38.0035 | 39.8827 | 36.3847 | 39.1261 | 37.1368 | 39.3953 | 37.7896 | 39.6129 | 37.5561 | 40.1586 | 37.1947 | 39.2687 | 40.8951 | 94.0469 | 94.4089 | 93.7728
2022-09-07 20:02 | 1:38 | 23.0134 | 24.3855 | 26.0755 | 36.3268 | 38.9387 | 35.8562 | 38.8222 | 35.0629 | 39.1541 | 36.6904 | 36.9348 | 40.29 | 34.8139 | 36.3409 | 37.4255 | 36.2708 | 35.9532 | 36.3106 | 36.5304 | 38.2016 | 25.0008 | 22.8117 | 28.7149 | 36.8608 | 35.5343 | 39.1074 | 37.3829 | 36.4249 | 35.7324 | 37.0827 | 33.2928 | 37.7184 | 35.7478 | 35.9474 | 34.6836 | 37.3533 | 37.1324 | 36.9388 | 38.5013 | 36.7856 | 37.175 | 38.4119 | 39.5723 | 36.8073 | 38.727 | 37.9497 | 39.8558 | 36.1775 | 39.0161 | 37.0637 | 38.7623 | 37.5468 | 39.6137 | 37.5382 | 39.8871 | 37.1552 | 38.9584 | 40.7894 | 94.2327 | 94.6231 | 93.8896
2022-09-07 20:02 | 1:38 | 23.0018 | 24.3135 | 25.987 | 36.2205 | 38.8732 | 35.5818 | 38.7046 | 35.0262 | 39.1286 | 36.6841 | 36.8859 | 40.3021 | 34.6809 | 36.4104 | 37.4779 | 36.2497 | 35.8592 | 36.2656 | 36.471 | 38.2227 | 24.9123 | 22.6526 | 28.6288 | 36.7257 | 35.4533 | 39.3085 | 37.3756 | 36.4038 | 35.7241 | 37.0787 | 33.1572 | 37.6834 | 35.6835 | 35.8729 | 34.5726 | 37.1405 | 37.1088 | 36.9367 | 38.4642 | 36.673 | 37.0885 | 38.2952 | 39.5059 | 36.7065 | 38.6056 | 37.9043 | 39.827 | 36.1747 | 38.9728 | 37.0169 | 39.217 | 37.4797 | 39.6347 | 37.4412 | 39.9043 | 37.0105 | 39.0679 | 40.8278 | 94.3697 | 94.8138 | 94.0083
2022-09-07 20:02 | 1:38 | 22.6514 | 23.9563 | 25.8196 | 36.2208 | 38.8236 | 35.7469 | 38.7175 | 34.9489 | 39.0911 | 36.5425 | 36.7917 | 40.2761 | 34.6107 | 36.4708 | 37.2134 | 36.1937 | 35.7772 | 36.1068 | 36.449 | 38.0507 | 24.8677 | 22.892 | 28.5397 | 36.6602 | 35.3504 | 39.1752 | 37.2835 | 36.5136 | 35.7112 | 37.0266 | 33.1042 | 37.7014 | 35.5943 | 35.8641 | 34.4888 | 37.1788 | 37.0698 | 36.8843 | 38.3988 | 36.5842 | 37.0715 | 38.253 | 39.4493 | 36.7024 | 38.4747 | 37.815 | 39.8242 | 36.14 | 38.9553 | 36.8552 | 39.4805 | 37.5243 | 39.6255 | 37.2467 | 40.0465 | 36.8691 | 38.9979 | 40.7916 | 94.5436 | 94.978 | 94.1052
2022-09-07 20:02 | 1:38 | 22.6202 | 23.9181 | 25.7006 | 35.9881 | 38.7755 | 35.874 | 38.6837 | 34.8808 | 39.044 | 36.5209 | 36.6854 | 40.233 | 34.5057 | 36.3953 | 37.094 | 36.1734 | 35.7154 | 36.0785 | 36.4266 | 38.0839 | 24.9404 | 23.2753 | 28.5066 | 36.5139 | 35.2686 | 39.1588 | 37.233 | 36.3541 | 35.6393 | 36.9709 | 33.1635 | 37.5038 | 35.6953 | 35.8555 | 34.5499 | 37.0787 | 37.1156 | 36.8319 | 38.4184 | 36.6138 | 37.1375 | 38.175 | 39.3042 | 36.6102 | 38.389 | 37.7666 | 39.7785 | 35.9976 | 38.9635 | 36.885 | 39.0607 | 37.4233 | 39.4483 | 37.247 | 40.0568 | 36.82 | 38.7157 | 40.7933 | 94.7046 | 95.1288 | 94.1995
2022-09-07 20:03 | 1:39 | 22.3803 | 23.6474 | 25.4986 | 36.0183 | 38.7838 | 35.6776 | 38.5829 | 34.843 | 39.0152 | 36.5114 | 36.7554 | 40.1665 | 34.4701 | 36.252 | 37.1886 | 36.1465 | 35.6671 | 35.9648 | 36.3205 | 37.9047 | 24.9577 | 22.8441 | 28.7414 | 36.422 | 35.2163 | 39.0396 | 37.175 | 36.3267 | 35.5915 | 36.9377 | 33.1578 | 37.6353 | 35.6056 | 35.7242 | 34.3222 | 37.2296 | 36.8724 | 36.7557 | 38.4188 | 36.491 | 37.1842 | 38.0965 | 39.3694 | 36.6319 | 38.3758 | 37.7286 | 39.6821 | 35.9944 | 38.8785 | 36.8006 | 38.9038 | 37.1752 | 39.3338 | 37.1726 | 40.2058 | 36.7983 | 38.7182 | 40.7591 | 94.8611 | 95.2721 | 94.3117
2022-09-07 20:03 | 1:39 | 23.5527 | 24.234 | 27.5988 | 36.0183 | 38.7599 | 35.7781 | 38.6539 | 34.7293 | 38.9964 | 36.6231 | 36.8342 | 40.1014 | 34.5313 | 36.274 | 37.2154 | 36.1165 | 35.6566 | 36.0036 | 36.4203 | 38.0669 | 25.158 | 22.7294 | 29.0166 | 36.3158 | 35.1621 | 38.9504 | 37.0885 | 36.3946 | 35.5007 | 36.8729 | 33.1555 | 37.5137 | 35.5064 | 35.6869 | 34.3234 | 37.2 | 36.8599 | 36.708 | 38.4704 | 36.4261 | 37.1024 | 38.1388 | 39.3864 | 36.6796 | 38.4126 | 37.6673 | 39.7251 | 36.0862 | 38.8752 | 36.7437 | 38.9831 | 37.2772 | 39.3899 | 37.1459 | 40.2374 | 36.7953 | 38.8058 | 40.6648 | 94.9002 | 95.3834 | 94.404
2022-09-07 20:03 | 1:39 | 27.2355 | 24.3619 | 28.9063 | 36.3726 | 38.836 | 35.7366 | 38.6386 | 34.9222 | 39.054 | 36.6128 | 37.0187 | 40.1924 | 34.7198 | 36.4332 | 37.2263 | 36.1685 | 35.8241 | 36.2455 | 36.4789 | 38.0822 | 25.7442 | 22.6886 | 29.9333 | 36.361 | 35.1686 | 38.9514 | 37.0715 | 36.4953 | 35.4761 | 37.0251 | 33.3349 | 37.4753 | 35.486 | 35.8742 | 34.3144 | 37.1124 | 36.974 | 36.8152 | 38.4769 | 36.5575 | 37.0696 | 38.1405 | 39.33 | 36.6977 | 38.5855 | 37.635 | 39.5856 | 36.0996 | 38.8241 | 36.8117 | 39.3688 | 37.3235 | 39.5182 | 37.1863 | 39.9865 | 36.8167 | 38.9549 | 40.687 | 95.0292 | 95.4819 | 94.5258
2022-09-07 20:03 | 1:39 | 28.3746 | 24.3577 | 28.6467 | 36.4526 | 38.9345 | 35.72 | 38.6403 | 34.9741 | 38.991 | 36.6351 | 37.0639 | 40.2298 | 34.7087 | 36.3747 | 37.187 | 36.2017 | 35.8294 | 36.265 | 36.5898 | 38.0017 | 26.7692 | 22.8008 | 30.8609 | 36.495 | 35.1813 | 39.0737 | 37.1375 | 36.3807 | 35.5148 | 37.1936 | 33.6086 | 37.4242 | 35.5396 | 35.946 | 34.4875 | 37.1451 | 37.1976 | 36.8918 | 38.6848 | 36.9397 | 37.0254 | 38.1498 | 39.376 | 36.8391 | 38.611 | 37.6393 | 39.57 | 36.2025 | 39.0006 | 36.7659 | 39.1688 | 37.32 | 39.5278 | 37.2843 | 39.8973 | 36.8087 | 38.8237 | 40.5829 | 95.1187 | 95.5427 | 94.5242
2022-09-07 20:03 | 1:39 | 28.2625 | 24.4482 | 28.3456 | 36.5357 | 38.9201 | 35.6587 | 38.7597 | 34.941 | 39.0267 | 36.6007 | 37.2109 | 40.2231 | 34.7044 | 36.4286 | 37.1717 | 36.2073 | 35.8039 | 36.252 | 36.5128 | 38.0814 | 27.5478 | 22.7761 | 31.0123 | 36.5749 | 35.1844 | 39.05 | 37.1842 | 36.5037 | 35.5152 | 37.1571 | 33.7013 | 37.5191 | 35.7842 | 36.0452 | 34.5475 | 37.1791 | 37.3352 | 36.8791 | 38.7972 | 36.9994 | 36.9533 | 38.1986 | 39.3729 | 36.878 | 38.5991 | 37.5816 | 39.5253 | 36.2441 | 38.8684 | 36.6735 | 39.2953 | 37.1161 | 39.5097 | 37.096 | 39.9947 | 36.8106 | 39.0709 | 40.4065 | 95.1471 | 95.5658 | 94.5952
2022-09-07 20:03 | 1:39 | 28.3786 | 27.3875 | 28.0599 | 36.3969 | 38.9609 | 35.5423 | 38.8059 | 34.8714 | 39.0089 | 36.5058 | 37.0657 | 40.226 | 34.5795 | 36.3694 | 37.1473 | 36.1813 | 35.7596 | 36.2236 | 36.4449 | 38.0516 | 27.864 | 22.8782 | 30.966 | 36.5682 | 35.1384 | 39.0994 | 37.1024 | 36.3344 | 35.4915 | 37.0677 | 33.6023 | 37.5048 | 35.6621 | 35.9944 | 34.4697 | 37.3015 | 37.3151 | 36.8124 | 38.603 | 36.9204 | 36.9199 | 38.0848 | 39.3356 | 36.7923 | 38.5602 | 37.5645 | 39.5953 | 36.1697 | 38.7756 | 36.609 | 39.2656 | 37.0075 | 39.5478 | 37.0938 | 39.8885 | 36.7984 | 38.8438 | 40.3544 | 95.0621 | 95.4044 | 94.4594
2022-09-07 20:04 | 1:39 | 28.087 | 26.9125 | 27.7975 | 36.3167 | 39.0176 | 35.5286 | 38.7525 | 34.9455 | 39.0202 | 36.5275 | 37.0864 | 40.3115 | 34.558 | 36.3094 | 37.1936 | 36.1686 | 35.7244 | 36.142 | 36.4364 | 37.9562 | 27.8659 | 22.8833 | 30.8734 | 36.6003 | 35.0619 | 39.1705 | 37.0696 | 36.3009 | 35.4406 | 37.084 | 33.5411 | 37.241 | 35.4738 | 35.9544 | 34.2794 | 37.112 | 37.1506 | 36.7538 | 38.694 | 36.8325 | 36.7783 | 38.0909 | 39.3007 | 36.7865 | 38.5213 | 37.4969 | 39.6024 | 36.1441 | 38.7556 | 36.6573 | 39.2885 | 37.0968 | 39.4585 | 37.1245 | 39.9227 | 36.7738 | 38.9525 | 40.5744 | 94.794 | 95.188 | 94.2445
2022-09-07 20:04 | 1:40 | 27.8196 | 24.7023 | 27.3305 | 36.2984 | 38.995 | 35.5273 | 38.7261 | 34.8677 | 38.992 | 36.4623 | 37.1902 | 40.3032 | 34.5355 | 36.0317 | 36.9913 | 36.1173 | 35.6436 | 36.0897 | 36.4399 | 37.9849 | 27.7097 | 22.8637 | 30.7307 | 36.5518 | 35.0269 | 38.998 | 37.0254 | 36.2874 | 35.3687 | 37.025 | 33.3934 | 37.4 | 35.4215 | 35.9013 | 34.1448 | 37.159 | 36.9025 | 36.8036 | 38.5283 | 36.6525 | 36.7316 | 37.9714 | 39.2794 | 36.6361 | 38.4735 | 37.4359 | 39.5817 | 36.0751 | 38.7973 | 36.6226 | 38.9739 | 37.0103 | 39.4086 | 37.1647 | 39.6642 | 36.6262 | 38.8006 | 40.5762 | 94.5317 | 94.9907 | 94.0446
2022-09-07 20:04 | 1:40 | 26.492 | 24.3542 | 26.7906 | 36.2439 | 39.0136 | 35.2766 | 38.6272 | 34.7804 | 38.9747 | 36.529 | 37.1737 | 40.3171 | 34.4599 | 36.1502 | 37.0405 | 36.0617 | 35.5807 | 36.0613 | 36.3352 | 38.0555 | 27.4424 | 22.7745 | 30.5743 | 36.4293 | 34.9704 | 39.2966 | 36.9533 | 36.2347 | 35.3643 | 36.9198 | 33.2785 | 37.276 | 35.3395 | 35.8343 | 34.127 | 37.0263 | 36.7918 | 36.7615 | 38.5571 | 36.4991 | 36.7028 | 37.901 | 39.1222 | 36.5137 | 38.3571 | 37.3835 | 39.6766 | 35.9198 | 38.8 | 36.5004 | 38.4455 | 36.9896 | 39.1675 | 37.0628 | 39.7843 | 36.5331 | 38.5562 | 40.5045 | 94.3256 | 94.7429 | 93.914
2022-09-07 20:04 | 1:40 | 23.2158 | 24.2611 | 26.205 | 36.1022 | 38.9444 | 35.1151 | 38.5392 | 34.7127 | 38.961 | 36.3873 | 37.0139 | 40.1689 | 34.313 | 36.0895 | 36.9105 | 36.0636 | 35.5292 | 35.8711 | 36.3094 | 37.9729 | 27.1816 | 22.7575 | 30.403 | 36.3971 | 34.9058 | 38.9282 | 36.9199 | 36.1292 | 35.2712 | 36.8073 | 33.2698 | 37.163 | 35.2871 | 35.7896 | 34.1311 | 37.0692 | 36.6384 | 36.7621 | 38.2817 | 36.4133 | 36.5754 | 37.871 | 39.0305 | 36.5263 | 38.2809 | 37.3079 | 39.5217 | 35.8275 | 38.5634 | 36.4365 | 38.8942 | 36.9344 | 39.2297 | 37.0188 | 39.7136 | 36.43 | 38.6832 | 40.5701 | 94.2026 | 94.6099 | 93.8122
2022-09-07 20:04 | 1:40 | 22.8003 | 24.1208 | 25.8951 | 35.937 | 38.8464 | 35.1658 | 38.6322 | 34.5978 | 38.9143 | 36.1897 | 36.9094 | 40.2089 | 34.2657 | 35.916 | 36.8728 | 35.988 | 35.4283 | 35.8187 | 36.2537 | 37.8632 | 26.9115 | 22.6698 | 30.1416 | 36.3335 | 34.7948 | 38.7073 | 36.7783 | 36.0976 | 35.2281 | 36.7947 | 33.1633 | 37.1114 | 35.2589 | 35.674 | 34.0382 | 36.9743 | 36.7425 | 36.6494 | 38.3129 | 36.3692 | 36.6085 | 37.7327 | 39.1164 | 36.477 | 38.1847 | 37.2657 | 39.3335 | 35.7072 | 38.6298 | 36.3326 | 38.9181 | 36.9441 | 39.0386 | 36.9067 | 39.5856 | 36.459 | 38.5684 | 40.5465 | 94.169 | 94.5214 | 93.8815
2022-09-07 20:04 | 1:40 | 22.652 | 23.896 | 25.6882 | 35.7471 | 38.845 | 35.1416 | 38.5981 | 34.6371 | 38.9265 | 36.3087 | 36.8908 | 40.3092 | 34.2111 | 36.0209 | 36.7972 | 35.9033 | 35.346 | 35.9134 | 36.1745 | 37.8391 | 26.6161 | 22.6336 | 29.9066 | 36.2948 | 34.7433 | 38.5845 | 36.7316 | 35.9626 | 35.1563 | 36.7298 | 32.9589 | 37.088 | 35.185 | 35.5729 | 33.9577 | 36.9273 | 36.7455 | 36.5352 | 38.2753 | 36.3126 | 36.5903 | 37.7559 | 39.1148 | 36.3719 | 38.1184 | 37.204 | 39.3511 | 35.6544 | 38.4692 | 36.2672 | 38.6454 | 36.9137 | 39.1176 | 36.7533 | 39.5425 | 36.352 | 38.6224 | 40.5386 | 94.1015 | 94.3999 | 93.7837
2022-09-07 20:05 | 1:41 | 22.5011 | 23.7942 | 25.5535 | 35.7703 | 38.8616 | 35.0386 | 38.5452 | 34.5311 | 38.8749 | 36.2686 | 36.8841 | 40.2166 | 34.1321 | 35.8932 | 36.672 | 35.8451 | 35.3085 | 35.7041 | 36.041 | 37.6768 | 26.3559 | 22.4804 | 29.6306 | 36.1841 | 34.7029 | 38.5641 | 36.7028 | 36.0271 | 35.1024 | 36.6173 | 32.7765 | 37.1635 | 35.1149 | 35.4503 | 33.823 | 36.8551 | 36.6991 | 36.4209 | 38.2774 | 36.2939 | 36.4671 | 37.6581 | 38.937 | 36.2713 | 38.0229 | 37.1644 | 39.2343 | 35.5648 | 38.4971 | 36.198 | 38.7301 | 36.8428 | 39.0772 | 36.7306 | 39.6178 | 36.3181 | 38.55 | 40.3605 | 94.011 | 94.2977 | 93.7352
2022-09-07 20:05 | 1:41 | 22.3498 | 23.625 | 25.345 | 35.702 | 38.7816 | 35.1936 | 38.5854 | 34.4419 | 38.8376 | 36.2376 | 36.8103 | 40.1671 | 34.044 | 35.8949 | 36.6581 | 35.8549 | 35.2371 | 35.6284 | 36.0797 | 37.6567 | 26.0975 | 22.3626 | 29.4688 | 36.0746 | 34.6386 | 38.4385 | 36.5754 | 35.9601 | 35.0234 | 36.5718 | 32.8862 | 37.0487 | 35.0344 | 35.3769 | 33.6676 | 36.6494 | 36.5796 | 36.3865 | 38.1923 | 36.1942 | 36.3774 | 37.6215 | 38.9209 | 36.1418 | 38.0323 | 37.0894 | 39.1622 | 35.5381 | 38.4352 | 36.2504 | 38.5139 | 36.7691 | 39.0163 | 36.6825 | 39.4621 | 36.2822 | 38.4676 | 40.3511 | 93.9251 | 94.2021 | 93.7497
2022-09-07 20:05 | 1:41 | 22.1772 | 23.4531 | 25.2483 | 35.7042 | 38.7764 | 35.0262 | 38.4921 | 34.3362 | 38.8425 | 36.1541 | 36.6098 | 40.0985 | 33.9494 | 35.8407 | 36.6826 | 35.7992 | 35.1598 | 35.7013 | 36.0173 | 37.6762 | 25.8269 | 22.2226 | 29.1949 | 36.1158 | 34.5673 | 38.5456 | 36.6085 | 35.9755 | 35.0483 | 36.4403 | 32.5902 | 37.1518 | 35.0981 | 35.3154 | 33.7278 | 36.779 | 36.5802 | 36.4103 | 38.2582 | 36.1301 | 36.3315 | 37.5959 | 38.7983 | 36.0956 | 37.901 | 37.0192 | 39.0932 | 35.5385 | 38.3139 | 36.1075 | 38.5828 | 36.7444 | 39.0017 | 36.4737 | 39.459 | 36.1185 | 38.1989 | 40.22 | 93.9157 | 94.169 | 93.7256
2022-09-07 20:05 | 1:41 | 22.0871 | 23.3355 | 25.1333 | 35.5961 | 38.7164 | 34.9603 | 38.4403 | 34.283 | 38.7903 | 35.9671 | 36.54 | 40.0619 | 33.8855 | 35.7338 | 36.7042 | 35.7629 | 35.1242 | 35.6665 | 36.0169 | 37.5345 | 25.5874 | 22.1527 | 29.0184 | 35.9637 | 34.4648 | 38.5384 | 36.5903 | 35.8413 | 34.895 | 36.5997 | 32.5104 | 36.9325 | 34.9439 | 35.2259 | 33.652 | 36.6734 | 36.5257 | 36.2579 | 38.3325 | 36.0744 | 36.2667 | 37.505 | 38.8281 | 35.9706 | 37.8696 | 36.9851 | 39.1238 | 35.3988 | 38.2981 | 36.0309 | 38.2488 | 36.512 | 38.9485 | 36.4111 | 39.4285 | 36.0631 | 38.3113 | 40.0975 | 93.9033 | 94.1495 | 93.7947
2022-09-07 20:05 | 1:41 | 21.8498 | 23.097 | 24.9275 | 35.3573 | 38.6517 | 34.8728 | 38.4169 | 34.3422 | 38.7646 | 35.8746 | 36.5237 | 40.0537 | 33.8596 | 35.5901 | 36.5523 | 35.6979 | 35.084 | 35.4079 | 35.9106 | 37.278 | 25.3752 | 22.0313 | 28.834 | 35.8515 | 34.4352 | 38.4374 | 36.4671 | 35.7015 | 34.8354 | 36.3374 | 32.4385 | 36.9131 | 34.8991 | 35.1782 | 33.443 | 36.458 | 36.3889 | 36.2244 | 38.1867 | 36.0118 | 36.127 | 37.4794 | 38.7302 | 35.8556 | 37.796 | 36.9179 | 39.098 | 35.2626 | 38.1518 | 35.9918 | 37.9318 | 36.7426 | 38.6634 | 36.435 | 39.4085 | 36.0469 | 38.1879 | 40.1603 | 93.8258 | 94.0857 | 93.599
2022-09-07 20:05 | 1:41 | 21.812 | 23.0348 | 24.8313 | 35.5079 | 38.6374 | 34.8483 | 38.3688 | 34.2077 | 38.6679 | 35.9728 | 36.5401 | 39.9796 | 33.8174 | 35.6892 | 36.6632 | 35.6487 | 35.0063 | 35.4576 | 35.8236 | 37.2737 | 25.1613 | 21.8706 | 28.6571 | 35.8268 | 34.3222 | 38.2324 | 36.3774 | 35.5902 | 34.7549 | 36.2641 | 32.3044 | 36.8077 | 34.7484 | 35.1472 | 33.3565 | 36.6291 | 36.2667 | 36.1815 | 38.1101 | 35.8713 | 36.1005 | 37.3708 | 38.7138 | 35.7791 | 37.8135 | 36.8644 | 38.9772 | 35.1429 | 37.9779 | 35.9681 | 38.0382 | 36.5695 | 38.5952 | 36.3025 | 39.4461 | 35.9704 | 38.0518 | 40.2382 | 93.7592 | 94.038 | 93.5689
2022-09-07 20:06 | 1:41 | 21.6523 | 22.8296 | 24.6696 | 35.2188 | 38.6602 | 34.719 | 38.441 | 34.1135 | 38.6443 | 35.8241 | 36.4313 | 40.0218 | 33.6703 | 35.7122 | 36.4337 | 35.5763 | 34.9512 | 35.4466 | 35.7694 | 37.2427 | 24.9241 | 21.7415 | 28.5001 | 35.6486 | 34.2979 | 38.4239 | 36.3315 | 35.5978 | 34.7482 | 36.2128 | 32.1527 | 36.9554 | 34.7473 | 35.0641 | 33.2724 | 36.5451 | 36.0865 | 36.084 | 38.0742 | 35.7445 | 36.0428 | 37.2568 | 38.5279 | 35.7532 | 37.7184 | 36.7814 | 38.9117 | 35.192 | 38.1514 | 35.9048 | 38.4802 | 36.3905 | 38.6667 | 36.2129 | 39.0774 | 35.8999 | 38.0825 | 39.9057 | 93.7131 | 93.9517 | 93.6125
2022-09-07 20:06 | 1:42 | 21.5755 | 22.7253 | 24.5684 | 35.4318 | 38.5431 | 34.7889 | 38.3906 | 34.0662 | 38.6533 | 35.8938 | 36.1454 | 39.9144 | 33.6483 | 35.5 | 36.3582 | 35.544 | 34.839 | 35.3068 | 35.7888 | 37.3698 | 24.7231 | 21.5936 | 28.3988 | 35.5333 | 34.2046 | 38.0756 | 36.2667 | 35.8141 | 34.7037 | 36.1846 | 32.3691 | 36.8322 | 34.5902 | 34.9676 | 33.0423 | 36.6138 | 36.0196 | 36.0858 | 38.1604 | 35.6716 | 35.9725 | 37.1517 | 38.4915 | 35.649 | 37.5696 | 36.7348 | 38.8848 | 34.9841 | 38.1468 | 35.7878 | 38.7916 | 36.1227 | 38.8033 | 36.2 | 39.0478 | 35.7323 | 38.0568 | 39.6919 | 93.7374 | 93.8795 | 93.5976
2022-09-07 20:06 | 1:42 | 21.4272 | 22.6165 | 24.4476 | 35.2231 | 38.5597 | 34.6712 | 38.2801 | 34.0014 | 38.542 | 35.8188 | 36.2881 | 39.8625 | 33.6147 | 35.5133 | 36.3845 | 35.4609 | 34.8137 | 35.321 | 35.6149 | 37.2683 | 24.5937 | 21.5823 | 28.279 | 35.5026 | 34.1194 | 38.0932 | 36.127 | 35.6569 | 34.642 | 36.1609 | 32.2449 | 36.6458 | 34.6633 | 34.9107 | 33.0123 | 36.4508 | 36.0056 | 35.9817 | 38.0987 | 35.6212 | 35.9759 | 37.1933 | 38.4389 | 35.5621 | 37.4543 | 36.6227 | 38.8554 | 34.947 | 38.0418 | 35.7393 | 38.4199 | 36.2156 | 38.7473 | 36.0656 | 39.1107 | 35.642 | 37.9161 | 39.698 | 93.6758 | 93.8023 | 93.5776
2022-09-07 20:06 | 1:42 | 21.2618 | 22.4137 | 24.3013 | 35.0817 | 38.5014 | 34.5846 | 38.2485 | 33.95 | 38.5498 | 35.8233 | 36.2699 | 39.8999 | 33.4403 | 35.3982 | 36.2972 | 35.4083 | 34.7614 | 35.2283 | 35.6038 | 37.1207 | 24.4313 | 21.4808 | 28.1511 | 35.4947 | 34.0395 | 38.0155 | 36.1005 | 35.4629 | 34.5564 | 35.9776 | 32.0864 | 36.6466 | 34.571 | 34.7686 | 32.9783 | 36.4342 | 36.2215 | 35.8192 | 37.8861 | 35.7174 | 35.8701 | 37.0333 | 38.3258 | 35.5215 | 37.4207 | 36.6271 | 38.7964 | 34.9327 | 37.8133 | 35.5743 | 38.4418 | 36.2043 | 38.757 | 36.0946 | 38.7878 | 35.6862 | 37.9906 | 39.9891 | 93.556 | 93.7472 | 93.4456
2022-09-07 20:06 | 1:42 | 21.1892 | 22.3173 | 24.1695 | 35.0614 | 38.4793 | 34.6827 | 38.1926 | 33.8477 | 38.4518 | 35.7467 | 36.0782 | 39.8105 | 33.4145 | 35.3565 | 36.3158 | 35.3481 | 34.6135 | 35.1116 | 35.6489 | 37.2485 | 24.3105 | 21.3498 | 28.0118 | 35.3399 | 33.9783 | 37.8401 | 36.0428 | 35.3933 | 34.5561 | 35.9495 | 31.9839 | 36.5964 | 34.4454 | 34.6889 | 33.0859 | 36.3554 | 36.3153 | 35.7287 | 37.9238 | 35.8072 | 35.7881 | 36.9391 | 38.3222 | 35.4738 | 37.3849 | 36.5465 | 38.8894 | 34.8491 | 37.8213 | 35.5883 | 38.4013 | 36.0992 | 38.6745 | 36.0018 | 39.0863 | 35.5385 | 37.6913 | 39.8156 | 93.4576 | 93.6287 | 93.3078
2022-09-07 20:06 | 1:42 | 21.2042 | 22.2641 | 24.1152 | 34.9584 | 38.4096 | 34.533 | 38.1702 | 33.7243 | 38.4511 | 35.4816 | 35.9486 | 39.6696 | 33.3242 | 35.3393 | 36.2271 | 35.3251 | 34.5705 | 35.2303 | 35.5216 | 37.0833 | 24.1923 | 21.2005 | 27.9097 | 35.2977 | 33.9381 | 37.9579 | 35.9725 | 35.3328 | 34.4599 | 35.9613 | 31.8861 | 36.5868 | 34.3333 | 34.6654 | 33.0239 | 36.3804 | 36.111 | 35.7483 | 37.8307 | 35.675 | 35.8388 | 36.9302 | 38.2337 | 35.368 | 37.4275 | 36.4874 | 38.7643 | 34.8106 | 37.6523 | 35.4647 | 38.0742 | 36.0051 | 38.5677 | 35.8879 | 39.2585 | 35.4615 | 37.811 | 39.8787 | 93.3908 | 93.5408 | 93.2685
2022-09-07 20:07 | 1:43 | 20.9539 | 22.0882 | 23.9778 | 34.9118 | 38.4154 | 34.5234 | 38.0292 | 33.6986 | 38.4341 | 35.4085 | 36.0161 | 39.7601 | 33.2541 | 35.4035 | 36.1979 | 35.2715 | 34.5308 | 35.2751 | 35.4691 | 36.9968 | 24.0861 | 21.0243 | 27.8198 | 35.1672 | 33.876 | 38.257 | 35.9759 | 35.2407 | 34.3653 | 35.8809 | 31.7563 | 36.6039 | 34.3113 | 34.6143 | 32.8778 | 36.2588 | 36.0225 | 35.6018 | 37.6731 | 35.5452 | 35.7983 | 36.7867 | 38.2508 | 35.2908 | 37.2384 | 36.422 | 38.6541 | 34.6927 | 37.6142 | 35.4479 | 37.8367 | 35.779 | 38.4614 | 35.7762 | 38.7662 | 35.3663 | 37.6041 | 39.7409 | 93.2508 | 93.4327 | 93.1853
2022-09-07 20:07 | 1:43 | 20.95 | 22.0736 | 23.8516 | 34.8731 | 38.3661 | 34.3184 | 37.9687 | 33.6019 | 38.3789 | 35.5046 | 35.9445 | 39.7342 | 33.1783 | 35.2714 | 36.1439 | 35.2225 | 34.4698 | 35.0408 | 35.3822 | 36.898 | 23.9611 | 20.9116 | 27.7487 | 35.1869 | 33.7405 | 38.2162 | 35.8701 | 35.1709 | 34.2768 | 35.8571 | 31.71 | 36.4554 | 34.2041 | 34.4749 | 32.7618 | 36.0433 | 35.9347 | 35.6055 | 37.6136 | 35.4241 | 35.8879 | 36.7883 | 38.123 | 35.1289 | 37.2688 | 36.3591 | 38.6468 | 34.6483 | 37.5269 | 35.3321 | 37.4777 | 35.8248 | 38.2458 | 35.8037 | 39.0749 | 35.389 | 37.5545 | 39.719 | 93.1103 | 93.3181 | 93.0936
2022-09-07 20:07 | 1:43 | 20.0684 | 21.717 | 23.6 | 34.7826 | 38.2479 | 34.2133 | 37.964 | 33.6222 | 38.3429 | 35.4285 | 35.8612 | 39.7088 | 33.1003 | 35.1075 | 36.0012 | 35.1609 | 34.4193 | 34.9102 | 35.3379 | 36.8801 | 23.9066 | 20.7676 | 27.8503 | 35.1246 | 33.6963 | 38.0548 | 35.7881 | 35.1255 | 34.2238 | 35.7604 | 31.6644 | 36.2626 | 34.103 | 34.4453 | 32.8458 | 36.0831 | 35.7233 | 35.5646 | 37.4187 | 35.3674 | 35.8838 | 36.7243 | 38.0947 | 35.2191 | 37.22 | 36.3236 | 38.5145 | 34.598 | 37.5103 | 35.3819 | 37.4925 | 35.8101 | 38.2796 | 35.696 | 38.7097 | 35.3349 | 37.5482 | 39.605 | 93.0099 | 93.1923 | 93.0701
2022-09-07 20:07 | 1:43 | 18.7498 | 21.111 | 22.9108 | 34.57 | 38.2149 | 34.384 | 38.0117 | 33.4692 | 38.2926 | 35.3651 | 35.5515 | 39.6052 | 32.9591 | 34.9184 | 35.9097 | 35.0828 | 34.2879 | 34.8607 | 35.2714 | 36.8641 | 24.2361 | 21.7236 | 28.743 | 35.0526 | 33.6888 | 38.0713 | 35.8388 | 35.0356 | 34.1872 | 35.7293 | 31.8997 | 36.4375 | 34.084 | 34.4222 | 32.775 | 35.8858 | 35.7035 | 35.4574 | 37.4581 | 35.3241 | 35.987 | 36.8098 | 38.0992 | 35.2617 | 37.3478 | 36.2608 | 38.6446 | 34.7606 | 37.6973 | 35.3095 | 37.8331 | 35.7525 | 38.2501 | 35.5457 | 38.9185 | 35.3665 | 37.639 | 39.4784 | 92.8896 | 93.0716 | 92.978
2022-09-07 20:07 | 1:43 | 18.2328 | 20.7011 | 22.426 | 34.4446 | 38.099 | 34.2665 | 37.7689 | 33.4352 | 38.243 | 35.2941 | 35.5322 | 39.5964 | 32.8369 | 34.9419 | 35.8218 | 34.9713 | 34.2428 | 34.7712 | 35.1467 | 36.818 | 25.0957 | 23.0118 | 29.8146 | 35.0518 | 33.7285 | 38.0673 | 35.7983 | 35.1987 | 34.1727 | 35.8106 | 32.2028 | 36.4102 | 33.923 | 34.5314 | 32.8816 | 36.0189 | 35.6407 | 35.4672 | 37.4161 | 35.2406 | 35.9335 | 36.9174 | 38.1743 | 35.4554 | 37.5728 | 36.2509 | 38.7094 | 34.9323 | 37.7026 | 35.4697 | 37.5155 | 35.9281 | 38.3263 | 35.6138 | 38.9704 | 35.5198 | 38.0608 | 39.366 | 92.7532 | 92.9436 | 92.9502
2022-09-07 20:07 | 1:43 | 17.7056 | 20.2869 | 22.0302 | 34.2712 | 37.9267 | 33.9963 | 37.6014 | 33.229 | 38.1467 | 35.1831 | 35.4873 | 39.5924 | 32.7507 | 34.9905 | 35.6456 | 34.9233 | 34.0908 | 34.6454 | 35.0315 | 36.6355 | 26.0961 | 24.5192 | 30.682 | 35.1786 | 33.7487 | 38.3068 | 35.8879 | 35.0669 | 34.1781 | 35.7992 | 32.5409 | 36.3516 | 33.8645 | 34.504 | 33.1245 | 36.0021 | 35.7284 | 35.5573 | 37.3624 | 35.3235 | 36.011 | 36.984 | 38.3123 | 35.5747 | 37.5562 | 36.2543 | 38.6015 | 35.1037 | 37.7845 | 35.5339 | 37.2602 | 36.1195 | 38.3735 | 35.8314 | 39.0155 | 35.6515 | 37.9976 | 39.4409 | 92.5715 | 92.7545 | 92.8496
2022-09-07 20:08 | 1:43 | 17.2844 | 19.9418 | 21.5892 | 34.2591 | 37.9322 | 33.8977 | 37.5887 | 33.0272 | 38.0757 | 35.0918 | 35.3611 | 39.5382 | 32.6536 | 34.7667 | 35.735 | 34.893 | 34.0291 | 34.4374 | 34.9214 | 36.5618 | 27.0667 | 25.912 | 31.3004 | 35.3388 | 33.7998 | 38.1307 | 35.8838 | 35.0488 | 34.1542 | 35.9041 | 32.7263 | 36.2501 | 33.8828 | 34.664 | 33.2032 | 36.1389 | 35.6032 | 35.5592 | 37.332 | 35.2695 | 36.0853 | 37.0766 | 38.3779 | 35.746 | 37.794 | 36.2487 | 38.6229 | 35.238 | 37.8858 | 35.6039 | 37.2479 | 36.2142 | 38.4452 | 35.7438 | 39.0447 | 35.7475 | 38.0783 | 39.4906 | 92.4524 | 92.6688 | 92.7622
2022-09-07 20:08 | 1:44 | 16.9662 | 19.6372 | 21.308 | 34.2783 | 37.8625 | 33.8951 | 37.5409 | 33.0162 | 38.0509 | 35.1775 | 35.2296 | 39.3688 | 32.5491 | 34.7803 | 35.5343 | 34.7788 | 33.917 | 34.5228 | 34.9323 | 36.5444 | 27.9097 | 27.1021 | 31.7702 | 35.3453 | 33.8295 | 38.4181 | 35.987 | 35.175 | 34.065 | 36.0103 | 32.8775 | 36.1277 | 33.8635 | 34.7472 | 33.2634 | 36.1149 | 35.4885 | 35.5621 | 37.1668 | 35.2466 | 36.1793 | 37.1497 | 38.4609 | 35.8836 | 37.8153 | 36.2651 | 38.685 | 35.3371 | 37.9958 | 35.5928 | 37.2586 | 36.3066 | 38.3875 | 35.8657 | 39.1262 | 35.8349 | 38.1941 | 39.4812 | 92.3337 | 92.4722 | 92.7089
2022-09-07 20:08 | 1:44 | 16.6183 | 19.2948 | 20.9508 | 34.0232 | 37.678 | 33.9016 | 37.3748 | 32.8846 | 38.0097 | 35.1132 | 34.9893 | 39.4949 | 32.4896 | 34.6061 | 35.4493 | 34.711 | 33.7994 | 34.277 | 34.8482 | 36.4999 | 28.6605 | 28.0976 | 32.098 | 35.3854 | 33.8824 | 38.4382 | 35.9335 | 35.2216 | 34.159 | 35.9371 | 33.0597 | 36.0765 | 33.7847 | 34.7362 | 33.3453 | 36.0095 | 35.4724 | 35.5443 | 37.1915 | 35.2642 | 36.1996 | 37.1883 | 38.4918 | 35.9325 | 37.8708 | 36.2593 | 38.6607 | 35.4307 | 38.0514 | 35.67 | 37.3451 | 36.3784 | 38.4192 | 35.8553 | 39.1546 | 35.8757 | 38.2092 | 39.3699 | 92.2519 | 92.2821 | 92.6303
2022-09-07 20:08 | 1:44 | 16.3652 | 19.0374 | 20.7491 | 33.9808 | 37.5872 | 33.5863 | 37.3006 | 32.7707 | 37.8953 | 34.8113 | 34.5434 | 39.2157 | 32.3679 | 34.586 | 35.4301 | 34.5891 | 33.7937 | 34.1742 | 34.7237 | 36.4144 | 29.2665 | 28.8213 | 32.3689 | 35.3931 | 33.8768 | 38.5036 | 36.011 | 35.0902 | 34.0712 | 36.0311 | 33.1193 | 36.1313 | 33.7238 | 34.726 | 33.3967 | 36.0935 | 35.4502 | 35.5274 | 37.3128 | 35.2885 | 36.1975 | 37.1991 | 38.5293 | 36.0133 | 37.905 | 36.2764 | 38.6664 | 35.4964 | 38.0647 | 35.6807 | 37.333 | 36.4943 | 38.4513 | 35.8762 | 39.2188 | 35.9601 | 38.2923 | 39.3575 | 92.1297 | 92.0891 | 92.5125
2022-09-07 20:08 | 1:44 | 16.0961 | 18.7665 | 20.5414 | 33.7611 | 37.5335 | 33.5736 | 37.138 | 32.6566 | 37.852 | 34.9546 | 34.8091 | 39.0479 | 32.2233 | 34.4439 | 35.3242 | 34.5311 | 33.7024 | 34.2653 | 34.5775 | 36.2974 | 29.7699 | 29.4154 | 32.5671 | 35.4029 | 33.8975 | 38.5919 | 36.0853 | 34.788 | 33.9944 | 35.9352 | 33.209 | 36.042 | 33.6004 | 34.708 | 33.4538 | 36.1102 | 35.4165 | 35.5461 | 37.2928 | 35.2503 | 36.2366 | 37.2486 | 38.5315 | 36.08 | 37.931 | 36.2503 | 38.674 | 35.5525 | 38.1918 | 35.719 | 37.3501 | 36.4699 | 38.3995 | 35.7491 | 39.2324 | 35.9526 | 38.3419 | 39.6518 | 91.9537 | 92.0374 | 92.4058
2022-09-07 20:08 | 1:44 | 15.8149 | 18.4956 | 20.285 | 33.7554 | 37.4541 | 33.4002 | 37.1279 | 32.465 | 37.7846 | 34.9375 | 34.6618 | 39.0007 | 32.0785 | 34.183 | 35.2988 | 34.4437 | 33.593 | 34.0721 | 34.4891 | 36.3741 | 30.1864 | 29.9009 | 32.7126 | 35.382 | 33.8693 | 38.7784 | 36.1793 | 34.7433 | 34.0778 | 36.0254 | 33.2597 | 35.8671 | 33.5847 | 34.6875 | 33.5096 | 35.9621 | 35.3218 | 35.4492 | 37.0961 | 35.2153 | 36.2132 | 37.2743 | 38.5108 | 36.145 | 37.9447 | 36.2575 | 38.7147 | 35.6154 | 38.1858 | 35.7566 | 37.4337 | 36.4986 | 38.5698 | 35.7513 | 39.209 | 36.0055 | 38.2179 | 39.4403 | 91.8344 | 91.9847 | 92.4162
2022-09-07 20:09 | 1:44 | 15.5901 | 18.2674 | 20.0535 | 33.7315 | 37.29 | 33.2987 | 37.1381 | 32.3396 | 37.6964 | 34.7204 | 34.3439 | 38.8892 | 31.8834 | 34.1089 | 35.2479 | 34.3945 | 33.4178 | 33.9672 | 34.458 | 36.3314 | 30.5014 | 30.2149 | 32.8041 | 35.3827 | 33.8929 | 38.7352 | 36.1996 | 34.6346 | 34.0289 | 36.1029 | 33.3701 | 35.8897 | 33.5926 | 34.6952 | 33.5395 | 35.8483 | 35.2792 | 35.4838 | 37.0007 | 35.238 | 36.2274 | 37.3565 | 38.5718 | 36.224 | 38.0343 | 36.2705 | 38.7922 | 35.7198 | 38.2403 | 35.7505 | 37.4722 | 36.5344 | 38.6089 | 35.8459 | 39.1906 | 36.0783 | 38.2333 | 39.4337 | 91.8349 | 91.9182 | 92.3923
2022-09-07 20:09 | 1:45 | 15.4028 | 18.0121 | 19.8497 | 33.4856 | 37.1855 | 33.313 | 36.9661 | 32.2872 | 37.6242 | 34.5109 | 34.4307 | 38.9305 | 31.7612 | 34.0959 | 35.3225 | 34.3378 | 33.4016 | 33.7693 | 34.338 | 36.1612 | 30.7687 | 30.4763 | 32.9076 | 35.3388 | 33.9194 | 38.8892 | 36.1975 | 34.5788 | 33.9577 | 36.1369 | 33.4152 | 35.7509 | 33.4588 | 34.6181 | 33.5916 | 35.9752 | 35.3156 | 35.3726 | 37.189 | 35.2244 | 36.31 | 37.3623 | 38.5705 | 36.2715 | 38.0297 | 36.2532 | 38.7524 | 35.7567 | 38.2601 | 35.8349 | 37.449 | 36.5971 | 38.5336 | 35.8225 | 39.0852 | 36.0714 | 38.4595 | 39.3206 | 91.9249 | 91.933 | 92.483
2022-09-07 20:09 | 1:45 | 15.1193 | 17.7541 | 19.6097 | 33.5156 | 37.1035 | 33.1091 | 36.737 | 32.1118 | 37.6264 | 34.6771 | 34.247 | 38.8622 | 31.7359 | 34.1171 | 35.2267 | 34.1916 | 33.3013 | 33.7763 | 34.2067 | 36.1546 | 30.9678 | 30.6672 | 32.9976 | 35.3894 | 33.8837 | 38.7136 | 36.2366 | 34.6764 | 33.9747 | 36.2044 | 33.4667 | 35.6478 | 33.4755 | 34.6752 | 33.6358 | 35.8868 | 35.2734 | 35.4068 | 37.1309 | 35.2162 | 36.3166 | 37.42 | 38.6391 | 36.2718 | 38.0374 | 36.2366 | 38.6665 | 35.7844 | 38.3269 | 35.7938 | 37.5517 | 36.6039 | 38.5652 | 35.8576 | 39.2155 | 36.1287 | 38.4937 | 39.2848 | 91.9889 | 91.9653 | 92.4321
2022-09-07 20:09 | 1:45 | 14.8971 | 17.5395 | 19.2797 | 33.3711 | 37.0258 | 33.0286 | 36.7891 | 31.9793 | 37.4354 | 34.5729 | 34.0735 | 38.6883 | 31.6221 | 33.8732 | 35.3427 | 34.1208 | 33.1583 | 33.4937 | 34.1237 | 36.0314 | 31.1243 | 30.8152 | 33.047 | 35.3634 | 33.9386 | 38.6484 | 36.2132 | 34.4606 | 34.0606 | 36.0754 | 33.5179 | 35.6633 | 33.3925 | 34.821 | 33.671 | 35.7514 | 35.1882 | 35.4808 | 37.0809 | 35.1711 | 36.2908 | 37.3814 | 38.6091 | 36.3383 | 38.0432 | 36.2725 | 38.7567 | 35.852 | 38.3394 | 35.8182 | 37.4675 | 36.6933 | 38.4961 | 35.8064 | 39.101 | 36.1704 | 38.5802 | 39.2987 | 92.127 | 92.0518 | 92.5364
2022-09-07 20:09 | 1:45 | 14.6848 | 17.2754 | 19.0264 | 33.3245 | 36.8589 | 32.8973 | 36.7624 | 31.8036 | 37.3288 | 34.4571 | 33.8387 | 38.6487 | 31.513 | 33.8633 | 34.9926 | 34.1156 | 33.0366 | 33.3846 | 34.0157 | 36.0742 | 31.2298 | 30.9301 | 33.1199 | 35.3531 | 33.9155 | 38.7878 | 36.2274 | 34.6113 | 33.8932 | 36.0529 | 33.5512 | 35.5645 | 33.3567 | 34.7861 | 33.718 | 35.9516 | 35.1206 | 35.4112 | 36.9632 | 35.1412 | 36.3006 | 37.3987 | 38.6287 | 36.355 | 38.2044 | 36.2811 | 38.7806 | 35.8934 | 38.2914 | 35.9062 | 37.5558 | 36.6945 | 38.6163 | 35.8277 | 39.0498 | 36.2005 | 38.6914 | 39.2837 | 92.189 | 92.1449 | 92.6076
2022-09-07 20:09 | 1:45 | 14.5121 | 17.0853 | 18.8889 | 33.2281 | 36.7454 | 32.9344 | 36.6246 | 31.5858 | 37.313 | 34.1589 | 33.5577 | 38.4949 | 31.4112 | 33.6306 | 34.8948 | 33.9903 | 32.9103 | 33.1697 | 33.9812 | 36.1769 | 31.3369 | 31.0337 | 33.2006 | 35.3353 | 33.9138 | 39.0615 | 36.31 | 34.3813 | 33.9893 | 36.3512 | 33.5849 | 35.6284 | 33.3303 | 34.746 | 33.7312 | 35.7363 | 35.0569 | 35.396 | 36.9881 | 35.107 | 36.3895 | 37.4537 | 38.6369 | 36.3975 | 38.204 | 36.3013 | 38.6492 | 35.9484 | 38.3693 | 35.8606 | 37.5238 | 36.6999 | 38.6069 | 35.8366 | 39.0728 | 36.2696 | 38.5679 | 39.3447 | 92.2949 | 92.2212 | 92.6593
2022-09-07 20:10 | 1:46 | 14.2562 | 16.8138 | 18.7129 | 33.2109 | 36.6583 | 32.7823 | 36.413 | 31.5233 | 37.1708 | 34.1552 | 33.4836 | 38.4735 | 31.3773 | 33.5452 | 34.771 | 33.8466 | 32.9485 | 33.2764 | 33.8998 | 36.1153 | 31.4362 | 31.0796 | 33.2433 | 35.3048 | 33.9761 | 38.971 | 36.3166 | 34.5377 | 33.7938 | 36.3213 | 33.6103 | 35.4759 | 33.3037 | 34.6918 | 33.7493 | 35.7701 | 35.0615 | 35.2509 | 37.0115 | 35.0924 | 36.3393 | 37.4694 | 38.72 | 36.4285 | 38.2867 | 36.3215 | 38.7157 | 35.9925 | 38.3164 | 35.873 | 37.4673 | 36.7311 | 38.5533 | 35.9415 | 39.2949 | 36.2764 | 38.6518 | 39.3327 | 92.3144 | 92.2706 | 92.6981
2022-09-07 20:10 | 1:46 | 14.0761 | 16.6378 | 18.5132 | 33.021 | 36.4639 | 32.8314 | 36.2195 | 31.5063 | 37.0852 | 34.1604 | 33.4493 | 38.3675 | 31.1575 | 33.7124 | 34.7751 | 33.7481 | 32.8073 | 33.158 | 33.8092 | 35.8671 | 31.5061 | 31.1579 | 33.2666 | 35.2116 | 33.9551 | 38.7956 | 36.2908 | 34.4886 | 33.687 | 36.3021 | 33.649 | 35.4476 | 33.3627 | 34.8444 | 33.8093 | 35.6742 | 34.9359 | 35.4233 | 36.7859 | 35.0286 | 36.3641 | 37.5363 | 38.7507 | 36.4758 | 38.26 | 36.32 | 38.7396 | 36.0705 | 38.3281 | 35.9107 | 37.5537 | 36.8142 | 38.4854 | 35.8798 | 39.184 | 36.2987 | 38.7036 | 39.3353 | 92.4302 | 92.3957 | 92.759
2022-09-07 20:10 | 1:46 | 13.6565 | 14.443 | 18.0595 | 32.956 | 36.4241 | 32.8728 | 36.2728 | 31.3637 | 37.0033 | 34.1441 | 33.4639 | 38.2963 | 30.8787 | 33.5026 | 34.659 | 33.6336 | 32.7302 | 33.1002 | 33.7114 | 35.8888 | 31.5279 | 31.1901 | 33.3077 | 35.2379 | 33.9069 | 38.9697 | 36.3006 | 34.3947 | 33.8639 | 36.0353 | 33.7067 | 35.399 | 33.317 | 34.7604 | 33.8657 | 35.6488 | 34.9904 | 35.3902 | 36.6257 | 35.0386 | 36.3854 | 37.5226 | 38.7375 | 36.5115 | 38.1825 | 36.3114 | 38.7178 | 36.1021 | 38.3379 | 35.9239 | 37.6572 | 36.8653 | 38.4202 | 35.9445 | 39.1648 | 36.3512 | 38.7144 | 39.3163 | 92.5112 | 92.5263 | 92.7825
2022-09-07 20:10 | 1:46 | 15.7016 | 15.4072 | 20.497 | 32.9087 | 36.256 | 32.8503 | 35.9374 | 31.3921 | 36.9453 | 34.3235 | 33.3272 | 38.2957 | 31.0977 | 33.3067 | 34.5562 | 33.6026 | 32.7979 | 33.2364 | 33.6507 | 35.8167 | 31.522 | 31.2175 | 33.3368 | 35.2192 | 33.9732 | 39.036 | 36.3895 | 34.3237 | 33.755 | 36.365 | 33.7425 | 35.282 | 33.3169 | 34.8592 | 33.8803 | 35.7867 | 34.963 | 35.4148 | 36.6014 | 34.9962 | 36.468 | 37.5627 | 38.7484 | 36.5517 | 38.2397 | 36.351 | 38.6998 | 36.1565 | 38.3975 | 35.9971 | 37.5811 | 36.9363 | 38.6179 | 35.9322 | 39.1035 | 36.3928 | 38.6803 | 39.3438 | 92.6439 | 92.579 | 92.8678
2022-09-07 20:10 | 1:46 | 18.0402 | 17.9284 | 23.4803 | 33.6027 | 36.2599 | 32.9308 | 36.1684 | 31.5293 | 36.9331 | 34.4807 | 33.7475 | 38.3503 | 31.5211 | 33.58 | 34.8001 | 33.6219 | 32.8488 | 33.5162 | 33.7402 | 36.0598 | 31.5588 | 31.2464 | 33.4041 | 35.4224 | 34.0115 | 39.0311 | 36.3393 | 34.3509 | 33.8507 | 36.1242 | 33.7655 | 35.165 | 33.4943 | 34.8355 | 33.9124 | 35.7741 | 34.9759 | 35.5073 | 36.9841 | 35.0381 | 36.4786 | 37.5798 | 38.7702 | 36.6448 | 38.3457 | 36.4096 | 38.6853 | 36.2406 | 38.4278 | 36.0701 | 37.5878 | 36.953 | 38.5587 | 36.019 | 39.1763 | 36.4271 | 38.6483 | 39.3653 | 92.7427 | 92.6452 | 92.8842
2022-09-07 20:10 | 1:46 | 20.2239 | 20.655 | 25.8541 | 34.2111 | 36.3487 | 33.1501 | 36.319 | 31.9232 | 36.9665 | 34.7991 | 33.8863 | 38.3177 | 31.8907 | 33.8399 | 34.9691 | 33.6382 | 33.1122 | 33.8549 | 33.9278 | 36.1529 | 31.6194 | 31.2865 | 33.5015 | 35.5403 | 34.0676 | 38.9976 | 36.3641 | 34.4011 | 33.8252 | 36.1643 | 33.8123 | 35.1917 | 33.6052 | 34.8895 | 34.0055 | 35.781 | 35.0932 | 35.5858 | 37.0311 | 35.1055 | 36.5873 | 37.6256 | 38.8584 | 36.7392 | 38.3475 | 36.4347 | 38.7185 | 36.3213 | 38.5235 | 36.1211 | 37.6878 | 36.9795 | 38.5668 | 36.1686 | 39.218 | 36.506 | 38.7512 | 39.339 | 92.74 | 92.7756 | 93.0065
2022-09-07 20:11 | 1:46 | 22.0535 | 23.0758 | 27.5034 | 34.4705 | 36.4342 | 33.2742 | 36.4732 | 32.1589 | 36.9368 | 34.7811 | 34.3435 | 38.4539 | 32.1983 | 34.0598 | 35.1128 | 33.7462 | 33.296 | 34.0518 | 34.0388 | 36.3537 | 31.6904 | 31.3303 | 33.6356 | 35.6288 | 34.1401 | 38.9765 | 36.3854 | 34.3964 | 33.9375 | 36.2886 | 33.8935 | 35.3784 | 33.6953 | 35.0214 | 34.072 | 35.9183 | 35.2041 | 35.6773 | 37.1254 | 35.1821 | 36.6033 | 37.6856 | 38.88 | 36.8289 | 38.3525 | 36.471 | 38.7748 | 36.4002 | 38.5592 | 36.1373 | 37.6951 | 37.0233 | 38.5471 | 36.2202 | 39.2248 | 36.5979 | 38.8649 | 39.3909 | 92.8631 | 92.8673 | 93.0482
2022-09-07 20:11 | 1:47 | 23.6374 | 25.1576 | 28.7493 | 34.8022 | 36.4308 | 33.4528 | 36.5813 | 32.4017 | 36.955 | 34.8657 | 34.571 | 38.4056 | 32.4203 | 34.2656 | 35.1725 | 33.8605 | 33.4703 | 34.2798 | 34.2036 | 36.5675 | 31.7961 | 31.3885 | 33.7695 | 35.7642 | 34.1468 | 38.918 | 36.468 | 34.6876 | 34.0084 | 36.2662 | 33.9547 | 35.419 | 33.8357 | 35.133 | 34.1412 | 36.0112 | 35.3516 | 35.7666 | 37.3158 | 35.2464 | 36.6061 | 37.7454 | 38.9404 | 36.9234 | 38.4181 | 36.5354 | 38.8282 | 36.4865 | 38.6167 | 36.2126 | 37.816 | 37.0764 | 38.73 | 36.2841 | 39.1596 | 36.6664 | 38.8771 | 39.3963 | 92.9659 | 92.9801 | 93.1152
2022-09-07 20:11 | 1:47 | 24.9492 | 26.8285 | 29.5616 | 35.0383 | 36.5496 | 33.6398 | 36.6913 | 32.5756 | 36.9675 | 34.9649 | 34.7386 | 38.5153 | 32.6225 | 34.3399 | 35.2877 | 33.8941 | 33.6307 | 34.5315 | 34.3045 | 36.566 | 31.9246 | 31.4148 | 33.8917 | 35.9436 | 34.1983 | 38.8454 | 36.4786 | 34.7393 | 34.0665 | 36.3725 | 34.0102 | 35.5282 | 33.9475 | 35.1924 | 34.2099 | 36.1112 | 35.3077 | 35.8836 | 37.4106 | 35.286 | 36.6386 | 37.7382 | 38.9807 | 37.0059 | 38.5437 | 36.5447 | 38.8346 | 36.5623 | 38.6744 | 36.3115 | 37.7579 | 37.1396 | 38.6986 | 36.3751 | 39.26 | 36.7392 | 38.87 | 39.4306 | 93.0514 | 93.0874 | 93.1546
2022-09-07 20:11 | 1:47 | 26.0197 | 28.1234 | 30.0829 | 35.4009 | 36.5434 | 33.7352 | 36.7074 | 32.699 | 36.9744 | 35.1457 | 34.7754 | 38.4562 | 32.8178 | 34.4803 | 35.4236 | 33.9446 | 33.8354 | 34.7094 | 34.385 | 36.6026 | 32.0247 | 31.4533 | 34.0047 | 36.0653 | 34.2735 | 38.9983 | 36.5873 | 34.6803 | 34.1256 | 36.4929 | 34.0901 | 35.4623 | 34.0571 | 35.3352 | 34.2484 | 36.1057 | 35.4484 | 35.8998 | 37.3309 | 35.37 | 36.7246 | 37.786 | 38.9935 | 37.0969 | 38.6594 | 36.5978 | 38.8538 | 36.6663 | 38.6563 | 36.327 | 37.8081 | 37.1819 | 38.8634 | 36.327 | 39.2326 | 36.7677 | 38.9098 | 39.3638 | 93.2003 | 93.1962 | 93.2762
2022-09-07 20:11 | 1:47 | 26.8985 | 29.1055 | 30.4423 | 35.6081 | 36.5813 | 33.8881 | 36.7732 | 32.8618 | 36.9668 | 35.0819 | 34.9665 | 38.5869 | 32.9549 | 34.6038 | 35.3292 | 33.9959 | 33.9696 | 34.8253 | 34.447 | 36.885 | 32.1671 | 31.4929 | 34.1632 | 36.2586 | 34.3726 | 39.1429 | 36.6033 | 34.8271 | 34.1598 | 36.4419 | 34.154 | 35.5555 | 34.1472 | 35.3713 | 34.3118 | 36.2319 | 35.5 | 35.9498 | 37.3825 | 35.4086 | 36.7285 | 37.9147 | 39.0976 | 37.1951 | 38.6013 | 36.6243 | 38.9361 | 36.7689 | 38.7415 | 36.3789 | 37.8156 | 37.2908 | 38.8891 | 36.4036 | 39.3684 | 36.8473 | 38.9472 | 39.4438 | 93.2535 | 93.2712 | 93.2859
2022-09-07 20:11 | 1:47 | 27.5825 | 29.8265 | 30.7024 | 35.6406 | 36.5753 | 33.946 | 36.8746 | 32.9334 | 37.0144 | 35.1881 | 35.1846 | 38.6452 | 33.0405 | 34.5802 | 35.5631 | 34.0285 | 34.0074 | 34.8721 | 34.4948 | 36.8232 | 32.2766 | 31.5452 | 34.2602 | 36.2595 | 34.4066 | 39.2373 | 36.6061 | 34.7356 | 34.2372 | 36.4835 | 34.2347 | 35.6246 | 34.2093 | 35.4147 | 34.4019 | 36.2215 | 35.4759 | 36.028 | 37.5526 | 35.4312 | 36.7879 | 37.9172 | 39.1424 | 37.2905 | 38.602 | 36.6791 | 38.9573 | 36.8708 | 38.7649 | 36.4202 | 37.9706 | 37.3388 | 38.7969 | 36.4229 | 39.4355 | 36.9357 | 38.9359 | 39.5134 | 93.3785 | 93.4183 | 93.3763
2022-09-07 20:12 | 1:48 | 28.1328 | 30.3286 | 30.8575 | 35.8145 | 36.5598 | 33.9601 | 36.9744 | 33.1458 | 37.0521 | 35.2483 | 35.3423 | 38.5857 | 33.2026 | 34.612 | 35.5345 | 34.0398 | 34.1193 | 34.8836 | 34.5747 | 37.0694 | 32.3918 | 31.5631 | 34.4307 | 36.3575 | 34.5143 | 39.2086 | 36.6386 | 34.8384 | 34.3912 | 36.4662 | 34.2885 | 35.6134 | 34.2707 | 35.5083 | 34.4363 | 36.1863 | 35.5819 | 36.0889 | 37.5275 | 35.4955 | 36.8181 | 38.0337 | 39.191 | 37.3815 | 38.7007 | 36.6987 | 38.9582 | 36.9427 | 38.8741 | 36.4803 | 38.0568 | 37.4132 | 38.8887 | 36.4455 | 39.4719 | 36.9911 | 38.9933 | 39.5303 | 93.5076 | 93.5387 | 93.4786
2022-09-07 20:12 | 1:48 | 28.5398 | 30.6944 | 31.0398 | 35.9312 | 36.5969 | 34.1135 | 36.9639 | 33.2051 | 37.0376 | 35.265 | 35.2818 | 38.5907 | 33.2552 | 34.7013 | 35.4709 | 34.067 | 34.1445 | 34.9403 | 34.6326 | 37.1465 | 32.5369 | 31.5947 | 34.5663 | 36.4723 | 34.5538 | 39.2003 | 36.7246 | 34.9233 | 34.3768 | 36.5513 | 34.3571 | 35.6825 | 34.3698 | 35.6038 | 34.4654 | 36.2732 | 35.6372 | 36.1475 | 37.6013 | 35.5565 | 36.8369 | 38.1145 | 39.1766 | 37.4563 | 38.7859 | 36.7422 | 38.9942 | 36.9905 | 38.9208 | 36.551 | 38.0345 | 37.4926 | 38.8158 | 36.5317 | 39.5167 | 37.0598 | 39.0538 | 39.6192 | 93.7198 | 93.5939 | 93.5908
2022-09-07 20:12 | 1:48 | 28.9038 | 30.9274 | 31.1061 | 36.0042 | 36.5579 | 34.2054 | 37.0709 | 33.3663 | 37.0377 | 35.3764 | 35.3975 | 38.5344 | 33.3424 | 34.7772 | 35.5817 | 34.1209 | 34.324 | 35.042 | 34.6657 | 37.0325 | 32.6799 | 31.6284 | 34.7551 | 36.5189 | 34.6038 | 39.0681 | 36.7285 | 35.0373 | 34.4817 | 36.5446 | 34.4354 | 35.7322 | 34.4459 | 35.7064 | 34.5332 | 36.3375 | 35.6342 | 36.2546 | 37.5963 | 35.5663 | 36.7568 | 38.1351 | 39.2046 | 37.5161 | 38.8886 | 36.8135 | 39.0377 | 37.0686 | 39.0407 | 36.627 | 38.0991 | 37.5159 | 39.0193 | 36.629 | 39.4347 | 37.141 | 39.0943 | 39.5675 | 93.8391 | 93.8675 | 93.7255
2022-09-07 20:12 | 1:48 | 29.2138 | 31.096 | 31.2231 | 36.2234 | 36.6283 | 34.2939 | 37.0661 | 33.3789 | 37.095 | 35.4061 | 35.3893 | 38.5344 | 33.4012 | 34.8306 | 35.7902 | 34.1437 | 34.3469 | 35.0989 | 34.6898 | 37.1573 | 32.8303 | 31.6179 | 34.9479 | 36.4774 | 34.6603 | 39.2452 | 36.7879 | 35.0538 | 34.5157 | 36.6526 | 34.541 | 35.7186 | 34.5352 | 35.7407 | 34.6129 | 36.3693 | 35.73 | 36.2364 | 37.6101 | 35.626 | 36.7858 | 38.1413 | 39.2769 | 37.6295 | 38.8975 | 36.8403 | 39.0664 | 37.1933 | 39.0035 | 36.628 | 38.1639 | 37.5783 | 38.8395 | 36.6236 | 39.4775 | 37.1732 | 39.2591 | 39.5791 | 94.0209 | 94.0075 | 93.7977
2022-09-07 20:12 | 1:48 | 29.436 | 31.2339 | 31.3119 | 36.1722 | 36.6152 | 34.351 | 37.1777 | 33.479 | 37.0999 | 35.4787 | 35.3326 | 38.5248 | 33.4742 | 34.9415 | 35.693 | 34.17 | 34.4463 | 35.1442 | 34.7401 | 37.2198 | 32.949 | 31.6433 | 35.1181 | 36.6521 | 34.7481 | 39.2867 | 36.8181 | 35.0278 | 34.5787 | 36.7932 | 34.6121 | 35.7206 | 34.5981 | 35.8089 | 34.6872 | 36.3541 | 35.7878 | 36.3046 | 37.722 | 35.6859 | 36.7904 | 38.2375 | 39.3554 | 37.7101 | 39.0366 | 36.894 | 39.0762 | 37.2692 | 39.0518 | 36.7411 | 38.1582 | 37.664 | 38.9511 | 36.7019 | 39.4926 | 37.2503 | 39.2231 | 39.5787 | 94.2636 | 94.1628 | 93.9047
2022-09-07 20:12 | 1:48 | 30.3446 | 25.9209 | 30.9467 | 36.223 | 36.6383 | 34.3408 | 36.9581 | 33.4574 | 37.1098 | 35.4523 | 35.4752 | 38.5083 | 33.5156 | 34.9577 | 35.7098 | 34.1972 | 34.4999 | 35.1457 | 34.7879 | 37.0885 | 33.412 | 27.7631 | 34.8185 | 36.7514 | 34.7561 | 39.275 | 36.8369 | 35.1021 | 34.565 | 36.6833 | 34.5104 | 35.7923 | 34.6106 | 35.7972 | 34.6828 | 36.3719 | 35.8458 | 36.298 | 37.5636 | 35.7447 | 36.9042 | 38.2241 | 39.3055 | 37.5686 | 38.9438 | 36.9119 | 39.0742 | 37.144 | 39.0531 | 36.7042 | 38.0477 | 37.6115 | 38.8561 | 36.7518 | 39.4359 | 37.1488 | 39.1306 | 39.6036 | 94.4282 | 94.3401 | 94.0007
2022-09-07 20:13 | 1:48 | 31.2731 | 31.2629 | 31.2709 | 36.2442 | 36.662 | 34.4468 | 37.1094 | 33.6247 | 37.1322 | 35.4604 | 35.5942 | 38.5396 | 33.5294 | 34.9594 | 35.7165 | 34.2225 | 34.4726 | 35.2548 | 34.8177 | 37.1115 | 33.5338 | 30.2883 | 34.6422 | 36.7808 | 34.7496 | 39.1264 | 36.7568 | 35.1267 | 34.5363 | 36.6175 | 34.52 | 35.8359 | 34.6971 | 35.8425 | 34.7033 | 36.3407 | 35.9653 | 36.4029 | 37.7692 | 35.7979 | 37.0101 | 38.1496 | 39.2527 | 37.4949 | 38.7694 | 36.862 | 39.0808 | 37.0776 | 38.8562 | 36.5731 | 38.0439 | 37.5884 | 38.8683 | 36.7789 | 39.5007 | 37.1412 | 39.0816 | 39.6915 | 94.5427 | 94.5348 | 94.0601
2022-09-07 20:13 | 1:49 | 32.9637 | 31.8325 | 31.5683 | 36.3496 | 36.7257 | 34.4945 | 37.2154 | 33.7658 | 37.1821 | 35.5478 | 35.8381 | 38.6989 | 33.7181 | 35.1029 | 35.8939 | 34.2927 | 34.6245 | 35.3162 | 34.9205 | 37.2137 | 33.8837 | 31.1368 | 34.9128 | 36.818 | 34.8091 | 39.1286 | 36.7858 | 35.1747 | 34.5704 | 36.904 | 34.6156 | 35.8725 | 34.755 | 35.947 | 34.7732 | 36.3827 | 36.0543 | 36.3986 | 37.7541 | 35.9105 | 37.0514 | 38.213 | 39.3026 | 37.5439 | 38.8296 | 36.9021 | 39.1762 | 37.1417 | 38.9046 | 36.7099 | 38.0904 | 37.6401 | 38.8564 | 36.773 | 39.635 | 37.2338 | 39.0379 | 39.7336 | 94.6145 | 94.6807 | 94.1524
2022-09-07 20:13 | 1:49 | 33.9754 | 31.8506 | 31.8483 | 36.5555 | 36.7107 | 34.6853 | 37.2837 | 33.8692 | 37.2076 | 35.7392 | 35.6874 | 38.6861 | 33.8036 | 35.1932 | 35.8835 | 34.372 | 34.727 | 35.4249 | 35.003 | 37.2419 | 34.31 | 31.5097 | 35.2263 | 36.8429 | 34.8957 | 39.0476 | 36.7904 | 35.1677 | 34.6341 | 36.7244 | 34.7636 | 35.9069 | 34.8428 | 35.9704 | 34.8758 | 36.4516 | 36.0774 | 36.501 | 37.764 | 35.9351 | 37.0971 | 38.2707 | 39.3594 | 37.6382 | 38.901 | 36.9616 | 39.1476 | 37.2603 | 39.0186 | 36.7586 | 38.152 | 37.7399 | 38.9793 | 36.9485 | 39.6294 | 37.3216 | 39.0515 | 39.7848 | 94.7342 | 94.7166 | 94.1624
2022-09-07 20:13 | 1:49 | 34.598 | 31.8697 | 32.23 | 36.5671 | 36.766 | 34.745 | 37.2869 | 33.9223 | 37.2167 | 35.7831 | 35.9501 | 38.664 | 33.932 | 35.2906 | 35.983 | 34.4271 | 34.8188 | 35.5084 | 35.0815 | 37.3832 | 34.7326 | 31.6411 | 35.5139 | 36.8935 | 34.9742 | 39.3436 | 36.9042 | 35.3164 | 34.7321 | 36.9154 | 34.9178 | 36.0018 | 34.9702 | 36.0303 | 34.972 | 36.5508 | 36.1459 | 36.6395 | 37.7426 | 36.0011 | 37.1449 | 38.3774 | 39.3922 | 37.7821 | 38.9557 | 37.0377 | 39.1332 | 37.3619 | 39.0904 | 36.8391 | 38.2773 | 37.766 | 39.0178 | 36.932 | 39.664 | 37.382 | 39.306 | 39.7836 | 94.7923 | 94.9136 | 94.3067
2022-09-07 20:13 | 1:49 | 34.9817 | 31.8671 | 32.6714 | 36.6812 | 36.7835 | 34.8084 | 37.4089 | 33.99 | 37.271 | 35.831 | 35.9159 | 38.7053 | 34.0628 | 35.3687 | 35.9917 | 34.5299 | 34.9271 | 35.5699 | 35.159 | 37.38 | 34.965 | 31.6851 | 35.7508 | 37.0548 | 35.1065 | 39.3158 | 37.0101 | 35.4812 | 34.9344 | 37.009 | 35.0584 | 36.0082 | 35.1102 | 36.1314 | 35.0957 | 36.6463 | 36.2142 | 36.6616 | 37.8222 | 36.0588 | 37.2515 | 38.3988 | 39.4586 | 37.8897 | 39.0312 | 37.0809 | 39.2311 | 37.4902 | 39.232 | 36.9015 | 38.3231 | 37.8783 | 39.0288 | 37.0489 | 39.6769 | 37.4672 | 39.3676 | 39.7744 | 94.9846 | 95.0474 | 94.415
2022-09-07 20:13 | 1:49 | 35.0822 | 31.887 | 32.9726 | 36.8126 | 36.8502 | 34.9019 | 37.4124 | 34.1401 | 37.3169 | 35.9437 | 35.902 | 38.6931 | 34.0968 | 35.4308 | 35.9981 | 34.5762 | 34.9905 | 35.6508 | 35.2437 | 37.5396 | 35.0219 | 31.7052 | 35.855 | 37.1732 | 35.1611 | 39.4829 | 37.0514 | 35.6619 | 34.9208 | 37.1102 | 35.1738 | 36.154 | 35.1798 | 36.2123 | 35.1497 | 36.6378 | 36.2771 | 36.6958 | 37.8467 | 36.1315 | 37.3023 | 38.4934 | 39.534 | 37.9784 | 39.0943 | 37.1379 | 39.2429 | 37.5494 | 39.2694 | 37.0777 | 38.3711 | 37.9342 | 39.1833 | 37.1012 | 39.7044 | 37.5407 | 39.2696 | 39.8344 | 95.0548 | 95.0548 | 94.4877
2022-09-07 20:14 | 1:50 | 35.1568 | 31.9066 | 33.0862 | 36.9335 | 36.8672 | 34.9971 | 37.5151 | 34.1926 | 37.3196 | 36.0489 | 36.0871 | 38.6076 | 34.173 | 35.4899 | 36.0866 | 34.6098 | 35.067 | 35.707 | 35.2951 | 37.6007 | 35.0422 | 31.7395 | 35.9646 | 37.2603 | 35.2538 | 39.496 | 37.0971 | 35.6542 | 34.9758 | 37.1302 | 35.263 | 36.2099 | 35.2676 | 36.301 | 35.2748 | 36.7468 | 36.3309 | 36.7754 | 37.8903 | 36.2099 | 37.343 | 38.5334 | 39.5627 | 38.045 | 39.2006 | 37.1519 | 39.3005 | 37.6277 | 39.3145 | 37.069 | 38.4656 | 38.0022 | 39.1406 | 37.139 | 39.7218 | 37.6229 | 39.3239 | 39.8575 | 94.9451 | 94.9505 | 94.3216
2022-09-07 20:14 | 1:50 | 35.2899 | 31.9464 | 33.166 | 37.0174 | 36.8979 | 35.0577 | 37.4091 | 34.326 | 37.3603 | 36.0007 | 36.1038 | 38.6435 | 34.2801 | 35.5347 | 36.1741 | 34.6413 | 35.1631 | 35.7724 | 35.3725 | 37.658 | 35.1013 | 31.769 | 36.0415 | 37.2776 | 35.3003 | 39.789 | 37.1449 | 35.6905 | 35.0805 | 37.2542 | 35.3648 | 36.2565 | 35.3577 | 36.3653 | 35.3251 | 36.73 | 36.3428 | 36.8353 | 37.9782 | 36.2642 | 37.4045 | 38.6008 | 39.5977 | 38.1481 | 39.2554 | 37.193 | 39.3965 | 37.7203 | 39.384 | 37.12 | 38.522 | 38.0642 | 39.2255 | 37.1879 | 39.7837 | 37.6968 | 39.4604 | 39.8025 | 94.7288 | 94.749 | 94.1349
2022-09-07 20:14 | 1:50 | 35.3418 | 31.9753 | 33.2315 | 37.1899 | 36.8979 | 35.1626 | 37.4203 | 34.4427 | 37.3603 | 36.0849 | 36.1502 | 38.7187 | 34.3476 | 35.6145 | 36.302 | 34.7366 | 35.2065 | 35.7907 | 35.4242 | 37.7137 | 35.1654 | 31.7933 | 36.1559 | 37.3368 | 35.4199 | 39.7248 | 37.2515 | 35.6495 | 35.1515 | 37.2711 | 35.4315 | 36.1821 | 35.4268 | 36.4887 | 35.4433 | 36.7493 | 36.3647 | 36.8798 | 37.932 | 36.3242 | 37.3685 | 38.6709 | 39.6544 | 38.2498 | 39.2824 | 37.3031 | 39.402 | 37.7819 | 39.4861 | 37.1987 | 38.6038 | 38.1032 | 39.1521 | 37.2672 | 39.7491 | 37.7521 | 39.524 | 39.8433 | 94.4502 | 94.5553 | 93.9608
2022-09-07 20:14 | 1:50 | 35.4728 | 32.0225 | 33.4602 | 37.1434 | 36.9155 | 35.2188 | 37.4772 | 34.3764 | 37.3916 | 36.0666 | 36.2062 | 38.6883 | 34.4626 | 35.6943 | 36.3968 | 34.7828 | 35.325 | 35.8771 | 35.4802 | 37.8401 | 35.2549 | 31.8187 | 36.2672 | 37.471 | 35.4922 | 39.7628 | 37.3023 | 35.7491 | 35.2513 | 37.257 | 35.5245 | 36.2917 | 35.502 | 36.5129 | 35.5024 | 36.8909 | 36.4937 | 36.9382 | 37.9646 | 36.4067 | 37.4626 | 38.6959 | 39.7288 | 38.3208 | 39.3761 | 37.3118 | 39.4158 | 37.8483 | 39.478 | 37.2934 | 38.6245 | 38.2118 | 39.2544 | 37.2525 | 39.8556 | 37.8195 | 39.4059 | 39.9521 | 94.2034 | 94.3546 | 93.8483
2022-09-07 20:14 | 1:50 | 35.6481 | 32.0775 | 33.6571 | 37.2073 | 36.9923 | 35.279 | 37.5542 | 34.4795 | 37.4454 | 36.2777 | 36.3013 | 38.6964 | 34.5639 | 35.7759 | 36.4694 | 34.8718 | 35.4815 | 35.9453 | 35.5593 | 37.8662 | 35.4282 | 31.8417 | 36.4452 | 37.4447 | 35.6134 | 39.7231 | 37.343 | 35.6771 | 35.3201 | 37.303 | 35.6233 | 36.2646 | 35.6185 | 36.565 | 35.5887 | 36.9424 | 36.5448 | 37.0092 | 38.0047 | 36.4577 | 37.5954 | 38.7319 | 39.8053 | 38.3844 | 39.3308 | 37.3896 | 39.4352 | 37.9459 | 39.6905 | 37.3534 | 38.6827 | 38.2932 | 39.2105 | 37.4418 | 39.8624 | 37.9165 | 39.6104 | 39.9477 | 94.0388 | 94.1604 | 93.7435
2022-09-07 20:14 | 1:50 | 35.6042 | 32.1459 | 33.8271 | 37.4145 | 37.0384 | 35.3691 | 37.6366 | 34.6357 | 37.4865 | 36.3266 | 36.3268 | 38.714 | 34.763 | 35.9152 | 36.4628 | 34.9176 | 35.5208 | 36.0203 | 35.6423 | 37.9208 | 35.7058 | 31.8629 | 36.607 | 37.5556 | 35.6901 | 39.717 | 37.4045 | 35.8067 | 35.4802 | 37.3264 | 35.7327 | 36.4277 | 35.7294 | 36.6623 | 35.6724 | 36.923 | 36.5881 | 37.0643 | 38.0262 | 36.5091 | 37.651 | 38.7912 | 39.8396 | 38.4863 | 39.4049 | 37.4213 | 39.4965 | 38.0423 | 39.6489 | 37.3832 | 38.8271 | 38.3659 | 39.2764 | 37.4793 | 39.8872 | 37.9696 | 39.5846 | 40.0017 | 93.9707 | 94.1074 | 93.7078
2022-09-07 20:15 | 1:50 | 34.6175 | 32.1997 | 34.1405 | 37.5747 | 37.0532 | 35.506 | 37.6322 | 34.7622 | 37.5229 | 36.4127 | 36.3975 | 38.74 | 34.9467 | 36.034 | 36.5445 | 35.0378 | 35.6314 | 36.1343 | 35.7552 | 38.0482 | 36.1478 | 32.0067 | 36.7871 | 37.6949 | 35.7364 | 39.7998 | 37.3685 | 35.8722 | 35.6007 | 37.4208 | 35.8602 | 36.4665 | 35.8263 | 36.7675 | 35.7726 | 36.998 | 36.6634 | 37.1609 | 38.0694 | 36.6132 | 37.686 | 38.827 | 39.8648 | 38.5486 | 39.4721 | 37.4953 | 39.516 | 38.1022 | 39.7435 | 37.4933 | 38.8683 | 38.4156 | 39.3672 | 37.6047 | 39.941 | 38.0605 | 39.6713 | 40.0503 | 93.8889 | 93.956 | 93.6147
2022-09-07 20:15 | 1:51 | 34.1224 | 32.2828 | 34.4792 | 37.6075 | 37.1053 | 35.6026 | 37.7231 | 34.9487 | 37.5682 | 36.4374 | 36.6411 | 38.8275 | 35.0648 | 36.1311 | 36.6669 | 35.1352 | 35.7474 | 36.2549 | 35.8436 | 38.0545 | 36.6326 | 32.6354 | 37.0382 | 37.7809 | 35.8411 | 39.8243 | 37.4626 | 35.9655 | 35.6232 | 37.5635 | 35.997 | 36.5329 | 35.9618 | 36.8531 | 35.9287 | 37.0937 | 36.7348 | 37.2184 | 38.1896 | 36.7026 | 37.7936 | 38.9331 | 39.874 | 38.6417 | 39.5187 | 37.5326 | 39.602 | 38.2057 | 39.8047 | 37.5748 | 38.8932 | 38.4791 | 39.4709 | 37.673 | 39.9611 | 38.1238 | 39.7244 | 40.1281 | 93.8368 | 93.992 | 93.67
2022-09-07 20:15 | 1:51 | 33.9461 | 32.4048 | 34.8059 | 37.8036 | 37.1576 | 35.8015 | 37.7843 | 35.0879 | 37.614 | 36.5798 | 36.7076 | 38.944 | 35.2349 | 36.2974 | 36.8479 | 35.1957 | 35.8803 | 36.3428 | 35.925 | 38.1772 | 37.0661 | 33.7855 | 37.281 | 37.8769 | 35.9199 | 39.8988 | 37.5954 | 36.1303 | 35.7314 | 37.6473 | 36.1038 | 36.5819 | 36.0629 | 36.9408 | 36.0126 | 37.1258 | 36.8068 | 37.3038 | 38.2391 | 36.7773 | 37.8983 | 38.9965 | 39.9439 | 38.7495 | 39.6144 | 37.6365 | 39.5816 | 38.286 | 39.8462 | 37.6195 | 38.944 | 38.5059 | 39.5022 | 37.7603 | 39.9432 | 38.2142 | 39.7641 | 40.1742 | 93.7682 | 93.8776 | 93.5221
2022-09-07 20:15 | 1:51 | 33.9761 | 32.5249 | 35.1219 | 37.9516 | 37.2138 | 35.8765 | 37.9223 | 35.1722 | 37.6834 | 36.6646 | 36.8125 | 38.9346 | 35.3684 | 36.3093 | 37.0426 | 35.2782 | 36.0054 | 36.4391 | 36.0093 | 38.3514 | 37.4681 | 34.6415 | 37.5253 | 37.9924 | 36.06 | 40.0036 | 37.651 | 36.1926 | 35.8259 | 37.6736 | 36.2437 | 36.5851 | 36.167 | 37.0378 | 36.1126 | 37.1969 | 36.8757 | 37.4129 | 38.2613 | 36.8896 | 37.9451 | 39.0939 | 40.0005 | 38.8329 | 39.7319 | 37.6889 | 39.6667 | 38.3549 | 39.8656 | 37.6194 | 39.0051 | 38.5842 | 39.6464 | 37.7706 | 39.9878 | 38.2701 | 39.9984 | 40.2448 | 93.7081 | 93.8066 | 93.574
2022-09-07 20:15 | 1:51 | 34.0691 | 32.6626 | 35.4157 | 38.1209 | 37.2844 | 35.9965 | 37.8603 | 35.2943 | 37.7274 | 36.814 | 36.9738 | 38.9652 | 35.4447 | 36.4026 | 37.1061 | 35.3726 | 36.1117 | 36.555 | 36.1086 | 38.3414 | 37.7581 | 35.7019 | 37.7458 | 38.0594 | 36.1831 | 40.0309 | 37.686 | 36.2226 | 35.8198 | 37.7525 | 36.3466 | 36.7463 | 36.3012 | 37.1455 | 36.2427 | 37.2917 | 36.9717 | 37.4805 | 38.2756 | 36.9517 | 37.977 | 39.1397 | 40.0397 | 38.9112 | 39.6972 | 37.7462 | 39.7773 | 38.4442 | 39.8944 | 37.7607 | 39.087 | 38.6601 | 39.636 | 37.8829 | 40.0495 | 38.3605 | 39.9504 | 40.2103 | 93.6011 | 93.709 | 93.504
2022-09-07 20:15 | 1:51 | 34.2179 | 32.7595 | 35.6983 | 38.1635 | 37.3483 | 36.1522 | 37.9027 | 35.4581 | 37.7816 | 36.8388 | 37.0672 | 39.0204 | 35.5673 | 36.531 | 37.0391 | 35.4392 | 36.2149 | 36.6716 | 36.2058 | 38.3889 | 37.9896 | 36.5152 | 37.9404 | 38.171 | 36.2964 | 40.032 | 37.7936 | 36.3991 | 36.0144 | 37.9087 | 36.444 | 36.9029 | 36.435 | 37.2575 | 36.332 | 37.3942 | 37.0464 | 37.5644 | 38.3274 | 37.0449 | 38.0373 | 39.2462 | 40.1061 | 38.9892 | 39.7754 | 37.8166 | 39.7847 | 38.5419 | 39.9856 | 37.835 | 39.154 | 38.716 | 39.6465 | 37.9253 | 40.1216 | 38.4297 | 39.977 | 40.2872 | 93.5869 | 93.6742 | 93.5571
2022-09-07 20:16 | 1:51 | 34.2874 | 33.0247 | 35.9112 | 38.3388 | 37.4086 | 36.3065 | 37.9261 | 35.5994 | 37.8521 | 36.9381 | 37.1193 | 39.118 | 35.7014 | 36.6009 | 37.1574 | 35.57 | 36.3479 | 36.7569 | 36.3079 | 38.5017 | 38.2086 | 37.0045 | 38.1109 | 38.2315 | 36.3869 | 40.1982 | 37.8983 | 36.4575 | 36.0792 | 37.962 | 36.5896 | 36.9567 | 36.5236 | 37.3989 | 36.4406 | 37.4658 | 37.1206 | 37.6759 | 38.3862 | 37.1133 | 38.1592 | 39.2472 | 40.1595 | 39.0714 | 39.8807 | 37.8915 | 39.8794 | 38.6035 | 40.0546 | 37.894 | 39.2059 | 38.8211 | 39.6752 | 37.9645 | 40.1652 | 38.4915 | 40.0187 | 40.3543 | 93.5744 | 93.6244 | 93.4414
2022-09-07 20:16 | 1:52 | 34.3959 | 33.3617 | 36.1349 | 38.5452 | 37.4663 | 36.4083 | 38.0245 | 35.7565 | 37.8956 | 37.0314 | 37.2453 | 39.0997 | 35.8512 | 36.6909 | 37.1555 | 35.6542 | 36.472 | 36.8635 | 36.4074 | 38.5673 | 38.448 | 37.3287 | 38.2812 | 38.332 | 36.4693 | 40.2287 | 37.9451 | 36.6215 | 36.2665 | 38.1151 | 36.7408 | 36.9358 | 36.636 | 37.4599 | 36.5767 | 37.5514 | 37.2036 | 37.744 | 38.4754 | 37.2113 | 38.2161 | 39.3121 | 40.1493 | 39.1575 | 39.9059 | 37.932 | 39.8926 | 38.6985 | 40.0784 | 37.9643 | 39.2887 | 38.8629 | 39.7606 | 38.0546 | 40.1981 | 38.5707 | 40.0857 | 40.3371 | 93.4418 | 93.5823 | 93.4194
2022-09-07 20:16 | 1:52 | 34.5789 | 33.8391 | 36.3323 | 38.6122 | 37.4988 | 36.4998 | 38.1277 | 35.9358 | 37.9856 | 37.1971 | 37.3343 | 39.1324 | 36.0522 | 36.8616 | 37.3777 | 35.8135 | 36.5662 | 36.9921 | 36.5074 | 38.7149 | 38.5787 | 37.5729 | 38.4168 | 38.4838 | 36.5795 | 40.2059 | 37.977 | 36.6439 | 36.3877 | 38.1346 | 36.84 | 37.1039 | 36.7498 | 37.559 | 36.6794 | 37.5908 | 37.2947 | 37.8182 | 38.5675 | 37.3091 | 38.2348 | 39.3931 | 40.2235 | 39.2483 | 40.0129 | 37.9772 | 39.9821 | 38.7931 | 40.1984 | 38.0334 | 39.3191 | 38.9586 | 39.8537 | 38.1278 | 40.2193 | 38.6639 | 40.1334 | 40.4487 | 93.4164 | 93.5143 | 93.3524
2022-09-07 20:16 | 1:52 | 34.8113 | 34.4797 | 36.5562 | 38.69 | 37.5929 | 36.6374 | 38.211 | 36.0476 | 38.0265 | 37.265 | 37.4121 | 39.2301 | 36.1748 | 36.9004 | 37.422 | 35.8849 | 36.6985 | 37.0847 | 36.6293 | 38.7994 | 38.7277 | 37.7777 | 38.5664 | 38.6334 | 36.7668 | 40.3489 | 38.0373 | 36.7481 | 36.4258 | 38.2962 | 36.9423 | 37.1171 | 36.8739 | 37.6495 | 36.7959 | 37.6858 | 37.3716 | 37.9238 | 38.5725 | 37.3905 | 38.3448 | 39.4453 | 40.2742 | 39.3439 | 40.0455 | 38.0633 | 40.0002 | 38.8636 | 40.1936 | 38.1373 | 39.3943 | 39.0228 | 39.9554 | 38.2485 | 40.2661 | 38.7343 | 40.1136 | 40.4514 | 93.2577 | 93.4139 | 93.303
2022-09-07 20:16 | 1:52 | 35.0203 | 34.8875 | 36.718 | 38.7419 | 37.6623 | 36.7469 | 38.2564 | 36.2474 | 38.0944 | 37.3834 | 37.5976 | 39.2456 | 36.2823 | 37.0642 | 37.5228 | 35.9171 | 36.7927 | 37.2027 | 36.7326 | 38.8242 | 38.8751 | 38.0182 | 38.7057 | 38.6725 | 36.8398 | 40.4502 | 38.1592 | 36.7994 | 36.601 | 38.3551 | 37.0512 | 37.2315 | 36.9716 | 37.7267 | 36.907 | 37.791 | 37.4577 | 38.0051 | 38.6434 | 37.481 | 38.4648 | 39.5276 | 40.3126 | 39.4249 | 40.1108 | 38.1449 | 40.078 | 38.9562 | 40.3352 | 38.1863 | 39.4781 | 39.0806 | 39.8815 | 38.3296 | 40.3037 | 38.8075 | 40.262 | 40.6652 | 93.2241 | 93.4035 | 93.3714
2022-09-07 20:16 | 1:52 | 35.2018 | 35.2304 | 36.9118 | 38.9133 | 37.7101 | 36.8597 | 38.3302 | 36.327 | 38.1616 | 37.4322 | 37.6657 | 39.2746 | 36.4298 | 37.1419 | 37.5435 | 36.0718 | 36.9182 | 37.2814 | 36.8521 | 38.956 | 39.0079 | 38.1598 | 38.8355 | 38.727 | 36.8796 | 40.5591 | 38.2161 | 36.9045 | 36.6282 | 38.3424 | 37.161 | 37.3324 | 37.081 | 37.8326 | 37.0248 | 37.8743 | 37.5521 | 38.1013 | 38.72 | 37.5939 | 38.5106 | 39.6175 | 40.3782 | 39.5064 | 40.1626 | 38.2087 | 40.1202 | 39.0332 | 40.3765 | 38.2837 | 39.5289 | 39.1551 | 40.0517 | 38.4465 | 40.4319 | 38.8744 | 40.1888 | 40.6537 | 93.1435 | 93.2402 | 93.2215
2022-09-07 20:17 | 1:52 | 35.4493 | 35.5493 | 37.0533 | 38.9656 | 37.813 | 36.9377 | 38.3997 | 36.4643 | 38.2311 | 37.5593 | 37.7874 | 39.3963 | 36.5662 | 37.3066 | 37.7344 | 36.1661 | 37.0363 | 37.3959 | 36.978 | 38.9646 | 39.1101 | 38.2836 | 38.9473 | 38.845 | 37.0598 | 40.5297 | 38.2348 | 36.9642 | 36.8293 | 38.4109 | 37.2706 | 37.3551 | 37.2046 | 37.9333 | 37.1628 | 37.9213 | 37.6425 | 38.2051 | 38.7959 | 37.7067 | 38.5594 | 39.6442 | 40.4171 | 39.5861 | 40.2192 | 38.2871 | 40.1863 | 39.1172 | 40.4138 | 38.3666 | 39.6093 | 39.232 | 40.1072 | 38.5802 | 40.4385 | 38.9821 | 40.2696 | 40.608 | 93.0636 | 93.1299 | 93.1657
2022-09-07 20:17 | 1:53 | 35.798 | 35.8491 | 37.1984 | 39.1068 | 37.8806 | 37.117 | 38.4217 | 36.6045 | 38.2785 | 37.6396 | 37.9779 | 39.4685 | 36.6476 | 37.3608 | 37.861 | 36.3073 | 37.133 | 37.474 | 37.0334 | 39.0147 | 39.2155 | 38.3033 | 39.0691 | 38.9687 | 37.1335 | 40.5642 | 38.3448 | 37.1115 | 37.0318 | 38.5079 | 37.3729 | 37.4395 | 37.3033 | 38.0408 | 37.2339 | 37.9709 | 37.7223 | 38.2539 | 38.8234 | 37.7717 | 38.6622 | 39.7454 | 40.472 | 39.6635 | 40.3332 | 38.3775 | 40.2335 | 39.1984 | 40.5498 | 38.4166 | 39.657 | 39.3037 | 40.233 | 38.5707 | 40.4364 | 39.032 | 40.4017 | 40.6509 | 93.0469 | 93.0235 | 93.1258
2022-09-07 20:17 | 1:53 | 36.1487 | 36.153 | 37.3407 | 39.2316 | 37.9681 | 37.2183 | 38.541 | 36.716 | 38.358 | 37.7431 | 38.0663 | 39.5174 | 36.8016 | 37.4906 | 37.928 | 36.4011 | 37.2596 | 37.5874 | 37.1863 | 39.1488 | 39.3216 | 38.452 | 39.1752 | 39.0535 | 37.2708 | 40.6228 | 38.4648 | 37.1631 | 37.1007 | 38.6586 | 37.4809 | 37.5443 | 37.4179 | 38.1076 | 37.3896 | 38.0608 | 37.7784 | 38.3318 | 38.8525 | 37.8502 | 38.7548 | 39.8265 | 40.532 | 39.7489 | 40.4118 | 38.4583 | 40.325 | 39.2886 | 40.5075 | 38.5014 | 39.7205 | 39.375 | 40.2585 | 38.6508 | 40.4837 | 39.1173 | 40.43 | 40.6773 | 92.8933 | 92.9188 | 93.0172
2022-09-07 20:17 | 1:53 | 36.4568 | 36.4707 | 37.4758 | 39.3058 | 38.0492 | 37.303 | 38.5926 | 36.8868 | 38.4153 | 37.7754 | 38.1386 | 39.5915 | 36.9636 | 37.5423 | 37.9656 | 36.4848 | 37.3363 | 37.657 | 37.2282 | 39.1677 | 39.4295 | 38.5854 | 39.2772 | 39.0857 | 37.3604 | 40.6882 | 38.5106 | 37.198 | 37.1819 | 38.7296 | 37.6037 | 37.6991 | 37.5466 | 38.1887 | 37.4496 | 38.1283 | 37.8895 | 38.401 | 38.9296 | 37.9549 | 38.8257 | 39.904 | 40.5859 | 39.8456 | 40.4819 | 38.4772 | 40.3412 | 39.3852 | 40.6664 | 38.5892 | 39.8436 | 39.4482 | 40.2436 | 38.7488 | 40.5062 | 39.2028 | 40.5923 | 40.7047 | 92.7556 | 92.8056 | 92.9845
2022-09-07 20:17 | 1:53 | 36.7328 | 36.7397 | 37.6453 | 39.4849 | 38.1205 | 37.4863 | 38.7063 | 36.9926 | 38.4986 | 37.8716 | 38.2818 | 39.5665 | 37.0942 | 37.7459 | 38.1753 | 36.5988 | 37.5127 | 37.756 | 37.3414 | 39.3445 | 39.5479 | 38.6737 | 39.3883 | 39.2054 | 37.4515 | 40.8772 | 38.5594 | 37.3605 | 37.2369 | 38.6876 | 37.7024 | 37.7035 | 37.6327 | 38.2546 | 37.5824 | 38.2342 | 38.0134 | 38.4943 | 39.0011 | 38.0612 | 38.912 | 39.9604 | 40.6284 | 39.9259 | 40.4892 | 38.5757 | 40.3983 | 39.4555 | 40.6821 | 38.6921 | 39.8931 | 39.5174 | 40.2203 | 38.8064 | 40.5716 | 39.2741 | 40.5388 | 40.8079 | 92.6781 | 92.7072 | 92.8266
2022-09-07 20:17 | 1:53 | 37.0695 | 36.9905 | 37.7338 | 39.5188 | 38.1899 | 37.6382 | 38.7652 | 37.1067 | 38.576 | 38.0795 | 38.3716 | 39.5253 | 37.2033 | 37.7513 | 38.1371 | 36.6685 | 37.5919 | 37.8837 | 37.448 | 39.4948 | 39.6631 | 38.7853 | 39.4958 | 39.364 | 37.6847 | 40.846 | 38.6622 | 37.4703 | 37.3158 | 38.8814 | 37.7773 | 37.8265 | 37.7565 | 38.3681 | 37.728 | 38.262 | 38.0828 | 38.5716 | 39.0317 | 38.144 | 38.7484 | 40.0302 | 40.685 | 39.9691 | 40.5534 | 38.6879 | 40.4447 | 39.5351 | 40.7332 | 38.7502 | 39.94 | 39.612 | 40.3812 | 38.9019 | 40.6444 | 39.3455 | 40.5412 | 40.8993 | 92.5184 | 92.5283 | 92.8018
2022-09-07 20:18 | 1:53 | 37.3159 | 37.2475 | 37.9015 | 39.6948 | 38.2647 | 37.7292 | 38.8561 | 37.2931 | 38.6382 | 38.1532 | 38.5125 | 39.6056 | 37.309 | 37.948 | 38.2937 | 36.7816 | 37.7045 | 37.9372 | 37.5624 | 39.5331 | 39.7809 | 38.8849 | 39.5982 | 39.3728 | 37.7052 | 40.9126 | 38.7548 | 37.5768 | 37.5169 | 38.8564 | 37.8861 | 37.9016 | 37.8693 | 38.4364 | 37.8258 | 38.4171 | 38.1276 | 38.6757 | 39.1264 | 38.224 | 38.7463 | 40.0807 | 40.7621 | 40.0591 | 40.641 | 38.7061 | 40.5635 | 39.6101 | 40.8092 | 38.8177 | 40.0278 | 39.6764 | 40.4616 | 38.9701 | 40.7314 | 39.4113 | 40.616 | 40.9401 | 92.2857 | 92.3553 | 92.6212
2022-09-07 20:18 | 1:54 | 37.393 | 37.4577 | 38.0323 | 39.7809 | 38.3674 | 37.8055 | 38.9376 | 37.4126 | 38.7268 | 38.2326 | 38.5753 | 39.6375 | 37.4762 | 38.04 | 38.5598 | 36.8681 | 37.8181 | 38.0844 | 37.6403 | 39.5664 | 39.9004 | 39.005 | 39.7019 | 39.4397 | 37.8168 | 40.9286 | 38.8257 | 37.6493 | 37.6009 | 38.9505 | 38.0045 | 37.9148 | 37.9816 | 38.523 | 37.923 | 38.4559 | 38.2247 | 38.7659 | 39.2101 | 38.3012 | 38.7882 | 40.1402 | 40.7827 | 40.1396 | 40.6645 | 38.7726 | 40.6042 | 39.677 | 40.8662 | 38.9045 | 40.0827 | 39.7247 | 40.471 | 39.0444 | 40.739 | 39.5002 | 40.69 | 41.0061 | 92.1469 | 92.2469 | 92.5434
2022-09-07 20:18 | 1:54 | 36.872 | 36.9224 | 37.6128 | 39.8199 | 38.4626 | 37.8726 | 38.9813 | 37.479 | 38.7779 | 38.2944 | 38.6628 | 39.7499 | 37.5109 | 38.0802 | 38.4877 | 37.0041 | 37.8957 | 38.13 | 37.6983 | 39.6366 | 36.5073 | 37.223 | 38.7359 | 39.5425 | 37.8133 | 40.8772 | 38.912 | 37.7498 | 37.5835 | 39.0093 | 37.7619 | 38.0174 | 37.9477 | 38.5664 | 37.94 | 38.5116 | 38.2951 | 38.7671 | 39.2637 | 38.3599 | 38.8793 | 40.173 | 40.7357 | 40.0595 | 40.6737 | 38.8115 | 40.6052 | 39.5671 | 40.8104 | 38.9237 | 39.9822 | 39.7184 | 40.4966 | 39.0775 | 40.7923 | 39.4213 | 40.7124 | 41.0333 | 91.9683 | 92.0844 | 92.4794
2022-09-07 20:18 | 1:54 | 33.4002 | 28.4392 | 34.6443 | 39.5793 | 38.4141 | 37.6915 | 38.8492 | 37.1686 | 38.8064 | 38.1264 | 38.4322 | 39.8308 | 37.1338 | 37.7667 | 38.3508 | 36.9368 | 37.7408 | 37.7783 | 37.4894 | 39.4636 | 34.2888 | 31.9147 | 37.7766 | 39.4126 | 37.6454 | 40.7644 | 38.7484 | 37.5727 | 37.4545 | 38.6482 | 37.4266 | 37.9734 | 37.6456 | 38.2844 | 37.8482 | 38.4283 | 38.1766 | 38.5787 | 39.1793 | 38.2869 | 38.9458 | 40.0172 | 40.6008 | 39.7886 | 40.4367 | 38.8098 | 40.4877 | 39.3222 | 40.6028 | 38.7053 | 39.7602 | 39.5657 | 40.2965 | 38.9548 | 40.7361 | 39.2387 | 40.6751 | 40.9304 | 91.8497 | 91.9138 | 92.3699
2022-09-07 20:18 | 1:54 | 33.6253 | 23.9462 | 35.0447 | 39.0818 | 38.4002 | 37.5701 | 38.8799 | 37.0029 | 38.7906 | 38.0466 | 38.2399 | 39.7684 | 37.0107 | 37.7073 | 38.2741 | 36.8822 | 37.581 | 37.6846 | 37.4398 | 39.2577 | 34.6505 | 31.7227 | 38.0144 | 39.334 | 37.6797 | 40.8503 | 38.7463 | 37.5603 | 37.4179 | 38.7448 | 37.5316 | 38.0104 | 37.6372 | 38.2119 | 37.8461 | 38.3399 | 38.1729 | 38.5201 | 39.1744 | 38.2669 | 38.9108 | 40.0487 | 40.6564 | 39.7562 | 40.4388 | 38.7656 | 40.5987 | 39.3718 | 40.6594 | 38.7588 | 39.818 | 39.5865 | 40.3592 | 38.9061 | 40.7777 | 39.3073 | 40.6833 | 41.0036 | 91.7573 | 91.7624 | 92.3111
2022-09-07 20:18 | 1:54 | 34.0295 | 27.8448 | 36.2119 | 39.295 | 38.4832 | 37.677 | 38.8896 | 37.1767 | 38.8236 | 38.1262 | 38.3703 | 39.8669 | 37.183 | 37.7691 | 38.5261 | 36.9567 | 37.7055 | 37.8372 | 37.5443 | 39.4255 | 35.2768 | 32.5941 | 38.306 | 39.2981 | 37.7933 | 40.9558 | 38.7882 | 37.7796 | 37.5377 | 38.8997 | 37.6673 | 38.0778 | 37.7704 | 38.3146 | 37.924 | 38.4376 | 38.2216 | 38.6038 | 39.1964 | 38.2925 | 38.5055 | 40.1367 | 40.7303 | 39.9194 | 40.5325 | 38.8379 | 40.635 | 39.5104 | 40.7299 | 38.8449 | 39.9355 | 39.6654 | 40.3947 | 39.0474 | 40.7708 | 39.4537 | 40.6961 | 40.9812 | 91.6934 | 91.7468 | 92.2974
2022-09-07 20:19 | 1:55 | 34.6819 | 31.1886 | 37.0173 | 39.3871 | 38.5679 | 37.8691 | 38.9874 | 37.3985 | 38.9302 | 38.2554 | 38.6309 | 39.9948 | 37.398 | 37.9884 | 38.5723 | 37.0655 | 37.818 | 38.0356 | 37.68 | 39.606 | 35.8704 | 33.7212 | 38.5726 | 39.432 | 37.8855 | 41.1209 | 38.8793 | 37.7667 | 37.6599 | 38.9428 | 37.7854 | 38.2273 | 37.9168 | 38.4561 | 38.0186 | 38.5149 | 38.3583 | 38.7462 | 39.2377 | 38.364 | 38.2557 | 40.2465 | 40.8028 | 40.0282 | 40.6721 | 38.9285 | 40.7398 | 39.6277 | 40.7839 | 38.9176 | 40.0234 | 39.763 | 40.5655 | 39.1499 | 40.82 | 39.5607 | 40.8252 | 41.1292 | 91.7242 | 91.7694 | 92.3581
2022-09-07 20:19 | 1:55 | 35.3469 | 33.5912 | 37.5113 | 39.7037 | 38.6577 | 38.0284 | 39.0357 | 37.5683 | 38.9993 | 38.3988 | 38.801 | 40.122 | 37.5717 | 38.1253 | 38.7186 | 37.1917 | 37.9572 | 38.2142 | 37.8095 | 39.6929 | 36.4076 | 34.7846 | 38.7737 | 39.5942 | 37.9734 | 41.1861 | 38.9458 | 38 | 37.7919 | 39.0689 | 37.923 | 38.2796 | 38.0389 | 38.5718 | 38.0682 | 38.5973 | 38.3808 | 38.8552 | 39.346 | 38.442 | 38.2447 | 40.3412 | 40.8814 | 40.1394 | 40.7359 | 39.0044 | 40.7854 | 39.7274 | 40.8517 | 39.0186 | 40.1118 | 39.8624 | 40.6253 | 39.2485 | 40.9051 | 39.6416 | 40.8245 | 41.1716 | 91.7415 | 91.8366 | 92.3486
2022-09-07 20:19 | 1:55 | 35.9997 | 35.3201 | 37.9253 | 39.8732 | 38.7378 | 38.138 | 39.1366 | 37.7065 | 39.0899 | 38.535 | 38.9769 | 40.1322 | 37.6813 | 38.285 | 38.8338 | 37.2629 | 38.0688 | 38.2929 | 37.9179 | 39.8239 | 26.4679 | 28.7995 | 34.9742 | 39.6039 | 37.8362 | 41.0569 | 38.9108 | 37.9494 | 37.7716 | 38.8916 | 36.8312 | 38.3523 | 37.9608 | 38.5486 | 37.6717 | 38.6377 | 38.4265 | 38.9329 | 39.3597 | 38.4121 | 38.2041 | 40.1206 | 40.5202 | 39.5448 | 40.3699 | 38.959 | 40.6731 | 39.0114 | 40.6372 | 38.7811 | 39.7233 | 39.5183 | 40.3939 | 39.1367 | 40.7871 | 39.1146 | 40.7524 | 41.1172 | 91.9016 | 91.9802 | 92.431
2022-09-07 20:19 | 1:55 | 36.1421 | 28.9996 | 35.6739 | 39.7027 | 38.8285 | 37.9909 | 39.2062 | 37.5454 | 39.1604 | 38.4077 | 38.9606 | 40.234 | 37.4345 | 37.9296 | 38.6122 | 37.273 | 37.9996 | 38.0092 | 37.7489 | 39.6101 | 25.4176 | 27.2023 | 32.5075 | 39.2177 | 37.3318 | 40.2406 | 38.5055 | 37.6739 | 37.2913 | 38.4583 | 35.9809 | 38.2139 | 37.525 | 38.0513 | 37.304 | 38.3221 | 38.1972 | 38.4386 | 39.2079 | 38.1357 | 38.2096 | 39.6376 | 40.2323 | 38.9079 | 39.8601 | 38.7233 | 40.3025 | 38.4072 | 40.1254 | 38.304 | 39.7931 | 39.1562 | 40.1001 | 38.8581 | 40.5743 | 38.7534 | 40.2292 | 41.0969 | 91.984 | 92.0325 | 92.5316
2022-09-07 20:19 | 1:55 | 33.7241 | 27.1788 | 34.154 | 39.114 | 38.81 | 37.697 | 39.1311 | 37.1894 | 39.1054 | 38.1261 | 38.646 | 40.1227 | 37.0405 | 37.6855 | 38.4907 | 37.1009 | 37.7418 | 37.7312 | 37.5635 | 39.2651 | 24.8487 | 26.263 | 31.5602 | 38.8339 | 37.1165 | 39.9843 | 38.2557 | 37.5402 | 37.0011 | 38.2968 | 35.5595 | 38.0415 | 37.3153 | 37.7327 | 36.9568 | 38.1177 | 38.1168 | 38.2844 | 38.9845 | 37.9708 | 38.1502 | 39.4268 | 40.0946 | 38.5103 | 39.6611 | 38.5962 | 40.121 | 38.1159 | 39.8507 | 38.0475 | 39.3369 | 39.0235 | 40.0245 | 38.5447 | 40.5168 | 38.6376 | 39.9545 | 40.94 | 92.0768 | 92.1706 | 92.5613
2022-09-07 20:19 | 1:55 | 33.1535 | 27.0732 | 33.8309 | 38.7679 | 38.8303 | 37.4863 | 39.0644 | 37.0875 | 39.1313 | 38.0238 | 38.6224 | 40.1143 | 36.9314 | 37.6626 | 38.366 | 37.0429 | 37.637 | 37.6802 | 37.474 | 39.336 | 25.8162 | 26.0401 | 31.3642 | 38.6222 | 37.0143 | 39.6773 | 38.2447 | 37.5072 | 36.8147 | 38.0999 | 35.3913 | 38.1444 | 37.2048 | 37.6068 | 36.8283 | 38.0341 | 37.9757 | 38.1571 | 38.9534 | 37.8853 | 38.1874 | 39.404 | 39.968 | 38.1718 | 39.4586 | 38.5015 | 40.0412 | 38.0032 | 39.6247 | 37.951 | 39.184 | 38.9164 | 39.9774 | 38.5671 | 40.455 | 38.5362 | 40.0998 | 40.8004 | 92.2137 | 92.3242 | 92.6176
2022-09-07 20:20 | 1:55 | 32.8232 | 27.4635 | 33.6621 | 38.7066 | 38.8432 | 37.4522 | 39.1395 | 36.9997 | 39.1535 | 38.0135 | 38.5677 | 40.113 | 36.8896 | 37.6215 | 38.3469 | 37.0227 | 37.5808 | 37.6071 | 37.427 | 39.2191 | 26.943 | 26.0671 | 31.8365 | 38.4874 | 36.973 | 39.581 | 38.2041 | 37.4733 | 36.8629 | 38.182 | 35.456 | 38.1002 | 37.1872 | 37.5514 | 36.7339 | 38.02 | 37.8911 | 38.1276 | 38.9893 | 37.7933 | 38.0556 | 39.3493 | 40.0244 | 38.2358 | 39.4812 | 38.518 | 40.1002 | 37.9626 | 39.6739 | 37.9462 | 39.2532 | 38.8743 | 39.8762 | 38.5579 | 40.2382 | 38.4834 | 40.039 | 40.7544 | 92.2642 | 92.3854 | 92.6527
2022-09-07 20:20 | 1:56 | 32.1779 | 27.4372 | 32.9988 | 38.5516 | 38.8598 | 37.3607 | 39.0854 | 36.918 | 39.1573 | 37.8727 | 38.5533 | 40.1088 | 36.825 | 37.582 | 38.4755 | 36.9369 | 37.5425 | 37.5488 | 37.3466 | 39.1131 | 27.9822 | 26.0207 | 32.199 | 38.4566 | 36.9372 | 39.6296 | 38.2096 | 37.535 | 36.8338 | 38.1648 | 35.3646 | 38.202 | 37.1417 | 37.4528 | 36.6739 | 38.0255 | 37.9359 | 38.1081 | 38.9103 | 37.8371 | 37.9246 | 39.3727 | 39.9985 | 38.2632 | 39.4871 | 38.504 | 40.1688 | 37.9664 | 39.6882 | 37.9614 | 39.0419 | 38.815 | 39.9838 | 38.5136 | 40.3876 | 38.4846 | 39.8848 | 40.7466 | 92.3501 | 92.4653 | 92.6612
2022-09-07 20:20 | 1:56 | 31.5708 | 27.5822 | 32.3721 | 38.2516 | 38.8926 | 37.3174 | 39.1108 | 36.8033 | 39.1571 | 37.7152 | 38.3321 | 40.1732 | 36.6002 | 37.5138 | 38.2567 | 36.938 | 37.3985 | 37.4761 | 37.3419 | 39.0569 | 28.5661 | 25.972 | 32.3016 | 38.4708 | 36.868 | 39.6851 | 38.1502 | 37.5244 | 36.8503 | 38.0542 | 35.2477 | 38.0844 | 37.1103 | 37.4505 | 36.6038 | 38.0398 | 37.9327 | 38.0836 | 38.9708 | 37.7923 | 37.8638 | 39.3859 | 40.0166 | 38.2238 | 39.5027 | 38.5192 | 40.2371 | 37.957 | 39.7416 | 37.9673 | 39.1192 | 38.8291 | 40.0166 | 38.5947 | 40.5038 | 38.4977 | 39.7425 | 40.8936 | 92.4863 | 92.5507 | 92.7663
2022-09-07 20:20 | 1:56 | 31.0338 | 27.5143 | 31.6221 | 38.2039 | 38.8995 | 37.1376 | 39.0067 | 36.6295 | 39.1557 | 37.6707 | 38.2943 | 40.2234 | 36.4895 | 37.4414 | 38.2946 | 36.9045 | 37.2776 | 37.3169 | 37.2986 | 39.0557 | 28.5521 | 25.812 | 32.0068 | 38.2455 | 36.8593 | 39.6268 | 38.1874 | 37.4895 | 36.8134 | 38.0258 | 35.1257 | 38.1055 | 37.0746 | 37.3791 | 36.3973 | 37.9973 | 37.9556 | 38.0538 | 38.9361 | 37.7349 | 37.8102 | 39.2884 | 39.9764 | 38.0979 | 39.394 | 38.5001 | 40.0477 | 37.8587 | 39.5774 | 37.9323 | 38.9439 | 38.8225 | 40.0308 | 38.5443 | 40.4878 | 38.4233 | 39.6404 | 40.933 | 92.6875 | 92.664 | 92.8827
2022-09-07 20:20 | 1:56 | 30.2201 | 27.3398 | 30.8592 | 37.9741 | 38.9083 | 37.0212 | 38.9557 | 36.4939 | 39.1655 | 37.6515 | 38.1917 | 40.2239 | 36.3326 | 37.3716 | 38.3206 | 36.8491 | 37.1931 | 37.2592 | 37.2568 | 38.8853 | 28.2757 | 26.4691 | 31.4889 | 38.201 | 36.7826 | 39.776 | 38.0556 | 37.3832 | 36.772 | 37.8637 | 34.966 | 38.0483 | 36.9851 | 37.2097 | 36.2193 | 37.9457 | 37.9568 | 37.9046 | 39.0718 | 37.7362 | 37.7517 | 39.1797 | 39.8885 | 37.964 | 39.4131 | 38.4508 | 40.1169 | 37.6999 | 39.5954 | 37.8657 | 38.9731 | 38.8415 | 39.8179 | 38.5945 | 40.4385 | 38.3374 | 39.589 | 40.9635 | 92.6939 | 92.78 | 92.7969
2022-09-07 20:20 | 1:56 | 29.3105 | 27.1442 | 30.1391 | 37.8252 | 38.908 | 36.8939 | 38.928 | 36.3459 | 39.1778 | 37.5366 | 37.9737 | 40.1798 | 36.1255 | 37.2203 | 38.1662 | 36.8081 | 37.1089 | 37.1588 | 37.1753 | 38.8808 | 27.6423 | 25.9607 | 31.028 | 38.0317 | 36.6729 | 39.4684 | 37.9246 | 37.301 | 36.6964 | 37.8083 | 34.7856 | 38.0895 | 36.9004 | 37.1209 | 36.2591 | 37.8404 | 37.8879 | 37.8753 | 38.8756 | 37.7005 | 37.7041 | 39.0763 | 39.7928 | 37.8279 | 39.2871 | 38.3957 | 40.127 | 37.5374 | 39.3817 | 37.8235 | 38.9521 | 38.7052 | 39.8506 | 38.4321 | 40.4117 | 38.2526 | 39.6283 | 40.8689 | 92.7439 | 92.8451 | 92.9083
2022-09-07 20:21 | 1:57 | 28.1837 | 26.959 | 29.3134 | 37.7053 | 38.8819 | 36.6101 | 38.9618 | 36.2236 | 39.1215 | 37.4525 | 38.0442 | 40.1741 | 35.9866 | 37.0742 | 38.1486 | 36.7535 | 36.9745 | 37.0261 | 37.1147 | 38.7244 | 27.0545 | 25.6849 | 30.677 | 37.9337 | 36.5926 | 39.601 | 37.8638 | 37.197 | 36.5981 | 37.7831 | 34.5343 | 37.9455 | 36.825 | 36.9419 | 36.0979 | 37.6977 | 37.7835 | 37.7086 | 38.8248 | 37.5683 | 37.6512 | 39.0021 | 39.8146 | 37.6904 | 39.1873 | 38.3362 | 39.9818 | 37.3524 | 39.2998 | 37.7113 | 38.9053 | 38.6267 | 39.8418 | 38.3848 | 40.1081 | 38.1401 | 39.4574 | 40.8487 | 92.8602 | 92.9582 | 92.999
2022-09-07 20:21 | 1:57 | 26.1992 | 27.0474 | 28.8667 | 37.4921 | 38.8562 | 36.7647 | 38.9252 | 36.0249 | 39.1446 | 37.2903 | 37.6923 | 40.182 | 35.8863 | 36.9672 | 38.0425 | 36.7253 | 36.895 | 36.9228 | 37.1016 | 38.7124 | 26.6855 | 25.4424 | 30.4537 | 37.7403 | 36.4865 | 39.5835 | 37.8102 | 37.0743 | 36.5274 | 37.6189 | 34.5127 | 37.8374 | 36.6979 | 36.8351 | 36.0117 | 37.5836 | 37.7483 | 37.6492 | 38.7695 | 37.563 | 37.6099 | 38.903 | 39.7901 | 37.5844 | 39.0497 | 38.3276 | 39.8413 | 37.3368 | 39.2418 | 37.5925 | 39.2417 | 38.4002 | 39.822 | 38.3057 | 40.2081 | 38.0431 | 39.4854 | 40.8599 | 92.9901 | 93.0708 | 93.0895
2022-09-07 20:21 | 1:57 | 25.2452 | 26.9767 | 28.5826 | 37.3888 | 38.8683 | 36.5266 | 38.8411 | 35.9967 | 39.1743 | 37.3912 | 37.9334 | 40.2157 | 35.7587 | 37.0198 | 38.0003 | 36.6795 | 36.8239 | 36.8888 | 37.0453 | 38.6707 | 26.4354 | 25.3581 | 30.301 | 37.6937 | 36.454 | 39.2613 | 37.7517 | 37.1526 | 36.4487 | 37.6 | 34.386 | 37.8611 | 36.6229 | 36.727 | 35.9511 | 37.5902 | 37.6274 | 37.5888 | 38.775 | 37.4534 | 37.5211 | 38.8688 | 39.6816 | 37.5451 | 38.958 | 38.2781 | 39.8693 | 37.2361 | 39.3194 | 37.5867 | 39.0261 | 38.3624 | 39.7533 | 38.2847 | 40.2578 | 37.9689 | 39.3586 | 40.9379 | 93.0734 | 93.1649 | 93.1349
2022-09-07 20:21 | 1:57 | 25.2635 | 27.111 | 28.5105 | 37.2597 | 38.9068 | 36.569 | 38.8234 | 35.9355 | 39.1527 | 37.2444 | 37.7384 | 40.1741 | 35.6864 | 36.8663 | 37.9335 | 36.6715 | 36.7779 | 36.7751 | 37.0314 | 38.6667 | 26.2833 | 25.2527 | 30.1892 | 37.5501 | 36.3718 | 39.2947 | 37.7041 | 37.1303 | 36.3847 | 37.5874 | 34.2843 | 37.7397 | 36.5644 | 36.6649 | 35.7241 | 37.5477 | 37.6757 | 37.5123 | 38.8006 | 37.4195 | 37.46 | 38.7456 | 39.5702 | 37.4465 | 38.8342 | 38.2224 | 39.9732 | 37.0718 | 39.135 | 37.5119 | 39.0399 | 38.2791 | 39.7521 | 38.1473 | 40.1827 | 37.8425 | 39.3247 | 40.8426 | 93.199 | 93.2988 | 93.2008
2022-09-07 20:21 | 1:57 | 25.2379 | 27.122 | 28.4486 | 37.242 | 38.8673 | 36.469 | 38.702 | 35.8873 | 39.1531 | 37.2112 | 37.7689 | 40.2192 | 35.6786 | 36.8342 | 37.9144 | 36.6709 | 36.686 | 36.7978 | 37.1155 | 38.6467 | 26.1791 | 25.0572 | 30.0591 | 37.5388 | 36.2396 | 39.3694 | 37.6512 | 36.9896 | 36.3243 | 37.4989 | 34.2219 | 37.9017 | 36.4972 | 36.6454 | 35.7519 | 37.5222 | 37.5126 | 37.5046 | 38.8341 | 37.2873 | 37.3952 | 38.7298 | 39.7229 | 37.3754 | 38.8915 | 38.1669 | 39.8068 | 36.9713 | 39.2205 | 37.5031 | 38.9798 | 38.2517 | 39.4767 | 38.1623 | 40.231 | 37.764 | 39.3311 | 40.6983 | 93.2758 | 93.363 | 93.251
2022-09-07 20:21 | 1:57 | 25.0435 | 26.9778 | 28.3556 | 37.1736 | 38.8878 | 36.3368 | 38.7703 | 35.8388 | 39.1278 | 37.1688 | 37.7436 | 40.1301 | 35.5921 | 36.9156 | 37.8619 | 36.6668 | 36.6636 | 36.6471 | 36.9681 | 38.6048 | 25.942 | 24.7857 | 29.8797 | 37.4009 | 36.2193 | 39.1147 | 37.6099 | 36.8682 | 36.301 | 37.387 | 34.08 | 37.9662 | 36.3924 | 36.5574 | 35.6901 | 37.608 | 37.6468 | 37.488 | 38.7238 | 37.313 | 37.3327 | 38.6262 | 39.5857 | 37.2355 | 38.8117 | 38.115 | 39.8405 | 36.9283 | 39.0986 | 37.4114 | 39.0252 | 38.2615 | 39.586 | 38.0227 | 40.2059 | 37.6647 | 39.1928 | 40.6176 | 93.416 | 93.5498 | 93.3714
2022-09-07 20:22 | 1:57 | 24.9442 | 26.8171 | 28.2167 | 37.0097 | 38.8502 | 36.4435 | 38.7248 | 35.737 | 39.1151 | 36.9908 | 37.4858 | 40.1624 | 35.5628 | 36.8845 | 37.8 | 36.6159 | 36.5508 | 36.6149 | 36.9222 | 38.531 | 25.6636 | 24.6023 | 29.6893 | 37.3307 | 36.134 | 39.1286 | 37.5211 | 36.9341 | 36.2832 | 37.3202 | 33.981 | 37.9251 | 36.3717 | 36.489 | 35.5024 | 37.4926 | 37.5679 | 37.4594 | 38.6191 | 37.2547 | 37.2542 | 38.5013 | 39.4594 | 37.1148 | 38.76 | 38.0152 | 39.8676 | 36.7593 | 38.8262 | 37.3133 | 38.6915 | 38.1487 | 39.5755 | 38.0365 | 40.1547 | 37.6672 | 39.1676 | 40.5379 | 93.547 | 93.5925 | 93.4385
2022-09-07 20:22 | 1:58 | 24.7103 | 26.5675 | 28.0187 | 36.9992 | 38.864 | 36.2914 | 38.7491 | 35.7513 | 39.0515 | 37.0762 | 37.4423 | 40.1044 | 35.4475 | 36.7827 | 37.8224 | 36.6201 | 36.4806 | 36.6586 | 36.8744 | 38.3255 | 25.4125 | 24.4347 | 29.5292 | 37.2905 | 36.0689 | 38.9909 | 37.46 | 36.759 | 36.2386 | 37.2908 | 33.8977 | 37.934 | 36.2943 | 36.416 | 35.469 | 37.557 | 37.5444 | 37.2824 | 38.6917 | 37.1859 | 37.2274 | 38.4146 | 39.5775 | 37.0262 | 38.594 | 38.0111 | 39.6973 | 36.6551 | 38.8884 | 37.1894 | 38.5756 | 38.0364 | 39.4235 | 37.7944 | 40.141 | 37.5743 | 39.0511 | 40.7096 | 93.6842 | 93.8509 | 93.3903
2022-09-07 20:22 | 1:58 | 24.4958 | 26.3163 | 27.8104 | 36.8149 | 38.8568 | 36.1306 | 38.693 | 35.6457 | 39.0544 | 37.006 | 37.5159 | 40.2259 | 35.3753 | 36.7203 | 37.7493 | 36.5976 | 36.4533 | 36.556 | 36.8526 | 38.3727 | 25.192 | 24.1884 | 29.3461 | 37.2202 | 35.9909 | 39.1257 | 37.3952 | 36.9148 | 36.1905 | 37.2105 | 33.7886 | 37.8556 | 36.2846 | 36.3986 | 35.4729 | 37.5118 | 37.5787 | 37.2976 | 38.7806 | 37.1402 | 37.178 | 38.2961 | 39.4577 | 37.072 | 38.4678 | 37.8971 | 39.6206 | 36.5857 | 38.8312 | 37.1557 | 38.4002 | 37.9029 | 39.4842 | 37.6931 | 39.9016 | 37.4198 | 39.142 | 40.7934 | 93.8378 | 94.0119 | 93.6419
2022-09-07 20:22 | 1:58 | 24.2812 | 26.0723 | 27.6171 | 36.743 | 38.884 | 36.0089 | 38.5906 | 35.5761 | 39.0814 | 36.8732 | 37.5224 | 40.1803 | 35.2879 | 36.6802 | 37.7296 | 36.5635 | 36.4172 | 36.5062 | 36.8245 | 38.299 | 25.0372 | 23.8879 | 29.2177 | 37.0606 | 35.9056 | 38.9987 | 37.3327 | 36.8244 | 36.0887 | 37.2017 | 33.703 | 37.7213 | 36.2687 | 36.281 | 35.45 | 37.3242 | 37.5498 | 37.1707 | 38.7689 | 37.2162 | 37.122 | 38.3014 | 39.3945 | 36.9509 | 38.4359 | 37.8282 | 39.6112 | 36.4851 | 38.7328 | 37.0771 | 38.5829 | 37.7985 | 39.3657 | 37.6949 | 39.7801 | 37.3301 | 38.8643 | 40.8105 | 94.0388 | 94.1249 | 93.7355
2022-09-07 20:22 | 1:58 | 24.116 | 25.8832 | 27.3979 | 36.6227 | 38.8492 | 36.054 | 38.6284 | 35.5629 | 39.0229 | 36.7816 | 37.536 | 40.2361 | 35.2701 | 36.6819 | 37.5982 | 36.5317 | 36.2914 | 36.3707 | 36.7955 | 38.2631 | 25.0045 | 23.725 | 29.1021 | 36.9741 | 35.8383 | 39.0226 | 37.2542 | 36.7974 | 36.0533 | 37.1959 | 33.5148 | 37.8029 | 36.1965 | 36.2238 | 35.0512 | 37.346 | 37.5623 | 37.1419 | 38.62 | 37.0716 | 37.0554 | 38.1428 | 39.3577 | 36.7991 | 38.4504 | 37.8038 | 39.6125 | 36.3511 | 38.7292 | 37.0497 | 38.8332 | 37.7958 | 39.396 | 37.6641 | 39.9523 | 37.2555 | 38.8704 | 40.7163 | 94.1446 | 94.2652 | 93.7589
2022-09-07 20:22 | 1:58 | 23.8965 | 25.665 | 27.2349 | 36.5015 | 38.8056 | 36.1002 | 38.6253 | 35.413 | 39.0292 | 36.6902 | 37.2583 | 40.1512 | 35.164 | 36.554 | 37.492 | 36.4961 | 36.2426 | 36.3945 | 36.6923 | 38.2463 | 24.9142 | 23.5062 | 28.9632 | 36.895 | 35.7289 | 38.7071 | 37.2274 | 36.781 | 36.0458 | 37.1289 | 33.4406 | 37.821 | 36.0828 | 36.094 | 34.9201 | 37.3832 | 37.2378 | 37.0287 | 38.6702 | 36.9582 | 36.988 | 38.1147 | 39.2605 | 36.6814 | 38.4052 | 37.7493 | 39.3961 | 36.3002 | 38.736 | 36.9265 | 38.8576 | 37.579 | 39.269 | 37.5673 | 39.8844 | 37.1932 | 38.8585 | 40.6137 | 94.3469 | 94.4322 | 93.8783
2022-09-07 20:23 | 1:59 | 23.7606 | 25.479 | 27.058 | 36.5014 | 38.7543 | 35.8946 | 38.514 | 35.452 | 38.9804 | 36.7277 | 37.3319 | 40.1687 | 35.1275 | 36.4434 | 37.4324 | 36.4638 | 36.1338 | 36.3576 | 36.7321 | 38.1673 | 24.8442 | 23.3402 | 28.8226 | 36.8297 | 35.6688 | 38.6127 | 37.178 | 36.7405 | 35.884 | 37.0964 | 33.4347 | 37.7407 | 35.945 | 36.0443 | 34.8768 | 37.3024 | 37.1074 | 36.9637 | 38.5994 | 36.8241 | 36.8848 | 38.1251 | 39.1726 | 36.7014 | 38.38 | 37.6871 | 39.346 | 36.2156 | 38.5925 | 36.8772 | 39.0793 | 37.5374 | 39.2754 | 37.4751 | 40.0099 | 37.0818 | 38.7732 | 40.7752 | 94.5349 | 94.6052 | 94.0809
2022-09-07 20:23 | 1:59 | 23.6196 | 25.2987 | 26.9264 | 36.4241 | 38.7749 | 35.6698 | 38.6186 | 35.3443 | 38.967 | 36.6554 | 37.1592 | 40.16 | 35.077 | 36.4373 | 37.3589 | 36.4139 | 36.0859 | 36.3085 | 36.6214 | 38.2233 | 24.7554 | 23.1495 | 28.7047 | 36.6825 | 35.5241 | 38.5655 | 37.122 | 36.5022 | 35.8374 | 36.8441 | 33.2488 | 37.5252 | 35.8379 | 35.997 | 34.8158 | 37.2603 | 37.1198 | 36.9468 | 38.4679 | 36.8104 | 36.7688 | 37.9809 | 39.0507 | 36.6433 | 38.2047 | 37.6363 | 39.3356 | 36.0593 | 38.7352 | 36.7591 | 38.4144 | 37.5194 | 39.1137 | 37.6232 | 39.6323 | 36.9564 | 38.6786 | 40.6836 | 94.6497 | 94.6639 | 94.0805
2022-09-07 20:23 | 1:59 | 23.3941 | 25.0409 | 26.6837 | 36.3271 | 38.7108 | 35.7615 | 38.5177 | 35.1928 | 38.951 | 36.5908 | 37.0992 | 40.0881 | 34.9715 | 36.3382 | 37.3963 | 36.3755 | 35.9811 | 36.2184 | 36.5912 | 38.1042 | 24.6576 | 23.0252 | 28.5598 | 36.6037 | 35.4779 | 38.5482 | 37.0554 | 36.3569 | 35.8024 | 36.8397 | 33.2317 | 37.5064 | 35.8223 | 35.8447 | 34.5591 | 37.0787 | 36.9548 | 36.8109 | 38.4876 | 36.6581 | 36.7425 | 37.8933 | 39.0579 | 36.4394 | 38.1601 | 37.5692 | 39.3762 | 36.02 | 38.4887 | 36.6751 | 38.5028 | 37.4813 | 39.0517 | 37.5093 | 39.4425 | 36.9211 | 38.6114 | 40.6035 | 94.8008 | 94.7817 | 94.0657
2022-09-07 20:23 | 1:59 | 23.3012 | 24.9271 | 26.5668 | 36.2683 | 38.7147 | 35.7454 | 38.4827 | 35.0636 | 38.8999 | 36.497 | 37.0387 | 40.0581 | 34.9179 | 36.3374 | 37.3151 | 36.3653 | 35.9092 | 36.0473 | 36.5206 | 37.9965 | 24.5789 | 22.9149 | 28.4843 | 36.563 | 35.3932 | 38.4 | 36.988 | 36.6512 | 35.7321 | 36.773 | 33.1303 | 37.4987 | 35.7804 | 35.7756 | 34.3836 | 37.0693 | 36.9245 | 36.795 | 38.3639 | 36.6425 | 36.7079 | 37.8524 | 38.9564 | 36.3736 | 38.1156 | 37.4582 | 39.2895 | 35.8959 | 38.5103 | 36.7006 | 38.7893 | 37.3569 | 38.9262 | 37.3252 | 39.5671 | 36.8427 | 38.5723 | 40.3886 | 94.9004 | 94.8924 | 94.2132
2022-09-07 20:23 | 1:59 | 23.1382 | 24.7661 | 26.4043 | 36.2852 | 38.6888 | 35.7021 | 38.3007 | 35.0247 | 38.8948 | 36.5048 | 36.9341 | 40.038 | 34.7462 | 36.3996 | 37.2667 | 36.3143 | 35.8765 | 36.0678 | 36.5009 | 38.0108 | 24.4944 | 22.7322 | 28.3719 | 36.3384 | 35.33 | 38.4206 | 36.8848 | 36.3009 | 35.6328 | 36.7443 | 33.0192 | 37.4072 | 35.6283 | 35.7107 | 34.4528 | 37.1299 | 36.9644 | 36.7329 | 38.4317 | 36.5966 | 36.6663 | 37.8262 | 39.0432 | 36.3428 | 38.1085 | 37.4353 | 39.2919 | 35.7782 | 38.4286 | 36.6019 | 38.6017 | 37.1643 | 39.0452 | 37.0648 | 39.7588 | 36.682 | 38.691 | 40.1846 | 94.8241 | 94.9437 | 94.2699
2022-09-07 20:23 | 1:59 | 22.9685 | 24.5578 | 26.1773 | 36.1997 | 38.6776 | 35.5929 | 38.3809 | 34.9499 | 38.881 | 36.459 | 36.8645 | 39.9558 | 34.6757 | 36.2461 | 37.2544 | 36.2734 | 35.7847 | 36.1162 | 36.4446 | 37.802 | 24.3899 | 22.6042 | 28.2637 | 36.2876 | 35.2346 | 38.3376 | 36.7688 | 36.2215 | 35.5793 | 36.6578 | 32.9475 | 37.4459 | 35.6561 | 35.658 | 34.2874 | 37.0061 | 36.9336 | 36.7167 | 38.3153 | 36.506 | 36.5602 | 37.7037 | 38.8453 | 36.2001 | 37.9663 | 37.3882 | 39.1704 | 35.7214 | 38.2831 | 36.6053 | 38.4827 | 37.1482 | 39.0546 | 37.0396 | 39.4862 | 36.7106 | 38.3557 | 40.4581 | 94.7365 | 94.9449 | 94.1723
2022-09-07 20:24 | 1:59 | 22.8767 | 24.4066 | 26.0405 | 35.8997 | 38.537 | 35.6145 | 38.52 | 34.8661 | 38.8287 | 36.5527 | 36.6372 | 40.0334 | 34.6077 | 36.1716 | 37.1031 | 36.2149 | 35.7504 | 36.0139 | 36.4057 | 37.7584 | 24.3418 | 22.4741 | 28.1744 | 36.2694 | 35.1435 | 38.3032 | 36.7425 | 36.1494 | 35.4759 | 36.638 | 32.8755 | 37.397 | 35.5812 | 35.5542 | 34.3182 | 36.9063 | 36.88 | 36.6165 | 38.0791 | 36.4728 | 36.5493 | 37.66 | 38.8397 | 36.1895 | 37.8633 | 37.2675 | 39.197 | 35.6225 | 38.1633 | 36.3928 | 38.825 | 36.9592 | 38.9618 | 37.078 | 39.5967 | 36.6459 | 38.4044 | 40.509 | 94.514 | 94.7715 | 93.9882
2022-09-07 20:24 | 2:00 | 22.6581 | 24.2437 | 25.8986 | 36.1437 | 38.5691 | 35.4886 | 38.3977 | 34.809 | 38.7781 | 36.3157 | 36.6927 | 39.9468 | 34.5754 | 36.0608 | 37.0582 | 36.1861 | 35.6316 | 36.0398 | 36.4117 | 37.8464 | 24.2403 | 22.321 | 28.087 | 36.2098 | 35.0699 | 38.3624 | 36.7079 | 36.1364 | 35.4713 | 36.6114 | 32.7769 | 37.3449 | 35.4375 | 35.4892 | 34.1414 | 36.8976 | 36.7333 | 36.5686 | 38.2239 | 36.3082 | 36.4845 | 37.597 | 38.8527 | 36.1383 | 37.8338 | 37.2486 | 39.0989 | 35.5536 | 38.1097 | 36.3551 | 38.7038 | 36.9697 | 39.0258 | 37.013 | 39.4789 | 36.4916 | 38.3847 | 40.2797 | 94.3424 | 94.5823 | 93.8679
2022-09-07 20:24 | 2:00 | 22.8282 | 24.3007 | 25.9008 | 35.7822 | 38.5352 | 35.3272 | 38.2825 | 34.7928 | 38.7838 | 36.2038 | 36.7875 | 39.9979 | 34.5142 | 36.1313 | 37.0914 | 36.1144 | 35.5677 | 35.8176 | 36.3025 | 37.8219 | 24.2273 | 22.3922 | 28.0187 | 36.0478 | 34.9835 | 38.266 | 36.6663 | 36.0202 | 35.3582 | 36.4607 | 32.7468 | 37.3739 | 35.3777 | 35.4635 | 34.133 | 37.0543 | 36.825 | 36.5172 | 38.2202 | 36.3967 | 36.3775 | 37.4947 | 38.8336 | 36.014 | 37.8625 | 37.1893 | 39.0261 | 35.5505 | 38.0909 | 36.3218 | 38.5092 | 36.6868 | 38.9237 | 36.7685 | 39.4797 | 36.42 | 38.2958 | 40.2128 | 94.1277 | 94.34 | 93.6329
2022-09-07 20:24 | 2:00 | 25.6813 | 24.5834 | 29.0031 | 35.9978 | 38.6189 | 35.4097 | 38.3988 | 34.8515 | 38.7925 | 36.4159 | 36.9061 | 39.9484 | 34.6701 | 36.1387 | 37.1389 | 36.1608 | 35.6125 | 35.9903 | 36.3822 | 37.8992 | 24.2674 | 22.3864 | 28.062 | 36.0406 | 34.9629 | 37.9976 | 36.5602 | 36.1319 | 35.323 | 36.5568 | 32.6011 | 37.2529 | 35.5791 | 35.4302 | 34.0949 | 37.0178 | 36.9939 | 36.4198 | 38.3123 | 36.4996 | 36.3114 | 37.453 | 38.6594 | 35.9322 | 37.8144 | 37.0999 | 38.9818 | 35.4603 | 38.1004 | 36.2003 | 38.5747 | 36.7647 | 38.9671 | 36.8216 | 39.2652 | 36.3548 | 38.2908 | 39.9663 | 93.9435 | 94.1119 | 93.576
2022-09-07 20:24 | 2:00 | 28.2155 | 24.5398 | 29.1731 | 36.3728 | 38.6796 | 35.5729 | 38.4647 | 34.8998 | 38.7816 | 36.483 | 36.8158 | 39.9738 | 34.7731 | 36.1405 | 37.0363 | 36.1779 | 35.7482 | 36.1471 | 36.4556 | 37.7814 | 24.2822 | 22.3129 | 28.014 | 35.9573 | 34.8535 | 38.3494 | 36.5493 | 36.1951 | 35.337 | 36.5225 | 32.5436 | 37.2949 | 35.5656 | 35.5212 | 34.2352 | 37.0878 | 37.0681 | 36.406 | 38.372 | 36.6491 | 36.311 | 37.337 | 38.6903 | 35.9944 | 37.7677 | 37.0895 | 39.0852 | 35.3415 | 38.1636 | 36.1315 | 38.6085 | 36.7386 | 38.7935 | 36.6928 | 39.3392 | 36.31 | 38.2398 | 39.8531 | 93.8189 | 93.9335 | 93.5165
2022-09-07 20:24 | 2:00 | 28.716 | 24.5465 | 28.8909 | 36.3391 | 38.7104 | 35.5708 | 38.457 | 34.9826 | 38.8103 | 36.3576 | 36.9088 | 39.93 | 34.7301 | 36.13 | 37.0988 | 36.1765 | 35.7238 | 35.9949 | 36.4277 | 37.8641 | 24.2285 | 22.2141 | 27.9035 | 35.9135 | 34.7986 | 38.1693 | 36.4845 | 36.0917 | 35.3175 | 36.5463 | 32.6283 | 37.2666 | 35.5422 | 35.4749 | 34.2056 | 36.9537 | 37.0568 | 36.4264 | 38.3762 | 36.8755 | 36.2494 | 37.3255 | 38.6099 | 35.9835 | 37.6352 | 37.0214 | 38.9903 | 35.2563 | 38.0103 | 36.1516 | 38.7085 | 36.496 | 38.9045 | 36.6742 | 39.3564 | 36.2378 | 38.3647 | 39.9578 | 93.6585 | 93.8777 | 93.4579
2022-09-07 20:25 | 2:00 | 28.5611 | 26.0425 | 28.5452 | 36.194 | 38.773 | 35.5067 | 38.4447 | 34.8734 | 38.8243 | 36.345 | 36.948 | 39.96 | 34.6488 | 36.0593 | 37.131 | 36.1493 | 35.6711 | 36.0374 | 36.3683 | 37.7174 | 24.1959 | 22.2678 | 27.8526 | 35.7986 | 34.7189 | 38.0145 | 36.3775 | 36.2843 | 35.2519 | 36.4729 | 32.6046 | 37.236 | 35.5506 | 35.4349 | 34.1707 | 36.8409 | 37.1189 | 36.3477 | 38.3867 | 37.0022 | 36.2364 | 37.2924 | 38.6356 | 35.7825 | 37.6746 | 36.9607 | 38.9288 | 35.252 | 38.0324 | 35.9729 | 38.2514 | 36.4014 | 38.8635 | 36.6812 | 39.3485 | 36.0657 | 38.1365 | 39.9806 | 93.6273 | 93.8049 | 93.4054
2022-09-07 20:25 | 2:01 | 28.2687 | 27.1618 | 28.2366 | 36.1442 | 38.7862 | 35.3795 | 38.4826 | 34.8235 | 38.7686 | 36.2777 | 37.0132 | 39.9491 | 34.537 | 36.0413 | 37.0014 | 36.1352 | 35.6506 | 36.054 | 36.3827 | 37.6674 | 24.1568 | 22.2079 | 27.8237 | 35.8097 | 34.6475 | 38.1868 | 36.3114 | 35.9568 | 35.0831 | 36.4191 | 32.504 | 37.2953 | 35.4453 | 35.4079 | 33.9551 | 36.8001 | 37.0245 | 36.3673 | 38.2943 | 36.6031 | 36.1337 | 37.2324 | 38.4615 | 35.8834 | 37.6031 | 36.8541 | 38.9644 | 35.2262 | 37.8635 | 35.9905 | 38.6219 | 36.3392 | 38.8447 | 36.481 | 39.205 | 36.0592 | 38.1139 | 39.9681 | 93.5243 | 93.6946 | 93.3171
2022-09-07 20:25 | 2:01 | 28.0665 | 25.6639 | 27.9939 | 36.0076 | 38.8288 | 35.1906 | 38.4349 | 34.914 | 38.796 | 36.2849 | 37.042 | 40.0442 | 34.5028 | 36.0389 | 36.9069 | 36.0915 | 35.6003 | 35.9197 | 36.3188 | 37.7194 | 24.1634 | 22.1673 | 27.8062 | 35.8207 | 34.5892 | 38.238 | 36.311 | 36.0393 | 35.0192 | 36.3863 | 32.3669 | 37.1496 | 35.3428 | 35.358 | 33.5969 | 36.7466 | 36.9491 | 36.3002 | 38.1965 | 36.4737 | 36.0904 | 37.1849 | 38.4546 | 35.8137 | 37.5847 | 36.8364 | 38.7912 | 35.1199 | 37.9602 | 35.9861 | 38.549 | 36.3491 | 38.752 | 36.4183 | 39.0402 | 35.9717 | 37.8659 | 39.9245 | 93.453 | 93.6713 | 93.3304
2022-09-07 20:25 | 2:01 | 27.9316 | 24.7569 | 27.8012 | 36.0132 | 38.8414 | 35.2512 | 38.4806 | 35.0685 | 38.7805 | 36.2048 | 37.0433 | 39.9706 | 34.4898 | 35.957 | 36.9235 | 36.1242 | 35.5513 | 35.9246 | 36.2362 | 37.6226 | 24.195 | 22.0209 | 27.8064 | 35.5747 | 34.5346 | 38.0021 | 36.2494 | 35.9145 | 35.0452 | 36.3015 | 32.3725 | 37.0056 | 35.153 | 35.2705 | 33.7049 | 36.8098 | 36.9033 | 36.2507 | 38.1422 | 36.4143 | 36.0771 | 37.0684 | 38.3335 | 35.7025 | 37.5018 | 36.7944 | 38.6827 | 35.1588 | 37.9489 | 35.8629 | 38.5791 | 36.3337 | 38.6807 | 36.3526 | 39.049 | 35.8724 | 38.0325 | 39.9316 | 93.4001 | 93.6233 | 93.2484
2022-09-07 20:25 | 2:01 | 27.3802 | 24.5729 | 27.3482 | 36.0491 | 38.8409 | 35.1647 | 38.4878 | 34.8616 | 38.7912 | 36.2704 | 36.9726 | 40.0252 | 34.4579 | 35.8657 | 36.9801 | 36.0357 | 35.4635 | 35.8315 | 36.2503 | 37.6005 | 24.2924 | 22.1106 | 27.8923 | 35.6187 | 34.4933 | 37.9365 | 36.2364 | 36.0256 | 35.0424 | 36.3034 | 32.388 | 37.0114 | 35.2382 | 35.1977 | 33.5719 | 36.7263 | 36.8807 | 36.153 | 38.166 | 36.4033 | 36.0027 | 36.9895 | 38.3887 | 35.6164 | 37.4224 | 36.737 | 38.7628 | 35.1097 | 37.8237 | 35.7326 | 38.4472 | 36.3455 | 38.689 | 36.3943 | 38.8173 | 35.7309 | 37.8741 | 39.8727 | 93.3308 | 93.5384 | 93.2439
2022-09-07 20:25 | 2:01 | 26.3411 | 24.4138 | 26.8708 | 35.8984 | 38.8243 | 35.1033 | 38.4708 | 34.7488 | 38.7344 | 36.1447 | 36.9809 | 40.0061 | 34.3447 | 35.7752 | 36.727 | 36.0155 | 35.3946 | 35.7226 | 36.2034 | 37.5945 | 24.3003 | 21.7698 | 27.844 | 35.5699 | 34.411 | 37.6841 | 36.1337 | 35.8783 | 34.9416 | 36.14 | 32.2374 | 36.8999 | 35.193 | 35.1405 | 33.308 | 36.6113 | 36.4627 | 36.1945 | 38.149 | 36.186 | 35.9611 | 36.9293 | 38.3026 | 35.5995 | 37.3589 | 36.6621 | 38.6045 | 34.9537 | 37.7445 | 35.67 | 38.2455 | 36.1811 | 38.5754 | 36.3772 | 38.9268 | 35.7891 | 37.8733 | 39.6322 | 93.2856 | 93.4816 | 93.2455
2022-09-07 20:26 | 2:02 | 23.3418 | 24.3474 | 26.3367 | 35.7885 | 38.794 | 34.8892 | 38.5088 | 34.5788 | 38.6954 | 36.1052 | 36.6827 | 39.8357 | 34.2596 | 35.8533 | 36.8154 | 35.9327 | 35.3433 | 35.7424 | 36.0735 | 37.443 | 24.3553 | 21.7716 | 27.8985 | 35.501 | 34.3499 | 37.7053 | 36.0904 | 35.8409 | 34.845 | 36.126 | 32.1973 | 37.0312 | 35.1235 | 35.0631 | 33.2529 | 36.8088 | 36.603 | 36.0939 | 38.1366 | 36.0994 | 35.9023 | 36.9051 | 38.2642 | 35.4783 | 37.3894 | 36.5994 | 38.6795 | 34.9073 | 37.5641 | 35.5989 | 38.2117 | 36.1058 | 38.5202 | 36.2118 | 38.7477 | 35.7163 | 37.7726 | 39.778 | 93.2018 | 93.3983 | 93.1732
2022-09-07 20:26 | 2:02 | 22.568 | 24.1238 | 25.9261 | 35.6897 | 38.7455 | 34.9477 | 38.4467 | 34.5062 | 38.7148 | 36.1089 | 36.5928 | 39.8886 | 34.2012 | 35.7026 | 36.6384 | 35.9016 | 35.2405 | 35.5399 | 35.9987 | 37.4616 | 24.2865 | 21.6635 | 27.8091 | 35.4945 | 34.2509 | 37.591 | 36.0771 | 35.9206 | 34.7914 | 36.1 | 32.1968 | 36.8463 | 35.0852 | 34.9915 | 33.2881 | 36.6651 | 36.5383 | 36.0205 | 38.0286 | 36.022 | 35.8318 | 36.8591 | 38.2193 | 35.4154 | 37.261 | 36.5549 | 38.5924 | 34.83 | 37.5085 | 35.5616 | 37.929 | 36.1403 | 38.3913 | 36.0804 | 38.6377 | 35.6747 | 37.8664 | 39.4839 | 93.1176 | 93.3104 | 93.1235
2022-09-07 20:26 | 2:02 | 22.3516 | 23.9945 | 25.691 | 35.4967 | 38.7402 | 35.1269 | 38.4756 | 34.4446 | 38.633 | 35.9498 | 36.496 | 39.8793 | 34.1 | 35.6832 | 36.5379 | 35.8199 | 35.2093 | 35.6094 | 35.9469 | 37.3791 | 24.3113 | 21.5761 | 27.8738 | 35.4697 | 34.1967 | 37.7279 | 36.0027 | 35.6959 | 34.7676 | 35.9375 | 32.0914 | 36.7996 | 35.0297 | 34.8993 | 33.1547 | 36.5862 | 36.458 | 35.9745 | 37.9797 | 35.8974 | 35.7472 | 36.7287 | 38.0668 | 35.2899 | 37.1194 | 36.5093 | 38.5381 | 34.7398 | 37.5771 | 35.61 | 38.1545 | 35.8638 | 38.392 | 35.9295 | 38.8967 | 35.608 | 37.6355 | 39.4941 | 93.063 | 93.2432 | 93.0151
2022-09-07 20:26 | 2:02 | 22.2197 | 23.8295 | 25.4896 | 35.5455 | 38.6972 | 34.8787 | 38.3225 | 34.4255 | 38.6254 | 35.9323 | 36.6687 | 39.8673 | 33.9638 | 35.6711 | 36.5507 | 35.7566 | 35.1761 | 35.5733 | 35.9318 | 37.2831 | 24.3129 | 21.6099 | 27.8906 | 35.371 | 34.1535 | 37.6277 | 35.9611 | 35.5607 | 34.7787 | 35.8679 | 32.0595 | 36.8292 | 34.9945 | 34.8359 | 33.0518 | 36.6136 | 36.2448 | 35.8768 | 37.9401 | 35.8306 | 35.6658 | 36.681 | 38.0304 | 35.2075 | 37.0301 | 36.4459 | 38.3715 | 34.7262 | 37.5007 | 35.4915 | 37.9808 | 35.8679 | 38.3509 | 35.8346 | 38.6644 | 35.4584 | 37.6007 | 39.3201 | 92.9521 | 93.0979 | 93.0107
2022-09-07 20:26 | 2:02 | 22.0704 | 23.6499 | 25.3064 | 35.5558 | 38.7197 | 34.764 | 38.2751 | 34.3276 | 38.5858 | 35.9208 | 36.5577 | 39.7691 | 33.8971 | 35.5344 | 36.5031 | 35.7207 | 35.0795 | 35.4798 | 35.8533 | 37.2293 | 24.2758 | 21.402 | 27.8957 | 35.3488 | 34.0496 | 37.4956 | 35.9023 | 35.3172 | 34.6974 | 35.9057 | 32.0595 | 36.8804 | 34.8473 | 34.7796 | 32.8788 | 36.4632 | 36.1627 | 35.881 | 37.8232 | 35.7344 | 35.6868 | 36.731 | 37.9982 | 35.1551 | 37.0361 | 36.3501 | 38.4267 | 34.5586 | 37.5913 | 35.3291 | 37.5575 | 35.8433 | 38.2891 | 35.7449 | 38.6849 | 35.3778 | 37.6897 | 39.2283 | 92.8674 | 93.0204 | 92.9741
2022-09-07 20:26 | 2:02 | 21.9298 | 23.4739 | 25.1602 | 35.391 | 38.6579 | 34.721 | 38.2119 | 34.3305 | 38.547 | 35.7533 | 36.3083 | 39.8071 | 33.8746 | 35.5237 | 36.3608 | 35.6812 | 34.9808 | 35.407 | 35.8204 | 37.1862 | 24.2418 | 21.2895 | 27.8086 | 35.2364 | 33.9772 | 37.5469 | 35.8318 | 35.3401 | 34.5487 | 35.7738 | 32.059 | 36.6321 | 34.7276 | 34.6659 | 32.8804 | 36.295 | 36.2328 | 35.7292 | 37.8044 | 35.7845 | 35.7197 | 36.5984 | 38.025 | 35.0954 | 36.9902 | 36.3081 | 38.4304 | 34.5351 | 37.5435 | 35.3517 | 37.4656 | 35.6312 | 38.2631 | 35.7428 | 38.4593 | 35.3797 | 37.4831 | 39.4335 | 92.7623 | 92.9591 | 92.8619
2022-09-07 20:27 | 2:02 | 21.8081 | 23.3516 | 24.9753 | 35.315 | 38.5062 | 34.6241 | 38.3325 | 34.2831 | 38.524 | 35.7829 | 36.5248 | 39.6777 | 33.7306 | 35.3888 | 36.3016 | 35.6271 | 34.9053 | 35.191 | 35.7285 | 37.081 | 24.1933 | 21.2257 | 27.7632 | 35.2595 | 33.9106 | 37.631 | 35.7472 | 35.3787 | 34.5349 | 35.7126 | 31.8633 | 36.5481 | 34.6993 | 34.623 | 32.783 | 36.1715 | 36.1714 | 35.6847 | 37.8329 | 35.6897 | 35.7704 | 36.5872 | 37.9889 | 35.0462 | 37.0767 | 36.2426 | 38.3723 | 34.4645 | 37.4016 | 35.276 | 37.8097 | 35.6883 | 38.2371 | 35.5945 | 38.6107 | 35.3042 | 37.5895 | 39.3621 | 92.6638 | 92.8066 | 92.748
2022-09-07 20:27 | 2:03 | 21.2077 | 23.0755 | 24.7009 | 35.2364 | 38.5184 | 34.6004 | 38.0907 | 34.1445 | 38.5027 | 35.6605 | 36.125 | 39.7919 | 33.6856 | 35.3552 | 36.3985 | 35.5935 | 34.8548 | 35.226 | 35.6634 | 36.9216 | 24.1355 | 21.3137 | 27.8401 | 35.04 | 33.8469 | 37.6469 | 35.6658 | 35.2009 | 34.4922 | 35.693 | 31.7794 | 36.5964 | 34.5065 | 34.5794 | 32.607 | 36.1775 | 36.1311 | 35.6971 | 37.8133 | 35.637 | 35.7614 | 36.5488 | 37.9418 | 35.0341 | 36.9028 | 36.1944 | 38.2576 | 34.4711 | 37.3138 | 35.2338 | 37.4763 | 35.5269 | 38.1022 | 35.6422 | 38.4471 | 35.267 | 37.4443 | 39.35 | 92.6303 | 92.6436 | 92.7619
2022-09-07 20:27 | 2:03 | 20.3213 | 22.8182 | 24.3582 | 35.2335 | 38.3459 | 34.5635 | 38.0359 | 33.9329 | 38.4186 | 35.5827 | 35.996 | 39.6425 | 33.6294 | 35.2515 | 36.2923 | 35.4679 | 34.7706 | 35.0222 | 35.5289 | 36.8197 | 24.4429 | 22.3692 | 28.6413 | 34.9881 | 33.827 | 37.3305 | 35.6868 | 35.301 | 34.3698 | 35.7016 | 31.9529 | 36.6095 | 34.3482 | 34.5104 | 32.7365 | 36.2309 | 35.911 | 35.6057 | 37.7072 | 35.5576 | 35.8578 | 36.5901 | 37.9628 | 35.0934 | 37.0497 | 36.159 | 38.3603 | 34.6058 | 37.4032 | 35.289 | 37.8034 | 35.6575 | 38.2715 | 35.6704 | 38.5108 | 35.3019 | 37.6236 | 39.1748 | 92.5524 | 92.5921 | 92.6952
2022-09-07 20:27 | 2:03 | 19.4875 | 22.1982 | 23.8063 | 34.9538 | 38.3278 | 34.3559 | 37.9084 | 33.9161 | 38.397 | 35.5047 | 36.324 | 39.7447 | 33.424 | 35.1827 | 36.2312 | 35.423 | 34.7111 | 35.0272 | 35.4689 | 37.014 | 25.22 | 23.53 | 29.7204 | 35.1234 | 33.855 | 37.6374 | 35.7197 | 35.2481 | 34.4224 | 35.7149 | 32.312 | 36.5543 | 34.3404 | 34.5206 | 32.9347 | 36.4373 | 35.9533 | 35.5699 | 37.5512 | 35.5231 | 35.93 | 36.6592 | 38.0266 | 35.2366 | 37.2398 | 36.155 | 38.2877 | 34.7954 | 37.4886 | 35.2989 | 37.4534 | 35.8207 | 38.2079 | 35.6653 | 38.6918 | 35.4845 | 37.5003 | 39.307 | 92.392 | 92.4842 | 92.5864
2022-09-07 20:27 | 2:03 | 18.9786 | 21.7635 | 23.366 | 34.7069 | 38.2952 | 34.4905 | 37.9578 | 33.785 | 38.3339 | 35.4849 | 35.9463 | 39.6907 | 33.3211 | 35.1698 | 36.1654 | 35.3314 | 34.5747 | 34.9718 | 35.383 | 36.8581 | 26.231 | 24.8997 | 30.63 | 35.301 | 33.8881 | 37.6882 | 35.7704 | 35.3569 | 34.3857 | 35.7374 | 32.5256 | 36.4159 | 34.3181 | 34.6281 | 33.0815 | 36.2279 | 35.8595 | 35.694 | 37.4419 | 35.4904 | 35.9587 | 36.7277 | 38.0518 | 35.4678 | 37.3302 | 36.141 | 38.3148 | 34.9822 | 37.7875 | 35.4362 | 37.0572 | 36.0305 | 38.2131 | 35.7465 | 38.9213 | 35.6534 | 37.7241 | 39.2929 | 92.3555 | 92.428 | 92.5027
2022-09-07 20:27 | 2:03 | 18.5839 | 21.371 | 22.9951 | 34.7584 | 38.205 | 34.2362 | 37.8845 | 33.7147 | 38.2891 | 35.5206 | 35.7792 | 39.5074 | 33.2397 | 35.0543 | 36.1838 | 35.2995 | 34.5257 | 34.7544 | 35.3774 | 36.7502 | 27.1906 | 26.1705 | 31.26 | 35.3329 | 33.9113 | 38.0543 | 35.7614 | 35.2542 | 34.4457 | 35.8541 | 32.7282 | 36.27 | 34.2915 | 34.6298 | 33.1348 | 36.2307 | 35.8232 | 35.6122 | 37.2618 | 35.4989 | 35.9642 | 36.8185 | 38.141 | 35.5654 | 37.5008 | 36.1144 | 38.3814 | 35.0936 | 37.7215 | 35.4976 | 37.2552 | 36.0778 | 38.2515 | 35.7785 | 38.8668 | 35.7294 | 38.0036 | 39.1826 | 92.2195 | 92.3056 | 92.4785
2022-09-07 20:28 | 2:04 | 18.1628 | 20.9934 | 22.622 | 34.7165 | 38.1007 | 34.2961 | 37.8033 | 33.6052 | 38.2278 | 35.4579 | 35.634 | 39.4271 | 33.1128 | 34.937 | 36.0648 | 35.231 | 34.4473 | 34.6134 | 35.2453 | 37.0679 | 28.0808 | 27.3269 | 31.751 | 35.4186 | 33.9534 | 37.9836 | 35.8578 | 35.2999 | 34.3757 | 35.7955 | 32.9471 | 36.3311 | 34.1676 | 34.6953 | 33.271 | 36.2085 | 35.871 | 35.6154 | 37.3533 | 35.4957 | 35.9351 | 36.8909 | 38.1965 | 35.7232 | 37.6249 | 36.1297 | 38.3757 | 35.2272 | 37.7141 | 35.5241 | 37.1586 | 36.1273 | 38.2522 | 35.7263 | 38.8985 | 35.7698 | 37.8414 | 39.3364 | 92.1184 | 92.1466 | 92.4106
2022-09-07 20:28 | 2:04 | 17.8236 | 20.6984 | 22.3208 | 34.5154 | 38.025 | 34.288 | 37.6147 | 33.352 | 38.1337 | 35.3563 | 35.3658 | 39.3047 | 32.9713 | 34.9824 | 35.8708 | 35.1187 | 34.3219 | 34.7006 | 35.1733 | 36.8925 | 28.8122 | 28.318 | 32.1012 | 35.4708 | 33.9681 | 38.2431 | 35.93 | 35.1025 | 34.3176 | 35.9492 | 33.0241 | 36.2699 | 34.1158 | 34.7216 | 33.3276 | 36.1125 | 35.8558 | 35.6536 | 37.3118 | 35.5034 | 35.8708 | 36.9417 | 38.2037 | 35.7972 | 37.6671 | 36.1216 | 38.4324 | 35.3415 | 37.8528 | 35.5485 | 37.2517 | 36.1835 | 38.2264 | 35.72 | 38.8648 | 35.8227 | 37.8811 | 39.3567 | 91.9193 | 92.0053 | 92.2793
2022-09-07 20:28 | 2:04 | 17.5498 | 20.3561 | 22.0146 | 34.3769 | 37.9176 | 34.0862 | 37.4372 | 33.3388 | 38.0851 | 35.1294 | 35.4613 | 39.3947 | 32.862 | 34.928 | 35.7894 | 35.0562 | 34.1637 | 34.5085 | 35.0772 | 36.6047 | 29.4377 | 29.0208 | 32.3667 | 35.4716 | 33.9486 | 38.3843 | 35.9587 | 35.0602 | 34.3106 | 35.8861 | 33.1665 | 36.3258 | 34.1173 | 34.803 | 33.4124 | 36.2127 | 35.8779 | 35.6904 | 37.0542 | 35.545 | 35.9406 | 37.0152 | 38.2259 | 35.867 | 37.6657 | 36.0613 | 38.5215 | 35.3828 | 37.8914 | 35.5612 | 37.278 | 36.2514 | 38.2523 | 35.7347 | 38.8381 | 35.8633 | 37.9048 | 39.2445 | 91.8015 | 91.8536 | 92.1808
2022-09-07 20:28 | 2:04 | 17.2561 | 20.0652 | 21.7756 | 34.3176 | 37.7785 | 33.9599 | 37.4019 | 33.1768 | 38.0097 | 34.9511 | 35.2372 | 39.3011 | 32.6416 | 34.6879 | 35.8386 | 34.9526 | 34.1167 | 34.4716 | 35.0167 | 36.7079 | 29.9111 | 29.5864 | 32.5592 | 35.4862 | 33.9577 | 38.3229 | 35.9642 | 35.1192 | 34.2269 | 35.9898 | 33.2399 | 36.2067 | 34.0408 | 34.8172 | 33.4342 | 36.1284 | 35.6519 | 35.6393 | 37.1311 | 35.4434 | 35.9359 | 36.9851 | 38.3252 | 35.9135 | 37.6551 | 36.0897 | 38.5238 | 35.4801 | 37.8662 | 35.5863 | 37.254 | 36.3424 | 38.2246 | 35.7891 | 38.8287 | 35.8893 | 37.9353 | 39.2382 | 91.6563 | 91.6888 | 92.1277
2022-09-07 20:28 | 2:04 | 16.9377 | 19.7173 | 21.4503 | 34.2607 | 37.8044 | 33.7223 | 37.5051 | 33.0092 | 37.9425 | 35.022 | 35.0988 | 39.1328 | 32.7199 | 34.5324 | 35.6766 | 34.8587 | 33.9846 | 34.419 | 34.9207 | 36.6411 | 30.3195 | 30.0409 | 32.6811 | 35.4933 | 33.9884 | 38.3664 | 35.9351 | 35.1664 | 34.2845 | 35.9249 | 33.2843 | 35.9662 | 33.946 | 34.7945 | 33.4587 | 36.1321 | 35.6257 | 35.5623 | 37.0968 | 35.455 | 35.9687 | 37.0582 | 38.3004 | 35.9575 | 37.8216 | 36.0929 | 38.4434 | 35.4654 | 37.9005 | 35.6495 | 37.2471 | 36.3128 | 38.3402 | 35.7707 | 38.84 | 35.9475 | 38.0133 | 39.2345 | 91.6909 | 91.6309 | 92.1315
2022-09-07 20:28 | 2:04 | 16.6966 | 19.4666 | 21.1968 | 34.0853 | 37.6417 | 33.7168 | 37.4059 | 33.0454 | 37.8962 | 34.8272 | 35.0926 | 39.0912 | 32.545 | 34.4876 | 35.6649 | 34.826 | 33.907 | 34.2764 | 34.9086 | 36.5767 | 30.6247 | 30.3777 | 32.7799 | 35.4207 | 33.9626 | 38.4308 | 35.8708 | 35.0919 | 34.2398 | 35.8821 | 33.3521 | 36.0412 | 33.8937 | 34.7662 | 33.5358 | 36.122 | 35.5626 | 35.58 | 37.1628 | 35.4227 | 36.0475 | 37.0959 | 38.3751 | 35.9836 | 37.7773 | 36.074 | 38.443 | 35.5571 | 37.9278 | 35.6234 | 37.5217 | 36.4282 | 38.3573 | 35.7558 | 38.8135 | 36.019 | 38.1488 | 39.2166 | 91.6594 | 91.6727 | 92.186
2022-09-07 20:29 | 2:04 | 16.4631 | 19.2779 | 20.9852 | 33.9351 | 37.5461 | 33.7305 | 37.1249 | 32.7445 | 37.8604 | 34.7301 | 34.8016 | 39.2429 | 32.3786 | 34.5979 | 35.396 | 34.7668 | 33.7836 | 34.2186 | 34.7818 | 36.3866 | 30.8466 | 30.605 | 32.8627 | 35.4205 | 33.9888 | 38.3736 | 35.9406 | 35.1271 | 34.2408 | 35.9161 | 33.3988 | 36.0043 | 33.8203 | 34.7599 | 33.5982 | 35.9957 | 35.5628 | 35.5018 | 37.1569 | 35.4505 | 36.0158 | 37.0939 | 38.2963 | 36.0598 | 37.7882 | 36.1183 | 38.3962 | 35.6358 | 37.9099 | 35.6561 | 37.3584 | 36.511 | 38.2869 | 35.7897 | 38.8652 | 35.986 | 38.223 | 39.1684 | 91.721 | 91.7362 | 92.1883
2022-09-07 20:29 | 2:05 | 16.2072 | 19.0243 | 20.7278 | 33.9615 | 37.3897 | 33.6009 | 37.191 | 32.7388 | 37.7433 | 34.7989 | 34.6504 | 39.0454 | 32.3042 | 34.1493 | 35.5869 | 34.5907 | 33.6457 | 34.1619 | 34.6596 | 36.447 | 31.0742 | 30.7857 | 32.9558 | 35.4155 | 34.0105 | 38.4794 | 35.9359 | 34.9281 | 34.0749 | 35.9109 | 33.4692 | 35.9427 | 33.8386 | 34.76 | 33.6148 | 35.8365 | 35.4831 | 35.5509 | 37.2568 | 35.4002 | 36.135 | 37.1085 | 38.34 | 36.0882 | 37.8298 | 36.1179 | 38.434 | 35.6611 | 37.986 | 35.7078 | 37.1818 | 36.5388 | 38.2204 | 35.8363 | 38.9261 | 36.0467 | 38.168 | 39.2285 | 91.7663 | 91.7764 | 92.2564
2022-09-07 20:29 | 2:05 | 15.9685 | 18.7211 | 20.482 | 33.8925 | 37.2729 | 33.571 | 36.9569 | 32.6441 | 37.7115 | 34.7498 | 34.7961 | 38.9432 | 32.155 | 34.065 | 35.4133 | 34.5664 | 33.6026 | 33.8935 | 34.7697 | 36.5826 | 31.2357 | 30.9392 | 33.026 | 35.3968 | 34.0233 | 38.6412 | 35.9687 | 34.815 | 34.1718 | 35.9376 | 33.5069 | 35.9447 | 33.7915 | 34.781 | 33.6671 | 35.995 | 35.4709 | 35.4178 | 36.958 | 35.4261 | 36.0733 | 37.1299 | 38.3338 | 36.1468 | 37.8849 | 36.1314 | 38.4507 | 35.7298 | 37.9326 | 35.761 | 37.2133 | 36.6266 | 38.3456 | 35.7767 | 38.956 | 36.0872 | 38.1197 | 39.1673 | 91.87 | 91.9298 | 92.2737
2022-09-07 20:29 | 2:05 | 15.7386 | 18.4984 | 20.2552 | 33.7941 | 37.1253 | 33.5249 | 36.7928 | 32.6114 | 37.6206 | 34.7335 | 34.5871 | 39.0519 | 32.1964 | 33.8837 | 35.2284 | 34.4922 | 33.5523 | 33.6412 | 34.6411 | 36.6419 | 31.359 | 31.0346 | 33.1106 | 35.3707 | 33.9921 | 38.5726 | 36.0475 | 34.6154 | 34.2072 | 35.9959 | 33.5333 | 35.7834 | 33.7591 | 34.7721 | 33.7418 | 35.875 | 35.4281 | 35.3616 | 36.979 | 35.3576 | 36.1526 | 37.1555 | 38.3971 | 36.1694 | 37.8787 | 36.1287 | 38.4661 | 35.7906 | 37.9648 | 35.8076 | 37.2481 | 36.5855 | 38.2373 | 35.7526 | 39.0173 | 36.1283 | 38.17 | 39.3117 | 91.9584 | 92.099 | 92.3379
2022-09-07 20:29 | 2:05 | 15.5035 | 18.2317 | 20.0182 | 33.6137 | 37.0771 | 33.3274 | 36.7203 | 32.4748 | 37.527 | 34.6323 | 34.4787 | 38.7654 | 31.9398 | 33.9157 | 35.2571 | 34.4211 | 33.472 | 33.7619 | 34.4961 | 36.4222 | 31.4712 | 31.1233 | 33.1824 | 35.3476 | 34.0259 | 38.5523 | 36.0158 | 34.5369 | 34.1371 | 36.1048 | 33.6156 | 35.7706 | 33.7989 | 34.764 | 33.7833 | 35.7868 | 35.3115 | 35.43 | 37.0281 | 35.3554 | 36.1697 | 37.2017 | 38.4318 | 36.2311 | 37.9253 | 36.1715 | 38.4531 | 35.834 | 38.0898 | 35.8004 | 37.3809 | 36.5434 | 38.243 | 35.7253 | 39.0284 | 36.1865 | 38.3533 | 39.1654 | 92.0675 | 92.189 | 92.3364
2022-09-07 20:29 | 2:05 | 15.3242 | 18.0106 | 19.7867 | 33.5929 | 37.0053 | 33.2209 | 36.6316 | 32.2887 | 37.4185 | 34.6786 | 34.289 | 38.6671 | 31.8103 | 33.8027 | 35.2949 | 34.2704 | 33.3437 | 33.6195 | 34.4811 | 36.3696 | 31.5766 | 31.1929 | 33.2699 | 35.4049 | 33.9959 | 38.5519 | 36.135 | 34.5285 | 34.116 | 36.0562 | 33.6221 | 35.7638 | 33.673 | 34.7459 | 33.8188 | 35.8733 | 35.2349 | 35.453 | 36.9696 | 35.2789 | 36.1511 | 37.283 | 38.4377 | 36.2687 | 37.9216 | 36.2152 | 38.5522 | 35.884 | 38.0277 | 35.8111 | 37.3088 | 36.6041 | 38.2248 | 35.8696 | 39.023 | 36.196 | 38.4349 | 39.1863 | 92.1722 | 92.3059 | 92.4443
2022-09-07 20:30 | 2:06 | 15.057 | 17.7828 | 19.584 | 33.1565 | 36.885 | 33.4633 | 36.7739 | 32.182 | 37.3799 | 34.8758 | 34.0854 | 38.5322 | 31.7932 | 33.9683 | 35.0439 | 34.2115 | 33.1998 | 33.276 | 34.5037 | 36.1493 | 31.6447 | 31.2674 | 33.3264 | 35.4235 | 34.02 | 38.3998 | 36.0733 | 34.5335 | 34.003 | 35.9456 | 33.6259 | 35.6248 | 33.5628 | 34.7362 | 33.8373 | 35.9075 | 35.2588 | 35.4341 | 36.9391 | 35.2652 | 36.1771 | 37.212 | 38.4447 | 36.2529 | 37.8925 | 36.1683 | 38.4449 | 35.9314 | 38.0596 | 35.8132 | 37.3284 | 36.7077 | 38.2746 | 35.7782 | 39.0428 | 36.2632 | 38.3621 | 39.189 | 92.243 | 92.3673 | 92.4537
2022-09-07 20:30 | 2:06 | 14.8628 | 17.5688 | 19.3601 | 33.532 | 36.7895 | 33.2201 | 36.5239 | 31.9021 | 37.2154 | 34.7247 | 33.693 | 38.5348 | 31.7533 | 33.8209 | 35.1109 | 34.0801 | 33.1352 | 33.1931 | 34.3186 | 36.1773 | 31.7138 | 31.3192 | 33.333 | 35.3766 | 34.0437 | 38.638 | 36.1526 | 34.5702 | 34.0136 | 36.1909 | 33.7197 | 35.6186 | 33.6019 | 34.775 | 33.8689 | 35.8638 | 35.1973 | 35.3479 | 36.8097 | 35.2467 | 36.2273 | 37.2692 | 38.5191 | 36.3415 | 37.8944 | 36.2344 | 38.4816 | 36.0011 | 38.1768 | 35.8816 | 37.335 | 36.7959 | 38.2721 | 35.7783 | 38.9844 | 36.3024 | 38.3789 | 39.1626 | 92.3758 | 92.5091 | 92.5774
2022-09-07 20:30 | 2:06 | 14.7163 | 17.3611 | 19.1698 | 33.3353 | 36.6298 | 32.9414 | 36.2423 | 31.9262 | 37.1981 | 34.5755 | 33.9977 | 38.494 | 31.5493 | 33.5927 | 34.9534 | 34.0088 | 33.088 | 33.1803 | 34.1352 | 36.1783 | 31.7955 | 31.3491 | 33.3895 | 35.3273 | 34.0492 | 38.511 | 36.1697 | 34.5336 | 33.8714 | 36.059 | 33.7672 | 35.5234 | 33.4376 | 34.7931 | 33.8896 | 35.8902 | 35.173 | 35.4143 | 36.85 | 35.1967 | 36.2003 | 37.2848 | 38.4817 | 36.3887 | 37.9651 | 36.2079 | 38.5801 | 36.0301 | 38.2351 | 35.8726 | 37.3979 | 36.7237 | 38.3428 | 35.7482 | 38.9875 | 36.3088 | 38.4668 | 39.1427 | 92.4007 | 92.5184 | 92.5273
2022-09-07 20:30 | 2:06 | 14.5035 | 17.1747 | 18.9879 | 33.0494 | 36.6018 | 32.8636 | 36.3077 | 31.696 | 37.0611 | 34.6472 | 33.793 | 38.54 | 31.427 | 33.7272 | 34.8666 | 33.8725 | 32.9102 | 33.2232 | 34.046 | 35.9153 | 31.8292 | 31.4116 | 33.4161 | 35.3025 | 33.9988 | 38.5204 | 36.1511 | 34.5366 | 34.0849 | 36.0073 | 33.7705 | 35.493 | 33.5558 | 34.7674 | 33.918 | 35.7638 | 35.0816 | 35.4188 | 36.9979 | 35.1695 | 36.2828 | 37.3122 | 38.5706 | 36.4509 | 37.9754 | 36.249 | 38.4503 | 36.1212 | 38.1779 | 35.9077 | 37.4543 | 36.731 | 38.1779 | 36.0248 | 38.9746 | 36.3897 | 38.5839 | 39.1518 | 92.5172 | 92.585 | 92.6211
2022-09-07 20:30 | 2:06 | 14.2814 | 16.7598 | 18.7511 | 33.0278 | 36.4696 | 32.9216 | 36.1727 | 31.5949 | 36.9866 | 34.3552 | 33.4248 | 38.2841 | 31.3808 | 33.8225 | 34.8569 | 33.781 | 32.8795 | 33.0744 | 33.9446 | 35.84 | 31.8756 | 31.42 | 33.4397 | 35.2967 | 34.0331 | 38.5332 | 36.1771 | 34.471 | 34.0694 | 35.9674 | 33.7952 | 35.4993 | 33.5229 | 34.7116 | 33.9453 | 35.67 | 34.9792 | 35.4253 | 36.6584 | 35.123 | 36.224 | 37.3204 | 38.5848 | 36.4976 | 38.0885 | 36.2411 | 38.5747 | 36.121 | 38.1923 | 35.9548 | 37.4367 | 36.8126 | 38.1829 | 35.9178 | 39.098 | 36.4363 | 38.5394 | 39.2154 | 92.6008 | 92.7438 | 92.6896
2022-09-07 20:30 | 2:06 | 14.3347 | 14.7027 | 18.8204 | 32.8472 | 36.2457 | 32.8389 | 36.0812 | 31.5179 | 36.9741 | 34.5114 | 33.5551 | 38.178 | 31.2058 | 33.8422 | 34.8755 | 33.6834 | 32.8029 | 33.1284 | 33.9761 | 35.843 | 31.841 | 31.4499 | 33.4256 | 35.2131 | 34.0364 | 38.6043 | 36.2273 | 34.4792 | 34.0322 | 36.0415 | 33.8511 | 35.2548 | 33.4717 | 34.7788 | 33.9709 | 35.6815 | 34.9898 | 35.3861 | 36.5866 | 35.076 | 36.2517 | 37.359 | 38.6709 | 36.548 | 38.1051 | 36.261 | 38.5245 | 36.1805 | 38.1521 | 35.9865 | 37.6339 | 36.8404 | 38.2994 | 35.7717 | 39.0878 | 36.4668 | 38.6391 | 39.1997 | 92.6964 | 92.8611 | 92.7793
2022-09-07 20:31 | 2:06 | 16.6315 | 16.5076 | 21.6512 | 33.1078 | 36.2525 | 32.7009 | 36.0378 | 31.6025 | 36.9541 | 34.3791 | 33.6917 | 38.3062 | 31.3662 | 33.8891 | 34.7869 | 33.6255 | 32.8476 | 33.4689 | 33.8602 | 35.9132 | 31.8747 | 31.4708 | 33.4573 | 35.2233 | 34.0753 | 38.7223 | 36.2003 | 34.4908 | 34.2165 | 36.0617 | 33.8764 | 35.449 | 33.517 | 34.7354 | 34.0323 | 35.9107 | 35.0667 | 35.4556 | 36.823 | 35.0992 | 36.328 | 37.3606 | 38.587 | 36.5884 | 38.0895 | 36.3068 | 38.4785 | 36.242 | 38.1975 | 36.0262 | 37.578 | 36.9048 | 38.4237 | 35.8429 | 39.1923 | 36.5433 | 38.7124 | 39.2212 | 92.8594 | 93.0161 | 92.8191
2022-09-07 20:31 | 2:07 | 18.9341 | 19.0581 | 24.4058 | 33.6729 | 36.2688 | 33.2535 | 36.3122 | 31.8759 | 36.8682 | 34.6509 | 33.9407 | 38.3337 | 31.7414 | 34.1008 | 34.8727 | 33.7295 | 32.9905 | 33.6299 | 34.0283 | 36.189 | 31.9227 | 31.4791 | 33.5501 | 35.4661 | 34.0678 | 38.8509 | 36.2828 | 34.5562 | 34.1382 | 36.1175 | 33.8786 | 35.3929 | 33.6802 | 34.9183 | 34.0711 | 35.9775 | 35.1 | 35.465 | 36.8743 | 35.1555 | 36.4093 | 37.3951 | 38.6631 | 36.6086 | 38.1749 | 36.3285 | 38.4823 | 36.285 | 38.2943 | 36.1032 | 37.5425 | 37.0261 | 38.4906 | 35.9387 | 39.2537 | 36.602 | 38.6106 | 39.2437 | 92.9523 | 93.1581 | 92.9409
2022-09-07 20:31 | 2:07 | 20.9573 | 21.5987 | 26.4727 | 34.1879 | 36.3682 | 33.3238 | 36.4234 | 32.1211 | 36.8795 | 34.8151 | 34.1538 | 38.3951 | 32.0729 | 34.1761 | 35.0384 | 33.7828 | 33.2263 | 33.8968 | 34.0507 | 36.285 | 31.9679 | 31.5146 | 33.6615 | 35.681 | 34.1566 | 38.656 | 36.224 | 34.587 | 34.0623 | 36.0642 | 33.9668 | 35.4095 | 33.7535 | 35.089 | 34.1557 | 35.9375 | 35.2315 | 35.678 | 36.9483 | 35.2315 | 36.4306 | 37.4351 | 38.747 | 36.7607 | 38.1384 | 36.3718 | 38.5386 | 36.385 | 38.4384 | 36.1057 | 37.6219 | 37.0411 | 38.5081 | 36.0724 | 39.2475 | 36.6496 | 38.6887 | 39.3221 | 93.1029 | 93.2856 | 93.0477
2022-09-07 20:31 | 2:07 | 22.7454 | 23.8903 | 27.99 | 34.5151 | 36.3443 | 33.4082 | 36.3841 | 32.3648 | 36.9491 | 34.8751 | 34.3646 | 38.4867 | 32.3608 | 34.2389 | 35.1189 | 33.8501 | 33.4512 | 34.1399 | 34.2276 | 36.415 | 32.0691 | 31.5285 | 33.7597 | 35.8165 | 34.2173 | 38.7238 | 36.2517 | 34.5084 | 34.0188 | 36.1177 | 34.0125 | 35.2676 | 33.8852 | 35.1228 | 34.2223 | 35.956 | 35.3893 | 35.7649 | 37.1644 | 35.3252 | 36.4547 | 37.5248 | 38.756 | 36.8628 | 38.2507 | 36.3883 | 38.6715 | 36.4895 | 38.5036 | 36.1612 | 37.6169 | 37.0962 | 38.5369 | 36.1045 | 39.2421 | 36.718 | 38.7221 | 39.2741 | 93.236 | 93.44 | 93.0347
2022-09-07 20:31 | 2:07 | 24.2098 | 25.8186 | 29.0487 | 34.9159 | 36.3458 | 33.6345 | 36.5388 | 32.5641 | 36.8892 | 34.9413 | 34.4169 | 38.3899 | 32.5378 | 34.4282 | 35.1775 | 33.8785 | 33.5875 | 34.2593 | 34.3169 | 36.5383 | 32.1533 | 31.5707 | 33.8774 | 35.9144 | 34.2347 | 38.781 | 36.328 | 34.7433 | 34.2161 | 36.2556 | 34.0676 | 35.4158 | 33.9966 | 35.1971 | 34.2444 | 36.0402 | 35.4808 | 35.8445 | 37.3088 | 35.399 | 36.5427 | 37.5742 | 38.7927 | 36.9312 | 38.4184 | 36.4322 | 38.6325 | 36.5404 | 38.5218 | 36.2631 | 37.6093 | 37.1873 | 38.5251 | 36.2385 | 39.2801 | 36.8037 | 38.6029 | 39.3843 | 93.3517 | 93.567 | 93.1088
2022-09-07 20:31 | 2:07 | 25.4556 | 27.3505 | 29.7298 | 35.1592 | 36.4838 | 33.7522 | 36.6223 | 32.7636 | 36.9353 | 35.0376 | 34.7133 | 38.4138 | 32.741 | 34.4636 | 35.3063 | 33.9614 | 33.6954 | 34.5222 | 34.3698 | 36.6247 | 32.2485 | 31.5762 | 33.9998 | 36.11 | 34.3412 | 38.8259 | 36.4093 | 34.6518 | 34.2601 | 36.2921 | 34.1439 | 35.3916 | 34.0887 | 35.2414 | 34.3406 | 36.059 | 35.581 | 35.8718 | 37.4153 | 35.4376 | 36.5482 | 37.6319 | 38.8448 | 37.0059 | 38.4179 | 36.4747 | 38.6721 | 36.6428 | 38.5407 | 36.3285 | 37.7224 | 37.2112 | 38.5262 | 36.2519 | 39.3345 | 36.8436 | 38.7088 | 39.4555 | 93.4757 | 93.7927 | 93.2369
2022-09-07 20:32 | 2:08 | 26.4296 | 28.5196 | 30.2159 | 35.4317 | 36.504 | 33.813 | 36.6714 | 32.9157 | 36.9438 | 35.0693 | 34.928 | 38.4327 | 32.92 | 34.5964 | 35.5062 | 33.9816 | 33.877 | 34.7224 | 34.4338 | 36.8417 | 32.3611 | 31.5864 | 34.1264 | 36.1721 | 34.384 | 38.8413 | 36.4306 | 34.891 | 34.325 | 36.2401 | 34.1845 | 35.5256 | 34.1887 | 35.3359 | 34.3929 | 36.2278 | 35.6621 | 35.9402 | 37.5135 | 35.4817 | 36.5808 | 37.6815 | 38.8704 | 37.1046 | 38.4306 | 36.4615 | 38.693 | 36.7446 | 38.5869 | 36.3316 | 37.8002 | 37.2873 | 38.6174 | 36.238 | 39.4332 | 36.9113 | 38.6183 | 39.5129 | 93.6624 | 94.1281 | 93.3257
2022-09-07 20:32 | 2:08 | 27.2332 | 29.388 | 30.5058 | 35.5725 | 36.4494 | 34.0934 | 36.7107 | 33.0525 | 36.9169 | 35.2214 | 34.9906 | 38.5045 | 33.0347 | 34.5209 | 35.4539 | 34.0291 | 34.029 | 34.7553 | 34.5222 | 36.9204 | 32.4681 | 31.6114 | 34.268 | 36.1716 | 34.4269 | 38.8172 | 36.4547 | 34.8424 | 34.2715 | 36.3065 | 34.2704 | 35.5615 | 34.2942 | 35.4518 | 34.4346 | 36.2654 | 35.6148 | 36.0337 | 37.4829 | 35.5183 | 36.6292 | 37.7099 | 38.9692 | 37.1833 | 38.5038 | 36.5608 | 38.7696 | 36.8195 | 38.6517 | 36.4299 | 37.8599 | 37.3801 | 38.5495 | 36.414 | 39.3747 | 36.98 | 38.8893 | 39.4959 | 93.8837 | 94.4352 | 93.5272
2022-09-07 20:32 | 2:08 | 27.87 | 29.9987 | 30.7106 | 35.7873 | 36.4886 | 34.0786 | 36.8237 | 33.0832 | 36.9445 | 35.2173 | 35.0686 | 38.4773 | 33.1286 | 34.5924 | 35.6353 | 34.0495 | 34.0782 | 34.818 | 34.5456 | 37.0311 | 32.5798 | 31.6187 | 34.426 | 36.2326 | 34.5474 | 38.9037 | 36.5427 | 34.8046 | 34.309 | 36.3451 | 34.3552 | 35.5294 | 34.3309 | 35.5078 | 34.4815 | 36.2327 | 35.6071 | 36.0543 | 37.4258 | 35.576 | 36.6542 | 37.7873 | 39.0117 | 37.3002 | 38.5085 | 36.5883 | 38.7593 | 36.8959 | 38.6971 | 36.4715 | 37.8895 | 37.3905 | 38.6071 | 36.4083 | 39.336 | 37.0534 | 38.9578 | 39.5044 | 94.159 | 94.6879 | 93.7332
2022-09-07 20:32 | 2:08 | 28.3619 | 30.4535 | 30.9332 | 35.7646 | 36.5058 | 34.0939 | 36.7841 | 33.2229 | 36.9686 | 35.3321 | 35.1971 | 38.479 | 33.2122 | 34.7049 | 35.5758 | 34.0866 | 34.1328 | 34.866 | 34.5667 | 36.9416 | 32.7079 | 31.6338 | 34.5746 | 36.2762 | 34.5907 | 38.9005 | 36.5482 | 34.9031 | 34.4472 | 36.4208 | 34.4243 | 35.6819 | 34.4091 | 35.5829 | 34.5491 | 36.3238 | 35.6186 | 36.1024 | 37.4589 | 35.6113 | 36.7278 | 37.836 | 39.051 | 37.3507 | 38.6313 | 36.643 | 38.7691 | 36.9771 | 38.8303 | 36.5277 | 37.9486 | 37.4893 | 38.7635 | 36.4179 | 39.4115 | 37.1324 | 38.8925 | 39.5748 | 94.3384 | 94.8825 | 93.9049
2022-09-07 20:32 | 2:08 | 28.7512 | 30.7772 | 31.0178 | 35.7777 | 36.5255 | 34.2905 | 36.993 | 33.3429 | 36.9837 | 35.3837 | 35.2065 | 38.4309 | 33.2951 | 34.8074 | 35.6095 | 34.1264 | 34.216 | 34.9988 | 34.6533 | 37.0875 | 32.8395 | 31.6579 | 34.7555 | 36.4171 | 34.62 | 38.8974 | 36.5808 | 34.967 | 34.5797 | 36.4345 | 34.4906 | 35.6487 | 34.5031 | 35.6691 | 34.6137 | 36.3701 | 35.6674 | 36.1739 | 37.432 | 35.6404 | 36.6381 | 37.9205 | 39.1267 | 37.4247 | 38.6095 | 36.6512 | 38.8118 | 37.0504 | 38.9407 | 36.6116 | 38.0368 | 37.5676 | 38.6563 | 36.4925 | 39.4384 | 37.1722 | 39.0192 | 39.5878 | 94.5152 | 95.0746 | 93.9602
2022-09-07 20:32 | 2:08 | 29.0774 | 31.0034 | 31.1465 | 36.1402 | 36.4954 | 34.3395 | 37.0265 | 33.377 | 36.9789 | 35.6415 | 35.1776 | 38.388 | 33.4106 | 34.8492 | 35.6766 | 34.1577 | 34.3171 | 35.0961 | 34.7069 | 37.0918 | 32.9769 | 31.6549 | 34.8969 | 36.5008 | 34.7132 | 38.9443 | 36.6292 | 35.0137 | 34.5085 | 36.5593 | 34.5782 | 35.6698 | 34.5818 | 35.7385 | 34.6766 | 36.3443 | 35.7538 | 36.2145 | 37.4868 | 35.6983 | 36.6238 | 37.9536 | 39.1442 | 37.5206 | 38.6331 | 36.7145 | 38.8719 | 37.1309 | 38.9559 | 36.6317 | 38.0414 | 37.6056 | 38.6991 | 36.5364 | 39.393 | 37.2252 | 39.0796 | 39.5519 | 94.7208 | 95.2358 | 94.0698
2022-09-07 20:33 | 2:08 | 29.3573 | 31.1394 | 31.2333 | 36.2127 | 36.4802 | 34.4378 | 37.0549 | 33.5026 | 36.9787 | 35.4616 | 35.3802 | 38.4682 | 33.4648 | 34.8629 | 35.7812 | 34.1793 | 34.3997 | 35.1693 | 34.7544 | 37.1105 | 33.1188 | 31.6332 | 35.0433 | 36.5322 | 34.7847 | 38.9581 | 36.6542 | 35.1779 | 34.5871 | 36.5898 | 34.6392 | 35.7616 | 34.6232 | 35.7946 | 34.7639 | 36.3103 | 35.7615 | 36.306 | 37.4188 | 35.7186 | 36.6568 | 38.0589 | 39.2116 | 37.5879 | 38.6975 | 36.7564 | 38.9279 | 37.2076 | 39.0076 | 36.6973 | 38.0436 | 37.6735 | 38.839 | 36.6777 | 39.362 | 37.3106 | 39.1022 | 39.4939 | 94.831 | 95.3356 | 94.122
2022-09-07 20:33 | 2:09 | 29.627 | 30.7391 | 31.2988 | 36.1449 | 36.4899 | 34.4292 | 36.9253 | 33.5598 | 36.9982 | 35.4316 | 35.4647 | 38.4974 | 33.5131 | 34.9171 | 35.9074 | 34.2223 | 34.4376 | 35.1135 | 34.7621 | 37.152 | 33.473 | 27.4998 | 35.124 | 36.6315 | 34.8361 | 39.0858 | 36.7278 | 35.1555 | 34.6147 | 36.65 | 34.6904 | 35.7517 | 34.7228 | 35.8245 | 34.7499 | 36.3841 | 35.8669 | 36.2734 | 37.4703 | 35.7551 | 36.7071 | 38.0579 | 39.2459 | 37.578 | 38.7386 | 36.825 | 38.9152 | 37.1948 | 38.9714 | 36.7415 | 38.0552 | 37.6664 | 38.7439 | 36.6827 | 39.4643 | 37.3034 | 39.1312 | 39.5329 | 94.9002 | 95.4313 | 94.1509
2022-09-07 20:33 | 2:09 | 30.322 | 28.4714 | 30.9021 | 35.9626 | 36.535 | 34.3165 | 36.9374 | 33.5272 | 37.0315 | 35.4584 | 35.5679 | 38.491 | 33.4959 | 34.8692 | 35.7751 | 34.2072 | 34.4398 | 35.1516 | 34.7808 | 37.1188 | 33.4821 | 28.5891 | 34.377 | 36.6867 | 34.7158 | 38.844 | 36.6381 | 35.1171 | 34.5409 | 36.5395 | 34.4936 | 35.6597 | 34.6938 | 35.7596 | 34.711 | 36.3669 | 35.8948 | 36.2988 | 37.3809 | 35.8007 | 36.8295 | 37.931 | 39.0225 | 37.3552 | 38.5211 | 36.7962 | 38.8272 | 36.9796 | 38.8132 | 36.5608 | 37.9271 | 37.5753 | 38.6242 | 36.642 | 39.3914 | 37.1203 | 39.1317 | 39.4804 | 95.0066 | 95.5065 | 94.2473
2022-09-07 20:33 | 2:09 | 31.507 | 31.5293 | 31.3107 | 36.1623 | 36.5384 | 34.4698 | 37.0571 | 33.6858 | 37.0316 | 35.5007 | 35.6806 | 38.4307 | 33.6136 | 34.9472 | 35.9545 | 34.2641 | 34.5404 | 35.2049 | 34.8258 | 37.0615 | 33.4479 | 30.8454 | 34.4492 | 36.6881 | 34.7313 | 38.871 | 36.6238 | 35.1297 | 34.5456 | 36.5157 | 34.542 | 35.7702 | 34.7495 | 35.7442 | 34.7415 | 36.3477 | 35.9607 | 36.3077 | 37.4335 | 35.8306 | 36.8621 | 37.931 | 38.9643 | 37.3064 | 38.5101 | 36.7807 | 38.8277 | 36.9975 | 38.7373 | 36.4641 | 37.9322 | 37.6531 | 38.6357 | 36.752 | 39.502 | 37.1534 | 38.9151 | 39.5026 | 94.8839 | 95.3963 | 94.1697
2022-09-07 20:33 | 2:09 | 32.6791 | 31.8526 | 31.5453 | 36.2708 | 36.5808 | 34.5471 | 37.2116 | 33.7843 | 37.077 | 35.5989 | 35.7517 | 38.4331 | 33.7052 | 35.0279 | 35.9976 | 34.3253 | 34.6338 | 35.2719 | 34.9106 | 37.251 | 33.6608 | 31.3581 | 34.7838 | 36.7244 | 34.8256 | 38.7745 | 36.6568 | 35.2734 | 34.5792 | 36.5551 | 34.6369 | 35.841 | 34.7952 | 35.833 | 34.8141 | 36.3526 | 35.9448 | 36.3391 | 37.5357 | 35.8783 | 36.9822 | 38.0492 | 39.0654 | 37.3895 | 38.6163 | 36.7891 | 38.8673 | 37.0621 | 38.9031 | 36.5862 | 37.9605 | 37.6189 | 38.6961 | 36.7306 | 39.4993 | 37.2441 | 38.9545 | 39.6615 | 94.6855 | 95.1388 | 94.0317
2022-09-07 20:33 | 2:09 | 33.6529 | 31.8468 | 31.7569 | 36.5095 | 36.6185 | 34.6351 | 37.0557 | 33.8574 | 37.1026 | 35.652 | 35.861 | 38.5407 | 33.7932 | 35.1438 | 35.8796 | 34.3773 | 34.7487 | 35.362 | 34.9674 | 37.2395 | 34.0226 | 31.6035 | 35.072 | 36.7975 | 34.8864 | 39.0152 | 36.7071 | 35.3026 | 34.727 | 36.7244 | 34.7637 | 35.9421 | 34.9207 | 35.9192 | 34.8736 | 36.4674 | 36.046 | 36.4243 | 37.579 | 35.9695 | 37.0506 | 38.062 | 39.1902 | 37.448 | 38.6667 | 36.8448 | 38.9143 | 37.1889 | 38.8388 | 36.6924 | 38.0504 | 37.6992 | 38.946 | 36.7678 | 39.5251 | 37.3374 | 38.9747 | 39.5872 | 94.4198 | 94.8871 | 93.767
2022-09-07 20:34 | 2:10 | 34.2787 | 31.8408 | 32.0712 | 36.7341 | 36.6423 | 34.6925 | 37.2392 | 33.9094 | 37.1395 | 35.6427 | 35.8513 | 38.562 | 33.9264 | 35.1341 | 36.0132 | 34.4315 | 34.8545 | 35.3432 | 35.0358 | 37.3461 | 34.4104 | 31.6751 | 35.3191 | 36.9573 | 34.9686 | 39.1656 | 36.8295 | 35.2036 | 34.7486 | 36.7298 | 34.8907 | 35.9747 | 34.9843 | 35.9374 | 34.9647 | 36.4925 | 36.0842 | 36.4863 | 37.627 | 36.0184 | 37.0702 | 38.1499 | 39.1887 | 37.6016 | 38.8136 | 36.9174 | 39.0069 | 37.2854 | 38.9096 | 36.7799 | 38.1193 | 37.7805 | 38.9151 | 36.8487 | 39.6065 | 37.4288 | 39.0025 | 39.5984 | 94.2344 | 94.6437 | 93.6707
2022-09-07 20:34 | 2:10 | 34.6931 | 31.8738 | 32.4093 | 36.5822 | 36.6986 | 34.7188 | 37.1588 | 33.9868 | 37.1866 | 35.7148 | 35.9225 | 38.5192 | 33.9905 | 35.2519 | 36.0734 | 34.4877 | 34.8923 | 35.47 | 35.1048 | 37.3607 | 34.7144 | 31.7067 | 35.5328 | 36.9353 | 35.0825 | 39.2835 | 36.8621 | 35.3542 | 34.7908 | 36.8475 | 35.0333 | 35.9453 | 35.0983 | 36.0562 | 35.0737 | 36.5524 | 36.159 | 36.566 | 37.6522 | 36.0864 | 37.1289 | 38.1786 | 39.3097 | 37.6946 | 38.853 | 36.9666 | 39.0311 | 37.366 | 39.0217 | 36.8601 | 38.2266 | 37.8131 | 38.9088 | 36.8897 | 39.6088 | 37.4996 | 39.0733 | 39.649 | 94.0712 | 94.5109 | 93.6006
2022-09-07 20:34 | 2:10 | 35.0264 | 31.8651 | 32.7786 | 36.6927 | 36.7108 | 34.8826 | 37.2645 | 34.1831 | 37.2041 | 35.7794 | 36.0088 | 38.5678 | 34.0858 | 35.3437 | 36.1149 | 34.5381 | 34.9862 | 35.502 | 35.1988 | 37.4306 | 34.9154 | 31.73 | 35.7371 | 37.0994 | 35.1555 | 39.2729 | 36.9822 | 35.376 | 34.924 | 36.9647 | 35.1616 | 36.1355 | 35.1932 | 36.1635 | 35.1605 | 36.5801 | 36.1981 | 36.6277 | 37.6965 | 36.1703 | 37.1403 | 38.2393 | 39.3235 | 37.8107 | 38.9442 | 37.0275 | 39.0152 | 37.4805 | 39.0778 | 36.944 | 38.2908 | 37.9081 | 38.9577 | 36.9975 | 39.6174 | 37.5702 | 39.2083 | 39.691 | 93.9996 | 94.3896 | 93.512
2022-09-07 20:34 | 2:10 | 35.107 | 31.8638 | 32.9918 | 36.7888 | 36.7394 | 35.0076 | 37.251 | 34.2209 | 37.2422 | 35.8365 | 36.0265 | 38.6434 | 34.1294 | 35.3582 | 36.1946 | 34.6128 | 35.0549 | 35.5551 | 35.2561 | 37.441 | 34.9534 | 31.7505 | 35.8359 | 37.106 | 35.2487 | 39.3565 | 37.0506 | 35.5201 | 35.0847 | 37.1037 | 35.259 | 36.0626 | 35.299 | 36.2563 | 35.2429 | 36.6501 | 36.2824 | 36.685 | 37.8061 | 36.2165 | 37.1759 | 38.3469 | 39.3962 | 37.9054 | 39.0178 | 37.0829 | 39.1632 | 37.564 | 39.1522 | 37.0538 | 38.3481 | 37.9681 | 39.0369 | 37.0583 | 39.611 | 37.6507 | 39.3088 | 39.6917 | 93.9041 | 94.2673 | 93.4701
2022-09-07 20:34 | 2:10 | 35.1214 | 31.9011 | 33.0067 | 36.8712 | 36.7545 | 35.0769 | 37.2562 | 34.2552 | 37.2571 | 35.9288 | 36.1563 | 38.6987 | 34.2552 | 35.4455 | 36.1671 | 34.6371 | 35.1257 | 35.6594 | 35.3174 | 37.6301 | 34.9498 | 31.7696 | 35.9074 | 37.1739 | 35.3356 | 39.4243 | 37.0702 | 35.5782 | 35.0864 | 37.06 | 35.3578 | 36.1971 | 35.3619 | 36.326 | 35.3304 | 36.6787 | 36.3458 | 36.7274 | 37.7532 | 36.2844 | 37.2816 | 38.4162 | 39.4778 | 37.984 | 39.0791 | 37.1229 | 39.1642 | 37.6795 | 39.1802 | 37.1213 | 38.4301 | 38.0696 | 38.9803 | 37.1862 | 39.5877 | 37.7096 | 39.4293 | 39.6974 | 93.7966 | 94.1722 | 93.4339
2022-09-07 20:34 | 2:10 | 35.2197 | 31.925 | 33.0727 | 37.069 | 36.798 | 35.1438 | 37.3582 | 34.3775 | 37.2914 | 35.9056 | 36.2067 | 38.5847 | 34.3024 | 35.5061 | 36.2933 | 34.7209 | 35.1826 | 35.721 | 35.3662 | 37.5838 | 35.047 | 31.7829 | 36.0085 | 37.2393 | 35.3662 | 39.4684 | 37.1289 | 35.5991 | 35.237 | 37.1187 | 35.4523 | 36.1758 | 35.4278 | 36.3763 | 35.4099 | 36.7147 | 36.348 | 36.842 | 37.8438 | 36.3556 | 37.4068 | 38.4245 | 39.4653 | 38.0781 | 39.0899 | 37.2005 | 39.172 | 37.728 | 39.276 | 37.1838 | 38.47 | 38.0958 | 39.1101 | 37.2091 | 39.6883 | 37.7829 | 39.4413 | 39.7685 | 93.7524 | 94.1179 | 93.4444
2022-09-07 20:35 | 2:10 | 35.3915 | 31.9439 | 33.2123 | 37.0891 | 36.8057 | 35.228 | 37.459 | 34.4482 | 37.3407 | 35.9781 | 36.169 | 38.6097 | 34.4057 | 35.5294 | 36.432 | 34.7758 | 35.2417 | 35.7774 | 35.4263 | 37.6177 | 35.1013 | 31.8189 | 36.139 | 37.3604 | 35.4537 | 39.4625 | 37.1403 | 35.7616 | 35.2282 | 37.0928 | 35.5307 | 36.1901 | 35.5224 | 36.4359 | 35.5066 | 36.7535 | 36.4206 | 36.8975 | 37.814 | 36.4237 | 37.3582 | 38.4771 | 39.5222 | 38.1768 | 39.1914 | 37.236 | 39.2294 | 37.8066 | 39.392 | 37.2551 | 38.5471 | 38.1736 | 39.1505 | 37.3449 | 39.765 | 37.8463 | 39.5035 | 39.737 | 93.7552 | 94.0953 | 93.4348
2022-09-07 20:35 | 2:11 | 35.5463 | 31.9748 | 33.4022 | 37.1739 | 36.8374 | 35.2457 | 37.374 | 34.5228 | 37.3555 | 36.0247 | 36.1989 | 38.6943 | 34.4946 | 35.6138 | 36.4971 | 34.8445 | 35.2912 | 35.8394 | 35.4915 | 37.6625 | 35.2391 | 31.8759 | 36.2861 | 37.3987 | 35.544 | 39.4712 | 37.1759 | 35.813 | 35.2727 | 37.1775 | 35.6399 | 36.2483 | 35.6104 | 36.4817 | 35.5958 | 36.8439 | 36.5271 | 36.9223 | 37.8565 | 36.4692 | 37.5778 | 38.5918 | 39.548 | 38.2673 | 39.2808 | 37.2999 | 39.284 | 37.8979 | 39.3731 | 37.3082 | 38.6209 | 38.237 | 39.1691 | 37.2587 | 39.7541 | 37.9177 | 39.5827 | 39.7438 | 93.6885 | 94.0204 | 93.3713
2022-09-07 20:35 | 2:11 | 35.7664 | 32.0342 | 33.635 | 37.2186 | 36.8442 | 35.2916 | 37.4963 | 34.5759 | 37.4036 | 36.1018 | 36.3077 | 38.6983 | 34.6106 | 35.6509 | 36.5031 | 34.9258 | 35.3985 | 35.8877 | 35.5408 | 37.8169 | 35.493 | 31.9028 | 36.4657 | 37.4486 | 35.629 | 39.6117 | 37.2816 | 35.7968 | 35.3001 | 37.2409 | 35.7248 | 36.404 | 35.6987 | 36.5918 | 35.6917 | 36.8716 | 36.5645 | 36.9825 | 37.9363 | 36.5472 | 37.5998 | 38.5983 | 39.6271 | 38.3164 | 39.3217 | 37.3687 | 39.3778 | 37.9567 | 39.4711 | 37.4137 | 38.6577 | 38.3105 | 39.1373 | 37.2978 | 39.8498 | 38.0059 | 39.5226 | 39.8015 | 93.6348 | 93.989 | 93.3554
2022-09-07 20:35 | 2:11 | 36.1669 | 32.1065 | 33.9117 | 37.3063 | 36.9195 | 35.4779 | 37.5237 | 34.7222 | 37.4125 | 36.2225 | 36.4097 | 38.6632 | 34.7471 | 35.8006 | 36.5625 | 34.975 | 35.5213 | 36.0481 | 35.6029 | 37.8758 | 35.9145 | 31.9588 | 36.6402 | 37.5851 | 35.7149 | 39.7481 | 37.4068 | 35.8626 | 35.4064 | 37.3391 | 35.8573 | 36.4353 | 35.7761 | 36.6736 | 35.7863 | 36.9847 | 36.6335 | 37.0647 | 38.0038 | 36.6187 | 37.6543 | 38.6424 | 39.6626 | 38.4294 | 39.3505 | 37.4071 | 39.4097 | 38.0506 | 39.5365 | 37.4618 | 38.7272 | 38.3875 | 39.1688 | 37.3534 | 39.823 | 38.0651 | 39.5976 | 39.924 | 93.6543 | 93.9161 | 93.3781
2022-09-07 20:35 | 2:11 | 36.4249 | 32.1944 | 34.1138 | 37.5189 | 36.9826 | 35.5162 | 37.5845 | 34.7901 | 37.4617 | 36.3221 | 36.4897 | 38.7134 | 34.8809 | 35.8575 | 36.7548 | 35.0418 | 35.6243 | 36.1245 | 35.7373 | 37.8662 | 36.407 | 32.045 | 36.8708 | 37.7375 | 35.7625 | 39.8143 | 37.3582 | 35.8634 | 35.5152 | 37.4184 | 35.9478 | 36.3827 | 35.9019 | 36.7796 | 35.8431 | 37.0542 | 36.7 | 37.1564 | 38.0512 | 36.6911 | 37.7198 | 38.6753 | 39.7273 | 38.5011 | 39.4126 | 37.4639 | 39.4594 | 38.1255 | 39.5539 | 37.5306 | 38.7698 | 38.4471 | 39.2087 | 37.5179 | 39.8502 | 38.1192 | 39.6813 | 39.8925 | 93.5512 | 93.8748 | 93.3384
2022-09-07 20:35 | 2:11 | 36.5315 | 32.2934 | 34.2915 | 37.5584 | 37.0102 | 35.6582 | 37.5712 | 34.9119 | 37.5413 | 36.4095 | 36.6334 | 38.7655 | 35.04 | 35.9682 | 36.7988 | 35.1597 | 35.7815 | 36.2885 | 35.8065 | 38.0675 | 36.8088 | 32.2223 | 37.0865 | 37.7605 | 35.8833 | 39.8429 | 37.5778 | 35.986 | 35.7006 | 37.5149 | 36.0629 | 36.5035 | 36.0026 | 36.8424 | 35.9451 | 37.0989 | 36.7605 | 37.239 | 38.2237 | 36.7515 | 37.8029 | 38.7858 | 39.7854 | 38.561 | 39.5331 | 37.5363 | 39.5176 | 38.2145 | 39.6974 | 37.5917 | 38.8356 | 38.5112 | 39.3452 | 37.4933 | 39.9254 | 38.2018 | 39.7097 | 39.9485 | 93.4771 | 93.7702 | 93.2293
2022-09-07 20:36 | 2:11 | 36.5472 | 32.4812 | 34.5269 | 37.7019 | 37.073 | 35.8566 | 37.6651 | 35.0873 | 37.5459 | 36.5053 | 36.6835 | 38.8791 | 35.1276 | 36.0653 | 36.8449 | 35.2597 | 35.8243 | 36.3345 | 35.8944 | 38.0989 | 37.1656 | 32.472 | 37.309 | 37.9181 | 35.9936 | 39.9504 | 37.5998 | 36.078 | 35.7667 | 37.5919 | 36.1861 | 36.5667 | 36.1121 | 36.9414 | 36.0476 | 37.1556 | 36.8854 | 37.3183 | 38.2155 | 36.8528 | 37.8306 | 38.8892 | 39.8322 | 38.6528 | 39.5366 | 37.6235 | 39.5453 | 38.3032 | 39.6997 | 37.6294 | 38.8864 | 38.5588 | 39.4346 | 37.6438 | 39.9529 | 38.2851 | 39.7551 | 39.9763 | 93.4066 | 93.6695 | 93.1997
2022-09-07 20:36 | 2:12 | 36.5261 | 32.6657 | 34.8192 | 37.9347 | 37.1546 | 35.9858 | 37.7708 | 35.1971 | 37.6269 | 36.5678 | 36.7763 | 38.916 | 35.2863 | 36.2008 | 37.0037 | 35.3492 | 35.9653 | 36.4415 | 36.0112 | 38.2214 | 37.4804 | 32.8755 | 37.5202 | 38.067 | 36.1127 | 39.9244 | 37.6543 | 36.186 | 35.9901 | 37.7415 | 36.3046 | 36.6481 | 36.2416 | 37.0123 | 36.1795 | 37.2337 | 36.9414 | 37.3952 | 38.2192 | 36.9388 | 37.8963 | 38.9431 | 39.8633 | 38.7501 | 39.5856 | 37.6479 | 39.6328 | 38.3692 | 39.7472 | 37.7476 | 38.9328 | 38.6155 | 39.509 | 37.7903 | 39.9595 | 38.3364 | 39.7777 | 40.0011 | 93.3621 | 93.5875 | 93.2024
2022-09-07 20:36 | 2:12 | 36.2296 | 32.7752 | 35.1473 | 37.9821 | 37.1825 | 36.0562 | 37.7829 | 35.3383 | 37.6674 | 36.6312 | 36.8916 | 38.8383 | 35.4136 | 36.3025 | 36.9893 | 35.3752 | 36.0669 | 36.5685 | 36.1212 | 38.3575 | 37.7426 | 33.4034 | 37.7017 | 38.0343 | 36.2173 | 40.0003 | 37.7198 | 36.2739 | 35.9955 | 37.7507 | 36.4257 | 36.7791 | 36.3525 | 37.1173 | 36.2835 | 37.3088 | 37.0142 | 37.4694 | 38.2611 | 37.0102 | 37.9903 | 39.0059 | 39.9392 | 38.829 | 39.699 | 37.713 | 39.6686 | 38.4497 | 39.7912 | 37.7918 | 39.0441 | 38.7001 | 39.4486 | 37.806 | 40.0549 | 38.429 | 39.8335 | 40.1076 | 93.2793 | 93.5095 | 93.0678
2022-09-07 20:36 | 2:12 | 35.577 | 32.9486 | 35.4161 | 38.1634 | 37.2346 | 36.1706 | 37.8145 | 35.4668 | 37.7167 | 36.795 | 36.9499 | 38.9155 | 35.577 | 36.4137 | 37.1157 | 35.489 | 36.1902 | 36.6888 | 36.208 | 38.4046 | 37.9572 | 34.0666 | 37.8723 | 38.1955 | 36.3268 | 39.975 | 37.8029 | 36.3305 | 36.1366 | 37.7828 | 36.5428 | 36.7568 | 36.4529 | 37.1778 | 36.3978 | 37.3872 | 37.0738 | 37.5573 | 38.3714 | 37.1016 | 38.0416 | 39.0821 | 40.0038 | 38.9082 | 39.7023 | 37.7737 | 39.7038 | 38.5379 | 39.888 | 37.8768 | 39.1006 | 38.7628 | 39.4466 | 37.9089 | 40.1056 | 38.5065 | 39.8471 | 40.1203 | 93.1926 | 93.41 | 93.0204
2022-09-07 20:36 | 2:12 | 35.2037 | 33.1745 | 35.6752 | 38.3245 | 37.2887 | 36.2968 | 37.8855 | 35.6441 | 37.7691 | 36.852 | 37.0827 | 39.0577 | 35.68 | 36.5106 | 37.1782 | 35.6226 | 36.2998 | 36.7176 | 36.278 | 38.5304 | 38.1583 | 34.6238 | 38.0446 | 38.284 | 36.3746 | 40.1804 | 37.8306 | 36.4133 | 36.1754 | 37.9686 | 36.6542 | 36.8579 | 36.55 | 37.2885 | 36.4546 | 37.4506 | 37.1761 | 37.6669 | 38.3379 | 37.1866 | 38.0788 | 39.1036 | 40.0301 | 38.9802 | 39.7763 | 37.8122 | 39.7246 | 38.6361 | 39.9021 | 37.9002 | 39.1962 | 38.8112 | 39.6472 | 37.9599 | 40.1055 | 38.5883 | 39.9102 | 40.2153 | 93.143 | 93.3173 | 93.0309
2022-09-07 20:36 | 2:12 | 35.0543 | 33.5895 | 35.94 | 38.3553 | 37.3594 | 36.4416 | 37.9325 | 35.78 | 37.8276 | 36.9452 | 37.2189 | 39.0591 | 35.816 | 36.5793 | 37.3579 | 35.6767 | 36.3938 | 36.819 | 36.3883 | 38.5514 | 38.3234 | 35.1471 | 38.1819 | 38.3252 | 36.4504 | 40.1006 | 37.8963 | 36.6324 | 36.3331 | 37.9582 | 36.7585 | 37.0812 | 36.6812 | 37.3951 | 36.57 | 37.5352 | 37.2447 | 37.7859 | 38.391 | 37.2609 | 38.1515 | 39.1632 | 40.0719 | 39.081 | 39.8203 | 37.9138 | 39.8091 | 38.6916 | 39.981 | 38.0259 | 39.2199 | 38.9062 | 39.7041 | 38.1316 | 40.1534 | 38.6493 | 39.9347 | 40.2428 | 93.0397 | 93.1903 | 93.0052
2022-09-07 20:37 | 2:12 | 35.2542 | 34.0735 | 36.1527 | 38.5688 | 37.4129 | 36.5245 | 37.9881 | 35.8726 | 37.8839 | 37.0313 | 37.3015 | 39.0852 | 35.9702 | 36.6808 | 37.388 | 35.806 | 36.5094 | 36.9182 | 36.4568 | 38.6169 | 38.4535 | 35.5709 | 38.3239 | 38.4224 | 36.5937 | 40.303 | 37.9903 | 36.7361 | 36.3935 | 37.9752 | 36.8769 | 37.1367 | 36.7829 | 37.4658 | 36.6945 | 37.6181 | 37.3435 | 37.837 | 38.4188 | 37.3637 | 38.2635 | 39.2624 | 40.1373 | 39.1417 | 39.9064 | 38.0071 | 39.8517 | 38.7728 | 40.0487 | 38.1224 | 39.3087 | 38.9776 | 39.7849 | 38.1622 | 40.1816 | 38.7279 | 40.0641 | 40.3355 | 92.9389 | 93.1027 | 92.9036
2022-09-07 20:37 | 2:13 | 35.3188 | 34.6117 | 36.3659 | 38.6262 | 37.5025 | 36.6459 | 38.0151 | 35.994 | 37.953 | 37.0915 | 37.5095 | 39.1902 | 36.1041 | 36.8377 | 37.5194 | 35.8855 | 36.6481 | 37.0501 | 36.6316 | 38.6428 | 38.6239 | 35.9617 | 38.4743 | 38.5384 | 36.6517 | 40.4917 | 38.0416 | 36.7395 | 36.4223 | 38.1559 | 36.9839 | 37.1347 | 36.8528 | 37.6041 | 36.8174 | 37.6789 | 37.4247 | 37.9378 | 38.4942 | 37.4577 | 38.3482 | 39.3487 | 40.1755 | 39.2294 | 40.0047 | 38.0322 | 39.961 | 38.8428 | 40.1166 | 38.1685 | 39.3592 | 39.0347 | 39.783 | 38.2211 | 40.2826 | 38.7905 | 40.1 | 40.3701 | 92.7715 | 92.9739 | 92.7457
2022-09-07 20:37 | 2:13 | 35.3881 | 34.9689 | 36.5682 | 38.745 | 37.558 | 36.789 | 38.1273 | 36.1215 | 38.0192 | 37.2205 | 37.5986 | 39.2466 | 36.239 | 36.9084 | 37.6406 | 35.9774 | 36.7609 | 37.1464 | 36.6543 | 38.7842 | 38.8026 | 36.3121 | 38.6114 | 38.6192 | 36.7991 | 40.3454 | 38.0788 | 36.847 | 36.5444 | 38.2306 | 37.073 | 37.2433 | 36.9647 | 37.6831 | 36.9357 | 37.7653 | 37.5055 | 38.0215 | 38.541 | 37.5212 | 38.4442 | 39.4204 | 40.224 | 39.3387 | 40.081 | 38.1434 | 40.0117 | 38.9289 | 40.195 | 38.2327 | 39.4111 | 39.1028 | 39.9112 | 38.2858 | 40.3366 | 38.8668 | 40.1884 | 40.4182 | 92.668 | 92.8519 | 92.6389
2022-09-07 20:37 | 2:13 | 35.5295 | 35.2582 | 36.7643 | 38.8825 | 37.6132 | 36.872 | 38.2163 | 36.2604 | 38.083 | 37.3655 | 37.6395 | 39.2576 | 36.4016 | 37.0243 | 37.661 | 36.1104 | 36.8897 | 37.2382 | 36.8061 | 38.9616 | 38.9243 | 36.5692 | 38.7211 | 38.7854 | 36.9694 | 40.5593 | 38.1515 | 36.8676 | 36.6871 | 38.2567 | 37.1955 | 37.2714 | 37.1045 | 37.7828 | 37.0434 | 37.8522 | 37.5553 | 38.0759 | 38.6031 | 37.6025 | 38.4972 | 39.515 | 40.2582 | 39.4402 | 40.1575 | 38.1702 | 40.0791 | 39.0367 | 40.2578 | 38.3172 | 39.4892 | 39.1663 | 39.9353 | 38.3506 | 40.3453 | 38.9311 | 40.2076 | 40.4324 | 92.5268 | 92.6867 | 92.459
2022-09-07 20:37 | 2:13 | 35.817 | 35.5687 | 36.9341 | 38.8802 | 37.695 | 37.0031 | 38.3113 | 36.3914 | 38.1386 | 37.4139 | 37.7876 | 39.2978 | 36.5093 | 37.1047 | 37.7544 | 36.1774 | 36.9587 | 37.3456 | 36.8997 | 38.9471 | 39.0654 | 36.7949 | 38.838 | 38.8058 | 36.9899 | 40.5521 | 38.2635 | 36.9258 | 36.7934 | 38.3199 | 37.2903 | 37.3197 | 37.2185 | 37.8564 | 37.158 | 37.9898 | 37.68 | 38.2002 | 38.6525 | 37.6986 | 38.5896 | 39.5592 | 40.3353 | 39.5123 | 40.1361 | 38.2832 | 40.1362 | 39.1234 | 40.3424 | 38.3824 | 39.5569 | 39.2607 | 39.9582 | 38.4985 | 40.4256 | 39.0013 | 40.2238 | 40.4729 | 92.3989 | 92.5596 | 92.3871
2022-09-07 20:37 | 2:13 | 35.9192 | 35.6985 | 37.1188 | 39.0518 | 37.7634 | 37.2032 | 38.3829 | 36.4862 | 38.2068 | 37.5005 | 37.8963 | 39.3074 | 36.6321 | 37.2347 | 37.8019 | 36.3106 | 37.1243 | 37.3895 | 36.9552 | 39.014 | 39.1871 | 37.0268 | 38.9644 | 38.9038 | 37.0791 | 40.6861 | 38.3482 | 37.0229 | 36.9704 | 38.4594 | 37.4045 | 37.4801 | 37.2954 | 37.9577 | 37.2583 | 38.0205 | 37.7096 | 38.268 | 38.7002 | 37.7932 | 38.6382 | 39.6285 | 40.3779 | 39.5882 | 40.2051 | 38.3274 | 40.2099 | 39.192 | 40.3605 | 38.4317 | 39.6521 | 39.3142 | 39.9808 | 38.5712 | 40.5085 | 39.0978 | 40.3029 | 40.5431 | 92.2993 | 92.4768 | 92.3632
2022-09-07 20:38 | 2:13 | 36.0733 | 35.7731 | 37.2879 | 39.1905 | 37.8467 | 37.2793 | 38.465 | 36.6788 | 38.2687 | 37.6041 | 38.0022 | 39.3761 | 36.7841 | 37.313 | 37.9614 | 36.4118 | 37.1773 | 37.4673 | 37.0582 | 39.044 | 39.3056 | 37.2255 | 39.0551 | 38.9918 | 37.2292 | 40.6267 | 38.4442 | 37.1583 | 36.9828 | 38.4752 | 37.4986 | 37.5382 | 37.4192 | 38.0416 | 37.3607 | 38.1336 | 37.83 | 38.3391 | 38.7738 | 37.8463 | 38.6327 | 39.7078 | 40.4494 | 39.6852 | 40.2433 | 38.3931 | 40.1776 | 39.2709 | 40.4122 | 38.5054 | 39.6947 | 39.4002 | 40.0295 | 38.6415 | 40.5239 | 39.1835 | 40.3289 | 40.5755 | 92.1787 | 92.3509 | 92.3346
2022-09-07 20:38 | 2:14 | 36.2689 | 35.8956 | 37.4108 | 39.189 | 37.9248 | 37.3957 | 38.4729 | 36.8125 | 38.352 | 37.7398 | 38.1377 | 39.4693 | 36.8748 | 37.4652 | 38.0914 | 36.5068 | 37.3287 | 37.6656 | 37.1949 | 39.1886 | 39.4106 | 37.3765 | 39.1806 | 39.0951 | 37.3335 | 40.6607 | 38.4972 | 37.2521 | 37.0789 | 38.596 | 37.5942 | 37.6183 | 37.5275 | 38.1025 | 37.465 | 38.1882 | 37.8948 | 38.4113 | 38.8704 | 37.9554 | 38.6084 | 39.7557 | 40.4829 | 39.7392 | 40.2955 | 38.4981 | 40.2824 | 39.3556 | 40.4747 | 38.5898 | 39.7617 | 39.4768 | 40.0857 | 38.6929 | 40.5012 | 39.2405 | 40.4582 | 40.6001 | 92.064 | 92.1997 | 92.1351
2022-09-07 20:38 | 2:14 | 36.3297 | 36.0511 | 37.5537 | 39.3229 | 37.9989 | 37.4713 | 38.5505 | 36.9439 | 38.4227 | 37.869 | 38.1646 | 39.4545 | 36.9796 | 37.5451 | 38.1562 | 36.5808 | 37.4104 | 37.72 | 37.2413 | 39.2566 | 39.5492 | 37.5331 | 39.2866 | 39.1885 | 37.4425 | 40.7625 | 38.5896 | 37.2777 | 37.2554 | 38.6501 | 37.6898 | 37.683 | 37.6756 | 38.1987 | 37.6059 | 38.2365 | 37.9878 | 38.5095 | 38.9459 | 38.0648 | 38.3378 | 39.8265 | 40.5421 | 39.8387 | 40.4106 | 38.5446 | 40.31 | 39.4353 | 40.519 | 38.6481 | 39.839 | 39.5246 | 40.1274 | 38.8362 | 40.6008 | 39.2964 | 40.4927 | 40.7086 | 91.9212 | 92.0838 | 92.0953
2022-09-07 20:38 | 2:14 | 36.5943 | 36.2285 | 37.7181 | 39.3975 | 38.0597 | 37.5422 | 38.6474 | 37.0798 | 38.509 | 37.9132 | 38.3422 | 39.5908 | 37.1375 | 37.6732 | 38.221 | 36.7261 | 37.5292 | 37.8337 | 37.3787 | 39.3561 | 39.6149 | 37.6731 | 39.3738 | 39.2701 | 37.5824 | 40.8471 | 38.6382 | 37.4036 | 37.3567 | 38.8002 | 37.7806 | 37.835 | 37.7887 | 38.2749 | 37.6867 | 38.2933 | 38.0748 | 38.5801 | 39.0341 | 38.1491 | 38.1791 | 39.8632 | 40.583 | 39.9279 | 40.445 | 38.6074 | 40.3798 | 39.5092 | 40.5953 | 38.7589 | 39.8715 | 39.5998 | 40.249 | 38.9324 | 40.5915 | 39.3894 | 40.5801 | 40.7493 | 91.9423 | 92.0666 | 92.1309
2022-09-07 20:38 | 2:14 | 36.7699 | 36.3336 | 37.4445 | 39.5628 | 38.1607 | 37.6626 | 38.7213 | 37.188 | 38.5734 | 37.9796 | 38.4372 | 39.6446 | 37.218 | 37.721 | 38.3069 | 36.779 | 37.6266 | 37.8693 | 37.4997 | 39.4528 | 36.8056 | 36.8623 | 38.6241 | 39.373 | 37.565 | 40.8879 | 38.6327 | 37.4549 | 37.4449 | 38.7203 | 37.6502 | 37.8525 | 37.7965 | 38.3385 | 37.7329 | 38.3602 | 38.1588 | 38.6305 | 39.038 | 38.2025 | 38.0411 | 39.918 | 40.5552 | 39.8917 | 40.4376 | 38.6615 | 40.439 | 39.4607 | 40.5954 | 38.7627 | 39.8653 | 39.6238 | 40.3224 | 38.9007 | 40.6398 | 39.3472 | 40.6403 | 40.8276 | 92.0795 | 92.1577 | 92.3336
2022-09-07 20:38 | 2:14 | 33.1346 | 31.415 | 34.6851 | 39.3265 | 38.2295 | 37.4655 | 38.7052 | 37.0005 | 38.6161 | 37.993 | 38.3439 | 39.7256 | 36.9452 | 37.4855 | 38.2315 | 36.7961 | 37.58 | 37.5975 | 37.3604 | 39.3349 | 34.5994 | 31.5525 | 37.2544 | 39.249 | 37.4311 | 40.6116 | 38.6084 | 37.2991 | 37.3261 | 38.4594 | 37.1399 | 37.807 | 37.5065 | 38.1299 | 37.5699 | 38.2933 | 38.1004 | 38.4185 | 39.0412 | 38.134 | 37.9796 | 39.775 | 40.429 | 39.5677 | 40.1983 | 38.6305 | 40.3387 | 39.1507 | 40.5148 | 38.6305 | 39.6161 | 39.4398 | 40.2348 | 38.8541 | 40.6439 | 39.1244 | 40.5295 | 40.8615 | 92.1557 | 92.2124 | 92.3325
2022-09-07 20:39 | 2:15 | 29.3731 | 29.8252 | 32.3236 | 38.6944 | 38.2276 | 37.1001 | 38.5871 | 36.6301 | 38.6021 | 37.5379 | 38.191 | 39.6611 | 36.5042 | 37.2479 | 38.1616 | 36.6534 | 37.3123 | 37.3012 | 37.1264 | 39.127 | 33.5056 | 29.499 | 35.1103 | 39.0113 | 37.1332 | 40.4093 | 38.3378 | 37.2087 | 36.9767 | 38.2322 | 36.4695 | 37.787 | 37.2498 | 37.8553 | 37.2488 | 38.1351 | 37.9752 | 38.2563 | 38.8449 | 37.9812 | 37.934 | 39.5126 | 40.2077 | 39.0728 | 39.8745 | 38.5075 | 40.1923 | 38.6436 | 40.0757 | 38.2608 | 39.2719 | 39.1693 | 40.0166 | 38.6071 | 40.5187 | 38.8057 | 40.1662 | 40.7946 | 92.2004 | 92.3198 | 92.3112
2022-09-07 20:39 | 2:15 | 30.5824 | 30.016 | 31.832 | 38.2747 | 38.2834 | 36.9915 | 38.5635 | 36.4936 | 38.5883 | 37.4504 | 38.1528 | 39.6673 | 36.3524 | 37.1184 | 37.9552 | 36.5721 | 37.1453 | 37.1086 | 37.0377 | 38.8329 | 31.852 | 28.7783 | 33.8244 | 38.8287 | 36.8868 | 40.1366 | 38.1791 | 37.0568 | 36.6582 | 38.0316 | 36.0327 | 37.6659 | 37.0319 | 37.5273 | 36.9871 | 37.967 | 37.8808 | 38.0098 | 38.7158 | 37.7756 | 37.8433 | 39.3415 | 40.0779 | 38.6283 | 39.6293 | 38.375 | 40.0202 | 38.3715 | 39.9064 | 38.0472 | 39.1116 | 39.0092 | 39.8671 | 38.4141 | 40.4215 | 38.6296 | 39.8982 | 40.7191 | 92.2283 | 92.4253 | 92.3351
2022-09-07 20:39 | 2:15 | 28.1629 | 30.2821 | 30.9767 | 38.0406 | 38.3055 | 36.9235 | 38.558 | 36.3892 | 38.6401 | 37.3714 | 38.0817 | 39.7531 | 36.2148 | 37.0145 | 37.8437 | 36.4881 | 36.9986 | 36.9864 | 37.004 | 38.9363 | 27.9288 | 28.2059 | 32.8826 | 38.5145 | 36.8128 | 39.8665 | 38.0411 | 36.8699 | 36.5888 | 37.8385 | 35.6624 | 37.7657 | 36.8883 | 37.3346 | 36.7388 | 37.8292 | 37.7357 | 37.9177 | 38.6826 | 37.67 | 37.7787 | 39.2496 | 39.9542 | 38.3409 | 39.4519 | 38.289 | 39.9432 | 38.2285 | 39.6673 | 37.8629 | 39.0822 | 38.9168 | 39.7976 | 38.3488 | 40.3526 | 38.5012 | 39.8481 | 40.6472 | 92.344 | 92.5461 | 92.4222
2022-09-07 20:39 | 2:15 | 27.9049 | 30.0909 | 30.7541 | 37.8857 | 38.3579 | 36.7897 | 38.5212 | 36.4249 | 38.6252 | 37.2938 | 38.0129 | 39.8424 | 36.0991 | 36.9359 | 37.9001 | 36.4341 | 36.889 | 36.9425 | 36.7937 | 38.8387 | 27.0713 | 27.6722 | 32.3071 | 38.3415 | 36.6717 | 39.5898 | 37.9796 | 36.9064 | 36.4883 | 37.7619 | 35.4377 | 37.636 | 36.8207 | 37.1971 | 36.5157 | 37.6825 | 37.7072 | 37.8195 | 38.5818 | 37.596 | 37.7224 | 39.1333 | 39.8068 | 38.1656 | 39.3928 | 38.1862 | 39.9016 | 38.0215 | 39.5293 | 37.7668 | 38.9214 | 38.8431 | 39.7296 | 38.2616 | 40.3226 | 38.4185 | 39.6889 | 40.6861 | 92.476 | 92.665 | 92.531
2022-09-07 20:39 | 2:15 | 28.8751 | 29.9997 | 31.1375 | 37.8766 | 38.4412 | 36.6807 | 38.5882 | 36.2804 | 38.6655 | 37.2814 | 37.8685 | 39.8072 | 36.0645 | 36.912 | 37.8604 | 36.3981 | 36.8773 | 36.8522 | 36.7515 | 38.7681 | 26.7155 | 27.2304 | 31.9295 | 38.2194 | 36.6152 | 39.5322 | 37.934 | 36.9517 | 36.4331 | 37.6787 | 35.2403 | 37.7182 | 36.7696 | 37.0657 | 36.5155 | 37.6324 | 37.6874 | 37.7168 | 38.5644 | 37.5505 | 37.7041 | 39.1293 | 39.8646 | 38.0819 | 39.2642 | 38.1592 | 39.922 | 37.8508 | 39.4467 | 37.7458 | 38.98 | 38.7981 | 39.7595 | 38.1925 | 40.1949 | 38.3604 | 39.8256 | 40.5902 | 92.6091 | 92.7937 | 92.587
2022-09-07 20:39 | 2:15 | 30.3331 | 29.7007 | 31.7193 | 37.7776 | 38.4852 | 36.6759 | 38.5846 | 36.2563 | 38.7054 | 37.379 | 37.953 | 39.8108 | 36.0045 | 36.9189 | 37.938 | 36.3815 | 36.8507 | 36.8568 | 36.797 | 38.7283 | 26.4476 | 26.7942 | 31.6383 | 38.0966 | 36.525 | 39.4173 | 37.8433 | 36.8968 | 36.4265 | 37.6578 | 35.0351 | 37.6394 | 36.7755 | 37.0095 | 36.2843 | 37.5947 | 37.6346 | 37.7063 | 38.537 | 37.5095 | 37.6449 | 38.9942 | 39.7876 | 37.9806 | 39.2037 | 38.1529 | 39.8771 | 37.7308 | 39.3163 | 37.7162 | 38.7752 | 38.7161 | 39.6847 | 38.2729 | 40.2382 | 38.2668 | 39.5992 | 40.5611 | 92.6598 | 92.8897 | 92.6913
2022-09-07 20:40 | 2:15 | 30.9329 | 29.0821 | 31.8394 | 37.9502 | 38.5571 | 36.688 | 38.6933 | 36.2981 | 38.7556 | 37.3572 | 38.1093 | 39.8054 | 36.0336 | 36.8955 | 37.9018 | 36.3839 | 36.8302 | 36.9136 | 36.8271 | 38.7013 | 26.196 | 26.3856 | 31.3666 | 38.0273 | 36.5204 | 39.3671 | 37.7787 | 36.9328 | 36.3676 | 37.6115 | 34.8627 | 37.6467 | 36.736 | 36.9185 | 36.2615 | 37.601 | 37.5543 | 37.6333 | 38.5166 | 37.4153 | 37.6078 | 38.8702 | 39.6582 | 37.8806 | 39.0559 | 38.153 | 39.8269 | 37.6475 | 39.3506 | 37.6762 | 38.9415 | 38.6186 | 39.7318 | 38.2202 | 40.261 | 38.212 | 39.5735 | 40.8038 | 92.7658 | 92.9901 | 92.6828
2022-09-07 20:40 | 2:16 | 31.1066 | 28.5564 | 31.7375 | 37.856 | 38.6244 | 36.7502 | 38.7077 | 36.2379 | 38.7689 | 37.3055 | 37.9124 | 39.8723 | 35.9507 | 36.9883 | 37.7533 | 36.4128 | 36.8393 | 36.8974 | 36.8907 | 38.7293 | 26.1458 | 26.0021 | 31.1397 | 37.9092 | 36.4554 | 39.3085 | 37.7224 | 36.9596 | 36.3342 | 37.5836 | 34.7621 | 37.7778 | 36.7658 | 36.8846 | 36.0697 | 37.6347 | 37.7058 | 37.63 | 38.6198 | 37.4966 | 37.5587 | 38.7998 | 39.6508 | 37.7927 | 39.0157 | 38.1519 | 39.749 | 37.5374 | 39.3623 | 37.5762 | 38.9562 | 38.4532 | 39.6129 | 38.1759 | 40.2265 | 38.1179 | 39.4945 | 40.7249 | 92.8344 | 93.083 | 92.8162
2022-09-07 20:40 | 2:16 | 31.0881 | 28.3718 | 31.537 | 37.8026 | 38.6825 | 36.5504 | 38.6228 | 36.1475 | 38.7715 | 37.2118 | 38.0789 | 39.8811 | 35.9506 | 36.8823 | 37.8748 | 36.4205 | 36.8574 | 36.9091 | 36.8868 | 38.682 | 26.4532 | 25.851 | 30.9561 | 37.9036 | 36.4196 | 39.153 | 37.7041 | 37.0044 | 36.3109 | 37.5339 | 34.708 | 37.5091 | 36.6888 | 36.8783 | 36.0574 | 37.5375 | 37.6 | 37.6285 | 38.6522 | 37.3973 | 37.5194 | 38.7758 | 39.6369 | 37.6709 | 38.9105 | 38.1121 | 39.6891 | 37.4881 | 39.2663 | 37.5367 | 38.6759 | 38.3293 | 39.6502 | 38.1369 | 40.1223 | 38.0559 | 39.4141 | 40.7085 | 92.9473 | 93.2098 | 92.8383
2022-09-07 20:40 | 2:16 | 30.8716 | 28.2145 | 31.2049 | 37.6651 | 38.7516 | 36.5434 | 38.6396 | 36.0538 | 38.7958 | 37.2131 | 38.1549 | 39.875 | 35.8865 | 36.8083 | 37.858 | 36.4313 | 36.7778 | 36.8287 | 36.8789 | 38.5714 | 26.5942 | 25.7335 | 30.7843 | 37.8072 | 36.3815 | 39.1893 | 37.6449 | 36.8524 | 36.2667 | 37.5182 | 34.6246 | 37.5486 | 36.68 | 36.849 | 35.9092 | 37.6095 | 37.6365 | 37.5939 | 38.6568 | 37.3835 | 37.3959 | 38.6757 | 39.5626 | 37.569 | 38.9054 | 38.1015 | 39.7106 | 37.3844 | 39.1775 | 37.4518 | 38.8678 | 38.3485 | 39.6781 | 38.1368 | 40.0129 | 37.9977 | 39.3213 | 40.5366 | 93.1006 | 93.3611 | 92.9833
2022-09-07 20:40 | 2:16 | 30.5785 | 28.12 | 30.9441 | 37.6382 | 38.8214 | 36.4335 | 38.6881 | 36.102 | 38.8355 | 37.2518 | 38.0353 | 39.9059 | 35.8045 | 36.7843 | 37.7793 | 36.4506 | 36.7537 | 36.8366 | 36.8559 | 38.4832 | 26.5041 | 25.5481 | 30.6053 | 37.703 | 36.3144 | 39.1441 | 37.6078 | 36.998 | 36.1983 | 37.4603 | 34.5512 | 37.6234 | 36.6365 | 36.8074 | 35.8282 | 37.4999 | 37.6679 | 37.5275 | 38.5715 | 37.4061 | 37.3699 | 38.6529 | 39.4896 | 37.5351 | 38.9107 | 38.0382 | 39.6307 | 37.2821 | 39.0478 | 37.3646 | 39.1145 | 38.3139 | 39.6135 | 38.0254 | 40.0136 | 37.8968 | 39.3471 | 40.635 | 93.2578 | 93.5093 | 93.0537
2022-09-07 20:40 | 2:16 | 30.311 | 27.9916 | 30.5964 | 37.492 | 38.8624 | 36.5067 | 38.6651 | 36.0167 | 38.8683 | 37.1505 | 37.9005 | 39.957 | 35.791 | 36.7532 | 37.8152 | 36.467 | 36.7153 | 36.7798 | 36.913 | 38.3745 | 25.5916 | 25.3062 | 30.4073 | 37.6035 | 36.2466 | 39.0194 | 37.5587 | 37.0138 | 36.1986 | 37.44 | 34.3757 | 37.5721 | 36.5641 | 36.7573 | 35.7303 | 37.4246 | 37.5043 | 37.5319 | 38.5056 | 37.2831 | 37.3535 | 38.6281 | 39.505 | 37.4791 | 38.779 | 38.0009 | 39.672 | 37.151 | 39.0727 | 37.3742 | 38.6596 | 38.2233 | 39.4747 | 38.0357 | 39.708 | 37.8427 | 39.3045 | 40.7166 | 93.3747 | 93.6593 | 93.164
2022-09-07 20:41 | 2:17 | 29.7374 | 27.8459 | 30.1456 | 37.3923 | 38.9041 | 36.3266 | 38.6777 | 35.9019 | 38.865 | 37.0608 | 37.8894 | 39.8897 | 35.6651 | 36.7751 | 37.8344 | 36.467 | 36.6582 | 36.7663 | 36.843 | 38.5274 | 25.3695 | 25.0599 | 30.2081 | 37.6066 | 36.2096 | 38.9101 | 37.5194 | 36.858 | 36.1569 | 37.3792 | 34.2474 | 37.6477 | 36.527 | 36.6462 | 35.7253 | 37.5019 | 37.6197 | 37.3893 | 38.5744 | 37.3275 | 37.2802 | 38.5329 | 39.4352 | 37.3429 | 38.6617 | 37.9302 | 39.5867 | 37.0247 | 38.9458 | 37.3364 | 38.8049 | 38.1953 | 39.3692 | 38.0791 | 39.8359 | 37.8062 | 39.1516 | 40.6853 | 93.5123 | 93.8096 | 93.2731
2022-09-07 20:41 | 2:17 | 27.8809 | 27.7154 | 29.6302 | 37.3212 | 38.9141 | 36.1607 | 38.6728 | 35.8938 | 38.8687 | 37.0578 | 37.9122 | 39.9154 | 35.5962 | 36.6801 | 37.7875 | 36.4544 | 36.5882 | 36.6357 | 36.8558 | 38.4521 | 25.6504 | 24.8539 | 30.1506 | 37.394 | 36.1016 | 38.9231 | 37.3959 | 36.7777 | 36.1343 | 37.3177 | 34.2136 | 37.4801 | 36.523 | 36.5893 | 35.7373 | 37.4192 | 37.6597 | 37.3254 | 38.672 | 37.3572 | 37.1859 | 38.384 | 39.3451 | 37.3604 | 38.6282 | 37.8929 | 39.5693 | 36.9107 | 38.8818 | 37.2464 | 38.6481 | 38.1802 | 39.2988 | 37.9016 | 39.9593 | 37.7237 | 39.0666 | 40.6214 | 93.6822 | 93.9762 | 93.4166
2022-09-07 20:41 | 2:17 | 25.8405 | 27.379 | 29.0625 | 37.1812 | 38.9362 | 36.1798 | 38.6383 | 35.754 | 38.869 | 37.043 | 37.6965 | 39.8721 | 35.5288 | 36.6694 | 37.6769 | 36.4205 | 36.4678 | 36.5947 | 36.765 | 38.4489 | 25.868 | 24.6198 | 30.013 | 37.3293 | 36.0645 | 38.8949 | 37.3699 | 36.6388 | 36.1179 | 37.1572 | 34.1556 | 37.4994 | 36.461 | 36.5373 | 35.5343 | 37.3612 | 37.4004 | 37.2797 | 38.6387 | 37.204 | 37.126 | 38.3506 | 39.3174 | 37.1199 | 38.611 | 37.8681 | 39.341 | 36.8129 | 38.8875 | 37.1944 | 38.4311 | 38.1105 | 39.3595 | 37.8533 | 39.8281 | 37.5614 | 38.9742 | 40.5773 | 93.8391 | 94.1913 | 93.5558
2022-09-07 20:41 | 2:17 | 25.3673 | 27.0504 | 28.7239 | 36.9595 | 38.9546 | 36.031 | 38.6057 | 35.7055 | 38.8716 | 37.0016 | 37.8054 | 39.8879 | 35.4085 | 36.6115 | 37.7263 | 36.4092 | 36.4406 | 36.4483 | 36.7193 | 38.2981 | 25.961 | 24.4181 | 29.8953 | 37.2721 | 35.9977 | 38.7343 | 37.3535 | 36.5576 | 36.0136 | 37.1643 | 33.9416 | 37.5838 | 36.411 | 36.376 | 35.4777 | 37.3669 | 37.5262 | 37.1762 | 38.6328 | 37.1196 | 37.0309 | 38.3088 | 39.3226 | 37.1221 | 38.534 | 37.8085 | 39.4509 | 36.723 | 38.9535 | 37.0977 | 38.6684 | 38.041 | 39.1834 | 37.7265 | 39.6814 | 37.5144 | 39.0066 | 40.5992 | 93.9949 | 94.3596 | 93.6861
2022-09-07 20:41 | 2:17 | 25.173 | 26.82 | 28.4682 | 36.8677 | 38.9504 | 36.1014 | 38.5906 | 35.621 | 38.8921 | 36.8328 | 37.7902 | 39.9133 | 35.3777 | 36.4225 | 37.5974 | 36.3931 | 36.3583 | 36.4187 | 36.6684 | 38.4732 | 25.9224 | 24.2798 | 29.7474 | 37.1803 | 35.9002 | 38.7534 | 37.2802 | 36.7297 | 35.9523 | 37.132 | 33.8266 | 37.4701 | 36.2516 | 36.3342 | 35.4021 | 37.4051 | 37.4099 | 37.1382 | 38.5776 | 37.0742 | 36.9595 | 38.1834 | 39.3228 | 36.9891 | 38.3424 | 37.7691 | 39.3693 | 36.6023 | 38.9736 | 37.0814 | 38.5355 | 37.9953 | 39.2799 | 37.6534 | 39.8166 | 37.452 | 38.9836 | 40.5572 | 94.2458 | 94.5557 | 93.7876
2022-09-07 20:41 | 2:17 | 24.8908 | 26.5548 | 28.2432 | 36.8961 | 38.9723 | 36.0401 | 38.5601 | 35.5633 | 38.8864 | 36.846 | 37.5594 | 39.8599 | 35.2857 | 36.3956 | 37.597 | 36.3754 | 36.3202 | 36.4018 | 36.7066 | 38.2398 | 25.8123 | 24.1094 | 29.5833 | 37.0395 | 35.8515 | 38.7989 | 37.1859 | 36.6518 | 36.0321 | 36.9899 | 33.7364 | 37.5867 | 36.2478 | 36.2044 | 35.3322 | 37.2815 | 37.4019 | 37.071 | 38.5963 | 37.0294 | 36.9283 | 38.2341 | 39.2591 | 36.9705 | 38.2884 | 37.6844 | 39.3861 | 36.4783 | 38.7932 | 36.96 | 38.3738 | 37.7847 | 39.211 | 37.5747 | 39.7717 | 37.3524 | 38.8626 | 40.5382 | 94.2975 | 94.7198 | 93.8778
2022-09-07 20:42 | 2:18 | 24.66 | 26.2747 | 27.9916 | 36.7108 | 38.9658 | 35.842 | 38.5867 | 35.565 | 38.873 | 36.7543 | 37.6062 | 39.9393 | 35.1926 | 36.3931 | 37.4141 | 36.3232 | 36.2625 | 36.3527 | 36.6203 | 38.1515 | 25.6955 | 23.928 | 29.4379 | 36.9373 | 35.7617 | 38.5564 | 37.126 | 36.4942 | 35.9737 | 37.0118 | 33.5617 | 37.3871 | 36.1748 | 36.1438 | 35.2097 | 37.1741 | 37.1563 | 37.0523 | 38.4108 | 36.9549 | 36.8868 | 38.1385 | 39.2539 | 36.9028 | 38.3231 | 37.6625 | 39.2659 | 36.406 | 38.6098 | 36.9554 | 38.6221 | 37.8492 | 39.0757 | 37.5707 | 39.7022 | 37.2488 | 38.7756 | 40.5897 | 94.452 | 94.8748 | 93.8974
2022-09-07 20:42 | 2:18 | 24.4905 | 26.0633 | 27.7604 | 36.5762 | 38.9581 | 35.8038 | 38.5455 | 35.4743 | 38.8777 | 36.7495 | 37.6187 | 39.9794 | 35.1155 | 36.4015 | 37.3761 | 36.3233 | 36.229 | 36.3224 | 36.5992 | 38.0023 | 25.5521 | 23.817 | 29.2965 | 36.8616 | 35.6905 | 38.6883 | 37.0309 | 36.5564 | 35.882 | 37.0015 | 33.4738 | 37.4126 | 36.1477 | 36.106 | 35.1259 | 37.157 | 37.3471 | 37.0176 | 38.4449 | 36.922 | 36.8152 | 38.0898 | 39.1442 | 36.7418 | 38.2755 | 37.601 | 39.2771 | 36.3366 | 38.6792 | 36.8146 | 38.3533 | 37.7497 | 39.1436 | 37.4569 | 39.6929 | 37.1524 | 38.8385 | 40.4622 | 94.6015 | 95.0322 | 94.0197
2022-09-07 20:42 | 2:18 | 24.2346 | 25.8126 | 27.5749 | 36.5625 | 38.9703 | 35.6097 | 38.5874 | 35.4501 | 38.8866 | 36.6917 | 37.3261 | 40.013 | 35.0753 | 36.349 | 37.3142 | 36.2869 | 36.0729 | 36.3374 | 36.5617 | 37.9892 | 25.4147 | 23.5743 | 29.1263 | 36.7265 | 35.5677 | 38.5412 | 36.9595 | 36.4305 | 35.8571 | 36.899 | 33.4338 | 37.3471 | 36.1159 | 36.0025 | 35.1724 | 37.1531 | 37.4031 | 36.9121 | 38.4941 | 37.0836 | 36.7467 | 37.9718 | 39.0951 | 36.6292 | 38.2637 | 37.508 | 39.1033 | 36.2069 | 38.6788 | 36.7931 | 38.7361 | 37.648 | 39.0385 | 37.3905 | 39.4457 | 37.0651 | 38.6664 | 40.419 | 94.645 | 95.2041 | 94.1725
2022-09-07 20:42 | 2:18 | 24.0706 | 25.5915 | 27.3532 | 36.4406 | 38.9607 | 35.649 | 38.4917 | 35.3325 | 38.8492 | 36.6761 | 37.3614 | 39.8799 | 34.9797 | 36.2552 | 37.4055 | 36.2693 | 35.972 | 36.1682 | 36.4824 | 38.0781 | 25.2584 | 23.453 | 28.9604 | 36.691 | 35.5186 | 38.43 | 36.9283 | 36.287 | 35.7554 | 36.8985 | 33.3249 | 37.2595 | 36.0862 | 35.9349 | 34.9962 | 37.1247 | 37.3303 | 36.8375 | 38.393 | 36.9633 | 36.6948 | 37.8864 | 39.0506 | 36.5679 | 38.1707 | 37.5115 | 39.1661 | 36.0742 | 38.3717 | 36.7409 | 38.2215 | 37.4501 | 38.9934 | 37.3557 | 39.3401 | 36.9939 | 38.801 | 40.4167 | 94.8385 | 95.3108 | 94.2842
2022-09-07 20:42 | 2:18 | 23.8579 | 25.3964 | 27.1159 | 36.3699 | 38.9382 | 35.5849 | 38.3446 | 35.2686 | 38.8001 | 36.5486 | 37.2752 | 39.8781 | 34.9108 | 36.2454 | 37.3133 | 36.2527 | 35.9353 | 36.1079 | 36.4609 | 38.0008 | 25.1359 | 23.2908 | 28.8434 | 36.6269 | 35.4458 | 38.4694 | 36.8868 | 36.2515 | 35.6615 | 36.7552 | 33.1793 | 37.2417 | 35.9322 | 35.8732 | 34.7061 | 37.0861 | 37.3008 | 36.8293 | 38.3655 | 36.8353 | 36.6349 | 37.8307 | 38.9882 | 36.5032 | 38.1853 | 37.3645 | 39.0751 | 35.9506 | 38.3626 | 36.682 | 38.3662 | 37.4046 | 39.0345 | 37.3209 | 39.3017 | 36.8816 | 38.5056 | 40.1981 | 94.9509 | 95.4349 | 94.3057
2022-09-07 20:42 | 2:18 | 23.7077 | 25.1944 | 26.942 | 36.2366 | 38.9065 | 35.4232 | 38.4604 | 35.2316 | 38.8155 | 36.5598 | 37.2563 | 39.9584 | 34.8632 | 36.1871 | 37.2718 | 36.2008 | 35.9135 | 36.0343 | 36.4704 | 38.0273 | 25.0185 | 23.3523 | 28.7177 | 36.5263 | 35.3476 | 38.4332 | 36.8152 | 36.2019 | 35.6442 | 36.7463 | 33.1251 | 37.414 | 35.9353 | 35.7724 | 34.6492 | 36.9869 | 37.1663 | 36.7757 | 38.3314 | 36.7215 | 36.7008 | 37.7385 | 38.9248 | 36.4213 | 38.046 | 37.3441 | 38.989 | 35.959 | 38.4146 | 36.5552 | 38.5034 | 37.2179 | 38.9458 | 37.1767 | 39.469 | 36.8229 | 38.5188 | 40.4209 | 95.0606 | 95.5213 | 94.4789
2022-09-07 20:43 | 2:18 | 23.6027 | 25.0415 | 26.767 | 36.1163 | 38.8855 | 35.3634 | 38.5049 | 35.1637 | 38.7822 | 36.3184 | 37.1007 | 39.8855 | 34.7186 | 36.2136 | 37.2246 | 36.1786 | 35.8649 | 36.0677 | 36.3725 | 37.8077 | 25.069 | 23.9829 | 28.6871 | 36.4804 | 35.3104 | 38.321 | 36.7467 | 36.1989 | 35.5493 | 36.7468 | 33.0471 | 37.187 | 35.7962 | 35.6739 | 34.7111 | 36.9314 | 37.0971 | 36.5801 | 38.2283 | 36.6395 | 36.6416 | 37.7183 | 38.8737 | 36.329 | 37.9337 | 37.2928 | 39.0121 | 35.7923 | 38.4182 | 36.4832 | 38.1206 | 37.2029 | 38.9259 | 37.1571 | 39.4998 | 36.775 | 38.317 | 40.3034 | 95.1319 | 95.5924 | 94.5225
2022-09-07 20:43 | 2:19 | 23.41 | 24.8508 | 26.6128 | 36.24 | 38.8535 | 35.4457 | 38.4304 | 34.9682 | 38.7413 | 36.3757 | 36.814 | 39.8083 | 34.6983 | 36.1244 | 37.2117 | 36.138 | 35.7996 | 35.9568 | 36.3171 | 37.8478 | 25.0066 | 23.5419 | 28.685 | 36.3417 | 35.1887 | 38.2599 | 36.6948 | 36.1121 | 35.5485 | 36.5746 | 33.0072 | 37.2185 | 35.6339 | 35.6074 | 34.4724 | 36.9287 | 36.8845 | 36.5244 | 38.2077 | 36.5371 | 36.6344 | 37.6543 | 38.7949 | 36.2585 | 37.8501 | 37.2675 | 38.9413 | 35.7377 | 38.4659 | 36.418 | 38.1861 | 37.3305 | 38.8671 | 37.0861 | 39.3925 | 36.7317 | 38.4739 | 40.3229 | 95.1219 | 95.5851 | 94.4569
2022-09-07 20:43 | 2:19 | 23.4142 | 24.8322 | 26.5449 | 36.1243 | 38.8251 | 35.2388 | 38.3673 | 34.9507 | 38.7537 | 36.3204 | 36.9856 | 39.8754 | 34.6325 | 36.0726 | 37.2315 | 36.1094 | 35.704 | 35.9524 | 36.3005 | 37.6517 | 25.2279 | 23.3625 | 28.9994 | 36.3645 | 35.1562 | 38.3864 | 36.6349 | 36.0638 | 35.4967 | 36.5459 | 33.0482 | 37.2107 | 35.6608 | 35.5874 | 34.4545 | 36.873 | 36.993 | 36.4948 | 38.271 | 36.511 | 36.6071 | 37.5621 | 38.7906 | 36.2514 | 37.8693 | 37.2144 | 38.8876 | 35.9152 | 38.421 | 36.3981 | 38.347 | 37.2219 | 38.7238 | 36.9823 | 39.365 | 36.661 | 38.3909 | 39.9984 | 94.9421 | 95.3831 | 94.2946
2022-09-07 20:43 | 2:19 | 23.2951 | 24.6765 | 26.4039 | 35.9709 | 38.8332 | 35.0883 | 38.3079 | 35.0536 | 38.7823 | 36.2961 | 37.043 | 39.8824 | 34.6386 | 36.1184 | 37.0866 | 36.0721 | 35.6835 | 35.8749 | 36.2411 | 37.7519 | 26.0013 | 23.1676 | 30.1959 | 36.3254 | 35.1719 | 38.4413 | 36.7008 | 36.1125 | 35.4345 | 36.5525 | 33.2587 | 37.1544 | 35.5749 | 35.6075 | 34.3771 | 36.9061 | 36.8443 | 36.6067 | 38.1003 | 36.4996 | 36.5518 | 37.611 | 38.8712 | 36.3997 | 37.9097 | 37.1907 | 38.9031 | 35.8175 | 38.348 | 36.3929 | 38.2769 | 37.2446 | 38.7715 | 36.9343 | 39.383 | 36.7334 | 38.4442 | 40.0802 | 94.724 | 95.1669 | 94.1479
2022-09-07 20:43 | 2:19 | 23.2364 | 24.6127 | 26.3055 | 35.8944 | 38.837 | 35.2205 | 38.2581 | 34.8483 | 38.7178 | 36.1738 | 36.8128 | 39.8335 | 34.5507 | 35.944 | 37.1552 | 36.0814 | 35.6183 | 35.8176 | 36.3982 | 37.6325 | 26.977 | 23.1996 | 30.7665 | 36.4245 | 35.1495 | 38.3653 | 36.6416 | 36.2226 | 35.4007 | 36.719 | 33.4713 | 37.2394 | 35.6054 | 35.6238 | 34.4497 | 36.9558 | 36.7722 | 36.6777 | 38.1078 | 36.4695 | 36.514 | 37.6673 | 38.8624 | 36.3736 | 38.0318 | 37.1637 | 39.0101 | 35.8492 | 38.3374 | 36.4241 | 38.0095 | 37.0626 | 38.84 | 36.963 | 39.6618 | 36.707 | 38.4295 | 40.2501 | 94.5015 | 94.8764 | 93.9712
2022-09-07 20:43 | 2:19 | 22.9976 | 24.3536 | 26.1341 | 36.0894 | 38.7751 | 35.2811 | 38.1928 | 34.7912 | 38.657 | 36.2281 | 36.5339 | 39.8882 | 34.5479 | 35.9257 | 37.0312 | 36.0303 | 35.5635 | 35.6866 | 36.2469 | 37.6961 | 27.5043 | 23.0968 | 30.8751 | 36.4108 | 35.1073 | 38.3388 | 36.6344 | 36.1758 | 35.3849 | 36.5694 | 33.4704 | 37.0718 | 35.6028 | 35.6239 | 34.3617 | 36.9132 | 36.65 | 36.6283 | 38.2172 | 36.356 | 36.433 | 37.5719 | 38.8603 | 36.2831 | 38.0988 | 37.1211 | 38.9542 | 35.8174 | 38.3173 | 36.4266 | 37.9664 | 37.0887 | 38.6656 | 36.9867 | 39.5036 | 36.7424 | 38.4373 | 40.1413 | 94.2988 | 94.71 | 93.7646
2022-09-07 20:44 | 2:20 | 23.0238 | 24.2871 | 26.0206 | 35.8792 | 38.7124 | 35.0505 | 38.2721 | 34.7126 | 38.6677 | 36.2093 | 36.7428 | 39.8402 | 34.4149 | 35.8321 | 37.0261 | 35.9782 | 35.4905 | 35.6643 | 36.2109 | 37.6957 | 27.6219 | 23.1062 | 30.7706 | 36.3853 | 35.0701 | 38.3568 | 36.6071 | 36.1963 | 35.4069 | 36.5795 | 33.3436 | 37.0439 | 35.5722 | 35.5763 | 34.2933 | 36.8416 | 36.6558 | 36.6369 | 38.0316 | 36.317 | 36.4367 | 37.5971 | 38.9187 | 36.2754 | 38.0703 | 37.0364 | 38.8747 | 35.7275 | 38.3649 | 36.356 | 37.5777 | 37.0982 | 38.5703 | 36.9753 | 39.4068 | 36.7005 | 38.5047 | 40.1178 | 94.2062 | 94.5518 | 93.7446
2022-09-07 20:44 | 2:20 | 22.8103 | 24.0847 | 25.8851 | 35.7793 | 38.7424 | 35.0702 | 38.1651 | 34.7609 | 38.646 | 36.0953 | 36.7151 | 39.7918 | 34.3597 | 35.8975 | 36.87 | 35.926 | 35.4755 | 35.6192 | 36.1024 | 37.6143 | 27.5314 | 23.0198 | 30.6162 | 36.3233 | 34.9624 | 38.3034 | 36.5518 | 35.9381 | 35.3263 | 36.4824 | 33.2419 | 36.9744 | 35.4804 | 35.5665 | 34.3274 | 36.7751 | 36.5883 | 36.5957 | 37.946 | 36.3288 | 36.2991 | 37.5157 | 38.7295 | 36.2664 | 37.9256 | 36.9932 | 38.8356 | 35.7541 | 38.2998 | 36.3141 | 38.2579 | 37.1059 | 38.5459 | 36.9042 | 39.2362 | 36.5798 | 38.3761 | 40.1541 | 94.0776 | 94.385 | 93.6978
2022-09-07 20:44 | 2:20 | 22.7142 | 24.0161 | 25.7679 | 35.7083 | 38.6665 | 34.9793 | 38.1492 | 34.5734 | 38.6158 | 36.0822 | 36.6619 | 39.8125 | 34.2451 | 35.7558 | 36.8656 | 35.9373 | 35.3886 | 35.5547 | 36.0677 | 37.4934 | 27.2803 | 22.9272 | 30.446 | 36.2511 | 34.9158 | 38.4143 | 36.514 | 35.8757 | 35.2548 | 36.4385 | 33.1397 | 37.0134 | 35.3834 | 35.5354 | 34.1204 | 36.6894 | 36.5792 | 36.517 | 38.0506 | 36.285 | 36.2818 | 37.4888 | 38.6375 | 36.1314 | 37.8175 | 36.9097 | 38.8314 | 35.653 | 38.2131 | 36.1897 | 37.9912 | 36.9208 | 38.6373 | 36.7879 | 39.2897 | 36.4328 | 38.3173 | 40.1018 | 94.0166 | 94.3151 | 93.7188
2022-09-07 20:44 | 2:20 | 22.6756 | 23.9209 | 25.6903 | 35.6164 | 38.6571 | 34.9009 | 38.0791 | 34.4871 | 38.5856 | 36.0582 | 36.5427 | 39.727 | 34.2259 | 35.7255 | 36.9074 | 35.8751 | 35.3599 | 35.5765 | 35.9883 | 37.4141 | 26.9904 | 22.7853 | 30.2071 | 36.1592 | 34.8553 | 38.2636 | 36.433 | 35.8905 | 35.1868 | 36.3647 | 33.0317 | 36.9784 | 35.2982 | 35.4276 | 34.1921 | 36.6675 | 36.5643 | 36.4402 | 37.9672 | 36.2577 | 36.2768 | 37.38 | 38.7073 | 35.9785 | 37.7597 | 36.8877 | 38.7586 | 35.5418 | 38.0938 | 36.0949 | 38.0679 | 36.8699 | 38.5686 | 36.7464 | 39.1921 | 36.41 | 38.3929 | 39.883 | 93.9138 | 94.1973 | 93.6157
2022-09-07 20:44 | 2:20 | 22.503 | 23.7006 | 25.5608 | 35.6137 | 38.6381 | 34.8807 | 38.0595 | 34.5486 | 38.5913 | 35.8772 | 36.5042 | 39.7178 | 34.136 | 35.7403 | 36.9617 | 35.842 | 35.2614 | 35.6861 | 35.9961 | 37.3324 | 26.7087 | 22.692 | 29.9035 | 36.0921 | 34.8199 | 38.2307 | 36.4367 | 35.7849 | 35.1606 | 36.3467 | 32.8965 | 36.8907 | 35.3558 | 35.3337 | 34.0908 | 36.5928 | 36.6842 | 36.3419 | 38.0226 | 36.3289 | 36.2176 | 37.2918 | 38.6587 | 35.9482 | 37.7201 | 36.8483 | 38.6494 | 35.4339 | 38.0012 | 36.0452 | 37.9137 | 36.7829 | 38.4731 | 36.5908 | 39.1166 | 36.2613 | 38.2174 | 39.8351 | 93.8392 | 94.1448 | 93.5766
2022-09-07 20:44 | 2:20 | 22.361 | 23.5247 | 25.4031 | 35.4994 | 38.5722 | 34.7755 | 38.0047 | 34.4467 | 38.5466 | 35.9162 | 36.5061 | 39.6821 | 34.1433 | 35.662 | 36.8148 | 35.8182 | 35.2332 | 35.5342 | 35.9792 | 37.2226 | 26.4258 | 22.5688 | 29.6999 | 35.9785 | 34.7088 | 38.08 | 36.2991 | 35.7025 | 35.0943 | 36.2323 | 32.846 | 36.8572 | 35.2124 | 35.2753 | 34.2946 | 36.685 | 36.7683 | 36.2801 | 37.8849 | 36.3922 | 36.1647 | 37.1453 | 38.4924 | 35.8967 | 37.7133 | 36.7883 | 38.6854 | 35.3837 | 38.0476 | 35.9596 | 38.1162 | 36.6487 | 38.558 | 36.4683 | 39.3868 | 36.2293 | 38.1102 | 39.8121 | 93.8922 | 94.1222 | 93.5539
2022-09-07 20:45 | 2:20 | 22.3155 | 23.522 | 25.3457 | 35.5451 | 38.5446 | 34.8982 | 38.0241 | 34.4348 | 38.4641 | 35.8283 | 36.1424 | 39.6788 | 34.0989 | 35.6108 | 36.6069 | 35.7865 | 35.0914 | 35.5466 | 36.0248 | 37.3196 | 26.1864 | 22.4897 | 29.5198 | 35.983 | 34.6251 | 38.4463 | 36.2818 | 35.6855 | 34.9647 | 36.2741 | 32.7148 | 36.784 | 35.1359 | 35.2407 | 33.9681 | 36.4475 | 36.4614 | 36.2616 | 37.8943 | 36.1688 | 36.0759 | 37.1091 | 38.4635 | 35.847 | 37.6481 | 36.7633 | 38.5717 | 35.346 | 38.2929 | 35.9569 | 37.9778 | 36.6644 | 38.6341 | 36.5111 | 39.1712 | 36.181 | 38.1659 | 39.7607 | 93.8175 | 94.0549 | 93.648
2022-09-07 20:45 | 2:21 | 22.2051 | 23.33 | 25.1992 | 35.5165 | 38.5801 | 34.6813 | 38.0031 | 34.2505 | 38.5048 | 35.8201 | 36.1418 | 39.6473 | 33.9861 | 35.5491 | 36.7569 | 35.7366 | 35.0724 | 35.3994 | 35.8565 | 37.2811 | 25.9273 | 22.2873 | 29.2997 | 35.8797 | 34.5757 | 38.0547 | 36.2768 | 35.6664 | 34.8953 | 36.2017 | 32.6373 | 36.5581 | 35.0191 | 35.1278 | 33.6789 | 36.3768 | 36.2301 | 36.1526 | 37.7944 | 36.0419 | 35.9867 | 37.1457 | 38.4348 | 35.8973 | 37.6399 | 36.73 | 38.6438 | 35.2697 | 37.9586 | 35.9267 | 38.1474 | 36.6796 | 38.6551 | 36.4389 | 39.0471 | 36.051 | 37.9353 | 39.9361 | 93.729 | 94.0114 | 93.4651
2022-09-07 20:45 | 2:21 | 22.0222 | 23.1859 | 25.0246 | 35.448 | 38.4784 | 34.4496 | 38.0283 | 34.1687 | 38.4728 | 35.6416 | 36.149 | 39.6573 | 33.9893 | 35.3765 | 36.6178 | 35.7071 | 34.9875 | 35.3172 | 35.8078 | 37.242 | 25.7134 | 22.1964 | 29.1049 | 35.733 | 34.5034 | 38.0209 | 36.2176 | 35.8056 | 34.9112 | 36.089 | 32.4903 | 36.8023 | 35.0491 | 35.1382 | 33.7019 | 36.365 | 36.2946 | 36.1098 | 37.8022 | 35.9003 | 35.9831 | 37.1184 | 38.3674 | 35.744 | 37.5077 | 36.6753 | 38.54 | 35.2099 | 37.916 | 35.814 | 37.8694 | 36.4939 | 38.5503 | 36.3512 | 39.0558 | 36.0438 | 37.9984 | 39.8085 | 93.6937 | 93.9613 | 93.4717
2022-09-07 20:45 | 2:21 | 22.0249 | 23.1105 | 24.9594 | 35.1764 | 38.4488 | 34.3575 | 37.9105 | 34.1724 | 38.4203 | 35.6608 | 36.2903 | 39.7488 | 33.8295 | 35.4005 | 36.6299 | 35.6127 | 34.9131 | 35.2744 | 35.7349 | 37.197 | 25.4703 | 22.1416 | 28.9026 | 35.7167 | 34.416 | 37.8161 | 36.1647 | 35.4952 | 34.8971 | 36.0827 | 32.4113 | 36.7967 | 35.0794 | 34.9877 | 33.5599 | 36.4236 | 36.4575 | 36.0666 | 37.833 | 35.9153 | 35.8964 | 37.0043 | 38.4147 | 35.7411 | 37.4138 | 36.6337 | 38.5056 | 35.0948 | 37.9148 | 35.7266 | 38.1061 | 36.3936 | 38.4447 | 36.2787 | 39.067 | 35.9367 | 38.1318 | 39.6959 | 93.6785 | 93.8829 | 93.4776
2022-09-07 20:45 | 2:21 | 21.8039 | 22.91 | 24.8179 | 35.035 | 38.448 | 34.5626 | 37.9363 | 34.2567 | 38.3854 | 35.6253 | 36.2263 | 39.609 | 33.7674 | 35.3863 | 36.4298 | 35.6122 | 34.8873 | 35.2154 | 35.6939 | 37.0494 | 25.2567 | 21.9654 | 28.6632 | 35.6174 | 34.397 | 37.9483 | 36.0759 | 35.4036 | 34.848 | 35.9051 | 32.4269 | 36.6393 | 34.8679 | 34.9197 | 33.4183 | 36.4533 | 36.1665 | 36.0072 | 37.8416 | 35.8004 | 35.8457 | 37.0088 | 38.367 | 35.5848 | 37.3765 | 36.5446 | 38.364 | 35.0799 | 37.8167 | 35.7464 | 37.7714 | 36.3769 | 38.4389 | 36.2786 | 38.8588 | 35.8605 | 37.9458 | 39.7328 | 93.5608 | 93.7826 | 93.3795
2022-09-07 20:45 | 2:21 | 21.8085 | 22.8661 | 24.7362 | 35.131 | 38.3254 | 34.7205 | 37.9746 | 34.1185 | 38.3562 | 35.5955 | 36.1935 | 39.5696 | 33.7599 | 35.3912 | 36.3533 | 35.5212 | 34.86 | 35.2082 | 35.7547 | 37.0189 | 25.0803 | 21.9496 | 28.5546 | 35.4871 | 34.3174 | 37.7505 | 35.9867 | 35.3231 | 34.7326 | 35.8106 | 32.2391 | 36.6604 | 34.7528 | 34.8557 | 33.306 | 36.4481 | 36.2863 | 35.9393 | 37.8558 | 35.8317 | 35.7979 | 36.9648 | 38.1768 | 35.4064 | 37.3329 | 36.5324 | 38.4969 | 34.9565 | 37.8273 | 35.5981 | 37.6857 | 36.1815 | 38.2531 | 36.1899 | 38.8764 | 35.7779 | 37.9963 | 39.5151 | 93.4961 | 93.6899 | 93.3189
2022-09-07 20:46 | 2:22 | 21.6651 | 22.7518 | 24.6261 | 35.0839 | 38.2937 | 34.4546 | 37.8063 | 34.0179 | 38.3434 | 35.5779 | 35.9857 | 39.506 | 33.5833 | 35.2934 | 36.4152 | 35.4666 | 34.7526 | 35.0678 | 35.5596 | 36.944 | 24.9095 | 21.7291 | 28.427 | 35.4354 | 34.1871 | 37.8619 | 35.9831 | 35.3805 | 34.71 | 35.8047 | 32.1137 | 36.5715 | 34.8313 | 34.7736 | 33.449 | 36.4661 | 36.4449 | 35.8484 | 37.7458 | 36.0376 | 35.6262 | 36.8206 | 38.0855 | 35.4248 | 37.324 | 36.4308 | 38.4622 | 34.8686 | 37.637 | 35.485 | 37.8331 | 36.1688 | 38.1638 | 35.9081 | 38.8712 | 35.7481 | 37.8697 | 39.4176 | 93.3913 | 93.6453 | 93.2529
2022-09-07 20:46 | 2:22 | 21.5788 | 22.5941 | 24.4944 | 35.0487 | 38.2912 | 34.3442 | 37.808 | 33.9059 | 38.3053 | 35.5033 | 36.0544 | 39.5629 | 33.5407 | 35.2208 | 36.375 | 35.418 | 34.7164 | 34.9742 | 35.6189 | 36.8584 | 24.7024 | 21.7284 | 28.2687 | 35.3039 | 34.1583 | 37.6964 | 35.8964 | 35.2833 | 34.5889 | 35.7404 | 31.9751 | 36.4309 | 34.8724 | 34.7658 | 33.6814 | 36.4162 | 36.4874 | 35.8015 | 37.8661 | 36.1371 | 35.5772 | 36.7449 | 38.103 | 35.4036 | 37.1124 | 36.4051 | 38.3073 | 34.706 | 37.663 | 35.4828 | 38.202 | 36.0896 | 38.3458 | 35.7825 | 38.923 | 35.6389 | 37.6689 | 39.2572 | 93.361 | 93.5349 | 93.241
2022-09-07 20:46 | 2:22 | 21.4192 | 22.4536 | 24.3817 | 34.9682 | 38.2076 | 34.27 | 37.6957 | 33.8087 | 38.2401 | 35.4082 | 36.0887 | 39.5339 | 33.5509 | 35.1219 | 36.2385 | 35.3933 | 34.6509 | 34.915 | 35.4847 | 36.8514 | 24.5374 | 21.5172 | 28.1587 | 35.1711 | 34.0773 | 37.7534 | 35.8457 | 35.3252 | 34.596 | 35.8142 | 31.9852 | 36.3978 | 34.8116 | 34.624 | 33.4048 | 36.3648 | 36.3681 | 35.6697 | 37.7337 | 35.9401 | 35.6159 | 36.7277 | 37.994 | 35.4712 | 36.996 | 36.3349 | 38.369 | 34.7497 | 37.5235 | 35.3885 | 37.8498 | 35.9907 | 38.3595 | 35.7973 | 38.6591 | 35.524 | 37.7129 | 39.4876 | 93.2718 | 93.4856 | 93.1683
2022-09-07 20:46 | 2:22 | 21.3587 | 22.3817 | 24.2876 | 34.8709 | 38.192 | 34.2502 | 37.7125 | 33.8473 | 38.2101 | 35.5009 | 35.8094 | 39.4454 | 33.4059 | 35.0912 | 36.266 | 35.3168 | 34.5793 | 34.9147 | 35.3665 | 36.866 | 24.3983 | 21.3742 | 28.0321 | 35.1497 | 33.9595 | 37.5523 | 35.7979 | 35.1813 | 34.438 | 35.6606 | 31.8339 | 36.2811 | 34.5137 | 34.5917 | 33.0493 | 36.1696 | 36.161 | 35.6388 | 37.7404 | 35.7481 | 35.5877 | 36.6679 | 37.9094 | 35.2384 | 37.1341 | 36.2488 | 38.3234 | 34.6264 | 37.3721 | 35.3831 | 37.5169 | 35.9449 | 38.2041 | 35.772 | 38.5652 | 35.4855 | 37.5499 | 39.3714 | 93.195 | 93.387 | 93.1829
2022-09-07 20:46 | 2:22 | 21.1922 | 22.207 | 24.1549 | 34.8249 | 38.1562 | 34.0812 | 37.6582 | 33.751 | 38.1838 | 35.4749 | 35.8022 | 39.5291 | 33.3262 | 34.8908 | 36.2379 | 35.2803 | 34.5461 | 34.8212 | 35.3261 | 36.8497 | 24.2898 | 21.3706 | 27.9361 | 35.1256 | 33.9033 | 37.439 | 35.6262 | 35.0673 | 34.2994 | 35.6364 | 31.7563 | 36.1891 | 34.3706 | 34.4962 | 32.9327 | 36.0772 | 35.9646 | 35.5739 | 37.3979 | 35.6421 | 35.5298 | 36.5828 | 37.939 | 35.1979 | 37.0999 | 36.1737 | 38.2298 | 34.5928 | 37.2807 | 35.3471 | 37.7662 | 35.8817 | 38.0823 | 35.8533 | 38.4259 | 35.3797 | 37.5896 | 39.3062 | 93.1765 | 93.2929 | 93.1961
2022-09-07 20:46 | 2:22 | 21.111 | 22.1209 | 24.0541 | 34.7722 | 38.1221 | 33.9618 | 37.6602 | 33.6406 | 38.1477 | 35.3305 | 35.857 | 39.4479 | 33.2205 | 34.9995 | 36.1344 | 35.2114 | 34.4698 | 34.8173 | 35.2325 | 36.7425 | 24.1654 | 21.2523 | 27.8716 | 35.0931 | 33.8213 | 37.5733 | 35.5772 | 34.9662 | 34.2863 | 35.5287 | 31.699 | 36.2986 | 34.3365 | 34.4755 | 32.9217 | 36.1719 | 35.8791 | 35.499 | 37.5607 | 35.5532 | 35.5939 | 36.5453 | 37.904 | 35.085 | 36.8925 | 36.134 | 38.2037 | 34.5607 | 37.2178 | 35.2529 | 37.4733 | 35.9473 | 37.9009 | 35.697 | 38.6222 | 35.3756 | 37.5056 | 39.1681 | 93.0004 | 93.1747 | 92.965
2022-09-07 20:47 | 2:22 | 20.9824 | 22.0328 | 23.9415 | 34.5824 | 38.0435 | 34.1984 | 37.6413 | 33.5569 | 38.0979 | 35.3078 | 35.7439 | 39.3874 | 33.1395 | 35.0095 | 36.0136 | 35.1392 | 34.3965 | 34.9608 | 35.2356 | 36.6094 | 24.073 | 21.1456 | 27.7717 | 34.9633 | 33.7623 | 37.4615 | 35.6159 | 34.9288 | 34.2585 | 35.4807 | 31.5961 | 36.2918 | 34.4415 | 34.3626 | 32.8815 | 36.1246 | 35.642 | 35.4969 | 37.6086 | 35.3134 | 35.6215 | 36.5377 | 37.8321 | 35.0026 | 36.8015 | 36.0536 | 38.033 | 34.4419 | 37.3336 | 35.22 | 37.8507 | 35.8426 | 37.883 | 35.7008 | 38.5997 | 35.3028 | 37.4609 | 39.2181 | 92.8605 | 93.0678 | 92.9137
2022-09-07 20:47 | 2:23 | 20.5428 | 21.8945 | 23.8095 | 34.5336 | 37.9852 | 34.0834 | 37.6231 | 33.5505 | 38.0872 | 35.3269 | 35.5912 | 39.3596 | 33.1638 | 34.8538 | 35.9402 | 35.1146 | 34.3589 | 34.8906 | 35.2336 | 36.4634 | 24.0827 | 21.2953 | 28.0094 | 34.882 | 33.6712 | 37.3708 | 35.5877 | 34.8351 | 34.178 | 35.3865 | 31.6215 | 36.3318 | 34.3473 | 34.3379 | 32.8343 | 36.0299 | 35.9185 | 35.4614 | 37.484 | 35.423 | 35.6253 | 36.4132 | 37.7869 | 35.06 | 36.8681 | 36.0646 | 38.1152 | 34.4972 | 37.2841 | 35.1667 | 37.5245 | 35.7044 | 37.9524 | 35.597 | 38.5992 | 35.2388 | 37.2955 | 39.2733 | 92.777 | 92.9304 | 92.8047
2022-09-07 20:47 | 2:23 | 19.4596 | 21.3941 | 23.2666 | 34.5025 | 37.9122 | 33.9384 | 37.5897 | 33.4279 | 38.0276 | 35.1362 | 35.6176 | 39.4347 | 33.0236 | 34.8357 | 35.9118 | 35.017 | 34.2097 | 34.5473 | 35.0955 | 36.4532 | 24.4978 | 22.2688 | 28.9214 | 34.8066 | 33.6851 | 37.4978 | 35.5298 | 34.8379 | 34.0776 | 35.3774 | 31.9877 | 36.1233 | 34.2445 | 34.3664 | 32.8189 | 35.7897 | 35.8743 | 35.3581 | 37.3602 | 35.368 | 35.7177 | 36.5102 | 37.9038 | 35.1476 | 37.0677 | 36.0018 | 38.1852 | 34.6761 | 37.4067 | 35.2481 | 37.1657 | 35.8094 | 37.9182 | 35.5015 | 38.5746 | 35.3548 | 37.3922 | 39.3343 | 92.6475 | 92.819 | 92.8006
2022-09-07 20:47 | 2:23 | 19.044 | 21.0738 | 22.9215 | 34.3462 | 37.8831 | 33.6865 | 37.4821 | 33.3479 | 37.9434 | 35.0563 | 35.4472 | 39.3298 | 32.8765 | 34.5874 | 35.889 | 34.9524 | 34.1461 | 34.4862 | 35.0055 | 36.6686 | 25.3286 | 23.4988 | 29.9659 | 34.9665 | 33.7146 | 37.7657 | 35.5939 | 34.92 | 34.1234 | 35.4916 | 32.2284 | 36.1144 | 34.0576 | 34.3959 | 32.9597 | 35.9822 | 35.72 | 35.3281 | 37.0747 | 35.2806 | 35.7906 | 36.6542 | 37.9187 | 35.3548 | 37.2036 | 36.0042 | 38.1028 | 34.847 | 37.4788 | 35.2955 | 36.9615 | 35.8921 | 38.0337 | 35.5735 | 38.7514 | 35.5277 | 37.71 | 39.1776 | 92.5858 | 92.6946 | 92.7486
2022-09-07 20:47 | 2:23 | 18.6513 | 20.7417 | 22.6012 | 34.1295 | 37.7664 | 33.6548 | 37.4529 | 33.3556 | 37.9282 | 34.8895 | 35.4991 | 39.2413 | 32.7535 | 34.6146 | 35.6811 | 34.8674 | 34.0692 | 34.5358 | 34.8865 | 36.4403 | 26.3299 | 24.8859 | 30.7943 | 35.1133 | 33.7828 | 37.807 | 35.6215 | 35.0357 | 34.1173 | 35.5869 | 32.4863 | 36.1645 | 34.0828 | 34.5488 | 33.0787 | 35.8923 | 35.6068 | 35.4195 | 37.0634 | 35.3225 | 35.7968 | 36.745 | 38.0694 | 35.4791 | 37.2836 | 35.9976 | 38.286 | 35.0338 | 37.6839 | 35.422 | 36.9273 | 36.0709 | 38.045 | 35.7309 | 38.7695 | 35.6336 | 37.8156 | 39.0794 | 92.4454 | 92.5611 | 92.5859
2022-09-07 20:47 | 2:23 | 18.3418 | 20.4544 | 22.3127 | 34.0896 | 37.7333 | 33.5478 | 37.1486 | 33.1828 | 37.8412 | 34.9003 | 35.0655 | 39.1865 | 32.6054 | 34.5552 | 35.7158 | 34.801 | 33.9787 | 34.2053 | 34.8676 | 36.4788 | 27.2725 | 26.1907 | 31.3907 | 35.1832 | 33.8179 | 38.0047 | 35.6253 | 35.0343 | 34.1337 | 35.6856 | 32.6897 | 36.0585 | 33.9689 | 34.5693 | 33.1743 | 35.8192 | 35.6043 | 35.5122 | 37.1843 | 35.3324 | 35.824 | 36.8126 | 38.1414 | 35.6269 | 37.3034 | 35.9875 | 38.1918 | 35.1549 | 37.8286 | 35.4026 | 37.013 | 36.1152 | 38.0493 | 35.7527 | 38.8256 | 35.7051 | 37.7768 | 39.2273 | 92.294 | 92.4283 | 92.5957
2022-09-07 20:48 | 2:24 | 18.0169 | 20.2015 | 22.0456 | 34.2381 | 37.6471 | 33.4485 | 37.2347 | 32.8982 | 37.8098 | 34.7245 | 34.7811 | 39.0462 | 32.5367 | 34.5025 | 35.6976 | 34.7412 | 33.8807 | 34.2893 | 34.7796 | 36.3651 | 28.0999 | 27.2835 | 31.8453 | 35.2742 | 33.8387 | 38.0304 | 35.7177 | 34.9941 | 34.2057 | 35.7501 | 32.8304 | 35.9971 | 33.9872 | 34.5995 | 33.2674 | 35.9228 | 35.5415 | 35.5159 | 37.1812 | 35.3278 | 35.8113 | 36.8659 | 38.0693 | 35.7704 | 37.4733 | 36.0044 | 38.2386 | 35.2409 | 37.8658 | 35.46 | 37.0877 | 36.2317 | 38.0097 | 35.7013 | 38.9121 | 35.7938 | 37.9168 | 39.2584 | 92.1699 | 92.252 | 92.3678
2022-09-07 20:48 | 2:24 | 17.7995 | 19.9706 | 21.8245 | 34.0478 | 37.5679 | 33.5153 | 37.194 | 32.8398 | 37.7381 | 34.7318 | 34.838 | 39.0254 | 32.4791 | 34.4589 | 35.4717 | 34.6273 | 33.8342 | 34.0222 | 34.7684 | 36.3765 | 28.8099 | 28.226 | 32.1743 | 35.2965 | 33.8512 | 38.1094 | 35.7906 | 35.0075 | 34.0799 | 35.8072 | 32.985 | 35.9557 | 33.8725 | 34.6333 | 33.3115 | 35.8777 | 35.475 | 35.4678 | 37.2048 | 35.3182 | 35.8629 | 36.9088 | 38.1862 | 35.824 | 37.4933 | 36.0205 | 38.2987 | 35.3332 | 37.8849 | 35.4476 | 36.9442 | 36.2679 | 38.1119 | 35.7254 | 38.923 | 35.8736 | 37.8922 | 39.2496 | 92.0523 | 92.1536 | 92.2866
2022-09-07 20:48 | 2:24 | 17.6203 | 19.7346 | 21.6008 | 34.0409 | 37.514 | 33.5322 | 37.1154 | 32.8018 | 37.6627 | 34.7932 | 34.8152 | 38.9096 | 32.4676 | 34.2758 | 35.4975 | 34.504 | 33.7062 | 33.8774 | 34.61 | 36.5709 | 29.4456 | 28.9774 | 32.4058 | 35.3628 | 33.8784 | 38.1971 | 35.7968 | 34.8279 | 34.0958 | 35.8332 | 33.1262 | 35.801 | 33.7445 | 34.7344 | 33.4285 | 35.7952 | 35.4552 | 35.4421 | 37.0515 | 35.3165 | 35.9405 | 36.9127 | 38.2043 | 35.9025 | 37.5891 | 36.0389 | 38.2007 | 35.3902 | 37.8034 | 35.4989 | 37.0042 | 36.3181 | 38.1555 | 35.7125 | 38.9238 | 35.889 | 37.9652 | 39.2043 | 92.046 | 92.1904 | 92.3058
2022-09-07 20:48 | 2:24 | 17.3136 | 19.4948 | 21.3467 | 33.9557 | 37.4685 | 33.5334 | 36.995 | 32.6128 | 37.6015 | 34.6428 | 34.551 | 38.8286 | 32.323 | 34.276 | 35.4565 | 34.5154 | 33.6063 | 33.9505 | 34.4512 | 36.5239 | 29.9098 | 29.5614 | 32.6106 | 35.2957 | 33.9235 | 38.192 | 35.824 | 34.9342 | 33.9883 | 35.8081 | 33.1729 | 35.8807 | 33.7625 | 34.6849 | 33.4776 | 35.8628 | 35.4586 | 35.5164 | 37.1844 | 35.2976 | 35.9237 | 36.9449 | 38.2454 | 35.9641 | 37.5601 | 35.9712 | 38.2792 | 35.4386 | 37.9651 | 35.5377 | 37.0931 | 36.4279 | 38.1496 | 35.7267 | 38.9001 | 35.9297 | 38.0045 | 39.1433 | 92.1847 | 92.2474 | 92.4957
2022-09-07 20:48 | 2:24 | 17.1281 | 19.289 | 21.1631 | 33.8861 | 37.3283 | 33.2939 | 36.9446 | 32.5794 | 37.5365 | 34.5863 | 34.6355 | 38.8694 | 32.2376 | 33.9691 | 35.3147 | 34.436 | 33.5618 | 33.8601 | 34.5136 | 36.5031 | 30.3101 | 29.9842 | 32.7564 | 35.3982 | 33.9023 | 38.1466 | 35.8113 | 34.9689 | 34.12 | 35.7811 | 33.2463 | 35.8251 | 33.7335 | 34.7538 | 33.5149 | 35.8465 | 35.4047 | 35.4626 | 37.0787 | 35.267 | 35.8803 | 37.017 | 38.2948 | 36.0579 | 37.7437 | 35.9685 | 38.25 | 35.5794 | 37.8789 | 35.5325 | 37.0407 | 36.4007 | 38.1913 | 35.7073 | 39.0203 | 35.9749 | 38.0349 | 39.2403 | 92.1809 | 92.3051 | 92.4111
2022-09-07 20:48 | 2:24 | 16.9648 | 19.114 | 20.9823 | 33.6447 | 37.1949 | 33.2161 | 36.6822 | 32.5562 | 37.532 | 34.4899 | 34.7515 | 38.7788 | 32.0861 | 33.9434 | 35.2653 | 34.3939 | 33.4879 | 33.5175 | 34.4561 | 36.2308 | 30.6141 | 30.3102 | 32.8659 | 35.3664 | 33.9495 | 38.3116 | 35.8629 | 34.6884 | 34.0613 | 35.8897 | 33.3237 | 35.7134 | 33.7443 | 34.7146 | 33.5678 | 35.943 | 35.3198 | 35.4333 | 36.9895 | 35.2175 | 35.8685 | 37.0279 | 38.3015 | 36.1091 | 37.6291 | 36.0326 | 38.1933 | 35.5987 | 37.9489 | 35.5702 | 37.1315 | 36.4258 | 38.2369 | 35.7778 | 39.0794 | 35.9985 | 38.2683 | 39.1267 | 92.2439 | 92.4198 | 92.4463
2022-09-07 20:49 | 2:24 | 16.7625 | 18.8828 | 20.7962 | 33.5554 | 37.0969 | 33.2603 | 36.7509 | 32.4689 | 37.4321 | 34.6101 | 34.4491 | 38.8012 | 32.0435 | 33.9579 | 35.0949 | 34.2911 | 33.4223 | 33.6521 | 34.5555 | 36.3392 | 30.8694 | 30.5644 | 32.95 | 35.3158 | 33.9498 | 38.3275 | 35.9405 | 34.6585 | 33.9614 | 35.9554 | 33.3923 | 35.597 | 33.6279 | 34.7086 | 33.621 | 35.7377 | 35.2957 | 35.3536 | 36.8847 | 35.236 | 35.9798 | 37.0656 | 38.3659 | 36.1798 | 37.8554 | 36.0475 | 38.3577 | 35.6674 | 37.9847 | 35.613 | 37.1633 | 36.4562 | 38.1467 | 35.6695 | 38.9007 | 36.0195 | 38.3367 | 39.1298 | 92.3561 | 92.4915 | 92.5277
2022-09-07 20:49 | 2:25 | 16.5337 | 18.6909 | 20.5901 | 33.617 | 36.9916 | 33.0825 | 36.6222 | 32.3106 | 37.3616 | 34.7118 | 34.3379 | 38.8371 | 31.9206 | 34.0682 | 35.0565 | 34.1803 | 33.3777 | 33.4786 | 34.3497 | 36.31 | 31.0375 | 30.7433 | 33.0319 | 35.3521 | 33.9231 | 38.2016 | 35.9237 | 34.6287 | 34.0478 | 35.8267 | 33.4319 | 35.7034 | 33.6639 | 34.6857 | 33.6321 | 35.8272 | 35.2136 | 35.4768 | 36.8746 | 35.199 | 35.9954 | 37.0524 | 38.3993 | 36.2016 | 37.7955 | 36.0358 | 38.2728 | 35.7118 | 38.0479 | 35.5865 | 37.2085 | 36.5296 | 38.1223 | 35.7005 | 38.7586 | 36.0767 | 38.2704 | 39.1133 | 92.4208 | 92.5932 | 92.5737
2022-09-07 20:49 | 2:25 | 16.3563 | 18.4862 | 20.4237 | 33.4438 | 36.933 | 33.0432 | 36.3598 | 32.2148 | 37.2746 | 34.5142 | 34.1587 | 38.598 | 31.7043 | 33.8699 | 35.1173 | 34.1356 | 33.265 | 33.5456 | 34.2777 | 36.1438 | 31.2032 | 30.8806 | 33.1138 | 35.3242 | 33.9231 | 38.2513 | 35.8803 | 34.4622 | 33.9989 | 35.9023 | 33.4801 | 35.5348 | 33.6191 | 34.6784 | 33.6809 | 35.7709 | 35.1687 | 35.4194 | 36.7009 | 35.2071 | 36.045 | 37.0614 | 38.3683 | 36.2553 | 37.7559 | 36.0024 | 38.2221 | 35.7515 | 38.0103 | 35.7129 | 37.1029 | 36.6008 | 38.1764 | 35.7679 | 38.83 | 36.1453 | 38.2671 | 39.1334 | 92.514 | 92.72 | 92.6531
2022-09-07 20:49 | 2:25 | 16.1474 | 18.3355 | 20.2335 | 33.312 | 36.8166 | 33.1732 | 36.3061 | 31.997 | 37.1954 | 34.7084 | 33.9765 | 38.6309 | 31.5788 | 33.8661 | 34.9855 | 34.0597 | 33.1581 | 33.3397 | 34.1534 | 36.2272 | 31.323 | 30.9922 | 33.196 | 35.3441 | 33.9121 | 38.3174 | 35.8685 | 34.3748 | 34.0281 | 35.7983 | 33.5019 | 35.6805 | 33.4801 | 34.7047 | 33.7271 | 35.7029 | 35.2887 | 35.355 | 36.8223 | 35.2027 | 36.0983 | 37.1103 | 38.4231 | 36.2517 | 37.8822 | 36.0465 | 38.3045 | 35.786 | 38.0481 | 35.7068 | 37.1905 | 36.6494 | 38.21 | 35.7232 | 38.9439 | 36.2072 | 38.3502 | 39.2156 | 92.5917 | 92.7872 | 92.6489
2022-09-07 20:49 | 2:25 | 15.9485 | 18.1064 | 20.0657 | 33.4492 | 36.6265 | 32.9568 | 36.3822 | 31.8167 | 37.1323 | 34.6036 | 34.0031 | 38.5083 | 31.5421 | 33.8406 | 35.0309 | 33.9019 | 33.0716 | 33.2784 | 34.0841 | 35.8843 | 31.4465 | 31.0856 | 33.2342 | 35.3118 | 33.9623 | 38.3967 | 35.9798 | 34.4235 | 33.9525 | 36.0418 | 33.5447 | 35.4588 | 33.4457 | 34.7775 | 33.7536 | 35.6022 | 35.1248 | 35.4051 | 36.9704 | 35.1553 | 36.045 | 37.1985 | 38.4444 | 36.3418 | 37.8031 | 36.0728 | 38.3422 | 35.8739 | 38.069 | 35.7165 | 37.2002 | 36.6856 | 38.2151 | 35.7233 | 38.8868 | 36.2217 | 38.3514 | 39.2585 | 92.6855 | 92.8561 | 92.7673
2022-09-07 20:49 | 2:25 | 15.8219 | 17.9582 | 19.9013 | 33.4477 | 36.596 | 32.7751 | 36.2814 | 31.8082 | 37.0671 | 34.6654 | 33.5161 | 38.3521 | 31.2963 | 33.8133 | 34.9193 | 33.8493 | 33.0294 | 33.1259 | 34.0955 | 35.9646 | 31.5117 | 31.1518 | 33.3045 | 35.2977 | 33.9312 | 38.546 | 35.9954 | 34.5257 | 33.9415 | 36.079 | 33.5668 | 35.3116 | 33.4306 | 34.8174 | 33.775 | 35.5457 | 35.0081 | 35.4299 | 36.7583 | 35.109 | 36.0219 | 37.1515 | 38.4403 | 36.3313 | 37.8368 | 36.0424 | 38.3804 | 35.9159 | 38.1179 | 35.7087 | 37.1892 | 36.7414 | 38.1673 | 35.6522 | 39.0648 | 36.257 | 38.2665 | 39.3858 | 92.8457 | 92.9887 | 92.8007
2022-09-07 20:50 | 2:26 | 15.6533 | 17.7738 | 19.7345 | 33.2004 | 36.4476 | 32.8354 | 36.2321 | 31.8704 | 37.0457 | 34.3724 | 33.6596 | 38.3753 | 31.2677 | 33.8748 | 34.693 | 33.7146 | 32.9376 | 33.586 | 34.0884 | 35.8937 | 31.5586 | 31.2249 | 33.351 | 35.3146 | 33.9526 | 38.6457 | 36.045 | 34.4641 | 33.9084 | 35.9353 | 33.6326 | 35.2692 | 33.4572 | 34.7852 | 33.8291 | 35.6171 | 35.0362 | 35.525 | 36.8008 | 35.0823 | 36.0848 | 37.1969 | 38.448 | 36.3858 | 37.8886 | 36.0906 | 38.3522 | 35.9966 | 38.1519 | 35.7323 | 37.233 | 36.7809 | 38.2066 | 35.7201 | 38.9611 | 36.3098 | 38.3016 | 39.2341 | 92.9328 | 93.1005 | 92.8914
2022-09-07 20:50 | 2:26 | 14.8429 | 15.4917 | 19.2244 | 32.9383 | 36.3917 | 32.8711 | 35.9638 | 31.6654 | 36.9451 | 34.4283 | 33.6782 | 38.3614 | 31.155 | 33.578 | 34.5506 | 33.6916 | 32.8013 | 32.9416 | 34.165 | 35.9279 | 31.5322 | 31.2305 | 33.3561 | 35.222 | 33.924 | 38.515 | 36.0983 | 34.8312 | 33.9457 | 35.9951 | 33.6542 | 35.2187 | 33.3985 | 34.7595 | 33.8796 | 35.4458 | 34.9082 | 35.3565 | 36.7151 | 35.0624 | 36.119 | 37.2757 | 38.5045 | 36.447 | 37.8136 | 36.1039 | 38.3403 | 36.0487 | 38.2301 | 35.763 | 37.3478 | 36.7487 | 38.1551 | 35.7068 | 39.0744 | 36.3479 | 38.4459 | 39.1999 | 93.0646 | 93.2151 | 92.9879
2022-09-07 20:50 | 2:26 | 16.8414 | 16.5714 | 21.3722 | 33.0276 | 36.3419 | 32.5348 | 35.7988 | 31.7104 | 36.8321 | 34.3715 | 33.7502 | 38.0025 | 31.3165 | 33.7732 | 34.6768 | 33.654 | 32.7937 | 33.1951 | 33.8022 | 35.7679 | 31.5736 | 31.2593 | 33.3843 | 35.2258 | 33.9814 | 38.373 | 36.045 | 34.5078 | 34.0483 | 35.9079 | 33.6758 | 35.1953 | 33.4726 | 34.7749 | 33.9001 | 35.4329 | 34.9581 | 35.4198 | 36.7043 | 35.0368 | 36.146 | 37.2688 | 38.5545 | 36.4882 | 37.9164 | 36.1402 | 38.3888 | 36.0749 | 38.1593 | 35.83 | 37.2887 | 36.8257 | 38.2405 | 35.9037 | 39.0911 | 36.4054 | 38.5083 | 39.1896 | 93.1669 | 93.3305 | 93.0529
2022-09-07 20:50 | 2:26 | 19.0422 | 18.9994 | 24.0795 | 33.5628 | 36.3647 | 32.8982 | 36.0787 | 31.8382 | 36.7965 | 34.5468 | 33.6906 | 38.1262 | 31.7682 | 33.7616 | 34.8245 | 33.6786 | 33.0706 | 33.5524 | 33.9166 | 35.9019 | 31.6028 | 31.2866 | 33.4714 | 35.3794 | 34.0549 | 38.3717 | 36.0219 | 34.4517 | 34.0083 | 35.8058 | 33.7116 | 35.3534 | 33.5673 | 34.8001 | 33.9654 | 35.594 | 35.0654 | 35.487 | 36.7667 | 35.0579 | 36.2165 | 37.3098 | 38.5581 | 36.5659 | 37.9933 | 36.1059 | 38.4057 | 36.1541 | 38.1373 | 35.8494 | 37.3195 | 36.8708 | 38.3235 | 35.9734 | 39.0269 | 36.502 | 38.5802 | 39.2635 | 93.2104 | 93.4844 | 93.0921
2022-09-07 20:50 | 2:26 | 21.0127 | 21.4404 | 26.2147 | 34.1997 | 36.357 | 33.0816 | 36.0793 | 32.152 | 36.7961 | 34.5845 | 34.1169 | 38.1582 | 32.0268 | 33.9809 | 34.9871 | 33.7068 | 33.185 | 33.8206 | 34.0429 | 36.1599 | 31.6425 | 31.3163 | 33.5783 | 35.5314 | 34.1063 | 38.5033 | 36.0848 | 34.5664 | 34.0286 | 35.9008 | 33.757 | 35.3826 | 33.6951 | 34.9339 | 34.0273 | 35.8007 | 35.0936 | 35.5702 | 36.9805 | 35.1108 | 36.2492 | 37.4064 | 38.6032 | 36.6317 | 38.0211 | 36.1759 | 38.3953 | 36.2606 | 38.3358 | 35.916 | 37.3831 | 36.9286 | 38.3436 | 35.9847 | 39.0686 | 36.5326 | 38.5569 | 39.2389 | 93.3437 | 93.6299 | 93.2616
2022-09-07 20:50 | 2:26 | 22.7611 | 23.735 | 27.8056 | 34.5753 | 36.4486 | 33.3603 | 36.2399 | 32.3314 | 36.8871 | 34.5854 | 34.273 | 38.3979 | 32.3172 | 34.0938 | 34.9896 | 33.8071 | 33.3436 | 34.1454 | 34.2478 | 36.384 | 31.7482 | 31.3566 | 33.6898 | 35.6607 | 34.1215 | 38.4213 | 36.119 | 34.7681 | 34.1242 | 36.0377 | 33.8411 | 35.4318 | 33.8256 | 35.0776 | 34.0732 | 35.831 | 35.2704 | 35.6868 | 36.9276 | 35.2086 | 36.3089 | 37.4067 | 38.7405 | 36.7585 | 38.0589 | 36.2715 | 38.432 | 36.3567 | 38.2952 | 35.9858 | 37.4871 | 36.9776 | 38.2777 | 36.0122 | 38.9905 | 36.5849 | 38.7033 | 39.2245 | 93.5378 | 93.8087 | 93.335
2022-09-07 20:51 | 2:26 | 24.2022 | 25.6412 | 28.8512 | 34.7902 | 36.477 | 33.4407 | 36.42 | 32.5014 | 36.8941 | 34.8284 | 34.5131 | 38.2642 | 32.5103 | 34.2898 | 35.205 | 33.8647 | 33.4898 | 34.3006 | 34.2537 | 36.5783 | 31.8536 | 31.3944 | 33.8188 | 35.8589 | 34.1784 | 38.4 | 36.146 | 34.681 | 34.233 | 36.1626 | 33.9267 | 35.4404 | 33.9523 | 35.1026 | 34.1405 | 35.8375 | 35.3266 | 35.7358 | 37.0813 | 35.2446 | 36.3145 | 37.4759 | 38.7126 | 36.8549 | 38.0802 | 36.3145 | 38.4219 | 36.4394 | 38.3683 | 36.0687 | 37.552 | 37.0536 | 38.3319 | 36.0798 | 39.0448 | 36.6532 | 38.7546 | 39.2319 | 93.6577 | 93.9737 | 93.4818
2022-09-07 20:51 | 2:27 | 25.4097 | 27.1782 | 29.6401 | 35.1159 | 36.4765 | 33.5537 | 36.5278 | 32.7082 | 36.8695 | 34.8804 | 34.8062 | 38.3187 | 32.7077 | 34.3261 | 35.2095 | 33.8897 | 33.6675 | 34.4525 | 34.3441 | 36.6496 | 31.9596 | 31.4217 | 33.9677 | 35.9647 | 34.2516 | 38.5355 | 36.2165 | 34.7479 | 34.2175 | 36.1623 | 33.9781 | 35.3183 | 34.0358 | 35.1981 | 34.1748 | 35.8238 | 35.446 | 35.8285 | 37.1988 | 35.3107 | 36.4316 | 37.5252 | 38.7574 | 36.9275 | 38.2047 | 36.3034 | 38.5344 | 36.5177 | 38.4024 | 36.0652 | 37.5984 | 37.1033 | 38.4779 | 36.1452 | 39.0975 | 36.6936 | 38.7333 | 39.3456 | 93.8431 | 94.094 | 93.5812
2022-09-07 20:51 | 2:27 | 26.4258 | 28.4179 | 30.116 | 35.3259 | 36.5003 | 33.7424 | 36.603 | 32.8584 | 36.8765 | 34.9764 | 34.7298 | 38.3219 | 32.8743 | 34.448 | 35.438 | 33.9368 | 33.8183 | 34.6231 | 34.3698 | 36.6426 | 32.0651 | 31.4712 | 34.081 | 36.1388 | 34.3131 | 38.5605 | 36.2492 | 34.8486 | 34.2039 | 36.2393 | 34.058 | 35.3689 | 34.1134 | 35.32 | 34.2712 | 35.9391 | 35.4393 | 35.8939 | 37.2343 | 35.3631 | 36.4267 | 37.5628 | 38.7614 | 37.021 | 38.3317 | 36.3725 | 38.5026 | 36.5868 | 38.4324 | 36.1864 | 37.5744 | 37.2046 | 38.4877 | 36.1847 | 39.1904 | 36.7756 | 38.8259 | 39.3055 | 93.9229 | 94.2357 | 93.7226
2022-09-07 20:51 | 2:27 | 27.2467 | 29.3017 | 30.4526 | 35.5144 | 36.5106 | 33.8739 | 36.6872 | 32.9789 | 36.9152 | 35.0753 | 34.9259 | 38.3901 | 32.962 | 34.5216 | 35.5128 | 33.9817 | 33.8762 | 34.7121 | 34.484 | 36.7085 | 32.1841 | 31.5053 | 34.2108 | 36.1712 | 34.3591 | 38.5475 | 36.3089 | 34.7846 | 34.2215 | 36.2141 | 34.1182 | 35.6068 | 34.2139 | 35.4113 | 34.352 | 36.1309 | 35.4847 | 35.9627 | 37.2529 | 35.4183 | 36.4734 | 37.6202 | 38.8549 | 37.0951 | 38.2912 | 36.422 | 38.5892 | 36.6682 | 38.571 | 36.2577 | 37.6479 | 37.215 | 38.5039 | 36.2484 | 39.3012 | 36.838 | 38.7631 | 39.3369 | 94.0341 | 94.2586 | 93.8185
2022-09-07 20:51 | 2:27 | 27.87 | 29.9674 | 30.6738 | 35.6944 | 36.5694 | 33.8429 | 36.8 | 33.1214 | 36.9365 | 35.2002 | 35.174 | 38.4311 | 33.1092 | 34.5434 | 35.4796 | 33.9994 | 33.9988 | 34.8164 | 34.4962 | 36.8908 | 32.322 | 31.5218 | 34.361 | 36.2241 | 34.4204 | 38.6161 | 36.3145 | 34.7217 | 34.2598 | 36.3478 | 34.1781 | 35.5598 | 34.272 | 35.471 | 34.3656 | 36.1001 | 35.4924 | 36.0435 | 37.3209 | 35.4572 | 36.5375 | 37.6618 | 38.8829 | 37.2441 | 38.3532 | 36.4799 | 38.5796 | 36.7617 | 38.5464 | 36.3004 | 37.748 | 37.3296 | 38.5204 | 36.2777 | 39.1281 | 36.8887 | 38.8248 | 39.361 | 94.1655 | 94.2961 | 93.7755
2022-09-07 20:51 | 2:27 | 28.405 | 30.4306 | 30.8535 | 35.7809 | 36.5832 | 33.9079 | 36.7956 | 33.2035 | 36.9354 | 35.2745 | 35.3775 | 38.3767 | 33.1879 | 34.6906 | 35.544 | 34.0233 | 34.0817 | 34.8508 | 34.5729 | 37.0466 | 32.4582 | 31.5592 | 34.5187 | 36.2638 | 34.467 | 38.7236 | 36.4316 | 34.7935 | 34.3025 | 36.3895 | 34.2395 | 35.6271 | 34.3655 | 35.5083 | 34.4484 | 36.1962 | 35.5411 | 36.0917 | 37.254 | 35.5018 | 36.5675 | 37.7703 | 38.9537 | 37.307 | 38.3921 | 36.5284 | 38.6125 | 36.8573 | 38.6354 | 36.3969 | 37.8573 | 37.3876 | 38.4734 | 36.3634 | 39.1868 | 36.9705 | 38.9109 | 39.3225 | 94.3448 | 94.3662 | 93.9406
2022-09-07 20:52 | 2:28 | 28.7951 | 30.769 | 31.0688 | 35.8731 | 36.5421 | 34.091 | 36.8315 | 33.3028 | 36.9741 | 35.1938 | 35.2701 | 38.3771 | 33.2689 | 34.7033 | 35.6385 | 34.055 | 34.1865 | 34.8924 | 34.5815 | 37.0744 | 32.586 | 31.5838 | 34.6843 | 36.3868 | 34.5859 | 38.6194 | 36.4267 | 35.0282 | 34.3823 | 36.3157 | 34.3163 | 35.5298 | 34.4412 | 35.5243 | 34.5034 | 36.1314 | 35.6249 | 36.1202 | 37.2869 | 35.5379 | 36.6401 | 37.828 | 38.9997 | 37.3817 | 38.4926 | 36.5649 | 38.6098 | 36.9341 | 38.6805 | 36.4211 | 37.8678 | 37.4248 | 38.4943 | 36.4179 | 39.207 | 37.0243 | 38.9441 | 39.4234 | 94.5448 | 94.5101 | 94.0548
2022-09-07 20:52 | 2:28 | 29.1169 | 30.9754 | 31.1172 | 36.0703 | 36.5853 | 34.0466 | 36.8111 | 33.3462 | 36.9799 | 35.2421 | 35.3654 | 38.3835 | 33.3439 | 34.7659 | 35.7151 | 34.0842 | 34.2899 | 34.9674 | 34.653 | 37.1176 | 32.7345 | 31.5959 | 34.8709 | 36.4878 | 34.6385 | 38.7637 | 36.4734 | 35.0907 | 34.4222 | 36.5159 | 34.4018 | 35.6099 | 34.5281 | 35.6165 | 34.5496 | 36.1853 | 35.6391 | 36.1707 | 37.3931 | 35.5708 | 36.6613 | 37.8623 | 39.0581 | 37.4498 | 38.5318 | 36.567 | 38.6494 | 36.9982 | 38.7267 | 36.4969 | 37.8846 | 37.515 | 38.5975 | 36.4672 | 39.2203 | 37.0882 | 39.0281 | 39.4005 | 94.6986 | 94.6325 | 94.2085
2022-09-07 20:52 | 2:28 | 29.3955 | 31.1488 | 31.2273 | 36.0681 | 36.6039 | 34.1748 | 36.7801 | 33.4851 | 36.9984 | 35.3405 | 35.3599 | 38.3592 | 33.411 | 34.8574 | 35.6192 | 34.1411 | 34.3114 | 35.0466 | 34.7121 | 37.1423 | 32.8692 | 31.622 | 35.0331 | 36.5341 | 34.6993 | 38.8514 | 36.5375 | 35.1232 | 34.529 | 36.5069 | 34.5098 | 35.6643 | 34.5954 | 35.696 | 34.6265 | 36.125 | 35.6502 | 36.2081 | 37.3501 | 35.638 | 36.5887 | 37.8959 | 39.0849 | 37.5613 | 38.588 | 36.6464 | 38.7683 | 37.102 | 38.8015 | 36.553 | 37.9986 | 37.5608 | 38.6434 | 36.566 | 39.2773 | 37.161 | 39.04 | 39.4056 | 94.8501 | 94.7473 | 94.2556
2022-09-07 20:52 | 2:28 | 29.6099 | 31.2933 | 31.3183 | 36.0418 | 36.6075 | 34.2833 | 36.91 | 33.6157 | 36.9949 | 35.4757 | 35.4295 | 38.5497 | 33.4591 | 34.8299 | 35.7929 | 34.1575 | 34.3892 | 35.0627 | 34.7753 | 37.1736 | 33.0355 | 31.6181 | 35.2026 | 36.5832 | 34.7481 | 38.9269 | 36.5675 | 35.1651 | 34.4605 | 36.553 | 34.5645 | 35.7734 | 34.6233 | 35.7334 | 34.6951 | 36.242 | 35.7259 | 36.2992 | 37.3897 | 35.6998 | 36.6936 | 37.9357 | 39.1189 | 37.5845 | 38.6927 | 36.6919 | 38.8182 | 37.1557 | 38.8086 | 36.568 | 38.0133 | 37.5964 | 38.6075 | 36.6285 | 39.3814 | 37.2302 | 39.0975 | 39.4127 | 94.9651 | 94.9193 | 94.3209
2022-09-07 20:52 | 2:28 | 29.8023 | 31.3576 | 31.4217 | 36.154 | 36.6135 | 34.3548 | 36.994 | 33.6884 | 37.0206 | 35.4723 | 35.6053 | 38.5105 | 33.5421 | 34.9057 | 35.834 | 34.1966 | 34.443 | 35.1283 | 34.7912 | 37.1727 | 33.1572 | 31.655 | 35.3561 | 36.666 | 34.7933 | 38.9434 | 36.6401 | 35.2346 | 34.6446 | 36.5794 | 34.6364 | 35.7127 | 34.7197 | 35.7818 | 34.767 | 36.293 | 35.7853 | 36.3167 | 37.4829 | 35.7115 | 36.698 | 38.0207 | 39.2214 | 37.6607 | 38.69 | 36.7735 | 38.7811 | 37.2324 | 38.9019 | 36.6552 | 38.1137 | 37.6509 | 38.6367 | 36.6266 | 39.3285 | 37.2926 | 39.1124 | 39.409 | 95.0156 | 95.0081 | 94.374
2022-09-07 20:52 | 2:28 | 30.5209 | 27.3261 | 31.0955 | 36.2033 | 36.6302 | 34.316 | 36.9567 | 33.582 | 37.0432 | 35.4856 | 35.5135 | 38.4436 | 33.5758 | 34.9211 | 35.8286 | 34.2058 | 34.5047 | 35.1888 | 34.8029 | 37.1606 | 33.6073 | 28.5085 | 34.9184 | 36.6798 | 34.8037 | 39.0315 | 36.6613 | 35.1428 | 34.627 | 36.5434 | 34.5221 | 35.8126 | 34.7433 | 35.7852 | 34.7477 | 36.3999 | 35.8092 | 36.3708 | 37.4875 | 35.7502 | 36.7934 | 37.9666 | 39.1045 | 37.4953 | 38.6163 | 36.764 | 38.8387 | 37.0534 | 38.8115 | 36.5798 | 37.9448 | 37.6107 | 38.7528 | 36.7366 | 39.2298 | 37.1434 | 38.9293 | 39.4799 | 95.1002 | 95.0932 | 94.3987
2022-09-07 20:53 | 2:28 | 31.2501 | 31.2169 | 31.358 | 36.2044 | 36.6583 | 34.4466 | 36.9849 | 33.6925 | 37.0961 | 35.5112 | 35.7324 | 38.4843 | 33.6934 | 35.0103 | 35.8871 | 34.2626 | 34.5833 | 35.2191 | 34.8606 | 37.2499 | 33.6228 | 31.1099 | 34.749 | 36.7102 | 34.8072 | 38.9538 | 36.5887 | 35.2118 | 34.6194 | 36.5841 | 34.5187 | 35.7859 | 34.7854 | 35.781 | 34.7376 | 36.3378 | 35.8507 | 36.3427 | 37.4539 | 35.7894 | 36.8664 | 37.9266 | 39.0633 | 37.3867 | 38.5801 | 36.7169 | 38.7851 | 37.052 | 38.6856 | 36.5677 | 37.8946 | 37.5841 | 38.6699 | 36.6627 | 39.3905 | 37.1487 | 38.9748 | 39.4441 | 95.1397 | 95.2527 | 94.5176
2022-09-07 20:53 | 2:29 | 32.5331 | 31.8805 | 31.6005 | 36.2374 | 36.6841 | 34.5244 | 37.0743 | 33.8311 | 37.1113 | 35.6171 | 35.8513 | 38.6195 | 33.7679 | 35.0976 | 35.8689 | 34.3525 | 34.6553 | 35.3165 | 34.9587 | 37.1888 | 33.832 | 31.5503 | 34.968 | 36.7686 | 34.8929 | 38.9882 | 36.6936 | 35.3352 | 34.6501 | 36.6483 | 34.6286 | 35.904 | 34.8948 | 35.8765 | 34.8412 | 36.4049 | 35.9457 | 36.4152 | 37.4795 | 35.8698 | 36.8865 | 37.9652 | 39.0909 | 37.4563 | 38.5515 | 36.756 | 38.8927 | 37.1106 | 38.8086 | 36.5927 | 37.9431 | 37.6138 | 38.686 | 36.6769 | 39.3967 | 37.2303 | 38.9922 | 39.4988 | 95.0854 | 95.2104 | 94.47
2022-09-07 20:53 | 2:29 | 33.6398 | 31.8686 | 31.7703 | 36.4943 | 36.7292 | 34.6044 | 37.1343 | 33.9075 | 37.1567 | 35.6846 | 35.7498 | 38.6151 | 33.8611 | 35.1011 | 35.913 | 34.399 | 34.7842 | 35.306 | 34.9895 | 37.2397 | 34.1694 | 31.6921 | 35.235 | 36.844 | 34.9577 | 38.9534 | 36.698 | 35.4259 | 34.771 | 36.6966 | 34.7569 | 35.9015 | 34.9843 | 35.9597 | 34.9311 | 36.4419 | 35.9753 | 36.4836 | 37.5521 | 35.9264 | 36.9729 | 38.0384 | 39.1233 | 37.5706 | 38.7187 | 36.8399 | 38.9108 | 37.2118 | 38.8192 | 36.6683 | 38.0453 | 37.6482 | 38.7625 | 36.8401 | 39.4946 | 37.2872 | 39.0922 | 39.6799 | 94.921 | 95.0319 | 94.3071
2022-09-07 20:53 | 2:29 | 34.3182 | 31.8636 | 32.06 | 36.466 | 36.7661 | 34.6776 | 37.2074 | 33.9956 | 37.1514 | 35.678 | 35.7926 | 38.5399 | 33.9521 | 35.1738 | 36.0057 | 34.466 | 34.8256 | 35.3715 | 35.0842 | 37.3433 | 34.558 | 31.7249 | 35.4964 | 36.8727 | 35.0594 | 38.9986 | 36.7934 | 35.3406 | 34.7452 | 36.7939 | 34.9072 | 36.0076 | 35.0576 | 35.9988 | 35.0093 | 36.5193 | 36.0643 | 36.5304 | 37.5534 | 35.9855 | 37.0133 | 38.0859 | 39.182 | 37.7044 | 38.7811 | 36.8524 | 38.9185 | 37.3157 | 38.9069 | 36.7494 | 38.068 | 37.7629 | 38.8233 | 36.8478 | 39.504 | 37.3824 | 39.0637 | 39.6161 | 94.668 | 94.8556 | 94.1331
2022-09-07 20:53 | 2:29 | 34.9425 | 31.8947 | 32.4705 | 36.5947 | 36.764 | 34.7866 | 37.2834 | 34.0815 | 37.2023 | 35.7129 | 35.8065 | 38.5233 | 34.0094 | 35.2553 | 36.0216 | 34.5361 | 34.8713 | 35.4766 | 35.1434 | 37.4395 | 34.9042 | 31.7768 | 35.7762 | 37.0244 | 35.1487 | 39.1022 | 36.8664 | 35.4484 | 34.8709 | 36.8316 | 35.0798 | 36.0849 | 35.1739 | 36.1008 | 35.1411 | 36.5592 | 36.1211 | 36.6154 | 37.5479 | 36.0829 | 37.0369 | 38.1999 | 39.2272 | 37.8105 | 38.8449 | 36.9607 | 38.9637 | 37.4155 | 39.0623 | 36.858 | 38.1714 | 37.8367 | 38.8388 | 36.8894 | 39.553 | 37.4893 | 39.2264 | 39.5939 | 94.4678 | 94.6289 | 94.007
2022-09-07 20:53 | 2:29 | 35.2563 | 31.8727 | 32.912 | 36.6792 | 36.8203 | 34.7826 | 37.2478 | 34.1576 | 37.2536 | 35.8296 | 36.0295 | 38.5118 | 34.1688 | 35.3434 | 36.2397 | 34.5918 | 34.9834 | 35.5952 | 35.2512 | 37.5152 | 35.1689 | 31.7723 | 35.9697 | 37.132 | 35.2452 | 39.2239 | 36.8865 | 35.515 | 34.9659 | 36.9413 | 35.1999 | 36.0959 | 35.282 | 36.2201 | 35.2142 | 36.5662 | 36.2274 | 36.677 | 37.6324 | 36.1688 | 37.0927 | 38.2528 | 39.3189 | 37.8924 | 38.8364 | 37.026 | 39.0596 | 37.5194 | 39.0744 | 36.929 | 38.2123 | 37.9018 | 39.0062 | 37.0229 | 39.6393 | 37.5687 | 39.2115 | 39.5804 | 94.2419 | 94.4401 | 93.8691
2022-09-07 20:54 | 2:29 | 35.3908 | 31.8765 | 33.1752 | 36.7948 | 36.8411 | 34.9615 | 37.3422 | 34.3496 | 37.248 | 35.9401 | 36.0157 | 38.5237 | 34.1877 | 35.3921 | 36.3093 | 34.6406 | 35.0485 | 35.6272 | 35.2938 | 37.4992 | 35.2352 | 31.789 | 36.0955 | 37.1802 | 35.365 | 39.1326 | 36.9729 | 35.5279 | 35.0847 | 36.9742 | 35.2839 | 36.0615 | 35.4013 | 36.2958 | 35.3014 | 36.6729 | 36.3155 | 36.7704 | 37.7154 | 36.2217 | 37.2157 | 38.2766 | 39.3513 | 38.0138 | 38.9241 | 37.0422 | 39.122 | 37.615 | 39.1162 | 37.0261 | 38.2966 | 37.9667 | 38.9356 | 37.1309 | 39.6409 | 37.6519 | 39.2236 | 39.6309 | 94.0482 | 94.224 | 93.7845
2022-09-07 20:54 | 2:30 | 35.3735 | 31.905 | 33.1949 | 36.9284 | 36.8676 | 35.0582 | 37.2983 | 34.3449 | 37.2957 | 35.9483 | 36.0798 | 38.5544 | 34.2472 | 35.4697 | 36.3133 | 34.6964 | 35.1199 | 35.6873 | 35.3927 | 37.5073 | 35.2587 | 31.8108 | 36.1736 | 37.3315 | 35.407 | 39.2805 | 37.0133 | 35.5405 | 35.2388 | 36.9864 | 35.3632 | 36.1535 | 35.4866 | 36.3141 | 35.3659 | 36.6747 | 36.4381 | 36.8315 | 37.8432 | 36.3023 | 37.2065 | 38.3772 | 39.4166 | 38.0663 | 38.9834 | 37.0956 | 39.1659 | 37.6681 | 39.204 | 37.0699 | 38.3175 | 38.0276 | 38.9902 | 37.1767 | 39.6581 | 37.7209 | 39.2761 | 39.6845 | 93.9394 | 94.0943 | 93.7143
2022-09-07 20:54 | 2:30 | 35.4484 | 31.936 | 33.2072 | 37.0475 | 36.9236 | 35.1373 | 37.3389 | 34.4239 | 37.2956 | 36.0303 | 36.1629 | 38.6252 | 34.384 | 35.57 | 36.3203 | 34.7864 | 35.2141 | 35.7026 | 35.4362 | 37.6412 | 35.282 | 31.8163 | 36.2651 | 37.4245 | 35.4934 | 39.3681 | 37.0369 | 35.6162 | 35.2145 | 37.0376 | 35.4666 | 36.2183 | 35.5402 | 36.4251 | 35.4568 | 36.7313 | 36.5061 | 36.8664 | 37.8371 | 36.3461 | 37.3269 | 38.4092 | 39.4459 | 38.1348 | 39.037 | 37.1495 | 39.1496 | 37.7433 | 39.2683 | 37.0646 | 38.3688 | 38.1068 | 39.0832 | 37.2154 | 39.6754 | 37.7796 | 39.2843 | 39.7199 | 93.8906 | 94.0447 | 93.7268
2022-09-07 20:54 | 2:30 | 35.5222 | 31.9406 | 33.297 | 37.0775 | 36.9293 | 35.0681 | 37.3337 | 34.4607 | 37.3705 | 36.0026 | 36.3412 | 38.7088 | 34.5027 | 35.6149 | 36.5104 | 34.8385 | 35.318 | 35.7709 | 35.4919 | 37.6679 | 35.3708 | 31.8595 | 36.352 | 37.4942 | 35.5487 | 39.4608 | 37.0927 | 35.7653 | 35.2394 | 37.1202 | 35.5318 | 36.2902 | 35.604 | 36.441 | 35.5408 | 36.8095 | 36.5481 | 36.9094 | 37.9476 | 36.4379 | 37.3574 | 38.4432 | 39.4781 | 38.2308 | 39.1123 | 37.1802 | 39.2096 | 37.8375 | 39.3169 | 37.1917 | 38.4688 | 38.1596 | 39.1843 | 37.2691 | 39.7275 | 37.85 | 39.4362 | 39.7644 | 93.858 | 93.9986 | 93.7157
2022-09-07 20:54 | 2:30 | 35.7448 | 31.9693 | 33.4737 | 37.1252 | 36.9747 | 35.1287 | 37.2766 | 34.4973 | 37.4041 | 36.0847 | 36.3395 | 38.7087 | 34.5684 | 35.6117 | 36.5601 | 34.8701 | 35.4156 | 35.8462 | 35.5327 | 37.7377 | 35.5076 | 31.8791 | 36.4827 | 37.4948 | 35.6112 | 39.4692 | 37.2157 | 35.736 | 35.4029 | 37.2783 | 35.6308 | 36.3591 | 35.6951 | 36.5104 | 35.603 | 36.8087 | 36.6112 | 37.0263 | 37.9352 | 36.4917 | 37.4905 | 38.5662 | 39.5705 | 38.3075 | 39.1855 | 37.2369 | 39.2211 | 37.9125 | 39.366 | 37.2753 | 38.5622 | 38.2271 | 39.2067 | 37.3527 | 39.673 | 37.911 | 39.5258 | 39.8215 | 93.7397 | 93.8577 | 93.6305
2022-09-07 20:54 | 2:30 | 35.9656 | 31.996 | 33.6971 | 37.1476 | 37.0176 | 35.2784 | 37.3469 | 34.6114 | 37.4339 | 36.1143 | 36.4015 | 38.7501 | 34.6596 | 35.6999 | 36.691 | 34.917 | 35.4754 | 35.9142 | 35.6259 | 37.8334 | 35.7522 | 31.884 | 36.6324 | 37.5894 | 35.6904 | 39.4734 | 37.2065 | 35.8299 | 35.4861 | 37.2403 | 35.7213 | 36.4173 | 35.8046 | 36.5988 | 35.6885 | 36.8631 | 36.6733 | 37.0585 | 37.9275 | 36.5286 | 37.5107 | 38.6061 | 39.5747 | 38.3841 | 39.213 | 37.3076 | 39.3145 | 37.9783 | 39.4808 | 37.2729 | 38.5805 | 38.298 | 39.1805 | 37.3786 | 39.7321 | 37.9768 | 39.5602 | 39.9086 | 93.6338 | 93.7597 | 93.5724
2022-09-07 20:55 | 2:31 | 36.2326 | 32.0654 | 33.8985 | 37.2232 | 37.0383 | 35.368 | 37.3541 | 34.7204 | 37.4871 | 36.2635 | 36.5058 | 38.7463 | 34.7554 | 35.8096 | 36.5884 | 34.9911 | 35.5033 | 36.0318 | 35.7099 | 37.8897 | 36.0544 | 32.1771 | 36.8105 | 37.7114 | 35.7732 | 39.7537 | 37.3269 | 35.8468 | 35.5474 | 37.4326 | 35.8443 | 36.5448 | 35.8553 | 36.6901 | 35.7955 | 37.0189 | 36.7611 | 37.1276 | 38.0256 | 36.5942 | 37.5989 | 38.6531 | 39.5893 | 38.4715 | 39.3659 | 37.3597 | 39.3359 | 38.0661 | 39.5222 | 37.3741 | 38.6758 | 38.3428 | 39.214 | 37.5305 | 39.8218 | 38.0563 | 39.558 | 39.9307 | 93.6042 | 93.6939 | 93.5229
2022-09-07 20:55 | 2:31 | 36.5106 | 32.128 | 34.052 | 37.5284 | 37.0927 | 35.4993 | 37.3976 | 34.835 | 37.5241 | 36.3628 | 36.4935 | 38.8278 | 34.9127 | 35.8506 | 36.6986 | 35.0628 | 35.6327 | 36.1116 | 35.792 | 37.9674 | 36.4216 | 33.4599 | 37.0358 | 37.7496 | 35.834 | 39.6969 | 37.3574 | 35.9699 | 35.6393 | 37.4151 | 35.9507 | 36.4883 | 35.9881 | 36.7555 | 35.8568 | 37.0147 | 36.8311 | 37.1889 | 38.1018 | 36.6696 | 37.6681 | 38.7093 | 39.7006 | 38.5465 | 39.3149 | 37.4184 | 39.4175 | 38.1479 | 39.5635 | 37.4601 | 38.7145 | 38.4171 | 39.1471 | 37.536 | 39.9011 | 38.1272 | 39.6489 | 39.9903 | 93.5735 | 93.6382 | 93.5148
2022-09-07 20:55 | 2:31 | 36.6526 | 32.201 | 34.1618 | 37.5276 | 37.1284 | 35.6347 | 37.5046 | 34.9564 | 37.5648 | 36.4317 | 36.5787 | 38.7822 | 35.0273 | 35.9643 | 36.8126 | 35.151 | 35.7337 | 36.1767 | 35.8487 | 38.0213 | 36.841 | 34.7288 | 37.2488 | 37.8605 | 35.9824 | 39.8617 | 37.4905 | 36.0312 | 35.7679 | 37.5696 | 36.0626 | 36.5765 | 36.071 | 36.8587 | 35.9782 | 37.0826 | 36.9325 | 37.269 | 38.2024 | 36.7018 | 37.6585 | 38.7748 | 39.745 | 38.634 | 39.4447 | 37.492 | 39.4631 | 38.2156 | 39.5999 | 37.5409 | 38.7937 | 38.4771 | 39.2931 | 37.691 | 39.8599 | 38.1818 | 39.6821 | 40.0616 | 93.4532 | 93.5306 | 93.3939
2022-09-07 20:55 | 2:31 | 36.651 | 32.3248 | 34.3785 | 37.6703 | 37.1425 | 35.7309 | 37.5962 | 35.084 | 37.6154 | 36.4721 | 36.6675 | 38.8613 | 35.1762 | 36.0414 | 36.8947 | 35.1963 | 35.8306 | 36.3122 | 35.9405 | 38.1373 | 37.2303 | 35.4764 | 37.4406 | 37.9055 | 36.0547 | 39.9292 | 37.5107 | 36.2026 | 35.856 | 37.6304 | 36.1963 | 36.6681 | 36.1645 | 36.9343 | 36.0883 | 37.1364 | 36.9674 | 37.3714 | 38.2453 | 36.8362 | 37.8533 | 38.8716 | 39.7703 | 38.7065 | 39.4763 | 37.5674 | 39.4686 | 38.3047 | 39.647 | 37.562 | 38.8882 | 38.5848 | 39.3963 | 37.7567 | 39.9286 | 38.2849 | 39.697 | 40.0492 | 93.3907 | 93.4768 | 93.3759
2022-09-07 20:55 | 2:31 | 36.671 | 32.4705 | 34.6161 | 37.9215 | 37.2027 | 35.8679 | 37.5909 | 35.2299 | 37.6546 | 36.5856 | 36.8015 | 38.8513 | 35.255 | 36.2217 | 36.9112 | 35.3211 | 35.9464 | 36.4048 | 36.0444 | 38.2958 | 37.6036 | 36.4101 | 37.6761 | 37.9852 | 36.1228 | 40.0444 | 37.5989 | 36.1989 | 35.8706 | 37.6835 | 36.3065 | 36.6721 | 36.252 | 37.0539 | 36.2157 | 37.2299 | 36.985 | 37.4686 | 38.2613 | 36.9293 | 37.8717 | 38.9419 | 39.8224 | 38.8172 | 39.5646 | 37.6457 | 39.5416 | 38.4031 | 39.7504 | 37.6529 | 38.9115 | 38.6472 | 39.422 | 37.8069 | 39.926 | 38.3454 | 39.7758 | 40.1169 | 93.3436 | 93.3925 | 93.3519
2022-09-07 20:55 | 2:31 | 36.456 | 32.6643 | 34.8704 | 38.0132 | 37.2794 | 35.9651 | 37.759 | 35.2985 | 37.7062 | 36.6574 | 36.9467 | 38.8449 | 35.4513 | 36.3371 | 37.1172 | 35.4595 | 36.0451 | 36.4779 | 36.1453 | 38.2778 | 37.8796 | 36.7338 | 37.847 | 38.0542 | 36.2415 | 39.9839 | 37.6681 | 36.2302 | 36.0826 | 37.7464 | 36.4531 | 36.7235 | 36.3581 | 37.1424 | 36.3408 | 37.3022 | 37.0254 | 37.5252 | 38.2853 | 37.0327 | 37.9981 | 38.9935 | 39.8749 | 38.8963 | 39.6699 | 37.7034 | 39.6228 | 38.4595 | 39.829 | 37.7685 | 39.003 | 38.6938 | 39.5591 | 37.8708 | 39.9409 | 38.4192 | 39.8522 | 40.1447 | 93.2433 | 93.3875 | 93.2899
2022-09-07 20:56 | 2:31 | 36.0314 | 32.7928 | 35.1356 | 38.0086 | 37.3233 | 36.0879 | 37.8211 | 35.4309 | 37.751 | 36.7479 | 37.0404 | 38.8804 | 35.5622 | 36.4286 | 37.2268 | 35.5391 | 36.2133 | 36.6414 | 36.2223 | 38.388 | 38.0785 | 37.1253 | 38.0297 | 38.2037 | 36.3471 | 39.8782 | 37.6585 | 36.3886 | 36.1177 | 37.7629 | 36.562 | 36.8585 | 36.4742 | 37.2469 | 36.4323 | 37.3558 | 37.1178 | 37.6204 | 38.3394 | 37.1041 | 38.0989 | 39.1014 | 39.9029 | 38.9535 | 39.708 | 37.7887 | 39.6763 | 38.5549 | 39.8646 | 37.8068 | 39.0492 | 38.7702 | 39.658 | 37.9384 | 40.0081 | 38.4941 | 39.8423 | 40.1808 | 93.1137 | 93.3199 | 93.2317
2022-09-07 20:56 | 2:32 | 35.7 | 32.8933 | 35.4075 | 38.1499 | 37.3582 | 36.2165 | 38.0294 | 35.6247 | 37.8316 | 36.8483 | 37.06 | 38.9414 | 35.7012 | 36.5295 | 37.2808 | 35.603 | 36.3147 | 36.7273 | 36.322 | 38.3907 | 38.2512 | 37.3956 | 38.1996 | 38.267 | 36.4582 | 40.0943 | 37.8533 | 36.5658 | 36.1468 | 37.993 | 36.6947 | 36.937 | 36.5697 | 37.3515 | 36.5218 | 37.4169 | 37.2122 | 37.6955 | 38.3884 | 37.1688 | 38.1097 | 39.1231 | 40.0141 | 39.0776 | 39.7882 | 37.8244 | 39.7038 | 38.632 | 39.9365 | 37.8728 | 39.1218 | 38.8571 | 39.6129 | 37.9848 | 40.0524 | 38.5739 | 39.9316 | 40.252 | 93.057 | 93.1885 | 93.1628
2022-09-07 20:56 | 2:32 | 35.4276 | 33.1148 | 35.6316 | 38.2395 | 37.4271 | 36.3485 | 38.0256 | 35.7293 | 37.8786 | 36.9195 | 37.177 | 38.9952 | 35.7512 | 36.5906 | 37.328 | 35.6857 | 36.3698 | 36.7904 | 36.4175 | 38.4496 | 38.4072 | 37.6126 | 38.3296 | 38.4044 | 36.5854 | 40.1805 | 37.8717 | 36.5014 | 36.303 | 38.0085 | 36.7801 | 37.0181 | 36.702 | 37.4555 | 36.668 | 37.5093 | 37.2886 | 37.7975 | 38.4072 | 37.2486 | 38.118 | 39.2297 | 40.0446 | 39.1703 | 39.7959 | 37.8669 | 39.801 | 38.7116 | 40.0125 | 37.9005 | 39.1666 | 38.9289 | 39.6817 | 38.0472 | 40.1646 | 38.6496 | 39.9125 | 40.2736 | 92.923 | 93.0501 | 93.106
2022-09-07 20:56 | 2:32 | 35.2785 | 33.477 | 35.8833 | 38.4124 | 37.4868 | 36.4588 | 37.989 | 35.8887 | 37.9255 | 37.0669 | 37.2719 | 39.0073 | 35.8953 | 36.7124 | 37.3939 | 35.7927 | 36.5404 | 36.9018 | 36.5448 | 38.6918 | 38.5534 | 37.7629 | 38.4819 | 38.444 | 36.6408 | 40.2246 | 37.9981 | 36.6673 | 36.4075 | 38.0591 | 36.8857 | 37.1156 | 36.8036 | 37.5408 | 36.7494 | 37.555 | 37.34 | 37.869 | 38.4512 | 37.3464 | 38.2166 | 39.3069 | 40.0995 | 39.2602 | 39.8922 | 37.9442 | 39.8499 | 38.7999 | 40.0453 | 38.0353 | 39.2662 | 38.9745 | 39.7149 | 38.1756 | 40.2158 | 38.7213 | 40.0774 | 40.3987 | 92.8657 | 92.9614 | 93.0475
2022-09-07 20:56 | 2:32 | 35.2074 | 33.9988 | 36.1111 | 38.4835 | 37.5542 | 36.6054 | 38.02 | 36.0178 | 37.9875 | 37.1208 | 37.3487 | 39.102 | 36.034 | 36.7621 | 37.5258 | 35.8688 | 36.6013 | 36.9932 | 36.6202 | 38.7552 | 38.6823 | 37.8681 | 38.6262 | 38.6404 | 36.7588 | 40.3911 | 38.0989 | 36.7375 | 36.532 | 38.0932 | 36.9932 | 37.1592 | 36.9005 | 37.6238 | 36.8715 | 37.64 | 37.4538 | 37.9652 | 38.5449 | 37.4428 | 38.2897 | 39.3699 | 40.1573 | 39.3294 | 39.9372 | 38.0284 | 39.8759 | 38.8887 | 40.1342 | 38.1158 | 39.3314 | 39.0454 | 39.7854 | 38.2674 | 40.2032 | 38.8062 | 40.1465 | 40.4053 | 92.716 | 92.7624 | 92.8898
2022-09-07 20:56 | 2:32 | 35.3024 | 34.4396 | 36.3298 | 38.6376 | 37.6026 | 36.6523 | 38.1233 | 36.0963 | 38.0409 | 37.2397 | 37.5243 | 39.2466 | 36.1514 | 36.8809 | 37.567 | 35.9672 | 36.7563 | 37.1264 | 36.6923 | 38.7644 | 38.8217 | 38.0078 | 38.763 | 38.6372 | 36.8926 | 40.3074 | 38.1097 | 36.8188 | 36.7084 | 38.2012 | 37.0951 | 37.1562 | 37.0155 | 37.7312 | 36.9644 | 37.7381 | 37.5021 | 38.0192 | 38.6284 | 37.5277 | 38.4289 | 39.4303 | 40.1985 | 39.4306 | 40.0152 | 38.0883 | 39.9497 | 38.9759 | 40.1898 | 38.1492 | 39.3877 | 39.1043 | 39.8215 | 38.3328 | 40.2333 | 38.8729 | 40.1618 | 40.4626 | 92.6093 | 92.6397 | 92.8425
2022-09-07 20:57 | 2:33 | 35.4183 | 34.7788 | 36.5435 | 38.7544 | 37.6632 | 36.8706 | 38.1406 | 36.2345 | 38.1265 | 37.4964 | 37.6426 | 39.233 | 36.2994 | 37.0074 | 37.6392 | 36.0573 | 36.8273 | 37.2538 | 36.8017 | 38.9072 | 38.9268 | 38.1136 | 38.8783 | 38.7262 | 36.9648 | 40.4494 | 38.118 | 36.9412 | 36.7288 | 38.3061 | 37.1692 | 37.2735 | 37.1327 | 37.7918 | 37.0923 | 37.8111 | 37.5729 | 38.096 | 38.6823 | 37.6145 | 38.4735 | 39.5308 | 40.2744 | 39.507 | 40.0981 | 38.1662 | 40.0627 | 39.0673 | 40.3134 | 38.2441 | 39.4475 | 39.1972 | 39.8901 | 38.4124 | 40.2932 | 38.9273 | 40.2168 | 40.5127 | 92.5396 | 92.5549 | 92.7875
2022-09-07 20:57 | 2:33 | 35.5568 | 35.0534 | 36.7197 | 38.8208 | 37.7433 | 36.878 | 38.1724 | 36.3372 | 38.1707 | 37.4614 | 37.7498 | 39.2558 | 36.4265 | 37.0331 | 37.7661 | 36.1858 | 36.9315 | 37.3098 | 36.8976 | 38.9337 | 39.0332 | 38.1429 | 38.9936 | 38.8332 | 37.0784 | 40.5283 | 38.2166 | 37.0201 | 36.9139 | 38.4237 | 37.2904 | 37.4405 | 37.245 | 37.8873 | 37.1857 | 37.9022 | 37.6588 | 38.1878 | 38.6888 | 37.6664 | 38.5057 | 39.5776 | 40.3116 | 39.5724 | 40.1641 | 38.2314 | 40.0963 | 39.1328 | 40.358 | 38.3413 | 39.5511 | 39.2438 | 39.9873 | 38.47 | 40.2929 | 38.9981 | 40.294 | 40.5444 | 92.4476 | 92.4384 | 92.7506
2022-09-07 20:57 | 2:33 | 35.8039 | 35.3527 | 36.9092 | 38.8888 | 37.8143 | 37.0229 | 38.2237 | 36.471 | 38.2484 | 37.5596 | 37.7819 | 39.3277 | 36.5946 | 37.1472 | 37.8332 | 36.2935 | 37.0349 | 37.4101 | 37.0122 | 39.0864 | 39.1349 | 38.2144 | 39.0898 | 38.9339 | 37.2216 | 40.5914 | 38.2897 | 37.0257 | 37.0014 | 38.4806 | 37.4008 | 37.4677 | 37.3479 | 37.9664 | 37.3459 | 37.9551 | 37.7539 | 38.2712 | 38.7603 | 37.777 | 38.6653 | 39.6718 | 40.3729 | 39.6834 | 40.2708 | 38.3068 | 40.1328 | 39.2312 | 40.4155 | 38.4163 | 39.5853 | 39.3423 | 39.971 | 38.6351 | 40.4156 | 39.096 | 40.354 | 40.5426 | 92.3264 | 92.3208 | 92.6806
2022-09-07 20:57 | 2:33 | 36.0852 | 35.6809 | 37.0745 | 39.0211 | 37.8929 | 37.1145 | 38.373 | 36.6176 | 38.3038 | 37.6351 | 37.9283 | 39.4215 | 36.6845 | 37.2511 | 38.0108 | 36.3599 | 37.2023 | 37.5264 | 37.0802 | 39.17 | 39.2319 | 38.2741 | 39.1744 | 39.0016 | 37.3301 | 40.6137 | 38.4289 | 37.2859 | 37.0834 | 38.5665 | 37.4706 | 37.5561 | 37.4589 | 38.0598 | 37.4439 | 38.0516 | 37.8483 | 38.3523 | 38.7855 | 37.8424 | 38.5781 | 39.7149 | 40.4052 | 39.7677 | 40.2771 | 38.4031 | 40.2087 | 39.3133 | 40.4276 | 38.5381 | 39.6397 | 39.4158 | 40.0667 | 38.7062 | 40.4144 | 39.1598 | 40.3721 | 40.7617 | 92.2805 | 92.2324 | 92.6096
2022-09-07 20:57 | 2:33 | 36.2322 | 35.9933 | 37.2744 | 39.2682 | 37.9498 | 37.2255 | 38.4486 | 36.7376 | 38.3871 | 37.6938 | 38.0076 | 39.428 | 36.8519 | 37.4481 | 37.9715 | 36.4862 | 37.2888 | 37.6445 | 37.1969 | 39.1827 | 39.3238 | 38.2946 | 39.2874 | 39.1616 | 37.4124 | 40.6344 | 38.4735 | 37.2904 | 37.164 | 38.5973 | 37.5664 | 37.6696 | 37.5515 | 38.1474 | 37.5277 | 38.1255 | 37.9183 | 38.3989 | 38.934 | 37.9175 | 38.4487 | 39.7886 | 40.4558 | 39.8514 | 40.3049 | 38.431 | 40.2951 | 39.3646 | 40.5529 | 38.601 | 39.6798 | 39.4438 | 40.1399 | 38.8505 | 40.4434 | 39.2241 | 40.4014 | 40.7195 | 92.0908 | 92.0923 | 92.4551
2022-09-07 20:57 | 2:33 | 36.3776 | 36.2769 | 37.4319 | 39.2293 | 38.0284 | 37.3459 | 38.5088 | 36.8902 | 38.446 | 37.819 | 38.1762 | 39.5002 | 36.9543 | 37.5394 | 38.1894 | 36.5945 | 37.4266 | 37.7316 | 37.3039 | 39.3561 | 39.4332 | 38.4427 | 39.3809 | 39.2266 | 37.5813 | 40.7537 | 38.5057 | 37.4017 | 37.2993 | 38.6607 | 37.6928 | 37.8197 | 37.6719 | 38.2475 | 37.661 | 38.2247 | 37.9974 | 38.4744 | 38.9583 | 38.033 | 38.2694 | 39.8488 | 40.5113 | 39.9261 | 40.3571 | 38.512 | 40.3385 | 39.4551 | 40.5432 | 38.6392 | 39.7806 | 39.5192 | 40.2342 | 38.864 | 40.4757 | 39.3132 | 40.563 | 40.7462 | 91.8738 | 91.9058 | 92.338
2022-09-07 20:58 | 2:33 | 36.5496 | 36.5227 | 37.5749 | 39.4182 | 38.1237 | 37.4843 | 38.5855 | 37.0044 | 38.4849 | 37.9733 | 38.2163 | 39.6141 | 37.0331 | 37.6665 | 38.3021 | 36.6928 | 37.4997 | 37.8117 | 37.4452 | 39.3731 | 39.2747 | 38.3051 | 39.4439 | 39.3162 | 37.6055 | 40.7201 | 38.6653 | 37.4351 | 37.4053 | 38.749 | 37.799 | 37.7752 | 37.7765 | 38.3376 | 37.7341 | 38.2679 | 38.0732 | 38.565 | 39.0406 | 38.1051 | 38.0712 | 39.9558 | 40.5663 | 39.9921 | 40.4914 | 38.5541 | 40.4164 | 39.5173 | 40.5988 | 38.7116 | 39.8254 | 39.623 | 40.3492 | 38.9275 | 40.5696 | 39.3939 | 40.5198 | 40.8424 | 91.7797 | 91.7805 | 92.3116
2022-09-07 20:58 | 2:34 | 35.8851 | 35.7588 | 37.0433 | 39.5269 | 38.2031 | 37.5823 | 38.6702 | 37.1144 | 38.5789 | 38.0297 | 38.3513 | 39.632 | 37.1036 | 37.6988 | 38.421 | 36.8302 | 37.5707 | 37.7814 | 37.4737 | 39.4358 | 35.6891 | 36.4745 | 38.3212 | 39.4073 | 37.6219 | 40.6192 | 38.5781 | 37.4731 | 37.4142 | 38.7004 | 37.5312 | 37.8359 | 37.7352 | 38.3796 | 37.7473 | 38.309 | 38.1413 | 38.6167 | 39.0793 | 38.1822 | 37.9027 | 39.9043 | 40.5174 | 39.9049 | 40.4119 | 38.5992 | 40.4297 | 39.392 | 40.5913 | 38.6734 | 39.7524 | 39.5601 | 40.3742 | 38.9454 | 40.6114 | 39.2759 | 40.5337 | 40.9062 | 91.7223 | 91.7047 | 92.24
2022-09-07 20:58 | 2:34 | 31.6648 | 30.9881 | 34.045 | 39.1006 | 38.243 | 37.3814 | 38.5702 | 36.9103 | 38.63 | 37.8655 | 38.1695 | 39.7631 | 36.7683 | 37.2834 | 38.1988 | 36.7349 | 37.4417 | 37.4895 | 37.2809 | 39.2669 | 34.5975 | 30.8329 | 36.9499 | 39.2343 | 37.4132 | 40.5081 | 38.4487 | 37.3399 | 37.2912 | 38.4252 | 37.0029 | 37.8266 | 37.4294 | 38.1193 | 37.5909 | 38.2016 | 38.0683 | 38.3959 | 39.0161 | 38.0825 | 37.8036 | 39.739 | 40.3211 | 39.5335 | 40.1334 | 38.5445 | 40.2627 | 39.0315 | 40.3373 | 38.4245 | 39.3723 | 39.3798 | 40.2069 | 38.7606 | 40.6071 | 39.032 | 40.2446 | 40.9401 | 91.7182 | 91.7239 | 92.3143
2022-09-07 20:58 | 2:34 | 29.6519 | 29.5265 | 32.1974 | 38.6796 | 38.2276 | 37.1583 | 38.4957 | 36.5939 | 38.5973 | 37.6402 | 38.0054 | 39.6932 | 36.3755 | 37.076 | 37.9948 | 36.5712 | 37.1886 | 37.1832 | 37.0447 | 39.015 | 33.0901 | 29.2262 | 34.7409 | 39.0123 | 37.1168 | 40.1779 | 38.2694 | 37.0996 | 36.9485 | 38.1417 | 36.2916 | 37.7641 | 37.1279 | 37.775 | 37.2001 | 37.9788 | 37.9822 | 38.2547 | 38.8212 | 37.9064 | 37.7938 | 39.4549 | 40.1208 | 38.9508 | 39.7329 | 38.4098 | 40.0703 | 38.5821 | 39.989 | 38.0699 | 39.0527 | 39.1283 | 39.9823 | 38.5091 | 40.4839 | 38.7332 | 39.9848 | 40.8678 | 91.7918 | 91.788 | 92.3451
2022-09-07 20:58 | 2:34 | 30.4257 | 29.3557 | 31.6211 | 38.2651 | 38.2915 | 36.8891 | 38.512 | 36.4288 | 38.6102 | 37.489 | 38.0235 | 39.7357 | 36.2354 | 36.9706 | 37.95 | 36.5074 | 37.0407 | 37.0051 | 37.0203 | 38.9402 | 30.2165 | 28.5488 | 33.4658 | 38.7936 | 36.9022 | 39.656 | 38.0712 | 37.0179 | 36.6621 | 37.9141 | 35.9205 | 37.6531 | 36.9912 | 37.4956 | 36.8873 | 37.8293 | 37.828 | 38.0675 | 38.8938 | 37.7415 | 37.776 | 39.2294 | 39.9681 | 38.5571 | 39.5097 | 38.2578 | 40.0384 | 38.2795 | 39.777 | 37.8807 | 38.9156 | 38.9853 | 39.7807 | 38.4224 | 40.2858 | 38.5491 | 39.7659 | 40.795 | 91.9688 | 91.9348 | 92.4785
2022-09-07 20:58 | 2:34 | 28.0406 | 29.2138 | 31.001 | 38.0611 | 38.3595 | 36.6541 | 38.4789 | 36.3429 | 38.6448 | 37.3694 | 37.9807 | 39.729 | 36.108 | 36.9455 | 38.0295 | 36.4223 | 36.9269 | 36.935 | 36.8309 | 38.8322 | 27.4448 | 27.937 | 32.64 | 38.4868 | 36.782 | 39.4782 | 37.9027 | 36.8715 | 36.5795 | 37.7687 | 35.6135 | 37.6227 | 36.9119 | 37.2971 | 36.8193 | 37.6665 | 37.7744 | 37.8918 | 38.704 | 37.6463 | 37.6954 | 39.1407 | 39.9209 | 38.3616 | 39.3014 | 38.216 | 39.9541 | 38.0533 | 39.5837 | 37.7919 | 38.8291 | 38.8338 | 39.6743 | 38.3041 | 40.313 | 38.4883 | 39.6556 | 40.7087 | 92.0162 | 92.0004 | 92.4862
2022-09-07 20:59 | 2:35 | 28.659 | 29.0853 | 31.2059 | 37.7966 | 38.3907 | 36.6667 | 38.5192 | 36.2989 | 38.6764 | 37.3213 | 37.9122 | 39.6924 | 36.0703 | 36.8997 | 37.9571 | 36.3572 | 36.8617 | 36.8281 | 36.8024 | 38.6847 | 26.8573 | 27.4801 | 32.1774 | 38.3254 | 36.7099 | 39.598 | 37.8036 | 36.9112 | 36.529 | 37.7401 | 35.2784 | 37.6014 | 36.8493 | 37.1267 | 36.534 | 37.6261 | 37.7012 | 37.7473 | 38.6182 | 37.5953 | 37.6612 | 39.0252 | 39.8205 | 38.1884 | 39.1774 | 38.1616 | 39.9132 | 37.9577 | 39.4556 | 37.6614 | 38.8365 | 38.764 | 39.5959 | 38.2616 | 40.1656 | 38.379 | 39.7198 | 40.6588 | 92.1669 | 92.1259 | 92.535
2022-09-07 20:59 | 2:35 | 30.3156 | 28.977 | 31.7384 | 37.8975 | 38.4445 | 36.6945 | 38.5564 | 36.3201 | 38.6786 | 37.2915 | 37.9783 | 39.7737 | 35.9857 | 36.9476 | 37.8988 | 36.3452 | 36.7968 | 36.8218 | 36.8337 | 38.6696 | 26.5823 | 27.3041 | 31.8181 | 38.1625 | 36.6372 | 39.5204 | 37.7938 | 36.8818 | 36.4137 | 37.7108 | 35.1118 | 37.6695 | 36.8148 | 37.0845 | 36.4477 | 37.6101 | 37.6599 | 37.7762 | 38.5869 | 37.5008 | 37.6387 | 39.0246 | 39.8427 | 37.9971 | 39.1408 | 38.1415 | 39.8895 | 37.9062 | 39.4456 | 37.7093 | 38.5766 | 38.7424 | 39.5006 | 38.183 | 40.307 | 38.2868 | 39.6033 | 40.6472 | 92.2322 | 92.2239 | 92.5801
2022-09-07 20:59 | 2:35 | 30.9642 | 28.8407 | 31.9941 | 37.8518 | 38.5599 | 36.6373 | 38.5695 | 36.2816 | 38.7195 | 37.3057 | 38.0622 | 39.8451 | 36.0067 | 36.9627 | 37.9517 | 36.3331 | 36.836 | 36.8672 | 36.8624 | 38.6318 | 26.4465 | 27.5254 | 31.6089 | 38.1756 | 36.5926 | 39.3763 | 37.776 | 36.9623 | 36.4008 | 37.6582 | 35.0146 | 37.7024 | 36.8329 | 37.0222 | 36.3669 | 37.5692 | 37.6089 | 37.7668 | 38.6411 | 37.3968 | 37.6345 | 38.9374 | 39.7274 | 37.8857 | 39.1317 | 38.1015 | 39.7887 | 37.7008 | 39.3724 | 37.6156 | 38.6323 | 38.6898 | 39.4814 | 38.1679 | 40.2455 | 38.2279 | 39.6495 | 40.6634 | 92.3514 | 92.2943 | 92.6458
2022-09-07 20:59 | 2:35 | 31.2503 | 28.6719 | 31.9202 | 37.8954 | 38.622 | 36.7474 | 38.5779 | 36.2361 | 38.756 | 37.3378 | 38.0484 | 39.8352 | 36.0447 | 36.9403 | 37.8602 | 36.3538 | 36.8521 | 36.8918 | 36.9184 | 38.6797 | 26.3382 | 26.8007 | 31.363 | 38.0595 | 36.5533 | 39.3254 | 37.6954 | 36.9594 | 36.351 | 37.6379 | 34.8698 | 37.6576 | 36.8739 | 36.9911 | 36.3666 | 37.6669 | 37.6978 | 37.6973 | 38.6638 | 37.4954 | 37.5493 | 38.8684 | 39.6328 | 37.7944 | 39.1365 | 38.0943 | 39.7012 | 37.6249 | 39.2272 | 37.5248 | 38.8586 | 38.6287 | 39.5336 | 38.1043 | 40.1975 | 38.1164 | 39.5246 | 40.6884 | 92.4018 | 92.4118 | 92.6956
2022-09-07 20:59 | 2:35 | 31.289 | 28.508 | 31.7469 | 37.8651 | 38.681 | 36.6347 | 38.6617 | 36.1637 | 38.7563 | 37.3274 | 37.933 | 39.7981 | 35.9539 | 36.8749 | 37.9219 | 36.4003 | 36.8167 | 36.9013 | 36.9338 | 38.7994 | 26.6767 | 26.4245 | 31.228 | 38.0467 | 36.4881 | 39.2203 | 37.6612 | 37.0535 | 36.3359 | 37.5582 | 34.8063 | 37.6301 | 36.7821 | 36.9565 | 36.1905 | 37.5978 | 37.653 | 37.7028 | 38.7025 | 37.4447 | 37.4888 | 38.7833 | 39.5869 | 37.7857 | 39.0169 | 38.0618 | 39.709 | 37.465 | 39.277 | 37.4799 | 38.6487 | 38.5634 | 39.5244 | 38.1389 | 40.0597 | 38.1 | 39.4839 | 40.6118 | 92.4969 | 92.4515 | 92.768
2022-09-07 20:59 | 2:35 | 31.1758 | 28.404 | 31.5474 | 37.826 | 38.7386 | 36.6004 | 38.6307 | 36.1093 | 38.7925 | 37.2572 | 37.9987 | 39.7924 | 35.8795 | 36.8524 | 37.9296 | 36.4072 | 36.7955 | 36.8315 | 36.9591 | 38.7254 | 26.9762 | 26.2257 | 31.0745 | 37.8431 | 36.4811 | 39.1438 | 37.6387 | 37.0757 | 36.3259 | 37.6442 | 34.6937 | 37.5423 | 36.7253 | 36.9101 | 36.0854 | 37.5933 | 37.6823 | 37.6429 | 38.7197 | 37.4173 | 37.49 | 38.7199 | 39.5765 | 37.7659 | 38.9228 | 38.0694 | 39.7052 | 37.4229 | 39.17 | 37.4422 | 39.0537 | 38.4804 | 39.444 | 38.1852 | 39.9388 | 38.0173 | 39.3774 | 40.7014 | 92.6147 | 92.5598 | 92.8195
2022-09-07 21:00 | 2:35 | 30.9274 | 28.2951 | 31.2758 | 37.6959 | 38.7923 | 36.5278 | 38.6012 | 36.0893 | 38.7846 | 37.1738 | 38.0389 | 39.8683 | 35.812 | 36.8218 | 37.9763 | 36.4259 | 36.7603 | 36.7501 | 36.9516 | 38.5834 | 27.0275 | 26.0134 | 30.8777 | 37.816 | 36.438 | 38.9994 | 37.6345 | 37.0365 | 36.3121 | 37.5092 | 34.5675 | 37.5808 | 36.7272 | 36.93 | 36.0514 | 37.5598 | 37.5843 | 37.626 | 38.7038 | 37.3208 | 37.4487 | 38.7094 | 39.5675 | 37.7585 | 38.8631 | 38.0448 | 39.6786 | 37.2674 | 39.1238 | 37.4151 | 38.7103 | 38.4437 | 39.6804 | 38.1884 | 39.9922 | 37.9871 | 39.3757 | 40.5727 | 92.7791 | 92.6989 | 92.857
2022-09-07 21:00 | 2:36 | 30.689 | 28.2894 | 31.0089 | 37.5567 | 38.8876 | 36.4105 | 38.6583 | 35.9706 | 38.8368 | 37.1836 | 37.936 | 39.8363 | 35.7718 | 36.7576 | 37.8146 | 36.4311 | 36.7247 | 36.773 | 36.9105 | 38.598 | 27.0032 | 25.9369 | 30.8508 | 37.8261 | 36.3703 | 39.1171 | 37.5493 | 36.897 | 36.3199 | 37.5322 | 34.5759 | 37.6969 | 36.7494 | 36.8797 | 36.0394 | 37.5215 | 37.6904 | 37.6108 | 38.7606 | 37.4173 | 37.4075 | 38.7018 | 39.5209 | 37.6293 | 38.8462 | 37.9851 | 39.6473 | 37.2067 | 39.0972 | 37.3891 | 38.5871 | 38.348 | 39.552 | 38.0667 | 40.049 | 37.9456 | 39.4094 | 40.5728 | 92.8132 | 92.8206 | 92.9432
2022-09-07 21:00 | 2:36 | 30.3856 | 29.6647 | 30.7925 | 37.5878 | 38.9145 | 36.3798 | 38.6235 | 36.0489 | 38.8596 | 37.2083 | 38.0142 | 39.8985 | 35.7561 | 36.8033 | 37.8809 | 36.4768 | 36.7173 | 36.77 | 36.9116 | 38.5147 | 27.0812 | 25.8806 | 31.0132 | 37.6934 | 36.3238 | 39.2747 | 37.4888 | 36.9311 | 36.3248 | 37.5183 | 34.5153 | 37.6749 | 36.7438 | 36.8107 | 35.8423 | 37.5658 | 37.5353 | 37.506 | 38.7104 | 37.2597 | 37.4202 | 38.6423 | 39.4925 | 37.5842 | 38.8129 | 37.9304 | 39.5472 | 37.2458 | 39.0849 | 37.3768 | 38.7571 | 38.3839 | 39.5344 | 38.1064 | 40.0252 | 37.79 | 39.1639 | 40.5928 | 92.9668 | 92.9642 | 93.0628
2022-09-07 21:00 | 2:36 | 29.1681 | 29.548 | 30.22 | 37.4514 | 38.931 | 36.327 | 38.6269 | 35.9326 | 38.8735 | 37.1068 | 37.9715 | 39.8645 | 35.6811 | 36.7346 | 37.7694 | 36.4382 | 36.6533 | 36.7044 | 36.9368 | 38.5427 | 27.5457 | 25.6766 | 31.4892 | 37.684 | 36.3235 | 39.1239 | 37.49 | 37.0033 | 36.2405 | 37.5337 | 34.5361 | 37.5916 | 36.6216 | 36.7944 | 35.8415 | 37.5472 | 37.4667 | 37.5569 | 38.6168 | 37.2106 | 37.4 | 38.6247 | 39.4254 | 37.511 | 38.808 | 37.8393 | 39.5746 | 37.19 | 39.0156 | 37.3238 | 38.5941 | 38.3626 | 39.4764 | 38.1809 | 39.8319 | 37.7962 | 39.2689 | 40.6285 | 93.0709 | 93.094 | 93.0741
2022-09-07 21:00 | 2:36 | 26.746 | 29.3556 | 29.7102 | 37.2834 | 39.0103 | 36.2889 | 38.6254 | 35.9127 | 38.9047 | 37.0495 | 37.9694 | 39.8716 | 35.6422 | 36.7124 | 37.7979 | 36.4315 | 36.5961 | 36.7969 | 36.8978 | 38.4173 | 28.0468 | 25.6984 | 31.7011 | 37.6362 | 36.2828 | 38.9947 | 37.4487 | 36.8533 | 36.2559 | 37.4531 | 34.6067 | 37.656 | 36.5547 | 36.7778 | 35.923 | 37.4919 | 37.6192 | 37.5581 | 38.6319 | 37.2607 | 37.3892 | 38.6283 | 39.434 | 37.4695 | 38.7951 | 37.8954 | 39.5877 | 37.1149 | 38.9972 | 37.2845 | 38.7631 | 38.2284 | 39.4291 | 38.1474 | 39.841 | 37.7876 | 39.243 | 40.6189 | 93.1373 | 93.1413 | 93.0789
2022-09-07 21:00 | 2:36 | 26.1854 | 28.6952 | 29.4026 | 37.3685 | 39.0265 | 36.2751 | 38.6646 | 35.7468 | 38.8845 | 37.0402 | 37.7684 | 39.9338 | 35.5732 | 36.6711 | 37.7725 | 36.4217 | 36.5557 | 36.5805 | 36.9252 | 38.3827 | 28.4841 | 25.6108 | 31.885 | 37.7051 | 36.2681 | 39.0668 | 37.4075 | 36.7867 | 36.2578 | 37.4417 | 34.5854 | 37.5158 | 36.5213 | 36.7377 | 35.9078 | 37.3909 | 37.5652 | 37.4737 | 38.598 | 37.2852 | 37.3303 | 38.5575 | 39.4116 | 37.5161 | 38.7352 | 37.8701 | 39.4938 | 37.1009 | 39.2426 | 37.3318 | 38.5037 | 38.1925 | 39.3565 | 37.9502 | 40.0282 | 37.7807 | 39.1428 | 40.6912 | 93.2878 | 93.2634 | 93.2031
2022-09-07 21:01 | 2:37 | 25.9261 | 27.615 | 29.1542 | 37.1685 | 39.0361 | 36.1333 | 38.6608 | 35.8786 | 38.9286 | 36.9874 | 37.7506 | 39.9394 | 35.5029 | 36.593 | 37.7608 | 36.4425 | 36.5094 | 36.5375 | 36.9118 | 38.3244 | 28.686 | 25.4285 | 31.8798 | 37.593 | 36.2467 | 39.11 | 37.4202 | 36.7847 | 36.2372 | 37.391 | 34.5778 | 37.5707 | 36.4865 | 36.711 | 35.8702 | 37.3843 | 37.4178 | 37.4977 | 38.5844 | 37.1761 | 37.3111 | 38.5019 | 39.4501 | 37.4502 | 38.7083 | 37.8566 | 39.5804 | 37.0508 | 39.0437 | 37.2627 | 38.5121 | 38.2093 | 39.4531 | 37.998 | 39.952 | 37.7918 | 39.1561 | 40.6197 | 93.5485 | 93.4172 | 93.4249
2022-09-07 21:01 | 2:37 | 25.7851 | 27.3606 | 28.9372 | 37.0915 | 39.0524 | 36.1081 | 38.5715 | 35.7623 | 38.9257 | 36.9331 | 37.725 | 39.9231 | 35.4523 | 36.6116 | 37.7833 | 36.3641 | 36.4623 | 36.485 | 36.8047 | 38.2933 | 28.6719 | 25.3327 | 31.679 | 37.4846 | 36.1679 | 39.2334 | 37.4 | 36.7069 | 36.2009 | 37.3891 | 34.4804 | 37.6334 | 36.4315 | 36.5773 | 35.6856 | 37.4556 | 37.3562 | 37.3453 | 38.5222 | 37.122 | 37.2713 | 38.4484 | 39.4675 | 37.4273 | 38.7373 | 37.7823 | 39.4988 | 36.9222 | 38.9688 | 37.2419 | 38.6016 | 38.1108 | 39.3866 | 37.879 | 40.0396 | 37.6732 | 39.1684 | 40.5613 | 93.6363 | 93.5679 | 93.5
2022-09-07 21:01 | 2:37 | 25.5278 | 27.1191 | 28.7394 | 37.0609 | 39.0624 | 36.0698 | 38.6185 | 35.753 | 38.9183 | 36.8999 | 37.6132 | 39.8597 | 35.3855 | 36.5344 | 37.7362 | 36.4013 | 36.4061 | 36.4829 | 36.8048 | 38.2508 | 28.4928 | 25.2013 | 31.4536 | 37.4556 | 36.1025 | 39.1888 | 37.3892 | 36.8408 | 36.16 | 37.3265 | 34.3849 | 37.4633 | 36.3748 | 36.5865 | 35.7013 | 37.3284 | 37.4228 | 37.3044 | 38.6033 | 37.0865 | 37.1396 | 38.4746 | 39.4141 | 37.3989 | 38.7013 | 37.8095 | 39.4014 | 36.8701 | 38.9597 | 37.2054 | 38.5941 | 38.1455 | 39.3075 | 37.8407 | 39.9215 | 37.5759 | 39.1023 | 40.5512 | 93.8571 | 93.7135 | 93.5252
2022-09-07 21:01 | 2:37 | 25.2863 | 26.8327 | 28.5132 | 37.0097 | 39.0715 | 36.0972 | 38.5125 | 35.6294 | 38.9521 | 36.8716 | 37.5589 | 39.9596 | 35.4029 | 36.4378 | 37.6611 | 36.4044 | 36.3559 | 36.3704 | 36.8025 | 38.3719 | 28.2073 | 25.0305 | 31.2525 | 37.3306 | 36.0483 | 39.0134 | 37.3303 | 36.6013 | 36.1225 | 37.2887 | 34.2441 | 37.3967 | 36.3217 | 36.4986 | 35.6563 | 37.28 | 37.3278 | 37.253 | 38.5455 | 37.0591 | 37.0849 | 38.3531 | 39.4043 | 37.2891 | 38.7045 | 37.7681 | 39.4235 | 36.8064 | 38.8957 | 37.1504 | 38.4322 | 37.9584 | 39.3837 | 37.8582 | 39.8673 | 37.4856 | 39.0474 | 40.4425 | 93.9867 | 93.9017 | 93.604
2022-09-07 21:01 | 2:37 | 25.1295 | 26.6492 | 28.3289 | 36.9455 | 39.0606 | 35.8858 | 38.4213 | 35.6668 | 38.935 | 36.9122 | 37.568 | 39.9295 | 35.3116 | 36.3559 | 37.6018 | 36.4144 | 36.2851 | 36.272 | 36.7899 | 38.389 | 27.9042 | 24.8226 | 31.0514 | 37.2353 | 35.9757 | 38.9741 | 37.3111 | 36.6168 | 36.1067 | 37.3109 | 34.183 | 37.5418 | 36.2529 | 36.443 | 35.507 | 37.3634 | 37.2142 | 37.2623 | 38.4943 | 36.9254 | 37.0855 | 38.2575 | 39.3449 | 37.1078 | 38.4886 | 37.6904 | 39.3074 | 36.6867 | 38.8028 | 37.117 | 38.5086 | 37.9828 | 39.2499 | 37.849 | 39.9439 | 37.4398 | 39.0592 | 40.3587 | 94.1528 | 94.1003 | 93.671
2022-09-07 21:01 | 2:37 | 24.8879 | 26.3869 | 28.1166 | 36.7562 | 39.0735 | 35.7534 | 38.3903 | 35.6015 | 38.945 | 36.8566 | 37.5037 | 39.9243 | 35.251 | 36.3892 | 37.6068 | 36.3678 | 36.2157 | 36.3195 | 36.7432 | 38.2753 | 27.5503 | 24.7259 | 30.68 | 37.2709 | 35.9228 | 38.9702 | 37.2713 | 36.5959 | 36.0863 | 37.1531 | 34.0193 | 37.4212 | 36.2424 | 36.3462 | 35.4113 | 37.267 | 37.31 | 37.2256 | 38.5023 | 36.9787 | 37.0069 | 38.1931 | 39.2668 | 37.07 | 38.5055 | 37.6457 | 39.4271 | 36.5664 | 38.7787 | 36.9689 | 38.4594 | 37.7976 | 39.3066 | 37.7417 | 39.8823 | 37.3733 | 38.969 | 40.3244 | 94.2691 | 94.2446 | 93.7784
2022-09-07 21:02 | 2:38 | 24.6865 | 26.1392 | 27.8776 | 36.6727 | 39.0685 | 35.7997 | 38.4182 | 35.557 | 38.9405 | 36.8436 | 37.5914 | 39.9111 | 35.1481 | 36.3297 | 37.5173 | 36.3526 | 36.1472 | 36.2582 | 36.6601 | 38.1428 | 27.1965 | 24.5273 | 30.3907 | 37.1354 | 35.8439 | 38.9342 | 37.1396 | 36.5174 | 35.9804 | 37.0795 | 33.8373 | 37.246 | 36.1987 | 36.2856 | 35.3117 | 37.1662 | 37.2162 | 37.1549 | 38.4432 | 36.8439 | 36.9707 | 38.0656 | 39.2367 | 36.9615 | 38.5178 | 37.585 | 39.2442 | 36.4799 | 38.6545 | 36.938 | 38.1131 | 37.6299 | 39.1879 | 37.5662 | 39.8764 | 37.3257 | 38.9094 | 40.5324 | 94.4332 | 94.3484 | 93.9486
2022-09-07 21:02 | 2:38 | 24.5063 | 25.947 | 27.7249 | 36.6344 | 39.0361 | 35.8315 | 38.4251 | 35.3961 | 38.9068 | 36.7345 | 37.3716 | 39.8132 | 35.0781 | 36.2443 | 37.4061 | 36.3249 | 36.0774 | 36.2027 | 36.6982 | 38.1191 | 26.9353 | 24.4546 | 30.2095 | 37.0469 | 35.7569 | 38.7717 | 37.0849 | 36.5622 | 35.9337 | 37.0515 | 33.7331 | 37.3143 | 36.0282 | 36.2319 | 35.1628 | 37.1446 | 37.2643 | 37.0733 | 38.5219 | 36.9196 | 36.8632 | 38.0272 | 39.1976 | 36.8887 | 38.3643 | 37.5463 | 39.2745 | 36.4477 | 38.6943 | 36.8382 | 38.5829 | 37.677 | 39.2822 | 37.5181 | 39.6334 | 37.2184 | 38.9388 | 40.4218 | 94.5375 | 94.4858 | 94.0032
2022-09-07 21:02 | 2:38 | 24.335 | 25.7589 | 27.5347 | 36.6057 | 39.048 | 35.5598 | 38.472 | 35.3485 | 38.9186 | 36.5431 | 37.2557 | 39.9717 | 35.0707 | 36.1959 | 37.476 | 36.2789 | 36.0262 | 36.1509 | 36.6401 | 38.1534 | 26.6572 | 24.391 | 29.9588 | 36.9674 | 35.7037 | 38.779 | 37.0855 | 36.4431 | 35.9102 | 36.9445 | 33.6053 | 37.3516 | 36.0363 | 36.1903 | 35.1148 | 37.1739 | 37.1369 | 37.0715 | 38.4491 | 36.8315 | 36.8107 | 38.0195 | 39.0793 | 36.7816 | 38.241 | 37.5027 | 39.138 | 36.3021 | 38.5539 | 36.764 | 38.5586 | 37.5065 | 38.9934 | 37.3994 | 39.5837 | 37.118 | 38.766 | 40.5604 | 94.6632 | 94.7036 | 94.1424
2022-09-07 21:02 | 2:38 | 24.2667 | 25.6635 | 27.3877 | 36.5163 | 39.0078 | 35.576 | 38.4457 | 35.2218 | 38.9335 | 36.5871 | 37.2688 | 39.8846 | 34.9676 | 36.1743 | 37.5627 | 36.2529 | 35.9375 | 36.1957 | 36.6046 | 38.1348 | 26.418 | 24.0348 | 29.7591 | 36.8769 | 35.6344 | 38.6375 | 37.0069 | 36.4033 | 35.8629 | 36.8822 | 33.5322 | 37.1062 | 35.9771 | 36.0981 | 34.8387 | 37.0393 | 37.1449 | 36.9892 | 38.4076 | 36.6831 | 36.729 | 37.964 | 39.151 | 36.7509 | 38.2355 | 37.4701 | 39.1188 | 36.2538 | 38.6028 | 36.6868 | 38.6576 | 37.4264 | 38.9575 | 37.4279 | 39.4936 | 37.0594 | 38.7424 | 40.4668 | 94.68 | 94.8738 | 94.1682
2022-09-07 21:02 | 2:38 | 23.9862 | 25.3324 | 27.1529 | 36.3696 | 39.0333 | 35.4947 | 38.4652 | 35.1614 | 38.8607 | 36.4835 | 37.152 | 39.8502 | 34.9008 | 36.1707 | 37.3364 | 36.2228 | 35.8947 | 36.1014 | 36.5716 | 38.0288 | 26.1704 | 23.8708 | 29.5175 | 36.6759 | 35.5315 | 38.3947 | 36.9707 | 36.3155 | 35.7642 | 36.8005 | 33.4793 | 37.1992 | 35.8823 | 35.9877 | 34.7495 | 37.1024 | 36.9397 | 36.8991 | 38.3716 | 36.674 | 36.7811 | 37.867 | 39.0259 | 36.6623 | 38.1183 | 37.4348 | 39.2211 | 36.2219 | 38.59 | 36.706 | 38.4383 | 37.2282 | 39.0599 | 37.3096 | 39.6459 | 37.017 | 38.5145 | 40.4298 | 94.8965 | 94.9191 | 94.2787
2022-09-07 21:02 | 2:38 | 23.8279 | 25.2436 | 26.9773 | 36.3907 | 38.9828 | 35.5329 | 38.3605 | 35.1082 | 38.8854 | 36.5011 | 37.1715 | 39.8796 | 34.8106 | 36.1427 | 37.2434 | 36.1973 | 35.8535 | 36.1035 | 36.459 | 37.8781 | 25.9495 | 23.7075 | 29.325 | 36.6634 | 35.4743 | 38.3787 | 36.8632 | 36.4951 | 35.6875 | 36.7971 | 33.2273 | 37.2144 | 35.8524 | 35.8755 | 34.7517 | 37.0913 | 36.9371 | 36.8085 | 38.2715 | 36.5896 | 36.6232 | 37.8215 | 39.0055 | 36.5784 | 38.1024 | 37.3725 | 39.0244 | 36.1205 | 38.4326 | 36.6086 | 38.2852 | 37.2452 | 39.0221 | 37.3684 | 39.3875 | 36.8966 | 38.6458 | 40.2931 | 94.9375 | 95.0359 | 94.3061
2022-09-07 21:03 | 2:38 | 23.6413 | 24.9809 | 26.8395 | 36.267 | 38.9667 | 35.5225 | 38.295 | 35.0966 | 38.8264 | 36.4509 | 37.0674 | 39.804 | 34.7505 | 36.0177 | 37.2992 | 36.1843 | 35.8204 | 35.9284 | 36.4287 | 37.8696 | 25.7624 | 23.5311 | 29.1893 | 36.562 | 35.3882 | 38.377 | 36.8107 | 36.3413 | 35.6108 | 36.6691 | 33.2135 | 37.1113 | 35.7931 | 35.8028 | 34.681 | 36.9699 | 37.0493 | 36.8384 | 38.1775 | 36.578 | 36.5779 | 37.756 | 38.9007 | 36.4793 | 38.0296 | 37.3349 | 39.0924 | 35.9906 | 38.3581 | 36.5519 | 37.9742 | 37.1972 | 38.8805 | 37.3296 | 39.4696 | 36.8502 | 38.3853 | 40.2689 | 94.9277 | 94.9754 | 94.2597
2022-09-07 21:03 | 2:39 | 23.4764 | 24.852 | 26.638 | 36.1534 | 38.9123 | 35.2901 | 38.3367 | 35.0638 | 38.8344 | 36.3128 | 36.9361 | 39.8606 | 34.6874 | 35.9992 | 37.2878 | 36.1331 | 35.7355 | 35.7741 | 36.3435 | 37.8742 | 25.6287 | 23.346 | 29.0935 | 36.5637 | 35.3058 | 38.5003 | 36.729 | 36.2862 | 35.5976 | 36.6216 | 33.149 | 37.0243 | 35.7376 | 35.723 | 34.6815 | 36.9247 | 36.7807 | 36.684 | 38.2297 | 36.4192 | 36.4854 | 37.6329 | 38.8845 | 36.3404 | 38.009 | 37.2635 | 39.0479 | 35.9394 | 38.3863 | 36.4217 | 38.1254 | 37.1552 | 38.7101 | 37.0824 | 39.4528 | 36.7671 | 38.4542 | 40.2637 | 94.7917 | 94.9249 | 94.2057
2022-09-07 21:03 | 2:39 | 23.3593 | 24.6878 | 26.4931 | 36.1314 | 38.8947 | 35.1735 | 38.3132 | 35.0284 | 38.7832 | 36.4534 | 36.8842 | 39.9434 | 34.5722 | 35.9148 | 37.279 | 36.0812 | 35.6867 | 35.7919 | 36.3088 | 37.7758 | 25.4758 | 23.2256 | 28.9494 | 36.4217 | 35.2424 | 38.4075 | 36.7811 | 36.173 | 35.4949 | 36.624 | 33.1071 | 37.0045 | 35.6843 | 35.6792 | 34.4155 | 36.8249 | 36.8891 | 36.647 | 38.1979 | 36.4573 | 36.4908 | 37.6037 | 38.8533 | 36.3044 | 37.8592 | 37.1587 | 38.8673 | 35.7763 | 38.2301 | 36.3456 | 38.3382 | 37.0953 | 38.7529 | 37.0147 | 39.2677 | 36.681 | 38.5337 | 40.3558 | 94.5934 | 94.8143 | 94.0658
2022-09-07 21:03 | 2:39 | 23.2502 | 24.5288 | 26.3344 | 36.0288 | 38.9217 | 35.222 | 38.2696 | 34.8404 | 38.7815 | 36.2426 | 36.8332 | 39.8695 | 34.5898 | 36.0096 | 37.1692 | 36.0612 | 35.5711 | 35.7491 | 36.2913 | 37.7843 | 25.3526 | 23.0927 | 28.8223 | 36.3392 | 35.1505 | 38.4321 | 36.6232 | 36.1709 | 35.4317 | 36.505 | 32.999 | 37.013 | 35.5564 | 35.6407 | 34.3754 | 36.9041 | 36.9204 | 36.6133 | 38.1187 | 36.4761 | 36.4582 | 37.5832 | 38.7522 | 36.335 | 37.8339 | 37.1344 | 38.8347 | 35.7626 | 38.4442 | 36.255 | 38.6912 | 37.0717 | 38.7701 | 36.9664 | 39.1813 | 36.5748 | 38.5463 | 40.0698 | 94.3515 | 94.5947 | 93.9163
2022-09-07 21:03 | 2:39 | 23.101 | 24.3557 | 26.1777 | 35.9754 | 38.9178 | 34.9695 | 38.2643 | 34.8176 | 38.797 | 36.2496 | 36.8045 | 39.8302 | 34.5172 | 35.8443 | 37.0404 | 36.0501 | 35.5528 | 35.748 | 36.2374 | 37.5663 | 25.2686 | 22.945 | 28.7785 | 36.1876 | 35.1005 | 38.3024 | 36.5779 | 35.9802 | 35.4551 | 36.5083 | 32.9198 | 37.0088 | 35.6262 | 35.5306 | 34.3219 | 36.9025 | 36.7156 | 36.5403 | 38.3044 | 36.3315 | 36.3684 | 37.5846 | 38.6692 | 36.1882 | 37.8456 | 37.0815 | 38.876 | 35.5965 | 38.2971 | 36.2006 | 38.1278 | 36.9927 | 38.6853 | 36.8663 | 39.2277 | 36.5025 | 38.3977 | 40.127 | 94.2102 | 94.4256 | 93.79
2022-09-07 21:03 | 2:39 | 22.8497 | 24.0849 | 26.0053 | 35.9318 | 38.8653 | 34.9366 | 38.2039 | 34.7487 | 38.7167 | 36.227 | 36.6 | 39.7557 | 34.4971 | 35.8652 | 37.0476 | 35.9656 | 35.5179 | 35.742 | 36.1776 | 37.5622 | 25.1867 | 22.7429 | 28.6912 | 36.2662 | 35.0336 | 38.2287 | 36.4854 | 35.8961 | 35.3959 | 36.3969 | 32.8096 | 37.0111 | 35.4864 | 35.4618 | 34.2092 | 36.9192 | 36.6816 | 36.5031 | 38.2695 | 36.2935 | 36.2942 | 37.4214 | 38.5998 | 36.0695 | 37.8012 | 37.0254 | 38.7474 | 35.5264 | 38.1018 | 36.2442 | 37.7528 | 36.8396 | 38.7185 | 36.8424 | 39.2711 | 36.4453 | 38.2637 | 40.1689 | 94.0882 | 94.2629 | 93.7861
2022-09-07 21:04 | 2:40 | 22.7771 | 24.0502 | 25.8754 | 35.8561 | 38.819 | 34.945 | 38.2034 | 34.6475 | 38.7145 | 36.0894 | 36.631 | 39.7599 | 34.3642 | 35.8119 | 37.0243 | 35.9306 | 35.4418 | 35.7452 | 36.2177 | 37.5961 | 25.0679 | 22.5833 | 28.557 | 36.1872 | 34.961 | 38.1861 | 36.4908 | 35.8318 | 35.3051 | 36.3922 | 32.7191 | 36.8926 | 35.3249 | 35.4123 | 34.1713 | 36.7917 | 36.5956 | 36.4738 | 38.0662 | 36.3166 | 36.166 | 37.3749 | 38.5957 | 35.977 | 37.688 | 36.9892 | 38.6854 | 35.5163 | 38.1164 | 36.1028 | 38.0983 | 36.6633 | 38.7167 | 36.7173 | 39.0649 | 36.3718 | 38.3835 | 40.1031 | 93.991 | 94.2074 | 93.7158
2022-09-07 21:04 | 2:40 | 22.6077 | 23.8553 | 25.753 | 35.7894 | 38.7615 | 34.9532 | 38.2232 | 34.6534 | 38.6374 | 36.0423 | 36.5425 | 39.7732 | 34.2573 | 35.7655 | 36.9639 | 35.8595 | 35.3619 | 35.5809 | 36.1309 | 37.6329 | 24.9883 | 22.4287 | 28.4874 | 36.0331 | 34.8741 | 38.1022 | 36.4582 | 35.9153 | 35.2348 | 36.3064 | 32.5536 | 36.7869 | 35.2484 | 35.3496 | 33.9136 | 36.5848 | 36.6294 | 36.4197 | 37.98 | 36.1686 | 36.1763 | 37.3227 | 38.623 | 35.9732 | 37.5388 | 36.9184 | 38.6992 | 35.3906 | 37.9942 | 36.0276 | 38.3784 | 36.5478 | 38.7204 | 36.5963 | 38.9484 | 36.2774 | 38.264 | 39.8398 | 93.8743 | 94.0199 | 93.6562
2022-09-07 21:04 | 2:40 | 22.4926 | 23.7336 | 25.5827 | 35.7652 | 38.7228 | 34.8883 | 38.1608 | 34.502 | 38.5388 | 35.9501 | 36.5932 | 39.6643 | 34.2352 | 35.6279 | 36.8981 | 35.8072 | 35.2313 | 35.5094 | 36.0312 | 37.5998 | 24.8769 | 22.3896 | 28.4155 | 35.9689 | 34.7774 | 38.0075 | 36.3684 | 35.8203 | 35.0984 | 36.2768 | 32.4655 | 36.8466 | 35.2167 | 35.3071 | 33.8488 | 36.5665 | 36.4365 | 36.3778 | 38.0722 | 36.1392 | 36.1028 | 37.1637 | 38.5959 | 35.8565 | 37.4959 | 36.8649 | 38.6493 | 35.2599 | 38.0661 | 36.0431 | 38.367 | 36.5404 | 38.5403 | 36.6649 | 39.0992 | 36.2202 | 38.1788 | 39.9078 | 93.7183 | 93.9294 | 93.5924
2022-09-07 21:04 | 2:40 | 22.34 | 23.5543 | 25.4399 | 35.5221 | 38.7158 | 34.7641 | 38.167 | 34.4716 | 38.5609 | 36.0493 | 36.5209 | 39.7515 | 34.1615 | 35.5418 | 36.9122 | 35.7686 | 35.2436 | 35.4766 | 35.9905 | 37.4989 | 24.8035 | 22.2195 | 28.3659 | 35.7432 | 34.7167 | 38.0439 | 36.2942 | 35.8907 | 35.0976 | 36.2603 | 32.4019 | 36.8597 | 35.272 | 35.2978 | 34.0008 | 36.6523 | 36.7011 | 36.2362 | 38.043 | 36.3296 | 36.0485 | 37.147 | 38.4661 | 35.7689 | 37.4529 | 36.8055 | 38.547 | 35.1576 | 37.9835 | 36.0003 | 38.0525 | 36.5287 | 38.4448 | 36.4381 | 39.167 | 36.173 | 38.0245 | 39.9565 | 93.6361 | 93.8203 | 93.5426
2022-09-07 21:04 | 2:40 | 22.1874 | 23.3378 | 25.2905 | 35.4839 | 38.6887 | 34.662 | 37.9823 | 34.4693 | 38.5667 | 35.9357 | 36.5773 | 39.6758 | 34.0403 | 35.4938 | 36.846 | 35.7126 | 35.1875 | 35.3398 | 35.9586 | 37.5126 | 24.7163 | 22.0822 | 28.2685 | 35.7298 | 34.6068 | 38.1225 | 36.166 | 35.7628 | 35.0576 | 36.1047 | 32.3705 | 36.8711 | 35.1671 | 35.1838 | 34.0476 | 36.5066 | 36.7343 | 36.184 | 37.8854 | 36.2877 | 35.9802 | 37.0681 | 38.3649 | 35.677 | 37.3856 | 36.7172 | 38.5863 | 35.138 | 37.9362 | 35.9546 | 38.3424 | 36.352 | 38.5003 | 36.361 | 39.1461 | 36.0606 | 37.8957 | 39.7319 | 93.625 | 93.6753 | 93.5209
2022-09-07 21:04 | 2:40 | 22.1173 | 23.2642 | 25.1716 | 35.3755 | 38.6429 | 34.6613 | 38.0596 | 34.4671 | 38.5116 | 35.9528 | 36.5086 | 39.7342 | 33.9238 | 35.4333 | 36.7185 | 35.703 | 35.0582 | 35.3663 | 35.9495 | 37.4213 | 24.6087 | 21.922 | 28.1977 | 35.6701 | 34.5472 | 38.0708 | 36.1763 | 35.584 | 34.9502 | 36.1043 | 32.3265 | 36.7997 | 35.0965 | 35.1039 | 33.961 | 36.5622 | 36.6067 | 36.1407 | 37.9502 | 36.1977 | 35.9156 | 37.0498 | 38.3122 | 35.7171 | 37.3389 | 36.6446 | 38.5848 | 35.1224 | 37.788 | 35.8132 | 38.0553 | 36.3973 | 38.3504 | 36.3971 | 38.9744 | 35.9724 | 37.9592 | 39.7542 | 93.5765 | 93.6668 | 93.5
2022-09-07 21:05 | 2:40 | 21.8956 | 23.0547 | 25.034 | 35.3716 | 38.5902 | 34.5127 | 38.0098 | 34.4226 | 38.4805 | 35.717 | 36.4132 | 39.7436 | 33.9036 | 35.4789 | 36.6799 | 35.6309 | 35.0468 | 35.3832 | 35.8162 | 37.2974 | 24.537 | 21.7857 | 28.1288 | 35.66 | 34.4522 | 38.0115 | 36.1028 | 35.6571 | 34.8972 | 36.0941 | 32.3388 | 36.6447 | 34.8886 | 35.0286 | 33.6204 | 36.5239 | 36.5351 | 36.2145 | 38.0042 | 36.1325 | 35.8717 | 37.0355 | 38.2482 | 35.5192 | 37.2915 | 36.616 | 38.475 | 34.988 | 37.6401 | 35.751 | 37.9728 | 36.2425 | 38.3453 | 36.2886 | 39.1934 | 35.8773 | 37.6403 | 39.8202 | 93.5436 | 93.6015 | 93.4555
2022-09-07 21:05 | 2:41 | 21.8003 | 22.9659 | 24.8765 | 35.1972 | 38.5066 | 34.7645 | 37.9721 | 34.2467 | 38.4503 | 35.8409 | 36.2157 | 39.6408 | 33.9197 | 35.3193 | 36.5888 | 35.5493 | 34.9402 | 35.165 | 35.7871 | 37.2957 | 24.4335 | 21.6664 | 28.0917 | 35.4856 | 34.37 | 37.8781 | 36.0485 | 35.5905 | 34.8229 | 35.9904 | 32.2171 | 36.6892 | 34.7655 | 35.012 | 33.6032 | 36.4316 | 36.2983 | 36.1079 | 37.9845 | 36.0532 | 35.8274 | 36.8986 | 38.3618 | 35.5644 | 37.2839 | 36.564 | 38.3908 | 34.9301 | 37.7418 | 35.7612 | 38.2419 | 36.1753 | 38.3726 | 36.2432 | 39.0064 | 35.8239 | 37.9734 | 39.6045 | 93.3856 | 93.5614 | 93.3909
2022-09-07 21:05 | 2:41 | 21.6633 | 22.7719 | 24.7459 | 35.3727 | 38.5685 | 34.5455 | 38.0647 | 34.1418 | 38.4155 | 35.769 | 36.1189 | 39.6088 | 33.8496 | 35.2888 | 36.5861 | 35.5589 | 34.867 | 35.2358 | 35.7061 | 37.4007 | 24.3603 | 21.5538 | 28.048 | 35.4951 | 34.3123 | 37.8052 | 35.9802 | 35.5694 | 34.8131 | 35.8772 | 32.1292 | 36.6732 | 34.7113 | 34.9001 | 33.4963 | 36.4827 | 36.2851 | 36.0273 | 37.8488 | 35.9018 | 35.7934 | 36.8526 | 38.1736 | 35.4701 | 37.2007 | 36.4955 | 38.2821 | 34.8137 | 37.773 | 35.624 | 37.9014 | 36.0429 | 38.3034 | 36.1463 | 38.8065 | 35.7822 | 37.8676 | 39.6553 | 93.3123 | 93.4425 | 93.2741
2022-09-07 21:05 | 2:41 | 21.6226 | 22.7088 | 24.6343 | 35.124 | 38.4924 | 34.4092 | 38.0357 | 34.0901 | 38.4256 | 35.6797 | 36.1135 | 39.6067 | 33.7516 | 35.3171 | 36.6179 | 35.4522 | 34.8183 | 35.0808 | 35.6342 | 37.0631 | 24.2802 | 21.455 | 28.0256 | 35.4704 | 34.2096 | 37.622 | 35.9156 | 35.4956 | 34.7059 | 35.9295 | 32.0061 | 36.5274 | 34.6369 | 34.8976 | 33.3748 | 36.3537 | 36.1979 | 35.9442 | 37.7937 | 35.7927 | 35.7181 | 36.7883 | 38.1731 | 35.4445 | 37.1434 | 36.4784 | 38.3496 | 34.8154 | 37.6585 | 35.5723 | 37.6945 | 35.8658 | 38.2624 | 36.1485 | 38.9853 | 35.6926 | 37.7107 | 39.5108 | 93.1139 | 93.4907 | 93.1916
2022-09-07 21:05 | 2:41 | 21.4941 | 22.5946 | 24.5267 | 35.0064 | 38.4102 | 34.4261 | 37.9861 | 34.0749 | 38.4059 | 35.6888 | 36.1855 | 39.5975 | 33.6995 | 35.2559 | 36.5138 | 35.4422 | 34.8341 | 35.1975 | 35.5663 | 36.8377 | 24.1982 | 21.3417 | 27.957 | 35.2753 | 34.1611 | 37.5258 | 35.8717 | 35.4248 | 34.6125 | 35.7657 | 32.0144 | 36.47 | 34.6541 | 34.7745 | 33.1874 | 36.3784 | 36.0347 | 35.9004 | 37.7167 | 35.6422 | 35.6492 | 36.7134 | 38.169 | 35.3953 | 37.0959 | 36.3877 | 38.2396 | 34.7251 | 37.7543 | 35.5568 | 38.1773 | 35.7208 | 38.3306 | 36.1096 | 38.8167 | 35.5877 | 37.7355 | 39.4051 | 93.0893 | 93.4086 | 93.2164
2022-09-07 21:05 | 2:41 | 21.4501 | 22.564 | 24.439 | 34.9252 | 38.3978 | 34.4849 | 37.9185 | 33.9909 | 38.3997 | 35.5832 | 36.0296 | 39.5777 | 33.6309 | 35.1447 | 36.4175 | 35.3457 | 34.7077 | 35.0204 | 35.5507 | 37.0044 | 24.16 | 21.2142 | 27.893 | 35.333 | 34.0757 | 37.5593 | 35.8274 | 35.3834 | 34.5749 | 35.7628 | 31.868 | 36.4865 | 34.52 | 34.7371 | 33.1498 | 36.3237 | 36.0316 | 35.8718 | 37.6977 | 35.6498 | 35.5917 | 36.7217 | 38.0542 | 35.3237 | 37.0932 | 36.31 | 38.1939 | 34.5922 | 37.4737 | 35.3876 | 37.7001 | 35.9142 | 38.1159 | 35.9909 | 38.7159 | 35.5571 | 37.5687 | 39.4117 | 93.014 | 93.3072 | 93.1359
2022-09-07 21:06 | 2:42 | 21.1655 | 22.3154 | 24.2909 | 34.9691 | 38.2517 | 34.3878 | 37.8362 | 33.9675 | 38.3077 | 35.5179 | 35.8378 | 39.5667 | 33.5406 | 35.0936 | 36.343 | 35.3459 | 34.644 | 34.9511 | 35.4549 | 37.0862 | 24.1076 | 21.1371 | 27.8055 | 35.252 | 34.0429 | 37.6591 | 35.7934 | 35.2407 | 34.5126 | 35.731 | 31.9147 | 36.3701 | 34.5647 | 34.6639 | 33.0751 | 36.154 | 35.9993 | 35.7092 | 37.668 | 35.6648 | 35.5524 | 36.6917 | 37.8458 | 35.1996 | 36.9785 | 36.2646 | 38.1203 | 34.5996 | 37.3847 | 35.3205 | 37.6891 | 35.7794 | 38.1299 | 35.933 | 38.5798 | 35.5363 | 37.4997 | 39.5589 | 92.9446 | 93.1968 | 93.0496
2022-09-07 21:06 | 2:42 | 21.1719 | 22.2177 | 24.1776 | 34.7874 | 38.1964 | 34.3638 | 37.8886 | 33.9004 | 38.2432 | 35.4959 | 35.9044 | 39.5024 | 33.4978 | 35.0684 | 36.3166 | 35.2946 | 34.5557 | 34.9139 | 35.4106 | 36.9985 | 24.0386 | 21.112 | 27.7507 | 35.2458 | 33.9635 | 37.702 | 35.7181 | 35.1283 | 34.4559 | 35.6762 | 31.7256 | 36.2685 | 34.4854 | 34.6751 | 32.9847 | 36.1753 | 35.975 | 35.7187 | 37.593 | 35.5211 | 35.5919 | 36.5098 | 37.9908 | 35.1652 | 36.8575 | 36.1891 | 38.1243 | 34.5229 | 37.3959 | 35.2382 | 37.6296 | 35.6627 | 38.0791 | 35.8224 | 38.5803 | 35.3558 | 37.5163 | 39.4424 | 92.8626 | 93.049 | 92.89
2022-09-07 21:06 | 2:42 | 20.9972 | 22.1222 | 24.0904 | 34.6645 | 38.2353 | 34.016 | 37.6834 | 33.8688 | 38.2501 | 35.4008 | 35.9207 | 39.4535 | 33.3607 | 34.989 | 36.2675 | 35.2431 | 34.5227 | 34.9926 | 35.3736 | 36.8898 | 23.9703 | 20.9376 | 27.6798 | 35.053 | 33.8633 | 37.4845 | 35.6492 | 35.1996 | 34.4122 | 35.5938 | 31.7421 | 36.3606 | 34.3938 | 34.6177 | 32.9805 | 36.1889 | 36.0385 | 35.691 | 37.6435 | 35.5556 | 35.6576 | 36.5388 | 37.8991 | 35.1562 | 36.8065 | 36.1789 | 38.1119 | 34.4253 | 37.2942 | 35.2213 | 37.4676 | 35.7659 | 38.0168 | 35.5791 | 38.6094 | 35.3204 | 37.4499 | 39.4352 | 92.7847 | 92.9084 | 92.8609
2022-09-07 21:06 | 2:42 | 21.0064 | 22.0447 | 24.0123 | 34.7059 | 38.1776 | 33.9 | 37.6788 | 33.7294 | 38.2262 | 35.3735 | 35.7888 | 39.5209 | 33.3231 | 34.9882 | 36.2821 | 35.1971 | 34.4537 | 34.9689 | 35.3282 | 36.7976 | 23.9206 | 21.0176 | 27.6654 | 34.9885 | 33.8075 | 37.4424 | 35.5917 | 35.1302 | 34.3569 | 35.4998 | 31.6437 | 36.3633 | 34.2608 | 34.5526 | 32.9637 | 36.1492 | 35.8959 | 35.6847 | 37.5225 | 35.4637 | 35.6816 | 36.4682 | 37.8214 | 34.9949 | 36.7594 | 36.0923 | 38.0462 | 34.3867 | 37.3226 | 35.1635 | 37.6806 | 35.7685 | 37.8959 | 35.5591 | 38.723 | 35.2063 | 37.3917 | 39.3263 | 92.6033 | 92.7739 | 92.811
2022-09-07 21:06 | 2:42 | 19.9929 | 21.7848 | 23.7183 | 34.4911 | 38.1276 | 33.8697 | 37.6679 | 33.5917 | 38.1654 | 35.2037 | 35.5086 | 39.5438 | 33.1835 | 34.8528 | 36.2352 | 35.1602 | 34.3877 | 34.6906 | 35.2588 | 36.7653 | 24.061 | 21.6696 | 28.1554 | 34.9055 | 33.7379 | 37.439 | 35.5524 | 34.9733 | 34.2516 | 35.5564 | 31.7469 | 36.2702 | 34.1837 | 34.4309 | 32.7686 | 36.2783 | 35.6562 | 35.5457 | 37.5362 | 35.3003 | 35.7331 | 36.3612 | 37.7533 | 35.1447 | 36.8637 | 36.0443 | 38.1423 | 34.388 | 37.3719 | 35.0303 | 37.7945 | 35.6401 | 37.9448 | 35.4931 | 38.7261 | 35.2819 | 37.4127 | 39.3214 | 92.4813 | 92.6841 | 92.7064
2022-09-07 21:06 | 2:42 | 19.3637 | 21.349 | 23.2474 | 34.5575 | 38.0678 | 34.1537 | 37.6209 | 33.4267 | 38.0892 | 35.1814 | 35.2995 | 39.4626 | 33.1098 | 34.7228 | 36.0504 | 35.0314 | 34.2765 | 34.5902 | 35.1308 | 36.5808 | 24.7311 | 22.733 | 29.2919 | 34.9449 | 33.7492 | 37.7244 | 35.5919 | 34.8857 | 34.2354 | 35.5246 | 32.0224 | 36.2163 | 34.0832 | 34.4838 | 32.9213 | 36.1574 | 35.5603 | 35.519 | 37.4202 | 35.2961 | 35.7111 | 36.4955 | 37.9459 | 35.2925 | 37.0273 | 36.0321 | 38.0836 | 34.6915 | 37.4372 | 35.2214 | 37.5146 | 35.7959 | 37.9702 | 35.5969 | 38.7933 | 35.4166 | 37.4004 | 39.3203 | 92.3791 | 92.5036 | 92.6682
2022-09-07 21:07 | 2:42 | 18.9433 | 21.0026 | 22.9138 | 34.3544 | 37.8776 | 33.8042 | 37.5365 | 33.3849 | 38.0734 | 35.1344 | 35.5934 | 39.3235 | 32.9133 | 34.6617 | 36.0608 | 34.931 | 34.2459 | 34.5739 | 35.0253 | 36.7127 | 25.6823 | 24.08 | 30.2287 | 35.0876 | 33.8062 | 37.9515 | 35.6576 | 34.8887 | 34.282 | 35.5544 | 32.3302 | 36.1 | 34.0853 | 34.495 | 33.0025 | 35.9729 | 35.6353 | 35.5016 | 37.3627 | 35.3044 | 35.7726 | 36.6099 | 38.0158 | 35.4133 | 37.2334 | 36.0306 | 38.1448 | 34.851 | 37.5286 | 35.2695 | 37.1142 | 35.933 | 37.9872 | 35.6292 | 38.8696 | 35.5574 | 37.714 | 39.137 | 92.2315 | 92.4619 | 92.5466
2022-09-07 21:07 | 2:43 | 18.5404 | 20.6636 | 22.5802 | 34.3394 | 37.8105 | 33.8546 | 37.5094 | 33.2316 | 37.9786 | 34.9594 | 35.1585 | 39.1129 | 32.7929 | 34.6788 | 36.0263 | 34.8847 | 34.1157 | 34.317 | 35.016 | 36.4891 | 26.6519 | 25.4006 | 30.9696 | 35.2996 | 33.8531 | 37.914 | 35.6816 | 35.0002 | 34.2487 | 35.6831 | 32.5663 | 36.2724 | 34.0497 | 34.6602 | 33.1917 | 36.0888 | 35.6203 | 35.5243 | 37.3046 | 35.2561 | 35.6982 | 36.7232 | 38.0869 | 35.5472 | 37.3321 | 36.0305 | 38.18 | 35.0628 | 37.6217 | 35.3464 | 37.0337 | 35.9835 | 38.0553 | 35.7322 | 38.7891 | 35.6705 | 37.8698 | 39.2817 | 92.1023 | 92.3423 | 92.3688
2022-09-07 21:07 | 2:43 | 18.2379 | 20.4105 | 22.3019 | 34.128 | 37.7018 | 33.5817 | 37.2682 | 33.1852 | 37.9629 | 35.0322 | 35.2043 | 39.1742 | 32.7974 | 34.549 | 35.9139 | 34.891 | 34.0543 | 34.3659 | 34.9373 | 36.5709 | 27.6048 | 26.6527 | 31.5559 | 35.3036 | 33.8703 | 38.0294 | 35.7331 | 34.9958 | 34.2028 | 35.7924 | 32.7936 | 36.0062 | 33.9916 | 34.6745 | 33.2149 | 35.8291 | 35.5536 | 35.5424 | 37.2546 | 35.3161 | 35.7948 | 36.8287 | 38.1404 | 35.7252 | 37.3776 | 35.9812 | 38.268 | 35.186 | 37.7157 | 35.426 | 37.0642 | 36.1583 | 38.0688 | 35.7213 | 38.6775 | 35.7136 | 37.7367 | 39.2898 | 91.989 | 92.1938 | 92.3905
2022-09-07 21:07 | 2:43 | 17.9461 | 20.1536 | 22.0473 | 34.1726 | 37.5861 | 33.6948 | 37.2803 | 33.0577 | 37.9056 | 35.0341 | 35.1169 | 39.2363 | 32.6997 | 34.4992 | 35.894 | 34.7495 | 33.9366 | 34.2177 | 34.861 | 36.5466 | 28.3933 | 27.7019 | 31.9409 | 35.3203 | 33.896 | 38.0637 | 35.7111 | 34.907 | 34.2957 | 35.7915 | 32.9418 | 36.038 | 33.8543 | 34.726 | 33.3005 | 35.9995 | 35.6276 | 35.5539 | 37.142 | 35.3329 | 35.8538 | 36.865 | 38.165 | 35.8415 | 37.6032 | 35.9646 | 38.2308 | 35.2783 | 37.7237 | 35.4831 | 37.1141 | 36.2328 | 37.9842 | 35.801 | 38.7027 | 35.7465 | 37.9458 | 39.2455 | 91.8822 | 92.0424 | 92.2937
2022-09-07 21:07 | 2:43 | 17.7425 | 19.9381 | 21.8427 | 34.0941 | 37.5591 | 33.4446 | 37.1706 | 32.9445 | 37.8384 | 34.8471 | 35.1399 | 39.2004 | 32.4829 | 34.5803 | 35.9711 | 34.6759 | 33.8575 | 34.0571 | 34.8638 | 36.513 | 29.0665 | 28.577 | 32.2361 | 35.3247 | 33.9005 | 37.8787 | 35.7726 | 34.9151 | 34.2931 | 35.678 | 33.0169 | 35.8934 | 33.8696 | 34.7831 | 33.4354 | 36.0144 | 35.6779 | 35.6407 | 37.3167 | 35.4215 | 35.8441 | 36.9067 | 38.2379 | 35.9258 | 37.5692 | 35.9902 | 38.3349 | 35.3551 | 37.8262 | 35.4768 | 37.0733 | 36.2715 | 38.1772 | 35.7275 | 38.7161 | 35.8153 | 37.9886 | 39.1917 | 91.7251 | 91.9613 | 92.0831
2022-09-07 21:07 | 2:43 | 17.526 | 19.694 | 21.6657 | 34.0112 | 37.4422 | 33.4005 | 37.0455 | 32.7588 | 37.7728 | 34.8924 | 34.9378 | 39.1426 | 32.4057 | 34.3721 | 35.8066 | 34.5475 | 33.8021 | 34.2021 | 34.7388 | 36.3818 | 29.6005 | 29.2741 | 32.47 | 35.4094 | 33.9105 | 38.1542 | 35.6982 | 34.7995 | 34.3195 | 35.7834 | 33.1246 | 35.8488 | 33.8895 | 34.7809 | 33.5982 | 35.9437 | 35.7114 | 35.6064 | 37.5697 | 35.5458 | 35.9008 | 36.9347 | 38.2478 | 35.9958 | 37.6544 | 35.9956 | 38.2825 | 35.4452 | 37.8825 | 35.4838 | 37.1508 | 36.2116 | 38.2227 | 35.7227 | 38.6558 | 35.8848 | 38.0916 | 39.1635 | 91.5964 | 91.7994 | 92.0321
2022-09-07 21:08 | 2:44 | 17.3011 | 19.462 | 21.415 | 34.0719 | 37.3931 | 33.4357 | 36.9977 | 32.5855 | 37.6556 | 34.7928 | 34.5886 | 38.9472 | 32.4255 | 34.3052 | 35.6168 | 34.4327 | 33.6766 | 34.0055 | 34.6681 | 36.2675 | 30.0986 | 29.7745 | 32.6372 | 35.4349 | 33.9221 | 38.3682 | 35.7948 | 34.73 | 34.2685 | 35.9199 | 33.2034 | 35.8722 | 33.9062 | 34.8335 | 33.6901 | 35.9206 | 35.6688 | 35.6073 | 37.2902 | 35.5138 | 35.89 | 36.9869 | 38.2699 | 36.0303 | 37.6099 | 35.9336 | 38.2341 | 35.4901 | 37.8819 | 35.489 | 37.1521 | 36.3474 | 38.2352 | 35.8143 | 38.902 | 35.907 | 37.9895 | 39.2044 | 91.5297 | 91.7117 | 92.0286
2022-09-07 21:08 | 2:44 | 17.1023 | 19.2665 | 21.1939 | 33.9069 | 37.3038 | 33.4241 | 36.8581 | 32.5263 | 37.6212 | 34.7267 | 34.4766 | 38.9773 | 32.3119 | 34.1874 | 35.5548 | 34.4371 | 33.6109 | 34.0884 | 34.6088 | 36.2761 | 30.4308 | 30.1538 | 32.7543 | 35.3665 | 33.9216 | 38.3449 | 35.8538 | 34.6205 | 34.2629 | 35.8942 | 33.2646 | 35.7957 | 33.7829 | 34.8564 | 33.677 | 35.7987 | 35.6277 | 35.6119 | 37.066 | 35.4488 | 35.9485 | 37.0031 | 38.2627 | 36.0221 | 37.66 | 35.9691 | 38.1782 | 35.5606 | 37.938 | 35.5647 | 37.1075 | 36.4009 | 38.2252 | 35.7846 | 38.8684 | 36.0147 | 38.1161 | 39.2823 | 91.5276 | 91.7026 | 92.0586
2022-09-07 21:08 | 2:44 | 16.8777 | 19.0556 | 20.9824 | 33.7845 | 37.2657 | 33.212 | 36.9521 | 32.4507 | 37.4552 | 34.671 | 34.4239 | 38.8297 | 32.1787 | 33.988 | 35.6435 | 34.2968 | 33.5354 | 33.8808 | 34.4622 | 36.1187 | 30.7012 | 30.4332 | 32.8382 | 35.3238 | 33.9409 | 38.2462 | 35.8441 | 34.6545 | 34.103 | 35.8458 | 33.3148 | 35.9123 | 33.7863 | 34.8061 | 33.676 | 35.9044 | 35.4985 | 35.5685 | 36.9866 | 35.3416 | 35.9797 | 37.0493 | 38.3909 | 36.12 | 37.6282 | 35.9849 | 38.2473 | 35.6108 | 37.9143 | 35.5752 | 37.1598 | 36.4195 | 38.2571 | 35.8075 | 38.7711 | 35.9874 | 38.3195 | 39.1728 | 91.5163 | 91.7657 | 92.0966
2022-09-07 21:08 | 2:44 | 16.6932 | 18.8514 | 20.8132 | 33.7996 | 37.1921 | 33.1589 | 36.5778 | 32.4005 | 37.4098 | 34.6497 | 34.2923 | 38.759 | 32.1021 | 33.8773 | 35.45 | 34.2619 | 33.4384 | 33.7519 | 34.3526 | 36.3515 | 30.9448 | 30.6483 | 32.9705 | 35.388 | 33.9294 | 38.3438 | 35.9008 | 34.7861 | 34.0971 | 35.9432 | 33.3855 | 35.8695 | 33.6758 | 34.7425 | 33.6896 | 35.8621 | 35.3718 | 35.5778 | 37.0266 | 35.2874 | 36.0016 | 37.0241 | 38.3875 | 36.2193 | 37.7381 | 36.0776 | 38.2628 | 35.6783 | 37.9057 | 35.5655 | 37.0969 | 36.4295 | 38.3131 | 35.7916 | 38.7123 | 36.0277 | 38.3958 | 39.1885 | 91.6103 | 91.8143 | 92.1564
2022-09-07 21:08 | 2:44 | 16.5479 | 18.697 | 20.6352 | 33.5947 | 37.0433 | 32.9595 | 36.6873 | 32.3526 | 37.3629 | 34.4646 | 34.3063 | 38.6177 | 31.9343 | 33.7162 | 35.4066 | 34.2092 | 33.4152 | 33.7155 | 34.3256 | 36.5025 | 31.1243 | 30.8263 | 33.0395 | 35.3672 | 33.9694 | 38.2761 | 35.89 | 34.6674 | 34.018 | 35.8799 | 33.4207 | 35.5781 | 33.6995 | 34.6994 | 33.7178 | 35.7852 | 35.2727 | 35.5301 | 37.0894 | 35.2488 | 35.9809 | 37.1095 | 38.3591 | 36.2031 | 37.6899 | 36.0512 | 38.2912 | 35.6861 | 37.9146 | 35.6283 | 37.0563 | 36.5061 | 38.2333 | 35.7506 | 38.7187 | 36.0979 | 38.2543 | 39.2475 | 91.6769 | 92.0125 | 92.1049
2022-09-07 21:08 | 2:44 | 16.3831 | 18.4979 | 20.4618 | 33.5708 | 36.9673 | 32.8021 | 36.5801 | 32.2446 | 37.2796 | 34.3929 | 34.3262 | 38.5876 | 31.8741 | 33.8332 | 35.4056 | 34.171 | 33.2756 | 33.5448 | 34.2168 | 36.3046 | 31.2947 | 30.9461 | 33.1394 | 35.4419 | 33.9125 | 38.5331 | 35.9485 | 34.6844 | 34.0516 | 36.0065 | 33.4411 | 35.6103 | 33.8045 | 34.7129 | 33.7417 | 35.6688 | 35.4393 | 35.5418 | 37.0629 | 35.2608 | 35.9792 | 37.1043 | 38.445 | 36.2147 | 37.7467 | 36.0177 | 38.3506 | 35.7633 | 38.003 | 35.669 | 37.1267 | 36.5404 | 38.2285 | 35.7854 | 38.859 | 36.1361 | 38.2674 | 39.2829 | 91.7855 | 92.0667 | 92.2373
2022-09-07 21:09 | 2:44 | 16.1932 | 18.3115 | 20.2685 | 33.542 | 36.8662 | 32.904 | 36.3425 | 32.2319 | 37.2022 | 34.3048 | 34.2427 | 38.3622 | 31.8464 | 33.5393 | 35.4645 | 34.1063 | 33.1844 | 33.3921 | 34.1792 | 36.1442 | 31.4239 | 31.0508 | 33.2117 | 35.3342 | 33.9588 | 38.5829 | 35.9797 | 34.657 | 34.0762 | 36.0289 | 33.5024 | 35.4881 | 33.5903 | 34.8 | 33.7901 | 35.6424 | 35.3494 | 35.5468 | 36.8944 | 35.2168 | 36.0437 | 37.1149 | 38.3553 | 36.2516 | 37.7688 | 36.0445 | 38.2774 | 35.8071 | 37.9802 | 35.7076 | 37.2065 | 36.6469 | 38.1315 | 35.7156 | 38.8958 | 36.1749 | 38.2684 | 39.2163 | 91.8996 | 92.1352 | 92.3735
2022-09-07 21:09 | 2:45 | 15.9626 | 18.0904 | 20.0863 | 33.4537 | 36.8891 | 32.7744 | 36.373 | 31.9503 | 37.151 | 34.3289 | 34.0895 | 38.4335 | 31.6254 | 33.683 | 35.2987 | 33.9759 | 33.0922 | 33.2584 | 34.0527 | 35.8985 | 31.5229 | 31.1294 | 33.2824 | 35.3055 | 33.9421 | 38.5596 | 36.0016 | 34.64 | 34.1379 | 35.8964 | 33.5467 | 35.5828 | 33.6862 | 34.8308 | 33.8125 | 35.6248 | 35.2168 | 35.4909 | 36.8676 | 35.1692 | 36.0601 | 37.1283 | 38.4161 | 36.2981 | 37.8438 | 36.0184 | 38.3045 | 35.8613 | 38.0481 | 35.6926 | 37.3508 | 36.6543 | 38.1153 | 35.776 | 38.9355 | 36.1705 | 38.5032 | 39.1356 | 92.0215 | 92.2043 | 92.2854
2022-09-07 21:09 | 2:45 | 15.8026 | 17.938 | 19.9139 | 33.4449 | 36.7438 | 32.8771 | 36.2214 | 31.7933 | 37.0817 | 34.1495 | 33.4338 | 38.316 | 31.4892 | 33.9348 | 35.1088 | 33.8353 | 33.0194 | 33.1819 | 34.0091 | 36.088 | 31.5878 | 31.2023 | 33.2966 | 35.3687 | 33.9637 | 38.4402 | 35.9809 | 34.6323 | 34.0566 | 35.9198 | 33.6036 | 35.3365 | 33.5917 | 34.6763 | 33.8409 | 35.59 | 35.194 | 35.4276 | 36.5847 | 35.1271 | 36.0907 | 37.1775 | 38.3887 | 36.3518 | 37.837 | 36.0709 | 38.3328 | 35.9 | 38.1296 | 35.7415 | 37.2931 | 36.6363 | 38.255 | 35.8308 | 38.8805 | 36.2729 | 38.5124 | 39.1713 | 92.0949 | 92.3565 | 92.3656
2022-09-07 21:09 | 2:45 | 15.6301 | 17.7932 | 19.7581 | 33.1519 | 36.5808 | 32.8748 | 36.3252 | 31.645 | 37.0142 | 34.1045 | 33.6344 | 38.4257 | 31.4209 | 33.7519 | 34.9711 | 33.8302 | 32.8973 | 32.9128 | 33.8534 | 36.0597 | 31.6536 | 31.2539 | 33.3403 | 35.3802 | 33.9845 | 38.4352 | 35.9792 | 34.4049 | 34.0529 | 36.0016 | 33.6347 | 35.4909 | 33.4306 | 34.7474 | 33.8904 | 35.6654 | 35.288 | 35.4503 | 36.8464 | 35.1212 | 36.0675 | 37.2208 | 38.4835 | 36.4272 | 37.8633 | 36.067 | 38.2799 | 35.9647 | 38.1236 | 35.7767 | 37.2548 | 36.6833 | 38.192 | 35.7522 | 38.9289 | 36.3081 | 38.5009 | 39.186 | 92.1983 | 92.4251 | 92.4395
2022-09-07 21:09 | 2:45 | 14.7379 | 16.2685 | 19.3471 | 33.234 | 36.38 | 32.7119 | 36.1513 | 31.6039 | 36.9249 | 34.1684 | 33.7174 | 38.2387 | 31.2722 | 33.5466 | 34.7992 | 33.7309 | 32.8291 | 32.9333 | 33.8347 | 35.7272 | 31.6736 | 31.3065 | 33.3658 | 35.2895 | 33.9747 | 38.6701 | 36.0437 | 34.3415 | 34.0078 | 35.9301 | 33.6654 | 35.2687 | 33.5069 | 34.795 | 33.9281 | 35.5231 | 35.1605 | 35.4181 | 36.78 | 35.0889 | 36.109 | 37.254 | 38.4952 | 36.473 | 37.8473 | 36.0662 | 38.3011 | 36.0336 | 38.1456 | 35.7923 | 37.2856 | 36.7253 | 38.2549 | 35.8734 | 39.0267 | 36.3607 | 38.6014 | 39.1595 | 92.2901 | 92.4623 | 92.5168
2022-09-07 21:09 | 2:45 | 16.2822 | 15.9629 | 20.6285 | 33.0459 | 36.2658 | 32.5402 | 36.2074 | 31.4565 | 36.7926 | 34.3711 | 33.3891 | 38.0551 | 31.3277 | 33.3431 | 35.043 | 33.5731 | 32.8742 | 32.8924 | 33.7786 | 35.8102 | 31.6434 | 31.3055 | 33.3665 | 35.2161 | 33.9754 | 38.4331 | 36.0601 | 34.5454 | 34.0942 | 36.1463 | 33.6895 | 35.2392 | 33.4361 | 34.8358 | 33.9461 | 35.6388 | 35.1308 | 35.5363 | 36.6703 | 35.0714 | 36.2012 | 37.2715 | 38.5312 | 36.468 | 37.9336 | 36.1177 | 38.3644 | 36.1142 | 38.1034 | 35.828 | 37.2953 | 36.7376 | 38.2918 | 35.8877 | 39.0763 | 36.3801 | 38.6852 | 39.2662 | 92.3976 | 92.5622 | 92.5458
2022-09-07 21:10 | 2:46 | 18.4433 | 18.1187 | 23.287 | 33.4807 | 36.3464 | 32.6556 | 36.175 | 31.7487 | 36.8246 | 34.3312 | 33.6869 | 38.0685 | 31.5714 | 33.732 | 35.1012 | 33.6193 | 32.9007 | 33.3157 | 33.8967 | 35.8612 | 31.679 | 31.3231 | 33.4556 | 35.4348 | 34.0461 | 38.4986 | 36.0907 | 34.4638 | 34.0508 | 36.0245 | 33.7377 | 35.4175 | 33.6312 | 34.8815 | 34.0145 | 35.7746 | 35.2718 | 35.5638 | 36.8396 | 35.1038 | 36.1238 | 37.3361 | 38.5613 | 36.5634 | 38.0278 | 36.1526 | 38.3479 | 36.1684 | 38.1996 | 35.8602 | 37.3507 | 36.7863 | 38.251 | 35.9286 | 38.9802 | 36.478 | 38.6914 | 39.3399 | 92.4814 | 92.6616 | 92.6459
2022-09-07 21:10 | 2:46 | 20.4314 | 20.556 | 25.5835 | 34.0162 | 36.3719 | 33.02 | 36.1324 | 32.0442 | 36.7865 | 34.333 | 33.97 | 38.1816 | 31.9161 | 33.8003 | 35.1927 | 33.6752 | 33.0899 | 33.6461 | 33.9635 | 36.2031 | 31.7209 | 31.3423 | 33.5602 | 35.5552 | 34.0727 | 38.4271 | 36.0675 | 34.482 | 34.1443 | 36.0172 | 33.7984 | 35.3505 | 33.6991 | 35.0101 | 34.0494 | 35.7646 | 35.2803 | 35.7459 | 37.0035 | 35.173 | 36.2122 | 37.348 | 38.6118 | 36.6482 | 38.0206 | 36.1979 | 38.3953 | 36.2326 | 38.2725 | 35.9355 | 37.4521 | 36.8858 | 38.4346 | 35.8264 | 39.0897 | 36.5172 | 38.5573 | 39.4192 | 92.6018 | 92.7941 | 92.7199
2022-09-07 21:10 | 2:46 | 22.2395 | 22.9587 | 27.2851 | 34.4126 | 36.4051 | 33.1153 | 36.4915 | 32.3646 | 36.8408 | 34.4801 | 34.4809 | 38.2365 | 32.243 | 34.1591 | 35.3501 | 33.7509 | 33.3383 | 33.955 | 34.1038 | 36.3273 | 31.7908 | 31.3805 | 33.6873 | 35.6495 | 34.1409 | 38.4431 | 36.109 | 34.6311 | 34.2424 | 36.0891 | 33.8568 | 35.4666 | 33.8055 | 35.113 | 34.141 | 35.8495 | 35.334 | 35.7382 | 37.0708 | 35.2346 | 36.299 | 37.3598 | 38.7306 | 36.7546 | 38.1022 | 36.2579 | 38.4716 | 36.3316 | 38.3759 | 35.9731 | 37.4828 | 36.9059 | 38.2997 | 35.9899 | 39.1097 | 36.5995 | 38.6336 | 39.3026 | 92.8303 | 92.925 | 92.8741
2022-09-07 21:10 | 2:46 | 23.7628 | 24.949 | 28.5871 | 34.8109 | 36.4455 | 33.4268 | 36.5192 | 32.4821 | 36.8108 | 34.7403 | 34.4428 | 38.228 | 32.4506 | 34.0489 | 35.1902 | 33.8316 | 33.4653 | 34.1372 | 34.2135 | 36.4606 | 31.8864 | 31.4243 | 33.8027 | 35.7866 | 34.1708 | 38.7762 | 36.2012 | 34.6124 | 34.2164 | 36.2389 | 33.8997 | 35.4413 | 33.944 | 35.1536 | 34.2128 | 35.8907 | 35.4603 | 35.796 | 37.1844 | 35.28 | 36.3829 | 37.4811 | 38.6878 | 36.8317 | 38.1749 | 36.2893 | 38.4368 | 36.4329 | 38.4049 | 36.0357 | 37.5225 | 36.9766 | 38.4499 | 36.0602 | 39.1349 | 36.6284 | 38.7134 | 39.3174 | 93.0145 | 93.0298 | 92.9823
2022-09-07 21:10 | 2:46 | 25.0256 | 26.6349 | 29.4156 | 34.9732 | 36.5016 | 33.612 | 36.4544 | 32.712 | 36.8478 | 34.7731 | 34.5625 | 38.2786 | 32.6882 | 34.2297 | 35.407 | 33.8971 | 33.6059 | 34.384 | 34.2773 | 36.5878 | 31.9841 | 31.4797 | 33.9489 | 35.9184 | 34.2302 | 38.7611 | 36.1238 | 34.7539 | 34.2605 | 36.1718 | 33.9813 | 35.4248 | 34.0503 | 35.2819 | 34.2336 | 35.9068 | 35.5195 | 35.863 | 37.3421 | 35.3693 | 36.4436 | 37.5037 | 38.7276 | 36.9259 | 38.2203 | 36.3395 | 38.5366 | 36.523 | 38.433 | 36.1377 | 37.5975 | 37.0588 | 38.4055 | 36.1516 | 39.216 | 36.7405 | 38.8167 | 39.342 | 93.1282 | 93.2568 | 93.0091
2022-09-07 21:10 | 2:46 | 26.0944 | 27.9625 | 29.9708 | 35.3266 | 36.5072 | 33.7019 | 36.6352 | 32.8865 | 36.8422 | 34.8906 | 34.6934 | 38.3138 | 32.8364 | 34.3259 | 35.4128 | 33.9358 | 33.7581 | 34.5299 | 34.3622 | 36.7403 | 32.1133 | 31.512 | 34.0645 | 36.0691 | 34.336 | 38.6189 | 36.2122 | 34.7652 | 34.2922 | 36.2672 | 34.0636 | 35.4571 | 34.1419 | 35.3695 | 34.3531 | 36.0007 | 35.604 | 35.9787 | 37.4913 | 35.4153 | 36.4823 | 37.5861 | 38.8361 | 37.0134 | 38.2659 | 36.3702 | 38.5309 | 36.5928 | 38.548 | 36.1835 | 37.5988 | 37.1398 | 38.4414 | 36.2402 | 39.2151 | 36.7969 | 38.8032 | 39.3878 | 93.246 | 93.4903 | 93.1482
2022-09-07 21:11 | 2:46 | 26.9974 | 28.9799 | 30.3687 | 35.5091 | 36.5756 | 33.7095 | 36.7624 | 32.9293 | 36.908 | 35.037 | 35.0593 | 38.2995 | 33.0235 | 34.4387 | 35.5481 | 33.9659 | 33.9631 | 34.5886 | 34.4447 | 36.7769 | 32.2007 | 31.5344 | 34.2283 | 36.1924 | 34.3794 | 38.7469 | 36.299 | 34.8897 | 34.2938 | 36.3766 | 34.0864 | 35.4706 | 34.212 | 35.47 | 34.3577 | 36.0413 | 35.6477 | 36.0405 | 37.4257 | 35.4481 | 36.5036 | 37.5987 | 38.866 | 37.0912 | 38.3284 | 36.4104 | 38.5776 | 36.672 | 38.5954 | 36.2365 | 37.6634 | 37.2304 | 38.5425 | 36.3289 | 39.2709 | 36.8738 | 38.8851 | 39.4301 | 93.3645 | 93.6018 | 93.1757
2022-09-07 21:11 | 2:47 | 27.6858 | 29.7207 | 30.6234 | 35.5419 | 36.5425 | 33.9444 | 36.8027 | 33.1125 | 36.9231 | 35.043 | 35.0665 | 38.3051 | 33.0835 | 34.457 | 35.5369 | 34.0061 | 33.983 | 34.6934 | 34.5012 | 36.8119 | 32.3456 | 31.5545 | 34.3904 | 36.2547 | 34.4355 | 38.7629 | 36.3829 | 34.9218 | 34.3176 | 36.3499 | 34.197 | 35.5409 | 34.2707 | 35.503 | 34.4029 | 36.081 | 35.6558 | 36.0739 | 37.4233 | 35.4949 | 36.5626 | 37.6646 | 38.8513 | 37.1759 | 38.3641 | 36.4314 | 38.6032 | 36.7626 | 38.5984 | 36.2803 | 37.7381 | 37.2563 | 38.615 | 36.3398 | 39.2593 | 36.9153 | 38.8468 | 39.4209 | 93.6085 | 93.6648 | 93.2644
2022-09-07 21:11 | 2:47 | 28.2174 | 30.2457 | 30.8127 | 35.8053 | 36.5646 | 33.9436 | 36.742 | 33.2006 | 36.9312 | 35.13 | 35.2179 | 38.3781 | 33.187 | 34.5307 | 35.5517 | 34.053 | 34.1052 | 34.7617 | 34.5407 | 36.9591 | 32.475 | 31.5778 | 34.5755 | 36.353 | 34.5352 | 38.7403 | 36.4436 | 35.0316 | 34.3428 | 36.4245 | 34.263 | 35.6288 | 34.404 | 35.5442 | 34.4702 | 36.1417 | 35.6471 | 36.1052 | 37.4445 | 35.5452 | 36.6742 | 37.7509 | 38.8978 | 37.2777 | 38.3674 | 36.5089 | 38.6226 | 36.874 | 38.765 | 36.3788 | 37.8427 | 37.3424 | 38.5644 | 36.446 | 39.2803 | 37.0043 | 38.8868 | 39.4266 | 93.7827 | 93.8766 | 93.3894
2022-09-07 21:11 | 2:47 | 28.6861 | 30.6379 | 30.9845 | 35.9025 | 36.5995 | 34.0379 | 36.9218 | 33.3613 | 36.9612 | 35.2092 | 35.1791 | 38.308 | 33.3065 | 34.6122 | 35.6067 | 34.0668 | 34.1506 | 34.8705 | 34.6198 | 36.9952 | 32.6061 | 31.5815 | 34.737 | 36.4336 | 34.5774 | 38.9074 | 36.4823 | 35.1133 | 34.4223 | 36.5206 | 34.3759 | 35.7097 | 34.4477 | 35.6489 | 34.5444 | 36.124 | 35.6993 | 36.2096 | 37.5371 | 35.5987 | 36.6811 | 37.7458 | 38.9326 | 37.3767 | 38.5048 | 36.5382 | 38.6467 | 36.9479 | 38.8098 | 36.4113 | 37.8868 | 37.4323 | 38.6333 | 36.3549 | 39.1864 | 37.0621 | 38.9678 | 39.4228 | 93.9218 | 94.0655 | 93.5539
2022-09-07 21:11 | 2:47 | 29.0424 | 30.906 | 31.1066 | 36.0018 | 36.5956 | 34.1428 | 36.841 | 33.4143 | 36.9784 | 35.2069 | 35.4109 | 38.4342 | 33.3682 | 34.6651 | 35.6998 | 34.0888 | 34.2325 | 34.9598 | 34.6424 | 37.062 | 32.7588 | 31.6135 | 34.9189 | 36.5116 | 34.6252 | 38.9249 | 36.5036 | 35.0886 | 34.4825 | 36.5265 | 34.4372 | 35.6791 | 34.5391 | 35.7005 | 34.5978 | 36.2398 | 35.7888 | 36.2221 | 37.4579 | 35.6087 | 36.7244 | 37.8568 | 39.0023 | 37.4238 | 38.5234 | 36.5929 | 38.7233 | 37.0262 | 38.7965 | 36.538 | 37.9437 | 37.4597 | 38.6984 | 36.5136 | 39.302 | 37.1006 | 39.0108 | 39.4644 | 94.1636 | 94.2823 | 93.6188
2022-09-07 21:11 | 2:47 | 29.3193 | 31.0876 | 31.2057 | 36.0035 | 36.606 | 34.2097 | 36.9066 | 33.4986 | 36.9848 | 35.4079 | 35.2501 | 38.4673 | 33.4228 | 34.7098 | 35.7449 | 34.1308 | 34.2928 | 35.0272 | 34.7028 | 37.0142 | 32.9119 | 31.6281 | 35.0809 | 36.5092 | 34.716 | 38.9359 | 36.5626 | 35.1387 | 34.4761 | 36.5753 | 34.486 | 35.7065 | 34.5852 | 35.7704 | 34.6946 | 36.2191 | 35.8391 | 36.3083 | 37.5231 | 35.7171 | 36.6482 | 37.9157 | 39.0307 | 37.517 | 38.6556 | 36.6664 | 38.779 | 37.0876 | 38.8192 | 36.5318 | 38.0135 | 37.4937 | 38.6502 | 36.6778 | 39.3199 | 37.1957 | 39.0151 | 39.4391 | 94.2919 | 94.4437 | 93.5982
2022-09-07 21:12 | 2:47 | 29.5463 | 31.2347 | 31.2782 | 36.2849 | 36.6103 | 34.4029 | 36.9162 | 33.5478 | 37.0076 | 35.3743 | 35.4768 | 38.3869 | 33.4777 | 34.7443 | 35.8204 | 34.1546 | 34.4399 | 34.9642 | 34.7138 | 36.987 | 33.0351 | 31.6505 | 35.2346 | 36.6005 | 34.8131 | 38.9823 | 36.6742 | 35.1618 | 34.5459 | 36.6721 | 34.5801 | 35.8361 | 34.6568 | 35.8403 | 34.732 | 36.297 | 35.8148 | 36.3588 | 37.5987 | 35.7144 | 36.639 | 37.964 | 39.0671 | 37.6072 | 38.6986 | 36.708 | 38.798 | 37.1733 | 38.8817 | 36.581 | 38.07 | 37.5596 | 38.7251 | 36.6604 | 39.3341 | 37.2259 | 39.1608 | 39.4537 | 94.4237 | 94.5231 | 93.7666
2022-09-07 21:12 | 2:48 | 29.7461 | 31.3376 | 31.3843 | 36.2324 | 36.6082 | 34.4912 | 36.9216 | 33.6433 | 37.0167 | 35.3885 | 35.4952 | 38.4524 | 33.5125 | 34.8348 | 35.8356 | 34.177 | 34.4467 | 35.0918 | 34.7735 | 37.1502 | 33.1791 | 31.6664 | 35.3759 | 36.6638 | 34.863 | 38.9772 | 36.6811 | 35.296 | 34.6321 | 36.5802 | 34.6551 | 35.8284 | 34.7125 | 35.8222 | 34.7676 | 36.2984 | 35.8324 | 36.336 | 37.5627 | 35.7475 | 36.7276 | 38.0366 | 39.1364 | 37.6863 | 38.7063 | 36.7945 | 38.8412 | 37.2429 | 38.9479 | 36.6859 | 38.0815 | 37.6421 | 38.6797 | 36.607 | 39.3577 | 37.3129 | 39.1671 | 39.4461 | 94.5108 | 94.5814 | 93.9165
2022-09-07 21:12 | 2:48 | 30.5469 | 25.9616 | 31.1712 | 36.3409 | 36.6293 | 34.5458 | 37.0536 | 33.616 | 36.9994 | 35.5548 | 35.4129 | 38.4067 | 33.5483 | 34.7767 | 35.8421 | 34.2074 | 34.5176 | 35.0357 | 34.7967 | 37.1445 | 33.6282 | 28.037 | 35.1244 | 36.709 | 34.8524 | 39.0836 | 36.7244 | 35.2118 | 34.7547 | 36.6535 | 34.5808 | 35.8392 | 34.7873 | 35.8815 | 34.7706 | 36.284 | 35.9198 | 36.4197 | 37.5206 | 35.8135 | 36.7737 | 37.9475 | 39.0641 | 37.5219 | 38.6517 | 36.7571 | 38.7832 | 37.1119 | 38.9242 | 36.5832 | 38.003 | 37.6208 | 38.5882 | 36.7262 | 39.3864 | 37.2228 | 39.0971 | 39.5777 | 94.6188 | 94.7426 | 93.9778
2022-09-07 21:12 | 2:48 | 31.1306 | 30.9416 | 31.2993 | 36.2578 | 36.6885 | 34.4019 | 37.0817 | 33.7066 | 37.04 | 35.3872 | 35.6242 | 38.406 | 33.6266 | 34.7933 | 35.9209 | 34.2227 | 34.5538 | 35.1762 | 34.8262 | 37.0972 | 33.6049 | 30.3558 | 34.752 | 36.7786 | 34.8294 | 38.9277 | 36.6482 | 35.1618 | 34.6645 | 36.5731 | 34.5332 | 35.8718 | 34.8046 | 35.8977 | 34.8124 | 36.3082 | 36.0007 | 36.4524 | 37.4983 | 35.869 | 36.8529 | 37.9517 | 38.9703 | 37.432 | 38.5626 | 36.7366 | 38.7165 | 37.0302 | 38.7223 | 36.5533 | 37.8607 | 37.6146 | 38.7349 | 36.5951 | 39.4298 | 37.1954 | 38.7973 | 39.6296 | 94.7734 | 94.8032 | 93.9406
2022-09-07 21:12 | 2:48 | 32.4638 | 31.8825 | 31.5659 | 36.3263 | 36.7089 | 34.5208 | 37.1636 | 33.8228 | 37.082 | 35.4483 | 35.8276 | 38.4218 | 33.7495 | 34.9854 | 35.9178 | 34.2978 | 34.6383 | 35.1839 | 34.9481 | 37.1821 | 33.7489 | 31.242 | 34.9374 | 36.7831 | 34.8821 | 39.0156 | 36.639 | 35.2306 | 34.6484 | 36.6437 | 34.6402 | 36.1023 | 34.8992 | 35.9702 | 34.8507 | 36.3421 | 36.0261 | 36.525 | 37.5294 | 35.9162 | 36.8946 | 37.9183 | 39.0116 | 37.4428 | 38.6084 | 36.7817 | 38.8399 | 37.0923 | 38.7093 | 36.5877 | 37.931 | 37.6462 | 38.7919 | 36.69 | 39.4683 | 37.2641 | 38.898 | 39.5465 | 94.7726 | 94.9408 | 94.0164
2022-09-07 21:12 | 2:48 | 33.5868 | 31.846 | 31.7561 | 36.423 | 36.7306 | 34.6077 | 37.0183 | 33.9027 | 37.1065 | 35.4811 | 35.7687 | 38.4548 | 33.846 | 35.0076 | 35.954 | 34.3717 | 34.7447 | 35.2052 | 34.9584 | 37.2199 | 34.1201 | 31.5626 | 35.2316 | 36.9396 | 34.9462 | 39.1332 | 36.7276 | 35.1373 | 34.7595 | 36.7309 | 34.7698 | 35.961 | 34.9869 | 35.9749 | 34.9487 | 36.4247 | 36.0632 | 36.5757 | 37.5219 | 35.9693 | 36.9908 | 37.9656 | 39.0783 | 37.5363 | 38.6716 | 36.841 | 38.8386 | 37.1991 | 38.8113 | 36.6702 | 38.0408 | 37.7097 | 38.9479 | 36.7462 | 39.4657 | 37.3348 | 39.1518 | 39.5782 | 94.7925 | 94.999 | 94.0377
2022-09-07 21:13 | 2:49 | 34.4143 | 31.8906 | 32.0564 | 36.599 | 36.7405 | 34.6628 | 37.2001 | 34.0108 | 37.1093 | 35.5328 | 35.8395 | 38.7308 | 33.9665 | 35.0962 | 36.0848 | 34.4308 | 34.7739 | 35.3412 | 35.0293 | 37.2659 | 34.5873 | 31.6753 | 35.5176 | 37.0046 | 35.0373 | 39.0152 | 36.7737 | 35.3417 | 34.9309 | 36.8842 | 34.9361 | 35.9689 | 35.0935 | 36.0982 | 35.0563 | 36.5407 | 36.1352 | 36.662 | 37.5874 | 36.0355 | 37.0189 | 38.0764 | 39.0946 | 37.6667 | 38.7272 | 36.872 | 38.903 | 37.327 | 38.9258 | 36.8039 | 38.1206 | 37.7712 | 38.9059 | 36.8948 | 39.4911 | 37.4372 | 39.1002 | 39.5824 | 94.6791 | 94.9691 | 93.9727
2022-09-07 21:13 | 2:49 | 34.8615 | 31.8635 | 32.4578 | 36.5793 | 36.776 | 34.7587 | 37.1642 | 34.0857 | 37.1467 | 35.7205 | 36.0121 | 38.5106 | 34.0598 | 35.1837 | 36.1981 | 34.4792 | 34.848 | 35.408 | 35.1205 | 37.3481 | 34.8738 | 31.7062 | 35.7808 | 37.0505 | 35.1635 | 39.0364 | 36.8529 | 35.2977 | 34.9459 | 36.8341 | 35.0714 | 35.9998 | 35.171 | 36.1496 | 35.1173 | 36.5809 | 36.23 | 36.672 | 37.6352 | 36.1217 | 37.0501 | 38.1691 | 39.2026 | 37.7708 | 38.7631 | 36.9378 | 38.9542 | 37.4191 | 39.0135 | 36.8363 | 38.2064 | 37.8428 | 38.8824 | 36.8672 | 39.5147 | 37.5034 | 39.2118 | 39.626 | 94.4448 | 94.7614 | 93.8021
2022-09-07 21:13 | 2:49 | 35.1063 | 31.862 | 32.7821 | 36.8166 | 36.7852 | 34.8499 | 37.3304 | 34.2136 | 37.1786 | 35.7682 | 35.9829 | 38.5045 | 34.1578 | 35.2778 | 36.2674 | 34.569 | 35.0057 | 35.3938 | 35.1773 | 37.4436 | 34.9852 | 31.7154 | 35.9363 | 37.1537 | 35.2313 | 39.1114 | 36.8946 | 35.3975 | 35.0803 | 36.9499 | 35.185 | 36.0575 | 35.281 | 36.2466 | 35.1914 | 36.617 | 36.3137 | 36.7365 | 37.7387 | 36.224 | 37.1082 | 38.2333 | 39.1916 | 37.8716 | 38.9214 | 36.9969 | 39.0369 | 37.5125 | 39.0286 | 36.9404 | 38.2991 | 37.8957 | 38.8949 | 37.0177 | 39.541 | 37.5885 | 39.2461 | 39.6605 | 94.219 | 94.5065 | 93.7002
2022-09-07 21:13 | 2:49 | 35.0944 | 31.8693 | 32.9478 | 36.8491 | 36.8244 | 34.9204 | 37.2335 | 34.2464 | 37.2248 | 35.786 | 35.9768 | 38.6118 | 34.1935 | 35.263 | 36.2177 | 34.5878 | 35.0196 | 35.4731 | 35.2781 | 37.4532 | 35.0035 | 31.7433 | 36.0265 | 37.2056 | 35.3066 | 39.181 | 36.9908 | 35.4173 | 35.1028 | 36.9468 | 35.2717 | 36.0942 | 35.3609 | 36.3601 | 35.2697 | 36.6256 | 36.4104 | 36.8389 | 37.7537 | 36.2629 | 37.2347 | 38.2959 | 39.3004 | 37.9595 | 38.9722 | 37.087 | 39.0604 | 37.5918 | 39.0896 | 36.9932 | 38.3183 | 37.9589 | 39.0205 | 37.0138 | 39.6228 | 37.6565 | 39.2127 | 39.8206 | 94.0178 | 94.2563 | 93.5403
2022-09-07 21:13 | 2:49 | 35.0792 | 31.883 | 32.9445 | 36.8432 | 36.8426 | 34.9663 | 37.2512 | 34.3454 | 37.2667 | 35.758 | 36.1169 | 38.5645 | 34.3137 | 35.3242 | 36.3244 | 34.6534 | 35.1116 | 35.5314 | 35.3357 | 37.4727 | 35.0494 | 31.764 | 36.0753 | 37.3541 | 35.3226 | 39.3154 | 37.0189 | 35.551 | 35.2515 | 37.0589 | 35.3671 | 36.1769 | 35.4611 | 36.4188 | 35.3758 | 36.6629 | 36.4605 | 36.8618 | 37.7809 | 36.3096 | 37.2635 | 38.3188 | 39.3395 | 38.0211 | 38.9779 | 37.1275 | 39.0965 | 37.6641 | 39.2111 | 37.1054 | 38.3894 | 38.0352 | 39.0213 | 37.1182 | 39.5942 | 37.7224 | 39.334 | 39.782 | 93.8493 | 94.0368 | 93.474
2022-09-07 21:13 | 2:49 | 35.1743 | 31.9036 | 33.0012 | 36.9457 | 36.8656 | 35.0189 | 37.2664 | 34.3947 | 37.3261 | 35.8124 | 36.1013 | 38.63 | 34.3613 | 35.4288 | 36.3352 | 34.7225 | 35.1996 | 35.6349 | 35.39 | 37.5736 | 35.0853 | 31.7821 | 36.1788 | 37.3714 | 35.4607 | 39.3274 | 37.0501 | 35.5998 | 35.2635 | 37.0545 | 35.4404 | 36.1055 | 35.5122 | 36.4789 | 35.4565 | 36.7341 | 36.5321 | 36.9124 | 37.8635 | 36.3974 | 37.3318 | 38.3651 | 39.3715 | 38.1004 | 39.0455 | 37.1381 | 39.1728 | 37.7451 | 39.2077 | 37.1476 | 38.4637 | 38.0905 | 39.0719 | 37.2052 | 39.561 | 37.7799 | 39.4177 | 39.7893 | 93.7341 | 93.849 | 93.3989
2022-09-07 21:14 | 2:49 | 35.2732 | 31.939 | 33.1103 | 37.0601 | 36.9022 | 35.0692 | 37.3347 | 34.4299 | 37.3282 | 35.7938 | 36.2472 | 38.5728 | 34.4571 | 35.4128 | 36.4855 | 34.7656 | 35.3241 | 35.7231 | 35.4381 | 37.6446 | 35.1697 | 31.8208 | 36.2636 | 37.4562 | 35.4885 | 39.4209 | 37.1082 | 35.6093 | 35.268 | 37.1265 | 35.5346 | 36.345 | 35.5622 | 36.4819 | 35.5233 | 36.7808 | 36.5262 | 36.937 | 37.8257 | 36.4298 | 37.3915 | 38.4343 | 39.4156 | 38.1909 | 39.1318 | 37.2276 | 39.2382 | 37.8172 | 39.3654 | 37.2074 | 38.49 | 38.1534 | 39.143 | 37.2028 | 39.7131 | 37.8635 | 39.4406 | 39.7877 | 93.6213 | 93.7887 | 93.2659
2022-09-07 21:14 | 2:50 | 35.5249 | 31.9642 | 33.2711 | 37.1353 | 36.9002 | 35.1866 | 37.4054 | 34.5127 | 37.3436 | 35.9467 | 36.1868 | 38.5695 | 34.5435 | 35.567 | 36.5048 | 34.8374 | 35.3516 | 35.7523 | 35.4679 | 37.6523 | 35.2892 | 31.8276 | 36.3789 | 37.5003 | 35.5683 | 39.543 | 37.2347 | 35.6819 | 35.3045 | 37.2253 | 35.6357 | 36.272 | 35.6208 | 36.5083 | 35.6156 | 36.8075 | 36.5307 | 36.9932 | 37.9174 | 36.4852 | 37.4169 | 38.5188 | 39.5011 | 38.2814 | 39.1325 | 37.2681 | 39.2871 | 37.8853 | 39.405 | 37.2865 | 38.5642 | 38.2087 | 39.1454 | 37.2535 | 39.7304 | 37.9291 | 39.5655 | 39.8442 | 93.575 | 93.7329 | 93.256
2022-09-07 21:14 | 2:50 | 35.6581 | 31.9948 | 33.4449 | 37.1504 | 36.9175 | 35.2753 | 37.3321 | 34.5476 | 37.388 | 35.9746 | 36.3134 | 38.617 | 34.628 | 35.615 | 36.5656 | 34.881 | 35.4629 | 35.7912 | 35.5529 | 37.6792 | 35.4154 | 31.8379 | 36.5318 | 37.5246 | 35.6834 | 39.5574 | 37.2635 | 35.7997 | 35.4351 | 37.2533 | 35.7315 | 36.2709 | 35.6929 | 36.6263 | 35.659 | 36.891 | 36.619 | 37.0648 | 37.933 | 36.5566 | 37.4875 | 38.6016 | 39.5095 | 38.3406 | 39.2051 | 37.3577 | 39.3068 | 37.9663 | 39.4921 | 37.3736 | 38.6246 | 38.2836 | 39.2144 | 37.2974 | 39.8057 | 37.9887 | 39.4692 | 39.8566 | 93.5358 | 93.6268 | 93.1232
2022-09-07 21:14 | 2:50 | 35.8913 | 32.0213 | 33.6525 | 37.1315 | 36.9831 | 35.2958 | 37.3637 | 34.635 | 37.4494 | 36.0284 | 36.4513 | 38.6287 | 34.7248 | 35.6584 | 36.6453 | 34.9314 | 35.482 | 35.8662 | 35.5887 | 37.6639 | 35.6157 | 31.8661 | 36.6555 | 37.6563 | 35.7002 | 39.5911 | 37.3318 | 35.8668 | 35.6013 | 37.2948 | 35.7945 | 36.3844 | 35.7959 | 36.6407 | 35.7789 | 36.8848 | 36.6613 | 37.0949 | 37.9833 | 36.6121 | 37.5861 | 38.632 | 39.5542 | 38.4206 | 39.3525 | 37.366 | 39.3425 | 38.0496 | 39.4551 | 37.4079 | 38.6608 | 38.3887 | 39.2415 | 37.3856 | 39.8 | 38.0692 | 39.5672 | 39.894 | 93.441 | 93.5763 | 93.0933
2022-09-07 21:14 | 2:50 | 36.2061 | 32.0685 | 33.873 | 37.3139 | 37.0187 | 35.4449 | 37.5608 | 34.7438 | 37.4747 | 36.0924 | 36.3519 | 38.6345 | 34.8041 | 35.7668 | 36.626 | 35.0103 | 35.5511 | 35.9463 | 35.6878 | 37.9184 | 35.7987 | 32.0424 | 36.8159 | 37.6934 | 35.8348 | 39.7854 | 37.3915 | 35.9276 | 35.6765 | 37.3245 | 35.9098 | 36.3803 | 35.8924 | 36.7519 | 35.8729 | 36.9948 | 36.7019 | 37.1783 | 38.017 | 36.6653 | 37.6614 | 38.6326 | 39.6112 | 38.4918 | 39.4061 | 37.4112 | 39.3888 | 38.1085 | 39.5 | 37.4927 | 38.7412 | 38.4153 | 39.3179 | 37.471 | 39.8456 | 38.1406 | 39.6171 | 39.9112 | 93.351 | 93.5043 | 93.0483
2022-09-07 21:14 | 2:50 | 36.454 | 32.1331 | 34.0029 | 37.4389 | 37.0595 | 35.539 | 37.4878 | 34.8674 | 37.5208 | 36.2499 | 36.5244 | 38.6786 | 34.9361 | 35.8942 | 36.7704 | 35.0786 | 35.6204 | 35.992 | 35.7228 | 37.9041 | 36.1335 | 32.6065 | 36.9857 | 37.8084 | 35.9003 | 39.8177 | 37.4169 | 36.088 | 35.6295 | 37.5025 | 35.9911 | 36.602 | 35.983 | 36.8721 | 35.9578 | 37.0635 | 36.7795 | 37.2754 | 38.0299 | 36.7405 | 37.6895 | 38.7424 | 39.6552 | 38.5773 | 39.4045 | 37.4986 | 39.449 | 38.1985 | 39.6247 | 37.5365 | 38.8031 | 38.484 | 39.4054 | 37.5534 | 39.8866 | 38.2249 | 39.7498 | 39.9782 | 93.2863 | 93.4584 | 93.1087
2022-09-07 21:15 | 2:51 | 36.5849 | 32.1943 | 34.0404 | 37.5417 | 37.1014 | 35.6329 | 37.5423 | 35.0096 | 37.5392 | 36.3244 | 36.5773 | 38.7657 | 35.0283 | 35.9013 | 36.7782 | 35.1627 | 35.7237 | 36.1414 | 35.8355 | 37.9767 | 36.5474 | 34.167 | 37.191 | 37.8317 | 36.002 | 39.876 | 37.4875 | 36.0742 | 35.7683 | 37.4434 | 36.1277 | 36.7083 | 36.0726 | 36.9316 | 36.0605 | 37.1559 | 36.8755 | 37.376 | 38.0745 | 36.8321 | 37.8754 | 38.8087 | 39.7074 | 38.6707 | 39.4778 | 37.5824 | 39.5042 | 38.2732 | 39.6507 | 37.5759 | 38.9001 | 38.5543 | 39.3654 | 37.6771 | 39.9051 | 38.2842 | 39.702 | 40.0476 | 93.2298 | 93.3819 | 92.9305
2022-09-07 21:15 | 2:51 | 36.6181 | 32.2709 | 34.1993 | 37.5784 | 37.1507 | 35.7469 | 37.6876 | 35.079 | 37.6106 | 36.4405 | 36.7125 | 38.8447 | 35.17 | 36.0108 | 36.8764 | 35.2294 | 35.8683 | 36.1777 | 35.877 | 38.0585 | 36.9584 | 34.848 | 37.3952 | 37.9795 | 36.0799 | 39.9514 | 37.5861 | 36.1697 | 35.8448 | 37.5604 | 36.2562 | 36.6727 | 36.1552 | 37.005 | 36.1616 | 37.2282 | 36.9189 | 37.4656 | 38.1647 | 36.8875 | 37.8799 | 38.8926 | 39.74 | 38.7543 | 39.4616 | 37.6412 | 39.5343 | 38.3673 | 39.7366 | 37.6942 | 38.8992 | 38.5979 | 39.4744 | 37.6551 | 39.9949 | 38.3591 | 39.7151 | 40.0894 | 93.1373 | 93.2871 | 93.0116
2022-09-07 21:15 | 2:51 | 36.4856 | 32.4105 | 34.4177 | 37.7368 | 37.1834 | 35.8938 | 37.7791 | 35.2096 | 37.6631 | 36.5607 | 36.9028 | 38.8119 | 35.2746 | 36.1222 | 37.0348 | 35.3085 | 35.9409 | 36.2974 | 35.9965 | 38.116 | 37.3072 | 36.0146 | 37.6019 | 38.0688 | 36.1794 | 39.9083 | 37.6614 | 36.2265 | 35.9888 | 37.7319 | 36.373 | 36.7014 | 36.2912 | 37.1604 | 36.285 | 37.2469 | 36.9844 | 37.5135 | 38.202 | 36.9847 | 37.9162 | 38.9465 | 39.814 | 38.852 | 39.5928 | 37.6887 | 39.6099 | 38.453 | 39.8289 | 37.8013 | 38.9835 | 38.676 | 39.4474 | 37.7211 | 40.0299 | 38.4406 | 39.8129 | 40.1367 | 93.0549 | 93.2154 | 92.8458
2022-09-07 21:15 | 2:51 | 36.467 | 32.5778 | 34.6184 | 37.8687 | 37.2177 | 36.0063 | 37.8306 | 35.3115 | 37.7067 | 36.5532 | 36.9052 | 38.9614 | 35.37 | 36.2816 | 37.1247 | 35.3623 | 36.0358 | 36.41 | 36.1188 | 38.2357 | 37.5923 | 36.41 | 37.7828 | 38.1638 | 36.2485 | 40.0121 | 37.6895 | 36.3536 | 35.9888 | 37.7232 | 36.4917 | 36.8165 | 36.3551 | 37.2159 | 36.3603 | 37.2697 | 37.1217 | 37.5755 | 38.2742 | 37.055 | 38.0242 | 39.0171 | 39.8993 | 38.9072 | 39.6625 | 37.7466 | 39.6242 | 38.5099 | 39.8624 | 37.7996 | 39.0424 | 38.7482 | 39.4242 | 37.8164 | 40.0614 | 38.5041 | 39.9362 | 40.1965 | 92.9761 | 93.1276 | 92.883
2022-09-07 21:15 | 2:51 | 36.8401 | 32.7062 | 34.8334 | 37.9134 | 37.2758 | 36.062 | 37.7638 | 35.4324 | 37.7691 | 36.6656 | 37.0266 | 38.9944 | 35.5041 | 36.3599 | 37.1461 | 35.4911 | 36.1712 | 36.4502 | 36.193 | 38.3118 | 37.8115 | 36.7298 | 37.9262 | 38.2041 | 36.3601 | 40.1137 | 37.8754 | 36.3909 | 36.1288 | 37.7654 | 36.5754 | 36.9091 | 36.4894 | 37.2826 | 36.47 | 37.4002 | 37.1577 | 37.6654 | 38.363 | 37.1494 | 38.107 | 39.0978 | 39.9577 | 39.0036 | 39.6984 | 37.8215 | 39.6708 | 38.599 | 39.911 | 37.8764 | 39.1081 | 38.8584 | 39.6335 | 37.9391 | 40.1103 | 38.5577 | 39.9795 | 40.2197 | 92.8742 | 93.0658 | 92.8326
2022-09-07 21:15 | 2:51 | 36.7858 | 32.8213 | 35.0509 | 38.1297 | 37.3255 | 36.2683 | 37.8549 | 35.5481 | 37.7737 | 36.7863 | 37.0244 | 38.9003 | 35.6268 | 36.4032 | 37.1302 | 35.5682 | 36.2401 | 36.542 | 36.3201 | 38.3471 | 38.0072 | 36.9919 | 38.111 | 38.3617 | 36.4495 | 40.0247 | 37.8799 | 36.4374 | 36.1536 | 37.882 | 36.6907 | 36.9618 | 36.5829 | 37.3597 | 36.5817 | 37.5006 | 37.2784 | 37.7277 | 38.3521 | 37.189 | 38.1438 | 39.1265 | 40.0022 | 39.0822 | 39.7812 | 37.879 | 39.7578 | 38.6705 | 39.959 | 37.9738 | 39.1632 | 38.9026 | 39.6562 | 37.9879 | 40.2055 | 38.6383 | 40.0294 | 40.2715 | 92.8606 | 93.0605 | 92.8243
2022-09-07 21:16 | 2:51 | 36.6397 | 32.9998 | 35.2752 | 38.2451 | 37.398 | 36.3379 | 37.8762 | 35.6461 | 37.8286 | 36.8361 | 37.1387 | 38.8905 | 35.7532 | 36.5107 | 37.4512 | 35.6156 | 36.3467 | 36.679 | 36.3901 | 38.4356 | 38.167 | 37.2932 | 38.2618 | 38.3961 | 36.5648 | 40.2003 | 37.9162 | 36.6539 | 36.3441 | 37.9228 | 36.7948 | 37.0668 | 36.6668 | 37.4338 | 36.7036 | 37.5539 | 37.3784 | 37.8204 | 38.5004 | 37.1813 | 38.2116 | 39.2083 | 40.0309 | 39.1878 | 39.8271 | 37.9489 | 39.8173 | 38.7722 | 40.004 | 38.0216 | 39.3027 | 38.9668 | 39.6651 | 38.0973 | 40.2099 | 38.677 | 40.0991 | 40.289 | 92.7903 | 93.0327 | 92.768
2022-09-07 21:16 | 2:52 | 36.1403 | 33.2396 | 35.515 | 38.3113 | 37.4218 | 36.4119 | 38.0099 | 35.7746 | 37.8786 | 36.9713 | 37.2147 | 38.97 | 35.8822 | 36.5837 | 37.4399 | 35.7099 | 36.4813 | 36.7523 | 36.449 | 38.5391 | 38.3061 | 37.4045 | 38.3923 | 38.5097 | 36.6601 | 40.2522 | 38.0242 | 36.6559 | 36.428 | 38.0421 | 36.9069 | 37.1417 | 36.8265 | 37.5505 | 36.7918 | 37.6111 | 37.4344 | 37.912 | 38.5225 | 37.3353 | 38.3298 | 39.2957 | 40.0707 | 39.248 | 39.9186 | 38.0153 | 39.8892 | 38.8483 | 40.0509 | 38.0464 | 39.3374 | 39.0156 | 39.7738 | 38.2582 | 40.2073 | 38.7948 | 40.1424 | 40.3763 | 92.7773 | 92.9827 | 92.7181
2022-09-07 21:16 | 2:52 | 35.7048 | 33.6289 | 35.7277 | 38.4983 | 37.4745 | 36.5513 | 38.0636 | 35.895 | 37.9557 | 37.1151 | 37.2691 | 39.0068 | 35.9988 | 36.7361 | 37.4889 | 35.8311 | 36.5885 | 36.8666 | 36.5479 | 38.5999 | 38.4419 | 37.5837 | 38.5109 | 38.6675 | 36.7793 | 40.2305 | 38.107 | 36.758 | 36.4808 | 38.1318 | 36.9877 | 37.107 | 36.9023 | 37.6479 | 36.8366 | 37.6716 | 37.467 | 37.9653 | 38.5966 | 37.4343 | 38.3618 | 39.3818 | 40.1373 | 39.3366 | 39.9592 | 38.0591 | 39.9224 | 38.929 | 40.1713 | 38.0924 | 39.3816 | 39.1069 | 39.8218 | 38.2967 | 40.2399 | 38.846 | 40.1536 | 40.4182 | 92.7903 | 92.9573 | 92.7065
2022-09-07 21:16 | 2:52 | 35.4099 | 34.0765 | 35.955 | 38.5933 | 37.544 | 36.6433 | 38.1422 | 36.0312 | 37.9928 | 37.1649 | 37.4459 | 39.0558 | 36.0898 | 36.8285 | 37.5493 | 35.8887 | 36.6541 | 36.9541 | 36.6757 | 38.6635 | 38.5588 | 37.7592 | 38.6281 | 38.6915 | 36.822 | 40.2544 | 38.1438 | 36.8141 | 36.6998 | 38.1589 | 37.1112 | 37.2973 | 36.9865 | 37.72 | 36.9747 | 37.7221 | 37.5408 | 38.0123 | 38.6518 | 37.4786 | 38.4071 | 39.3978 | 40.1831 | 39.3818 | 40.0102 | 38.1221 | 39.979 | 38.9837 | 40.2027 | 38.1734 | 39.4342 | 39.1609 | 39.9468 | 38.3395 | 40.2777 | 38.9127 | 40.2239 | 40.5025 | 92.6797 | 92.8753 | 92.5789
2022-09-07 21:16 | 2:52 | 35.3205 | 34.3682 | 36.1827 | 38.6028 | 37.5954 | 36.7456 | 38.2466 | 36.1512 | 38.0666 | 37.2176 | 37.5557 | 39.1016 | 36.2251 | 36.8726 | 37.5694 | 35.9892 | 36.7285 | 37.0614 | 36.7435 | 38.7482 | 38.7338 | 37.7751 | 38.7676 | 38.7882 | 36.9466 | 40.5537 | 38.2116 | 36.8818 | 36.8038 | 38.3859 | 37.2096 | 37.3501 | 37.0959 | 37.841 | 37.0752 | 37.7891 | 37.5823 | 38.1463 | 38.6654 | 37.5673 | 38.5303 | 39.4848 | 40.2368 | 39.5084 | 40.053 | 38.1919 | 40.0551 | 39.0643 | 40.2609 | 38.3001 | 39.4937 | 39.247 | 39.9634 | 38.4548 | 40.3554 | 38.9947 | 40.2966 | 40.5321 | 92.5918 | 92.7732 | 92.4975
2022-09-07 21:16 | 2:52 | 35.3511 | 34.6003 | 36.3622 | 38.7103 | 37.6638 | 36.8533 | 38.2108 | 36.2557 | 38.1301 | 37.2936 | 37.6106 | 39.1802 | 36.4332 | 37.0216 | 37.7242 | 36.0987 | 36.8708 | 37.1779 | 36.8945 | 38.8285 | 38.888 | 37.9855 | 38.8715 | 38.8613 | 37.012 | 40.5051 | 38.3298 | 36.9637 | 36.8482 | 38.3089 | 37.3049 | 37.3569 | 37.1816 | 37.8902 | 37.2028 | 37.9 | 37.684 | 38.2122 | 38.7224 | 37.6816 | 38.6154 | 39.5711 | 40.2871 | 39.5676 | 40.1327 | 38.3068 | 40.0913 | 39.1483 | 40.2956 | 38.3486 | 39.5695 | 39.2933 | 40.069 | 38.481 | 40.3891 | 39.0867 | 40.349 | 40.6387 | 92.466 | 92.6721 | 92.5218
2022-09-07 21:17 | 2:53 | 35.5281 | 34.8421 | 36.6167 | 38.7674 | 37.7265 | 36.9352 | 38.253 | 36.3578 | 38.1806 | 37.4114 | 37.7363 | 39.2355 | 36.5316 | 37.1139 | 37.9046 | 36.1881 | 36.9771 | 37.2392 | 36.9362 | 38.8994 | 38.9993 | 38.1969 | 39.0071 | 38.9257 | 37.0889 | 40.659 | 38.3618 | 36.9977 | 36.9392 | 38.4133 | 37.4013 | 37.4092 | 37.2923 | 37.9836 | 37.2685 | 37.9512 | 37.749 | 38.2693 | 38.7962 | 37.7645 | 38.615 | 39.5746 | 40.3324 | 39.6441 | 40.1971 | 38.3446 | 40.1605 | 39.2273 | 40.4058 | 38.4296 | 39.6055 | 39.3522 | 39.9641 | 38.5641 | 40.4634 | 39.1332 | 40.4267 | 40.5974 | 92.3836 | 92.6056 | 92.3813
2022-09-07 21:17 | 2:53 | 35.6798 | 35.1035 | 36.8072 | 39.0495 | 37.8048 | 37.0657 | 38.3042 | 36.5049 | 38.2479 | 37.5972 | 37.7425 | 39.2326 | 36.6294 | 37.2139 | 37.912 | 36.2998 | 37.1095 | 37.3284 | 37.0643 | 38.9912 | 39.11 | 38.3404 | 39.0985 | 38.9879 | 37.2059 | 40.6386 | 38.4071 | 37.0981 | 37.0041 | 38.5218 | 37.5034 | 37.5026 | 37.4149 | 38.1209 | 37.4172 | 38.0383 | 37.8217 | 38.3683 | 38.8858 | 37.8624 | 38.5267 | 39.6457 | 40.412 | 39.744 | 40.2218 | 38.4251 | 40.2081 | 39.3383 | 40.4703 | 38.5295 | 39.6795 | 39.4458 | 40.1678 | 38.663 | 40.516 | 39.2266 | 40.394 | 40.6962 | 92.2634 | 92.487 | 92.2974
2022-09-07 21:17 | 2:53 | 35.8251 | 35.3927 | 36.993 | 39.0917 | 37.8603 | 37.183 | 38.3975 | 36.6471 | 38.315 | 37.6223 | 37.9071 | 39.3792 | 36.7611 | 37.3204 | 38.0187 | 36.3818 | 37.2181 | 37.4363 | 37.1385 | 39.0929 | 39.1923 | 38.4789 | 39.2205 | 39.0729 | 37.3504 | 40.7843 | 38.5303 | 37.1515 | 37.191 | 38.6843 | 37.5818 | 37.654 | 37.5112 | 38.1594 | 37.5173 | 38.0747 | 37.913 | 38.4296 | 38.9607 | 37.9583 | 38.3006 | 39.7339 | 40.4494 | 39.7935 | 40.3206 | 38.4835 | 40.2421 | 39.3904 | 40.5425 | 38.6302 | 39.7168 | 39.5008 | 40.2725 | 38.7315 | 40.5575 | 39.2892 | 40.4261 | 40.7396 | 92.1484 | 92.3338 | 92.2538
2022-09-07 21:17 | 2:53 | 36.0504 | 35.7039 | 37.1392 | 39.1117 | 37.9413 | 37.3078 | 38.4751 | 36.7338 | 38.3821 | 37.6857 | 38.01 | 39.3707 | 36.897 | 37.4671 | 38.1368 | 36.4824 | 37.3011 | 37.5483 | 37.2508 | 39.1728 | 39.3278 | 38.5193 | 39.3252 | 39.1726 | 37.407 | 40.7775 | 38.6154 | 37.2897 | 37.2691 | 38.6672 | 37.6798 | 37.7303 | 37.6092 | 38.2502 | 37.6365 | 38.166 | 37.9959 | 38.5051 | 38.9602 | 38.0168 | 38.0838 | 39.8501 | 40.4941 | 39.8866 | 40.3935 | 38.5164 | 40.3365 | 39.4671 | 40.5856 | 38.6589 | 39.7988 | 39.5386 | 40.3339 | 38.8037 | 40.595 | 39.369 | 40.5161 | 40.7384 | 92.0292 | 92.1525 | 92.2233
2022-09-07 21:17 | 2:53 | 36.4381 | 36.0267 | 37.0758 | 39.2124 | 38.0111 | 37.3725 | 38.5365 | 36.8023 | 38.441 | 37.7722 | 38.1647 | 39.3838 | 36.9439 | 37.4641 | 38.2399 | 36.6518 | 37.3944 | 37.6088 | 37.3191 | 39.2334 | 37.1767 | 37.3336 | 38.7829 | 39.2188 | 37.4911 | 40.8664 | 38.615 | 37.4009 | 37.3107 | 38.6938 | 37.5808 | 37.8536 | 37.6539 | 38.3077 | 37.6345 | 38.2372 | 38.0572 | 38.547 | 39.0001 | 38.0836 | 37.9911 | 39.8952 | 40.5151 | 39.8914 | 40.4587 | 38.6227 | 40.3552 | 39.4362 | 40.6121 | 38.7286 | 39.8173 | 39.5942 | 40.2551 | 38.8411 | 40.5839 | 39.3379 | 40.5834 | 40.8646 | 91.9074 | 92.0708 | 92.0043
2022-09-07 21:17 | 2:53 | 32.6445 | 31.5846 | 34.7095 | 39.2018 | 38.0755 | 37.2619 | 38.5288 | 36.7082 | 38.4975 | 37.7483 | 38.2045 | 39.4989 | 36.7853 | 37.249 | 38.1557 | 36.6045 | 37.3941 | 37.3205 | 37.1915 | 39.1165 | 34.2156 | 31.7772 | 37.5016 | 39.236 | 37.3501 | 40.6193 | 38.5267 | 37.18 | 37.2043 | 38.409 | 37.1502 | 37.7229 | 37.4349 | 38.114 | 37.5134 | 38.1831 | 38.018 | 38.4463 | 38.94 | 38.0376 | 37.9019 | 39.7383 | 40.3941 | 39.607 | 40.2814 | 38.5443 | 40.3103 | 39.1746 | 40.4698 | 38.5855 | 39.581 | 39.4712 | 40.1243 | 38.7776 | 40.5875 | 39.1478 | 40.4886 | 40.9054 | 91.8319 | 91.9982 | 91.9786
2022-09-07 21:18 | 2:53 | 28.9734 | 29.7848 | 32.3392 | 38.6004 | 38.0863 | 37.009 | 38.4797 | 36.4188 | 38.488 | 37.4501 | 37.9024 | 39.5934 | 36.3416 | 36.9376 | 37.9643 | 36.4702 | 37.157 | 37.0228 | 37.0307 | 38.9487 | 33.4569 | 29.4911 | 35.344 | 38.9421 | 37.0752 | 40.2817 | 38.3006 | 37.0596 | 36.9034 | 38.1303 | 36.5114 | 37.6323 | 37.2048 | 37.8362 | 37.2167 | 38.0252 | 37.9342 | 38.2817 | 38.8624 | 37.9085 | 37.8187 | 39.494 | 40.1496 | 39.1104 | 39.9122 | 38.4372 | 40.1012 | 38.6866 | 40.1377 | 38.2109 | 39.3223 | 39.1845 | 39.8772 | 38.5878 | 40.529 | 38.8367 | 40.3191 | 40.8298 | 91.8462 | 92.011 | 91.9802
2022-09-07 21:18 | 2:54 | 30.1617 | 29.3761 | 31.7247 | 38.2385 | 38.1343 | 36.8152 | 38.4259 | 36.2894 | 38.5056 | 37.3224 | 37.9554 | 39.5841 | 36.1368 | 36.8881 | 37.8146 | 36.3775 | 36.9669 | 36.8869 | 36.8666 | 38.7402 | 31.8694 | 28.6515 | 33.8732 | 38.7071 | 36.8567 | 40.0049 | 38.0838 | 36.8888 | 36.6627 | 37.8773 | 35.9736 | 37.6021 | 37.0378 | 37.5308 | 36.9293 | 37.8378 | 37.85 | 38.0144 | 38.6668 | 37.7556 | 37.7046 | 39.2522 | 39.961 | 38.6473 | 39.6041 | 38.3393 | 40.0111 | 38.3218 | 39.8534 | 37.9737 | 38.9227 | 39.0476 | 39.8639 | 38.408 | 40.437 | 38.6379 | 40.1667 | 40.6681 | 91.9026 | 92.086 | 92.0984
2022-09-07 21:18 | 2:54 | 28.1116 | 29.3226 | 31.0073 | 37.9889 | 38.1707 | 36.6628 | 38.4853 | 36.173 | 38.4959 | 37.2272 | 37.8747 | 39.5153 | 35.9889 | 36.7979 | 37.7954 | 36.305 | 36.8407 | 36.8002 | 36.7779 | 38.6367 | 28.0566 | 28.1314 | 32.8225 | 38.4517 | 36.7135 | 39.8974 | 37.9911 | 36.7531 | 36.4739 | 37.7479 | 35.681 | 37.4781 | 36.8657 | 37.3422 | 36.7664 | 37.6674 | 37.735 | 37.9163 | 38.6303 | 37.6157 | 37.735 | 39.1587 | 39.801 | 38.3576 | 39.4771 | 38.2425 | 39.9463 | 38.1735 | 39.7081 | 37.8179 | 38.912 | 38.8978 | 39.8034 | 38.3769 | 40.2978 | 38.4821 | 39.9408 | 40.5467 | 92.0293 | 92.1918 | 92.2132
2022-09-07 21:18 | 2:54 | 29.6761 | 29.7572 | 31.2453 | 37.8822 | 38.2659 | 36.5016 | 38.5021 | 36.1472 | 38.5229 | 37.0904 | 37.8958 | 39.5091 | 35.9561 | 36.7902 | 37.8943 | 36.2518 | 36.7918 | 36.7963 | 36.713 | 38.5424 | 27.0457 | 27.5843 | 32.2765 | 38.3493 | 36.6375 | 39.6731 | 37.9019 | 36.7867 | 36.4021 | 37.6619 | 35.5178 | 37.5311 | 36.7809 | 37.1795 | 36.5552 | 37.5638 | 37.658 | 37.7509 | 38.5774 | 37.5866 | 37.695 | 39.1022 | 39.7032 | 38.191 | 39.2707 | 38.1755 | 39.9387 | 37.9902 | 39.5034 | 37.7239 | 38.7211 | 38.8924 | 39.7107 | 38.3111 | 40.3444 | 38.4063 | 39.7492 | 40.4865 | 92.0989 | 92.3593 | 92.2831
2022-09-07 21:18 | 2:54 | 30.7371 | 30.1771 | 31.8098 | 37.8364 | 38.3192 | 36.6095 | 38.5287 | 36.135 | 38.5776 | 37.1402 | 37.8189 | 39.5924 | 35.9265 | 36.7263 | 37.7785 | 36.219 | 36.7434 | 36.7699 | 36.7374 | 38.5735 | 26.6326 | 27.1347 | 31.8899 | 38.0869 | 36.5966 | 39.7554 | 37.8187 | 36.9546 | 36.3771 | 37.6868 | 35.2252 | 37.5509 | 36.8344 | 37.1079 | 36.4415 | 37.5282 | 37.6849 | 37.8084 | 38.4985 | 37.5284 | 37.6739 | 38.9809 | 39.7332 | 37.9796 | 39.1577 | 38.1305 | 39.8162 | 37.8391 | 39.5175 | 37.7006 | 38.6229 | 38.7267 | 39.6392 | 38.2321 | 40.2362 | 38.3393 | 39.7195 | 40.5225 | 92.1955 | 92.4624 | 92.3645
2022-09-07 21:18 | 2:54 | 31.1466 | 30.0269 | 32.0569 | 37.8703 | 38.4037 | 36.7291 | 38.5748 | 36.1655 | 38.6258 | 37.1704 | 37.9056 | 39.6004 | 35.9123 | 36.8444 | 37.7152 | 36.2399 | 36.7671 | 36.843 | 36.7638 | 38.491 | 26.3537 | 26.7316 | 31.5707 | 38.0817 | 36.5234 | 39.4323 | 37.7046 | 36.8764 | 36.3453 | 37.6686 | 35.068 | 37.6202 | 36.7786 | 37.0665 | 36.3825 | 37.5373 | 37.6851 | 37.695 | 38.5828 | 37.5586 | 37.5912 | 38.9115 | 39.6406 | 37.9262 | 39.159 | 38.091 | 39.7625 | 37.7402 | 39.3447 | 37.5949 | 38.7878 | 38.6972 | 39.6713 | 38.3072 | 40.0497 | 38.2481 | 39.5635 | 40.507 | 92.3843 | 92.5791 | 92.4467
2022-09-07 21:19 | 2:55 | 31.3695 | 29.7548 | 31.9772 | 37.8402 | 38.4971 | 36.5952 | 38.5389 | 36.0925 | 38.6557 | 37.1902 | 37.9159 | 39.5891 | 35.9133 | 36.8052 | 37.7968 | 36.2633 | 36.7912 | 36.7453 | 36.8406 | 38.5017 | 26.0914 | 26.3326 | 31.2983 | 37.9981 | 36.4771 | 39.3839 | 37.735 | 36.9881 | 36.302 | 37.5597 | 34.9447 | 37.709 | 36.7985 | 37.0071 | 36.3278 | 37.5172 | 37.5636 | 37.687 | 38.6082 | 37.4111 | 37.5442 | 38.8404 | 39.6166 | 37.8746 | 38.9783 | 38.104 | 39.7955 | 37.6356 | 39.2518 | 37.6308 | 38.7822 | 38.6588 | 39.5725 | 38.2117 | 39.9143 | 38.1893 | 39.5385 | 40.6447 | 92.4692 | 92.7405 | 92.5512
2022-09-07 21:19 | 2:55 | 31.3739 | 29.3928 | 31.8159 | 37.6952 | 38.5888 | 36.5497 | 38.5589 | 36.0981 | 38.6596 | 37.1812 | 37.8982 | 39.7135 | 35.9134 | 36.8097 | 37.9191 | 36.3037 | 36.7499 | 36.7799 | 36.84 | 38.5293 | 25.9393 | 25.9695 | 31.0626 | 37.9594 | 36.4474 | 39.3017 | 37.695 | 36.8636 | 36.285 | 37.5646 | 34.789 | 37.4964 | 36.7653 | 36.9581 | 36.1194 | 37.4813 | 37.6838 | 37.6659 | 38.6552 | 37.4318 | 37.5452 | 38.811 | 39.5793 | 37.7072 | 38.9312 | 38.0949 | 39.6393 | 37.5133 | 39.1938 | 37.5341 | 38.7075 | 38.5498 | 39.5832 | 38.1491 | 40.118 | 38.0786 | 39.4642 | 40.6153 | 92.652 | 92.8851 | 92.6635
2022-09-07 21:19 | 2:55 | 31.279 | 28.5555 | 31.5903 | 37.6907 | 38.636 | 36.4604 | 38.721 | 36.0379 | 38.7014 | 37.1451 | 38.0396 | 39.6684 | 35.8579 | 36.7012 | 37.9701 | 36.3212 | 36.6983 | 36.691 | 36.8663 | 38.5501 | 26.0347 | 25.7231 | 30.8733 | 37.8929 | 36.4134 | 39.2541 | 37.6739 | 36.9752 | 36.2941 | 37.592 | 34.6914 | 37.3758 | 36.7086 | 36.9449 | 36.0873 | 37.5142 | 37.4985 | 37.5821 | 38.6909 | 37.3398 | 37.4841 | 38.7723 | 39.5598 | 37.6974 | 38.8823 | 38.0841 | 39.6584 | 37.42 | 39.1209 | 37.4423 | 38.9212 | 38.4517 | 39.5474 | 38.1123 | 39.9976 | 38.0288 | 39.444 | 40.5852 | 92.7764 | 93.0017 | 92.7335
2022-09-07 21:19 | 2:55 | 31.0561 | 28.1949 | 31.3758 | 37.6489 | 38.6885 | 36.3253 | 38.5627 | 36.0048 | 38.74 | 37.1878 | 37.9916 | 39.7567 | 35.7734 | 36.6891 | 37.8381 | 36.3398 | 36.7067 | 36.6694 | 36.8526 | 38.4134 | 26.22 | 25.5003 | 30.7079 | 37.7815 | 36.3648 | 39.1731 | 37.5912 | 37.0128 | 36.2915 | 37.5049 | 34.6663 | 37.3896 | 36.6495 | 36.8809 | 36.0628 | 37.4307 | 37.585 | 37.5511 | 38.719 | 37.3439 | 37.4069 | 38.5964 | 39.5682 | 37.6152 | 38.8087 | 38.0525 | 39.7181 | 37.2792 | 39.0903 | 37.425 | 38.8463 | 38.2779 | 39.5614 | 38.1335 | 39.9611 | 37.966 | 39.3618 | 40.4979 | 92.9039 | 93.1725 | 92.7609
2022-09-07 21:19 | 2:55 | 30.8339 | 28.1503 | 31.1695 | 37.5176 | 38.7551 | 36.2461 | 38.6195 | 35.9329 | 38.7722 | 37.0835 | 38.0576 | 39.8055 | 35.717 | 36.6638 | 37.9699 | 36.3406 | 36.6906 | 36.6078 | 36.867 | 38.4942 | 26.3434 | 25.345 | 30.5288 | 37.6105 | 36.3372 | 39.1211 | 37.5442 | 36.7596 | 36.2356 | 37.3839 | 34.4811 | 37.5004 | 36.7193 | 36.8336 | 36.0068 | 37.4928 | 37.7068 | 37.5436 | 38.6802 | 37.3968 | 37.3606 | 38.5659 | 39.4898 | 37.5461 | 38.743 | 38.0398 | 39.6048 | 37.1853 | 39.1313 | 37.3611 | 39.16 | 38.2578 | 39.4969 | 38.1901 | 39.8284 | 37.8892 | 39.2867 | 40.643 | 92.9892 | 93.2943 | 92.8155
2022-09-07 21:19 | 2:55 | 30.5646 | 28.0337 | 30.8897 | 37.4738 | 38.8222 | 36.2979 | 38.6498 | 35.957 | 38.7801 | 37.0806 | 37.9564 | 39.7882 | 35.6673 | 36.6812 | 37.8362 | 36.3655 | 36.6306 | 36.7048 | 36.8748 | 38.3576 | 26.2639 | 25.2533 | 30.3889 | 37.4898 | 36.2368 | 39.1591 | 37.5452 | 36.8564 | 36.2439 | 37.3558 | 34.3811 | 37.536 | 36.6942 | 36.8392 | 36.0019 | 37.4824 | 37.7613 | 37.5302 | 38.6748 | 37.6202 | 37.3333 | 38.4426 | 39.4279 | 37.4685 | 38.7017 | 37.9864 | 39.501 | 37.1138 | 38.9584 | 37.2786 | 39.1665 | 38.0712 | 39.4887 | 37.9937 | 39.8167 | 37.791 | 39.2982 | 40.5571 | 93.1332 | 93.4705 | 92.9671
2022-09-07 21:20 | 2:56 | 30.262 | 27.8535 | 30.6539 | 37.4823 | 38.8465 | 36.373 | 38.6458 | 35.9194 | 38.8004 | 37.0646 | 37.8356 | 39.7991 | 35.6694 | 36.5989 | 37.6975 | 36.3948 | 36.6157 | 36.6348 | 36.8379 | 38.4339 | 26.1235 | 25.0544 | 30.2301 | 37.4248 | 36.2141 | 39.0723 | 37.4841 | 36.7844 | 36.2472 | 37.331 | 34.3189 | 37.4891 | 36.7155 | 36.6861 | 35.9801 | 37.4566 | 37.7589 | 37.4868 | 38.7893 | 37.6253 | 37.2223 | 38.4631 | 39.4086 | 37.4188 | 38.6329 | 37.9036 | 39.5207 | 36.9997 | 39.0198 | 37.2608 | 39.1873 | 37.9981 | 39.449 | 37.9021 | 39.9266 | 37.7106 | 39.3285 | 40.4753 | 93.3067 | 93.6025 | 93.1047
2022-09-07 21:20 | 2:56 | 29.7782 | 27.7686 | 30.3588 | 37.2967 | 38.9154 | 36.0666 | 38.656 | 35.9073 | 38.8427 | 37.1119 | 37.8677 | 39.8898 | 35.6026 | 36.6394 | 37.7294 | 36.3713 | 36.5648 | 36.6339 | 36.8384 | 38.3835 | 25.9139 | 24.8865 | 30.1143 | 37.372 | 36.1718 | 39.0444 | 37.4069 | 36.9362 | 36.2321 | 37.2875 | 34.1802 | 37.5869 | 36.7517 | 36.6459 | 35.9109 | 37.3996 | 37.7785 | 37.3798 | 38.7209 | 37.6396 | 37.1304 | 38.3793 | 39.3703 | 37.2893 | 38.5597 | 37.9035 | 39.4162 | 36.8556 | 39.0503 | 37.1968 | 38.6632 | 37.9642 | 39.4728 | 37.8974 | 39.9731 | 37.6664 | 39.2585 | 40.6089 | 93.381 | 93.769 | 93.1686
2022-09-07 21:20 | 2:56 | 28.8812 | 27.4692 | 29.8722 | 37.1815 | 38.958 | 36.2038 | 38.6222 | 35.8796 | 38.8375 | 37.0695 | 37.821 | 39.884 | 35.5513 | 36.5643 | 37.668 | 36.4149 | 36.5074 | 36.4858 | 36.8048 | 38.2838 | 25.8065 | 24.5307 | 29.9717 | 37.3033 | 36.1121 | 38.8215 | 37.3606 | 36.9226 | 36.1833 | 37.2194 | 34.2284 | 37.5142 | 36.6811 | 36.5325 | 35.7466 | 37.2694 | 37.7361 | 37.3698 | 38.7306 | 37.6277 | 37.1178 | 38.2738 | 39.2647 | 37.2001 | 38.5174 | 37.8542 | 39.4087 | 36.8223 | 38.9928 | 37.1117 | 38.8205 | 37.9492 | 39.3887 | 37.8884 | 39.7276 | 37.5942 | 39.0569 | 40.5009 | 93.6064 | 93.9582 | 93.2961
2022-09-07 21:20 | 2:56 | 27.3183 | 27.4588 | 29.4036 | 37.1178 | 38.9412 | 36.0298 | 38.5669 | 35.7916 | 38.8712 | 37.0367 | 37.8159 | 40.028 | 35.5258 | 36.4649 | 37.732 | 36.3755 | 36.487 | 36.4836 | 36.8038 | 38.197 | 25.8071 | 24.3273 | 29.8468 | 37.2807 | 36.0016 | 38.8037 | 37.3333 | 36.918 | 36.1239 | 37.1761 | 34.0059 | 37.4071 | 36.7917 | 36.4751 | 35.8069 | 37.2392 | 37.7604 | 37.2938 | 38.6563 | 37.5989 | 37.0715 | 38.2766 | 39.2859 | 37.1317 | 38.6265 | 37.7797 | 39.4693 | 36.6911 | 38.8644 | 37.0488 | 38.7714 | 37.8203 | 39.3553 | 37.6389 | 39.8222 | 37.4947 | 39.074 | 40.5004 | 93.7621 | 94.1662 | 93.452
2022-09-07 21:20 | 2:56 | 25.6235 | 27.1063 | 28.9865 | 37.0435 | 38.9893 | 35.9792 | 38.6174 | 35.7355 | 38.8524 | 36.8812 | 37.7518 | 39.9147 | 35.375 | 36.4279 | 37.6538 | 36.3619 | 36.427 | 36.4411 | 36.7076 | 38.1507 | 25.8671 | 24.2665 | 29.7827 | 37.0482 | 35.9509 | 38.9569 | 37.2223 | 36.8169 | 36.1578 | 37.1924 | 34.0291 | 37.4786 | 36.6813 | 36.4694 | 35.7443 | 37.3714 | 37.7315 | 37.2349 | 38.7558 | 37.5953 | 37.0808 | 38.2359 | 39.2985 | 37.0922 | 38.4728 | 37.6688 | 39.3346 | 36.5864 | 38.7645 | 37.0311 | 38.5447 | 37.7242 | 39.3582 | 37.623 | 39.7228 | 37.4591 | 38.9492 | 40.5492 | 93.9091 | 94.3492 | 93.5703
2022-09-07 21:20 | 2:56 | 25.2472 | 26.7858 | 28.6309 | 36.9845 | 39.03 | 36.0725 | 38.5506 | 35.7191 | 38.8828 | 36.718 | 37.596 | 39.9407 | 35.3603 | 36.3322 | 37.4992 | 36.3557 | 36.3217 | 36.3615 | 36.7049 | 38.1989 | 25.8693 | 24.1123 | 29.5934 | 37.0692 | 35.8775 | 38.9278 | 37.1304 | 36.7027 | 36.0971 | 37.1078 | 33.7906 | 37.5517 | 36.5017 | 36.3895 | 35.4681 | 37.3897 | 37.5512 | 37.1618 | 38.5896 | 37.4111 | 37.0181 | 38.1798 | 39.187 | 36.9068 | 38.3845 | 37.6549 | 39.3253 | 36.4838 | 38.6569 | 36.9534 | 38.4983 | 37.693 | 39.1961 | 37.812 | 39.3372 | 37.3524 | 38.9516 | 40.4566 | 94.1218 | 94.5469 | 93.714
2022-09-07 21:21 | 2:56 | 24.9297 | 26.516 | 28.3547 | 36.825 | 38.9915 | 35.9692 | 38.623 | 35.5503 | 38.8589 | 36.7779 | 37.5092 | 39.8599 | 35.268 | 36.3625 | 37.5536 | 36.3308 | 36.2103 | 36.1812 | 36.6647 | 38.1859 | 25.756 | 23.9046 | 29.4563 | 37.0208 | 35.7807 | 38.9063 | 37.1178 | 36.5885 | 35.9922 | 37.0401 | 33.719 | 37.4574 | 36.3901 | 36.26 | 35.275 | 37.2198 | 37.4254 | 37.1417 | 38.4425 | 37.1388 | 36.951 | 38.0569 | 39.1572 | 36.7855 | 38.2158 | 37.6078 | 39.3749 | 36.4485 | 38.7075 | 36.9439 | 38.4775 | 37.7151 | 39.2047 | 37.6966 | 39.4667 | 37.317 | 38.8206 | 40.2598 | 94.2733 | 94.7067 | 93.7499
2022-09-07 21:21 | 2:57 | 24.7626 | 26.3218 | 28.1642 | 36.7361 | 39.0248 | 35.8929 | 38.6604 | 35.5085 | 38.8599 | 36.7576 | 37.4742 | 39.8984 | 35.146 | 36.2789 | 37.5012 | 36.2868 | 36.2014 | 36.1434 | 36.6352 | 38.0503 | 25.867 | 24.8682 | 29.4137 | 36.8979 | 35.7304 | 38.8546 | 37.0715 | 36.5335 | 35.9883 | 37.0137 | 33.6491 | 37.4494 | 36.2608 | 36.221 | 35.3397 | 37.189 | 37.4099 | 37.2108 | 38.4827 | 37.1182 | 36.9391 | 38.0013 | 39.139 | 36.7599 | 38.2818 | 37.5942 | 39.2699 | 36.3262 | 38.6552 | 36.7986 | 38.4501 | 37.5593 | 39.0063 | 37.4313 | 39.5226 | 37.1832 | 38.8065 | 40.3382 | 94.4082 | 94.9133 | 93.9391
2022-09-07 21:21 | 2:57 | 24.5059 | 26.0868 | 27.9506 | 36.7059 | 39.0377 | 35.8108 | 38.568 | 35.4416 | 38.866 | 36.6835 | 37.4493 | 39.8556 | 35.0654 | 36.2273 | 37.4503 | 36.2791 | 36.151 | 36.1001 | 36.5812 | 37.9894 | 25.6583 | 24.4399 | 29.3095 | 36.7978 | 35.6485 | 38.6019 | 37.0808 | 36.7583 | 35.908 | 36.8677 | 33.5523 | 37.312 | 36.0187 | 36.1654 | 35.213 | 37.0883 | 37.3288 | 37.0931 | 38.3756 | 37.1087 | 36.9324 | 38.0223 | 39.0249 | 36.6183 | 38.1555 | 37.5136 | 39.306 | 36.2368 | 38.5947 | 36.7291 | 38.388 | 37.5213 | 39.0711 | 37.3891 | 39.6714 | 37.076 | 38.6429 | 40.3501 | 94.5964 | 95.0276 | 94.0523
2022-09-07 21:21 | 2:57 | 24.4206 | 25.9453 | 27.7377 | 36.5861 | 39.0335 | 35.6901 | 38.4822 | 35.4008 | 38.8713 | 36.714 | 37.5126 | 39.957 | 35.0493 | 36.2056 | 37.4102 | 36.2413 | 36.0796 | 36.1457 | 36.5605 | 37.9354 | 25.6137 | 24.1592 | 29.2442 | 36.7376 | 35.6011 | 38.6271 | 37.0181 | 36.5238 | 35.8301 | 36.824 | 33.4971 | 37.2551 | 36.0141 | 36.098 | 34.9561 | 37.048 | 37.2897 | 36.9945 | 38.2881 | 36.9759 | 36.9876 | 37.8972 | 38.9303 | 36.6183 | 38.1977 | 37.5162 | 39.0893 | 36.2282 | 38.5311 | 36.7719 | 38.8377 | 37.375 | 38.9759 | 37.4296 | 39.5358 | 37.0373 | 38.7968 | 40.2058 | 94.727 | 95.1974 | 94.147
2022-09-07 21:21 | 2:57 | 24.2121 | 25.8174 | 27.5917 | 36.6307 | 39.0315 | 35.6706 | 38.5576 | 35.3434 | 38.8426 | 36.6501 | 37.328 | 39.8725 | 34.9432 | 36.138 | 37.5309 | 36.147 | 36.0235 | 36.1004 | 36.4728 | 37.9258 | 25.9041 | 23.8838 | 29.9193 | 36.6648 | 35.5528 | 38.7511 | 36.951 | 36.5677 | 35.8568 | 36.8376 | 33.5934 | 37.2627 | 36.0104 | 36.0999 | 35.0852 | 37.031 | 37.3139 | 36.9898 | 38.4633 | 36.9376 | 36.9064 | 37.8425 | 38.9583 | 36.5998 | 38.1262 | 37.4437 | 39.2008 | 36.1747 | 38.4418 | 36.6751 | 38.3587 | 37.3573 | 39.0784 | 37.3217 | 39.4437 | 37.0418 | 38.6838 | 40.2534 | 94.8948 | 95.301 | 94.2403
2022-09-07 21:21 | 2:57 | 24.1508 | 25.6739 | 27.4254 | 36.4873 | 39.0332 | 35.5938 | 38.4806 | 35.2566 | 38.8305 | 36.5266 | 37.1877 | 39.8817 | 34.9464 | 36.1521 | 37.4733 | 36.1744 | 35.9453 | 35.9281 | 36.4654 | 37.895 | 26.679 | 23.8015 | 30.7887 | 36.7338 | 35.5215 | 38.8196 | 36.9391 | 36.334 | 35.8596 | 36.9034 | 33.7428 | 37.2417 | 35.9447 | 36.1168 | 35.0488 | 37.078 | 37.297 | 37.0117 | 38.364 | 36.9475 | 36.8233 | 37.8622 | 39.1371 | 36.6265 | 38.2124 | 37.4189 | 39.2615 | 36.2043 | 38.5283 | 36.7007 | 38.804 | 37.4938 | 39.1387 | 37.3076 | 39.4909 | 37.0455 | 38.7015 | 40.3372 | 95.0491 | 95.4433 | 94.3392
2022-09-07 21:22 | 2:58 | 23.9316 | 25.475 | 27.2805 | 36.331 | 39.0274 | 35.5547 | 38.471 | 35.2371 | 38.8184 | 36.6266 | 37.3855 | 39.9065 | 34.8573 | 36.1253 | 37.3066 | 36.1573 | 35.894 | 35.9827 | 36.4083 | 37.8909 | 27.4042 | 23.7849 | 31.0635 | 36.7437 | 35.4885 | 38.9468 | 36.9324 | 36.3506 | 35.7788 | 36.9027 | 33.8394 | 37.3189 | 35.8282 | 36.2517 | 34.907 | 37.1818 | 37.1127 | 37.115 | 38.3505 | 36.9235 | 36.7999 | 37.902 | 38.9541 | 36.6358 | 38.2541 | 37.3672 | 39.2219 | 36.2473 | 38.5304 | 36.6369 | 38.3966 | 37.3542 | 38.9968 | 37.3589 | 39.4511 | 37.0197 | 38.685 | 40.5425 | 95.0673 | 95.5195 | 94.3991
2022-09-07 21:22 | 2:58 | 23.9773 | 25.4191 | 27.1676 | 36.1918 | 38.9845 | 35.3626 | 38.3907 | 35.1893 | 38.8477 | 36.6335 | 37.3641 | 39.8166 | 34.847 | 36.0935 | 37.3482 | 36.1459 | 35.9226 | 35.9757 | 36.5781 | 37.9608 | 27.7999 | 23.7812 | 31.163 | 36.7286 | 35.4383 | 38.7496 | 36.9876 | 36.3447 | 35.6933 | 36.9356 | 33.7719 | 37.1162 | 35.7973 | 36.1118 | 34.8795 | 37.0421 | 37.0573 | 36.9677 | 38.3263 | 36.8177 | 36.7676 | 37.8916 | 38.9989 | 36.6705 | 38.2278 | 37.369 | 39.0511 | 36.2133 | 38.5674 | 36.6972 | 38.2675 | 37.3538 | 39.0225 | 37.2791 | 39.3981 | 36.974 | 38.7758 | 40.3191 | 95.1602 | 95.5621 | 94.3774
2022-09-07 21:22 | 2:58 | 23.701 | 25.2024 | 26.9841 | 36.2615 | 38.9274 | 35.425 | 38.345 | 35.1307 | 38.7865 | 36.5954 | 37.2896 | 39.8337 | 34.784 | 36.0539 | 37.2227 | 36.1172 | 35.8472 | 35.8894 | 36.3928 | 37.8309 | 27.8821 | 23.6913 | 31.0378 | 36.7272 | 35.3879 | 38.6332 | 36.9064 | 36.3269 | 35.6597 | 36.7363 | 33.7438 | 37.0654 | 35.8108 | 36.0107 | 34.676 | 37.0552 | 36.9757 | 36.9275 | 38.4094 | 36.7462 | 36.6643 | 37.8971 | 38.9141 | 36.5866 | 38.1703 | 37.2831 | 39.0848 | 36.132 | 38.5573 | 36.6034 | 38.4064 | 37.2683 | 38.9275 | 37.2229 | 39.2715 | 36.9511 | 38.6362 | 40.3987 | 95.1596 | 95.609 | 94.3989
2022-09-07 21:22 | 2:58 | 23.6756 | 25.0876 | 26.8767 | 36.1465 | 38.931 | 35.5033 | 38.3681 | 35.0601 | 38.8061 | 36.4568 | 37.2033 | 39.8803 | 34.7351 | 35.948 | 37.2932 | 36.098 | 35.8054 | 35.7661 | 36.3723 | 38.0777 | 27.7543 | 23.5959 | 30.7847 | 36.7208 | 35.3112 | 38.679 | 36.8233 | 36.3426 | 35.6374 | 36.7557 | 33.669 | 37.1855 | 35.7559 | 35.9989 | 34.6999 | 37.0019 | 37.0595 | 36.9282 | 38.2171 | 36.7493 | 36.6256 | 37.7671 | 38.9163 | 36.5056 | 38.103 | 37.2751 | 39.1087 | 36.0865 | 38.4476 | 36.4753 | 38.791 | 37.1682 | 38.9477 | 37.1379 | 39.4126 | 36.8706 | 38.6834 | 40.2335 | 95.0224 | 95.4805 | 94.3003
2022-09-07 21:22 | 2:58 | 23.4897 | 24.8531 | 26.6962 | 36.1993 | 38.9273 | 35.274 | 38.3869 | 34.982 | 38.7902 | 36.3036 | 37.0414 | 39.963 | 34.6251 | 35.874 | 37.2521 | 36.06 | 35.6793 | 35.7231 | 36.27 | 37.8908 | 27.5091 | 23.4838 | 30.536 | 36.6328 | 35.2785 | 38.5028 | 36.7999 | 36.2678 | 35.6382 | 36.7005 | 33.58 | 37.0372 | 35.68 | 35.9164 | 34.6054 | 37.0398 | 36.9074 | 36.8443 | 38.2296 | 36.5892 | 36.6228 | 37.7448 | 38.8357 | 36.3983 | 38.0003 | 37.2179 | 39.0233 | 35.9716 | 38.3254 | 36.5188 | 38.2756 | 37.1661 | 39.0031 | 37.1033 | 39.4523 | 36.765 | 38.537 | 40.3965 | 94.7051 | 95.2063 | 94.0974
2022-09-07 21:22 | 2:58 | 23.3328 | 24.6909 | 26.5493 | 36.0529 | 38.8943 | 35.0472 | 38.4222 | 34.9871 | 38.7681 | 36.3421 | 37.1052 | 39.9088 | 34.6217 | 35.8302 | 37.2009 | 36.0182 | 35.6918 | 35.7583 | 36.2342 | 37.6912 | 27.2311 | 23.2546 | 30.3428 | 36.5389 | 35.227 | 38.4044 | 36.7676 | 36.2868 | 35.5691 | 36.6642 | 33.3938 | 37.0712 | 35.6196 | 35.8946 | 34.5025 | 36.8526 | 37.0034 | 36.7666 | 38.1429 | 36.5846 | 36.5653 | 37.7272 | 38.7549 | 36.3186 | 37.9734 | 37.1521 | 39.039 | 35.8697 | 38.3772 | 36.4553 | 38.3205 | 37.1133 | 38.9065 | 37.0604 | 39.2215 | 36.7053 | 38.5872 | 40.1377 | 94.5296 | 95.0262 | 93.9596
2022-09-07 21:23 | 2:58 | 23.2138 | 24.5508 | 26.4017 | 35.9455 | 38.8492 | 35.1052 | 38.3593 | 34.8764 | 38.7156 | 36.428 | 37.1139 | 39.8538 | 34.5219 | 35.8024 | 37.18 | 35.9671 | 35.6095 | 35.7603 | 36.2192 | 37.8203 | 26.9792 | 23.2108 | 30.1383 | 36.4218 | 35.1504 | 38.6784 | 36.6643 | 36.3965 | 35.5844 | 36.7452 | 33.2583 | 37.0357 | 35.6227 | 35.7786 | 34.5547 | 37.0019 | 37.0278 | 36.8062 | 38.248 | 36.6931 | 36.461 | 37.589 | 38.7194 | 36.3684 | 37.9822 | 37.1412 | 39.023 | 35.7926 | 38.3088 | 36.3432 | 38.6522 | 36.9551 | 38.8531 | 36.9455 | 39.3034 | 36.5925 | 38.5155 | 39.9859 | 94.3666 | 94.7769 | 93.9043
2022-09-07 21:23 | 2:59 | 23.1656 | 24.3966 | 26.2764 | 36.0195 | 38.8365 | 35.3062 | 38.3845 | 34.9043 | 38.685 | 36.2104 | 36.7588 | 39.8469 | 34.503 | 35.7631 | 37.0774 | 35.9498 | 35.5377 | 35.5947 | 36.2038 | 37.6858 | 26.7213 | 23.0437 | 29.9128 | 36.4004 | 35.0737 | 38.4954 | 36.6256 | 36.2692 | 35.4708 | 36.6083 | 33.0967 | 36.9468 | 35.5532 | 35.6841 | 34.4021 | 36.8389 | 36.852 | 36.7595 | 38.1831 | 36.5045 | 36.4398 | 37.4727 | 38.6697 | 36.3273 | 37.9849 | 37.0666 | 38.9551 | 35.7724 | 38.1461 | 36.3048 | 38.7162 | 37.015 | 38.9449 | 36.8493 | 39.3663 | 36.6039 | 38.3957 | 40.1078 | 94.2344 | 94.5915 | 93.7199
2022-09-07 21:23 | 2:59 | 22.9551 | 24.221 | 26.1004 | 35.9486 | 38.8357 | 35.142 | 38.284 | 34.6804 | 38.6627 | 36.0672 | 36.7263 | 39.7623 | 34.412 | 35.7147 | 37.0624 | 35.9266 | 35.4443 | 35.5978 | 36.2147 | 37.7435 | 26.4236 | 22.9793 | 29.7186 | 36.2877 | 35.0073 | 38.4717 | 36.6228 | 36.1421 | 35.4252 | 36.5232 | 33.0825 | 36.8554 | 35.5393 | 35.6404 | 34.2381 | 36.7936 | 36.7427 | 36.7114 | 38.151 | 36.4316 | 36.2456 | 37.4548 | 38.7008 | 36.1682 | 37.7936 | 37.0365 | 38.8435 | 35.6993 | 38.1859 | 36.2805 | 38.3117 | 36.9128 | 38.7639 | 36.7678 | 39.4222 | 36.5351 | 38.3908 | 40.0763 | 94.1258 | 94.5036 | 93.7072
2022-09-07 21:23 | 2:59 | 22.9028 | 24.0924 | 25.9746 | 35.8771 | 38.7725 | 35.023 | 38.1933 | 34.6892 | 38.5947 | 36.0311 | 36.7428 | 39.7082 | 34.4014 | 35.5779 | 37.0118 | 35.9111 | 35.3923 | 35.5301 | 36.0949 | 37.5974 | 26.2026 | 22.8068 | 29.515 | 36.2095 | 34.9187 | 38.4231 | 36.5653 | 36.1134 | 35.3131 | 36.4832 | 32.8703 | 36.9116 | 35.496 | 35.5637 | 34.2572 | 36.7024 | 36.6192 | 36.6315 | 38.1352 | 36.3672 | 36.2659 | 37.4365 | 38.4962 | 36.0961 | 37.8144 | 36.9508 | 38.814 | 35.6313 | 38.0235 | 36.1481 | 37.9676 | 36.9328 | 38.7583 | 36.7604 | 39.4352 | 36.4554 | 38.3267 | 39.9873 | 94.0214 | 94.3756 | 93.6311
2022-09-07 21:23 | 2:59 | 22.6671 | 23.9266 | 25.8339 | 35.7587 | 38.7265 | 34.7964 | 38.2031 | 34.6536 | 38.6263 | 36.002 | 36.6763 | 39.7121 | 34.2794 | 35.6883 | 36.9972 | 35.8937 | 35.358 | 35.4714 | 36.0722 | 37.5355 | 25.9994 | 22.6591 | 29.3632 | 36.1718 | 34.8625 | 38.4842 | 36.461 | 35.9687 | 35.345 | 36.4341 | 32.8908 | 36.9511 | 35.4905 | 35.5082 | 34.1672 | 36.78 | 36.7874 | 36.5638 | 38.0476 | 36.3933 | 36.2347 | 37.3222 | 38.5329 | 35.987 | 37.7516 | 36.9098 | 38.7143 | 35.5095 | 38.0507 | 36.1355 | 37.9206 | 36.8164 | 38.6669 | 36.6202 | 39.1127 | 36.3881 | 38.2292 | 39.8201 | 93.9821 | 94.2712 | 93.7373
2022-09-07 21:23 | 2:59 | 22.5688 | 23.8066 | 25.7079 | 35.6862 | 38.7456 | 34.9734 | 38.1992 | 34.5357 | 38.6084 | 36.0176 | 36.5314 | 39.7118 | 34.1744 | 35.4659 | 36.8735 | 35.8237 | 35.2805 | 35.3284 | 36.007 | 37.5015 | 25.7993 | 22.5744 | 29.1943 | 36.1362 | 34.8211 | 38.3762 | 36.4398 | 35.8427 | 35.209 | 36.3413 | 32.7294 | 36.7978 | 35.414 | 35.4267 | 33.895 | 36.6108 | 36.64 | 36.4271 | 37.8899 | 36.2905 | 36.1096 | 37.2638 | 38.4775 | 35.8853 | 37.7273 | 36.8221 | 38.6953 | 35.4124 | 38.0166 | 36.1216 | 37.9583 | 36.8047 | 38.6927 | 36.663 | 39.1373 | 36.272 | 38.2652 | 39.8633 | 93.8686 | 94.1733 | 93.5834
2022-09-07 21:24 | 3:00 | 22.5185 | 23.6838 | 25.5942 | 35.6501 | 38.6973 | 34.8558 | 38.1254 | 34.5241 | 38.5949 | 35.8904 | 36.6263 | 39.7947 | 34.132 | 35.446 | 36.9725 | 35.76 | 35.2132 | 35.5344 | 36.0001 | 37.3292 | 25.6204 | 22.5523 | 29.07 | 35.9545 | 34.7145 | 38.1148 | 36.2456 | 36.0229 | 35.1923 | 36.3406 | 32.5878 | 36.8509 | 35.2433 | 35.3918 | 33.8331 | 36.5246 | 36.5309 | 36.5231 | 37.9556 | 36.1839 | 36.1104 | 37.2735 | 38.3998 | 35.8236 | 37.5976 | 36.781 | 38.7367 | 35.2874 | 37.9686 | 36.1275 | 37.8249 | 36.7952 | 38.5421 | 36.6408 | 39.0099 | 36.2965 | 38.0909 | 39.7122 | 93.8514 | 94.1058 | 93.5942
2022-09-07 21:24 | 3:00 | 22.4625 | 23.5689 | 25.4744 | 35.6478 | 38.6556 | 34.7124 | 38.1527 | 34.4085 | 38.5051 | 35.8409 | 36.4633 | 39.6619 | 34.0958 | 35.3476 | 36.9333 | 35.7546 | 35.1299 | 35.2753 | 35.9175 | 37.3645 | 25.44 | 22.3447 | 28.9576 | 35.9751 | 34.6537 | 38.0235 | 36.2659 | 36.0131 | 35.1043 | 36.2292 | 32.5789 | 36.7835 | 35.2354 | 35.3448 | 33.8795 | 36.4742 | 36.5175 | 36.3798 | 37.8951 | 36.2329 | 36.0486 | 37.1847 | 38.3096 | 35.7237 | 37.5227 | 36.76 | 38.5283 | 35.2485 | 37.8755 | 36.0189 | 37.4295 | 36.8109 | 38.4256 | 36.5792 | 39.0531 | 36.1679 | 37.9441 | 39.7574 | 93.8912 | 94.0725 | 93.6436
2022-09-07 21:24 | 3:00 | 22.1756 | 23.413 | 25.3236 | 35.4735 | 38.593 | 34.6867 | 38.1628 | 34.2814 | 38.4942 | 35.8405 | 36.4796 | 39.6097 | 34.0551 | 35.3453 | 36.7353 | 35.6604 | 35.1325 | 35.1786 | 35.9074 | 37.3872 | 25.2798 | 22.1751 | 28.8138 | 35.9443 | 34.5858 | 37.9532 | 36.2347 | 35.9453 | 35.0669 | 36.1437 | 32.4676 | 36.6613 | 35.1602 | 35.2455 | 33.7888 | 36.4962 | 36.3612 | 36.2929 | 38.0024 | 36.0206 | 35.9197 | 37.1604 | 38.2979 | 35.6226 | 37.5242 | 36.6933 | 38.4977 | 35.1521 | 37.6547 | 35.9492 | 37.6094 | 36.6906 | 38.4092 | 36.4542 | 38.9015 | 36.094 | 38.0159 | 39.7499 | 93.7868 | 94.044 | 93.52
2022-09-07 21:24 | 3:00 | 22.2193 | 23.2834 | 25.2115 | 35.4509 | 38.5234 | 34.4849 | 37.9557 | 34.2446 | 38.4635 | 35.8524 | 36.3335 | 39.5626 | 33.996 | 35.2672 | 36.6582 | 35.6258 | 35.0355 | 35.147 | 35.7954 | 37.3005 | 25.1322 | 22.1312 | 28.7007 | 35.6886 | 34.5043 | 37.8858 | 36.1096 | 35.6935 | 35.0108 | 36.0451 | 32.4861 | 36.6856 | 35.0096 | 35.202 | 33.695 | 36.4257 | 36.3685 | 36.2332 | 37.9436 | 36.0568 | 35.9436 | 36.9945 | 38.2814 | 35.6208 | 37.5335 | 36.6656 | 38.4678 | 35.074 | 37.7721 | 35.7785 | 38.0047 | 36.4856 | 38.4488 | 36.4359 | 38.9434 | 35.9942 | 37.9971 | 39.7602 | 93.7626 | 94.003 | 93.5792
2022-09-07 21:24 | 3:00 | 21.9979 | 23.13 | 25.0682 | 35.4109 | 38.5029 | 34.5946 | 38.0839 | 34.1791 | 38.4331 | 35.812 | 36.3503 | 39.5697 | 33.8239 | 35.2831 | 36.7085 | 35.5133 | 35.0225 | 35.0915 | 35.7015 | 37.3391 | 24.9811 | 21.938 | 28.5439 | 35.6187 | 34.4459 | 37.8434 | 36.1104 | 35.6033 | 34.9385 | 36.0438 | 32.4843 | 36.6203 | 34.9459 | 35.1304 | 33.6124 | 36.4235 | 36.4624 | 36.1699 | 37.8166 | 36.0021 | 35.8938 | 37.059 | 38.1904 | 35.5774 | 37.3725 | 36.5763 | 38.4346 | 35.0197 | 37.7791 | 35.865 | 37.922 | 36.4698 | 38.4401 | 36.3107 | 39.0322 | 35.9488 | 38.0099 | 39.6371 | 93.7662 | 93.9148 | 93.5067
2022-09-07 21:24 | 3:00 | 21.8265 | 22.9453 | 24.931 | 35.21 | 38.4745 | 34.4761 | 37.9899 | 34.194 | 38.3753 | 35.7451 | 36.4405 | 39.6346 | 33.7745 | 35.145 | 36.6246 | 35.5638 | 34.9552 | 35.1038 | 35.6496 | 37.1302 | 24.8292 | 21.8452 | 28.4605 | 35.6312 | 34.3909 | 37.7356 | 36.0486 | 35.5649 | 34.9631 | 35.9988 | 32.3111 | 36.5817 | 34.9898 | 35.0521 | 33.4362 | 36.509 | 36.4582 | 36.1157 | 37.9571 | 36.0313 | 35.8172 | 36.9354 | 38.1553 | 35.5357 | 37.3526 | 36.5282 | 38.2729 | 34.9902 | 37.6451 | 35.6983 | 37.9738 | 36.397 | 38.3566 | 36.2835 | 38.7953 | 35.8243 | 37.9326 | 39.5766 | 93.6584 | 93.8602 | 93.3676
2022-09-07 21:25 | 3:00 | 21.8179 | 22.8636 | 24.7851 | 35.0986 | 38.4177 | 34.5445 | 38.09 | 34.0562 | 38.3676 | 35.7608 | 36.0632 | 39.5958 | 33.7135 | 35.1792 | 36.5226 | 35.4825 | 34.9157 | 35.0503 | 35.6653 | 37.1609 | 24.7081 | 21.84 | 28.3375 | 35.4683 | 34.3244 | 37.8642 | 35.9197 | 35.673 | 34.871 | 35.9858 | 32.2466 | 36.5384 | 34.9132 | 35.002 | 33.3466 | 36.398 | 36.1705 | 36.0975 | 37.8864 | 35.8775 | 35.7304 | 36.913 | 38.0799 | 35.434 | 37.2402 | 36.482 | 38.5185 | 34.8742 | 37.5771 | 35.6181 | 38.0957 | 36.3016 | 38.4541 | 36.2304 | 38.7658 | 35.745 | 38.0128 | 39.4361 | 93.59 | 93.7607 | 93.3756
2022-09-07 21:25 | 3:01 | 21.6475 | 22.7375 | 24.6903 | 35.1465 | 38.4184 | 34.4384 | 37.8691 | 34.0453 | 38.3571 | 35.5772 | 35.9902 | 39.5662 | 33.6381 | 35.2077 | 36.4745 | 35.447 | 34.7992 | 35.0332 | 35.6323 | 37.0753 | 24.597 | 21.6433 | 28.2458 | 35.4522 | 34.2134 | 37.9645 | 35.9436 | 35.2936 | 34.7667 | 35.9007 | 32.2346 | 36.5612 | 34.8059 | 34.9088 | 33.2824 | 36.3705 | 36.0114 | 35.997 | 37.8952 | 35.7087 | 35.7471 | 36.8503 | 38.0962 | 35.3024 | 37.2549 | 36.3921 | 38.3274 | 34.8457 | 37.4383 | 35.5787 | 37.2747 | 36.2621 | 38.1971 | 36.0965 | 38.7266 | 35.6543 | 38.1978 | 39.2926 | 93.4798 | 93.6952 | 93.3475
2022-09-07 21:25 | 3:01 | 21.6046 | 22.6211 | 24.5884 | 35.0649 | 38.3411 | 34.3114 | 37.9373 | 34.0671 | 38.3032 | 35.5091 | 36.0275 | 39.4912 | 33.5922 | 35.0291 | 36.6309 | 35.4311 | 34.7634 | 35.0857 | 35.5168 | 36.9636 | 24.5086 | 21.522 | 28.1926 | 35.4101 | 34.1487 | 37.9534 | 35.8938 | 35.3032 | 34.6978 | 35.7531 | 32.1206 | 36.5067 | 34.6097 | 34.8313 | 33.1858 | 36.237 | 35.9942 | 35.9465 | 37.8852 | 35.6739 | 35.6562 | 36.7325 | 37.9456 | 35.2751 | 37.1341 | 36.379 | 38.4274 | 34.7993 | 37.3586 | 35.5399 | 37.4813 | 36.1383 | 38.1447 | 36.0772 | 38.8738 | 35.6387 | 37.648 | 39.5287 | 93.3962 | 93.5802 | 93.1928
2022-09-07 21:25 | 3:01 | 21.5049 | 22.5282 | 24.451 | 35.0834 | 38.2726 | 34.3747 | 37.9032 | 33.8812 | 38.309 | 35.494 | 35.8599 | 39.4808 | 33.516 | 34.9772 | 36.4004 | 35.3953 | 34.6723 | 34.7386 | 35.5082 | 37.0147 | 24.4017 | 21.3954 | 28.0882 | 35.371 | 34.0678 | 37.6077 | 35.8172 | 35.3865 | 34.5344 | 35.7323 | 32.0189 | 36.4883 | 34.5924 | 34.8093 | 33.053 | 36.3087 | 35.9502 | 36.0199 | 37.6649 | 35.6155 | 35.5522 | 36.679 | 37.9087 | 35.21 | 37.1464 | 36.279 | 38.2612 | 34.6573 | 37.4381 | 35.4114 | 37.9223 | 36.1349 | 38.1419 | 36.063 | 38.4376 | 35.5495 | 37.7482 | 39.5607 | 93.3031 | 93.5102 | 93.151
2022-09-07 21:25 | 3:01 | 21.2678 | 22.3895 | 24.3573 | 34.9888 | 38.2874 | 34.1852 | 37.8939 | 33.8657 | 38.2377 | 35.567 | 35.8676 | 39.5325 | 33.4504 | 34.9734 | 36.4315 | 35.3113 | 34.6457 | 34.905 | 35.4337 | 36.8089 | 24.3231 | 21.2124 | 27.986 | 35.0939 | 34.0338 | 37.6763 | 35.7304 | 35.2312 | 34.6097 | 35.7349 | 31.8784 | 36.2894 | 34.6222 | 34.759 | 33.2381 | 36.2341 | 36.1787 | 35.8077 | 37.6806 | 35.8118 | 35.577 | 36.5485 | 37.8688 | 35.2103 | 37.0664 | 36.2102 | 38.3077 | 34.5457 | 37.4597 | 35.3188 | 37.6717 | 35.9536 | 38.083 | 35.8562 | 38.6895 | 35.4959 | 37.6204 | 39.7098 | 93.194 | 93.4167 | 93.0786
2022-09-07 21:25 | 3:01 | 21.1609 | 22.2201 | 24.2126 | 34.9086 | 38.2204 | 34.2273 | 37.8243 | 33.813 | 38.2282 | 35.4277 | 35.8958 | 39.4781 | 33.3939 | 34.9845 | 36.3546 | 35.252 | 34.6061 | 34.7743 | 35.3771 | 36.7833 | 24.2231 | 21.3083 | 27.8609 | 35.0421 | 33.9499 | 37.592 | 35.7471 | 35.0382 | 34.4797 | 35.6328 | 31.8847 | 36.3233 | 34.5172 | 34.7245 | 33.1347 | 36.2472 | 36.242 | 35.7862 | 37.5703 | 35.8712 | 35.5604 | 36.6139 | 37.7223 | 35.219 | 36.9513 | 36.2102 | 38.045 | 34.5274 | 37.558 | 35.2554 | 38.0796 | 35.8096 | 38.2549 | 35.8719 | 38.6807 | 35.4241 | 37.5421 | 39.4374 | 93.1903 | 93.35 | 93.1616
2022-09-07 21:26 | 3:02 | 21.1676 | 22.1791 | 24.1505 | 34.7511 | 38.1636 | 34.3419 | 37.6454 | 33.6563 | 38.1504 | 35.328 | 35.6214 | 39.4563 | 33.2539 | 34.6823 | 36.1394 | 35.1904 | 34.4811 | 34.5373 | 35.362 | 36.6871 | 24.1668 | 21.0772 | 27.7771 | 35.0688 | 33.8888 | 37.4989 | 35.6562 | 35.0864 | 34.4019 | 35.6285 | 31.7994 | 36.3964 | 34.3898 | 34.6762 | 32.9024 | 36.1818 | 35.9606 | 35.8108 | 37.5624 | 35.6011 | 35.5258 | 36.4843 | 37.7674 | 35.0796 | 36.9639 | 36.1001 | 38.1041 | 34.4772 | 37.318 | 35.2116 | 37.8305 | 35.8165 | 38.0136 | 35.8496 | 38.5162 | 35.3237 | 37.5598 | 39.2523 | 93.1585 | 93.268 | 93.1336
2022-09-07 21:26 | 3:02 | 20.9616 | 22.0763 | 24.0197 | 34.5889 | 38.1016 | 34.0778 | 37.7376 | 33.6285 | 38.1685 | 35.2985 | 35.895 | 39.3972 | 33.2862 | 34.7742 | 36.106 | 35.1675 | 34.4518 | 34.6406 | 35.3356 | 36.7869 | 24.0818 | 20.8875 | 27.7143 | 35.0325 | 33.8019 | 37.5491 | 35.5522 | 35.0844 | 34.4117 | 35.5206 | 31.6205 | 36.3195 | 34.3166 | 34.5582 | 32.6574 | 36.1203 | 35.8726 | 35.7077 | 37.5142 | 35.5068 | 35.6096 | 36.4385 | 37.6941 | 34.9867 | 36.8687 | 36.0753 | 38.0479 | 34.4359 | 37.2955 | 35.2126 | 37.8709 | 35.8277 | 37.8877 | 35.6812 | 38.5653 | 35.2519 | 37.5327 | 39.3402 | 93.0329 | 93.1535 | 92.9819
2022-09-07 21:26 | 3:02 | 20.9828 | 21.9995 | 23.9454 | 34.7062 | 38.1332 | 33.951 | 37.6619 | 33.5316 | 38.1063 | 35.3416 | 35.5898 | 39.2806 | 33.1853 | 34.6768 | 36.2377 | 35.1378 | 34.3569 | 34.5969 | 35.2254 | 36.6324 | 24.0857 | 21.0969 | 27.8437 | 35.0224 | 33.7556 | 37.7214 | 35.577 | 35.1172 | 34.3143 | 35.4392 | 31.6717 | 36.2543 | 34.4172 | 34.5666 | 32.6978 | 36.0179 | 35.5905 | 35.6566 | 37.3209 | 35.3366 | 35.727 | 36.4264 | 37.6556 | 34.9707 | 36.7523 | 36.0246 | 38.1217 | 34.4471 | 37.3417 | 35.1406 | 38.0322 | 35.7514 | 38.0566 | 35.5534 | 38.485 | 35.213 | 37.4516 | 39.2452 | 92.8461 | 93.0378 | 92.8635
2022-09-07 21:26 | 3:02 | 19.6257 | 21.5944 | 23.5437 | 34.5287 | 38.0395 | 33.8445 | 37.5292 | 33.5201 | 38.1023 | 35.1996 | 35.7073 | 39.2925 | 33.0714 | 34.5928 | 36.058 | 35.0795 | 34.2874 | 34.6134 | 35.1089 | 36.6244 | 24.294 | 21.7462 | 28.5181 | 34.8885 | 33.7118 | 37.7721 | 35.5604 | 35.0054 | 34.3273 | 35.5099 | 31.7064 | 36.2627 | 34.2491 | 34.4675 | 32.812 | 35.9793 | 35.6689 | 35.5294 | 37.4575 | 35.3091 | 35.6994 | 36.4748 | 37.7312 | 35.0319 | 36.8227 | 35.9545 | 38.0518 | 34.5911 | 37.268 | 35.1083 | 37.5854 | 35.8504 | 38.028 | 35.5479 | 38.4614 | 35.3253 | 37.4226 | 39.3628 | 92.7155 | 92.9279 | 92.722
2022-09-07 21:26 | 3:02 | 19.1576 | 21.1965 | 23.0855 | 34.4848 | 37.9275 | 33.7389 | 37.5902 | 33.3209 | 38.0404 | 35.0303 | 35.4294 | 39.2054 | 32.9365 | 34.5341 | 35.9533 | 34.9721 | 34.163 | 34.4901 | 35.0549 | 36.7302 | 25.0211 | 22.9221 | 29.6363 | 35.0185 | 33.7253 | 37.8356 | 35.5258 | 34.8913 | 34.2133 | 35.5672 | 32.0988 | 36.1096 | 34.1605 | 34.5618 | 32.9524 | 35.9755 | 35.6784 | 35.5958 | 37.396 | 35.2662 | 35.7085 | 36.5807 | 37.8012 | 35.1449 | 37.0819 | 35.9332 | 38.1228 | 34.7394 | 37.2782 | 35.2273 | 37.1589 | 35.8747 | 37.9435 | 35.5509 | 38.5815 | 35.4286 | 37.4441 | 39.2719 | 92.6635 | 92.7722 | 92.7235
2022-09-07 21:26 | 3:02 | 18.7792 | 20.856 | 22.7779 | 34.3322 | 37.9034 | 33.6357 | 37.4882 | 33.3242 | 37.9821 | 35.0668 | 35.4316 | 39.2561 | 32.8073 | 34.4731 | 36.1302 | 34.8757 | 34.1315 | 34.3162 | 35.0243 | 36.5975 | 25.9677 | 24.2977 | 30.5151 | 35.1242 | 33.7536 | 37.7796 | 35.6096 | 35.1797 | 34.1856 | 35.6213 | 32.412 | 36.0506 | 34.0177 | 34.6255 | 33.0149 | 35.8746 | 35.6009 | 35.7127 | 37.1662 | 35.2264 | 35.7486 | 36.682 | 37.9605 | 35.4073 | 37.3002 | 35.953 | 38.1541 | 34.9278 | 37.6328 | 35.2506 | 37.3867 | 36.0373 | 38.0531 | 35.6935 | 38.6026 | 35.5557 | 37.9176 | 39.2314 | 92.4484 | 92.622 | 92.5626
2022-09-07 21:27 | 3:02 | 18.4225 | 20.5972 | 22.503 | 34.2596 | 37.7581 | 33.6188 | 37.3737 | 33.1778 | 37.9299 | 34.8885 | 35.2529 | 39.2347 | 32.7437 | 34.5074 | 36.002 | 34.8103 | 34.0253 | 34.2118 | 34.9279 | 36.6647 | 26.9312 | 25.6198 | 31.1694 | 35.2315 | 33.8059 | 37.9443 | 35.727 | 34.9609 | 34.1907 | 35.7152 | 32.6313 | 36.0311 | 33.9566 | 34.7002 | 33.2122 | 35.8974 | 35.6295 | 35.7455 | 37.2849 | 35.2891 | 35.8005 | 36.7447 | 37.9925 | 35.5603 | 37.5011 | 35.9573 | 38.2682 | 35.0934 | 37.7214 | 35.3893 | 37.0896 | 36.102 | 38.0722 | 35.6688 | 38.7119 | 35.6755 | 37.9424 | 39.2092 | 92.3774 | 92.506 | 92.5564
2022-09-07 21:27 | 3:03 | 18.1364 | 20.2839 | 22.2227 | 34.0606 | 37.6835 | 33.5665 | 37.2187 | 33.1005 | 37.8435 | 35.0015 | 35.2389 | 39.0697 | 32.6694 | 34.4354 | 35.9907 | 34.691 | 33.9778 | 34.2659 | 34.8691 | 36.58 | 27.8168 | 26.836 | 31.6668 | 35.3244 | 33.8304 | 38.0271 | 35.6994 | 34.7852 | 34.2459 | 35.7131 | 32.8047 | 36.0189 | 33.9649 | 34.6876 | 33.2693 | 35.9733 | 35.5842 | 35.632 | 37.15 | 35.2414 | 35.8359 | 36.8066 | 38.0554 | 35.6377 | 37.4267 | 35.9583 | 38.1849 | 35.1888 | 37.6492 | 35.4478 | 36.9817 | 36.1401 | 38.106 | 35.6962 | 38.7384 | 35.6918 | 37.9743 | 39.3015 | 92.2988 | 92.4262 | 92.4313
2022-09-07 21:27 | 3:03 | 17.8607 | 20.0266 | 21.956 | 34.2308 | 37.6617 | 33.5361 | 37.2813 | 33.0222 | 37.8016 | 34.8477 | 34.9128 | 39.1292 | 32.5691 | 34.0636 | 35.7655 | 34.5981 | 33.8828 | 34.2234 | 34.6888 | 36.4572 | 28.5922 | 27.878 | 32.0428 | 35.3282 | 33.8196 | 38.1057 | 35.7085 | 34.7794 | 34.2277 | 35.8291 | 32.9581 | 35.9714 | 33.9027 | 34.6822 | 33.336 | 36.0588 | 35.5048 | 35.5839 | 37.1053 | 35.2931 | 35.8168 | 36.8491 | 38.2082 | 35.7512 | 37.4736 | 35.8851 | 38.2005 | 35.2902 | 37.6693 | 35.4429 | 37.0038 | 36.2484 | 38.1471 | 35.6983 | 38.7955 | 35.7612 | 37.8645 | 39.1912 | 92.1952 | 92.3292 | 92.4178
2022-09-07 21:27 | 3:03 | 17.6226 | 19.7923 | 21.7693 | 33.9757 | 37.5657 | 33.371 | 37.1934 | 32.9154 | 37.795 | 34.8415 | 35.0171 | 39.0494 | 32.3732 | 34.0938 | 35.6664 | 34.5612 | 33.7661 | 33.9552 | 34.7174 | 36.3979 | 29.2029 | 28.6578 | 32.3341 | 35.3766 | 33.8628 | 38.2471 | 35.7486 | 35.0659 | 34.2 | 35.7548 | 33.0339 | 35.9175 | 33.8935 | 34.7068 | 33.3766 | 35.9831 | 35.4088 | 35.5803 | 37.1437 | 35.265 | 35.8501 | 36.8849 | 38.2107 | 35.8302 | 37.5249 | 35.9494 | 38.2711 | 35.3763 | 37.7671 | 35.5157 | 37.1825 | 36.2407 | 38.0733 | 35.7724 | 38.7074 | 35.7945 | 38.1327 | 39.1263 | 92.1421 | 92.2297 | 92.3435
2022-09-07 21:27 | 3:03 | 17.4267 | 19.5937 | 21.555 | 34.0025 | 37.3797 | 33.1743 | 37.0252 | 32.8966 | 37.7006 | 34.6203 | 34.8979 | 39.0377 | 32.3474 | 34.0317 | 35.4879 | 34.4954 | 33.7062 | 33.9782 | 34.6334 | 36.6196 | 29.7217 | 29.2968 | 32.5158 | 35.3205 | 33.8383 | 38.2502 | 35.8005 | 34.6793 | 34.1381 | 35.9174 | 33.1605 | 35.8926 | 33.8577 | 34.7506 | 33.4383 | 35.9663 | 35.3833 | 35.7345 | 37.2322 | 35.2548 | 35.9249 | 36.9064 | 38.1981 | 35.8991 | 37.6386 | 35.969 | 38.3174 | 35.4273 | 37.859 | 35.5249 | 37.1636 | 36.2469 | 38.1691 | 35.7647 | 38.7311 | 35.8576 | 38.2096 | 39.1341 | 92.1101 | 92.1887 | 92.2996
2022-09-07 21:27 | 3:03 | 17.1897 | 19.3824 | 21.3 | 33.8071 | 37.3481 | 33.2253 | 36.935 | 32.6726 | 37.6431 | 34.5604 | 34.758 | 38.9063 | 32.2001 | 34.0019 | 35.4504 | 34.4696 | 33.5732 | 33.7395 | 34.5305 | 36.4231 | 30.132 | 29.7724 | 32.6697 | 35.3704 | 33.8544 | 38.2722 | 35.8359 | 34.9416 | 34.1206 | 35.7737 | 33.2248 | 35.9119 | 33.7868 | 34.7008 | 33.5218 | 35.9753 | 35.3394 | 35.7103 | 37.0341 | 35.2397 | 35.8391 | 36.945 | 38.2192 | 35.9921 | 37.5847 | 35.9313 | 38.3245 | 35.4998 | 37.9135 | 35.6022 | 37.0741 | 36.3484 | 38.1156 | 35.7637 | 38.8661 | 35.8716 | 38.0188 | 39.2092 | 92.1266 | 92.2322 | 92.2866
2022-09-07 21:28 | 3:04 | 16.9794 | 19.1685 | 21.1048 | 33.689 | 37.1944 | 33.176 | 36.9487 | 32.5422 | 37.5288 | 34.6539 | 34.6653 | 38.8174 | 32.0922 | 33.9699 | 35.4049 | 34.3561 | 33.5696 | 33.7411 | 34.448 | 36.7718 | 30.4682 | 30.1311 | 32.803 | 35.3863 | 33.886 | 38.4197 | 35.8168 | 35.0041 | 34.2131 | 35.9946 | 33.2826 | 35.7542 | 33.7389 | 34.7122 | 33.5806 | 35.9357 | 35.3546 | 35.6941 | 37.1583 | 35.261 | 35.8962 | 36.9248 | 38.2876 | 36.0216 | 37.6593 | 35.9154 | 38.3408 | 35.5721 | 37.8874 | 35.5805 | 37.0375 | 36.446 | 38.1097 | 35.782 | 38.8644 | 35.9318 | 38.111 | 39.3394 | 92.2119 | 92.3666 | 92.3584
2022-09-07 21:28 | 3:04 | 16.8045 | 18.9779 | 20.9857 | 33.6559 | 37.1994 | 33.1853 | 36.898 | 32.4071 | 37.4998 | 34.5665 | 34.4305 | 38.837 | 32.1803 | 33.7831 | 35.3561 | 34.3307 | 33.4785 | 33.5643 | 34.4309 | 36.6078 | 30.7397 | 30.4214 | 32.9002 | 35.4108 | 33.925 | 38.4335 | 35.8501 | 34.9845 | 34.2081 | 35.958 | 33.3274 | 35.7114 | 33.7494 | 34.8196 | 33.6424 | 35.8513 | 35.3509 | 35.6569 | 37.2255 | 35.24 | 35.8702 | 36.9978 | 38.2308 | 36.0819 | 37.6842 | 35.9276 | 38.2491 | 35.6265 | 37.9582 | 35.6073 | 37.2272 | 36.4886 | 38.2302 | 35.6913 | 38.7537 | 35.9932 | 38.1869 | 39.1569 | 92.2966 | 92.4252 | 92.4598
2022-09-07 21:28 | 3:04 | 16.6369 | 18.793 | 20.7869 | 33.7005 | 37.0901 | 33.1241 | 36.9608 | 32.3562 | 37.461 | 34.5136 | 34.4021 | 38.784 | 32.0035 | 33.7519 | 35.2665 | 34.1409 | 33.4221 | 33.6185 | 34.2876 | 36.3039 | 30.9623 | 30.6263 | 33.011 | 35.3852 | 33.9426 | 38.4 | 35.9249 | 34.7859 | 34.121 | 36.0188 | 33.3809 | 35.5879 | 33.7002 | 34.9083 | 33.6818 | 35.7108 | 35.2553 | 35.6948 | 37.0482 | 35.2036 | 35.9389 | 37.0411 | 38.2863 | 36.1639 | 37.7834 | 35.9855 | 38.3147 | 35.6876 | 37.919 | 35.6229 | 37.1105 | 36.5807 | 38.2703 | 35.7076 | 38.9165 | 36.0456 | 38.1483 | 39.1139 | 92.3606 | 92.5291 | 92.4668
2022-09-07 21:28 | 3:04 | 16.4882 | 18.6023 | 20.6 | 33.6431 | 36.9521 | 33.06 | 36.6063 | 32.2919 | 37.3614 | 34.4846 | 34.3637 | 38.5981 | 31.7092 | 33.6853 | 35.273 | 34.1326 | 33.3123 | 33.489 | 34.1647 | 36.1708 | 31.1207 | 30.7896 | 33.1212 | 35.3793 | 33.9293 | 38.5224 | 35.8391 | 34.8565 | 34.1921 | 36.0318 | 33.437 | 35.6617 | 33.6585 | 34.9744 | 33.7626 | 35.7894 | 35.2502 | 35.5919 | 37.0591 | 35.2015 | 35.9772 | 37.0438 | 38.3476 | 36.1674 | 37.7632 | 35.9727 | 38.2265 | 35.7518 | 38.0466 | 35.648 | 37.1223 | 36.5661 | 38.1535 | 35.6694 | 38.8671 | 36.1131 | 38.322 | 39.1839 | 92.4454 | 92.6292 | 92.5142
2022-09-07 21:28 | 3:04 | 16.2501 | 18.4091 | 20.4115 | 33.558 | 36.7621 | 32.9593 | 36.5382 | 32.0596 | 37.2489 | 34.4692 | 33.9439 | 38.5438 | 31.6802 | 33.5189 | 35.2183 | 34.0963 | 33.1718 | 33.619 | 34.2208 | 36.147 | 31.2779 | 30.9266 | 33.1808 | 35.2778 | 33.9265 | 38.2443 | 35.8962 | 34.6795 | 34.1844 | 35.9642 | 33.4756 | 35.5315 | 33.5649 | 34.87 | 33.7673 | 35.6868 | 35.2633 | 35.5089 | 37.0241 | 35.177 | 36.0708 | 37.0968 | 38.325 | 36.228 | 37.8695 | 36.0072 | 38.2933 | 35.8086 | 38.042 | 35.6505 | 37.1891 | 36.5597 | 38.1305 | 35.7346 | 38.9887 | 36.1721 | 38.3779 | 39.1199 | 92.5988 | 92.7922 | 92.661
2022-09-07 21:28 | 3:04 | 16.1696 | 18.2375 | 20.2558 | 33.6067 | 36.6803 | 32.824 | 36.4952 | 32.0147 | 37.1743 | 34.2457 | 34.0274 | 38.3686 | 31.6754 | 33.341 | 35.0775 | 33.9832 | 33.1464 | 33.5173 | 34.0457 | 36.2169 | 31.3937 | 31.0387 | 33.271 | 35.2871 | 33.9267 | 38.1554 | 35.8702 | 34.4849 | 34.0983 | 35.8976 | 33.5424 | 35.4955 | 33.4106 | 34.8953 | 33.7897 | 35.7215 | 35.2989 | 35.5346 | 36.8659 | 35.161 | 36.0795 | 37.1265 | 38.3373 | 36.3122 | 37.8276 | 36.0214 | 38.2857 | 35.872 | 38.0692 | 35.6774 | 37.1728 | 36.5942 | 38.1021 | 35.8346 | 38.9448 | 36.1911 | 38.3716 | 39.1388 | 92.7166 | 92.9418 | 92.7626
2022-09-07 21:29 | 3:04 | 15.9535 | 18.0731 | 20.055 | 33.3661 | 36.62 | 32.6774 | 36.4085 | 31.886 | 37.1452 | 34.3292 | 33.9226 | 38.4109 | 31.5727 | 33.4456 | 35.1117 | 33.9088 | 33.1137 | 33.3099 | 34.0534 | 36.0116 | 31.483 | 31.1015 | 33.3049 | 35.3408 | 33.9344 | 38.371 | 35.9389 | 34.581 | 34.1206 | 36.1451 | 33.581 | 35.443 | 33.5303 | 34.8741 | 33.8298 | 35.707 | 35.2771 | 35.4988 | 36.8461 | 35.1646 | 36.1431 | 37.1988 | 38.4025 | 36.351 | 37.8956 | 36.0481 | 38.3194 | 35.9415 | 38.0481 | 35.7334 | 37.2337 | 36.6214 | 38.1767 | 35.7733 | 39.0182 | 36.24 | 38.2893 | 39.2263 | 92.8189 | 93.0512 | 92.8705
2022-09-07 21:29 | 3:05 | 15.8014 | 17.9319 | 19.9201 | 33.2944 | 36.5463 | 32.6735 | 36.2765 | 31.8261 | 37.0754 | 34.4773 | 33.712 | 38.3281 | 31.5152 | 33.2671 | 35.0589 | 33.8226 | 33.0632 | 33.3967 | 33.8914 | 36.1333 | 31.5534 | 31.1881 | 33.3349 | 35.3723 | 33.9628 | 38.4453 | 35.9772 | 34.4822 | 34.029 | 36.1461 | 33.627 | 35.3229 | 33.5593 | 34.9346 | 33.8641 | 35.6792 | 35.2135 | 35.554 | 36.7258 | 35.1134 | 36.1421 | 37.2147 | 38.4589 | 36.4213 | 37.8552 | 36.0828 | 38.3814 | 36.0069 | 38.253 | 35.7405 | 37.387 | 36.6169 | 38.1331 | 35.8159 | 38.8258 | 36.3044 | 38.5294 | 39.1431 | 92.9506 | 93.1837 | 93.0294
2022-09-07 21:29 | 3:05 | 15.6051 | 17.5507 | 19.748 | 33.3311 | 36.5401 | 32.4475 | 36.1639 | 31.7411 | 37.018 | 34.4034 | 33.7771 | 38.3015 | 31.3223 | 33.2591 | 34.9019 | 33.7505 | 32.9396 | 33.1455 | 33.7679 | 36.0016 | 31.602 | 31.206 | 33.3761 | 35.351 | 34.0113 | 38.7198 | 36.0708 | 34.5432 | 34.0528 | 36.0924 | 33.683 | 35.3085 | 33.3713 | 34.7651 | 33.9423 | 35.6442 | 35.1673 | 35.5342 | 36.7651 | 35.1003 | 36.1867 | 37.234 | 38.5063 | 36.4556 | 37.8978 | 36.0617 | 38.3154 | 36.0533 | 38.1991 | 35.7742 | 37.3802 | 36.7521 | 38.1638 | 35.8819 | 38.8908 | 36.3597 | 38.5737 | 39.2351 | 93.0525 | 93.2869 | 93.0498
2022-09-07 21:29 | 3:05 | 15.2979 | 15.2863 | 19.6123 | 33.1178 | 36.4069 | 32.5478 | 36.0388 | 31.5201 | 36.8761 | 34.4602 | 33.4549 | 38.1444 | 31.2224 | 32.8229 | 34.9327 | 33.6482 | 32.8472 | 32.7346 | 33.6977 | 35.9436 | 31.5655 | 31.2227 | 33.4214 | 35.2181 | 33.9991 | 38.7181 | 36.0795 | 34.5357 | 34.0125 | 36.0341 | 33.7155 | 35.1829 | 33.3709 | 34.8296 | 33.9612 | 35.601 | 35.0903 | 35.5095 | 37.0907 | 35.0439 | 36.1709 | 37.276 | 38.5229 | 36.4826 | 37.9605 | 36.1401 | 38.3393 | 36.1283 | 38.1989 | 35.7692 | 37.4031 | 36.7865 | 38.2644 | 35.9413 | 38.8723 | 36.4036 | 38.5731 | 39.1373 | 93.2105 | 93.3939 | 93.1744
2022-09-07 21:29 | 3:05 | 17.3296 | 16.8776 | 21.9724 | 33.3077 | 36.2793 | 32.7485 | 36.0311 | 31.6105 | 36.7987 | 34.3378 | 33.5318 | 38.1452 | 31.424 | 32.7975 | 34.9386 | 33.6281 | 32.9278 | 33.0999 | 33.7347 | 36.1302 | 31.5917 | 31.2622 | 33.4854 | 35.3499 | 34.0346 | 38.6426 | 36.1431 | 34.4774 | 34.0364 | 36.063 | 33.7491 | 35.2457 | 33.4469 | 34.9149 | 34.031 | 35.7711 | 35.1465 | 35.5593 | 36.8201 | 35.0796 | 36.1535 | 37.3348 | 38.5722 | 36.5799 | 38.0062 | 36.1607 | 38.4378 | 36.2095 | 38.2467 | 35.8725 | 37.4109 | 36.8336 | 38.2677 | 35.8695 | 39.0204 | 36.4532 | 38.5131 | 39.1943 | 93.2862 | 93.5348 | 93.2212
2022-09-07 21:29 | 3:05 | 19.4242 | 19.2899 | 24.4843 | 33.8343 | 36.2607 | 32.86 | 36.0874 | 31.9299 | 36.8439 | 34.4856 | 33.9511 | 38.294 | 31.7913 | 33.2084 | 35.0253 | 33.6264 | 33.0525 | 33.3377 | 33.9398 | 36.2651 | 31.6395 | 31.2881 | 33.582 | 35.4823 | 34.0353 | 38.6567 | 36.1421 | 34.3124 | 34.0784 | 36.0926 | 33.7943 | 35.1285 | 33.5667 | 35.0195 | 34.0625 | 35.7455 | 35.1697 | 35.6585 | 36.9269 | 35.1127 | 36.2672 | 37.4035 | 38.6362 | 36.6811 | 38.091 | 36.1697 | 38.355 | 36.2629 | 38.3236 | 35.9082 | 37.4898 | 36.8831 | 38.2955 | 36.0154 | 39.0526 | 36.5447 | 38.5361 | 39.1912 | 93.4351 | 93.6457 | 93.2809
2022-09-07 21:30 | 3:05 | 21.2788 | 21.6875 | 26.428 | 34.3685 | 36.3912 | 32.9367 | 36.2745 | 32.1305 | 36.8575 | 34.5189 | 34.0706 | 38.2186 | 32.0974 | 33.4995 | 35.1612 | 33.7109 | 33.2234 | 33.7198 | 34.0316 | 36.3734 | 31.6968 | 31.3295 | 33.713 | 35.6332 | 34.0998 | 38.8589 | 36.1867 | 34.7241 | 34.1498 | 36.2001 | 33.834 | 35.2698 | 33.7278 | 35.0575 | 34.1177 | 35.8125 | 35.3429 | 35.7782 | 37.1647 | 35.1816 | 36.3775 | 37.3824 | 38.6757 | 36.7363 | 38.0994 | 36.1986 | 38.3664 | 36.3858 | 38.4061 | 35.9975 | 37.4439 | 36.9863 | 38.2656 | 36.0783 | 39.0796 | 36.5771 | 38.6096 | 39.3031 | 93.5628 | 93.8217 | 93.4398
2022-09-07 21:30 | 3:06 | 22.8823 | 23.8245 | 27.8475 | 34.6 | 36.3609 | 33.1413 | 36.3062 | 32.35 | 36.8665 | 34.7039 | 34.435 | 38.363 | 32.3347 | 33.7994 | 35.2052 | 33.7895 | 33.39 | 33.9096 | 34.127 | 36.5985 | 31.8112 | 31.3671 | 33.8389 | 35.8816 | 34.186 | 38.7931 | 36.1709 | 34.8684 | 34.2538 | 36.2648 | 33.9004 | 35.3607 | 33.895 | 35.1667 | 34.1781 | 35.8153 | 35.4052 | 35.8453 | 37.2836 | 35.2533 | 36.3895 | 37.4497 | 38.7638 | 36.812 | 38.1452 | 36.2438 | 38.4853 | 36.4481 | 38.4406 | 36.0878 | 37.5179 | 37.0484 | 38.2852 | 36.1247 | 39.1621 | 36.6827 | 38.6818 | 39.4006 | 93.7554 | 94.0212 | 93.5994
2022-09-07 21:30 | 3:06 | 24.2972 | 25.6964 | 28.9329 | 35.0338 | 36.4264 | 33.3165 | 36.5113 | 32.6016 | 36.8429 | 34.8579 | 34.6178 | 38.2511 | 32.618 | 33.9433 | 35.2447 | 33.8015 | 33.5962 | 34.0696 | 34.239 | 36.6326 | 31.9213 | 31.4023 | 33.9971 | 36.0022 | 34.2353 | 38.5433 | 36.1535 | 34.9146 | 34.19 | 36.2373 | 33.9511 | 35.2955 | 33.9951 | 35.2605 | 34.1981 | 35.8601 | 35.5018 | 35.9213 | 37.267 | 35.3474 | 36.4098 | 37.493 | 38.7228 | 36.9314 | 38.2318 | 36.2727 | 38.4676 | 36.5517 | 38.5333 | 36.0662 | 37.646 | 37.0408 | 38.3707 | 36.114 | 39.0795 | 36.6953 | 38.7037 | 39.3216 | 93.9796 | 94.1923 | 93.6751
2022-09-07 21:30 | 3:06 | 25.4586 | 27.1777 | 29.6236 | 35.1217 | 36.4832 | 33.5425 | 36.6121 | 32.731 | 36.875 | 34.8919 | 34.8073 | 38.3632 | 32.7648 | 34.026 | 35.2886 | 33.8575 | 33.717 | 34.2555 | 34.2908 | 36.7465 | 32.0437 | 31.4349 | 34.1173 | 36.0524 | 34.2761 | 38.7507 | 36.2672 | 35.029 | 34.2627 | 36.2466 | 34.0382 | 35.4828 | 34.1177 | 35.3549 | 34.2892 | 36.0603 | 35.5362 | 35.9718 | 37.3353 | 35.3576 | 36.4907 | 37.5979 | 38.782 | 37.0098 | 38.3153 | 36.337 | 38.5011 | 36.6197 | 38.5889 | 36.224 | 37.6446 | 37.1515 | 38.4718 | 36.2362 | 39.0567 | 36.7835 | 38.7831 | 39.325 | 94.0566 | 94.3253 | 93.6979
2022-09-07 21:30 | 3:06 | 26.4663 | 28.3746 | 30.0957 | 35.4029 | 36.4946 | 33.5744 | 36.6449 | 32.8701 | 36.9305 | 34.9173 | 34.9448 | 38.3599 | 32.8934 | 34.226 | 35.5625 | 33.9109 | 33.8881 | 34.4052 | 34.3965 | 36.8864 | 32.1724 | 31.4596 | 34.31 | 36.0805 | 34.3318 | 38.829 | 36.3775 | 34.9081 | 34.3249 | 36.2998 | 34.1273 | 35.4187 | 34.1793 | 35.4472 | 34.3513 | 36.0601 | 35.5035 | 36.0573 | 37.3173 | 35.4016 | 36.4529 | 37.6163 | 38.8589 | 37.1178 | 38.3466 | 36.4123 | 38.4939 | 36.7017 | 38.6196 | 36.2425 | 37.7346 | 37.2518 | 38.4138 | 36.2279 | 39.1104 | 36.868 | 38.8282 | 39.3633 | 94.2417 | 94.4943 | 93.8623
2022-09-07 21:30 | 3:06 | 27.2304 | 29.2714 | 30.4612 | 35.6366 | 36.5252 | 33.623 | 36.6792 | 32.9911 | 36.8874 | 35.0454 | 35.0687 | 38.4683 | 33.0387 | 34.2854 | 35.6748 | 33.9413 | 33.9859 | 34.5057 | 34.4264 | 36.9507 | 32.3189 | 31.4846 | 34.4586 | 36.2699 | 34.3978 | 38.8545 | 36.3895 | 34.9077 | 34.3632 | 36.4045 | 34.1841 | 35.5623 | 34.2622 | 35.5399 | 34.401 | 36.1277 | 35.5819 | 36.1378 | 37.4138 | 35.4755 | 36.5768 | 37.687 | 38.8451 | 37.2018 | 38.4297 | 36.4511 | 38.5246 | 36.786 | 38.6698 | 36.292 | 37.7831 | 37.3087 | 38.5031 | 36.2886 | 39.0673 | 36.9087 | 38.9413 | 39.3204 | 94.3629 | 94.7131 | 93.9401
2022-09-07 21:31 | 3:07 | 27.867 | 29.9109 | 30.6856 | 35.6373 | 36.5407 | 33.8549 | 36.7164 | 33.1782 | 36.8938 | 35.0904 | 35.1534 | 38.4106 | 33.1201 | 34.3878 | 35.7613 | 33.9596 | 34.0279 | 34.6169 | 34.5136 | 36.9076 | 32.4365 | 31.5356 | 34.6241 | 36.3585 | 34.4689 | 38.8191 | 36.4098 | 35.0595 | 34.4055 | 36.4423 | 34.2788 | 35.537 | 34.335 | 35.5909 | 34.4474 | 36.0905 | 35.6072 | 36.2206 | 37.4185 | 35.5275 | 36.7093 | 37.767 | 38.8951 | 37.2786 | 38.4591 | 36.4559 | 38.5981 | 36.8782 | 38.6635 | 36.3879 | 37.8462 | 37.3721 | 38.5838 | 36.3591 | 39.1981 | 36.9744 | 38.9837 | 39.3764 | 94.4731 | 94.8796 | 94.104
2022-09-07 21:31 | 3:07 | 28.3687 | 30.3985 | 30.8374 | 35.8663 | 36.5027 | 33.886 | 36.8274 | 33.2214 | 36.9486 | 35.1828 | 35.3206 | 38.4037 | 33.2291 | 34.4476 | 35.6911 | 34.0088 | 34.1841 | 34.6895 | 34.5782 | 36.9284 | 32.5934 | 31.5492 | 34.7902 | 36.3839 | 34.5348 | 38.9665 | 36.4907 | 35.059 | 34.5024 | 36.5605 | 34.3326 | 35.5715 | 34.4059 | 35.6546 | 34.4979 | 36.2241 | 35.7018 | 36.2476 | 37.4589 | 35.5357 | 36.7528 | 37.7883 | 38.9815 | 37.3777 | 38.4894 | 36.5267 | 38.6325 | 36.9623 | 38.7667 | 36.4243 | 37.8775 | 37.4245 | 38.6704 | 36.4665 | 39.2163 | 37.0414 | 39.0091 | 39.3619 | 94.6593 | 95.055 | 94.171
2022-09-07 21:31 | 3:07 | 28.7837 | 30.7233 | 30.959 | 35.9256 | 36.5308 | 33.963 | 36.8703 | 33.2777 | 36.923 | 35.193 | 35.2256 | 38.3697 | 33.3181 | 34.5668 | 35.7671 | 34.0341 | 34.2493 | 34.7219 | 34.6389 | 37.0294 | 32.7227 | 31.5723 | 34.951 | 36.4565 | 34.5831 | 38.9088 | 36.4529 | 35.1366 | 34.5108 | 36.513 | 34.4027 | 35.682 | 34.4839 | 35.7122 | 34.5673 | 36.245 | 35.7766 | 36.2672 | 37.5855 | 35.6013 | 36.7588 | 37.8512 | 38.973 | 37.4368 | 38.5579 | 36.5927 | 38.6953 | 37.04 | 38.7578 | 36.5025 | 37.9053 | 37.474 | 38.6272 | 36.5725 | 39.2447 | 37.1053 | 38.9626 | 39.4034 | 94.7715 | 95.2333 | 94.3918
2022-09-07 21:31 | 3:07 | 29.1149 | 30.9511 | 31.0969 | 36.0391 | 36.5329 | 34.1268 | 36.9662 | 33.4144 | 36.9371 | 35.2411 | 35.2677 | 38.3362 | 33.3866 | 34.5914 | 35.7818 | 34.0691 | 34.3246 | 34.7606 | 34.6498 | 37.0288 | 32.8738 | 31.5775 | 35.1086 | 36.5532 | 34.7039 | 38.927 | 36.5768 | 35.0984 | 34.5477 | 36.7097 | 34.5042 | 35.7299 | 34.5809 | 35.7836 | 34.6668 | 36.2544 | 35.6811 | 36.3524 | 37.481 | 35.6634 | 36.8 | 37.9145 | 39.0375 | 37.5155 | 38.5825 | 36.631 | 38.7322 | 37.1126 | 38.8413 | 36.6103 | 38.0056 | 37.5411 | 38.7506 | 36.5869 | 39.2498 | 37.1672 | 39.0297 | 39.4042 | 94.8947 | 95.3101 | 94.3661
2022-09-07 21:31 | 3:07 | 29.3876 | 31.1332 | 31.2252 | 36.169 | 36.5564 | 34.2425 | 36.9361 | 33.5462 | 37.0053 | 35.3327 | 35.3537 | 38.4366 | 33.4862 | 34.6347 | 35.7948 | 34.082 | 34.3999 | 34.7946 | 34.7007 | 37.1067 | 33.0211 | 31.5989 | 35.2584 | 36.585 | 34.7117 | 39.18 | 36.7093 | 35.2701 | 34.6437 | 36.6744 | 34.5941 | 35.8055 | 34.6267 | 35.8384 | 34.7116 | 36.3314 | 35.7631 | 36.3863 | 37.4442 | 35.6706 | 36.8116 | 37.9434 | 39.0598 | 37.6104 | 38.7269 | 36.6848 | 38.7591 | 37.2019 | 38.8965 | 36.6002 | 38.0353 | 37.615 | 38.6682 | 36.6507 | 39.283 | 37.2482 | 39.0302 | 39.4276 | 94.997 | 95.4905 | 94.4774
2022-09-07 21:31 | 3:07 | 29.6216 | 31.2591 | 31.2799 | 36.19 | 36.5775 | 34.3342 | 36.9596 | 33.5946 | 37.004 | 35.335 | 35.4665 | 38.4926 | 33.5085 | 34.6936 | 35.8302 | 34.1194 | 34.4325 | 34.8763 | 34.7377 | 37.1579 | 33.1663 | 31.6156 | 35.3918 | 36.6849 | 34.7976 | 39.1358 | 36.7528 | 35.3341 | 34.7015 | 36.762 | 34.6549 | 35.7467 | 34.6753 | 35.9172 | 34.8015 | 36.3328 | 35.7722 | 36.3945 | 37.5232 | 35.715 | 36.7442 | 38.0097 | 39.093 | 37.6494 | 38.6907 | 36.6921 | 38.8038 | 37.2655 | 38.9468 | 36.6287 | 38.0757 | 37.6577 | 38.7296 | 36.7145 | 39.3689 | 37.3075 | 39.1728 | 39.4222 | 95.0752 | 95.5617 | 94.5884
2022-09-07 21:32 | 3:07 | 29.8177 | 31.3673 | 31.3621 | 36.346 | 36.5675 | 34.3898 | 37.0295 | 33.6685 | 36.9894 | 35.4548 | 35.5457 | 38.5225 | 33.5995 | 34.7539 | 35.8946 | 34.1746 | 34.5029 | 34.9643 | 34.7629 | 37.175 | 33.3274 | 31.6298 | 35.5457 | 36.7061 | 34.879 | 39.0786 | 36.7588 | 35.3492 | 34.7123 | 36.7438 | 34.7421 | 35.818 | 34.7479 | 36.0022 | 34.8786 | 36.3723 | 35.7678 | 36.4894 | 37.6207 | 35.7877 | 36.8128 | 38.0842 | 39.1204 | 37.724 | 38.7914 | 36.8196 | 38.7854 | 37.3502 | 39.0078 | 36.7383 | 38.1564 | 37.7315 | 38.7128 | 36.6421 | 39.3943 | 37.3885 | 39.1764 | 39.4736 | 95.2249 | 95.6418 | 94.6064
2022-09-07 21:32 | 3:08 | 29.9913 | 31.3987 | 31.4423 | 36.4548 | 36.566 | 34.4042 | 37.0181 | 33.7878 | 37.0357 | 35.5073 | 35.6463 | 38.4612 | 33.6725 | 34.7682 | 36.0543 | 34.212 | 34.5902 | 34.9602 | 34.8211 | 37.1954 | 33.4791 | 31.6518 | 35.6845 | 36.739 | 34.9623 | 39.1144 | 36.8 | 35.4183 | 34.8509 | 36.8122 | 34.8082 | 35.7802 | 34.8507 | 36.0246 | 34.9407 | 36.3434 | 35.8227 | 36.4815 | 37.5447 | 35.8179 | 36.8548 | 38.1135 | 39.1786 | 37.8006 | 38.8536 | 36.8257 | 38.8638 | 37.3967 | 39.0715 | 36.7727 | 38.215 | 37.77 | 38.7636 | 36.7604 | 39.4605 | 37.4282 | 39.2735 | 39.525 | 95.2675 | 95.7083 | 94.5819
2022-09-07 21:32 | 3:08 | 30.6708 | 27.2121 | 31.2243 | 36.4483 | 36.6008 | 34.3878 | 36.9602 | 33.7557 | 37.0614 | 35.3992 | 35.5399 | 38.446 | 33.6698 | 34.8075 | 35.8885 | 34.2492 | 34.6358 | 35.0126 | 34.8438 | 37.3165 | 33.911 | 28.7867 | 35.2807 | 36.8259 | 34.944 | 39.2811 | 36.8116 | 35.3223 | 34.8639 | 36.8274 | 34.6851 | 35.8046 | 34.8849 | 36.0435 | 34.9182 | 36.3774 | 35.8945 | 36.5045 | 37.5813 | 35.8647 | 36.8391 | 38.0504 | 39.1081 | 37.6051 | 38.743 | 36.8674 | 38.829 | 37.2301 | 38.953 | 36.7469 | 38.0452 | 37.7297 | 38.8617 | 36.8005 | 39.5366 | 37.3435 | 39.1253 | 39.5995 | 95.1921 | 95.6027 | 94.5953
2022-09-07 21:32 | 3:08 | 31.5505 | 31.496 | 31.4877 | 36.3327 | 36.6282 | 34.47 | 37.1074 | 33.8153 | 37.099 | 35.5208 | 35.7272 | 38.4354 | 33.7744 | 34.8844 | 35.9682 | 34.2854 | 34.6746 | 35.0886 | 34.8939 | 37.2559 | 33.9078 | 30.9832 | 34.989 | 36.8655 | 34.9629 | 38.9912 | 36.7442 | 35.3058 | 34.8663 | 36.7436 | 34.735 | 35.9287 | 34.918 | 36.0736 | 34.9654 | 36.4012 | 35.9807 | 36.509 | 37.538 | 35.9204 | 36.9602 | 38.0071 | 39.1535 | 37.5336 | 38.6195 | 36.834 | 38.8918 | 37.1927 | 38.8783 | 36.6662 | 37.98 | 37.7324 | 38.7308 | 36.8145 | 39.4392 | 37.3443 | 39.0371 | 39.5303 | 94.9846 | 95.3484 | 94.3495
2022-09-07 21:32 | 3:08 | 33.0598 | 31.8397 | 31.6736 | 36.3988 | 36.6859 | 34.5661 | 37.1221 | 33.9424 | 37.1333 | 35.5893 | 35.8792 | 38.4665 | 33.8703 | 34.9356 | 36.1288 | 34.3385 | 34.7824 | 35.1217 | 34.9573 | 37.305 | 34.1263 | 31.4918 | 35.2043 | 36.9883 | 34.997 | 39.0609 | 36.8128 | 35.4018 | 34.8813 | 36.7974 | 34.8291 | 35.8325 | 35.02 | 36.1014 | 35.0312 | 36.4237 | 36.0441 | 36.5702 | 37.5955 | 35.9778 | 37.0694 | 38.1026 | 39.1499 | 37.6025 | 38.6831 | 36.8377 | 38.8726 | 37.2662 | 38.8935 | 36.752 | 38.0033 | 37.751 | 38.7693 | 36.8368 | 39.4738 | 37.4225 | 39.083 | 39.5997 | 94.7197 | 95.0756 | 94.1723
2022-09-07 21:32 | 3:08 | 34.1622 | 31.8359 | 31.9132 | 36.5087 | 36.6981 | 34.6643 | 37.2064 | 34.0702 | 37.1567 | 35.5833 | 35.8943 | 38.4381 | 33.9791 | 35.0005 | 36.2818 | 34.4139 | 34.8408 | 35.2155 | 35.0881 | 37.3131 | 34.5393 | 31.6528 | 35.4984 | 37.0008 | 35.0977 | 39.296 | 36.8548 | 35.3955 | 34.9536 | 36.9234 | 34.98 | 35.9224 | 35.1013 | 36.1583 | 35.102 | 36.4788 | 36.1778 | 36.6321 | 37.7036 | 36.0806 | 37.1676 | 38.136 | 39.1678 | 37.7132 | 38.7656 | 36.9475 | 38.9865 | 37.4078 | 38.9891 | 36.7984 | 38.1051 | 37.8414 | 38.8628 | 36.9442 | 39.5121 | 37.4883 | 39.1175 | 39.5895 | 94.5493 | 94.8827 | 94.1052
2022-09-07 21:33 | 3:09 | 34.9224 | 31.8563 | 32.3466 | 36.7307 | 36.7046 | 34.7518 | 37.1801 | 34.1599 | 37.219 | 35.7084 | 35.981 | 38.5387 | 34.0647 | 35.0933 | 36.2573 | 34.4867 | 34.9408 | 35.2657 | 35.1454 | 37.3635 | 35.0074 | 31.6932 | 35.8287 | 37.0824 | 35.1542 | 39.3164 | 36.8391 | 35.4031 | 35.0611 | 36.9622 | 35.1464 | 36.0695 | 35.2288 | 36.282 | 35.2401 | 36.5702 | 36.2031 | 36.7526 | 37.6863 | 36.1474 | 37.1964 | 38.2465 | 39.228 | 37.8471 | 38.8414 | 37.0064 | 38.9926 | 37.5057 | 39.1004 | 36.9152 | 38.2002 | 37.9001 | 38.9174 | 37.0007 | 39.5465 | 37.5817 | 39.1329 | 39.6312 | 94.3685 | 94.6942 | 93.9484
2022-09-07 21:33 | 3:09 | 35.4225 | 31.8467 | 32.8508 | 36.7496 | 36.7601 | 34.8773 | 37.2953 | 34.2562 | 37.2374 | 35.7968 | 36.0499 | 38.6306 | 34.1642 | 35.2129 | 36.2469 | 34.5556 | 35.0269 | 35.3779 | 35.2166 | 37.4183 | 35.2542 | 31.7035 | 36.0642 | 37.1754 | 35.2917 | 39.3025 | 36.9602 | 35.5869 | 35.1252 | 37.0448 | 35.2666 | 36.037 | 35.3023 | 36.3705 | 35.3239 | 36.5821 | 36.2732 | 36.8449 | 37.7636 | 36.2192 | 37.2371 | 38.2958 | 39.2803 | 37.9361 | 38.9438 | 37.0457 | 39.0727 | 37.6194 | 39.1624 | 37.0094 | 38.305 | 37.9665 | 38.9639 | 37.0925 | 39.6125 | 37.6782 | 39.1812 | 39.7786 | 94.2953 | 94.5673 | 93.8575
2022-09-07 21:33 | 3:09 | 35.4602 | 31.8593 | 33.1219 | 36.8106 | 36.8004 | 34.8888 | 37.2719 | 34.2675 | 37.2734 | 35.8328 | 36.1619 | 38.5892 | 34.2737 | 35.2739 | 36.343 | 34.6074 | 35.1033 | 35.413 | 35.2933 | 37.4982 | 35.3131 | 31.7405 | 36.1772 | 37.2837 | 35.3577 | 39.4057 | 37.0694 | 35.6947 | 35.2428 | 37.152 | 35.3803 | 36.1556 | 35.4302 | 36.5053 | 35.4107 | 36.6873 | 36.3564 | 36.9186 | 37.8189 | 36.3048 | 37.2387 | 38.3455 | 39.3651 | 38.0508 | 38.9567 | 37.1093 | 39.1235 | 37.7048 | 39.185 | 37.0972 | 38.362 | 38.0448 | 38.9851 | 37.2133 | 39.6655 | 37.727 | 39.3934 | 39.7374 | 94.2035 | 94.4621 | 93.8768
2022-09-07 21:33 | 3:09 | 35.4942 | 31.8678 | 33.2458 | 36.8459 | 36.8051 | 35.0218 | 37.3089 | 34.3641 | 37.3064 | 35.8503 | 36.0782 | 38.5982 | 34.3484 | 35.318 | 36.4392 | 34.6684 | 35.1616 | 35.4892 | 35.3714 | 37.538 | 35.3519 | 31.7638 | 36.2498 | 37.3771 | 35.4073 | 39.5138 | 37.1676 | 35.6448 | 35.2976 | 37.2762 | 35.4862 | 36.197 | 35.5045 | 36.5187 | 35.5245 | 36.7326 | 36.412 | 36.9523 | 37.8223 | 36.3461 | 37.3427 | 38.4386 | 39.4225 | 38.1686 | 39.0642 | 37.1673 | 39.1305 | 37.793 | 39.2387 | 37.1241 | 38.4365 | 38.1596 | 39.0564 | 37.2602 | 39.6573 | 37.8264 | 39.4001 | 39.8069 | 94.0987 | 94.4071 | 93.7827
2022-09-07 21:33 | 3:09 | 35.4995 | 31.8884 | 33.1972 | 36.9057 | 36.8804 | 35.0718 | 37.3515 | 34.4307 | 37.3011 | 35.9296 | 36.2433 | 38.6663 | 34.3975 | 35.3845 | 36.4893 | 34.7127 | 35.2448 | 35.5348 | 35.407 | 37.6657 | 35.3762 | 31.7863 | 36.3176 | 37.4428 | 35.4629 | 39.6374 | 37.1964 | 35.8306 | 35.2532 | 37.3143 | 35.5639 | 36.2218 | 35.5602 | 36.5915 | 35.6017 | 36.7472 | 36.4605 | 37.0358 | 37.889 | 36.4365 | 37.4693 | 38.4651 | 39.4527 | 38.2412 | 39.1216 | 37.2216 | 39.2191 | 37.8748 | 39.3286 | 37.2088 | 38.501 | 38.1828 | 39.0872 | 37.3212 | 39.7139 | 37.8503 | 39.4058 | 39.868 | 93.9985 | 94.2587 | 93.7377
2022-09-07 21:33 | 3:09 | 35.5343 | 31.8952 | 33.2405 | 37.0829 | 36.8629 | 35.14 | 37.4604 | 34.4681 | 37.3638 | 35.9882 | 36.1633 | 38.6206 | 34.4805 | 35.466 | 36.5342 | 34.7634 | 35.3476 | 35.6281 | 35.4908 | 37.6847 | 35.4037 | 31.8117 | 36.4204 | 37.4958 | 35.5695 | 39.6544 | 37.2371 | 35.7937 | 35.3567 | 37.3135 | 35.632 | 36.2276 | 35.6307 | 36.6617 | 35.6665 | 36.8148 | 36.5048 | 37.1011 | 37.8608 | 36.4829 | 37.5652 | 38.5679 | 39.5008 | 38.3161 | 39.2636 | 37.3182 | 39.2602 | 37.9462 | 39.3659 | 37.2988 | 38.555 | 38.2675 | 39.0388 | 37.3661 | 39.6774 | 37.9353 | 39.472 | 39.8693 | 93.9221 | 94.1682 | 93.7317
2022-09-07 21:34 | 3:09 | 35.8668 | 31.928 | 33.3925 | 36.9913 | 36.9064 | 35.1834 | 37.4425 | 34.5381 | 37.3923 | 36.1032 | 36.4141 | 38.6959 | 34.5519 | 35.4666 | 36.5714 | 34.8259 | 35.3752 | 35.6865 | 35.5432 | 37.7753 | 35.5862 | 31.8306 | 36.5476 | 37.6027 | 35.6666 | 39.6846 | 37.2387 | 35.8862 | 35.413 | 37.3701 | 35.7202 | 36.3443 | 35.743 | 36.6845 | 35.7212 | 36.8751 | 36.5739 | 37.122 | 37.992 | 36.546 | 37.5378 | 38.5719 | 39.5473 | 38.3842 | 39.3386 | 37.3594 | 39.2727 | 38.0131 | 39.4748 | 37.3803 | 38.6319 | 38.3356 | 39.1508 | 37.4133 | 39.7196 | 38.006 | 39.4941 | 39.9197 | 93.9242 | 94.1175 | 93.7389
2022-09-07 21:34 | 3:10 | 36.1607 | 31.9743 | 33.5962 | 37.1788 | 36.937 | 35.3069 | 37.4559 | 34.6426 | 37.4415 | 36.1772 | 36.3696 | 38.723 | 34.6108 | 35.5705 | 36.5847 | 34.8959 | 35.4238 | 35.7333 | 35.6157 | 37.7604 | 35.7595 | 31.8348 | 36.7172 | 37.6632 | 35.7172 | 39.7282 | 37.3427 | 35.9817 | 35.5848 | 37.4423 | 35.8138 | 36.4071 | 35.8395 | 36.7661 | 35.836 | 36.9174 | 36.6942 | 37.1761 | 38.0506 | 36.6081 | 37.5935 | 38.6543 | 39.6178 | 38.4798 | 39.3418 | 37.4019 | 39.3852 | 38.102 | 39.4977 | 37.4029 | 38.6648 | 38.4195 | 39.2632 | 37.4239 | 39.8227 | 38.0939 | 39.4825 | 39.9209 | 93.8375 | 94.0518 | 93.6245
2022-09-07 21:34 | 3:10 | 36.3168 | 31.9978 | 33.8006 | 37.3026 | 36.9513 | 35.3302 | 37.4164 | 34.7126 | 37.4726 | 36.2461 | 36.4104 | 38.7107 | 34.7114 | 35.626 | 36.7204 | 34.9892 | 35.5738 | 35.7988 | 35.7055 | 37.8799 | 35.9809 | 31.8563 | 36.8646 | 37.7346 | 35.7715 | 39.7042 | 37.4693 | 36.0229 | 35.7053 | 37.4405 | 35.9128 | 36.5101 | 35.8955 | 36.8286 | 35.9232 | 37.0011 | 36.719 | 37.2685 | 38.0645 | 36.6791 | 37.6841 | 38.7021 | 39.682 | 38.5452 | 39.429 | 37.4749 | 39.3865 | 38.1624 | 39.5935 | 37.4567 | 38.7551 | 38.4654 | 39.2507 | 37.5378 | 39.9126 | 38.1641 | 39.5952 | 39.9401 | 93.8276 | 94.0257 | 93.6505
2022-09-07 21:34 | 3:10 | 36.517 | 32.0372 | 33.9776 | 37.3012 | 37.0107 | 35.3542 | 37.56 | 34.8091 | 37.5091 | 36.2437 | 36.5025 | 38.7093 | 34.8416 | 35.7317 | 36.8102 | 35.0363 | 35.6448 | 35.9019 | 35.7737 | 37.9581 | 36.1901 | 31.9015 | 36.983 | 37.8157 | 35.8952 | 39.9069 | 37.5652 | 36.104 | 35.7349 | 37.6485 | 36.0211 | 36.5227 | 35.9833 | 36.956 | 36.02 | 37.0514 | 36.7831 | 37.3977 | 38.0453 | 36.7338 | 37.7823 | 38.7802 | 39.7373 | 38.6205 | 39.3804 | 37.4955 | 39.4359 | 38.2484 | 39.7043 | 37.5142 | 38.787 | 38.5229 | 39.2086 | 37.6565 | 39.8623 | 38.2367 | 39.6889 | 39.9501 | 93.7478 | 93.9734 | 93.5323
2022-09-07 21:34 | 3:10 | 36.6613 | 32.0858 | 34.1694 | 37.4372 | 37.0316 | 35.4924 | 37.6335 | 34.9049 | 37.5398 | 36.2924 | 36.5586 | 38.7066 | 34.9907 | 35.8238 | 36.7474 | 35.1187 | 35.7179 | 36.008 | 35.8737 | 38.0187 | 36.5229 | 32.149 | 37.1802 | 37.8858 | 35.9637 | 39.8417 | 37.5378 | 36.1488 | 35.884 | 37.5423 | 36.1529 | 36.612 | 36.105 | 36.9878 | 36.1298 | 37.1353 | 36.8392 | 37.4641 | 38.1664 | 36.8318 | 37.864 | 38.8479 | 39.7737 | 38.7301 | 39.4664 | 37.606 | 39.5004 | 38.3159 | 39.7533 | 37.5995 | 38.8351 | 38.5902 | 39.4663 | 37.7615 | 39.9016 | 38.2953 | 39.8006 | 40.0604 | 93.698 | 93.9163 | 93.5621
2022-09-07 21:34 | 3:10 | 36.8847 | 32.1321 | 34.3546 | 37.5672 | 37.0703 | 35.685 | 37.5928 | 35.0055 | 37.5747 | 36.327 | 36.5994 | 38.7874 | 35.0962 | 35.9452 | 36.8761 | 35.1798 | 35.8022 | 36.1017 | 35.8827 | 38.1463 | 36.9459 | 34.0797 | 37.405 | 38.0393 | 36.0363 | 39.9754 | 37.5935 | 36.2584 | 35.9371 | 37.6753 | 36.2588 | 36.6215 | 36.1711 | 37.0655 | 36.2146 | 37.2132 | 36.8764 | 37.5256 | 38.1617 | 36.898 | 37.8537 | 38.9091 | 39.8101 | 38.8057 | 39.5085 | 37.682 | 39.516 | 38.4325 | 39.7832 | 37.7115 | 38.9086 | 38.6472 | 39.4356 | 37.7475 | 39.9916 | 38.3644 | 39.8119 | 40.0726 | 93.6463 | 93.8699 | 93.4626
2022-09-07 21:35 | 3:11 | 37.1033 | 32.1913 | 34.5389 | 37.6508 | 37.1284 | 35.7808 | 37.6652 | 35.1384 | 37.6502 | 36.5259 | 36.7277 | 38.872 | 35.2091 | 36.0694 | 37.0945 | 35.2756 | 35.9836 | 36.2026 | 35.9821 | 38.0888 | 37.292 | 35.2455 | 37.622 | 38.0725 | 36.1607 | 39.9524 | 37.6841 | 36.3121 | 35.9964 | 37.7848 | 36.3765 | 36.6921 | 36.2819 | 37.1387 | 36.2925 | 37.2654 | 36.973 | 37.579 | 38.2509 | 36.9815 | 37.9456 | 38.9499 | 39.8896 | 38.9176 | 39.6061 | 37.685 | 39.5803 | 38.5063 | 39.8526 | 37.7641 | 38.9948 | 38.7282 | 39.4558 | 37.7967 | 39.9985 | 38.4513 | 39.8165 | 40.0765 | 93.6388 | 93.7936 | 93.5037
2022-09-07 21:35 | 3:11 | 37.2931 | 32.3337 | 34.7183 | 37.8351 | 37.1688 | 35.8881 | 37.7388 | 35.2341 | 37.6909 | 36.6363 | 36.8003 | 38.8464 | 35.3243 | 36.1665 | 37.1442 | 35.3341 | 36.0491 | 36.2762 | 36.0695 | 38.2129 | 37.5746 | 36.303 | 37.8185 | 38.1447 | 36.2601 | 40.0227 | 37.7823 | 36.3448 | 36.0829 | 37.8444 | 36.4946 | 36.761 | 36.3626 | 37.2732 | 36.3699 | 37.3103 | 37.0439 | 37.6435 | 38.2579 | 37.0429 | 38.0909 | 39.0337 | 39.9204 | 38.9944 | 39.6706 | 37.7656 | 39.6646 | 38.5938 | 39.9211 | 37.8597 | 39.0954 | 38.7808 | 39.5727 | 37.8929 | 40.0655 | 38.5158 | 39.8408 | 40.1525 | 93.5379 | 93.6818 | 93.4246
2022-09-07 21:35 | 3:11 | 37.4841 | 32.4964 | 34.8431 | 37.8921 | 37.2291 | 36.0293 | 37.7504 | 35.383 | 37.7313 | 36.6475 | 36.9299 | 38.8572 | 35.4455 | 36.1958 | 37.1537 | 35.412 | 36.088 | 36.3257 | 36.167 | 38.3642 | 37.7963 | 37.0041 | 37.9653 | 38.2518 | 36.3466 | 40.1014 | 37.864 | 36.4575 | 36.1424 | 38.0087 | 36.597 | 36.8897 | 36.4748 | 37.3092 | 36.5242 | 37.3624 | 37.1162 | 37.7295 | 38.3292 | 37.0974 | 38.1591 | 39.1256 | 39.9858 | 39.0908 | 39.7094 | 37.8559 | 39.6939 | 38.658 | 39.9271 | 37.8827 | 39.1427 | 38.8535 | 39.6463 | 37.9963 | 40.096 | 38.5817 | 40.0199 | 40.2156 | 93.4458 | 93.6298 | 93.4174
2022-09-07 21:35 | 3:11 | 37.6907 | 32.6826 | 35.008 | 38.1885 | 37.2905 | 36.0716 | 37.8995 | 35.511 | 37.7855 | 36.7263 | 37.0189 | 38.8602 | 35.547 | 36.2732 | 37.2336 | 35.5041 | 36.1864 | 36.4318 | 36.2527 | 38.3997 | 37.943 | 37.3063 | 38.1486 | 38.3697 | 36.4698 | 40.2234 | 37.8537 | 36.5539 | 36.3314 | 38.0303 | 36.7017 | 36.9595 | 36.5568 | 37.3889 | 36.5822 | 37.4674 | 37.1738 | 37.8481 | 38.3506 | 37.1964 | 38.152 | 39.2036 | 40.0163 | 39.1557 | 39.7403 | 37.8873 | 39.7679 | 38.7419 | 40.0519 | 37.9138 | 39.2276 | 38.8984 | 39.6698 | 38.031 | 40.1103 | 38.6446 | 39.9972 | 40.4139 | 93.3242 | 93.5124 | 93.3489
2022-09-07 21:35 | 3:11 | 37.9207 | 32.8807 | 35.2169 | 38.1178 | 37.3616 | 36.1681 | 37.8993 | 35.619 | 37.8478 | 36.8611 | 37.1476 | 38.9364 | 35.6661 | 36.4007 | 37.2667 | 35.5769 | 36.3219 | 36.5209 | 36.3471 | 38.4968 | 38.1859 | 37.5493 | 38.3028 | 38.3942 | 36.5184 | 40.4013 | 37.9456 | 36.5957 | 36.384 | 38.1173 | 36.7963 | 36.955 | 36.6496 | 37.4867 | 36.7065 | 37.5029 | 37.2551 | 37.8566 | 38.4027 | 37.2661 | 38.2438 | 39.2225 | 40.0493 | 39.2324 | 39.8984 | 37.9507 | 39.8141 | 38.8278 | 40.1337 | 38.0148 | 39.243 | 39.0079 | 39.8017 | 38.1352 | 40.1638 | 38.7252 | 40.0336 | 40.4384 | 93.2134 | 93.3272 | 93.298
2022-09-07 21:35 | 3:11 | 38.1286 | 33.0521 | 35.5085 | 38.2148 | 37.4136 | 36.3098 | 38.0894 | 35.751 | 37.8969 | 36.9625 | 37.1587 | 38.9673 | 35.7776 | 36.4974 | 37.4353 | 35.6584 | 36.3604 | 36.6294 | 36.4149 | 38.5122 | 38.3583 | 37.8148 | 38.4517 | 38.4572 | 36.6395 | 40.4471 | 38.0909 | 36.6941 | 36.4154 | 38.1475 | 36.9083 | 37.1032 | 36.7604 | 37.5622 | 36.8169 | 37.6269 | 37.3478 | 37.9277 | 38.4315 | 37.3498 | 38.3157 | 39.2956 | 40.1034 | 39.3026 | 39.9877 | 38.0071 | 39.8708 | 38.8966 | 40.1795 | 38.0723 | 39.3172 | 39.0537 | 39.8012 | 38.2101 | 40.1348 | 38.7835 | 40.1367 | 40.4299 | 93.1386 | 93.1339 | 93.1954
2022-09-07 21:36 | 3:11 | 38.1614 | 33.2468 | 35.5576 | 38.3403 | 37.4464 | 36.4274 | 38.076 | 35.8615 | 37.9436 | 37.0589 | 37.2792 | 39.0325 | 35.9041 | 36.5984 | 37.6323 | 35.7684 | 36.5431 | 36.7205 | 36.5108 | 38.6554 | 38.4751 | 37.9315 | 38.6032 | 38.6298 | 36.7671 | 40.4009 | 38.1591 | 36.7084 | 36.4995 | 38.2585 | 37.0254 | 37.111 | 36.8637 | 37.696 | 36.9402 | 37.638 | 37.4199 | 38.0689 | 38.5764 | 37.4211 | 38.2669 | 39.4065 | 40.16 | 39.4072 | 39.9438 | 38.0889 | 39.9373 | 38.9713 | 40.2026 | 38.1575 | 39.4118 | 39.1208 | 39.7763 | 38.3547 | 40.3074 | 38.8729 | 40.1517 | 40.5165 | 93.0204 | 92.9904 | 93.1478
2022-09-07 21:36 | 3:12 | 38.255 | 33.5935 | 35.6264 | 38.5095 | 37.5088 | 36.5264 | 38.1144 | 35.9453 | 38.0043 | 37.1272 | 37.3376 | 39.0414 | 36.0212 | 36.6523 | 37.6796 | 35.8357 | 36.6058 | 36.8094 | 36.602 | 38.6388 | 38.6441 | 38.088 | 38.7103 | 38.7243 | 36.8119 | 40.503 | 38.152 | 36.8259 | 36.6728 | 38.2873 | 37.1208 | 37.1355 | 36.9216 | 37.7426 | 37.0655 | 37.6767 | 37.4965 | 38.1069 | 38.5752 | 37.5132 | 38.1709 | 39.4471 | 40.2576 | 39.4947 | 39.9678 | 38.1659 | 39.9971 | 39.0703 | 40.2973 | 38.2564 | 39.4348 | 39.2239 | 39.8914 | 38.3725 | 40.2472 | 38.9321 | 40.2388 | 40.4968 | 92.8687 | 92.9331 | 93.0462
2022-09-07 21:36 | 3:12 | 38.3586 | 34.0858 | 35.7957 | 38.6391 | 37.5582 | 36.6146 | 38.0297 | 36.0374 | 38.0592 | 37.1837 | 37.414 | 39.1578 | 36.1229 | 36.7513 | 37.6181 | 35.9357 | 36.698 | 36.8934 | 36.6971 | 38.7591 | 38.7905 | 38.2437 | 38.8425 | 38.8262 | 36.9733 | 40.5314 | 38.2438 | 36.8719 | 36.8064 | 38.295 | 37.1751 | 37.2548 | 37.0304 | 37.8379 | 37.1252 | 37.7987 | 37.5847 | 38.1855 | 38.6628 | 37.5876 | 37.9424 | 39.5272 | 40.303 | 39.5644 | 40.0797 | 38.1795 | 40.0625 | 39.1317 | 40.3248 | 38.3049 | 39.5067 | 39.2595 | 39.9223 | 38.5305 | 40.3729 | 39.0024 | 40.3389 | 40.5471 | 92.6425 | 92.8414 | 92.8571
2022-09-07 21:36 | 3:12 | 37.581 | 34.4652 | 35.9472 | 38.7394 | 37.6216 | 36.6921 | 38.2352 | 36.1566 | 38.1118 | 37.3255 | 37.4938 | 39.064 | 36.2485 | 36.874 | 37.7349 | 36.0358 | 36.7969 | 37.0104 | 36.7552 | 38.8464 | 37.8665 | 37.7319 | 38.6614 | 38.8736 | 37.0367 | 40.5173 | 38.3157 | 36.9764 | 36.9201 | 38.4914 | 37.2264 | 37.2977 | 37.1204 | 37.9319 | 37.2279 | 37.7964 | 37.6304 | 38.3052 | 38.7255 | 37.6697 | 37.7469 | 39.57 | 40.319 | 39.6255 | 40.1564 | 38.3025 | 40.1425 | 39.1968 | 40.3976 | 38.3818 | 39.5462 | 39.3341 | 39.9885 | 38.5341 | 40.3958 | 39.0833 | 40.4043 | 40.6492 | 92.514 | 92.6527 | 92.7666
2022-09-07 21:36 | 3:12 | 33.244 | 32.9235 | 34.9793 | 38.698 | 37.6885 | 36.766 | 38.293 | 36.2109 | 38.1743 | 37.3405 | 37.539 | 39.103 | 36.2416 | 36.8384 | 37.7878 | 36.0843 | 36.8492 | 36.9504 | 36.7699 | 38.911 | 35.3577 | 34.8545 | 37.6422 | 38.8539 | 36.9618 | 40.342 | 38.2669 | 36.9941 | 36.8318 | 38.3847 | 36.9208 | 37.4185 | 37.047 | 37.8693 | 37.1577 | 37.8366 | 37.6343 | 38.2919 | 38.7261 | 37.6705 | 37.644 | 39.5221 | 40.2632 | 39.4665 | 39.9804 | 38.3209 | 40.0984 | 38.9919 | 40.2715 | 38.2846 | 39.3758 | 39.2446 | 39.9184 | 38.532 | 40.3724 | 38.9725 | 40.2163 | 40.6278 | 92.4217 | 92.5012 | 92.7692
2022-09-07 21:36 | 3:12 | 29.2614 | 30.3187 | 32.4608 | 38.3892 | 37.6962 | 36.4351 | 38.2407 | 35.9446 | 38.1709 | 37.2281 | 37.4361 | 39.2756 | 35.9524 | 36.6226 | 37.6625 | 35.9895 | 36.7489 | 36.6508 | 36.5956 | 38.68 | 34.6389 | 29.8408 | 36.0677 | 38.7393 | 36.8105 | 40.2796 | 38.1709 | 36.7899 | 36.6482 | 38.0936 | 36.352 | 37.2951 | 36.8301 | 37.6538 | 36.9344 | 37.7074 | 37.5912 | 38.096 | 38.6795 | 37.6001 | 37.6052 | 39.4009 | 40.112 | 39.0616 | 39.8417 | 38.2096 | 39.9549 | 38.6213 | 40.0795 | 38.0584 | 39.1144 | 39.0439 | 39.8526 | 38.4186 | 40.3297 | 38.6654 | 40.0262 | 40.6936 | 92.2314 | 92.3295 | 92.6919
2022-09-07 21:37 | 3:13 | 29.7316 | 29.8078 | 31.7583 | 37.8729 | 37.7411 | 36.1663 | 38.0923 | 35.8314 | 38.2063 | 36.9978 | 37.4956 | 39.3296 | 35.705 | 36.4121 | 37.5607 | 35.8857 | 36.5352 | 36.4175 | 36.4753 | 38.618 | 32.4847 | 28.5452 | 33.8725 | 38.5432 | 36.5355 | 39.9204 | 37.9424 | 36.7306 | 36.3312 | 37.7588 | 35.711 | 37.2668 | 36.6256 | 37.3745 | 36.6486 | 37.56 | 37.5386 | 37.9098 | 38.5161 | 37.4345 | 37.5589 | 39.1348 | 39.8413 | 38.5153 | 39.4125 | 38.0862 | 39.7763 | 38.2135 | 39.7932 | 37.6984 | 38.7141 | 38.89 | 39.6624 | 38.1617 | 40.0761 | 38.428 | 39.7671 | 40.5289 | 92.1836 | 92.2617 | 92.6133
2022-09-07 21:37 | 3:13 | 30.7047 | 30.0782 | 31.8097 | 37.7269 | 37.7946 | 36.0662 | 38.1992 | 35.7504 | 38.2076 | 36.9467 | 37.5436 | 39.2716 | 35.5782 | 36.348 | 37.6271 | 35.8474 | 36.4662 | 36.3693 | 36.4028 | 38.4679 | 27.6043 | 27.7541 | 32.6073 | 38.2238 | 36.4008 | 39.5602 | 37.7469 | 36.5169 | 36.1632 | 37.6155 | 35.3009 | 37.192 | 36.5013 | 37.1052 | 36.4333 | 37.4761 | 37.4403 | 37.6979 | 38.3895 | 37.3327 | 37.4969 | 38.9556 | 39.7106 | 38.1857 | 39.1623 | 37.9183 | 39.6942 | 37.9294 | 39.4897 | 37.5283 | 38.6961 | 38.7226 | 39.482 | 37.9943 | 40.0612 | 38.2263 | 39.5916 | 40.4645 | 92.0177 | 92.0783 | 92.482
2022-09-07 21:37 | 3:13 | 31.229 | 29.9874 | 32.0729 | 37.6469 | 37.8849 | 36.1052 | 38.2025 | 35.7464 | 38.2478 | 36.8932 | 37.5236 | 39.3176 | 35.5805 | 36.4275 | 37.4926 | 35.8589 | 36.4223 | 36.4337 | 36.4377 | 38.382 | 26.6899 | 27.1913 | 31.967 | 38.0518 | 36.3703 | 39.3877 | 37.644 | 36.6413 | 36.0784 | 37.5581 | 35.1179 | 37.2689 | 36.4761 | 37.0034 | 36.3367 | 37.3175 | 37.4046 | 37.6264 | 38.3554 | 37.2943 | 37.4611 | 38.819 | 39.5887 | 38.0316 | 38.9963 | 37.9272 | 39.6219 | 37.6784 | 39.3383 | 37.5133 | 38.5174 | 38.5947 | 39.5243 | 37.9517 | 40.0629 | 38.1587 | 39.4488 | 40.4884 | 91.9076 | 91.9402 | 92.405
2022-09-07 21:37 | 3:13 | 31.4646 | 29.8313 | 32.2167 | 37.6068 | 37.9954 | 36.1677 | 38.3056 | 35.7035 | 38.2865 | 36.9292 | 37.5959 | 39.2908 | 35.5959 | 36.4427 | 37.4837 | 35.8733 | 36.4827 | 36.4545 | 36.4655 | 38.2426 | 26.2537 | 26.7434 | 31.5177 | 37.9234 | 36.2962 | 39.2829 | 37.6052 | 36.6665 | 36.0275 | 37.4763 | 34.8598 | 37.1096 | 36.4777 | 36.9314 | 36.1737 | 37.2925 | 37.4629 | 37.6152 | 38.4396 | 37.3263 | 37.4172 | 38.7498 | 39.5885 | 37.895 | 39.0254 | 37.8847 | 39.5024 | 37.5452 | 39.2011 | 37.4196 | 38.4492 | 38.48 | 39.4832 | 38.0024 | 40.0997 | 38.0863 | 39.457 | 40.5305 | 91.9094 | 91.8641 | 92.3192
2022-09-07 21:37 | 3:13 | 31.519 | 29.5418 | 32.1466 | 37.5371 | 38.0772 | 36.0553 | 38.3376 | 35.6925 | 38.322 | 36.9275 | 37.5848 | 39.3551 | 35.6179 | 36.4349 | 37.6904 | 35.8783 | 36.4686 | 36.4171 | 36.5043 | 38.3115 | 25.9273 | 26.2906 | 31.2021 | 37.8592 | 36.2638 | 39.2744 | 37.5589 | 36.6296 | 36.0493 | 37.4602 | 34.6835 | 37.0766 | 36.4748 | 36.8601 | 36.1004 | 37.2768 | 37.4152 | 37.5132 | 38.3405 | 37.2156 | 37.3458 | 38.6597 | 39.4267 | 37.7249 | 38.8861 | 37.9061 | 39.509 | 37.4587 | 39.2023 | 37.362 | 38.515 | 38.4867 | 39.4652 | 37.9504 | 39.9963 | 37.9964 | 39.3199 | 40.4685 | 91.9301 | 91.9124 | 92.4299
2022-09-07 21:37 | 3:13 | 31.4007 | 28.787 | 31.9363 | 37.6752 | 38.144 | 36.1061 | 38.3471 | 35.6979 | 38.3388 | 36.9527 | 37.5554 | 39.3914 | 35.5345 | 36.3997 | 37.5724 | 35.9211 | 36.4348 | 36.3433 | 36.5201 | 38.3463 | 25.735 | 25.9053 | 30.9286 | 37.7356 | 36.2241 | 39.2309 | 37.4969 | 36.511 | 36.0119 | 37.4074 | 34.49 | 37.1632 | 36.4367 | 36.7572 | 35.9302 | 37.2672 | 37.3578 | 37.4467 | 38.4139 | 37.1659 | 37.3567 | 38.6268 | 39.4049 | 37.7045 | 38.7857 | 37.8488 | 39.4401 | 37.3591 | 39.0904 | 37.2834 | 38.5736 | 38.3708 | 39.3931 | 37.953 | 39.8858 | 37.883 | 39.2698 | 40.4814 | 91.9492 | 91.9705 | 92.5255
2022-09-07 21:38 | 3:14 | 31.2313 | 28.3541 | 31.6418 | 37.571 | 38.2114 | 36.1751 | 38.3479 | 35.6852 | 38.3721 | 36.8391 | 37.4688 | 39.3706 | 35.4012 | 36.3597 | 37.4619 | 35.9173 | 36.4173 | 36.3278 | 36.5153 | 38.3539 | 25.6779 | 25.5492 | 30.7414 | 37.6988 | 36.16 | 39.1858 | 37.4611 | 36.6189 | 36.0226 | 37.3932 | 34.4739 | 37.1082 | 36.3826 | 36.7162 | 35.9369 | 37.2295 | 37.3404 | 37.4046 | 38.4219 | 37.112 | 37.295 | 38.5639 | 39.3886 | 37.5029 | 38.7237 | 37.8458 | 39.3672 | 37.2438 | 39.097 | 37.2074 | 38.5971 | 38.3458 | 39.2649 | 37.9066 | 39.7944 | 37.797 | 39.1818 | 40.4143 | 92.022 | 92.0331 | 92.4834
2022-09-07 21:38 | 3:14 | 31.1005 | 28.2312 | 31.4178 | 37.3964 | 38.2717 | 36.0307 | 38.3683 | 35.6007 | 38.4091 | 36.8606 | 37.5964 | 39.5129 | 35.371 | 36.3113 | 37.5015 | 35.9499 | 36.4132 | 36.3997 | 36.5282 | 38.2413 | 25.9847 | 25.4034 | 30.5458 | 37.6185 | 36.0986 | 39.0584 | 37.4172 | 36.661 | 36.004 | 37.3591 | 34.3997 | 37.0882 | 36.3604 | 36.6929 | 35.8059 | 37.1551 | 37.281 | 37.432 | 38.481 | 37.0751 | 37.2494 | 38.5144 | 39.3784 | 37.4639 | 38.573 | 37.8482 | 39.4083 | 37.1742 | 39.0303 | 37.2002 | 38.4813 | 38.1929 | 39.3634 | 37.7951 | 39.8284 | 37.78 | 39.0748 | 40.3817 | 91.9933 | 92.1604 | 92.5438
2022-09-07 21:38 | 3:14 | 31.0134 | 28.1025 | 31.2559 | 37.2513 | 38.3348 | 35.915 | 38.3927 | 35.6206 | 38.4587 | 36.8921 | 37.622 | 39.5397 | 35.3173 | 36.334 | 37.5508 | 35.962 | 36.3455 | 36.346 | 36.5566 | 38.2366 | 26.1439 | 25.2475 | 30.4001 | 37.3849 | 36.0627 | 39.123 | 37.3458 | 36.5109 | 35.9887 | 37.2578 | 34.2191 | 37.1328 | 36.3157 | 36.6784 | 35.7584 | 37.2448 | 37.3579 | 37.4156 | 38.3394 | 37.0919 | 37.1789 | 38.4727 | 39.3063 | 37.353 | 38.5966 | 37.8056 | 39.3186 | 37.0822 | 39.0695 | 37.1254 | 38.5369 | 38.046 | 39.283 | 37.9626 | 39.8898 | 37.6512 | 39.106 | 40.2763 | 92.1475 | 92.2053 | 92.6419
2022-09-07 21:38 | 3:14 | 30.8327 | 28.0162 | 31.0417 | 37.2386 | 38.4072 | 35.9424 | 38.361 | 35.5325 | 38.4877 | 36.7839 | 37.6417 | 39.5489 | 35.2529 | 36.2898 | 37.5502 | 35.9834 | 36.2966 | 36.302 | 36.5798 | 38.1757 | 25.82 | 25.1914 | 30.2859 | 37.3867 | 36.0614 | 39.0005 | 37.3567 | 36.4841 | 35.934 | 37.2844 | 34.2792 | 37.0839 | 36.3845 | 36.5577 | 35.6702 | 37.0784 | 37.3307 | 37.2964 | 38.3674 | 37.0504 | 37.1651 | 38.4347 | 39.2756 | 37.3259 | 38.4904 | 37.7458 | 39.3093 | 37.0017 | 38.9037 | 37.08 | 38.4209 | 38.054 | 39.2748 | 37.8409 | 39.7842 | 37.5743 | 39.0412 | 40.4046 | 92.3074 | 92.3389 | 92.7588
2022-09-07 21:38 | 3:14 | 30.5761 | 27.9314 | 30.7664 | 37.2617 | 38.4862 | 35.7978 | 38.3824 | 35.5734 | 38.5183 | 36.7039 | 37.6025 | 39.8014 | 35.2951 | 36.2968 | 37.6028 | 35.9901 | 36.2898 | 36.2716 | 36.6506 | 38.1635 | 25.5696 | 24.9405 | 30.1309 | 37.362 | 35.9823 | 38.9816 | 37.295 | 36.4759 | 35.9439 | 37.1936 | 34.0823 | 37.146 | 36.3122 | 36.4964 | 35.5119 | 37.2059 | 37.1824 | 37.3042 | 38.3803 | 37.0038 | 37.1439 | 38.354 | 39.2114 | 37.2368 | 38.5804 | 37.7259 | 39.3378 | 36.8906 | 38.9145 | 37.0225 | 38.5039 | 37.9729 | 39.2919 | 37.8283 | 39.6466 | 37.5461 | 38.9869 | 40.3795 | 92.5201 | 92.4624 | 92.808
2022-09-07 21:38 | 3:14 | 30.2301 | 27.7692 | 30.4118 | 37.271 | 38.5375 | 35.6876 | 38.3416 | 35.5878 | 38.5463 | 36.7242 | 37.7515 | 39.6452 | 35.2713 | 36.2068 | 37.5097 | 35.9981 | 36.2307 | 36.2217 | 36.5673 | 38.2144 | 25.4615 | 24.7253 | 30.0362 | 37.2841 | 35.9336 | 38.9698 | 37.2494 | 36.461 | 35.9595 | 37.2032 | 33.9615 | 37.2509 | 36.3424 | 36.4998 | 35.6046 | 37.1457 | 37.199 | 37.2563 | 38.3266 | 36.9459 | 37.1029 | 38.3468 | 39.2097 | 37.1243 | 38.5499 | 37.6471 | 39.2689 | 36.7591 | 38.7447 | 37.0577 | 38.3069 | 37.9184 | 39.1328 | 37.779 | 39.6839 | 37.4652 | 38.8916 | 40.407 | 92.5767 | 92.5257 | 92.8334
2022-09-07 21:39 | 3:14 | 29.1336 | 27.5326 | 29.8277 | 37.0488 | 38.58 | 35.66 | 38.4127 | 35.5534 | 38.5378 | 36.6713 | 37.5014 | 39.5742 | 35.1873 | 36.16 | 37.5819 | 36.0027 | 36.1863 | 36.1101 | 36.5849 | 38.096 | 25.5053 | 24.5474 | 29.9576 | 37.1966 | 35.8948 | 38.8693 | 37.1789 | 36.6583 | 35.9266 | 37.145 | 33.8679 | 37.2496 | 36.2119 | 36.3743 | 35.3923 | 37.1895 | 37.1385 | 37.2312 | 38.3175 | 36.8967 | 36.9914 | 38.2176 | 39.0909 | 37.001 | 38.3933 | 37.6499 | 39.2769 | 36.6437 | 38.7876 | 36.9851 | 38.2585 | 37.8259 | 39.0597 | 37.652 | 39.5291 | 37.4029 | 38.7971 | 40.313 | 92.6493 | 92.631 | 92.881
2022-09-07 21:39 | 3:15 | 26.7721 | 27.391 | 29.3519 | 36.9572 | 38.599 | 35.6953 | 38.4048 | 35.5703 | 38.5752 | 36.6627 | 37.5252 | 39.6018 | 35.1245 | 36.0837 | 37.4953 | 35.9949 | 36.1307 | 36.1012 | 36.5227 | 38.2483 | 25.6586 | 24.3383 | 29.8109 | 37.1212 | 35.8408 | 38.7514 | 37.1651 | 36.6821 | 35.8478 | 37.0904 | 33.8362 | 37.2112 | 36.1627 | 36.3191 | 35.3471 | 37.0398 | 37.229 | 37.1683 | 38.1459 | 36.908 | 37.0117 | 38.0954 | 39.0754 | 36.9642 | 38.2382 | 37.5856 | 39.202 | 36.5471 | 38.7537 | 36.8454 | 38.3895 | 37.801 | 39.0701 | 37.6022 | 39.6851 | 37.3328 | 38.8063 | 40.2891 | 92.677 | 92.8143 | 92.9282
2022-09-07 21:39 | 3:15 | 25.4513 | 27.0763 | 28.9071 | 36.9506 | 38.6358 | 35.6755 | 38.3621 | 35.4393 | 38.5677 | 36.7451 | 37.1888 | 39.6841 | 35.1045 | 36.1992 | 37.4773 | 35.9833 | 36.0903 | 36.121 | 36.4569 | 38.1302 | 25.7408 | 24.1851 | 29.6441 | 37.0242 | 35.7837 | 38.7168 | 37.1439 | 36.3926 | 35.844 | 37.0193 | 33.7597 | 37.0667 | 36.0525 | 36.2339 | 35.271 | 37.0623 | 37.2099 | 37.0986 | 38.2736 | 36.8508 | 36.8876 | 38.0698 | 39.1315 | 36.9119 | 38.2442 | 37.5396 | 39.1387 | 36.4723 | 38.7453 | 36.815 | 38.7162 | 37.6444 | 38.9616 | 37.4258 | 39.227 | 37.2666 | 38.736 | 40.3907 | 92.8239 | 92.9265 | 93.0704
2022-09-07 21:39 | 3:15 | 25.0681 | 26.8112 | 28.5791 | 36.8201 | 38.6468 | 35.5503 | 38.3651 | 35.4149 | 38.5648 | 36.5957 | 37.3359 | 39.5954 | 34.9827 | 36.0866 | 37.4361 | 35.9852 | 36.0123 | 35.9758 | 36.4288 | 38.003 | 25.7114 | 24.0333 | 29.5147 | 36.9595 | 35.699 | 38.6694 | 37.1029 | 36.3091 | 35.8148 | 36.905 | 33.6251 | 36.9804 | 35.9966 | 36.1737 | 35.2234 | 36.9159 | 37.2264 | 36.9536 | 38.2833 | 36.8434 | 36.7659 | 38.0354 | 38.971 | 36.8786 | 38.2022 | 37.486 | 39.2131 | 36.3815 | 38.6807 | 36.761 | 38.5065 | 37.6339 | 39.0267 | 37.4337 | 39.4805 | 37.1657 | 38.7737 | 40.2601 | 92.9078 | 93.0029 | 93.0223
2022-09-07 21:39 | 3:15 | 24.8364 | 26.4634 | 28.2838 | 36.6931 | 38.6544 | 35.5322 | 38.3447 | 35.3294 | 38.5718 | 36.6734 | 37.1868 | 39.6624 | 34.9487 | 35.9818 | 37.229 | 35.9616 | 35.9897 | 35.9478 | 36.366 | 37.9323 | 25.5937 | 23.8743 | 29.3489 | 36.806 | 35.6211 | 38.73 | 36.9914 | 36.261 | 35.7734 | 36.905 | 33.4505 | 36.9693 | 35.856 | 36.0823 | 35.149 | 36.9023 | 36.9927 | 36.9753 | 38.2192 | 36.7637 | 36.7625 | 37.9635 | 38.9593 | 36.7988 | 38.1312 | 37.4458 | 39.0938 | 36.3239 | 38.6268 | 36.6417 | 38.7974 | 37.5627 | 38.8537 | 37.427 | 39.5174 | 37.1047 | 38.6475 | 40.2898 | 93.0812 | 93.0907 | 93.1342
2022-09-07 21:39 | 3:15 | 24.6206 | 26.3098 | 28.0721 | 36.7366 | 38.6581 | 35.6858 | 38.3974 | 35.3083 | 38.5757 | 36.6491 | 37.1312 | 39.6305 | 34.8695 | 35.9391 | 37.1943 | 35.9478 | 35.9128 | 35.8756 | 36.3394 | 38.0653 | 25.5114 | 23.7533 | 29.2376 | 36.6758 | 35.537 | 38.6636 | 37.0117 | 36.4688 | 35.7214 | 36.8872 | 33.4684 | 37.0581 | 35.8685 | 36.0813 | 34.8772 | 36.9078 | 36.8349 | 37.0769 | 38.1381 | 36.5834 | 36.7239 | 37.9104 | 38.9112 | 36.6464 | 38.0227 | 37.3847 | 39.1415 | 36.144 | 38.5502 | 36.6339 | 38.2844 | 37.4308 | 39.0679 | 37.3413 | 39.5019 | 37.0364 | 38.5958 | 40.5579 | 93.2529 | 93.2034 | 93.2531
2022-09-07 21:40 | 3:16 | 24.4159 | 26.0287 | 27.8789 | 36.5199 | 38.6695 | 35.4213 | 38.3662 | 35.2398 | 38.5669 | 36.5627 | 37.2826 | 39.5996 | 34.7987 | 35.9135 | 37.448 | 35.9246 | 35.8483 | 35.7662 | 36.3098 | 38.04 | 25.3113 | 23.6592 | 29.0245 | 36.6969 | 35.4927 | 38.6167 | 36.8876 | 36.2769 | 35.6604 | 36.756 | 33.3294 | 36.9891 | 35.8337 | 35.9826 | 34.8198 | 36.9153 | 36.9443 | 36.8643 | 38.1404 | 36.6253 | 36.6941 | 37.8031 | 38.9567 | 36.6797 | 37.9628 | 37.311 | 39.0376 | 36.0409 | 38.4295 | 36.5368 | 38.3559 | 37.3587 | 38.7865 | 37.3648 | 39.3513 | 36.9233 | 38.6893 | 40.2294 | 93.2594 | 93.3315 | 93.1557
2022-09-07 21:40 | 3:16 | 24.2487 | 25.8136 | 27.6682 | 36.3944 | 38.677 | 35.4228 | 38.3551 | 35.134 | 38.5629 | 36.4781 | 37.1228 | 39.4868 | 34.7705 | 35.7297 | 37.3094 | 35.8605 | 35.7836 | 35.7855 | 36.3612 | 37.8448 | 25.3961 | 24.5933 | 28.9743 | 36.4849 | 35.3991 | 38.479 | 36.7659 | 36.2645 | 35.6208 | 36.6655 | 33.3028 | 36.9989 | 35.764 | 35.8679 | 34.8587 | 36.8501 | 37.0198 | 36.855 | 38.1256 | 36.7209 | 36.6667 | 37.6901 | 38.8397 | 36.4948 | 37.8701 | 37.2815 | 38.9927 | 35.9848 | 38.2686 | 36.4683 | 38.1321 | 37.262 | 38.8659 | 37.292 | 39.4699 | 36.8018 | 38.5188 | 40.1802 | 93.4008 | 93.4981 | 93.3596
2022-09-07 21:40 | 3:16 | 23.9758 | 25.582 | 27.4756 | 36.4115 | 38.7049 | 35.3062 | 38.3094 | 35.0824 | 38.5425 | 36.3805 | 37.0703 | 39.5524 | 34.6265 | 35.7519 | 37.2354 | 35.8701 | 35.7629 | 35.6052 | 36.2971 | 37.8124 | 25.1368 | 23.907 | 28.8128 | 36.4525 | 35.3225 | 38.5412 | 36.7625 | 36.1812 | 35.6225 | 36.658 | 33.1424 | 37.0426 | 35.7004 | 35.8593 | 34.8202 | 36.8869 | 36.967 | 36.7612 | 38.2216 | 36.59 | 36.6663 | 37.6428 | 38.8771 | 36.4432 | 37.8985 | 37.239 | 38.9536 | 35.9105 | 38.2593 | 36.4804 | 38.0141 | 37.2278 | 38.9035 | 37.2453 | 39.32 | 36.7649 | 38.4923 | 40.1055 | 93.577 | 93.6431 | 93.4831
2022-09-07 21:40 | 3:16 | 23.9908 | 25.4422 | 27.2923 | 36.2367 | 38.7186 | 35.2927 | 38.295 | 35.1399 | 38.5625 | 36.3946 | 37.0345 | 39.5827 | 34.5198 | 35.6805 | 37.1848 | 35.827 | 35.7007 | 35.5886 | 36.2186 | 37.8819 | 25.1825 | 23.8036 | 28.9162 | 36.4333 | 35.2563 | 38.6325 | 36.7239 | 36.0924 | 35.5148 | 36.6458 | 33.0483 | 36.9568 | 35.7092 | 35.8098 | 34.6895 | 36.803 | 36.8034 | 36.7471 | 38.1102 | 36.4184 | 36.6123 | 37.6079 | 38.8238 | 36.3055 | 37.8707 | 37.1797 | 38.9001 | 35.9317 | 38.4212 | 36.4094 | 38.0005 | 37.1725 | 38.6643 | 37.1502 | 39.3101 | 36.7561 | 38.4865 | 40.2638 | 93.7541 | 93.7574 | 93.5517
2022-09-07 21:40 | 3:16 | 23.7907 | 25.338 | 27.13 | 36.1803 | 38.6816 | 35.3381 | 38.2456 | 35.1132 | 38.5413 | 36.4379 | 37.0521 | 39.6283 | 34.5313 | 35.7395 | 37.1805 | 35.8522 | 35.6388 | 35.597 | 36.1591 | 37.855 | 25.6815 | 23.5369 | 29.8224 | 36.4107 | 35.2207 | 38.4188 | 36.6941 | 36.2189 | 35.5019 | 36.6345 | 33.1921 | 36.976 | 35.5674 | 35.8394 | 34.6744 | 36.8119 | 36.798 | 36.782 | 38.1504 | 36.4446 | 36.571 | 37.6409 | 38.7701 | 36.4224 | 37.9024 | 37.1471 | 38.9555 | 35.9248 | 38.3558 | 36.3821 | 38.5827 | 37.1814 | 38.8431 | 37.0609 | 39.4493 | 36.6825 | 38.4514 | 40.1489 | 93.9425 | 93.9552 | 93.6606
2022-09-07 21:40 | 3:16 | 23.6482 | 25.21 | 26.9983 | 36.0861 | 38.6538 | 35.1788 | 38.1779 | 34.997 | 38.5276 | 36.199 | 36.8324 | 39.5606 | 34.5175 | 35.6869 | 37.044 | 35.8364 | 35.6082 | 35.5708 | 36.1463 | 37.7998 | 26.6288 | 23.5559 | 30.5186 | 36.3674 | 35.2068 | 38.3669 | 36.6667 | 36.1655 | 35.4476 | 36.5873 | 33.4639 | 36.9628 | 35.476 | 35.8414 | 34.7621 | 36.7217 | 36.897 | 36.6876 | 38.1056 | 36.5308 | 36.5108 | 37.707 | 38.8627 | 36.5132 | 37.9239 | 37.1159 | 38.8943 | 35.9258 | 38.2822 | 36.3764 | 38.5069 | 37.1499 | 38.873 | 37.0816 | 39.4128 | 36.6897 | 38.4917 | 39.8685 | 94.0921 | 94.1637 | 93.8107
2022-09-07 21:41 | 3:16 | 23.5773 | 25.0613 | 26.8247 | 36.1262 | 38.6687 | 35.2392 | 38.172 | 34.828 | 38.5465 | 36.0635 | 36.7505 | 39.5093 | 34.4432 | 35.6866 | 37.1609 | 35.7796 | 35.5511 | 35.5364 | 36.1038 | 37.631 | 27.2018 | 23.5313 | 30.6917 | 36.4153 | 35.1782 | 38.5411 | 36.6663 | 36.2192 | 35.5171 | 36.6379 | 33.547 | 36.8109 | 35.5037 | 35.8684 | 34.5172 | 36.6847 | 36.8465 | 36.7288 | 38.2147 | 36.4935 | 36.4222 | 37.6139 | 38.8511 | 36.5186 | 37.9491 | 37.0755 | 38.9285 | 35.9334 | 38.2644 | 36.3638 | 38.1867 | 37.0636 | 38.7609 | 37.121 | 39.1203 | 36.6091 | 38.5181 | 39.8867 | 94.2435 | 94.2869 | 93.8814
2022-09-07 21:41 | 3:17 | 23.3883 | 24.9164 | 26.6949 | 36.0686 | 38.6392 | 35.2307 | 38.1046 | 34.768 | 38.5361 | 36.1134 | 36.6053 | 39.5293 | 34.4418 | 35.6764 | 36.9981 | 35.7502 | 35.4718 | 35.4514 | 36.0648 | 37.6588 | 27.3964 | 23.3155 | 30.6111 | 36.4374 | 35.1038 | 38.6282 | 36.6123 | 36.0823 | 35.4047 | 36.6872 | 33.3772 | 36.8095 | 35.4281 | 35.8127 | 34.5623 | 36.697 | 36.5944 | 36.7699 | 38.039 | 36.4165 | 36.4324 | 37.5697 | 38.6609 | 36.375 | 37.9651 | 37.006 | 38.8768 | 35.7545 | 38.2336 | 36.372 | 38.1062 | 37.0446 | 38.7584 | 37.0078 | 39.3696 | 36.6027 | 38.501 | 39.9104 | 94.4002 | 94.4701 | 93.923
2022-09-07 21:41 | 3:17 | 23.2704 | 24.6937 | 26.5075 | 36.0146 | 38.6108 | 35.1558 | 38.0847 | 34.7419 | 38.4708 | 36.0836 | 36.6471 | 39.535 | 34.3897 | 35.6172 | 36.9765 | 35.7378 | 35.4 | 35.2792 | 36.033 | 37.7002 | 27.2981 | 23.2257 | 30.3703 | 36.3664 | 35.0424 | 38.6448 | 36.571 | 35.9353 | 35.3592 | 36.5694 | 33.2759 | 36.8039 | 35.4188 | 35.7255 | 34.4893 | 36.6993 | 36.6434 | 36.6497 | 38.0252 | 36.3078 | 36.3703 | 37.5137 | 38.6757 | 36.2632 | 37.83 | 36.9513 | 38.7916 | 35.6941 | 38.1817 | 36.3397 | 38.0421 | 37.0236 | 38.7602 | 36.9365 | 38.8298 | 36.5546 | 38.3528 | 39.8521 | 94.5831 | 94.5695 | 94.0938
2022-09-07 21:41 | 3:17 | 23.0681 | 24.5027 | 26.3545 | 36.0345 | 38.5815 | 35.0624 | 38.1221 | 34.6426 | 38.4423 | 36.0467 | 36.6285 | 39.5726 | 34.2897 | 35.4819 | 37.1033 | 35.7075 | 35.3484 | 35.2581 | 36.0177 | 37.7564 | 27.1027 | 23.0628 | 30.1786 | 36.2951 | 34.9953 | 38.4598 | 36.5108 | 35.8993 | 35.3277 | 36.5534 | 33.0601 | 36.7609 | 35.3285 | 35.6381 | 34.3948 | 36.5782 | 36.6806 | 36.5735 | 37.9786 | 36.3371 | 36.3612 | 37.5109 | 38.6014 | 36.1718 | 37.7426 | 36.8989 | 38.8396 | 35.6927 | 38.0311 | 36.3005 | 38.2703 | 36.9271 | 38.6528 | 36.8075 | 39.0863 | 36.4969 | 38.3915 | 39.9065 | 94.75 | 94.7465 | 94.2159
2022-09-07 21:41 | 3:17 | 22.9789 | 24.3235 | 26.1864 | 35.8279 | 38.5534 | 34.8085 | 38.0819 | 34.6345 | 38.4466 | 36.1294 | 36.7417 | 39.5396 | 34.2531 | 35.4286 | 36.9308 | 35.6456 | 35.3697 | 35.2886 | 35.9576 | 37.663 | 26.8451 | 22.9013 | 29.9798 | 36.2013 | 34.9255 | 38.3524 | 36.4222 | 35.9585 | 35.2432 | 36.4397 | 32.9645 | 36.6931 | 35.3262 | 35.617 | 34.3028 | 36.5451 | 36.4391 | 36.5739 | 37.9445 | 36.2474 | 36.2716 | 37.4776 | 38.5084 | 36.0751 | 37.8508 | 36.8565 | 38.7535 | 35.6624 | 37.9937 | 36.1826 | 37.8847 | 36.8905 | 38.6174 | 36.8385 | 39.0191 | 36.3709 | 38.2319 | 39.8737 | 94.8513 | 94.8489 | 94.2391
2022-09-07 21:41 | 3:17 | 22.8508 | 24.202 | 26.0564 | 35.8202 | 38.5716 | 34.8582 | 38.0265 | 34.6021 | 38.455 | 35.9838 | 36.4936 | 39.4981 | 34.2147 | 35.3769 | 36.8525 | 35.6462 | 35.2991 | 35.2463 | 35.9014 | 37.575 | 26.5898 | 22.7776 | 29.8055 | 36.219 | 34.8457 | 38.4005 | 36.4324 | 35.7621 | 35.1699 | 36.4397 | 32.8864 | 36.8401 | 35.2215 | 35.5428 | 34.1996 | 36.5981 | 36.5682 | 36.5381 | 37.894 | 36.2473 | 36.2114 | 37.3708 | 38.5311 | 36.0264 | 37.8047 | 36.8264 | 38.7122 | 35.545 | 37.9488 | 36.0782 | 37.7172 | 36.8483 | 38.6097 | 36.6186 | 39.0287 | 36.3297 | 38.1951 | 39.9613 | 94.8946 | 94.8987 | 94.3093
2022-09-07 21:42 | 3:18 | 22.7419 | 24.0723 | 25.9308 | 35.651 | 38.5389 | 34.8208 | 38.0101 | 34.5471 | 38.4459 | 35.9125 | 36.565 | 39.5275 | 34.009 | 35.4295 | 36.8896 | 35.5998 | 35.1954 | 35.2953 | 35.9058 | 37.5083 | 26.3243 | 22.704 | 29.5691 | 36.0767 | 34.8014 | 38.2872 | 36.3703 | 35.7535 | 35.1013 | 36.2816 | 32.8684 | 36.8042 | 35.1582 | 35.4752 | 34.2057 | 36.586 | 36.5836 | 36.5472 | 37.8582 | 36.2189 | 36.1554 | 37.2506 | 38.5285 | 35.9775 | 37.6411 | 36.789 | 38.6429 | 35.5162 | 37.9669 | 36.006 | 37.9989 | 36.7961 | 38.4583 | 36.5894 | 39.1657 | 36.2594 | 38.0562 | 39.7296 | 94.9613 | 95.0292 | 94.3803
2022-09-07 21:42 | 3:18 | 22.5696 | 23.9187 | 25.7927 | 35.5818 | 38.5095 | 34.88 | 37.9192 | 34.4712 | 38.3702 | 35.883 | 36.3917 | 39.5241 | 34.0733 | 35.4236 | 36.8214 | 35.5743 | 35.1669 | 35.2489 | 35.9085 | 37.3943 | 26.0625 | 22.5984 | 29.3352 | 36.0308 | 34.7406 | 38.1145 | 36.3612 | 35.7361 | 35.0821 | 36.2289 | 32.7889 | 36.5912 | 35.1048 | 35.4107 | 33.8675 | 36.489 | 36.4514 | 36.4985 | 37.8239 | 36.101 | 36.0613 | 37.236 | 38.5184 | 35.9166 | 37.5794 | 36.7533 | 38.7063 | 35.385 | 37.8995 | 35.9568 | 37.9551 | 36.6501 | 38.5103 | 36.5171 | 39.2484 | 36.2026 | 37.9711 | 39.7129 | 95.0315 | 95.0657 | 94.4257
2022-09-07 21:42 | 3:18 | 22.508 | 23.748 | 25.6708 | 35.5403 | 38.4764 | 34.868 | 37.9001 | 34.3899 | 38.3522 | 35.8176 | 36.322 | 39.4328 | 34.0528 | 35.3298 | 36.796 | 35.5683 | 35.1103 | 35.2134 | 35.8028 | 37.3018 | 25.8155 | 22.4532 | 29.1825 | 35.8695 | 34.6765 | 37.989 | 36.2716 | 35.9153 | 35.0862 | 36.2014 | 32.716 | 36.6258 | 35.0699 | 35.3408 | 33.7887 | 36.4832 | 36.3466 | 36.3941 | 37.8847 | 36.0354 | 36.0547 | 37.1903 | 38.4429 | 35.9088 | 37.4999 | 36.6965 | 38.6511 | 35.3463 | 37.8753 | 35.9192 | 37.8155 | 36.4081 | 38.5986 | 36.4403 | 39.1007 | 36.1286 | 38.1687 | 39.7496 | 94.9755 | 95.0157 | 94.3689
2022-09-07 21:42 | 3:18 | 22.3271 | 23.5413 | 25.5357 | 35.522 | 38.4519 | 34.6392 | 37.8537 | 34.353 | 38.369 | 35.9041 | 36.2906 | 39.4258 | 33.9109 | 35.1778 | 36.7161 | 35.4813 | 35.0419 | 35.2334 | 35.7852 | 37.3348 | 25.5925 | 22.3632 | 29.0017 | 35.8092 | 34.5822 | 37.9494 | 36.2114 | 35.6903 | 35.0425 | 36.1708 | 32.5926 | 36.4919 | 34.9734 | 35.2214 | 33.9888 | 36.4234 | 36.4436 | 36.3402 | 37.8471 | 36.0713 | 35.9278 | 37.0932 | 38.3771 | 35.7752 | 37.4733 | 36.6327 | 38.5413 | 35.2484 | 37.7726 | 35.8113 | 37.8734 | 36.4962 | 38.4727 | 36.4371 | 38.9568 | 36.08 | 37.9677 | 39.6028 | 94.7375 | 94.9206 | 94.2124
2022-09-07 21:42 | 3:18 | 22.2787 | 23.4871 | 25.4088 | 35.4878 | 38.4216 | 34.6046 | 37.8558 | 34.2543 | 38.3105 | 35.8172 | 36.316 | 39.4883 | 33.8649 | 35.2398 | 36.7772 | 35.4643 | 35.0166 | 35.1626 | 35.6808 | 37.345 | 25.3928 | 22.2474 | 28.8613 | 35.8272 | 34.5384 | 38.1648 | 36.1554 | 35.4809 | 34.983 | 36.0598 | 32.4866 | 36.4474 | 34.8917 | 35.1065 | 33.7573 | 36.5109 | 36.3138 | 36.1794 | 37.8497 | 35.9222 | 35.9444 | 37.0096 | 38.249 | 35.7368 | 37.4002 | 36.6003 | 38.5697 | 35.2082 | 37.6855 | 35.8287 | 37.8049 | 36.4818 | 38.4432 | 36.4166 | 38.8708 | 35.9759 | 37.8214 | 39.883 | 94.563 | 94.7132 | 94.0027
2022-09-07 21:42 | 3:18 | 22.0457 | 23.2642 | 25.2296 | 35.4148 | 38.3639 | 34.4313 | 37.8931 | 34.2665 | 38.3314 | 35.6222 | 36.2381 | 39.4318 | 33.7916 | 35.1038 | 36.7065 | 35.3987 | 34.9802 | 34.9199 | 35.6508 | 37.1943 | 25.2136 | 22.0884 | 28.6961 | 35.6563 | 34.4352 | 37.8325 | 36.0613 | 35.3919 | 34.8802 | 36.0797 | 32.3739 | 36.538 | 34.9417 | 35.0767 | 33.6261 | 36.309 | 36.3739 | 36.1458 | 37.8181 | 36.0042 | 35.9028 | 36.9937 | 38.3103 | 35.5971 | 37.3438 | 36.5545 | 38.5052 | 35.1201 | 37.7748 | 35.7297 | 37.7327 | 36.32 | 38.4215 | 36.3096 | 38.7649 | 35.9378 | 37.7855 | 39.6673 | 94.3098 | 94.4791 | 93.917
2022-09-07 21:43 | 3:18 | 22.0673 | 23.1662 | 25.1157 | 35.3035 | 38.3308 | 34.3077 | 37.729 | 34.1234 | 38.2491 | 35.6304 | 36.0489 | 39.5246 | 33.7307 | 35.1014 | 36.6735 | 35.3537 | 34.8638 | 34.885 | 35.6034 | 37.208 | 25.0506 | 22.0476 | 28.5778 | 35.6026 | 34.3928 | 37.8596 | 36.0547 | 35.5625 | 34.8604 | 36.0262 | 32.3523 | 36.3856 | 34.8577 | 35.0515 | 33.7173 | 36.3449 | 36.4526 | 36.1542 | 37.8213 | 36.0418 | 35.7701 | 36.8884 | 38.191 | 35.6025 | 37.3102 | 36.5044 | 38.337 | 35.0576 | 37.8359 | 35.619 | 37.9945 | 36.2069 | 38.4538 | 36.3248 | 38.8093 | 35.8206 | 37.8099 | 39.4796 | 94.1539 | 94.3219 | 93.7591
2022-09-07 21:43 | 3:19 | 21.8827 | 23.0412 | 25.0044 | 35.258 | 38.2917 | 34.5244 | 37.751 | 34.0488 | 38.2456 | 35.7288 | 35.9942 | 39.4589 | 33.6673 | 35.0338 | 36.5689 | 35.3477 | 34.7966 | 34.9502 | 35.5629 | 37.1414 | 24.8717 | 21.8125 | 28.4047 | 35.5006 | 34.3062 | 37.8847 | 35.9278 | 35.4463 | 34.7847 | 35.9621 | 32.2353 | 36.2478 | 34.7722 | 35.0425 | 33.4569 | 36.2278 | 36.3071 | 36.0671 | 37.7876 | 35.8986 | 35.7125 | 36.8518 | 38.1834 | 35.5422 | 37.139 | 36.4623 | 38.3686 | 34.9181 | 37.7486 | 35.6285 | 38.066 | 36.0017 | 38.429 | 36.1988 | 38.798 | 35.7059 | 37.7201 | 39.3749 | 94.0133 | 94.167 | 93.75
2022-09-07 21:43 | 3:19 | 21.7117 | 22.8578 | 24.8537 | 35.2731 | 38.2369 | 34.2768 | 37.8274 | 34.0256 | 38.253 | 35.7038 | 36.0827 | 39.356 | 33.5785 | 34.9326 | 36.4601 | 35.2828 | 34.7482 | 34.8441 | 35.4944 | 37.0318 | 24.6702 | 21.6879 | 28.2766 | 35.3674 | 34.2037 | 37.8663 | 35.9444 | 35.458 | 34.7191 | 35.8887 | 32.1156 | 36.2895 | 34.7834 | 34.9145 | 33.2907 | 36.2429 | 36.1928 | 36.0057 | 37.5962 | 35.8081 | 35.6744 | 36.8146 | 38.0635 | 35.4108 | 37.1671 | 36.3697 | 38.2796 | 34.7897 | 37.6437 | 35.5488 | 37.3144 | 36.1655 | 38.188 | 36.2065 | 38.7782 | 35.6456 | 37.6734 | 39.3703 | 93.9379 | 94.0331 | 93.7212
2022-09-07 21:43 | 3:19 | 21.5824 | 22.7472 | 24.7239 | 35.0904 | 38.2273 | 34.1655 | 37.8295 | 33.9551 | 38.2535 | 35.5512 | 36.183 | 39.4278 | 33.5699 | 34.9451 | 36.3888 | 35.2325 | 34.6772 | 34.8777 | 35.4137 | 37.0018 | 24.5212 | 21.6265 | 28.1853 | 35.3719 | 34.1479 | 37.7671 | 35.9028 | 35.3477 | 34.6467 | 35.7712 | 32.0312 | 36.2549 | 34.6932 | 34.8588 | 33.4561 | 36.2372 | 36.2258 | 35.955 | 37.5719 | 35.8161 | 35.598 | 36.7704 | 37.9136 | 35.2424 | 37.1424 | 36.3058 | 38.1836 | 34.7654 | 37.4324 | 35.4928 | 37.3082 | 36.0373 | 38.1293 | 36.0619 | 38.572 | 35.6331 | 37.5117 | 39.6889 | 93.8885 | 93.9946 | 93.7276
2022-09-07 21:43 | 3:19 | 21.4822 | 22.6596 | 24.6254 | 35.0982 | 38.2403 | 34.1264 | 37.845 | 33.8806 | 38.184 | 35.5051 | 35.8322 | 39.3814 | 33.4699 | 34.9718 | 36.3386 | 35.1914 | 34.6853 | 34.7477 | 35.3835 | 36.941 | 24.3773 | 21.4071 | 28.0944 | 35.3233 | 34.0825 | 37.7487 | 35.7701 | 35.1767 | 34.6168 | 35.6935 | 31.9518 | 36.4078 | 34.7801 | 34.7426 | 33.3085 | 36.134 | 36.1441 | 35.9935 | 37.5268 | 35.7697 | 35.5386 | 36.6688 | 37.9907 | 35.252 | 36.9662 | 36.2447 | 38.0572 | 34.7163 | 37.36 | 35.3975 | 37.3897 | 35.9935 | 38.1519 | 36.0148 | 38.514 | 35.5394 | 37.6399 | 39.558 | 93.8417 | 93.9681 | 93.6865
2022-09-07 21:43 | 3:19 | 21.4102 | 22.4641 | 24.4869 | 35.107 | 38.1533 | 34.1837 | 37.7043 | 33.7953 | 38.1152 | 35.4616 | 35.8116 | 39.3173 | 33.3262 | 34.8678 | 36.4607 | 35.1571 | 34.5791 | 34.773 | 35.3314 | 36.9474 | 24.2608 | 21.4465 | 27.99 | 35.3124 | 34.0012 | 37.6906 | 35.7125 | 35.2688 | 34.5391 | 35.79 | 31.9002 | 36.1369 | 34.6215 | 34.766 | 33.1976 | 35.9691 | 35.9034 | 35.8679 | 37.5613 | 35.6347 | 35.5166 | 36.6018 | 37.8676 | 35.1676 | 36.9004 | 36.214 | 38.1818 | 34.6423 | 37.2379 | 35.2895 | 37.8721 | 35.8673 | 38.1634 | 35.8083 | 38.4556 | 35.4624 | 37.4805 | 39.3218 | 93.7325 | 93.8655 | 93.5745
2022-09-07 21:44 | 3:20 | 21.3571 | 22.42 | 24.3813 | 34.9537 | 38.1338 | 33.9598 | 37.7509 | 33.7814 | 38.0718 | 35.4187 | 35.9832 | 39.3134 | 33.3402 | 34.7129 | 36.2279 | 35.1158 | 34.4839 | 34.6692 | 35.3171 | 36.921 | 24.1741 | 21.2929 | 27.8912 | 35.1722 | 33.9618 | 37.6919 | 35.6744 | 35.2783 | 34.4555 | 35.7208 | 31.8256 | 36.1599 | 34.5479 | 34.647 | 32.9746 | 36.0915 | 35.9809 | 35.7713 | 37.5546 | 35.5393 | 35.5048 | 36.5571 | 37.8754 | 35.2325 | 36.8725 | 36.1365 | 38.1955 | 34.6286 | 37.3997 | 35.2061 | 37.8571 | 35.9886 | 38.119 | 35.8972 | 38.5188 | 35.3876 | 37.494 | 39.3884 | 93.6381 | 93.7864 | 93.5375
2022-09-07 21:44 | 3:20 | 21.1664 | 22.2916 | 24.2913 | 34.7945 | 38.085 | 33.9523 | 37.5672 | 33.6781 | 38.0866 | 35.3379 | 35.7703 | 39.2175 | 33.2722 | 34.6303 | 36.2524 | 35.086 | 34.4172 | 34.5374 | 35.2591 | 36.9612 | 24.0793 | 21.1309 | 27.805 | 35.0104 | 33.8798 | 37.541 | 35.598 | 35.3143 | 34.3781 | 35.7028 | 31.7879 | 36.2129 | 34.3935 | 34.6463 | 33.0519 | 35.9581 | 36.0246 | 35.7581 | 37.5382 | 35.5771 | 35.5341 | 36.5625 | 37.8399 | 35.1039 | 36.8878 | 36.0879 | 38.0386 | 34.4955 | 37.2009 | 35.2122 | 37.932 | 35.8906 | 38.1281 | 35.6587 | 38.4695 | 35.294 | 37.4633 | 39.3598 | 93.5025 | 93.6815 | 93.4595
2022-09-07 21:44 | 3:20 | 21.0232 | 22.1179 | 24.1518 | 34.6729 | 38.0531 | 33.8691 | 37.6729 | 33.7426 | 38.0186 | 35.3944 | 35.8206 | 39.255 | 33.183 | 34.5934 | 36.1285 | 35.0384 | 34.3808 | 34.4124 | 35.2117 | 36.7971 | 23.9463 | 20.9296 | 27.6829 | 34.9594 | 33.8052 | 37.5464 | 35.5386 | 35.139 | 34.3802 | 35.5939 | 31.7589 | 36.209 | 34.3918 | 34.6396 | 32.8719 | 36.0867 | 35.9154 | 35.8079 | 37.6169 | 35.4948 | 35.5317 | 36.4826 | 37.7839 | 35.0245 | 36.8142 | 36.0106 | 38.0296 | 34.4705 | 37.1677 | 35.1453 | 37.954 | 35.7068 | 38.0112 | 35.573 | 38.3208 | 35.2284 | 37.3459 | 39.3567 | 93.466 | 93.6952 | 93.4752
2022-09-07 21:44 | 3:20 | 21.0237 | 22.032 | 24.0601 | 34.6553 | 38.0174 | 33.7753 | 37.6069 | 33.5483 | 38.0152 | 35.0688 | 35.6468 | 39.1553 | 33.0966 | 34.5692 | 36.1804 | 35.0016 | 34.3054 | 34.363 | 35.1244 | 36.6909 | 23.9509 | 21.1257 | 27.745 | 34.9372 | 33.7427 | 37.2815 | 35.5166 | 35.1256 | 34.335 | 35.4942 | 31.764 | 36.1778 | 34.2998 | 34.5575 | 32.7941 | 35.9921 | 35.8703 | 35.7217 | 37.5954 | 35.4249 | 35.6203 | 36.4254 | 37.7804 | 34.9337 | 36.7517 | 35.995 | 37.9038 | 34.515 | 37.2608 | 35.1076 | 37.1969 | 35.6789 | 37.8329 | 35.546 | 38.5766 | 35.1913 | 37.297 | 39.1839 | 93.4403 | 93.5943 | 93.4392
2022-09-07 21:44 | 3:20 | 19.7634 | 21.7057 | 23.6463 | 34.7086 | 37.8462 | 34.0468 | 37.578 | 33.3896 | 37.9308 | 35.3158 | 35.2568 | 39.1641 | 33.0213 | 34.566 | 36.0352 | 34.9344 | 34.2945 | 34.3256 | 35.0098 | 36.7264 | 24.1731 | 21.7502 | 28.4981 | 34.9409 | 33.7178 | 37.3352 | 35.5048 | 35.0132 | 34.2594 | 35.5028 | 31.7852 | 35.8912 | 34.0477 | 34.4819 | 32.7942 | 35.8613 | 35.7874 | 35.602 | 37.324 | 35.3185 | 35.5934 | 36.4531 | 37.6847 | 35.0422 | 36.8472 | 35.9551 | 38.0456 | 34.5332 | 37.1838 | 35.0919 | 36.9925 | 35.687 | 37.978 | 35.51 | 38.5743 | 35.2679 | 37.4836 | 39.1271 | 93.3566 | 93.5223 | 93.3611
2022-09-07 21:44 | 3:20 | 19.2517 | 21.2644 | 23.2302 | 34.6058 | 37.7566 | 33.834 | 37.4884 | 33.2093 | 37.8576 | 35.216 | 35.1101 | 39.0502 | 32.9304 | 34.401 | 36.1489 | 34.7966 | 34.1892 | 34.2533 | 34.9811 | 36.6965 | 24.9397 | 23.0101 | 29.5993 | 35.087 | 33.7183 | 37.5522 | 35.5341 | 35.1695 | 34.2274 | 35.5717 | 32.1624 | 35.9327 | 33.9405 | 34.5714 | 33.0385 | 35.7542 | 35.7489 | 35.6097 | 37.3454 | 35.3657 | 35.7071 | 36.5163 | 37.8513 | 35.2563 | 37.0611 | 35.9112 | 38.0179 | 34.7284 | 37.4413 | 35.1061 | 37.1333 | 35.8093 | 37.9288 | 35.5385 | 38.5611 | 35.4089 | 37.4062 | 39.1326 | 93.3208 | 93.4405 | 93.3452
2022-09-07 21:45 | 3:20 | 18.8673 | 20.922 | 22.9183 | 34.4513 | 37.7123 | 33.7139 | 37.4198 | 33.2298 | 37.85 | 35.0371 | 35.2656 | 39.0272 | 32.7844 | 34.4342 | 36.0839 | 34.6912 | 34.1389 | 34.3064 | 34.9408 | 36.6055 | 25.9019 | 24.3871 | 30.4991 | 35.16 | 33.7614 | 37.7871 | 35.5317 | 35.0583 | 34.2219 | 35.6943 | 32.37 | 35.8945 | 33.9421 | 34.6103 | 33.1242 | 35.7558 | 35.6176 | 35.5772 | 37.04 | 35.2671 | 35.7763 | 36.6748 | 37.8972 | 35.3719 | 37.2554 | 35.8863 | 37.9929 | 34.9191 | 37.4718 | 35.2319 | 36.9516 | 35.9255 | 37.9746 | 35.6226 | 38.6054 | 35.5771 | 37.5309 | 39.2356 | 93.2522 | 93.3757 | 93.2291
2022-09-07 21:45 | 3:21 | 18.4834 | 20.6604 | 22.5912 | 34.3284 | 37.5597 | 33.7438 | 37.3751 | 33.1396 | 37.7508 | 35.0823 | 35.088 | 38.9847 | 32.6851 | 34.3491 | 35.9488 | 34.6775 | 34.0033 | 34.0049 | 34.8396 | 36.72 | 26.8992 | 25.8184 | 31.1853 | 35.1823 | 33.8307 | 37.8043 | 35.6203 | 35.041 | 34.254 | 35.6414 | 32.6009 | 35.9642 | 33.9197 | 34.6927 | 33.2385 | 35.6678 | 35.5843 | 35.6398 | 37.0032 | 35.2692 | 35.7698 | 36.723 | 38.0097 | 35.5349 | 37.3403 | 35.9674 | 38.0545 | 35.051 | 37.5576 | 35.3146 | 36.8851 | 36.0213 | 38.0661 | 35.6237 | 38.6362 | 35.6187 | 37.7699 | 39.1698 | 93.201 | 93.2847 | 93.2215
2022-09-07 21:45 | 3:21 | 18.1792 | 20.3758 | 22.319 | 34.1925 | 37.6117 | 33.4402 | 37.4494 | 33.0601 | 37.7394 | 34.9227 | 35.1611 | 38.8579 | 32.5863 | 34.3702 | 35.8071 | 34.605 | 33.913 | 34.0248 | 34.7458 | 36.8448 | 27.7956 | 27.1144 | 31.6738 | 35.2342 | 33.8397 | 37.7938 | 35.5934 | 34.8248 | 34.3319 | 35.7486 | 32.7791 | 35.8584 | 33.9509 | 34.6793 | 33.3168 | 35.7164 | 35.496 | 35.6584 | 37.1443 | 35.2389 | 35.8036 | 36.8305 | 38.0929 | 35.6892 | 37.3702 | 35.8851 | 38.2339 | 35.169 | 37.6228 | 35.3587 | 37.1767 | 36.1364 | 38.1103 | 35.6505 | 38.706 | 35.7124 | 37.7763 | 39.159 | 93.1184 | 93.2037 | 93.1679
2022-09-07 21:45 | 3:21 | 17.8977 | 20.1011 | 22.0437 | 34.1614 | 37.4823 | 33.3811 | 37.2821 | 33.0357 | 37.6873 | 34.8369 | 34.9919 | 38.966 | 32.4726 | 34.2362 | 35.8267 | 34.5214 | 33.8694 | 33.8875 | 34.6523 | 36.6231 | 28.5431 | 28.1247 | 32.0363 | 35.2612 | 33.872 | 38.0304 | 35.7071 | 34.9055 | 34.2604 | 35.809 | 32.9234 | 35.7694 | 33.8491 | 34.7775 | 33.4052 | 35.7672 | 35.4806 | 35.6774 | 37.0567 | 35.2469 | 35.8041 | 36.8471 | 38.1201 | 35.7685 | 37.4964 | 35.8714 | 38.2485 | 35.263 | 37.7128 | 35.4108 | 37.0819 | 36.1994 | 38.087 | 35.6619 | 38.7099 | 35.7694 | 37.8488 | 39.286 | 93.0213 | 93.0669 | 93.0687
2022-09-07 21:45 | 3:21 | 17.6412 | 19.8241 | 21.8129 | 34.0924 | 37.4406 | 33.3341 | 37.1391 | 32.8614 | 37.6583 | 34.9462 | 34.8907 | 38.8504 | 32.3995 | 34.251 | 35.7435 | 34.3847 | 33.7508 | 33.9789 | 34.5802 | 36.4451 | 29.1944 | 28.9056 | 32.3119 | 35.3021 | 33.8808 | 38.2507 | 35.7763 | 35.126 | 34.1823 | 35.8364 | 33.0476 | 35.5932 | 33.8094 | 34.7893 | 33.4303 | 35.8022 | 35.4725 | 35.6538 | 37.1815 | 35.3065 | 35.8355 | 36.8261 | 38.1386 | 35.8321 | 37.5274 | 35.9492 | 38.2135 | 35.3337 | 37.9129 | 35.4445 | 37.0288 | 36.2379 | 38.1713 | 35.7565 | 38.817 | 35.814 | 37.7491 | 39.1269 | 92.847 | 92.9842 | 93.0107
2022-09-07 21:45 | 3:21 | 17.4001 | 19.5606 | 21.5742 | 33.8962 | 37.3431 | 33.2501 | 37.0484 | 32.7771 | 37.6263 | 34.7183 | 34.7373 | 38.8261 | 32.2977 | 33.9722 | 35.7567 | 34.4152 | 33.6753 | 33.9637 | 34.5594 | 36.581 | 29.7139 | 29.4851 | 32.5269 | 35.3742 | 33.8819 | 38.0575 | 35.7698 | 34.9524 | 34.2596 | 35.8623 | 33.1388 | 35.6178 | 33.8489 | 34.8296 | 33.4918 | 35.6123 | 35.6116 | 35.7428 | 37.2198 | 35.4023 | 35.8527 | 36.9275 | 38.1761 | 35.9258 | 37.5549 | 35.9613 | 38.2248 | 35.4344 | 37.8174 | 35.4159 | 37.0378 | 36.2824 | 38.1585 | 35.6884 | 38.8429 | 35.8583 | 37.9037 | 39.2085 | 92.7409 | 92.8651 | 92.8684
2022-09-07 21:46 | 3:22 | 17.2056 | 19.3331 | 21.3881 | 33.908 | 37.2664 | 33.097 | 37.0429 | 32.6804 | 37.5592 | 34.7465 | 34.6705 | 38.7855 | 32.0857 | 33.9034 | 35.658 | 34.3525 | 33.6739 | 33.885 | 34.5436 | 36.4663 | 30.1304 | 29.9064 | 32.682 | 35.4545 | 33.9151 | 38.3034 | 35.8036 | 35.1791 | 34.2214 | 35.8873 | 33.1946 | 35.6336 | 33.8093 | 34.8893 | 33.6373 | 35.7919 | 35.5896 | 35.6717 | 37.2653 | 35.4455 | 35.892 | 36.9666 | 38.1925 | 35.9949 | 37.5657 | 35.9497 | 38.2298 | 35.4873 | 37.8954 | 35.5242 | 36.9575 | 36.2983 | 38.2184 | 35.7324 | 38.8591 | 35.9224 | 37.9134 | 39.341 | 92.6017 | 92.7582 | 92.7892
2022-09-07 21:46 | 3:22 | 16.9577 | 19.1366 | 21.1447 | 33.8458 | 37.166 | 32.9102 | 36.9072 | 32.5384 | 37.4906 | 34.3745 | 34.6773 | 38.7079 | 32.1481 | 33.8505 | 35.4999 | 34.2639 | 33.5444 | 33.8682 | 34.389 | 36.3799 | 30.4909 | 30.2293 | 32.8192 | 35.4175 | 33.9131 | 38.2354 | 35.8041 | 34.9589 | 34.151 | 35.9477 | 33.2537 | 35.6081 | 33.7535 | 34.9863 | 33.6775 | 35.7935 | 35.5528 | 35.7049 | 37.2174 | 35.4325 | 35.9326 | 36.9803 | 38.2885 | 35.9964 | 37.618 | 35.9354 | 38.1806 | 35.5641 | 37.8775 | 35.536 | 37.007 | 36.2948 | 38.1338 | 35.7563 | 38.9066 | 35.9406 | 37.8961 | 39.2555 | 92.4666 | 92.5974 | 92.7105
2022-09-07 21:46 | 3:22 | 16.8177 | 18.9218 | 20.9553 | 33.7096 | 37.0835 | 33.0736 | 36.7661 | 32.5156 | 37.3633 | 34.7288 | 34.3655 | 38.6821 | 32.1256 | 33.8362 | 35.4909 | 34.1994 | 33.5136 | 33.6471 | 34.3167 | 36.3332 | 30.7489 | 30.4917 | 32.9432 | 35.3879 | 33.8855 | 38.3577 | 35.8355 | 34.85 | 34.2072 | 35.941 | 33.3308 | 35.6865 | 33.7529 | 34.8829 | 33.7718 | 35.7515 | 35.5833 | 35.7045 | 37.3011 | 35.4218 | 35.9609 | 36.9799 | 38.2895 | 36.0626 | 37.7107 | 35.876 | 38.1361 | 35.5827 | 37.9297 | 35.4663 | 37.1708 | 36.3787 | 38.0365 | 35.9722 | 38.9466 | 36.0134 | 38.1177 | 39.34 | 92.3326 | 92.4621 | 92.6625
2022-09-07 21:46 | 3:22 | 16.5809 | 18.7628 | 20.7752 | 33.6804 | 37.0232 | 33.0763 | 36.6414 | 32.2582 | 37.3377 | 34.6965 | 34.2686 | 38.4916 | 31.9383 | 33.705 | 35.3131 | 34.1623 | 33.3714 | 33.4891 | 34.2392 | 36.4273 | 30.963 | 30.6817 | 33.0497 | 35.3831 | 33.9021 | 38.4098 | 35.8527 | 34.9095 | 34.1109 | 35.9697 | 33.3601 | 35.5127 | 33.6466 | 34.9383 | 33.7812 | 35.7288 | 35.4644 | 35.6406 | 37.0793 | 35.3431 | 35.9796 | 36.9727 | 38.2852 | 36.1506 | 37.7841 | 35.8995 | 38.179 | 35.6279 | 37.9743 | 35.5024 | 37.1725 | 36.3618 | 38.1179 | 35.8735 | 38.8802 | 36.0354 | 38.0997 | 39.3441 | 92.2212 | 92.3506 | 92.5974
2022-09-07 21:46 | 3:22 | 16.4226 | 18.5459 | 20.5884 | 33.7837 | 36.919 | 33.0537 | 36.6853 | 32.1752 | 37.2486 | 34.7996 | 34.0113 | 38.4868 | 31.8669 | 33.3671 | 35.2746 | 34.0638 | 33.3238 | 33.4389 | 34.1954 | 36.4729 | 31.1216 | 30.8393 | 33.1472 | 35.3304 | 33.9333 | 38.4588 | 35.892 | 34.6519 | 34.132 | 36.0251 | 33.4187 | 35.5206 | 33.6539 | 34.933 | 33.7826 | 35.7878 | 35.3301 | 35.6707 | 36.7577 | 35.2494 | 35.8995 | 37.0683 | 38.3391 | 36.1803 | 37.7242 | 35.9343 | 38.2827 | 35.7367 | 38.1307 | 35.5994 | 37.1562 | 36.4713 | 38.0155 | 35.8867 | 38.8897 | 36.0755 | 38.1917 | 39.3341 | 92.1338 | 92.2467 | 92.5021
2022-09-07 21:46 | 3:22 | 16.1786 | 18.3555 | 20.4059 | 33.5093 | 36.8046 | 32.7991 | 36.5878 | 32.2589 | 37.2419 | 34.366 | 34.2309 | 38.4567 | 31.7364 | 33.592 | 35.1753 | 33.987 | 33.2681 | 33.2971 | 34.0282 | 36.4198 | 31.2785 | 30.9318 | 33.1975 | 35.3609 | 33.9482 | 38.5131 | 35.9326 | 34.7806 | 34.0283 | 35.9619 | 33.4917 | 35.4253 | 33.6007 | 34.9091 | 33.8014 | 35.7293 | 35.2879 | 35.6022 | 36.9262 | 35.2055 | 35.9158 | 37.152 | 38.3394 | 36.2617 | 37.8297 | 35.97 | 38.2935 | 35.8045 | 37.9928 | 35.6577 | 37.1371 | 36.5158 | 38.183 | 35.726 | 38.7848 | 36.1504 | 38.1854 | 39.2471 | 91.9392 | 92.0888 | 92.3257
2022-09-07 21:47 | 3:22 | 16.0021 | 18.1648 | 20.2202 | 33.4602 | 36.6651 | 32.7784 | 36.5279 | 32.1372 | 37.1754 | 34.4167 | 33.8652 | 38.4122 | 31.7334 | 33.639 | 35.1422 | 33.9121 | 33.2007 | 33.0919 | 34.0536 | 36.2417 | 31.3778 | 31.0675 | 33.2746 | 35.2884 | 33.9523 | 38.47 | 35.9609 | 34.8227 | 34.0454 | 35.9583 | 33.5281 | 35.4396 | 33.6032 | 34.9045 | 33.8156 | 35.5611 | 35.1881 | 35.521 | 36.8843 | 35.1688 | 36.0012 | 37.1512 | 38.415 | 36.357 | 37.8219 | 35.9703 | 38.2927 | 35.8652 | 38.0938 | 35.6557 | 37.223 | 36.5852 | 38.1863 | 35.7807 | 38.7588 | 36.1664 | 38.3125 | 39.1908 | 91.8322 | 91.9554 | 92.259
2022-09-07 21:47 | 3:23 | 15.846 | 17.99 | 20.0365 | 33.4368 | 36.5193 | 32.816 | 36.3972 | 31.9196 | 37.0598 | 34.7143 | 33.7013 | 38.2709 | 31.6138 | 33.4612 | 35.1839 | 33.6753 | 33.1385 | 32.9288 | 34.0971 | 36.0848 | 31.4375 | 31.1194 | 33.3101 | 35.2332 | 33.9768 | 38.391 | 35.9796 | 34.6825 | 34.0986 | 35.9182 | 33.5591 | 35.4033 | 33.5689 | 34.879 | 33.8523 | 35.677 | 35.138 | 35.6448 | 36.9783 | 35.1377 | 36.1083 | 37.0894 | 38.4216 | 36.4063 | 37.8641 | 35.9965 | 38.2926 | 35.9137 | 38.1264 | 35.7251 | 37.2828 | 36.6476 | 38.075 | 35.8066 | 38.9173 | 36.2231 | 38.4366 | 39.2019 | 91.6974 | 91.8251 | 92.201
2022-09-07 21:47 | 3:23 | 15.6511 | 17.7836 | 19.8738 | 33.5029 | 36.512 | 32.7529 | 36.2849 | 31.6682 | 37.0001 | 34.4355 | 33.5822 | 38.1882 | 31.4867 | 33.5962 | 35.0149 | 33.6375 | 33.0168 | 32.886 | 33.9085 | 35.9171 | 31.501 | 31.173 | 33.3471 | 35.2571 | 33.9968 | 38.3841 | 35.8995 | 34.7662 | 34.1814 | 35.9365 | 33.5867 | 35.2704 | 33.5571 | 34.9238 | 33.9017 | 35.6591 | 35.1626 | 35.634 | 36.8901 | 35.1109 | 36.1053 | 37.1607 | 38.4898 | 36.4773 | 37.8613 | 36.0315 | 38.2814 | 36.0144 | 38.1481 | 35.791 | 37.3159 | 36.7223 | 38.1657 | 35.7638 | 38.9823 | 36.2721 | 38.4379 | 39.1486 | 91.6423 | 91.7743 | 92.2088
2022-09-07 21:47 | 3:23 | 15.0487 | 16.9292 | 19.5317 | 33.3073 | 36.4588 | 32.7293 | 35.9734 | 31.5956 | 36.9409 | 34.5264 | 33.4494 | 38.1516 | 31.2037 | 33.4271 | 35.0134 | 33.5487 | 32.9791 | 33.0571 | 33.8996 | 35.8964 | 31.5275 | 31.2168 | 33.4052 | 35.2631 | 33.9896 | 38.3028 | 35.9158 | 34.7783 | 34.2121 | 35.9079 | 33.6429 | 35.2416 | 33.3635 | 34.8818 | 33.9383 | 35.4953 | 35.1745 | 35.5722 | 36.7152 | 35.0775 | 36.1688 | 37.1947 | 38.5464 | 36.4995 | 37.8755 | 36.0811 | 38.2524 | 36.0894 | 38.1799 | 35.7816 | 37.3323 | 36.7595 | 38.2336 | 35.7858 | 38.9914 | 36.3383 | 38.5238 | 39.1861 | 91.7092 | 91.8069 | 92.1857
2022-09-07 21:47 | 3:23 | 15.6425 | 15.4849 | 20.1902 | 33.0335 | 36.3307 | 32.7267 | 36.0028 | 31.488 | 36.7619 | 34.2378 | 33.3642 | 38.0675 | 31.2098 | 33.4076 | 34.8893 | 33.5283 | 32.8779 | 32.6318 | 33.6431 | 35.8948 | 31.4723 | 31.2122 | 33.4286 | 35.2732 | 33.9942 | 38.5577 | 36.0012 | 34.7345 | 34.129 | 36.0513 | 33.6797 | 35.2241 | 33.362 | 34.9947 | 33.943 | 35.5561 | 35.1539 | 35.5369 | 36.8274 | 35.0584 | 36.1998 | 37.2972 | 38.563 | 36.5489 | 37.9499 | 36.096 | 38.2799 | 36.1302 | 38.2153 | 35.7605 | 37.3685 | 36.7759 | 38.1563 | 35.8351 | 38.977 | 36.3976 | 38.5681 | 39.1584 | 91.7732 | 91.8092 | 92.231
2022-09-07 21:47 | 3:23 | 17.822 | 17.4624 | 22.7674 | 33.5352 | 36.2272 | 32.7485 | 36.1314 | 31.7037 | 36.7706 | 34.441 | 33.7176 | 37.9951 | 31.5149 | 33.3119 | 35.0249 | 33.5432 | 32.9999 | 32.9855 | 33.7852 | 35.9228 | 31.4875 | 31.2322 | 33.5391 | 35.3492 | 34.0437 | 38.5052 | 36.1083 | 34.7607 | 34.1169 | 36.1061 | 33.7244 | 35.1027 | 33.4441 | 34.9695 | 34.0162 | 35.5087 | 35.1457 | 35.6296 | 36.965 | 35.0757 | 36.2648 | 37.2992 | 38.5522 | 36.6318 | 37.9709 | 36.0812 | 38.3728 | 36.2304 | 38.2799 | 35.8094 | 37.4945 | 36.8183 | 38.2349 | 35.8627 | 38.8737 | 36.4503 | 38.5789 | 39.2362 | 91.7863 | 91.8711 | 92.2932
2022-09-07 21:48 | 3:23 | 19.8 | 19.858 | 25.0501 | 33.941 | 36.3106 | 32.9873 | 36.2805 | 32.0996 | 36.7511 | 34.5173 | 33.8805 | 38.105 | 31.8852 | 33.5171 | 35.0902 | 33.5679 | 33.1802 | 33.3541 | 33.8943 | 36.2717 | 31.5401 | 31.2617 | 33.6576 | 35.5404 | 34.123 | 38.6216 | 36.1053 | 34.7477 | 34.23 | 36.0451 | 33.7753 | 35.1524 | 33.61 | 35.128 | 34.0583 | 35.6847 | 35.2246 | 35.7896 | 36.8463 | 35.1223 | 36.3396 | 37.3482 | 38.6197 | 36.7103 | 38.0185 | 36.1035 | 38.3607 | 36.3134 | 38.3369 | 35.882 | 37.4787 | 36.8982 | 38.2026 | 35.9616 | 39.0406 | 36.4941 | 38.6283 | 39.1669 | 91.849 | 91.9458 | 92.3244
2022-09-07 21:48 | 3:24 | 21.6384 | 22.1645 | 26.8586 | 34.4133 | 36.3517 | 33.2012 | 36.4211 | 32.2869 | 36.8065 | 34.7859 | 34.0418 | 38.1226 | 32.1232 | 33.8566 | 35.2152 | 33.6366 | 33.3306 | 33.777 | 34.0496 | 36.3841 | 31.6251 | 31.3021 | 33.8209 | 35.6585 | 34.1472 | 38.488 | 36.1688 | 34.8415 | 34.1592 | 36.1772 | 33.8605 | 35.2487 | 33.699 | 35.1635 | 34.1288 | 35.7954 | 35.2793 | 35.8079 | 37.078 | 35.1823 | 36.3379 | 37.4384 | 38.6369 | 36.7907 | 38.0797 | 36.182 | 38.35 | 36.3654 | 38.3969 | 35.9308 | 37.5243 | 36.9394 | 38.2385 | 36.0252 | 39.1055 | 36.5665 | 38.6589 | 39.2762 | 91.9396 | 92.0393 | 92.3852
2022-09-07 21:48 | 3:24 | 23.184 | 24.2322 | 28.1578 | 34.8278 | 36.3805 | 33.235 | 36.4857 | 32.4692 | 36.7859 | 34.8824 | 34.414 | 38.2671 | 32.3691 | 33.9487 | 35.3093 | 33.7188 | 33.4985 | 33.983 | 34.1427 | 36.5216 | 31.7408 | 31.344 | 33.9532 | 35.8518 | 34.2266 | 38.5421 | 36.1998 | 34.7753 | 34.2657 | 36.1215 | 33.9022 | 35.2681 | 33.8764 | 35.219 | 34.2059 | 35.7555 | 35.3215 | 35.8607 | 37.1758 | 35.2446 | 36.433 | 37.5296 | 38.694 | 36.8861 | 38.2457 | 36.2166 | 38.3779 | 36.4816 | 38.4112 | 36.0043 | 37.573 | 37.0298 | 38.364 | 36.0897 | 39.0832 | 36.6207 | 38.7247 | 39.2893 | 92.0031 | 92.1115 | 92.4115
2022-09-07 21:48 | 3:24 | 24.4946 | 25.9266 | 29.0679 | 34.892 | 36.3828 | 33.3347 | 36.4364 | 32.6341 | 36.8224 | 34.8267 | 34.7921 | 38.398 | 32.6168 | 34.0809 | 35.4719 | 33.7855 | 33.6407 | 34.1861 | 34.2507 | 36.5995 | 31.8537 | 31.3659 | 34.0808 | 35.9724 | 34.286 | 38.5796 | 36.2648 | 34.9172 | 34.2317 | 36.2458 | 33.9759 | 35.3274 | 34.009 | 35.3073 | 34.2815 | 35.8303 | 35.3016 | 35.9564 | 37.2643 | 35.3026 | 36.4226 | 37.566 | 38.7892 | 36.9939 | 38.217 | 36.2624 | 38.469 | 36.5516 | 38.4583 | 36.1232 | 37.543 | 37.106 | 38.4121 | 36.2038 | 39.1529 | 36.7007 | 38.6443 | 39.2625 | 92.1226 | 92.2519 | 92.4889
2022-09-07 21:48 | 3:24 | 25.6296 | 27.3559 | 29.7954 | 35.204 | 36.4753 | 33.5061 | 36.6014 | 32.7699 | 36.8053 | 34.9867 | 34.7328 | 38.3339 | 32.8136 | 34.1526 | 35.5581 | 33.8211 | 33.8112 | 34.3035 | 34.3304 | 36.8431 | 32.0109 | 31.4145 | 34.236 | 36.0845 | 34.3739 | 38.7358 | 36.3396 | 35.0151 | 34.3495 | 36.4067 | 34.065 | 35.3791 | 34.0928 | 35.412 | 34.3383 | 35.9709 | 35.4654 | 36.0596 | 37.3616 | 35.361 | 36.5178 | 37.6258 | 38.8206 | 37.0526 | 38.249 | 36.3036 | 38.4975 | 36.6754 | 38.5475 | 36.1781 | 37.6509 | 37.1519 | 38.4987 | 36.2864 | 39.1131 | 36.7871 | 38.7755 | 39.3572 | 92.249 | 92.4009 | 92.5474
2022-09-07 21:48 | 3:24 | 26.5416 | 28.4845 | 30.2075 | 35.5451 | 36.513 | 33.6063 | 36.5975 | 32.9552 | 36.8492 | 35.0971 | 34.8499 | 38.35 | 32.9439 | 34.2856 | 35.6928 | 33.856 | 33.925 | 34.4078 | 34.4 | 36.9124 | 32.169 | 31.4439 | 34.3954 | 36.2019 | 34.4186 | 38.7178 | 36.3379 | 34.9871 | 34.3714 | 36.3852 | 34.1312 | 35.4579 | 34.227 | 35.5324 | 34.409 | 36.0276 | 35.5748 | 36.113 | 37.4995 | 35.4534 | 36.5812 | 37.6136 | 38.8711 | 37.1642 | 38.3052 | 36.3862 | 38.5366 | 36.7166 | 38.5617 | 36.2917 | 37.653 | 37.1903 | 38.5301 | 36.3878 | 39.2072 | 36.8546 | 38.7537 | 39.4199 | 92.2658 | 92.4778 | 92.5123
2022-09-07 21:49 | 3:25 | 27.3088 | 29.3507 | 30.5044 | 35.6838 | 36.4993 | 33.7878 | 36.625 | 33.0745 | 36.8628 | 35.173 | 34.9202 | 38.2823 | 33.0732 | 34.3139 | 35.6537 | 33.8893 | 34.0089 | 34.5575 | 34.4808 | 36.9107 | 32.3157 | 31.4869 | 34.5755 | 36.2963 | 34.4835 | 38.7917 | 36.433 | 35.1288 | 34.4082 | 36.4663 | 34.2048 | 35.4743 | 34.2936 | 35.6018 | 34.4652 | 36.0993 | 35.5654 | 36.2158 | 37.4093 | 35.4716 | 36.5577 | 37.6613 | 38.92 | 37.218 | 38.3231 | 36.3982 | 38.5808 | 36.7971 | 38.5892 | 36.3074 | 37.731 | 37.2865 | 38.5813 | 36.3953 | 39.16 | 36.9212 | 38.8206 | 39.4304 | 92.3558 | 92.5751 | 92.6126
2022-09-07 21:49 | 3:25 | 27.9415 | 30.0094 | 30.7267 | 35.7093 | 36.5544 | 33.8409 | 36.7505 | 33.2004 | 36.9352 | 35.1929 | 35.2261 | 38.3257 | 33.1185 | 34.4003 | 35.7067 | 33.9288 | 34.0942 | 34.5999 | 34.5693 | 37.002 | 32.4451 | 31.5189 | 34.7318 | 36.3569 | 34.5365 | 38.7929 | 36.4226 | 35.0563 | 34.4587 | 36.4552 | 34.2857 | 35.4523 | 34.3469 | 35.6324 | 34.5168 | 36.1127 | 35.5216 | 36.2219 | 37.4264 | 35.4907 | 36.7345 | 37.7287 | 38.938 | 37.3363 | 38.3959 | 36.455 | 38.6155 | 36.8788 | 38.7035 | 36.3749 | 37.7796 | 37.3575 | 38.518 | 36.3939 | 39.1873 | 36.9624 | 38.8836 | 39.4037 | 92.4675 | 92.6713 | 92.6525
2022-09-07 21:49 | 3:25 | 28.4304 | 30.4264 | 30.8798 | 35.8409 | 36.4854 | 34.0007 | 36.853 | 33.3924 | 36.9004 | 35.2238 | 35.2726 | 38.3297 | 33.2494 | 34.5019 | 35.7469 | 33.9562 | 34.1756 | 34.7047 | 34.576 | 37.0759 | 32.6127 | 31.5528 | 34.9194 | 36.4722 | 34.6211 | 38.8044 | 36.5178 | 35.0196 | 34.5321 | 36.5392 | 34.3493 | 35.5698 | 34.4661 | 35.742 | 34.6187 | 36.1123 | 35.6111 | 36.2483 | 37.4792 | 35.5419 | 36.7187 | 37.7717 | 39.0138 | 37.4243 | 38.4313 | 36.5303 | 38.6594 | 36.9932 | 38.7599 | 36.3941 | 37.8681 | 37.4217 | 38.597 | 36.4707 | 39.1644 | 37.0457 | 38.8894 | 39.4341 | 92.6136 | 92.7574 | 92.6864
2022-09-07 21:49 | 3:25 | 28.8163 | 30.7674 | 31.0437 | 35.9374 | 36.5294 | 34.0094 | 36.8591 | 33.4382 | 36.982 | 35.3039 | 35.3688 | 38.4726 | 33.3662 | 34.4947 | 35.8703 | 33.9887 | 34.2559 | 34.7636 | 34.6682 | 37.1036 | 32.7534 | 31.5672 | 35.0411 | 36.459 | 34.6903 | 38.9039 | 36.5812 | 35.0462 | 34.6302 | 36.5699 | 34.4284 | 35.6768 | 34.5611 | 35.783 | 34.6392 | 36.1443 | 35.7072 | 36.3369 | 37.5006 | 35.5775 | 36.6928 | 37.8485 | 39.0579 | 37.4771 | 38.599 | 36.535 | 38.651 | 37.0681 | 38.8005 | 36.4683 | 37.8841 | 37.4855 | 38.697 | 36.5318 | 39.1941 | 37.1079 | 38.9313 | 39.4448 | 92.6762 | 92.8931 | 92.7039
2022-09-07 21:49 | 3:25 | 29.1174 | 30.9818 | 31.1408 | 36.1092 | 36.4904 | 34.1176 | 36.9357 | 33.4885 | 36.9387 | 35.3427 | 35.3918 | 38.3321 | 33.4398 | 34.6336 | 35.9169 | 34.008 | 34.3821 | 34.8597 | 34.6746 | 37.1224 | 32.9066 | 31.5995 | 35.2081 | 36.6272 | 34.7232 | 38.9668 | 36.5577 | 35.1897 | 34.6086 | 36.6718 | 34.4909 | 35.6298 | 34.6178 | 35.837 | 34.68 | 36.2024 | 35.7512 | 36.3104 | 37.5688 | 35.6539 | 36.7664 | 37.9417 | 39.1159 | 37.5879 | 38.6053 | 36.5934 | 38.716 | 37.1395 | 38.86 | 36.5627 | 37.9445 | 37.5324 | 38.6963 | 36.472 | 39.2903 | 37.1615 | 38.8833 | 39.4531 | 92.8195 | 93.0084 | 92.8047
2022-09-07 21:49 | 3:25 | 29.4083 | 31.157 | 31.2561 | 36.1316 | 36.5594 | 34.1808 | 36.9006 | 33.5465 | 36.9577 | 35.3828 | 35.4246 | 38.3237 | 33.4958 | 34.6642 | 35.994 | 34.0453 | 34.4326 | 34.8943 | 34.7194 | 37.0505 | 33.0629 | 31.6105 | 35.3546 | 36.6872 | 34.8243 | 39.1 | 36.7345 | 35.1992 | 34.7146 | 36.7139 | 34.5748 | 35.6082 | 34.661 | 35.8715 | 34.7929 | 36.2826 | 35.7544 | 36.4052 | 37.6141 | 35.7022 | 36.7273 | 37.9533 | 39.1216 | 37.6607 | 38.6453 | 36.6372 | 38.7537 | 37.1955 | 38.9132 | 36.6001 | 37.9984 | 37.5527 | 38.6907 | 36.7168 | 39.3547 | 37.2268 | 39.0842 | 39.5077 | 92.967 | 93.1294 | 92.9844
2022-09-07 21:50 | 3:25 | 29.613 | 31.2688 | 31.3334 | 36.262 | 36.5798 | 34.2847 | 36.9396 | 33.5996 | 37.0014 | 35.5515 | 35.5815 | 38.437 | 33.5732 | 34.7047 | 36.049 | 34.0861 | 34.5173 | 34.8993 | 34.7335 | 37.1668 | 33.2213 | 31.6373 | 35.4918 | 36.6813 | 34.9079 | 39.1405 | 36.7187 | 35.2166 | 34.7105 | 36.7938 | 34.6823 | 35.6716 | 34.7511 | 35.9136 | 34.8655 | 36.2512 | 35.8226 | 36.4285 | 37.6172 | 35.7302 | 36.6637 | 38.0138 | 39.1941 | 37.7501 | 38.7095 | 36.7186 | 38.7773 | 37.2848 | 38.9702 | 36.6591 | 38.1238 | 37.6613 | 38.6485 | 36.7164 | 39.4164 | 37.3113 | 39.0911 | 39.5565 | 93.1587 | 93.3121 | 93.1226
2022-09-07 21:50 | 3:26 | 29.8163 | 31.3404 | 31.3989 | 36.2727 | 36.6053 | 34.4196 | 36.974 | 33.7804 | 37.0513 | 35.49 | 35.5983 | 38.475 | 33.6265 | 34.7815 | 35.9526 | 34.1337 | 34.5506 | 34.9744 | 34.8051 | 37.1938 | 33.3754 | 31.6347 | 35.6173 | 36.815 | 35.0053 | 39.159 | 36.6928 | 35.2022 | 34.8611 | 36.7711 | 34.7462 | 35.7953 | 34.7762 | 35.9582 | 34.9245 | 36.3488 | 35.8974 | 36.5074 | 37.6222 | 35.7753 | 36.7247 | 38.0853 | 39.1912 | 37.805 | 38.727 | 36.7992 | 38.7996 | 37.3688 | 39.0207 | 36.7104 | 38.1829 | 37.7207 | 38.7099 | 36.8219 | 39.3935 | 37.366 | 39.1769 | 39.6012 | 93.3561 | 93.4274 | 93.1088
2022-09-07 21:50 | 3:26 | 30.5894 | 26.1977 | 31.1552 | 36.2771 | 36.5712 | 34.3345 | 36.9165 | 33.7121 | 37.047 | 35.433 | 35.6396 | 38.3711 | 33.5894 | 34.7353 | 36.0733 | 34.1428 | 34.5536 | 34.9514 | 34.8755 | 37.2533 | 33.849 | 28.213 | 35.2209 | 36.7985 | 34.9456 | 39.233 | 36.7664 | 35.2398 | 34.8428 | 36.8147 | 34.6123 | 35.8084 | 34.8302 | 35.9866 | 34.8714 | 36.3444 | 35.9361 | 36.5067 | 37.5277 | 35.8175 | 36.817 | 38.0253 | 39.1314 | 37.6187 | 38.6045 | 36.7843 | 38.7465 | 37.1834 | 38.9477 | 36.6455 | 38.0351 | 37.6726 | 38.6377 | 36.7512 | 39.3969 | 37.2364 | 39.0222 | 39.5709 | 93.5392 | 93.6488 | 93.2547
2022-09-07 21:50 | 3:26 | 31.4525 | 31.2549 | 31.4107 | 36.27 | 36.6222 | 34.2772 | 36.9921 | 33.8323 | 37.0768 | 35.4763 | 35.8169 | 38.4584 | 33.6389 | 34.7896 | 35.9914 | 34.1683 | 34.6538 | 34.9435 | 34.8833 | 37.301 | 33.8375 | 30.4945 | 34.8802 | 36.9151 | 34.9284 | 39.0235 | 36.7273 | 35.2808 | 34.7589 | 36.7714 | 34.5958 | 35.8177 | 34.8508 | 36.0215 | 34.9186 | 36.3832 | 35.9842 | 36.6428 | 37.5225 | 35.8742 | 36.9582 | 38.0369 | 39.0845 | 37.5156 | 38.5944 | 36.7424 | 38.8272 | 37.1337 | 38.8905 | 36.5779 | 37.9892 | 37.6604 | 38.582 | 36.7565 | 39.3523 | 37.2124 | 39.0918 | 39.6003 | 93.7577 | 93.8131 | 93.5134
2022-09-07 21:50 | 3:26 | 32.417 | 31.8841 | 31.6095 | 36.2908 | 36.662 | 34.4478 | 37.0294 | 33.9733 | 37.1002 | 35.5325 | 35.8387 | 38.4558 | 33.7998 | 34.8677 | 36.0434 | 34.2565 | 34.6927 | 35.0573 | 34.9839 | 37.295 | 33.8961 | 31.4363 | 35.0197 | 36.8912 | 34.9866 | 38.934 | 36.6637 | 35.3207 | 34.7931 | 36.6435 | 34.688 | 35.7985 | 34.9389 | 36.043 | 34.9793 | 36.4058 | 36.0873 | 36.5989 | 37.6719 | 35.9437 | 36.9774 | 38.0048 | 39.1365 | 37.5693 | 38.57 | 36.8276 | 38.7954 | 37.1911 | 38.8555 | 36.5581 | 38.0285 | 37.6768 | 38.6632 | 36.8032 | 39.3732 | 37.2644 | 39.0867 | 39.5801 | 93.9446 | 94.0412 | 93.5712
2022-09-07 21:50 | 3:26 | 33.4218 | 31.8747 | 31.7767 | 36.5258 | 36.6928 | 34.5054 | 37.0781 | 33.985 | 37.1242 | 35.5476 | 35.905 | 38.4424 | 33.9002 | 34.9544 | 36.1042 | 34.3129 | 34.8109 | 35.1725 | 35.0468 | 37.3704 | 34.0985 | 31.6435 | 35.2664 | 37.0935 | 35.0835 | 39.1071 | 36.7247 | 35.3248 | 34.8324 | 36.8072 | 34.7915 | 35.89 | 35.0331 | 36.1129 | 35.0724 | 36.3588 | 36.1972 | 36.6596 | 37.741 | 36.021 | 37.041 | 38.0877 | 39.1553 | 37.6855 | 38.6984 | 36.8624 | 38.8386 | 37.2744 | 38.8679 | 36.6261 | 38.0934 | 37.7387 | 38.7544 | 36.874 | 39.4377 | 37.3521 | 39.0047 | 39.6709 | 94.178 | 94.1532 | 93.7035
2022-09-07 21:51 | 3:27 | 34.1296 | 31.8591 | 32.0202 | 36.5068 | 36.7201 | 34.4968 | 37.1803 | 34.0619 | 37.1523 | 35.6445 | 35.9334 | 38.4047 | 34.0152 | 35.0572 | 36.1462 | 34.3565 | 34.8611 | 35.217 | 35.1336 | 37.3161 | 34.4419 | 31.6938 | 35.5144 | 37.0437 | 35.1281 | 39.3334 | 36.817 | 35.4107 | 34.9516 | 36.9289 | 34.9254 | 35.8066 | 35.1189 | 36.1854 | 35.1251 | 36.4396 | 36.177 | 36.6339 | 37.6542 | 36.0709 | 37.0332 | 38.1461 | 39.2246 | 37.7502 | 38.7227 | 36.9259 | 38.8721 | 37.4042 | 38.9711 | 36.7123 | 38.1286 | 37.794 | 38.8654 | 36.96 | 39.5368 | 37.4602 | 39.0998 | 39.6774 | 94.3227 | 94.3436 | 93.7155
2022-09-07 21:51 | 3:27 | 34.732 | 31.8636 | 32.4353 | 36.6748 | 36.7156 | 34.6213 | 37.0852 | 34.1611 | 37.1932 | 35.6712 | 35.9648 | 38.4484 | 34.0488 | 35.1487 | 36.3239 | 34.4175 | 34.9427 | 35.295 | 35.2246 | 37.4098 | 34.7481 | 31.7438 | 35.7525 | 37.1207 | 35.2268 | 39.2877 | 36.9582 | 35.4133 | 35.0282 | 37.0304 | 35.0729 | 35.887 | 35.242 | 36.2738 | 35.2427 | 36.5037 | 36.2052 | 36.7338 | 37.7211 | 36.1182 | 37.1174 | 38.2351 | 39.2813 | 37.8721 | 38.8667 | 36.9918 | 39.0042 | 37.5006 | 39.036 | 36.8518 | 38.1801 | 37.8743 | 38.8885 | 36.9583 | 39.5817 | 37.5527 | 39.1774 | 39.9073 | 94.4192 | 94.4927 | 93.7242
2022-09-07 21:51 | 3:27 | 35.0947 | 31.8709 | 32.8348 | 36.7218 | 36.786 | 34.6713 | 37.2298 | 34.1645 | 37.2282 | 35.7199 | 36.0558 | 38.4592 | 34.1645 | 35.2265 | 36.3578 | 34.4985 | 35.0342 | 35.3544 | 35.2526 | 37.5422 | 35.001 | 31.7835 | 35.9475 | 37.2118 | 35.3314 | 39.3839 | 36.9774 | 35.5538 | 35.1146 | 37.095 | 35.2158 | 36.0099 | 35.2935 | 36.3594 | 35.3202 | 36.5574 | 36.2544 | 36.8226 | 37.7639 | 36.225 | 37.1558 | 38.2714 | 39.3134 | 37.9528 | 38.8506 | 36.9879 | 39.012 | 37.5917 | 39.1269 | 36.9443 | 38.2867 | 37.9385 | 38.9317 | 37.109 | 39.5535 | 37.6367 | 39.2805 | 39.7583 | 94.5367 | 94.6625 | 93.7587
2022-09-07 21:51 | 3:27 | 35.2159 | 31.8726 | 33.0794 | 36.7952 | 36.8057 | 34.6669 | 37.1854 | 34.2425 | 37.2547 | 35.8207 | 36.1444 | 38.5211 | 34.25 | 35.223 | 36.4553 | 34.5533 | 35.1116 | 35.3997 | 35.297 | 37.5449 | 35.1042 | 31.7685 | 36.086 | 37.3496 | 35.3861 | 39.4472 | 37.041 | 35.63 | 35.2478 | 37.0765 | 35.321 | 36.0423 | 35.3991 | 36.4178 | 35.415 | 36.6188 | 36.3558 | 36.9278 | 37.855 | 36.2752 | 37.2765 | 38.3509 | 39.4017 | 38.0481 | 38.9395 | 37.0804 | 39.0722 | 37.6878 | 39.1678 | 37.0272 | 38.3278 | 38.0211 | 38.9445 | 37.1899 | 39.5856 | 37.726 | 39.3216 | 39.7759 | 94.6725 | 94.7937 | 93.9808
2022-09-07 21:51 | 3:27 | 35.2747 | 31.8784 | 33.1818 | 36.841 | 36.8355 | 34.8191 | 37.3411 | 34.328 | 37.2731 | 35.8033 | 36.0905 | 38.45 | 34.3222 | 35.3285 | 36.4726 | 34.6213 | 35.2411 | 35.4642 | 35.3463 | 37.5848 | 35.138 | 31.8041 | 36.1661 | 37.3936 | 35.4386 | 39.2569 | 37.0332 | 35.7152 | 35.3632 | 37.1559 | 35.403 | 36.1424 | 35.508 | 36.4793 | 35.4757 | 36.635 | 36.4847 | 36.9337 | 37.9081 | 36.3388 | 37.3407 | 38.3698 | 39.4851 | 38.1761 | 39.0626 | 37.1421 | 39.1309 | 37.752 | 39.3218 | 37.0433 | 38.3791 | 38.062 | 38.9557 | 37.2122 | 39.6035 | 37.7635 | 39.4585 | 39.779 | 94.7798 | 94.9059 | 94.1494
2022-09-07 21:51 | 3:27 | 35.3537 | 31.8962 | 33.1971 | 36.88 | 36.8657 | 34.9328 | 37.3627 | 34.3937 | 37.3379 | 35.8591 | 36.2144 | 38.5932 | 34.4067 | 35.3876 | 36.4563 | 34.681 | 35.2668 | 35.5159 | 35.4273 | 37.5442 | 35.2538 | 31.8432 | 36.2651 | 37.518 | 35.5625 | 39.4882 | 37.1174 | 35.6906 | 35.3244 | 37.2255 | 35.4717 | 36.203 | 35.5703 | 36.5311 | 35.5425 | 36.7568 | 36.52 | 36.9709 | 37.9776 | 36.4157 | 37.3452 | 38.4521 | 39.5127 | 38.238 | 39.1463 | 37.1492 | 39.1415 | 37.8323 | 39.3278 | 37.1001 | 38.4375 | 38.1622 | 39.182 | 37.2914 | 39.7366 | 37.8278 | 39.3366 | 39.8921 | 94.7966 | 94.9354 | 94.1531
2022-09-07 21:52 | 3:27 | 35.5115 | 31.9138 | 33.265 | 36.9276 | 36.8853 | 34.9598 | 37.3523 | 34.4625 | 37.3662 | 35.9087 | 36.2943 | 38.591 | 34.4879 | 35.4946 | 36.6555 | 34.6989 | 35.3932 | 35.6015 | 35.4832 | 37.6204 | 35.3476 | 31.8122 | 36.3973 | 37.4493 | 35.5638 | 39.3953 | 37.1558 | 35.823 | 35.5199 | 37.2724 | 35.5857 | 36.3214 | 35.6276 | 36.6423 | 35.6828 | 36.7246 | 36.5166 | 37.0499 | 37.9132 | 36.4583 | 37.4037 | 38.514 | 39.5407 | 38.3348 | 39.2076 | 37.2281 | 39.209 | 37.926 | 39.4121 | 37.2242 | 38.4828 | 38.2161 | 39.0984 | 37.4432 | 39.687 | 37.9193 | 39.4342 | 39.8691 | 94.8742 | 94.9723 | 94.1908
2022-09-07 21:52 | 3:28 | 35.835 | 31.938 | 33.4113 | 37.115 | 36.9207 | 35.0346 | 37.3865 | 34.5246 | 37.3987 | 35.9906 | 36.3381 | 38.4753 | 34.5699 | 35.5224 | 36.6055 | 34.7777 | 35.3961 | 35.651 | 35.5398 | 37.754 | 35.5253 | 31.8474 | 36.5363 | 37.5702 | 35.7049 | 39.6675 | 37.2765 | 35.9057 | 35.4795 | 37.3661 | 35.664 | 36.3539 | 35.7251 | 36.6994 | 35.7896 | 36.8826 | 36.638 | 37.1018 | 38.0217 | 36.4863 | 37.5432 | 38.6104 | 39.5668 | 38.4139 | 39.2067 | 37.2997 | 39.3167 | 38.0048 | 39.4084 | 37.2659 | 38.5817 | 38.276 | 39.1623 | 37.4338 | 39.7647 | 38.0058 | 39.483 | 39.8977 | 94.8387 | 94.9973 | 94.1938
2022-09-07 21:52 | 3:28 | 35.9971 | 31.9599 | 33.59 | 37.1718 | 36.9264 | 35.1457 | 37.5127 | 34.6504 | 37.42 | 36.0886 | 36.4014 | 38.5321 | 34.6492 | 35.5433 | 36.6692 | 34.8275 | 35.4943 | 35.6943 | 35.6501 | 37.7214 | 35.6502 | 31.8622 | 36.6778 | 37.6944 | 35.787 | 39.5968 | 37.3407 | 35.9598 | 35.5987 | 37.3358 | 35.7681 | 36.4053 | 35.7826 | 36.7458 | 35.8477 | 36.9259 | 36.6867 | 37.1875 | 38.0398 | 36.6005 | 37.5325 | 38.6234 | 39.656 | 38.502 | 39.2514 | 37.3748 | 39.4026 | 38.0628 | 39.5233 | 37.2974 | 38.648 | 38.3631 | 39.226 | 37.4685 | 39.8115 | 38.0411 | 39.6324 | 40.0404 | 94.728 | 94.8842 | 94.0356
2022-09-07 21:52 | 3:28 | 36.1568 | 31.9892 | 33.753 | 37.2982 | 37.0037 | 35.1675 | 37.4948 | 34.6844 | 37.4667 | 36.1246 | 36.3747 | 38.5859 | 34.7744 | 35.658 | 36.7246 | 34.9103 | 35.5701 | 35.7263 | 35.6867 | 37.9038 | 35.8376 | 31.9044 | 36.8034 | 37.8653 | 35.839 | 39.7541 | 37.3452 | 35.9527 | 35.6674 | 37.3716 | 35.8347 | 36.5194 | 35.8643 | 36.8154 | 35.926 | 36.998 | 36.7263 | 37.2754 | 38.1279 | 36.6732 | 37.5904 | 38.6685 | 39.6636 | 38.5447 | 39.3051 | 37.4122 | 39.376 | 38.1361 | 39.5628 | 37.3855 | 38.6897 | 38.4265 | 39.2875 | 37.5645 | 39.7819 | 38.1284 | 39.6442 | 39.989 | 94.5364 | 94.6829 | 93.894
2022-09-07 21:52 | 3:28 | 36.3489 | 32.0359 | 33.9577 | 37.4466 | 37.0237 | 35.2747 | 37.5945 | 34.7637 | 37.5138 | 36.2692 | 36.4363 | 38.5933 | 34.8496 | 35.7187 | 36.7065 | 34.9857 | 35.6207 | 35.8601 | 35.742 | 37.9128 | 36.0165 | 31.9327 | 36.9517 | 37.8033 | 35.9303 | 39.7846 | 37.4037 | 36.0579 | 35.697 | 37.5504 | 35.9563 | 36.4432 | 35.935 | 36.9032 | 36.0129 | 37.0296 | 36.7377 | 37.34 | 38.1889 | 36.7352 | 37.6786 | 38.7541 | 39.7064 | 38.663 | 39.34 | 37.4656 | 39.4348 | 38.224 | 39.5605 | 37.4559 | 38.7488 | 38.4745 | 39.4099 | 37.5769 | 39.8398 | 38.1945 | 39.6534 | 39.9975 | 94.3438 | 94.4965 | 93.7882
2022-09-07 21:52 | 3:28 | 36.5778 | 32.0637 | 34.1412 | 37.4506 | 37.0567 | 35.3982 | 37.5727 | 34.9227 | 37.5303 | 36.2829 | 36.4891 | 38.6255 | 34.9445 | 35.8582 | 36.9067 | 35.06 | 35.7007 | 35.9278 | 35.8735 | 37.9334 | 36.3049 | 32.0386 | 37.1019 | 37.8373 | 36.0113 | 39.9154 | 37.5432 | 36.1135 | 35.8141 | 37.6515 | 36.0701 | 36.6022 | 36.0274 | 37.0258 | 36.102 | 37.0144 | 36.8113 | 37.3921 | 38.1637 | 36.793 | 37.7702 | 38.8202 | 39.7418 | 38.7133 | 39.4619 | 37.5406 | 39.4761 | 38.3075 | 39.6827 | 37.5462 | 38.7912 | 38.5579 | 39.435 | 37.6203 | 39.8698 | 38.2611 | 39.662 | 40.0476 | 94.0841 | 94.2783 | 93.5462
2022-09-07 21:53 | 3:29 | 36.7912 | 32.1021 | 34.329 | 37.5364 | 37.0932 | 35.541 | 37.7026 | 34.9991 | 37.6012 | 36.3388 | 36.5402 | 38.6846 | 35.0836 | 35.9391 | 36.9703 | 35.1419 | 35.7675 | 36.0341 | 35.9021 | 38.1226 | 36.5771 | 32.1079 | 37.258 | 37.9636 | 36.0518 | 39.932 | 37.5325 | 36.0883 | 36.0105 | 37.6865 | 36.1503 | 36.6515 | 36.0989 | 37.0864 | 36.2013 | 37.1583 | 36.8724 | 37.4954 | 38.2167 | 36.8713 | 37.8316 | 38.9346 | 39.8227 | 38.771 | 39.4985 | 37.601 | 39.5282 | 38.3897 | 39.7387 | 37.6322 | 38.8686 | 38.618 | 39.4241 | 37.7119 | 39.9151 | 38.3313 | 39.723 | 40.074 | 93.9263 | 94.0955 | 93.5584
2022-09-07 21:53 | 3:29 | 36.9479 | 32.1565 | 34.5123 | 37.7439 | 37.1261 | 35.6469 | 37.6317 | 35.1463 | 37.6306 | 36.4024 | 36.6275 | 38.7439 | 35.198 | 36.0119 | 37.0162 | 35.1767 | 35.8524 | 36.1035 | 35.9987 | 38.1892 | 36.901 | 32.3063 | 37.4247 | 38.0432 | 36.1532 | 39.8984 | 37.5904 | 36.2079 | 35.9971 | 37.7034 | 36.2825 | 36.795 | 36.2267 | 37.138 | 36.2939 | 37.1869 | 36.9421 | 37.5153 | 38.2244 | 36.9393 | 37.8873 | 38.9515 | 39.8419 | 38.8784 | 39.577 | 37.6743 | 39.5926 | 38.4642 | 39.8319 | 37.7245 | 38.9347 | 38.6842 | 39.5284 | 37.7458 | 39.9503 | 38.4173 | 39.7286 | 40.1759 | 93.7956 | 93.9923 | 93.4472
2022-09-07 21:53 | 3:29 | 37.1124 | 32.2585 | 34.6551 | 37.8171 | 37.1748 | 35.7774 | 37.6142 | 35.2251 | 37.6632 | 36.531 | 36.8352 | 38.8246 | 35.333 | 36.078 | 37.1705 | 35.306 | 35.984 | 36.1804 | 36.06 | 38.2585 | 37.1331 | 32.6314 | 37.6155 | 38.1403 | 36.2533 | 40.0104 | 37.6786 | 36.273 | 36.0398 | 37.7551 | 36.384 | 36.7026 | 36.296 | 37.2218 | 36.4094 | 37.2678 | 37.0693 | 37.5811 | 38.2321 | 36.9901 | 38.0153 | 39.0258 | 39.9007 | 38.9637 | 39.6856 | 37.7298 | 39.6447 | 38.548 | 39.8785 | 37.8182 | 38.987 | 38.7521 | 39.5485 | 37.8235 | 39.9673 | 38.4883 | 39.8291 | 40.2544 | 93.6765 | 93.8848 | 93.3616
2022-09-07 21:53 | 3:29 | 37.3351 | 32.4159 | 34.8589 | 37.8476 | 37.2422 | 35.8642 | 37.755 | 35.304 | 37.7036 | 36.5881 | 36.856 | 38.8542 | 35.4126 | 36.1639 | 37.1893 | 35.3249 | 36.0995 | 36.2709 | 36.1985 | 38.2544 | 37.3433 | 33.0834 | 37.8023 | 38.2549 | 36.324 | 40.1625 | 37.7702 | 36.3597 | 36.0522 | 37.8997 | 36.4925 | 36.7268 | 36.3938 | 37.3068 | 36.4712 | 37.3675 | 37.149 | 37.6518 | 38.3386 | 37.0546 | 38.0256 | 39.0925 | 39.912 | 39.052 | 39.7179 | 37.7934 | 39.6871 | 38.6177 | 39.9115 | 37.8611 | 39.0899 | 38.8191 | 39.6606 | 37.9558 | 40.0364 | 38.5657 | 39.9418 | 40.2414 | 93.5647 | 93.7957 | 93.2662
2022-09-07 21:53 | 3:29 | 37.5552 | 32.6013 | 35.1103 | 37.9728 | 37.3016 | 36.0169 | 37.7111 | 35.3989 | 37.7783 | 36.7116 | 37.0133 | 38.9465 | 35.4851 | 36.2679 | 37.3184 | 35.4431 | 36.2042 | 36.3673 | 36.2501 | 38.4539 | 37.5915 | 33.6481 | 37.9711 | 38.3747 | 36.4409 | 40.2881 | 37.8316 | 36.5166 | 36.2482 | 37.9177 | 36.5852 | 37.0061 | 36.4933 | 37.3748 | 36.5694 | 37.4348 | 37.1988 | 37.7216 | 38.4237 | 37.1444 | 38.1161 | 39.1131 | 40.0037 | 39.1527 | 39.7561 | 37.8609 | 39.7705 | 38.7121 | 39.9997 | 37.9143 | 39.0979 | 38.8895 | 39.6828 | 38.0686 | 40.0896 | 38.6396 | 40.0092 | 40.3421 | 93.5071 | 93.6938 | 93.282
2022-09-07 21:53 | 3:29 | 37.7623 | 32.8022 | 35.323 | 38.0042 | 37.3389 | 36.0286 | 37.9512 | 35.5573 | 37.834 | 36.8154 | 37.1002 | 38.8881 | 35.6275 | 36.3427 | 37.3565 | 35.5529 | 36.2886 | 36.4487 | 36.3464 | 38.504 | 37.8049 | 34.3113 | 38.1145 | 38.3711 | 36.5349 | 40.2152 | 37.8873 | 36.5579 | 36.3709 | 37.9555 | 36.6833 | 36.9339 | 36.6037 | 37.4344 | 36.6918 | 37.4753 | 37.2446 | 37.818 | 38.4509 | 37.2307 | 38.1906 | 39.2326 | 40.06 | 39.1983 | 39.7869 | 37.9394 | 39.8744 | 38.7622 | 40.0995 | 37.9771 | 39.194 | 38.9705 | 39.6501 | 38.1678 | 40.1857 | 38.6846 | 40.0504 | 40.3375 | 93.4773 | 93.5699 | 93.2319
2022-09-07 21:54 | 3:29 | 37.9349 | 33.0456 | 35.4947 | 38.1307 | 37.3813 | 36.1739 | 38.0687 | 35.6907 | 37.8679 | 36.8876 | 37.1292 | 38.8834 | 35.6949 | 36.4182 | 37.4836 | 35.592 | 36.3721 | 36.541 | 36.4205 | 38.4568 | 37.997 | 34.8276 | 38.2581 | 38.493 | 36.5985 | 40.3289 | 38.0153 | 36.5663 | 36.4293 | 38.1305 | 36.8032 | 37.0329 | 36.6962 | 37.5313 | 36.7637 | 37.5271 | 37.3093 | 37.8839 | 38.5789 | 37.3095 | 38.2056 | 39.2816 | 40.1041 | 39.2812 | 39.8306 | 37.9667 | 39.8434 | 38.8689 | 40.1493 | 38.0458 | 39.2682 | 39.0341 | 39.6568 | 38.2015 | 40.1956 | 38.7512 | 40.0489 | 40.422 | 93.4044 | 93.5514 | 93.2066
2022-09-07 21:54 | 3:30 | 38.0496 | 33.3269 | 35.6083 | 38.2343 | 37.4525 | 36.2426 | 37.9206 | 35.8249 | 37.9075 | 36.9713 | 37.2254 | 38.914 | 35.8022 | 36.5802 | 37.4198 | 35.6826 | 36.4998 | 36.6346 | 36.5334 | 38.5581 | 38.1337 | 35.2271 | 38.3848 | 38.5868 | 36.7115 | 40.3458 | 38.0256 | 36.6082 | 36.4346 | 38.1156 | 36.897 | 37.0937 | 36.7548 | 37.6183 | 36.8974 | 37.6184 | 37.3824 | 37.9361 | 38.6391 | 37.3832 | 38.291 | 39.3339 | 40.1434 | 39.3499 | 39.935 | 38.0382 | 39.9186 | 38.9252 | 40.2595 | 38.1068 | 39.2942 | 39.1024 | 39.8611 | 38.2432 | 40.2416 | 38.832 | 40.0473 | 40.4707 | 93.3456 | 93.4763 | 93.1771
2022-09-07 21:54 | 3:30 | 38.1444 | 33.7536 | 35.6979 | 38.318 | 37.5121 | 36.3832 | 38.0236 | 35.9546 | 37.9791 | 37.0423 | 37.2919 | 39.103 | 35.9193 | 36.6452 | 37.5456 | 35.7596 | 36.5712 | 36.6859 | 36.6136 | 38.6287 | 38.2728 | 35.5818 | 38.5185 | 38.6572 | 36.8033 | 40.3913 | 38.1161 | 36.7759 | 36.5511 | 38.2739 | 36.9741 | 37.1149 | 36.8499 | 37.7123 | 36.9554 | 37.6534 | 37.4496 | 38.0214 | 38.6038 | 37.4315 | 38.2021 | 39.4126 | 40.2114 | 39.4346 | 39.934 | 38.121 | 39.9814 | 39.0297 | 40.2442 | 38.1959 | 39.3787 | 39.1596 | 39.8365 | 38.3594 | 40.3584 | 38.8846 | 40.1196 | 40.5549 | 93.2442 | 93.439 | 93.1186
2022-09-07 21:54 | 3:30 | 38.2417 | 34.3575 | 35.8003 | 38.5083 | 37.5512 | 36.5251 | 38.1657 | 36.0577 | 38.0345 | 37.1343 | 37.4112 | 39.0874 | 36.0272 | 36.6966 | 37.6859 | 35.8145 | 36.6434 | 36.801 | 36.7007 | 38.7262 | 38.4431 | 35.9018 | 38.6376 | 38.7765 | 36.8673 | 40.4574 | 38.1906 | 36.8695 | 36.6297 | 38.2932 | 37.087 | 37.1705 | 36.9702 | 37.7668 | 37.0458 | 37.7614 | 37.5636 | 38.1228 | 38.7242 | 37.4641 | 38.0258 | 39.5027 | 40.2487 | 39.5123 | 40.0374 | 38.1431 | 40.0349 | 39.0876 | 40.2933 | 38.2292 | 39.4592 | 39.1938 | 39.9876 | 38.4643 | 40.3214 | 38.945 | 40.2209 | 40.5982 | 93.1979 | 93.3686 | 93.0894
2022-09-07 21:54 | 3:30 | 38.3647 | 34.8087 | 35.874 | 38.5448 | 37.6293 | 36.6185 | 38.181 | 36.1648 | 38.1162 | 37.2072 | 37.4689 | 39.0839 | 36.1234 | 36.8522 | 37.7303 | 35.9088 | 36.7173 | 36.8924 | 36.7494 | 38.8038 | 38.6085 | 36.2364 | 38.7544 | 38.8105 | 36.9652 | 40.6493 | 38.2056 | 36.8737 | 36.7641 | 38.398 | 37.1853 | 37.2347 | 37.0675 | 37.8761 | 37.1771 | 37.7456 | 37.6692 | 38.1822 | 38.7571 | 37.5319 | 37.8554 | 39.591 | 40.289 | 39.6119 | 40.1209 | 38.2524 | 40.0859 | 39.1697 | 40.3369 | 38.2693 | 39.5273 | 39.2751 | 39.9609 | 38.6043 | 40.3247 | 39.0421 | 40.2933 | 40.6303 | 93.1181 | 93.2635 | 93.0056
2022-09-07 21:54 | 3:30 | 35.1379 | 34.6116 | 35.5973 | 38.6955 | 37.6906 | 36.701 | 38.2343 | 36.2277 | 38.146 | 37.3219 | 37.4962 | 39.1066 | 36.1798 | 36.8149 | 37.7638 | 35.9977 | 36.7855 | 36.9039 | 36.8172 | 38.8627 | 36.6092 | 35.0793 | 37.8399 | 38.8555 | 36.9973 | 40.663 | 38.291 | 36.9539 | 36.8526 | 38.4623 | 36.9665 | 37.3272 | 37.0485 | 37.9007 | 37.1447 | 37.8307 | 37.6773 | 38.2329 | 38.8296 | 37.6232 | 37.741 | 39.5645 | 40.2859 | 39.5274 | 40.0983 | 38.2897 | 40.0804 | 39.0776 | 40.3056 | 38.3096 | 39.4673 | 39.276 | 39.9555 | 38.6279 | 40.359 | 38.9962 | 40.3103 | 40.7455 | 93.0384 | 93.1951 | 92.9706
2022-09-07 21:55 | 3:31 | 29.796 | 30.9775 | 33.1727 | 38.466 | 37.7334 | 36.5392 | 38.181 | 36.0532 | 38.1876 | 37.1874 | 37.4831 | 39.2211 | 35.99 | 36.6201 | 37.7418 | 36.0169 | 36.7295 | 36.6532 | 36.616 | 38.7847 | 35.9 | 30.4739 | 37.0262 | 38.7741 | 36.9277 | 40.5069 | 38.2021 | 36.8873 | 36.7306 | 38.2285 | 36.628 | 37.2538 | 36.9045 | 37.7345 | 37.0555 | 37.7486 | 37.6309 | 38.0968 | 38.7624 | 37.5965 | 37.6217 | 39.4989 | 40.1536 | 39.2793 | 39.9693 | 38.2656 | 40.0311 | 38.8237 | 40.2245 | 38.197 | 39.2337 | 39.1538 | 39.9798 | 38.4507 | 40.3569 | 38.8431 | 40.1279 | 40.6641 | 92.9873 | 93.0778 | 92.9095
2022-09-07 21:55 | 3:31 | 29.0078 | 29.731 | 31.9084 | 38.0042 | 37.7481 | 36.2632 | 38.1287 | 35.8535 | 38.1802 | 36.9902 | 37.3781 | 39.2091 | 35.7171 | 36.5044 | 37.7033 | 35.8919 | 36.5407 | 36.4971 | 36.497 | 38.655 | 34.0836 | 28.9376 | 34.7557 | 38.5278 | 36.6396 | 40.1766 | 38.0258 | 36.7371 | 36.4689 | 37.9487 | 35.956 | 37.1447 | 36.6712 | 37.5018 | 36.7672 | 37.6254 | 37.5812 | 37.9583 | 38.642 | 37.5217 | 37.5803 | 39.2269 | 40.0164 | 38.7831 | 39.5635 | 38.1221 | 39.8637 | 38.3433 | 39.9411 | 37.8544 | 38.9645 | 38.8834 | 39.846 | 38.2803 | 40.2765 | 38.51 | 39.9961 | 40.597 | 92.9002 | 93.0136 | 92.8986
Overall |  | minimum | 15.4849 | 17.2345 | 33.0335 | 36.2272 | 32.7267 | 35.9734 | 31.488 | 36.7511 | 34.2378 | 33.3642 | 37.9951 | 31.2037 | 33.3119 | 34.8893 | 33.5283 | 32.8779 | [5 empty] | 27.6829 | 34.9372 | 33.7178 | 37.2815 | 35.5048 | 34.6519 | 34.0283 | 35.4942 | 31.7589
|  | maximum | 34.8087 | 92.9165 | 38.7394 | 38.7186 | 36.766 | 38.4127 | 36.2277 | 38.5757 | 37.3405 | 37.7515 | 39.8014 | 36.2485 | 36.874 | 37.7878 | 36.0843 | 36.8492 |  |  |  |  | #REF! | 38.8425 | 38.8736 | 37.0367 | 40.663 | 38.3157 | 36.9941 | 36.9201 | 38.4914 | 37.2264
|  | average | 27.6442 | 35.0141 | 36.3415 | 37.4629 | 34.8733 | 37.5681 | 34.3772 | 37.7495 | 35.9486 | 36.1954 | 38.9295 | 34.1906 | 35.3369 | 36.6174 | 35.0363 | 35.1799 |  |  |  |  | #REF! | 33.6074 | 36.8805 | 35.2648 | 39.0447 | 36.8755 | 35.8022 | 35.2999 | 36.9028 | 34.5008
3 | average | 24.6595 | 26.2979 | 28.1235 | 36.6466 | 38.6638 | 35.5134 | 38.3571 | 35.2783 | 38.5646 | 36.5835 | 37.1884 | 39.6016 | 34.8716 | 35.9431 | 37.3328 | 35.9333 | 35.9143 |  |  |  |  | #REF! | 29.2224 | 36.7286 | 35.5507 | 38.631 | 36.9523 | 36.3077 | 35.7225 | 36.828 | 33.4398
2 | average | 23.6721 | 25.2031 | 26.9843 | 36.1309 | 38.668 | 35.252 | 38.1985 | 34.9794 | 38.5385 | 36.2335 | 36.8783 | 39.5661 | 34.4973 | 35.7043 | 37.1285 | 35.8227 | 35.5994 |  |  |  |  | #REF! | 30.3442 | 36.3978 | 35.2019 | 38.4422 | 36.6757 | 36.2012 | 35.4889 | 36.6199 | 33.401
1 | average | 27.6252 | 29.68 | 30.6156 | 35.6966 | 36.5268 | 33.8143 | 36.6877 | 33.1374 | 36.899 | 35.183 | 35.0731 | 38.304 | 33.0958 | 34.3571 | 35.6802 | 33.9091 | 34.0516 |  |  |  |  | #REF! | 34.6537 | 36.3266 | 34.51 | 38.7923 | 36.4278 | 35.0925 | 34.4334 | 36.4608 | 34.2452
Overall |  | minimum | 0 | 17.2345 | 32.8472 | 36.2272 | 32.4475 | 35.7988 | 30.9554 | [6 empty] | 34.5506 | [7 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 0 | 0 | 0 | 0
|  | maximum | 0 | 92.9165 | 46.01 | 49.446 | 46.2682 | 50.3162 | 44.3461 | [6 empty] | 47.7973 | [7 empty] | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 0 | 0 | 0 | 0
|  | average | #DIV/0! | 28.5696 | 36.9955 | 38.8568 | 35.9805 | 39.0087 | 35.163 | [6 empty] | 37.5187 | [7 empty] | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Evaporators
3 |  | average | #DIV/0! | 35.0305 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! | [7 empty] | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2 |  | average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! | [7 empty] | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1 |  | average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [6 empty] | #DIV/0! | [7 empty] | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
<<< Do not use averages for these cells >>>

## T2 Chart
Evaporator Temperatures

## T3
Time |  | Ch 101 (F) | Ch 102 (F) | Ch 103 (F) | Ch 104 (F) | Ch 105 (F) | Ch 106 (F) | Ch 107 (F) | Ch 108 (F) | Ch 109 (F) | Ch 110 (F) | Ch 111 (F) | Ch 112 (F) | Ch 113 (F) | Ch 114 (F) | Ch 115 (F) | Ch 116 (F) | Ch 117 (F) | Ch 118 (F) | Ch 119 (F) | Ch 120 (F) | Ch 201 (F) | Ch 202 (F) | Ch 203 (F) | Ch 204 (F) | Ch 205 (F) | Ch 206 (F) | Ch 207 (F) | Ch 208 (F) | Ch 209 (F) | Ch 210 (F) | Ch 211 (F) | Ch 212 (F) | Ch 213 (F) | Ch 214 (F) | Ch 215 (F) | Ch 216 (F) | Ch 217 (F) | Ch 218 (F) | Ch 219 (F) | Ch 220 (F) | Ch 301 (F) | Ch 302 (F) | Ch 304 (F) | Ch 305 (F) | Ch 306 (F) | Ch 307 (F) | Ch 308 (F) | Ch 309 (F) | Ch 310 (F) | Ch 311 (F) | Ch 312 (F) | Ch 313 (F) | Ch 314 (F) | Ch 315 (F) | Ch 316 (F) | Ch 317 (F) | Ch 318 (F) | Ch 320 (F) | Ambient L | Ambient Right | Ambient Left
2022-09-07 21:50 | 0:00 | 31.4525 | 31.2549 | 31.4107 | 36.27 | 36.6222 | 34.2772 | 36.9921 | 33.8323 | 37.0768 | 35.4763 | 35.8169 | 38.4584 | 33.6389 | 34.7896 | 35.9914 | 34.1683 | 34.6538 | 34.9435 | 34.8833 | 37.301 | 33.8375 | 30.4945 | 34.8802 | 36.9151 | 34.9284 | 39.0235 | 36.7273 | 35.2808 | 34.7589 | 36.7714 | 34.5958 | 35.8177 | 34.8508 | 36.0215 | 34.9186 | 36.3832 | 35.9842 | 36.6428 | 37.5225 | 35.8742 | 36.9582 | 38.0369 | 39.0845 | 37.5156 | 38.5944 | 36.7424 | 38.8272 | 37.1337 | 38.8905 | 36.5779 | 37.9892 | 37.6604 | 38.582 | 36.7565 | 39.3523 | 37.2124 | 39.0918 | 39.6003 | 93.7577 | 93.8131 | 93.5134
2022-09-07 21:50 | 0:00 | 32.417 | 31.8841 | 31.6095 | 36.2908 | 36.662 | 34.4478 | 37.0294 | 33.9733 | 37.1002 | 35.5325 | 35.8387 | 38.4558 | 33.7998 | 34.8677 | 36.0434 | 34.2565 | 34.6927 | 35.0573 | 34.9839 | 37.295 | 33.8961 | 31.4363 | 35.0197 | 36.8912 | 34.9866 | 38.934 | 36.6637 | 35.3207 | 34.7931 | 36.6435 | 34.688 | 35.7985 | 34.9389 | 36.043 | 34.9793 | 36.4058 | 36.0873 | 36.5989 | 37.6719 | 35.9437 | 36.9774 | 38.0048 | 39.1365 | 37.5693 | 38.57 | 36.8276 | 38.7954 | 37.1911 | 38.8555 | 36.5581 | 38.0285 | 37.6768 | 38.6632 | 36.8032 | 39.3732 | 37.2644 | 39.0867 | 39.5801 | 93.9446 | 94.0412 | 93.5712
2022-09-07 21:50 | 0:00 | 33.4218 | 31.8747 | 31.7767 | 36.5258 | 36.6928 | 34.5054 | 37.0781 | 33.985 | 37.1242 | 35.5476 | 35.905 | 38.4424 | 33.9002 | 34.9544 | 36.1042 | 34.3129 | 34.8109 | 35.1725 | 35.0468 | 37.3704 | 34.0985 | 31.6435 | 35.2664 | 37.0935 | 35.0835 | 39.1071 | 36.7247 | 35.3248 | 34.8324 | 36.8072 | 34.7915 | 35.89 | 35.0331 | 36.1129 | 35.0724 | 36.3588 | 36.1972 | 36.6596 | 37.741 | 36.021 | 37.041 | 38.0877 | 39.1553 | 37.6855 | 38.6984 | 36.8624 | 38.8386 | 37.2744 | 38.8679 | 36.6261 | 38.0934 | 37.7387 | 38.7544 | 36.874 | 39.4377 | 37.3521 | 39.0047 | 39.6709 | 94.178 | 94.1532 | 93.7035
2022-09-07 21:51 | 0:00 | 34.1296 | 31.8591 | 32.0202 | 36.5068 | 36.7201 | 34.4968 | 37.1803 | 34.0619 | 37.1523 | 35.6445 | 35.9334 | 38.4047 | 34.0152 | 35.0572 | 36.1462 | 34.3565 | 34.8611 | 35.217 | 35.1336 | 37.3161 | 34.4419 | 31.6938 | 35.5144 | 37.0437 | 35.1281 | 39.3334 | 36.817 | 35.4107 | 34.9516 | 36.9289 | 34.9254 | 35.8066 | 35.1189 | 36.1854 | 35.1251 | 36.4396 | 36.177 | 36.6339 | 37.6542 | 36.0709 | 37.0332 | 38.1461 | 39.2246 | 37.7502 | 38.7227 | 36.9259 | 38.8721 | 37.4042 | 38.9711 | 36.7123 | 38.1286 | 37.794 | 38.8654 | 36.96 | 39.5368 | 37.4602 | 39.0998 | 39.6774 | 94.3227 | 94.3436 | 93.7155
2022-09-07 21:51 | 0:01 | 34.732 | 31.8636 | 32.4353 | 36.6748 | 36.7156 | 34.6213 | 37.0852 | 34.1611 | 37.1932 | 35.6712 | 35.9648 | 38.4484 | 34.0488 | 35.1487 | 36.3239 | 34.4175 | 34.9427 | 35.295 | 35.2246 | 37.4098 | 34.7481 | 31.7438 | 35.7525 | 37.1207 | 35.2268 | 39.2877 | 36.9582 | 35.4133 | 35.0282 | 37.0304 | 35.0729 | 35.887 | 35.242 | 36.2738 | 35.2427 | 36.5037 | 36.2052 | 36.7338 | 37.7211 | 36.1182 | 37.1174 | 38.2351 | 39.2813 | 37.8721 | 38.8667 | 36.9918 | 39.0042 | 37.5006 | 39.036 | 36.8518 | 38.1801 | 37.8743 | 38.8885 | 36.9583 | 39.5817 | 37.5527 | 39.1774 | 39.9073 | 94.4192 | 94.4927 | 93.7242
2022-09-07 21:51 | 0:01 | 35.0947 | 31.8709 | 32.8348 | 36.7218 | 36.786 | 34.6713 | 37.2298 | 34.1645 | 37.2282 | 35.7199 | 36.0558 | 38.4592 | 34.1645 | 35.2265 | 36.3578 | 34.4985 | 35.0342 | 35.3544 | 35.2526 | 37.5422 | 35.001 | 31.7835 | 35.9475 | 37.2118 | 35.3314 | 39.3839 | 36.9774 | 35.5538 | 35.1146 | 37.095 | 35.2158 | 36.0099 | 35.2935 | 36.3594 | 35.3202 | 36.5574 | 36.2544 | 36.8226 | 37.7639 | 36.225 | 37.1558 | 38.2714 | 39.3134 | 37.9528 | 38.8506 | 36.9879 | 39.012 | 37.5917 | 39.1269 | 36.9443 | 38.2867 | 37.9385 | 38.9317 | 37.109 | 39.5535 | 37.6367 | 39.2805 | 39.7583 | 94.5367 | 94.6625 | 93.7587
2022-09-07 21:51 | 0:01 | 35.2159 | 31.8726 | 33.0794 | 36.7952 | 36.8057 | 34.6669 | 37.1854 | 34.2425 | 37.2547 | 35.8207 | 36.1444 | 38.5211 | 34.25 | 35.223 | 36.4553 | 34.5533 | 35.1116 | 35.3997 | 35.297 | 37.5449 | 35.1042 | 31.7685 | 36.086 | 37.3496 | 35.3861 | 39.4472 | 37.041 | 35.63 | 35.2478 | 37.0765 | 35.321 | 36.0423 | 35.3991 | 36.4178 | 35.415 | 36.6188 | 36.3558 | 36.9278 | 37.855 | 36.2752 | 37.2765 | 38.3509 | 39.4017 | 38.0481 | 38.9395 | 37.0804 | 39.0722 | 37.6878 | 39.1678 | 37.0272 | 38.3278 | 38.0211 | 38.9445 | 37.1899 | 39.5856 | 37.726 | 39.3216 | 39.7759 | 94.6725 | 94.7937 | 93.9808
2022-09-07 21:51 | 0:01 | 35.2747 | 31.8784 | 33.1818 | 36.841 | 36.8355 | 34.8191 | 37.3411 | 34.328 | 37.2731 | 35.8033 | 36.0905 | 38.45 | 34.3222 | 35.3285 | 36.4726 | 34.6213 | 35.2411 | 35.4642 | 35.3463 | 37.5848 | 35.138 | 31.8041 | 36.1661 | 37.3936 | 35.4386 | 39.2569 | 37.0332 | 35.7152 | 35.3632 | 37.1559 | 35.403 | 36.1424 | 35.508 | 36.4793 | 35.4757 | 36.635 | 36.4847 | 36.9337 | 37.9081 | 36.3388 | 37.3407 | 38.3698 | 39.4851 | 38.1761 | 39.0626 | 37.1421 | 39.1309 | 37.752 | 39.3218 | 37.0433 | 38.3791 | 38.062 | 38.9557 | 37.2122 | 39.6035 | 37.7635 | 39.4585 | 39.779 | 94.7798 | 94.9059 | 94.1494
2022-09-07 21:51 | 0:01 | 35.3537 | 31.8962 | 33.1971 | 36.88 | 36.8657 | 34.9328 | 37.3627 | 34.3937 | 37.3379 | 35.8591 | 36.2144 | 38.5932 | 34.4067 | 35.3876 | 36.4563 | 34.681 | 35.2668 | 35.5159 | 35.4273 | 37.5442 | 35.2538 | 31.8432 | 36.2651 | 37.518 | 35.5625 | 39.4882 | 37.1174 | 35.6906 | 35.3244 | 37.2255 | 35.4717 | 36.203 | 35.5703 | 36.5311 | 35.5425 | 36.7568 | 36.52 | 36.9709 | 37.9776 | 36.4157 | 37.3452 | 38.4521 | 39.5127 | 38.238 | 39.1463 | 37.1492 | 39.1415 | 37.8323 | 39.3278 | 37.1001 | 38.4375 | 38.1622 | 39.182 | 37.2914 | 39.7366 | 37.8278 | 39.3366 | 39.8921 | 94.7966 | 94.9354 | 94.1531
2022-09-07 21:52 | 0:02 | 35.5115 | 31.9138 | 33.265 | 36.9276 | 36.8853 | 34.9598 | 37.3523 | 34.4625 | 37.3662 | 35.9087 | 36.2943 | 38.591 | 34.4879 | 35.4946 | 36.6555 | 34.6989 | 35.3932 | 35.6015 | 35.4832 | 37.6204 | 35.3476 | 31.8122 | 36.3973 | 37.4493 | 35.5638 | 39.3953 | 37.1558 | 35.823 | 35.5199 | 37.2724 | 35.5857 | 36.3214 | 35.6276 | 36.6423 | 35.6828 | 36.7246 | 36.5166 | 37.0499 | 37.9132 | 36.4583 | 37.4037 | 38.514 | 39.5407 | 38.3348 | 39.2076 | 37.2281 | 39.209 | 37.926 | 39.4121 | 37.2242 | 38.4828 | 38.2161 | 39.0984 | 37.4432 | 39.687 | 37.9193 | 39.4342 | 39.8691 | 94.8742 | 94.9723 | 94.1908
2022-09-07 21:52 | 0:02 | 35.835 | 31.938 | 33.4113 | 37.115 | 36.9207 | 35.0346 | 37.3865 | 34.5246 | 37.3987 | 35.9906 | 36.3381 | 38.4753 | 34.5699 | 35.5224 | 36.6055 | 34.7777 | 35.3961 | 35.651 | 35.5398 | 37.754 | 35.5253 | 31.8474 | 36.5363 | 37.5702 | 35.7049 | 39.6675 | 37.2765 | 35.9057 | 35.4795 | 37.3661 | 35.664 | 36.3539 | 35.7251 | 36.6994 | 35.7896 | 36.8826 | 36.638 | 37.1018 | 38.0217 | 36.4863 | 37.5432 | 38.6104 | 39.5668 | 38.4139 | 39.2067 | 37.2997 | 39.3167 | 38.0048 | 39.4084 | 37.2659 | 38.5817 | 38.276 | 39.1623 | 37.4338 | 39.7647 | 38.0058 | 39.483 | 39.8977 | 94.8387 | 94.9973 | 94.1938
2022-09-07 21:52 | 0:02 | 35.9971 | 31.9599 | 33.59 | 37.1718 | 36.9264 | 35.1457 | 37.5127 | 34.6504 | 37.42 | 36.0886 | 36.4014 | 38.5321 | 34.6492 | 35.5433 | 36.6692 | 34.8275 | 35.4943 | 35.6943 | 35.6501 | 37.7214 | 35.6502 | 31.8622 | 36.6778 | 37.6944 | 35.787 | 39.5968 | 37.3407 | 35.9598 | 35.5987 | 37.3358 | 35.7681 | 36.4053 | 35.7826 | 36.7458 | 35.8477 | 36.9259 | 36.6867 | 37.1875 | 38.0398 | 36.6005 | 37.5325 | 38.6234 | 39.656 | 38.502 | 39.2514 | 37.3748 | 39.4026 | 38.0628 | 39.5233 | 37.2974 | 38.648 | 38.3631 | 39.226 | 37.4685 | 39.8115 | 38.0411 | 39.6324 | 40.0404 | 94.728 | 94.8842 | 94.0356
2022-09-07 21:52 | 0:02 | 36.1568 | 31.9892 | 33.753 | 37.2982 | 37.0037 | 35.1675 | 37.4948 | 34.6844 | 37.4667 | 36.1246 | 36.3747 | 38.5859 | 34.7744 | 35.658 | 36.7246 | 34.9103 | 35.5701 | 35.7263 | 35.6867 | 37.9038 | 35.8376 | 31.9044 | 36.8034 | 37.8653 | 35.839 | 39.7541 | 37.3452 | 35.9527 | 35.6674 | 37.3716 | 35.8347 | 36.5194 | 35.8643 | 36.8154 | 35.926 | 36.998 | 36.7263 | 37.2754 | 38.1279 | 36.6732 | 37.5904 | 38.6685 | 39.6636 | 38.5447 | 39.3051 | 37.4122 | 39.376 | 38.1361 | 39.5628 | 37.3855 | 38.6897 | 38.4265 | 39.2875 | 37.5645 | 39.7819 | 38.1284 | 39.6442 | 39.989 | 94.5364 | 94.6829 | 93.894
2022-09-07 21:52 | 0:02 | 36.3489 | 32.0359 | 33.9577 | 37.4466 | 37.0237 | 35.2747 | 37.5945 | 34.7637 | 37.5138 | 36.2692 | 36.4363 | 38.5933 | 34.8496 | 35.7187 | 36.7065 | 34.9857 | 35.6207 | 35.8601 | 35.742 | 37.9128 | 36.0165 | 31.9327 | 36.9517 | 37.8033 | 35.9303 | 39.7846 | 37.4037 | 36.0579 | 35.697 | 37.5504 | 35.9563 | 36.4432 | 35.935 | 36.9032 | 36.0129 | 37.0296 | 36.7377 | 37.34 | 38.1889 | 36.7352 | 37.6786 | 38.7541 | 39.7064 | 38.663 | 39.34 | 37.4656 | 39.4348 | 38.224 | 39.5605 | 37.4559 | 38.7488 | 38.4745 | 39.4099 | 37.5769 | 39.8398 | 38.1945 | 39.6534 | 39.9975 | 94.3438 | 94.4965 | 93.7882
2022-09-07 21:52 | 0:02 | 36.5778 | 32.0637 | 34.1412 | 37.4506 | 37.0567 | 35.3982 | 37.5727 | 34.9227 | 37.5303 | 36.2829 | 36.4891 | 38.6255 | 34.9445 | 35.8582 | 36.9067 | 35.06 | 35.7007 | 35.9278 | 35.8735 | 37.9334 | 36.3049 | 32.0386 | 37.1019 | 37.8373 | 36.0113 | 39.9154 | 37.5432 | 36.1135 | 35.8141 | 37.6515 | 36.0701 | 36.6022 | 36.0274 | 37.0258 | 36.102 | 37.0144 | 36.8113 | 37.3921 | 38.1637 | 36.793 | 37.7702 | 38.8202 | 39.7418 | 38.7133 | 39.4619 | 37.5406 | 39.4761 | 38.3075 | 39.6827 | 37.5462 | 38.7912 | 38.5579 | 39.435 | 37.6203 | 39.8698 | 38.2611 | 39.662 | 40.0476 | 94.0841 | 94.2783 | 93.5462
2022-09-07 21:53 | 0:02 | 36.7912 | 32.1021 | 34.329 | 37.5364 | 37.0932 | 35.541 | 37.7026 | 34.9991 | 37.6012 | 36.3388 | 36.5402 | 38.6846 | 35.0836 | 35.9391 | 36.9703 | 35.1419 | 35.7675 | 36.0341 | 35.9021 | 38.1226 | 36.5771 | 32.1079 | 37.258 | 37.9636 | 36.0518 | 39.932 | 37.5325 | 36.0883 | 36.0105 | 37.6865 | 36.1503 | 36.6515 | 36.0989 | 37.0864 | 36.2013 | 37.1583 | 36.8724 | 37.4954 | 38.2167 | 36.8713 | 37.8316 | 38.9346 | 39.8227 | 38.771 | 39.4985 | 37.601 | 39.5282 | 38.3897 | 39.7387 | 37.6322 | 38.8686 | 38.618 | 39.4241 | 37.7119 | 39.9151 | 38.3313 | 39.723 | 40.074 | 93.9263 | 94.0955 | 93.5584
2022-09-07 21:53 | 0:03 | 36.9479 | 32.1565 | 34.5123 | 37.7439 | 37.1261 | 35.6469 | 37.6317 | 35.1463 | 37.6306 | 36.4024 | 36.6275 | 38.7439 | 35.198 | 36.0119 | 37.0162 | 35.1767 | 35.8524 | 36.1035 | 35.9987 | 38.1892 | 36.901 | 32.3063 | 37.4247 | 38.0432 | 36.1532 | 39.8984 | 37.5904 | 36.2079 | 35.9971 | 37.7034 | 36.2825 | 36.795 | 36.2267 | 37.138 | 36.2939 | 37.1869 | 36.9421 | 37.5153 | 38.2244 | 36.9393 | 37.8873 | 38.9515 | 39.8419 | 38.8784 | 39.577 | 37.6743 | 39.5926 | 38.4642 | 39.8319 | 37.7245 | 38.9347 | 38.6842 | 39.5284 | 37.7458 | 39.9503 | 38.4173 | 39.7286 | 40.1759 | 93.7956 | 93.9923 | 93.4472
2022-09-07 21:53 | 0:03 | 37.1124 | 32.2585 | 34.6551 | 37.8171 | 37.1748 | 35.7774 | 37.6142 | 35.2251 | 37.6632 | 36.531 | 36.8352 | 38.8246 | 35.333 | 36.078 | 37.1705 | 35.306 | 35.984 | 36.1804 | 36.06 | 38.2585 | 37.1331 | 32.6314 | 37.6155 | 38.1403 | 36.2533 | 40.0104 | 37.6786 | 36.273 | 36.0398 | 37.7551 | 36.384 | 36.7026 | 36.296 | 37.2218 | 36.4094 | 37.2678 | 37.0693 | 37.5811 | 38.2321 | 36.9901 | 38.0153 | 39.0258 | 39.9007 | 38.9637 | 39.6856 | 37.7298 | 39.6447 | 38.548 | 39.8785 | 37.8182 | 38.987 | 38.7521 | 39.5485 | 37.8235 | 39.9673 | 38.4883 | 39.8291 | 40.2544 | 93.6765 | 93.8848 | 93.3616
2022-09-07 21:53 | 0:03 | 37.3351 | 32.4159 | 34.8589 | 37.8476 | 37.2422 | 35.8642 | 37.755 | 35.304 | 37.7036 | 36.5881 | 36.856 | 38.8542 | 35.4126 | 36.1639 | 37.1893 | 35.3249 | 36.0995 | 36.2709 | 36.1985 | 38.2544 | 37.3433 | 33.0834 | 37.8023 | 38.2549 | 36.324 | 40.1625 | 37.7702 | 36.3597 | 36.0522 | 37.8997 | 36.4925 | 36.7268 | 36.3938 | 37.3068 | 36.4712 | 37.3675 | 37.149 | 37.6518 | 38.3386 | 37.0546 | 38.0256 | 39.0925 | 39.912 | 39.052 | 39.7179 | 37.7934 | 39.6871 | 38.6177 | 39.9115 | 37.8611 | 39.0899 | 38.8191 | 39.6606 | 37.9558 | 40.0364 | 38.5657 | 39.9418 | 40.2414 | 93.5647 | 93.7957 | 93.2662
2022-09-07 21:53 | 0:03 | 37.5552 | 32.6013 | 35.1103 | 37.9728 | 37.3016 | 36.0169 | 37.7111 | 35.3989 | 37.7783 | 36.7116 | 37.0133 | 38.9465 | 35.4851 | 36.2679 | 37.3184 | 35.4431 | 36.2042 | 36.3673 | 36.2501 | 38.4539 | 37.5915 | 33.6481 | 37.9711 | 38.3747 | 36.4409 | 40.2881 | 37.8316 | 36.5166 | 36.2482 | 37.9177 | 36.5852 | 37.0061 | 36.4933 | 37.3748 | 36.5694 | 37.4348 | 37.1988 | 37.7216 | 38.4237 | 37.1444 | 38.1161 | 39.1131 | 40.0037 | 39.1527 | 39.7561 | 37.8609 | 39.7705 | 38.7121 | 39.9997 | 37.9143 | 39.0979 | 38.8895 | 39.6828 | 38.0686 | 40.0896 | 38.6396 | 40.0092 | 40.3421 | 93.5071 | 93.6938 | 93.282
2022-09-07 21:53 | 0:03 | 37.7623 | 32.8022 | 35.323 | 38.0042 | 37.3389 | 36.0286 | 37.9512 | 35.5573 | 37.834 | 36.8154 | 37.1002 | 38.8881 | 35.6275 | 36.3427 | 37.3565 | 35.5529 | 36.2886 | 36.4487 | 36.3464 | 38.504 | 37.8049 | 34.3113 | 38.1145 | 38.3711 | 36.5349 | 40.2152 | 37.8873 | 36.5579 | 36.3709 | 37.9555 | 36.6833 | 36.9339 | 36.6037 | 37.4344 | 36.6918 | 37.4753 | 37.2446 | 37.818 | 38.4509 | 37.2307 | 38.1906 | 39.2326 | 40.06 | 39.1983 | 39.7869 | 37.9394 | 39.8744 | 38.7622 | 40.0995 | 37.9771 | 39.194 | 38.9705 | 39.6501 | 38.1678 | 40.1857 | 38.6846 | 40.0504 | 40.3375 | 93.4773 | 93.5699 | 93.2319
2022-09-07 21:54 | 0:04 | 37.9349 | 33.0456 | 35.4947 | 38.1307 | 37.3813 | 36.1739 | 38.0687 | 35.6907 | 37.8679 | 36.8876 | 37.1292 | 38.8834 | 35.6949 | 36.4182 | 37.4836 | 35.592 | 36.3721 | 36.541 | 36.4205 | 38.4568 | 37.997 | 34.8276 | 38.2581 | 38.493 | 36.5985 | 40.3289 | 38.0153 | 36.5663 | 36.4293 | 38.1305 | 36.8032 | 37.0329 | 36.6962 | 37.5313 | 36.7637 | 37.5271 | 37.3093 | 37.8839 | 38.5789 | 37.3095 | 38.2056 | 39.2816 | 40.1041 | 39.2812 | 39.8306 | 37.9667 | 39.8434 | 38.8689 | 40.1493 | 38.0458 | 39.2682 | 39.0341 | 39.6568 | 38.2015 | 40.1956 | 38.7512 | 40.0489 | 40.422 | 93.4044 | 93.5514 | 93.2066
2022-09-07 21:54 | 0:04 | 38.0496 | 33.3269 | 35.6083 | 38.2343 | 37.4525 | 36.2426 | 37.9206 | 35.8249 | 37.9075 | 36.9713 | 37.2254 | 38.914 | 35.8022 | 36.5802 | 37.4198 | 35.6826 | 36.4998 | 36.6346 | 36.5334 | 38.5581 | 38.1337 | 35.2271 | 38.3848 | 38.5868 | 36.7115 | 40.3458 | 38.0256 | 36.6082 | 36.4346 | 38.1156 | 36.897 | 37.0937 | 36.7548 | 37.6183 | 36.8974 | 37.6184 | 37.3824 | 37.9361 | 38.6391 | 37.3832 | 38.291 | 39.3339 | 40.1434 | 39.3499 | 39.935 | 38.0382 | 39.9186 | 38.9252 | 40.2595 | 38.1068 | 39.2942 | 39.1024 | 39.8611 | 38.2432 | 40.2416 | 38.832 | 40.0473 | 40.4707 | 93.3456 | 93.4763 | 93.1771
2022-09-07 21:54 | 0:04 | 38.1444 | 33.7536 | 35.6979 | 38.318 | 37.5121 | 36.3832 | 38.0236 | 35.9546 | 37.9791 | 37.0423 | 37.2919 | 39.103 | 35.9193 | 36.6452 | 37.5456 | 35.7596 | 36.5712 | 36.6859 | 36.6136 | 38.6287 | 38.2728 | 35.5818 | 38.5185 | 38.6572 | 36.8033 | 40.3913 | 38.1161 | 36.7759 | 36.5511 | 38.2739 | 36.9741 | 37.1149 | 36.8499 | 37.7123 | 36.9554 | 37.6534 | 37.4496 | 38.0214 | 38.6038 | 37.4315 | 38.2021 | 39.4126 | 40.2114 | 39.4346 | 39.934 | 38.121 | 39.9814 | 39.0297 | 40.2442 | 38.1959 | 39.3787 | 39.1596 | 39.8365 | 38.3594 | 40.3584 | 38.8846 | 40.1196 | 40.5549 | 93.2442 | 93.439 | 93.1186
2022-09-07 21:54 | 0:04 | 38.2417 | 34.3575 | 35.8003 | 38.5083 | 37.5512 | 36.5251 | 38.1657 | 36.0577 | 38.0345 | 37.1343 | 37.4112 | 39.0874 | 36.0272 | 36.6966 | 37.6859 | 35.8145 | 36.6434 | 36.801 | 36.7007 | 38.7262 | 38.4431 | 35.9018 | 38.6376 | 38.7765 | 36.8673 | 40.4574 | 38.1906 | 36.8695 | 36.6297 | 38.2932 | 37.087 | 37.1705 | 36.9702 | 37.7668 | 37.0458 | 37.7614 | 37.5636 | 38.1228 | 38.7242 | 37.4641 | 38.0258 | 39.5027 | 40.2487 | 39.5123 | 40.0374 | 38.1431 | 40.0349 | 39.0876 | 40.2933 | 38.2292 | 39.4592 | 39.1938 | 39.9876 | 38.4643 | 40.3214 | 38.945 | 40.2209 | 40.5982 | 93.1979 | 93.3686 | 93.0894
2022-09-07 21:54 | 0:04 | 38.3647 | 34.8087 | 35.874 | 38.5448 | 37.6293 | 36.6185 | 38.181 | 36.1648 | 38.1162 | 37.2072 | 37.4689 | 39.0839 | 36.1234 | 36.8522 | 37.7303 | 35.9088 | 36.7173 | 36.8924 | 36.7494 | 38.8038 | 38.6085 | 36.2364 | 38.7544 | 38.8105 | 36.9652 | 40.6493 | 38.2056 | 36.8737 | 36.7641 | 38.398 | 37.1853 | 37.2347 | 37.0675 | 37.8761 | 37.1771 | 37.7456 | 37.6692 | 38.1822 | 38.7571 | 37.5319 | 37.8554 | 39.591 | 40.289 | 39.6119 | 40.1209 | 38.2524 | 40.0859 | 39.1697 | 40.3369 | 38.2693 | 39.5273 | 39.2751 | 39.9609 | 38.6043 | 40.3247 | 39.0421 | 40.2933 | 40.6303 | 93.1181 | 93.2635 | 93.0056
2022-09-07 21:54 | 0:04 | 35.1379 | 34.6116 | 35.5973 | 38.6955 | 37.6906 | 36.701 | 38.2343 | 36.2277 | 38.146 | 37.3219 | 37.4962 | 39.1066 | 36.1798 | 36.8149 | 37.7638 | 35.9977 | 36.7855 | 36.9039 | 36.8172 | 38.8627 | 36.6092 | 35.0793 | 37.8399 | 38.8555 | 36.9973 | 40.663 | 38.291 | 36.9539 | 36.8526 | 38.4623 | 36.9665 | 37.3272 | 37.0485 | 37.9007 | 37.1447 | 37.8307 | 37.6773 | 38.2329 | 38.8296 | 37.6232 | 37.741 | 39.5645 | 40.2859 | 39.5274 | 40.0983 | 38.2897 | 40.0804 | 39.0776 | 40.3056 | 38.3096 | 39.4673 | 39.276 | 39.9555 | 38.6279 | 40.359 | 38.9962 | 40.3103 | 40.7455 | 93.0384 | 93.1951 | 92.9706
2022-09-07 21:55 | 0:04 | 29.796 | 30.9775 | 33.1727 | 38.466 | 37.7334 | 36.5392 | 38.181 | 36.0532 | 38.1876 | 37.1874 | 37.4831 | 39.2211 | 35.99 | 36.6201 | 37.7418 | 36.0169 | 36.7295 | 36.6532 | 36.616 | 38.7847 | 35.9 | 30.4739 | 37.0262 | 38.7741 | 36.9277 | 40.5069 | 38.2021 | 36.8873 | 36.7306 | 38.2285 | 36.628 | 37.2538 | 36.9045 | 37.7345 | 37.0555 | 37.7486 | 37.6309 | 38.0968 | 38.7624 | 37.5965 | 37.6217 | 39.4989 | 40.1536 | 39.2793 | 39.9693 | 38.2656 | 40.0311 | 38.8237 | 40.2245 | 38.197 | 39.2337 | 39.1538 | 39.9798 | 38.4507 | 40.3569 | 38.8431 | 40.1279 | 40.6641 | 92.9873 | 93.0778 | 92.9095
2022-09-07 21:55 | 0:05 | 29.0078 | 29.731 | 31.9084 | 38.0042 | 37.7481 | 36.2632 | 38.1287 | 35.8535 | 38.1802 | 36.9902 | 37.3781 | 39.2091 | 35.7171 | 36.5044 | 37.7033 | 35.8919 | 36.5407 | 36.4971 | 36.497 | 38.655 | 34.0836 | 28.9376 | 34.7557 | 38.5278 | 36.6396 | 40.1766 | 38.0258 | 36.7371 | 36.4689 | 37.9487 | 35.956 | 37.1447 | 36.6712 | 37.5018 | 36.7672 | 37.6254 | 37.5812 | 37.9583 | 38.642 | 37.5217 | 37.5803 | 39.2269 | 40.0164 | 38.7831 | 39.5635 | 38.1221 | 39.8637 | 38.3433 | 39.9411 | 37.8544 | 38.9645 | 38.8834 | 39.846 | 38.2803 | 40.2765 | 38.51 | 39.9961 | 40.597 | 92.9002 | 93.0136 | 92.8986
2022-09-07 21:55 | 0:05 | 30.51 | 29.8344 | 31.8426 | 37.7307 | 37.8003 | 36.0258 | 38.2257 | 35.7288 | 38.2083 | 36.8541 | 37.5067 | 39.2318 | 35.6014 | 36.401 | 37.5939 | 35.8442 | 36.4474 | 36.4029 | 36.4541 | 38.3897 | 30.736 | 27.9237 | 33.0533 | 38.3332 | 36.4646 | 39.805 | 37.8554 | 36.5512 | 36.2829 | 37.6945 | 35.43 | 37.2186 | 36.5374 | 37.2197 | 36.5067 | 37.5063 | 37.4731 | 37.848 | 38.495 | 37.381 | 37.5558 | 39.0513 | 39.7342 | 38.4015 | 39.3109 | 38.0177 | 39.7778 | 38.0168 | 39.5372 | 37.6359 | 38.8073 | 38.7549 | 39.5715 | 38.2027 | 40.0752 | 38.3205 | 39.5663 | 40.637 | 92.7776 | 92.9275 | 92.797
2022-09-07 21:55 | 0:05 | 31.0878 | 30.0493 | 32.1099 | 37.7195 | 37.8837 | 35.9943 | 38.1886 | 35.6901 | 38.2389 | 36.9353 | 37.4972 | 39.2754 | 35.6352 | 36.3896 | 37.6953 | 35.8183 | 36.4262 | 36.3823 | 36.4459 | 38.3978 | 27.0964 | 27.4276 | 32.1928 | 38.1488 | 36.4086 | 39.7292 | 37.741 | 36.6129 | 36.1366 | 37.631 | 35.1324 | 37.2568 | 36.4873 | 37.0474 | 36.4183 | 37.4101 | 37.4528 | 37.6631 | 38.5327 | 37.3139 | 37.4759 | 38.9015 | 39.6231 | 38.1223 | 39.1542 | 37.9467 | 39.6323 | 37.8405 | 39.4211 | 37.5433 | 38.6248 | 38.7046 | 39.5883 | 38.1115 | 40.1585 | 38.2066 | 39.5704 | 40.6271 | 92.6915 | 92.7979 | 92.758
2022-09-07 21:55 | 0:05 | 31.4112 | 29.9235 | 32.3134 | 37.6319 | 37.9803 | 35.9917 | 38.3105 | 35.8561 | 38.3043 | 36.8782 | 37.5388 | 39.2641 | 35.6401 | 36.3677 | 37.6454 | 35.8196 | 36.4576 | 36.3728 | 36.5323 | 38.4115 | 26.4108 | 26.9308 | 31.6932 | 38.0054 | 36.33 | 39.3608 | 37.6217 | 36.6644 | 36.1266 | 37.5262 | 34.9327 | 37.1685 | 36.4855 | 36.9882 | 36.2426 | 37.3411 | 37.4527 | 37.6342 | 38.4628 | 37.2681 | 37.4207 | 38.7642 | 39.6056 | 37.9816 | 39.0256 | 37.9192 | 39.5976 | 37.6881 | 39.3218 | 37.3933 | 39.1253 | 38.523 | 39.5127 | 37.9471 | 40.0326 | 38.1405 | 39.4678 | 40.5758 | 92.579 | 92.6886 | 92.6897
2022-09-07 21:55 | 0:05 | 31.5135 | 29.6891 | 32.2883 | 37.6419 | 38.0682 | 36.039 | 38.3944 | 35.7862 | 38.3282 | 36.8779 | 37.6514 | 39.3192 | 35.6178 | 36.3668 | 37.6578 | 35.8552 | 36.4421 | 36.3346 | 36.5931 | 38.4154 | 26.0793 | 26.4523 | 31.3385 | 37.9103 | 36.2772 | 39.3608 | 37.5803 | 36.6826 | 36.0672 | 37.5345 | 34.7703 | 37.1709 | 36.5014 | 36.8897 | 36.206 | 37.3825 | 37.4751 | 37.5987 | 38.5134 | 37.3083 | 37.3633 | 38.7188 | 39.6462 | 37.8305 | 38.9304 | 37.9111 | 39.6098 | 37.5215 | 39.1984 | 37.2861 | 38.5935 | 38.4564 | 39.5737 | 37.9669 | 39.8681 | 38.0316 | 39.4023 | 40.489 | 92.4511 | 92.643 | 92.4488
2022-09-07 21:56 | 0:05 | 31.4545 | 29.233 | 32.1403 | 37.5618 | 38.1484 | 36.0474 | 38.3241 | 35.7734 | 38.3488 | 36.7714 | 37.6952 | 39.3554 | 35.5899 | 36.3863 | 37.6232 | 35.8824 | 36.4442 | 36.3953 | 36.5591 | 38.369 | 25.8169 | 26.0373 | 31.03 | 37.8031 | 36.2441 | 39.3305 | 37.5558 | 36.5578 | 36.1053 | 37.4712 | 34.6728 | 37.1486 | 36.5345 | 36.8372 | 36.125 | 37.2755 | 37.5074 | 37.5007 | 38.521 | 37.2626 | 37.3089 | 38.6593 | 39.4346 | 37.761 | 38.8774 | 37.8648 | 39.495 | 37.4359 | 39.1664 | 37.292 | 38.8365 | 38.398 | 39.3502 | 37.9484 | 39.8912 | 37.944 | 39.3626 | 40.5421 | 92.3042 | 92.5118 | 92.4405
2022-09-07 21:56 | 0:06 | 31.2967 | 28.5411 | 31.8653 | 37.5025 | 38.233 | 35.8854 | 38.3533 | 35.7325 | 38.4142 | 36.8316 | 37.5965 | 39.4045 | 35.5354 | 36.2007 | 37.6146 | 35.8897 | 36.4356 | 36.362 | 36.5575 | 38.3299 | 25.6462 | 25.6915 | 30.7872 | 37.713 | 36.217 | 39.0944 | 37.4759 | 36.5457 | 36.0329 | 37.3658 | 34.4723 | 37.0773 | 36.4851 | 36.7905 | 36.0523 | 37.1825 | 37.4615 | 37.4286 | 38.5326 | 37.2876 | 37.263 | 38.6221 | 39.4483 | 37.6707 | 38.759 | 37.8535 | 39.487 | 37.3398 | 39.1944 | 37.236 | 38.5058 | 38.2895 | 39.3838 | 37.9074 | 39.8879 | 37.8411 | 39.1507 | 40.44 | 92.2045 | 92.4169 | 92.3795
2022-09-07 21:56 | 0:06 | 31.1515 | 28.2901 | 31.5576 | 37.3161 | 38.3043 | 35.9754 | 38.346 | 35.7745 | 38.449 | 36.8226 | 37.6374 | 39.4532 | 35.4158 | 36.2952 | 37.5174 | 35.9082 | 36.3665 | 36.3049 | 36.6617 | 38.3016 | 25.8412 | 25.4056 | 30.6946 | 37.7128 | 36.167 | 39.1304 | 37.4207 | 36.693 | 36.0304 | 37.3697 | 34.4028 | 37.224 | 36.4052 | 36.7488 | 35.9441 | 37.2638 | 37.3736 | 37.3917 | 38.4468 | 37.2029 | 37.1901 | 38.5198 | 39.4187 | 37.5982 | 38.7129 | 37.8393 | 39.4112 | 37.1924 | 39.1093 | 37.193 | 38.4749 | 38.2401 | 39.2419 | 37.9456 | 39.95 | 37.799 | 39.0927 | 40.4638 | 92.106 | 92.3227 | 92.3232
2022-09-07 21:56 | 0:06 | 31.0466 | 28.1146 | 31.3822 | 37.3664 | 38.342 | 35.8844 | 38.4543 | 35.6823 | 38.4221 | 36.7843 | 37.6257 | 39.4046 | 35.3704 | 36.2522 | 37.6559 | 35.9701 | 36.3256 | 36.2431 | 36.6249 | 38.2307 | 26.1224 | 25.2619 | 30.495 | 37.5378 | 36.1209 | 39.0964 | 37.3633 | 36.5758 | 36.0112 | 37.2919 | 34.3328 | 37.1795 | 36.3737 | 36.6593 | 35.7458 | 37.1798 | 37.3445 | 37.4382 | 38.4661 | 37.0769 | 37.1962 | 38.5088 | 39.33 | 37.4742 | 38.6533 | 37.7728 | 39.3346 | 37.0549 | 38.9095 | 37.132 | 38.4514 | 38.172 | 39.2961 | 37.9751 | 39.9892 | 37.7097 | 39.2086 | 40.2974 | 91.9626 | 92.1658 | 92.2199
2022-09-07 21:56 | 0:06 | 30.9245 | 28.0267 | 31.1982 | 37.3787 | 38.3966 | 35.8429 | 38.3861 | 35.7002 | 38.4516 | 36.7548 | 37.6471 | 39.5075 | 35.3591 | 36.3242 | 37.5959 | 35.984 | 36.3023 | 36.2184 | 36.6039 | 38.1705 | 26.212 | 25.1707 | 30.3251 | 37.4763 | 36.0501 | 39.0155 | 37.3089 | 36.5229 | 35.9756 | 37.203 | 34.1851 | 37.1757 | 36.3659 | 36.5869 | 35.7252 | 37.1616 | 37.342 | 37.3655 | 38.4045 | 37.075 | 37.1545 | 38.4069 | 39.3004 | 37.2929 | 38.6342 | 37.7292 | 39.3075 | 36.941 | 38.8328 | 37.0436 | 38.4394 | 38.1252 | 39.3138 | 37.9445 | 39.7182 | 37.6546 | 39.1006 | 40.2842 | 91.837 | 92.0064 | 92.2069
2022-09-07 21:56 | 0:06 | 30.7366 | 27.9607 | 31.0095 | 37.1822 | 38.483 | 35.7138 | 38.3634 | 35.6474 | 38.5222 | 36.7084 | 37.7197 | 39.5437 | 35.3656 | 36.2574 | 37.5563 | 35.9934 | 36.2832 | 36.2459 | 36.5602 | 38.2394 | 26.1589 | 25.0457 | 30.176 | 37.4302 | 36.0137 | 38.7589 | 37.263 | 36.5394 | 36.0044 | 37.2128 | 34.0263 | 37.1392 | 36.3159 | 36.5531 | 35.6337 | 37.1215 | 37.3242 | 37.3928 | 38.4537 | 37.046 | 37.128 | 38.3343 | 39.2645 | 37.2899 | 38.5516 | 37.7038 | 39.2784 | 36.8738 | 38.7701 | 37.0941 | 38.2188 | 37.9682 | 39.2803 | 37.7498 | 39.6812 | 37.5835 | 38.8828 | 40.4426 | 91.7259 | 91.8713 | 92.0949
2022-09-07 21:57 | 0:07 | 30.4901 | 27.8402 | 30.6779 | 37.1279 | 38.5137 | 35.723 | 38.4385 | 35.6539 | 38.5246 | 36.69 | 37.617 | 39.5173 | 35.3141 | 36.1952 | 37.5402 | 35.9848 | 36.2652 | 36.2037 | 36.5273 | 38.1659 | 25.3971 | 24.8196 | 30.0441 | 37.3081 | 35.95 | 38.728 | 37.1901 | 36.516 | 35.9411 | 37.0688 | 33.9998 | 37.2312 | 36.314 | 36.4766 | 35.5107 | 37.1838 | 37.3929 | 37.311 | 38.3998 | 37.1299 | 37.0272 | 38.2625 | 39.1196 | 37.1332 | 38.4517 | 37.6354 | 39.2711 | 36.8386 | 38.7545 | 36.9991 | 38.1098 | 37.9575 | 39.1691 | 37.7515 | 39.4333 | 37.5268 | 38.8618 | 40.2558 | 91.6052 | 91.7423 | 92.0584
2022-09-07 21:57 | 0:07 | 29.324 | 27.6423 | 30.0312 | 37.1087 | 38.5532 | 35.7545 | 38.4011 | 35.5593 | 38.526 | 36.7046 | 37.4654 | 39.4954 | 35.256 | 36.1754 | 37.5815 | 35.9843 | 36.2124 | 36.1704 | 36.5132 | 38.1778 | 24.9472 | 24.6167 | 29.8522 | 37.2443 | 35.8948 | 38.92 | 37.1962 | 36.4613 | 35.9564 | 37.0301 | 33.8733 | 37.207 | 36.2946 | 36.4293 | 35.5111 | 37.1907 | 37.4357 | 37.2504 | 38.4436 | 37.0584 | 36.9654 | 38.2059 | 39.1674 | 37.0382 | 38.346 | 37.6288 | 39.2491 | 36.729 | 38.6945 | 36.8899 | 38.2671 | 37.8559 | 39.129 | 37.6225 | 39.7463 | 37.4026 | 38.8986 | 40.3253 | 91.524 | 91.6791 | 91.9937
2022-09-07 21:57 | 0:07 | 26.2964 | 27.4819 | 29.4677 | 36.9738 | 38.5675 | 35.6653 | 38.4319 | 35.4492 | 38.5409 | 36.6366 | 37.3939 | 39.4907 | 35.1958 | 36.062 | 37.5375 | 35.9607 | 36.202 | 36.0573 | 36.4946 | 38.2367 | 25.0672 | 24.3894 | 29.6904 | 37.1012 | 35.8055 | 38.8441 | 37.1545 | 36.4133 | 35.8852 | 37.022 | 33.7677 | 37.1805 | 36.2296 | 36.3578 | 35.3522 | 37.0834 | 37.2714 | 37.1787 | 38.3853 | 36.9689 | 36.9194 | 38.1443 | 39.0782 | 36.9995 | 38.3013 | 37.5734 | 39.1127 | 36.6336 | 38.8812 | 36.8259 | 38.7371 | 37.8698 | 39.1529 | 37.6676 | 39.6229 | 37.3686 | 38.9028 | 40.3405 | 91.4446 | 91.6216 | 92.0186
2022-09-07 21:57 | 0:07 | 25.4522 | 27.1378 | 29.0074 | 36.9794 | 38.5879 | 35.554 | 38.3423 | 35.3508 | 38.5468 | 36.6403 | 37.246 | 39.5145 | 35.1239 | 36.0629 | 37.5198 | 35.9578 | 36.1067 | 36.0648 | 36.4577 | 38.1051 | 25.4825 | 25.5794 | 29.6799 | 36.985 | 35.7637 | 38.6814 | 37.128 | 36.3971 | 35.8867 | 36.9873 | 33.7279 | 37.0761 | 36.1515 | 36.2535 | 35.3431 | 36.9979 | 37.1014 | 37.1099 | 38.3954 | 36.8513 | 36.853 | 38.101 | 39.1223 | 36.9801 | 38.115 | 37.5322 | 39.2735 | 36.4787 | 38.6211 | 36.7566 | 38.3798 | 37.7113 | 39.1025 | 37.6091 | 39.5718 | 37.2941 | 38.8246 | 40.3608 | 91.5236 | 91.6727 | 92.0157
2022-09-07 21:57 | 0:07 | 25.1934 | 26.9093 | 28.753 | 36.7538 | 38.6248 | 35.2626 | 38.3337 | 35.4121 | 38.5658 | 36.5954 | 37.3537 | 39.6026 | 35.0326 | 35.9911 | 37.4727 | 35.955 | 36.0519 | 35.907 | 36.4283 | 38.0505 | 25.6723 | 25.0594 | 29.5332 | 36.9334 | 35.7149 | 38.7674 | 37.0272 | 36.4854 | 35.797 | 36.8827 | 33.5823 | 37.1093 | 36.0386 | 36.2351 | 35.2387 | 36.937 | 37.1061 | 36.9806 | 38.385 | 36.8287 | 36.8786 | 38.0664 | 39.1324 | 36.9251 | 38.1371 | 37.4768 | 39.1975 | 36.3201 | 38.6452 | 36.6932 | 38.6415 | 37.568 | 39.0404 | 37.4961 | 39.6546 | 37.1892 | 38.8494 | 40.4252 | 91.5779 | 91.7513 | 92.1265
2022-09-07 21:57 | 0:07 | 24.8378 | 26.6744 | 28.4904 | 36.7 | 38.6283 | 35.2794 | 38.3279 | 35.3792 | 38.5627 | 36.5361 | 37.3483 | 39.5566 | 34.9522 | 36.0448 | 37.4743 | 35.9115 | 35.9634 | 35.9382 | 36.3838 | 38.0668 | 25.4899 | 24.4626 | 29.3579 | 36.8117 | 35.6503 | 38.6851 | 36.9654 | 36.3137 | 35.7773 | 36.8954 | 33.542 | 37.0477 | 35.939 | 36.1288 | 35.1464 | 36.9848 | 37.1237 | 37.0641 | 38.3219 | 36.7608 | 36.8548 | 37.9053 | 39.0348 | 36.8385 | 38.075 | 37.4297 | 39.1173 | 36.3332 | 38.6512 | 36.6058 | 38.47 | 37.5095 | 38.9353 | 37.4024 | 39.5189 | 37.1257 | 38.6971 | 40.6383 | 91.7144 | 91.8494 | 92.1664
2022-09-07 21:58 | 0:07 | 24.6857 | 26.435 | 28.2604 | 36.6234 | 38.657 | 35.2091 | 38.2848 | 35.3506 | 38.5652 | 36.503 | 37.1915 | 39.584 | 34.8679 | 35.9402 | 37.4545 | 35.9263 | 35.9435 | 35.9008 | 36.3375 | 38.1006 | 25.6147 | 24.3854 | 29.4313 | 36.761 | 35.5784 | 38.7169 | 36.9194 | 36.3657 | 35.7888 | 36.8406 | 33.5023 | 37.0163 | 35.8943 | 36.0924 | 35.0984 | 36.968 | 37.1354 | 36.9744 | 38.3266 | 36.7312 | 36.8204 | 37.8685 | 39.1202 | 36.7617 | 38.1163 | 37.3924 | 39.108 | 36.2597 | 38.4921 | 36.6527 | 38.4283 | 37.4544 | 38.9478 | 37.3422 | 39.4796 | 37.0759 | 38.5629 | 40.5396 | 91.8443 | 91.9077 | 92.2003
2022-09-07 21:58 | 0:08 | 24.5768 | 26.2637 | 28.1077 | 36.5427 | 38.6598 | 35.1671 | 38.32 | 35.2711 | 38.5661 | 36.4373 | 37.2318 | 39.5263 | 34.893 | 35.824 | 37.4533 | 35.8859 | 35.8918 | 35.7616 | 36.3169 | 38.0585 | 25.9571 | 24.1666 | 30.0135 | 36.733 | 35.5347 | 38.6467 | 36.853 | 36.3663 | 35.739 | 36.7978 | 33.5685 | 37.0346 | 35.7687 | 35.9973 | 35.0176 | 36.8739 | 37.0982 | 36.8807 | 38.2923 | 36.7261 | 36.8045 | 37.8429 | 39.0432 | 36.7254 | 38.0904 | 37.33 | 39.0679 | 36.2644 | 38.5938 | 36.6056 | 38.6382 | 37.4254 | 38.9998 | 37.3379 | 39.1845 | 37.0464 | 38.6661 | 40.5522 | 91.9719 | 92.0842 | 92.2819
2022-09-07 21:58 | 0:08 | 24.4226 | 26.1061 | 27.908 | 36.4619 | 38.6323 | 35.1182 | 38.3096 | 35.2459 | 38.5587 | 36.4794 | 37.1092 | 39.5717 | 34.8156 | 35.9354 | 37.4487 | 35.8892 | 35.8313 | 35.689 | 36.335 | 37.9184 | 26.729 | 24.0537 | 30.6186 | 36.7362 | 35.5059 | 38.703 | 36.8786 | 36.3663 | 35.7102 | 36.8624 | 33.7325 | 37.0239 | 35.7535 | 36.0918 | 35.2132 | 36.9211 | 37.216 | 36.9734 | 38.2634 | 36.8397 | 36.7398 | 37.851 | 39.0053 | 36.8027 | 38.2019 | 37.3234 | 39.0781 | 36.2295 | 38.6441 | 36.573 | 38.5419 | 37.3263 | 39.1004 | 37.3984 | 39.5074 | 37.0075 | 38.8503 | 40.1503 | 92.1512 | 92.2613 | 92.4278
2022-09-07 21:58 | 0:08 | 24.2809 | 25.9128 | 27.7166 | 36.4275 | 38.629 | 35.168 | 38.313 | 35.1457 | 38.586 | 36.3227 | 37.0061 | 39.4799 | 34.763 | 35.9122 | 37.2409 | 35.8768 | 35.7707 | 35.6889 | 36.3863 | 37.9763 | 27.3638 | 23.962 | 30.8524 | 36.7484 | 35.497 | 39.1105 | 36.8548 | 36.2194 | 35.7478 | 36.8081 | 33.8201 | 36.8852 | 35.7911 | 36.074 | 35.1728 | 36.8778 | 37.1892 | 36.8868 | 38.34 | 36.9094 | 36.697 | 37.8343 | 38.9388 | 36.6913 | 38.1922 | 37.3223 | 39.1178 | 36.2256 | 38.5312 | 36.5517 | 38.1107 | 37.3685 | 39.0817 | 37.3888 | 39.4177 | 36.9852 | 38.7325 | 40.0823 | 92.2734 | 92.4275 | 92.4569
2022-09-07 21:58 | 0:08 | 24.0797 | 25.667 | 27.5034 | 36.3668 | 38.6285 | 35.0833 | 38.2549 | 35.1112 | 38.5373 | 36.3442 | 37.0956 | 39.5201 | 34.6754 | 35.8417 | 37.4437 | 35.8528 | 35.7069 | 35.7077 | 36.3156 | 37.8155 | 27.5335 | 23.869 | 30.7388 | 36.7746 | 35.4219 | 38.9562 | 36.8204 | 36.2773 | 35.6998 | 36.8637 | 33.7423 | 36.8855 | 35.716 | 36.0714 | 34.924 | 36.8141 | 37.03 | 36.8597 | 38.3127 | 36.7457 | 36.6305 | 37.7482 | 38.9816 | 36.6795 | 38.0924 | 37.235 | 39.0254 | 36.2217 | 38.6058 | 36.482 | 38.0581 | 37.2311 | 38.9806 | 37.2821 | 39.3664 | 36.9433 | 38.6006 | 40.0801 | 92.3736 | 92.5353 | 92.5362
2022-09-07 21:58 | 0:08 | 23.9329 | 25.5003 | 27.3603 | 36.2311 | 38.5907 | 35.0327 | 38.2545 | 35.0316 | 38.557 | 36.221 | 37.0414 | 39.4833 | 34.6138 | 35.8395 | 37.376 | 35.8289 | 35.7002 | 35.7409 | 36.2048 | 37.7842 | 27.4642 | 23.6882 | 30.5648 | 36.6702 | 35.3732 | 38.7692 | 36.8045 | 36.2224 | 35.6203 | 36.8736 | 33.5256 | 36.9756 | 35.6575 | 36.0098 | 34.8714 | 36.8441 | 36.892 | 36.8674 | 38.0551 | 36.6621 | 36.5157 | 37.7338 | 38.8408 | 36.6601 | 38.0196 | 37.209 | 38.9735 | 36.1532 | 38.3805 | 36.4506 | 38.0846 | 37.2046 | 38.9725 | 37.1928 | 39.3365 | 36.8722 | 38.5419 | 40.0977 | 92.5175 | 92.6699 | 92.558
2022-09-07 21:59 | 0:09 | 23.8089 | 25.2843 | 27.1502 | 36.2352 | 38.6559 | 34.9078 | 38.2608 | 34.9989 | 38.5545 | 36.2887 | 37.0047 | 39.5554 | 34.6305 | 35.6073 | 37.2086 | 35.8307 | 35.6336 | 35.6613 | 36.251 | 37.7206 | 27.2445 | 23.635 | 30.2734 | 36.6342 | 35.3156 | 38.6555 | 36.7398 | 36.2603 | 35.5522 | 36.6746 | 33.399 | 36.6889 | 35.6855 | 35.9007 | 34.6709 | 36.7541 | 36.7775 | 36.7934 | 38.0397 | 36.5499 | 36.5643 | 37.6344 | 38.8648 | 36.5071 | 38.0905 | 37.1827 | 38.9494 | 36.0856 | 38.3573 | 36.475 | 38.1396 | 37.1275 | 38.8265 | 37.1903 | 39.4136 | 36.8618 | 38.5318 | 40.0693 | 92.4833 | 92.7993 | 92.579
2022-09-07 21:59 | 0:09 | 23.6146 | 25.0786 | 26.9814 | 36.1277 | 38.6264 | 34.8187 | 38.1654 | 34.9434 | 38.539 | 36.2469 | 36.9146 | 39.643 | 34.5412 | 35.642 | 37.1603 | 35.8173 | 35.6241 | 35.492 | 36.1598 | 37.6585 | 26.9457 | 23.3908 | 30.0424 | 36.5229 | 35.2404 | 38.5267 | 36.697 | 36.1384 | 35.4776 | 36.6254 | 33.3342 | 36.7522 | 35.6031 | 35.8434 | 34.6126 | 36.7056 | 36.8776 | 36.7035 | 38.1413 | 36.528 | 36.4851 | 37.6473 | 38.8021 | 36.4436 | 37.9956 | 37.136 | 38.9053 | 35.9164 | 38.3524 | 36.4349 | 37.7647 | 37.2268 | 38.6362 | 37.1268 | 39.4045 | 36.7241 | 38.3513 | 40.0376 | 92.6295 | 92.9329 | 92.6861
2022-09-07 21:59 | 0:09 | 23.4841 | 24.9823 | 26.8422 | 36.117 | 38.6218 | 34.7916 | 38.2086 | 34.9278 | 38.5144 | 36.1713 | 36.7798 | 39.5416 | 34.4942 | 35.5135 | 37.1514 | 35.7667 | 35.5364 | 35.3739 | 36.0955 | 37.8591 | 26.6457 | 23.3705 | 29.8243 | 36.4529 | 35.1818 | 38.6726 | 36.6305 | 35.9913 | 35.4727 | 36.5982 | 33.1624 | 36.6887 | 35.5078 | 35.7122 | 34.5085 | 36.7985 | 36.6683 | 36.6628 | 38.0768 | 36.4397 | 36.4003 | 37.4773 | 38.7522 | 36.3584 | 37.8112 | 37.0632 | 38.8095 | 35.8255 | 38.3314 | 36.3376 | 37.9349 | 37.1873 | 38.7111 | 37.1532 | 39.3751 | 36.6502 | 38.4336 | 40.0322 | 92.8436 | 93.0763 | 92.787
2022-09-07 21:59 | 0:09 | 23.309 | 24.6653 | 26.6207 | 36.0215 | 38.6153 | 34.768 | 38.1556 | 34.835 | 38.4826 | 36.0793 | 36.8 | 39.5536 | 34.4162 | 35.5297 | 37.0427 | 35.7305 | 35.4678 | 35.3457 | 36.0942 | 37.6799 | 26.3719 | 23.1852 | 29.6492 | 36.4334 | 35.0929 | 38.3432 | 36.5157 | 35.9949 | 35.4182 | 36.5846 | 33.1089 | 36.667 | 35.4826 | 35.6819 | 34.509 | 36.6902 | 36.6733 | 36.6006 | 38.1422 | 36.3639 | 36.3812 | 37.4537 | 38.6568 | 36.271 | 37.7709 | 37.0148 | 38.7799 | 35.7176 | 38.1599 | 36.2504 | 37.9451 | 36.9483 | 38.6394 | 37.0336 | 39.097 | 36.5498 | 38.2503 | 40.0674 | 92.9682 | 93.1728 | 92.8365
2022-09-07 21:59 | 0:09 | 23.1653 | 24.5532 | 26.4989 | 35.9167 | 38.5639 | 34.7788 | 38.0656 | 34.7897 | 38.4547 | 36.0614 | 36.6645 | 39.4574 | 34.3459 | 35.5688 | 36.9325 | 35.6891 | 35.3809 | 35.4235 | 36.0867 | 37.5552 | 26.0775 | 23.0759 | 29.4669 | 36.3862 | 35.0191 | 38.4264 | 36.5643 | 35.9882 | 35.3694 | 36.4922 | 32.9593 | 36.6652 | 35.4679 | 35.6498 | 34.3823 | 36.6534 | 36.7591 | 36.5813 | 38.2119 | 36.3336 | 36.2931 | 37.37 | 38.5898 | 36.1967 | 37.6774 | 36.9571 | 38.7717 | 35.6868 | 38.1357 | 36.1395 | 37.8761 | 36.9594 | 38.5761 | 36.8268 | 39.1174 | 36.4616 | 38.2309 | 39.967 | 93.1715 | 93.2979 | 92.9228
2022-09-07 21:59 | 0:09 | 23.0271 | 24.3695 | 26.3044 | 35.8906 | 38.5339 | 34.7745 | 38.0514 | 34.7461 | 38.4945 | 35.9107 | 36.5025 | 39.5709 | 34.2701 | 35.5335 | 37.0188 | 35.6699 | 35.2944 | 35.438 | 36.0497 | 37.6286 | 25.8351 | 22.9801 | 29.3189 | 36.301 | 34.931 | 38.5303 | 36.4851 | 36.0098 | 35.3105 | 36.4538 | 32.8419 | 36.6411 | 35.4377 | 35.6063 | 34.3149 | 36.6832 | 36.5979 | 36.5344 | 38.0564 | 36.2691 | 36.1838 | 37.3218 | 38.547 | 36.1204 | 37.6947 | 36.888 | 38.8115 | 35.5382 | 38.0916 | 36.0328 | 38.3531 | 36.8485 | 38.5739 | 36.8553 | 39.1525 | 36.3623 | 38.2047 | 39.8002 | 93.3967 | 93.5829 | 93.1598
2022-09-07 22:00 | 0:09 | 22.9898 | 24.2788 | 26.198 | 35.7785 | 38.4831 | 34.6099 | 38.0353 | 34.613 | 38.4857 | 35.8799 | 36.5164 | 39.5966 | 34.25 | 35.4177 | 36.9406 | 35.651 | 35.2689 | 35.1893 | 35.9387 | 37.5614 | 25.5996 | 22.8523 | 29.0872 | 36.1739 | 34.8769 | 38.41 | 36.4003 | 35.8949 | 35.2211 | 36.3623 | 32.8097 | 36.7474 | 35.33 | 35.5528 | 34.2238 | 36.6245 | 36.7047 | 36.4609 | 38.0387 | 36.3077 | 36.1637 | 37.2751 | 38.4983 | 35.9931 | 37.5097 | 36.846 | 38.7516 | 35.4667 | 37.9468 | 36.0345 | 38.1292 | 36.7056 | 38.5844 | 36.7409 | 39.133 | 36.3136 | 38.2614 | 40.0545 | 93.6755 | 93.8569 | 93.2472
2022-09-07 22:00 | 0:10 | 22.7491 | 24.0908 | 26.0503 | 35.6532 | 38.5148 | 34.549 | 37.996 | 34.5344 | 38.4578 | 35.8326 | 36.5107 | 39.4803 | 34.1708 | 35.4003 | 36.9222 | 35.634 | 35.2102 | 35.2228 | 35.9481 | 37.4843 | 25.3694 | 22.6342 | 28.8363 | 36.0351 | 34.7704 | 38.2682 | 36.3812 | 35.9328 | 35.1629 | 36.2917 | 32.7953 | 36.657 | 35.2974 | 35.4353 | 34.1964 | 36.4938 | 36.7197 | 36.4109 | 38.04 | 36.3224 | 36.1896 | 37.2214 | 38.4612 | 35.9363 | 37.499 | 36.7726 | 38.6285 | 35.3949 | 37.9537 | 36.0029 | 38.3028 | 36.5562 | 38.6711 | 36.565 | 39.1397 | 36.2393 | 38.4109 | 39.8321 | 93.8935 | 94.1293 | 93.4214
2022-09-07 22:00 | 0:10 | 22.57 | 23.8924 | 25.8758 | 35.6719 | 38.4156 | 34.6292 | 38.0783 | 34.6172 | 38.3524 | 35.8622 | 36.2555 | 39.332 | 34.1588 | 35.29 | 36.8641 | 35.5511 | 35.1409 | 35.2606 | 35.7857 | 37.3457 | 25.1709 | 22.501 | 28.6422 | 35.9171 | 34.7494 | 38.0872 | 36.2931 | 35.8399 | 35.1401 | 36.2385 | 32.5611 | 36.657 | 35.2319 | 35.3777 | 34.0004 | 36.5846 | 36.7269 | 36.4001 | 38.0567 | 36.2507 | 36.0255 | 37.1965 | 38.4157 | 35.8304 | 37.4744 | 36.7566 | 38.5203 | 35.3146 | 37.8726 | 35.9452 | 38.0114 | 36.5126 | 38.5643 | 36.5213 | 39.1468 | 36.2309 | 38.0714 | 39.9404 | 94.1436 | 94.4156 | 93.6633
2022-09-07 22:00 | 0:10 | 22.5334 | 23.7674 | 25.7126 | 35.6473 | 38.3969 | 34.6579 | 37.9328 | 34.4314 | 38.3508 | 35.7822 | 36.2979 | 39.4288 | 34.0384 | 35.2908 | 36.8225 | 35.5297 | 35.102 | 35.1233 | 35.7633 | 37.2793 | 24.9526 | 22.5078 | 28.4993 | 35.8092 | 34.6569 | 38.3287 | 36.1838 | 35.6894 | 35.1074 | 36.166 | 32.5049 | 36.649 | 35.1584 | 35.2828 | 34.0322 | 36.4036 | 36.6676 | 36.3456 | 37.9472 | 36.3004 | 36.0307 | 37.1392 | 38.4378 | 35.8223 | 37.4131 | 36.6828 | 38.5861 | 35.238 | 37.9027 | 35.8453 | 38.2188 | 36.4387 | 38.4731 | 36.4138 | 38.9672 | 36.0615 | 38.1698 | 39.7834 | 94.3424 | 94.6469 | 93.7281
2022-09-07 22:00 | 0:10 | 22.3135 | 23.5977 | 25.5582 | 35.5365 | 38.3435 | 34.6142 | 38.0249 | 34.4161 | 38.2875 | 35.7583 | 36.2284 | 39.4367 | 33.9534 | 35.2738 | 36.6768 | 35.4982 | 35.0884 | 35.1009 | 35.7808 | 37.2868 | 24.7766 | 22.2933 | 28.3418 | 35.6512 | 34.5849 | 38.2119 | 36.1637 | 35.6568 | 35.0458 | 36.2146 | 32.4307 | 36.5195 | 35.0431 | 35.1977 | 33.7281 | 36.4377 | 36.3688 | 36.228 | 37.966 | 36.0554 | 35.9173 | 37.0397 | 38.2492 | 35.6779 | 37.3711 | 36.632 | 38.5485 | 35.2037 | 37.7821 | 35.8091 | 38.1162 | 36.4442 | 38.5269 | 36.3544 | 39.0463 | 36.0718 | 37.8905 | 39.5841 | 94.5748 | 94.8619 | 93.9631
2022-09-07 22:00 | 0:10 | 22.095 | 23.3799 | 25.3982 | 35.4142 | 38.2908 | 34.5155 | 37.9037 | 34.284 | 38.2879 | 35.6625 | 36.2339 | 39.4171 | 33.9299 | 34.9948 | 36.6742 | 35.4286 | 35.0221 | 34.989 | 35.6752 | 37.2663 | 24.6162 | 22.0804 | 28.1998 | 35.6506 | 34.5169 | 38.1705 | 36.1896 | 35.4328 | 35.0024 | 36.0446 | 32.2257 | 36.3808 | 34.8942 | 35.131 | 33.7418 | 36.3465 | 36.3218 | 36.1546 | 37.894 | 36.0468 | 35.8037 | 37.0168 | 38.1955 | 35.5914 | 37.2838 | 36.5499 | 38.4831 | 35.1865 | 37.663 | 35.7837 | 37.9361 | 36.4126 | 38.325 | 36.3479 | 38.9128 | 35.9644 | 37.7768 | 39.5426 | 94.8024 | 95.0797 | 94.0341
2022-09-07 22:01 | 0:11 | 21.9934 | 23.2559 | 25.2793 | 35.4434 | 38.3468 | 34.4087 | 37.9639 | 34.2371 | 38.2599 | 35.6538 | 36.0662 | 39.3768 | 33.8496 | 35.0876 | 36.6068 | 35.3756 | 34.965 | 34.8787 | 35.64 | 37.3649 | 24.5014 | 21.8577 | 28.1532 | 35.5531 | 34.4086 | 38.1111 | 36.0255 | 35.4173 | 34.9158 | 36.0028 | 32.3074 | 36.4223 | 35.0967 | 35.0528 | 33.7668 | 36.3174 | 36.519 | 36.0591 | 37.8692 | 36.1894 | 35.8061 | 36.9078 | 38.2279 | 35.5781 | 37.236 | 36.5093 | 38.4163 | 34.9871 | 37.6608 | 35.646 | 38.1118 | 36.276 | 38.1305 | 36.3793 | 38.871 | 35.868 | 37.7856 | 39.4857 | 94.8375 | 95.2461 | 94.118
2022-09-07 22:01 | 0:11 | 21.9516 | 23.1132 | 25.1363 | 35.306 | 38.3205 | 34.3275 | 37.8199 | 34.1764 | 38.2221 | 35.6747 | 36.2936 | 39.4067 | 33.7867 | 34.8756 | 36.6282 | 35.344 | 34.8736 | 34.8694 | 35.5649 | 37.1973 | 24.4323 | 21.7535 | 28.1015 | 35.4944 | 34.3514 | 38.1033 | 36.0307 | 35.4687 | 34.7665 | 36.091 | 32.1737 | 36.3405 | 34.9636 | 35.0297 | 33.917 | 36.3488 | 36.5593 | 35.9988 | 37.8982 | 36.247 | 35.8238 | 36.8652 | 38.1851 | 35.5335 | 37.2671 | 36.4498 | 38.354 | 34.9305 | 37.6669 | 35.5464 | 38.1686 | 36.3167 | 38.3546 | 36.2088 | 38.808 | 35.7687 | 37.6814 | 39.4026 | 94.8923 | 95.3549 | 94.1362
2022-09-07 22:01 | 0:11 | 21.7221 | 22.9636 | 24.9999 | 35.324 | 38.2641 | 34.1739 | 37.8097 | 34.0432 | 38.2366 | 35.6588 | 35.8393 | 39.2702 | 33.6951 | 34.965 | 36.6124 | 35.3411 | 34.7955 | 34.9619 | 35.5088 | 37.3628 | 24.3503 | 21.6344 | 27.9818 | 35.3129 | 34.2643 | 37.8913 | 35.9173 | 35.3758 | 34.8095 | 35.874 | 32.1375 | 36.3402 | 34.9812 | 34.9113 | 33.8802 | 36.2805 | 36.5879 | 35.9808 | 37.8717 | 36.267 | 35.7233 | 36.7584 | 38.0358 | 35.4005 | 37.2344 | 36.3926 | 38.3457 | 34.8473 | 37.5059 | 35.4338 | 38.24 | 36.1258 | 38.3293 | 36.0065 | 38.8722 | 35.6601 | 37.6604 | 39.4657 | 94.9915 | 95.4769 | 94.3227
2022-09-07 22:01 | 0:11 | 21.6146 | 22.76 | 24.8587 | 35.1274 | 38.2437 | 34.1378 | 37.6951 | 34.0726 | 38.1723 | 35.6561 | 35.8911 | 39.3217 | 33.6831 | 34.9653 | 36.5794 | 35.2465 | 34.7914 | 34.9242 | 35.4668 | 37.0828 | 24.2442 | 21.5184 | 27.8924 | 35.3277 | 34.1927 | 37.7324 | 35.8037 | 35.5765 | 34.6597 | 35.8366 | 32.1594 | 36.1174 | 34.8851 | 34.8196 | 33.6983 | 36.1987 | 36.4483 | 35.8711 | 37.8774 | 36.1601 | 35.6804 | 36.6497 | 38.0528 | 35.4334 | 37.0891 | 36.322 | 38.2506 | 34.8075 | 37.4559 | 35.3488 | 38.1209 | 35.9387 | 38.3033 | 36.0156 | 38.6928 | 35.5934 | 37.5891 | 39.3437 | 95.0878 | 95.5303 | 94.3731
2022-09-07 22:01 | 0:11 | 21.5524 | 22.7035 | 24.7231 | 35.1097 | 38.1977 | 34.2664 | 37.7726 | 33.9656 | 38.1436 | 35.4372 | 35.981 | 39.2706 | 33.5217 | 34.8946 | 36.468 | 35.207 | 34.6583 | 34.6689 | 35.409 | 36.9854 | 24.1521 | 21.4496 | 27.8093 | 35.2549 | 34.0904 | 38.1497 | 35.8061 | 35.397 | 34.5235 | 35.7657 | 32.003 | 36.3227 | 34.7442 | 34.8204 | 33.4647 | 36.1598 | 36.1554 | 35.9435 | 37.7047 | 35.9418 | 35.5234 | 36.6221 | 37.9942 | 35.2886 | 37.0522 | 36.2891 | 38.1938 | 34.6913 | 37.408 | 35.3529 | 37.5327 | 35.8699 | 38.1899 | 35.8942 | 38.7251 | 35.5576 | 37.4419 | 39.3802 | 95.1435 | 95.5748 | 94.3815
2022-09-07 22:01 | 0:11 | 21.3916 | 22.5532 | 24.6006 | 35.0642 | 38.1549 | 33.9821 | 37.6804 | 33.8651 | 38.0949 | 35.2925 | 35.8407 | 39.1851 | 33.5087 | 34.8053 | 36.4811 | 35.1656 | 34.6569 | 34.7251 | 35.3673 | 36.8758 | 24.0847 | 21.3309 | 27.8046 | 35.1998 | 34.0585 | 37.9798 | 35.8238 | 35.349 | 34.4988 | 35.7252 | 31.8189 | 36.1482 | 34.6179 | 34.7586 | 33.2108 | 35.9989 | 36.0597 | 35.8279 | 37.7064 | 35.7478 | 35.6161 | 36.6034 | 37.8024 | 35.1976 | 36.9557 | 36.2241 | 38.2381 | 34.6423 | 37.3653 | 35.4096 | 37.7292 | 35.8305 | 38.1349 | 35.8951 | 38.5894 | 35.4648 | 37.4601 | 39.4108 | 95.0856 | 95.553 | 94.3385
2022-09-07 22:02 | 0:12 | 21.324 | 22.4576 | 24.477 | 34.9762 | 38.109 | 33.8741 | 37.5774 | 33.763 | 38.0915 | 35.3789 | 35.9134 | 39.2226 | 33.4084 | 34.7797 | 36.4427 | 35.1375 | 34.5815 | 34.5457 | 35.3415 | 36.8488 | 24.0068 | 21.1953 | 27.6861 | 35.1433 | 33.9628 | 37.667 | 35.7233 | 35.2546 | 34.4908 | 35.7661 | 31.8345 | 36.161 | 34.5515 | 34.7156 | 33.0216 | 36.1908 | 36.1127 | 35.7575 | 37.5573 | 35.7149 | 35.5394 | 36.5467 | 37.6958 | 35.0898 | 36.9318 | 36.1773 | 38.0076 | 34.5543 | 37.2853 | 35.2838 | 37.746 | 35.5891 | 38.154 | 35.7503 | 38.6522 | 35.3567 | 37.4922 | 39.3059 | 94.8493 | 95.3613 | 94.1274
2022-09-07 22:02 | 0:12 | 21.1611 | 22.2931 | 24.3541 | 34.7877 | 38.0266 | 33.7775 | 37.6068 | 33.6154 | 37.9715 | 35.2272 | 35.4648 | 39.1832 | 33.3895 | 34.7019 | 36.3641 | 35.0416 | 34.5002 | 34.5003 | 35.2494 | 36.7557 | 23.888 | 20.967 | 27.6187 | 35.0922 | 33.8732 | 37.6723 | 35.6804 | 35.1407 | 34.437 | 35.5733 | 31.7612 | 36.1887 | 34.4111 | 34.6813 | 32.8964 | 36.0797 | 35.9168 | 35.7253 | 37.5046 | 35.6043 | 35.4449 | 36.4844 | 37.7838 | 34.9575 | 36.9203 | 36.0998 | 38.0523 | 34.482 | 37.2246 | 35.2941 | 37.2276 | 35.7456 | 37.8778 | 35.7189 | 38.2788 | 35.3289 | 37.368 | 39.194 | 94.6605 | 95.1079 | 93.9224
2022-09-07 22:02 | 0:12 | 21.121 | 22.2244 | 24.2625 | 34.7683 | 38.0159 | 33.6737 | 37.5981 | 33.6948 | 37.9766 | 35.3039 | 35.7734 | 39.2243 | 33.3319 | 34.6991 | 36.3367 | 35.0132 | 34.4888 | 34.5131 | 35.205 | 36.6448 | 23.8391 | 20.9968 | 27.5793 | 35.0277 | 33.8053 | 37.6745 | 35.5234 | 35.1524 | 34.3908 | 35.5453 | 31.6709 | 36.0499 | 34.4145 | 34.5977 | 33.1169 | 36.0177 | 36.0376 | 35.6776 | 37.2459 | 35.6676 | 35.5062 | 36.3768 | 37.6792 | 34.9409 | 36.7843 | 36.0663 | 38.1016 | 34.4 | 37.1675 | 35.1546 | 37.3087 | 35.7805 | 37.9243 | 35.7045 | 38.2797 | 35.2364 | 37.3318 | 39.1883 | 94.3764 | 94.8253 | 93.7503
2022-09-07 22:02 | 0:12 | 20.9229 | 22.0449 | 24.1077 | 34.6855 | 37.9364 | 33.7068 | 37.5708 | 33.6701 | 37.9506 | 35.2038 | 35.8244 | 39.2209 | 33.1777 | 34.5263 | 36.2666 | 34.9652 | 34.373 | 34.3951 | 35.0951 | 36.8633 | 23.7692 | 20.8435 | 27.5376 | 34.986 | 33.7383 | 37.9 | 35.6161 | 34.9449 | 34.3352 | 35.5114 | 31.5774 | 36.1086 | 34.4003 | 34.476 | 33.059 | 35.9462 | 35.876 | 35.664 | 37.3703 | 35.5801 | 35.5325 | 36.3548 | 37.5995 | 34.8889 | 36.6919 | 35.988 | 37.9943 | 34.3265 | 37.0369 | 35.0485 | 37.7314 | 35.7208 | 37.885 | 35.6466 | 38.3607 | 35.2176 | 37.2531 | 39.5082 | 94.3028 | 94.6817 | 93.7947
2022-09-07 22:02 | 0:12 | 20.9157 | 21.9857 | 24.0643 | 34.7169 | 37.912 | 33.6986 | 37.6155 | 33.5084 | 37.9199 | 35.0648 | 35.5687 | 39.07 | 33.1277 | 34.5052 | 36.0363 | 34.9141 | 34.2796 | 34.4005 | 35.0766 | 36.8022 | 23.787 | 21.0735 | 27.5988 | 34.9118 | 33.6401 | 37.6985 | 35.5394 | 34.897 | 34.2793 | 35.3353 | 31.6471 | 36.0895 | 34.3355 | 34.47 | 32.9074 | 35.9291 | 35.9276 | 35.6845 | 37.3451 | 35.5013 | 35.5658 | 36.2182 | 37.7027 | 34.9305 | 36.6948 | 35.9292 | 37.9018 | 34.3169 | 37.0485 | 34.9913 | 37.8181 | 35.6285 | 37.986 | 35.4943 | 38.3062 | 35.1191 | 37.2635 | 39.3363 | 94.2286 | 94.5175 | 93.7348
2022-09-07 22:02 | 0:12 | 19.8156 | 21.683 | 23.6929 | 34.7192 | 37.7897 | 33.4402 | 37.4959 | 33.4691 | 37.8837 | 35.0097 | 35.5479 | 39.0978 | 33.0635 | 34.4727 | 36.0141 | 34.8396 | 34.2093 | 34.3595 | 35.0506 | 36.7444 | 24.0299 | 21.7031 | 28.2757 | 34.771 | 33.6384 | 37.8071 | 35.4449 | 34.8398 | 34.1408 | 35.4084 | 31.69 | 36.0563 | 34.2712 | 34.49 | 32.9047 | 35.9003 | 35.8948 | 35.5669 | 37.4639 | 35.407 | 35.6077 | 36.2749 | 37.6949 | 35.0132 | 36.8031 | 35.8832 | 37.9854 | 34.3991 | 37.2042 | 34.984 | 37.5809 | 35.6902 | 37.9397 | 35.405 | 38.2066 | 35.1763 | 37.2914 | 39.2094 | 94.1096 | 94.4168 | 93.6193
2022-09-07 22:03 | 0:12 | 19.2607 | 21.2819 | 23.2648 | 34.3509 | 37.8035 | 33.5073 | 37.5095 | 33.367 | 37.9095 | 34.9436 | 35.4005 | 39.0038 | 32.8655 | 34.4677 | 35.8662 | 34.7673 | 34.1512 | 34.2429 | 34.8794 | 36.7452 | 24.7829 | 22.943 | 29.4259 | 34.873 | 33.6676 | 37.9294 | 35.5062 | 34.859 | 34.1437 | 35.5681 | 32.0385 | 35.9179 | 33.9755 | 34.4678 | 32.9686 | 35.7571 | 35.6996 | 35.4704 | 37.3568 | 35.3048 | 35.6388 | 36.4751 | 37.7638 | 35.0964 | 37.0374 | 35.9231 | 38.0825 | 34.6276 | 37.2592 | 35.0268 | 37.3312 | 35.6818 | 37.9953 | 35.4112 | 38.4088 | 35.3503 | 37.3276 | 39.1378 | 93.9651 | 94.3129 | 93.5956
2022-09-07 22:03 | 0:13 | 18.8384 | 20.8862 | 22.9301 | 34.3316 | 37.6196 | 33.4917 | 37.2472 | 33.2568 | 37.7778 | 34.7326 | 35.1812 | 38.9642 | 32.7318 | 34.3251 | 35.685 | 34.6419 | 34.0757 | 34.1365 | 34.8142 | 36.7169 | 25.7684 | 24.2739 | 30.3796 | 35.0291 | 33.7207 | 37.8589 | 35.5325 | 35.0951 | 34.1827 | 35.6946 | 32.3285 | 36.0001 | 33.9502 | 34.5706 | 33.0822 | 35.7218 | 35.6288 | 35.54 | 37.2796 | 35.3624 | 35.6604 | 36.5967 | 38.0038 | 35.354 | 37.1636 | 35.9165 | 38.158 | 34.7995 | 37.3807 | 35.1549 | 37.1891 | 35.9123 | 37.9538 | 35.5013 | 38.4598 | 35.4886 | 37.4417 | 39.2775 | 93.9303 | 94.236 | 93.5557
2022-09-07 22:03 | 0:13 | 18.5179 | 20.6316 | 22.6151 | 34.2588 | 37.552 | 33.4825 | 37.3121 | 33.2451 | 37.721 | 34.7562 | 35.066 | 38.9832 | 32.6623 | 34.2919 | 35.8419 | 34.5926 | 33.9911 | 34.0254 | 34.7188 | 36.6255 | 26.7404 | 25.5956 | 31.0654 | 35.1882 | 33.7764 | 38.0941 | 35.5658 | 35.0866 | 34.2124 | 35.6781 | 32.5252 | 35.8935 | 33.7966 | 34.6548 | 33.2067 | 35.6447 | 35.7168 | 35.6412 | 37.1903 | 35.4639 | 35.7193 | 36.6785 | 37.9278 | 35.4605 | 37.1998 | 35.9037 | 38.0811 | 34.998 | 37.4925 | 35.2084 | 36.8803 | 35.9958 | 37.9295 | 35.5813 | 38.7688 | 35.6051 | 37.5158 | 39.3045 | 93.8756 | 94.1601 | 93.5316
2022-09-07 22:03 | 0:13 | 18.1521 | 20.3591 | 22.3534 | 34.16 | 37.5158 | 33.2613 | 37.2757 | 33.1609 | 37.7156 | 34.7555 | 35.1239 | 38.8252 | 32.5004 | 34.1984 | 35.8743 | 34.5133 | 33.8396 | 33.9886 | 34.6924 | 36.4438 | 27.657 | 26.7964 | 31.5651 | 35.2247 | 33.7795 | 38.0377 | 35.6077 | 35.1196 | 34.1688 | 35.776 | 32.7126 | 35.7099 | 33.8377 | 34.7459 | 33.2714 | 35.6931 | 35.794 | 35.7271 | 37.3122 | 35.6151 | 35.7258 | 36.7132 | 38.0263 | 35.5933 | 37.2681 | 35.8904 | 38.1392 | 35.1032 | 37.5594 | 35.33 | 37.2339 | 36.0591 | 38.0251 | 35.667 | 38.6459 | 35.6859 | 37.6196 | 39.2847 | 93.8166 | 94.1121 | 93.5135
2022-09-07 22:03 | 0:13 | 17.9335 | 20.0995 | 22.1154 | 34.0543 | 37.5134 | 33.2645 | 37.3425 | 32.9202 | 37.6708 | 34.7785 | 34.8456 | 38.8396 | 32.4265 | 34.0961 | 35.7559 | 34.5059 | 33.8638 | 33.9162 | 34.593 | 36.3816 | 28.4388 | 27.8505 | 31.9522 | 35.3644 | 33.8073 | 38.0567 | 35.6388 | 35.1096 | 34.2259 | 35.7102 | 32.8537 | 35.8118 | 33.8323 | 34.7782 | 33.4583 | 35.752 | 35.8692 | 35.6734 | 37.5116 | 35.636 | 35.8188 | 36.7629 | 38.0009 | 35.6805 | 37.5047 | 35.8357 | 38.074 | 35.1894 | 37.5871 | 35.3714 | 37.0455 | 36.1236 | 38.112 | 35.6614 | 38.7848 | 35.7297 | 37.8466 | 39.2726 | 93.7625 | 94.0333 | 93.3945
2022-09-07 22:03 | 0:13 | 17.6729 | 19.8345 | 21.8654 | 34.0377 | 37.3491 | 33.2976 | 37.0905 | 32.8203 | 37.5769 | 34.8748 | 34.6288 | 38.751 | 32.3425 | 34.1676 | 35.755 | 34.4356 | 33.7429 | 33.787 | 34.5663 | 36.3931 | 29.1239 | 28.7393 | 32.246 | 35.3404 | 33.8115 | 38.397 | 35.6604 | 34.9521 | 34.2244 | 35.9126 | 32.9647 | 35.5716 | 33.8188 | 34.8223 | 33.4812 | 35.9207 | 35.758 | 35.6501 | 37.1666 | 35.5696 | 35.8772 | 36.8398 | 38.1173 | 35.769 | 37.4572 | 35.8643 | 38.0515 | 35.2826 | 37.7212 | 35.38 | 37.0865 | 36.0953 | 38.112 | 35.6718 | 38.6699 | 35.7561 | 37.9358 | 39.2343 | 93.7161 | 93.9985 | 93.4623
2022-09-07 22:04 | 0:14 | 17.4232 | 19.6283 | 21.6619 | 34.0044 | 37.2544 | 33.2377 | 37.1971 | 32.7315 | 37.5138 | 34.9091 | 34.5804 | 38.6825 | 32.2849 | 33.9463 | 35.5262 | 34.3317 | 33.7338 | 33.7373 | 34.4881 | 36.3937 | 29.6441 | 29.3232 | 32.45 | 35.3594 | 33.8144 | 38.341 | 35.7193 | 34.8815 | 34.2133 | 35.8689 | 33.0557 | 35.856 | 33.793 | 34.8705 | 33.5048 | 35.8223 | 35.6821 | 35.7166 | 37.0836 | 35.5386 | 35.9082 | 36.8278 | 38.2136 | 35.8504 | 37.572 | 35.9027 | 38.1396 | 35.3793 | 37.8323 | 35.4264 | 37.072 | 36.2128 | 38.1695 | 35.743 | 38.6674 | 35.8259 | 37.8173 | 39.175 | 93.6818 | 93.926 | 93.374
2022-09-07 22:04 | 0:14 | 17.2498 | 19.401 | 21.479 | 33.9344 | 37.2209 | 33.2982 | 37.0332 | 32.739 | 37.4138 | 34.7976 | 34.6014 | 38.7321 | 32.3199 | 33.8382 | 35.6094 | 34.2053 | 33.6315 | 33.7481 | 34.452 | 36.4029 | 30.1131 | 29.8003 | 32.6196 | 35.3788 | 33.8157 | 38.3994 | 35.7258 | 34.7992 | 34.1854 | 35.7732 | 33.1456 | 35.5066 | 33.8133 | 34.9046 | 33.5433 | 35.8882 | 35.5862 | 35.7676 | 37.0839 | 35.4493 | 35.9116 | 36.8863 | 38.2181 | 35.8763 | 37.6094 | 35.8994 | 38.1744 | 35.4555 | 37.752 | 35.4898 | 36.992 | 36.2551 | 38.0894 | 35.7001 | 38.8465 | 35.8751 | 37.8048 | 39.2662 | 93.6153 | 93.8511 | 93.3483
2022-09-07 22:04 | 0:14 | 17.028 | 19.1731 | 21.2197 | 33.95 | 37.1399 | 33.1472 | 37.0262 | 32.4841 | 37.3825 | 34.649 | 34.5281 | 38.6803 | 32.2045 | 33.4859 | 35.3681 | 34.1617 | 33.5348 | 33.4424 | 34.3836 | 36.3056 | 30.4401 | 30.1464 | 32.7686 | 35.3755 | 33.8189 | 38.5164 | 35.8188 | 34.9434 | 34.1521 | 35.9329 | 33.2559 | 35.5767 | 33.7306 | 34.8359 | 33.5989 | 35.7837 | 35.4628 | 35.6119 | 37.1019 | 35.4243 | 35.969 | 36.8942 | 38.1633 | 35.9528 | 37.6761 | 35.8904 | 38.0905 | 35.4855 | 37.8123 | 35.5015 | 37.0525 | 36.2369 | 37.9943 | 35.6786 | 38.9119 | 35.9459 | 38.0797 | 39.1218 | 93.5473 | 93.8083 | 93.3379
2022-09-07 22:04 | 0:14 | 16.8069 | 18.9558 | 21.0682 | 33.7505 | 37.0082 | 32.8913 | 36.9494 | 32.4743 | 37.2909 | 34.7275 | 34.4725 | 38.5671 | 32.0835 | 33.713 | 35.4494 | 34.1376 | 33.5438 | 33.2472 | 34.3152 | 36.4354 | 30.7326 | 30.4203 | 32.8795 | 35.3862 | 33.8851 | 38.458 | 35.8772 | 35.0185 | 34.1161 | 36.0078 | 33.3073 | 35.6271 | 33.7349 | 34.8373 | 33.6168 | 35.6878 | 35.4113 | 35.5618 | 36.9477 | 35.3228 | 36.0176 | 36.9398 | 38.157 | 36.0095 | 37.6956 | 35.8625 | 38.1542 | 35.5316 | 37.8447 | 35.5061 | 36.9804 | 36.2434 | 38.0575 | 35.6776 | 38.7365 | 35.992 | 38.0936 | 39.1032 | 93.518 | 93.7395 | 93.3188
2022-09-07 22:04 | 0:14 | 16.5689 | 18.7238 | 20.8433 | 33.8356 | 36.9099 | 32.702 | 36.7548 | 32.3847 | 37.2723 | 34.729 | 34.2616 | 38.6594 | 32.0757 | 33.4257 | 35.4234 | 33.9408 | 33.4764 | 33.2903 | 34.2307 | 36.4612 | 30.9579 | 30.6597 | 32.9861 | 35.3004 | 33.9111 | 38.5675 | 35.9082 | 34.9524 | 34.044 | 35.9406 | 33.3488 | 35.5881 | 33.6426 | 34.9004 | 33.6741 | 35.725 | 35.4746 | 35.6097 | 36.7624 | 35.321 | 36.0263 | 36.9613 | 38.2417 | 36.0568 | 37.6773 | 35.9109 | 38.1258 | 35.5998 | 37.9143 | 35.5585 | 36.9735 | 36.373 | 38.1702 | 35.6546 | 38.883 | 36.0662 | 38.0134 | 39.1753 | 93.4241 | 93.6538 | 93.2844
2022-09-07 22:04 | 0:14 | 16.3585 | 18.5194 | 20.633 | 33.5874 | 36.7823 | 32.7969 | 36.7275 | 32.2724 | 37.2412 | 34.4821 | 34.0458 | 38.4866 | 31.8267 | 33.5614 | 35.222 | 33.9565 | 33.4068 | 33.0347 | 34.0802 | 36.3045 | 31.1569 | 30.835 | 33.1028 | 35.3714 | 33.8993 | 38.4597 | 35.9116 | 34.7641 | 34.0734 | 35.9716 | 33.395 | 35.5762 | 33.627 | 34.8538 | 33.7216 | 35.8152 | 35.5059 | 35.7058 | 37.0015 | 35.3474 | 36.0264 | 37.0183 | 38.2936 | 36.1372 | 37.6921 | 35.9149 | 38.1544 | 35.6657 | 37.9323 | 35.5416 | 37.1019 | 36.4308 | 38.1044 | 35.7564 | 38.9132 | 36.0832 | 38.1324 | 39.0938 | 93.3239 | 93.5662 | 93.2047
2022-09-07 22:05 | 0:14 | 16.1573 | 18.3213 | 20.4491 | 33.5756 | 36.6447 | 32.7377 | 36.6421 | 32.1666 | 37.1814 | 34.3936 | 34.0843 | 38.4493 | 31.6603 | 33.3592 | 35.1859 | 33.8344 | 33.242 | 33.0462 | 34.0124 | 36.3017 | 31.3034 | 30.9669 | 33.2007 | 35.3625 | 33.8962 | 38.6061 | 35.969 | 34.7532 | 34.154 | 35.9919 | 33.4503 | 35.3895 | 33.5651 | 34.7835 | 33.7291 | 35.6863 | 35.3898 | 35.6255 | 37.0468 | 35.3005 | 36.0209 | 37.0303 | 38.3234 | 36.2011 | 37.7196 | 35.9934 | 38.2502 | 35.7517 | 37.9617 | 35.6356 | 37.1053 | 36.548 | 38.1404 | 35.7499 | 38.9008 | 36.1459 | 38.2537 | 39.1607 | 93.2615 | 93.4862 | 93.1792
2022-09-07 22:05 | 0:15 | 15.9725 | 18.1764 | 20.2577 | 33.5662 | 36.5814 | 32.5223 | 36.5104 | 32.1086 | 37.0737 | 34.2049 | 34.1713 | 38.2794 | 31.5213 | 33.4683 | 35.3715 | 33.861 | 33.1443 | 33.1838 | 33.8954 | 36.0077 | 31.4169 | 31.0458 | 33.2373 | 35.3466 | 33.9094 | 38.7231 | 36.0176 | 34.7475 | 34.0408 | 36.027 | 33.5028 | 35.2635 | 33.5582 | 34.8611 | 33.7862 | 35.6635 | 35.404 | 35.6474 | 36.8772 | 35.2421 | 36.1002 | 37.0857 | 38.3595 | 36.285 | 37.7493 | 35.9922 | 38.3286 | 35.8234 | 38.0162 | 35.6345 | 37.1991 | 36.6011 | 38.1594 | 35.7469 | 38.8858 | 36.1942 | 38.2835 | 39.2574 | 93.2185 | 93.3996 | 93.215
2022-09-07 22:05 | 0:15 | 15.8869 | 17.9859 | 20.1282 | 33.3448 | 36.4822 | 32.5355 | 36.5803 | 31.8789 | 36.9842 | 34.4919 | 33.7437 | 38.2507 | 31.5674 | 33.0967 | 35.3531 | 33.716 | 33.1299 | 33.0301 | 33.9682 | 36.1067 | 31.5136 | 31.1298 | 33.3026 | 35.3273 | 33.9132 | 38.577 | 36.0263 | 34.7601 | 34.1144 | 35.9845 | 33.5563 | 35.2372 | 33.4675 | 34.8778 | 33.809 | 35.6429 | 35.3744 | 35.6509 | 36.7989 | 35.2408 | 36.136 | 37.0833 | 38.4542 | 36.3537 | 37.8795 | 36.0272 | 38.2051 | 35.9181 | 38.0218 | 35.7104 | 37.2251 | 36.6355 | 38.2079 | 35.7243 | 38.8528 | 36.253 | 38.4455 | 39.1758 | 93.1211 | 93.3262 | 93.0338
2022-09-07 22:05 | 0:15 | 15.6976 | 17.8083 | 19.9585 | 33.4349 | 36.4545 | 32.474 | 36.2991 | 31.819 | 36.8759 | 34.0712 | 33.6583 | 38.1968 | 31.5484 | 33.1919 | 35.0107 | 33.653 | 33.0939 | 33.0428 | 33.7903 | 36.0158 | 31.5827 | 31.1945 | 33.3454 | 35.2916 | 33.9293 | 38.5523 | 36.0264 | 34.6346 | 34.008 | 35.9687 | 33.5816 | 35.4228 | 33.5389 | 34.8845 | 33.8699 | 35.711 | 35.241 | 35.6664 | 36.7729 | 35.1581 | 36.1468 | 37.133 | 38.4423 | 36.3654 | 37.8405 | 36.0078 | 38.2677 | 35.9738 | 38.1069 | 35.7653 | 37.2093 | 36.696 | 38.225 | 35.8811 | 39.0119 | 36.3271 | 38.4144 | 39.1766 | 93.0479 | 93.2235 | 93.004
2022-09-07 22:05 | 0:15 | 15.1518 | 17.0671 | 19.6078 | 33.3121 | 36.3213 | 32.4453 | 36.3633 | 31.6933 | 36.8639 | 33.9816 | 33.6156 | 38.1014 | 31.2918 | 33.2633 | 34.986 | 33.628 | 32.8785 | 32.9029 | 33.7193 | 35.9674 | 31.6142 | 31.2262 | 33.3883 | 35.2927 | 33.9389 | 38.5952 | 36.0209 | 34.6823 | 34.1323 | 36.0677 | 33.6309 | 35.1424 | 33.3944 | 34.9897 | 33.8953 | 35.5491 | 35.2588 | 35.6078 | 36.8373 | 35.1411 | 36.1838 | 37.2619 | 38.4436 | 36.4426 | 37.8835 | 36.0504 | 38.2291 | 36.035 | 38.1259 | 35.7871 | 37.2946 | 36.7804 | 38.1817 | 35.7823 | 39.1129 | 36.3429 | 38.4278 | 39.2049 | 92.9325 | 93.1058 | 92.8897
2022-09-07 22:05 | 0:15 | 15.4828 | 15.4084 | 20.0715 | 33.0025 | 36.2097 | 32.2655 | 36.0823 | 31.5758 | 36.7299 | 34.1009 | 33.4862 | 38.0129 | 31.2552 | 33.1966 | 35.1176 | 33.4544 | 32.8989 | 32.8298 | 33.6743 | 35.9059 | 31.5503 | 31.2373 | 33.4192 | 35.2042 | 33.9477 | 38.5941 | 36.1002 | 34.7007 | 34.1508 | 36.0303 | 33.6802 | 35.2898 | 33.3652 | 34.929 | 33.9003 | 35.5367 | 35.1955 | 35.6051 | 36.8862 | 35.1092 | 36.1737 | 37.2686 | 38.506 | 36.5173 | 37.9631 | 36.0897 | 38.2774 | 36.1031 | 38.1491 | 35.8498 | 37.4092 | 36.7977 | 38.2704 | 35.7957 | 39.128 | 36.4116 | 38.5607 | 39.191 | 92.7924 | 92.9818 | 92.7359
2022-09-07 22:06 | 0:16 | 17.6242 | 17.3058 | 22.6188 | 33.3484 | 36.2 | 32.4338 | 36.0187 | 31.7127 | 36.7332 | 34.2243 | 33.5578 | 37.9476 | 31.4939 | 33.2982 | 35.2244 | 33.4787 | 32.9471 | 33.0662 | 33.7404 | 36.1099 | 31.5646 | 31.2634 | 33.5092 | 35.3857 | 34.0126 | 38.5679 | 36.136 | 34.7034 | 34.1364 | 36.1214 | 33.7389 | 35.0506 | 33.4742 | 34.9068 | 33.9495 | 35.6142 | 35.2858 | 35.6613 | 37.06 | 35.1701 | 36.2861 | 37.2536 | 38.562 | 36.5603 | 38.0073 | 36.0911 | 38.3308 | 36.1754 | 38.1492 | 35.8776 | 37.5112 | 36.8406 | 38.139 | 35.9693 | 38.952 | 36.4946 | 38.5772 | 39.2049 | 92.703 | 92.8709 | 92.7209
2022-09-07 22:06 | 0:16 | 19.6081 | 19.6298 | 24.8906 | 34.0232 | 36.2467 | 32.8533 | 36.1966 | 31.9646 | 36.6434 | 34.4446 | 33.5697 | 38.0335 | 31.8717 | 33.4058 | 35.2182 | 33.522 | 33.1846 | 33.4343 | 33.9353 | 36.2662 | 31.6083 | 31.2891 | 33.6386 | 35.6125 | 34.0364 | 38.7582 | 36.1468 | 34.6795 | 34.1949 | 36.1457 | 33.7536 | 35.2158 | 33.5834 | 35.0493 | 34.0155 | 35.7092 | 35.3836 | 35.662 | 37.2605 | 35.2205 | 36.3133 | 37.3098 | 38.6065 | 36.6504 | 38.1566 | 36.1456 | 38.2743 | 36.24 | 38.2433 | 35.9768 | 37.4294 | 36.9277 | 38.2496 | 35.8662 | 38.9656 | 36.5171 | 38.5395 | 39.2053 | 92.6522 | 92.7704 | 92.7027
2022-09-07 22:06 | 0:16 | 21.3935 | 21.8727 | 26.6685 | 34.4278 | 36.2768 | 33.0324 | 36.3839 | 32.1817 | 36.7196 | 34.5871 | 33.986 | 38.0573 | 32.1608 | 33.5966 | 35.3936 | 33.603 | 33.2703 | 33.6504 | 34.0243 | 36.2569 | 31.6777 | 31.3145 | 33.7891 | 35.7153 | 34.0905 | 38.6957 | 36.1838 | 34.6621 | 34.2473 | 36.061 | 33.8188 | 35.1469 | 33.7319 | 35.1057 | 34.0624 | 35.75 | 35.4262 | 35.7567 | 37.2904 | 35.3021 | 36.3296 | 37.3673 | 38.6225 | 36.7331 | 38.1654 | 36.1903 | 38.3193 | 36.3536 | 38.2776 | 35.9782 | 37.4314 | 36.9736 | 38.2007 | 35.9534 | 38.9975 | 36.5798 | 38.6359 | 39.166 | 92.5632 | 92.661 | 92.6237
2022-09-07 22:06 | 0:16 | 22.9705 | 23.9527 | 28.0554 | 34.7866 | 36.2801 | 33.1938 | 36.3667 | 32.4236 | 36.7185 | 34.7369 | 34.3522 | 38.0497 | 32.4124 | 33.8179 | 35.3212 | 33.6666 | 33.4886 | 33.8345 | 34.2085 | 36.5556 | 31.7757 | 31.3601 | 33.9355 | 35.8298 | 34.1489 | 38.7032 | 36.1737 | 34.9327 | 34.2403 | 36.1734 | 33.9043 | 35.2939 | 33.8478 | 35.2351 | 34.1462 | 35.8747 | 35.4215 | 35.8409 | 37.2912 | 35.3484 | 36.4519 | 37.3715 | 38.7179 | 36.79 | 38.0939 | 36.2396 | 38.3833 | 36.4227 | 38.3813 | 36.0367 | 37.5397 | 37.0049 | 38.2611 | 36.01 | 39.1167 | 36.6577 | 38.6405 | 39.2465 | 92.4834 | 92.4997 | 92.6155
2022-09-07 22:06 | 0:16 | 24.299 | 25.6972 | 29.0287 | 34.9838 | 36.3211 | 33.2589 | 36.4724 | 32.6154 | 36.8044 | 34.6717 | 34.6634 | 38.2057 | 32.5953 | 33.9186 | 35.4823 | 33.7179 | 33.6818 | 34.0564 | 34.2722 | 36.6266 | 31.8961 | 31.3683 | 34.0865 | 35.9302 | 34.2288 | 38.9054 | 36.2861 | 34.9209 | 34.2497 | 36.3338 | 33.9762 | 35.4958 | 33.9766 | 35.3575 | 34.1856 | 35.9516 | 35.5041 | 35.9304 | 37.3416 | 35.38 | 36.477 | 37.4683 | 38.7518 | 36.8902 | 38.2843 | 36.2543 | 38.4642 | 36.5128 | 38.5224 | 36.0861 | 37.6063 | 37.0939 | 38.3284 | 36.1121 | 39.1578 | 36.7284 | 38.7283 | 39.3126 | 92.317 | 92.3362 | 92.445
2022-09-07 22:06 | 0:16 | 25.4528 | 27.1398 | 29.7051 | 35.1795 | 36.3677 | 33.33 | 36.6942 | 32.7634 | 36.7721 | 34.7957 | 34.8169 | 38.2324 | 32.7869 | 34.0255 | 35.4542 | 33.7619 | 33.7653 | 34.2107 | 34.3103 | 36.6992 | 32.0239 | 31.4378 | 34.2442 | 36.0964 | 34.2774 | 38.8782 | 36.3133 | 34.9823 | 34.2788 | 36.2379 | 34.0712 | 35.3586 | 34.0787 | 35.4064 | 34.2652 | 35.9764 | 35.5191 | 35.9784 | 37.2767 | 35.4062 | 36.5173 | 37.5887 | 38.829 | 36.9747 | 38.3222 | 36.3044 | 38.4693 | 36.5939 | 38.522 | 36.2285 | 37.6488 | 37.1812 | 38.4178 | 36.1116 | 39.1006 | 36.8055 | 38.794 | 39.2891 | 92.1525 | 92.2766 | 92.2644
2022-09-07 22:07 | 0:16 | 26.4206 | 28.3031 | 30.1921 | 35.4294 | 36.4108 | 33.5518 | 36.5804 | 32.9617 | 36.7974 | 34.8497 | 34.7653 | 38.278 | 32.9055 | 34.0612 | 35.5676 | 33.7918 | 33.8567 | 34.3835 | 34.3953 | 36.7907 | 32.1835 | 31.4526 | 34.4329 | 36.1815 | 34.3505 | 38.8933 | 36.3296 | 35.0552 | 34.4046 | 36.2873 | 34.1528 | 35.4823 | 34.1832 | 35.459 | 34.3119 | 36.0277 | 35.4779 | 36.113 | 37.3025 | 35.4393 | 36.5592 | 37.6201 | 38.8065 | 37.1107 | 38.3051 | 36.386 | 38.4721 | 36.6582 | 38.6099 | 36.2852 | 37.6872 | 37.2137 | 38.4089 | 36.2533 | 39.1805 | 36.8739 | 38.7966 | 39.3323 | 92.0565 | 92.1934 | 92.2578
2022-09-07 22:07 | 0:17 | 27.2191 | 29.1728 | 30.4738 | 35.5219 | 36.4396 | 33.7181 | 36.7708 | 33.1168 | 36.7871 | 35.0378 | 35.0689 | 38.2362 | 33.0336 | 34.2046 | 35.5675 | 33.8607 | 33.9464 | 34.4511 | 34.4488 | 36.8568 | 32.3347 | 31.4803 | 34.5682 | 36.1803 | 34.398 | 38.8288 | 36.4519 | 35.0469 | 34.4485 | 36.3272 | 34.2078 | 35.443 | 34.2724 | 35.568 | 34.3819 | 36.0503 | 35.5544 | 36.2455 | 37.3169 | 35.4834 | 36.6328 | 37.6221 | 38.8521 | 37.1823 | 38.4104 | 36.4081 | 38.4964 | 36.7741 | 38.6043 | 36.3503 | 37.737 | 37.2945 | 38.4589 | 36.2713 | 39.2253 | 36.9543 | 38.7016 | 39.3301 | 92.1511 | 92.2451 | 92.2453
2022-09-07 22:07 | 0:17 | 27.8284 | 29.8587 | 30.667 | 35.7029 | 36.469 | 33.8355 | 36.7507 | 33.1618 | 36.8493 | 35.128 | 35.0865 | 38.2638 | 33.1219 | 34.2674 | 35.7679 | 33.8835 | 34.0869 | 34.513 | 34.4919 | 36.9031 | 32.4875 | 31.5161 | 34.7606 | 36.3729 | 34.4676 | 38.8284 | 36.477 | 35.0983 | 34.5049 | 36.414 | 34.2935 | 35.6161 | 34.3231 | 35.6309 | 34.441 | 36.0969 | 35.5856 | 36.3908 | 37.3708 | 35.5376 | 36.6736 | 37.6944 | 38.8919 | 37.2447 | 38.4226 | 36.4177 | 38.58 | 36.8814 | 38.6459 | 36.3853 | 37.8048 | 37.3317 | 38.5846 | 36.3701 | 39.308 | 37.0055 | 38.6985 | 39.3772 | 92.1693 | 92.3201 | 92.3477
2022-09-07 22:07 | 0:17 | 28.3254 | 30.32 | 30.8569 | 35.783 | 36.4583 | 33.8959 | 36.9719 | 33.2738 | 36.8569 | 35.1265 | 35.1843 | 38.2689 | 33.2333 | 34.3693 | 35.8423 | 33.948 | 34.2228 | 34.6261 | 34.5484 | 36.8648 | 32.636 | 31.531 | 34.9029 | 36.479 | 34.5955 | 38.8647 | 36.5173 | 35.1314 | 34.5788 | 36.5776 | 34.3424 | 35.6316 | 34.4448 | 35.7244 | 34.5365 | 36.1838 | 35.6006 | 36.3776 | 37.3994 | 35.5869 | 36.7585 | 37.7304 | 38.9663 | 37.354 | 38.5454 | 36.4892 | 38.5976 | 36.952 | 38.6768 | 36.4133 | 37.8406 | 37.4127 | 38.4996 | 36.4291 | 39.2244 | 37.0755 | 38.8654 | 39.4327 | 92.285 | 92.4121 | 92.4031
2022-09-07 22:07 | 0:17 | 28.7762 | 30.6699 | 31.0201 | 35.9587 | 36.4557 | 33.9309 | 36.8065 | 33.3944 | 36.8655 | 35.3152 | 35.346 | 38.2818 | 33.3367 | 34.499 | 35.7703 | 33.9572 | 34.279 | 34.6655 | 34.612 | 37.0172 | 32.7893 | 31.5615 | 35.081 | 36.4741 | 34.6286 | 38.9969 | 36.5592 | 35.1672 | 34.6217 | 36.5707 | 34.4582 | 35.5115 | 34.5271 | 35.8014 | 34.5976 | 36.1506 | 35.7521 | 36.3624 | 37.472 | 35.6413 | 36.79 | 37.82 | 39.0035 | 37.4305 | 38.5428 | 36.5543 | 38.678 | 37.0407 | 38.7363 | 36.4774 | 37.9245 | 37.4741 | 38.6078 | 36.4688 | 39.2127 | 37.1357 | 38.8846 | 39.4519 | 92.3608 | 92.5087 | 92.4467
2022-09-07 22:07 | 0:17 | 29.0887 | 30.9462 | 31.1079 | 36.0436 | 36.5083 | 33.9935 | 36.8699 | 33.4588 | 36.9096 | 35.2396 | 35.3574 | 38.2877 | 33.4567 | 34.5308 | 35.922 | 33.9981 | 34.3332 | 34.713 | 34.7171 | 37.0594 | 32.9228 | 31.5912 | 35.2086 | 36.6546 | 34.7143 | 39.0476 | 36.6328 | 35.1568 | 34.5977 | 36.5858 | 34.5379 | 35.7139 | 34.6015 | 35.8277 | 34.6802 | 36.2311 | 35.8195 | 36.4278 | 37.476 | 35.6999 | 36.7127 | 37.8695 | 39.0959 | 37.5371 | 38.5733 | 36.6245 | 38.6885 | 37.1178 | 38.83 | 36.5342 | 38.0173 | 37.5346 | 38.5827 | 36.5971 | 39.2225 | 37.1953 | 38.9851 | 39.556 | 92.3879 | 92.6073 | 92.5506
2022-09-07 22:08 | 0:18 | 29.3748 | 31.1219 | 31.2568 | 36.1629 | 36.4797 | 34.1087 | 36.8584 | 33.5851 | 36.9004 | 35.3198 | 35.3798 | 38.38 | 33.4881 | 34.5684 | 36.0021 | 34.0268 | 34.4048 | 34.7639 | 34.7076 | 37.1122 | 33.0812 | 31.6029 | 35.3567 | 36.6506 | 34.7706 | 39.1505 | 36.6736 | 35.2764 | 34.734 | 36.6135 | 34.5827 | 35.7054 | 34.6517 | 35.9058 | 34.707 | 36.2711 | 35.9219 | 36.4436 | 37.5918 | 35.747 | 36.6514 | 37.8938 | 39.1309 | 37.5957 | 38.6346 | 36.6696 | 38.7065 | 37.1921 | 38.9439 | 36.6174 | 38.0159 | 37.5929 | 38.7627 | 36.6192 | 39.3631 | 37.2597 | 39.0095 | 39.5523 | 92.5006 | 92.7073 | 92.5663
2022-09-07 22:08 | 0:18 | 29.5931 | 31.2587 | 31.3413 | 36.1241 | 36.4982 | 34.0916 | 36.9028 | 33.5761 | 36.9571 | 35.3472 | 35.5313 | 38.3689 | 33.5668 | 34.6156 | 35.8727 | 34.0647 | 34.5057 | 34.8436 | 34.7795 | 37.1798 | 33.2482 | 31.6247 | 35.5 | 36.7731 | 34.8515 | 39.1722 | 36.7585 | 35.1928 | 34.7774 | 36.7071 | 34.6661 | 35.5922 | 34.7519 | 35.9344 | 34.7799 | 36.283 | 35.9828 | 36.4334 | 37.6983 | 35.7725 | 36.6645 | 37.9764 | 39.0824 | 37.6748 | 38.7463 | 36.686 | 38.7575 | 37.2587 | 38.9633 | 36.6317 | 38.0938 | 37.6402 | 38.8349 | 36.6206 | 39.3847 | 37.3255 | 39.0675 | 39.5105 | 92.5775 | 92.7877 | 92.5984
2022-09-07 22:08 | 0:18 | 29.7935 | 31.3416 | 31.4047 | 36.3669 | 36.508 | 34.1285 | 36.9223 | 33.6098 | 36.9879 | 35.3716 | 35.5256 | 38.315 | 33.6338 | 34.74 | 36.0937 | 34.1106 | 34.5967 | 34.8958 | 34.8064 | 37.2358 | 33.4199 | 31.1285 | 35.6429 | 36.8371 | 34.9066 | 39.1427 | 36.79 | 35.2831 | 34.8623 | 36.6776 | 34.7475 | 35.7222 | 34.8013 | 35.9776 | 34.8489 | 36.3642 | 36.0058 | 36.477 | 37.6831 | 35.8131 | 36.7637 | 38.0548 | 39.1716 | 37.744 | 38.7881 | 36.7594 | 38.8322 | 37.3207 | 39.0203 | 36.7593 | 38.1802 | 37.7112 | 38.8338 | 36.6835 | 39.3947 | 37.3664 | 39.0439 | 39.5246 | 92.6677 | 92.9094 | 92.7667
2022-09-07 22:08 | 0:18 | 30.5049 | 27.7944 | 31.1569 | 36.2534 | 36.5371 | 34.1136 | 36.8789 | 33.562 | 37.0067 | 35.3682 | 35.519 | 38.4319 | 33.6459 | 34.6814 | 36.1686 | 34.1375 | 34.5811 | 34.8663 | 34.807 | 37.2361 | 33.7593 | 28.8229 | 35.0448 | 36.8354 | 34.8582 | 39.0023 | 36.7127 | 35.2649 | 34.866 | 36.6192 | 34.5829 | 35.7388 | 34.8346 | 35.9895 | 34.8613 | 36.3759 | 36.0548 | 36.5275 | 37.6577 | 35.8847 | 36.9333 | 37.986 | 39.0674 | 37.5591 | 38.6647 | 36.7778 | 38.8068 | 37.1117 | 38.8294 | 36.6278 | 37.9589 | 37.5998 | 38.7031 | 36.7089 | 39.3897 | 37.2579 | 39.0127 | 39.5555 | 92.8555 | 93.0575 | 92.9475
2022-09-07 22:08 | 0:18 | 31.4877 | 31.4423 | 31.4184 | 36.1456 | 36.5953 | 34.1993 | 36.9827 | 33.73 | 37.0263 | 35.4284 | 35.7634 | 38.3639 | 33.7499 | 34.7937 | 35.9923 | 34.1778 | 34.7042 | 34.9224 | 34.8634 | 37.1646 | 33.744 | 30.9917 | 34.8164 | 36.7863 | 34.8941 | 38.9016 | 36.6514 | 35.304 | 34.7869 | 36.5658 | 34.6109 | 35.8237 | 34.8516 | 35.9818 | 34.8413 | 36.3221 | 36.0692 | 36.5004 | 37.657 | 35.9356 | 36.9424 | 37.9517 | 39.0479 | 37.4905 | 38.5511 | 36.7657 | 38.8449 | 37.1291 | 38.8516 | 36.6011 | 37.9178 | 37.6566 | 38.6505 | 36.6892 | 39.3848 | 37.2515 | 39.1062 | 39.5797 | 92.9923 | 93.1817 | 92.9577
2022-09-07 22:08 | 0:18 | 32.7091 | 31.8848 | 31.6408 | 36.4061 | 36.6212 | 34.3836 | 37.1287 | 33.8494 | 37.0824 | 35.4979 | 35.8427 | 38.356 | 33.8201 | 34.8258 | 35.9721 | 34.2457 | 34.8047 | 34.9918 | 34.9456 | 37.2488 | 33.8997 | 31.4393 | 35.0388 | 36.9143 | 34.9513 | 38.9898 | 36.6645 | 35.2585 | 34.8153 | 36.672 | 34.7448 | 35.8249 | 34.9464 | 36.0507 | 34.9436 | 36.3437 | 36.0804 | 36.5692 | 37.6568 | 35.9951 | 36.9785 | 37.9939 | 39.0523 | 37.5547 | 38.6812 | 36.8015 | 38.9054 | 37.1988 | 38.8626 | 36.6166 | 37.9664 | 37.6739 | 38.7289 | 36.7544 | 39.4423 | 37.325 | 39.0176 | 39.6424 | 93.1118 | 93.2943 | 93.019
2022-09-07 22:09 | 0:18 | 33.6869 | 31.8617 | 31.8327 | 36.4828 | 36.6362 | 34.411 | 37.1387 | 33.9161 | 37.1063 | 35.5628 | 35.8201 | 38.3366 | 33.9227 | 34.8415 | 36.1905 | 34.2982 | 34.8664 | 35.0587 | 35.0254 | 37.3255 | 34.1951 | 31.6149 | 35.2984 | 36.9429 | 35.0287 | 39.2045 | 36.7637 | 35.3052 | 34.9179 | 36.7916 | 34.8234 | 35.9281 | 35.0186 | 36.0982 | 35.0261 | 36.4518 | 36.1942 | 36.6412 | 37.6259 | 36.0557 | 37.0278 | 38.0791 | 39.1579 | 37.6557 | 38.8405 | 36.8684 | 38.8426 | 37.2986 | 38.8921 | 36.7388 | 38.0624 | 37.7743 | 38.8878 | 36.8288 | 39.46 | 37.412 | 39.167 | 39.6542 | 93.1523 | 93.3954 | 93.0657
2022-09-07 22:09 | 0:19 | 34.3647 | 31.8612 | 32.132 | 36.5872 | 36.6387 | 34.554 | 37.206 | 34.0708 | 37.103 | 35.5732 | 35.8437 | 38.3477 | 34.0175 | 34.9996 | 36.235 | 34.3739 | 34.9137 | 35.1474 | 35.1043 | 37.43 | 34.5325 | 31.6677 | 35.5646 | 37.0121 | 35.1054 | 39.3899 | 36.9333 | 35.4286 | 34.9111 | 36.7939 | 34.9734 | 36.002 | 35.1165 | 36.1576 | 35.0891 | 36.4978 | 36.1844 | 36.6929 | 37.763 | 36.1113 | 37.1363 | 38.1695 | 39.2035 | 37.7642 | 38.8337 | 36.9387 | 38.9675 | 37.4366 | 39.02 | 36.7869 | 38.1604 | 37.8436 | 38.9555 | 36.9039 | 39.4651 | 37.49 | 39.1487 | 39.6382 | 93.2479 | 93.4967 | 93.0932
2022-09-07 22:09 | 0:19 | 34.8402 | 31.8705 | 32.5342 | 36.7467 | 36.7071 | 34.6693 | 37.2472 | 34.1369 | 37.1567 | 35.711 | 35.9482 | 38.4436 | 34.0609 | 35.0384 | 36.1407 | 34.4209 | 34.9802 | 35.1863 | 35.1973 | 37.4298 | 34.8267 | 31.7039 | 35.7996 | 37.0919 | 35.1774 | 39.3397 | 36.9424 | 35.5697 | 35.092 | 36.9031 | 35.1347 | 36.1042 | 35.2308 | 36.2643 | 35.2169 | 36.6315 | 36.279 | 36.797 | 37.7467 | 36.1729 | 37.1675 | 38.2101 | 39.2258 | 37.8711 | 38.8887 | 36.9851 | 38.9648 | 37.5382 | 39.1608 | 36.9062 | 38.2475 | 37.9101 | 38.8597 | 37.0095 | 39.4377 | 37.5986 | 39.2846 | 39.5644 | 93.3752 | 93.6875 | 93.2047
2022-09-07 22:09 | 0:19 | 35.1174 | 31.8692 | 32.8853 | 36.7751 | 36.722 | 34.6363 | 37.347 | 34.1786 | 37.1525 | 35.7493 | 36.0071 | 38.3883 | 34.1831 | 35.1469 | 36.4218 | 34.4997 | 35.0719 | 35.2432 | 35.2505 | 37.4524 | 35.0061 | 31.7068 | 35.9741 | 37.1938 | 35.2472 | 39.3355 | 36.9785 | 35.5536 | 35.1312 | 37.0885 | 35.2197 | 36.0285 | 35.314 | 36.3871 | 35.2986 | 36.6278 | 36.3173 | 36.8788 | 37.9 | 36.2386 | 37.285 | 38.3144 | 39.3103 | 37.9568 | 38.9705 | 37.0186 | 39.0064 | 37.6036 | 39.1141 | 36.9552 | 38.3204 | 37.9938 | 38.9771 | 37.0503 | 39.5239 | 37.6635 | 39.3076 | 39.6366 | 93.5153 | 93.8311 | 93.3149
2022-09-07 22:09 | 0:19 | 35.2245 | 31.8719 | 33.1345 | 36.8602 | 36.7568 | 34.7259 | 37.2791 | 34.2774 | 37.2033 | 35.7583 | 36.1493 | 38.3878 | 34.2376 | 35.1906 | 36.3623 | 34.5459 | 35.1625 | 35.317 | 35.3264 | 37.5094 | 35.0496 | 31.7318 | 36.0597 | 37.3302 | 35.3607 | 39.379 | 37.0278 | 35.676 | 35.2326 | 37.1224 | 35.314 | 36.099 | 35.3876 | 36.4146 | 35.4006 | 36.6745 | 36.3639 | 36.9228 | 37.8023 | 36.3009 | 37.3185 | 38.3322 | 39.3552 | 38.0766 | 38.9901 | 37.0836 | 39.0988 | 37.7027 | 39.2355 | 37.0717 | 38.3618 | 38.0489 | 39.0343 | 37.1527 | 39.5728 | 37.7437 | 39.3198 | 39.6836 | 93.6282 | 93.9787 | 93.398
2022-09-07 22:09 | 0:19 | 35.2784 | 31.8899 | 33.1867 | 36.958 | 36.8028 | 34.8691 | 37.2702 | 34.362 | 37.2457 | 35.8715 | 36.0218 | 38.4247 | 34.3575 | 35.2447 | 36.4415 | 34.608 | 35.2027 | 35.3602 | 35.3687 | 37.5664 | 35.0849 | 31.7339 | 36.1515 | 37.3529 | 35.395 | 39.54 | 37.1363 | 35.6789 | 35.2118 | 37.175 | 35.4206 | 36.1375 | 35.4655 | 36.4828 | 35.4968 | 36.7509 | 36.435 | 36.9679 | 37.8883 | 36.3698 | 37.3577 | 38.4093 | 39.4128 | 38.1592 | 39.1128 | 37.1445 | 39.1922 | 37.8154 | 39.2655 | 37.1598 | 38.4654 | 38.1051 | 39.0983 | 37.2987 | 39.5819 | 37.8198 | 39.362 | 39.7269 | 93.8442 | 94.2004 | 93.4878
2022-09-07 22:10 | 0:20 | 35.3537 | 31.8857 | 33.1958 | 37.0365 | 36.8051 | 34.8509 | 37.3379 | 34.3707 | 37.2833 | 35.8569 | 36.1259 | 38.5394 | 34.428 | 35.3103 | 36.4765 | 34.6594 | 35.2708 | 35.4612 | 35.4546 | 37.6616 | 35.2033 | 31.7536 | 36.2403 | 37.3896 | 35.479 | 39.5344 | 37.1675 | 35.7401 | 35.2805 | 37.1867 | 35.4863 | 36.2374 | 35.5583 | 36.5389 | 35.5733 | 36.7737 | 36.4837 | 36.9985 | 37.8385 | 36.4472 | 37.4196 | 38.4715 | 39.468 | 38.2465 | 39.1179 | 37.2388 | 39.1873 | 37.8664 | 39.3021 | 37.1787 | 38.5055 | 38.1987 | 39.0359 | 37.2893 | 39.6563 | 37.873 | 39.5198 | 39.787 | 94.0876 | 94.3665 | 93.6878
2022-09-07 22:10 | 0:20 | 35.5788 | 31.9132 | 33.3084 | 37.0669 | 36.8421 | 34.9199 | 37.5639 | 34.4654 | 37.3067 | 35.908 | 36.1813 | 38.4591 | 34.5001 | 35.3734 | 36.5079 | 34.7112 | 35.3566 | 35.5171 | 35.4838 | 37.6264 | 35.3468 | 31.7703 | 36.3668 | 37.5219 | 35.5607 | 39.5466 | 37.285 | 35.7413 | 35.4441 | 37.2234 | 35.5996 | 36.2034 | 35.624 | 36.6255 | 35.6459 | 36.8074 | 36.5549 | 37.0739 | 37.9216 | 36.495 | 37.4456 | 38.5333 | 39.5246 | 38.3037 | 39.2167 | 37.2665 | 39.1799 | 37.9495 | 39.3899 | 37.2734 | 38.5407 | 38.25 | 39.1921 | 37.3438 | 39.6565 | 37.9679 | 39.4641 | 39.8255 | 94.2464 | 94.5443 | 93.7885
2022-09-07 22:10 | 0:20 | 35.877 | 31.9251 | 33.5069 | 37.1021 | 36.8631 | 34.9265 | 37.5055 | 34.5294 | 37.3496 | 35.9897 | 36.3064 | 38.4338 | 34.5973 | 35.4789 | 36.6214 | 34.7996 | 35.4139 | 35.569 | 35.5576 | 37.6899 | 35.4918 | 31.7775 | 36.4875 | 37.585 | 35.619 | 39.7431 | 37.3185 | 35.7986 | 35.4543 | 37.3152 | 35.6701 | 36.3993 | 35.7372 | 36.8804 | 35.75 | 36.9239 | 36.5921 | 37.1204 | 37.9121 | 36.5423 | 37.4529 | 38.5548 | 39.5223 | 38.3864 | 39.2372 | 37.3239 | 39.2848 | 38.0108 | 39.4445 | 37.3319 | 38.6231 | 38.3264 | 39.2243 | 37.3542 | 39.7291 | 38.0103 | 39.5319 | 39.8394 | 94.3977 | 94.7272 | 93.9601
2022-09-07 22:10 | 0:20 | 35.9558 | 31.9466 | 33.6182 | 37.1548 | 36.8979 | 35.0815 | 37.5924 | 34.6185 | 37.3589 | 36.0729 | 36.3425 | 38.4775 | 34.6684 | 35.5749 | 36.6853 | 34.861 | 35.4515 | 35.6462 | 35.6454 | 37.8504 | 35.6599 | 31.7932 | 36.6376 | 37.6444 | 35.6927 | 39.6659 | 37.3577 | 35.8312 | 35.5811 | 37.3468 | 35.7842 | 36.351 | 35.769 | 36.9511 | 35.8253 | 36.9099 | 36.6162 | 37.1806 | 37.9499 | 36.6164 | 37.5634 | 38.6138 | 39.5761 | 38.4391 | 39.363 | 37.3869 | 39.2842 | 38.085 | 39.475 | 37.3769 | 38.6603 | 38.3902 | 39.2623 | 37.3531 | 39.8445 | 38.0932 | 39.5819 | 39.9501 | 94.6153 | 94.9545 | 94.0357
2022-09-07 22:10 | 0:20 | 36.1515 | 31.9491 | 33.7572 | 37.1711 | 36.9263 | 35.1695 | 37.5752 | 34.7023 | 37.3511 | 36.0783 | 36.3292 | 38.4539 | 34.7111 | 35.6362 | 36.6536 | 34.9058 | 35.5415 | 35.692 | 35.6974 | 37.8194 | 35.817 | 31.9066 | 36.7744 | 37.6968 | 35.7857 | 39.7861 | 37.4196 | 35.9006 | 35.6125 | 37.3975 | 35.8629 | 36.477 | 35.8826 | 37.0198 | 35.9031 | 36.9391 | 36.7049 | 37.2174 | 37.9778 | 36.6846 | 37.664 | 38.6324 | 39.646 | 38.5449 | 39.3548 | 37.4335 | 39.3982 | 38.159 | 39.5063 | 37.4483 | 38.7484 | 38.4362 | 39.294 | 37.5105 | 39.8282 | 38.1759 | 39.6244 | 39.9515 | 94.8037 | 95.1311 | 94.2713
2022-09-07 22:10 | 0:20 | 36.3016 | 31.9959 | 33.9227 | 37.3085 | 36.9629 | 35.2313 | 37.5651 | 34.7747 | 37.3855 | 36.1841 | 36.3772 | 38.496 | 34.8025 | 35.6675 | 36.7073 | 34.9416 | 35.6078 | 35.7458 | 35.7708 | 37.8945 | 35.963 | 31.8416 | 36.9069 | 37.811 | 35.8806 | 39.6445 | 37.4456 | 35.9846 | 35.7144 | 37.4419 | 35.9524 | 36.4272 | 35.9505 | 37.0914 | 35.9305 | 36.9855 | 36.8497 | 37.3387 | 38.1375 | 36.7623 | 37.7114 | 38.732 | 39.7005 | 38.6091 | 39.3986 | 37.4683 | 39.3901 | 38.2373 | 39.5712 | 37.5323 | 38.8141 | 38.4938 | 39.2871 | 37.5721 | 39.8846 | 38.2288 | 39.6524 | 39.9393 | 94.841 | 95.273 | 94.3379
2022-09-07 22:11 | 0:20 | 36.4749 | 32.0333 | 34.0822 | 37.3558 | 36.9895 | 35.2899 | 37.7514 | 34.8184 | 37.4868 | 36.248 | 36.492 | 38.5513 | 34.9319 | 35.7129 | 36.9971 | 35.0494 | 35.7436 | 35.8484 | 35.8119 | 37.9607 | 36.1361 | 31.8733 | 37.0384 | 37.8518 | 35.9229 | 39.727 | 37.4529 | 36.0157 | 35.9034 | 37.5879 | 36.0414 | 36.6089 | 36.0465 | 37.1782 | 36.1935 | 37.0928 | 36.8695 | 37.5013 | 38.1024 | 36.8015 | 37.8322 | 38.8281 | 39.7387 | 38.686 | 39.5158 | 37.5407 | 39.4412 | 38.3022 | 39.7026 | 37.5853 | 38.8528 | 38.592 | 39.3131 | 37.5973 | 39.903 | 38.3098 | 39.7496 | 40.0797 | 95.0233 | 95.4178 | 94.3877
2022-09-07 22:11 | 0:21 | 36.6544 | 32.0855 | 34.2499 | 37.4737 | 37.0369 | 35.4194 | 37.688 | 34.9131 | 37.5105 | 36.2396 | 36.5416 | 38.5762 | 35.0384 | 35.7958 | 37.0736 | 35.1135 | 35.7672 | 35.9009 | 35.8541 | 38.0087 | 36.3722 | 31.9345 | 37.1844 | 37.9244 | 36.0281 | 39.7847 | 37.5634 | 36.1978 | 35.9151 | 37.5446 | 36.14 | 36.5624 | 36.1336 | 37.2264 | 36.2921 | 37.1088 | 36.9195 | 37.4825 | 38.1702 | 36.8804 | 37.8407 | 38.8933 | 39.8242 | 38.7613 | 39.5281 | 37.5983 | 39.485 | 38.3961 | 39.7024 | 37.6092 | 38.9175 | 38.65 | 39.4299 | 37.6261 | 39.9415 | 38.3679 | 39.7365 | 40.0543 | 95.0642 | 95.5175 | 94.3099
2022-09-07 22:11 | 0:21 | 36.8171 | 32.1226 | 34.4232 | 37.5872 | 37.0718 | 35.5166 | 37.6912 | 35.0327 | 37.5428 | 36.2809 | 36.5859 | 38.609 | 35.1109 | 35.8946 | 37.1117 | 35.1794 | 35.8454 | 35.9373 | 35.926 | 38.0997 | 36.6321 | 32.0773 | 37.3438 | 38.0029 | 36.0992 | 40.009 | 37.664 | 36.1699 | 36.0283 | 37.6736 | 36.247 | 36.6933 | 36.1913 | 37.2967 | 36.243 | 37.2032 | 37.1782 | 37.57 | 38.1879 | 36.9511 | 37.913 | 38.9304 | 39.8399 | 38.8251 | 39.5518 | 37.6447 | 39.5478 | 38.4523 | 39.7778 | 37.6899 | 39.0391 | 38.6962 | 39.5214 | 37.7921 | 39.9713 | 38.4328 | 39.793 | 40.1083 | 95.1681 | 95.6004 | 94.4908
2022-09-07 22:11 | 0:21 | 37.0301 | 32.2174 | 34.5993 | 37.6531 | 37.1238 | 35.6309 | 37.7785 | 35.1403 | 37.5939 | 36.4323 | 36.7097 | 38.6495 | 35.2492 | 35.9598 | 37.0843 | 35.2013 | 35.9812 | 36.0582 | 36.0677 | 38.1091 | 36.9822 | 33.1385 | 37.5326 | 38.1046 | 36.1767 | 39.9511 | 37.7114 | 36.3378 | 36.0055 | 37.7418 | 36.3696 | 36.6681 | 36.2986 | 37.368 | 36.3814 | 37.2851 | 37.2264 | 37.5987 | 38.2341 | 37.0198 | 37.9625 | 38.9958 | 39.9025 | 38.9037 | 39.6498 | 37.7547 | 39.6061 | 38.5496 | 39.8368 | 37.7965 | 39.0414 | 38.7595 | 39.5721 | 37.8622 | 39.9623 | 38.5071 | 39.8576 | 40.1288 | 95.2718 | 95.6874 | 94.5534
2022-09-07 22:11 | 0:21 | 37.218 | 32.3356 | 34.7813 | 37.7635 | 37.1595 | 35.742 | 37.827 | 35.2806 | 37.6715 | 36.5144 | 36.8264 | 38.6541 | 35.3439 | 36.0417 | 37.0924 | 35.2949 | 36.0451 | 36.153 | 36.1425 | 38.1713 | 37.272 | 33.7506 | 37.7251 | 38.1739 | 36.2696 | 40.3201 | 37.8322 | 36.3447 | 36.1935 | 38.0365 | 36.4698 | 36.8267 | 36.3585 | 37.4437 | 36.5213 | 37.364 | 37.2967 | 37.6845 | 38.2596 | 37.0914 | 38.0425 | 39.0302 | 39.9254 | 38.9752 | 39.6832 | 37.7879 | 39.6905 | 38.601 | 39.9021 | 37.8683 | 39.0784 | 38.8061 | 39.4779 | 37.9021 | 40.0468 | 38.5709 | 39.9826 | 40.1258 | 95.3396 | 95.6921 | 94.585
2022-09-07 22:11 | 0:21 | 37.394 | 32.4989 | 34.9551 | 37.882 | 37.1823 | 35.8982 | 37.8805 | 35.3846 | 37.6868 | 36.616 | 36.9056 | 38.6828 | 35.4459 | 36.1913 | 37.1416 | 35.412 | 36.1217 | 36.2241 | 36.2204 | 38.2394 | 37.4996 | 34.2552 | 37.8635 | 38.22 | 36.3405 | 40.3173 | 37.8407 | 36.4572 | 36.2921 | 37.9323 | 36.5927 | 36.8049 | 36.4526 | 37.5283 | 36.4964 | 37.4127 | 37.368 | 37.718 | 38.3611 | 37.1782 | 38.1478 | 39.1214 | 39.9828 | 39.0427 | 39.752 | 37.84 | 39.7505 | 38.6845 | 39.9636 | 37.9357 | 39.1616 | 38.8843 | 39.6065 | 37.938 | 40.0959 | 38.6407 | 39.9177 | 40.2139 | 95.1503 | 95.5307 | 94.4015
2022-09-07 22:12 | 0:22 | 37.5802 | 32.7162 | 35.0972 | 37.9926 | 37.251 | 35.9114 | 37.899 | 35.4226 | 37.7526 | 36.6788 | 36.9863 | 38.6994 | 35.5462 | 36.2814 | 37.3076 | 35.4575 | 36.2261 | 36.3157 | 36.3064 | 38.3543 | 37.7289 | 35.1064 | 38.0295 | 38.3577 | 36.4689 | 40.2716 | 37.913 | 36.5709 | 36.243 | 37.9714 | 36.701 | 36.89 | 36.5496 | 37.611 | 36.6274 | 37.4984 | 37.4437 | 37.7933 | 38.4118 | 37.2264 | 38.2764 | 39.1995 | 40.0346 | 39.1434 | 39.7984 | 37.9071 | 39.7904 | 38.765 | 39.9686 | 38.0135 | 39.2301 | 38.9538 | 39.6605 | 38.0779 | 40.143 | 38.7088 | 39.977 | 40.2537 | 94.8722 | 95.3027 | 94.1962
2022-09-07 22:12 | 0:22 | 37.7308 | 32.8791 | 35.2862 | 38.0699 | 37.3113 | 36.0813 | 37.9552 | 35.6169 | 37.7937 | 36.7695 | 37.1628 | 38.7599 | 35.6355 | 36.3192 | 37.4076 | 35.5532 | 36.3327 | 36.405 | 36.3426 | 38.4397 | 37.881 | 35.4107 | 38.1633 | 38.4023 | 36.5649 | 40.3771 | 37.9625 | 36.5612 | 36.3814 | 38.0462 | 36.7777 | 36.9481 | 36.6252 | 37.7179 | 36.8311 | 37.5035 | 37.5283 | 37.9112 | 38.5063 | 37.2967 | 38.3744 | 39.2726 | 40.0945 | 39.2224 | 39.8642 | 37.9817 | 39.8362 | 38.8373 | 40.047 | 38.0791 | 39.2862 | 39.0303 | 39.6774 | 38.154 | 40.2632 | 38.7536 | 40.0836 | 40.4064 | 94.6555 | 95.0345 | 94.1054
2022-09-07 22:12 | 0:22 | 37.8891 | 33.1697 | 35.4346 | 38.201 | 37.3798 | 36.1565 | 37.9798 | 35.705 | 37.8725 | 36.8601 | 37.2023 | 38.859 | 35.7743 | 36.4685 | 37.384 | 35.6306 | 36.4234 | 36.4542 | 36.4688 | 38.5615 | 38.0521 | 35.9721 | 38.288 | 38.4977 | 36.6285 | 40.5046 | 38.0425 | 36.6475 | 36.5213 | 38.1564 | 36.877 | 37.0159 | 36.7415 | 38.0274 | 49.0133 | 37.6031 | 37.611 | 37.9749 | 38.5752 | 37.368 | 52.6247 | 39.3338 | 40.1284 | 39.3168 | 39.8935 | 38.0618 | 39.9358 | 38.9398 | 40.1349 | 38.1517 | 39.3473 | 39.0777 | 39.7593 | 38.2203 | 40.2534 | 38.8238 | 40.0955 | 40.4609 | 94.4676 | 94.8311 | 93.939
2022-09-07 22:12 | 0:22 | 38.0382 | 33.5268 | 35.5854 | 38.2573 | 37.4269 | 36.3232 | 38.0791 | 35.8236 | 37.904 | 36.9318 | 37.3124 | 38.911 | 35.8804 | 36.565 | 37.4511 | 35.7207 | 36.4801 | 36.5836 | 36.5827 | 38.6048 | 38.2088 | 36.1229 | 38.4279 | 38.5864 | 36.7138 | 40.5049 | 38.1478 | 36.6748 | 36.4964 | 38.1941 | 36.9915 | 37.0271 | 36.8212 | 38.4779 | 52.0582 | 37.6808 | 37.7179 | 38.0349 | 38.5736 | 37.4437 | 55.7996 | 39.3835 | 40.1656 | 39.415 | 40.0144 | 38.1131 | 39.9766 | 38.9912 | 40.195 | 38.1865 | 39.3958 | 39.1649 | 39.8899 | 38.2947 | 40.2669 | 38.9251 | 40.2187 | 40.4069 | 94.3071 | 94.6867 | 93.8706
2022-09-07 22:12 | 0:22 | 38.1799 | 33.9935 | 35.7343 | 38.4085 | 37.4904 | 36.4188 | 38.0998 | 35.9302 | 37.9774 | 37.0183 | 37.3786 | 38.9495 | 35.9434 | 36.5658 | 37.5993 | 35.76 | 36.5591 | 36.6631 | 36.6645 | 38.6132 | 38.4065 | 36.6524 | 38.5925 | 38.6612 | 36.8426 | 40.4514 | 38.2764 | 36.8124 | 36.6274 | 38.1783 | 37.0985 | 37.2054 | 36.904 | 38.6264 | 46.3731 | 37.7137 | 38.0274 | 38.1463 | 38.6808 | 37.5283 | 49.1027 | 39.4637 | 40.2517 | 39.4591 | 40.1619 | 38.1764 | 40.0424 | 39.1042 | 40.2333 | 38.2816 | 39.4745 | 39.2316 | 39.934 | 38.3378 | 40.3795 | 39.0115 | 40.1907 | 40.4619 | 94.1966 | 94.5581 | 93.7851
2022-09-07 22:12 | 0:22 | 38.3132 | 34.5609 | 35.8355 | 38.4651 | 37.5416 | 36.4565 | 38.1521 | 36.0491 | 38.0146 | 37.1416 | 37.459 | 38.9553 | 36.0636 | 36.7067 | 37.6275 | 35.8674 | 36.715 | 36.7676 | 36.7388 | 38.6664 | 38.4993 | 36.7924 | 38.6917 | 38.7365 | 36.9218 | 40.6362 | 38.3744 | 36.891 | 36.8311 | 38.3489 | 37.5181 | 37.3626 | 37.0692 | 38.3672 | 41.9156 | 37.7728 | 38.4779 | 38.1688 | 38.7223 | 37.611 | 45.3239 | 45.8043 | 52.4888 | 42.9254 | 64.1457 | 47.0372 | 48.4306 | 43.5956 | 56.8484 | 46.1259 | 53.2598 | 42.4001 | 46.3226 | 42.7654 | 47.2916 | 40.343 | 40.4702 | 43.921 | 94.1405 | 94.4686 | 93.7968
2022-09-07 22:13 | 0:22 | 34.8351 | 34.3878 | 35.4243 | 39.0686 | 37.6501 | 37.4754 | 38.6544 | 36.2807 | 38.1118 | 37.7657 | 38.0352 | 39.0733 | 36.2727 | 38.4041 | 38.4426 | 36.3204 | 37.1774 | 38.2099 | 37.3265 | 39.347 | 36.7854 | 35.1436 | 38.2495 | 44.1162 | 50.0103 | 54.4371 | 52.6247 | 53.9329 | 49.0133 | 50.4293 | 48.0299 | 40.3815 | 43.9603 | 38.4026 | 40.2943 | 40.6972 | 38.6264 | 45.386 | 42.4043 | 37.7179 | 43.5881 | 81.9917 | 78.3027 | 77.563 | 79.8697 | 58.7994 | 63.0764 | 53.1851 | 69.6067 | 54.0351 | 66.4659 | 48.7573 | 55.2827 | 46.8549 | 52.5754 | 41.7336 | 45.0135 | 48.1027 | 94.1101 | 94.3705 | 93.8307
2022-09-07 22:13 | 0:23 | 29.9994 | 31.0042 | 33.2856 | 41.6668 | 37.9732 | 42.6596 | 39.6953 | 38.3576 | 38.4697 | 39.5468 | 40.2202 | 39.4894 | 37.4748 | 41.5278 | 41.2646 | 37.6707 | 39.0814 | 41.112 | 39.0434 | 40.7638 | 37.2784 | 30.739 | 39.0819 | 47.5438 | 52.0304 | 57.5179 | 55.7996 | 55.9886 | 52.0582 | 53.5041 | 49.6641 | 41.8641 | 45.6417 | 38.33 | 39.6782 | 41.9412 | 38.3672 | 47.2278 | 44.6742 | 38.0274 | 42.9296 | 85.0833 | 84.2251 | 83.1788 | 84.0115 | 56.7853 | 61.5521 | 50.0222 | 63.586 | 52.8115 | 59.2187 | 47.3877 | 51.6803 | 47.0631 | 49.1862 | 42.1269 | 45.7167 | 47.0193 | 94.0044 | 94.2663 | 93.7432
2022-09-07 22:13 | 0:23 | 29.8605 | 30.0604 | 32.661 | 43.3699 | 38.1665 | 42.2158 | 39.6718 | 38.7774 | 38.8156 | 40.7492 | 40.2076 | 39.7245 | 38.2833 | 41.7985 | 40.8937 | 37.4115 | 40.1756 | 40.8694 | 38.896 | 42.0509 | 37.2073 | 29.9614 | 38.1031 | 44.4236 | 43.7649 | 50.7616 | 49.1027 | 47.3876 | 46.3731 | 45.6547 | 42.5961 | 40.5129 | 41.0316 | 38.4297 | 39.2109 | 41.3187 | 38.4026 | 43.7592 | 42.8037 | 38.4779 | 42.4198 | 88.6944 | 89.0156 | 86.771 | 91.7437 | 47.7867 | 49.2014 | 43.5499 | 52.1711 | 46.2092 | 47.6707 | 43.4555 | 46.512 | 43.8802 | 45.3384 | 41.7464 | 44.137 | 44.3576 | 93.9413 | 94.1858 | 93.7063
2022-09-07 22:13 | 0:23 | 31.4928 | 29.809 | 32.57 | 41.2614 | 38.1475 | 39.0617 | 38.9373 | 37.5051 | 38.7185 | 39.1446 | 38.6651 | 39.6221 | 37.4839 | 39.1252 | 39.8307 | 37.004 | 38.8227 | 38.7477 | 37.6301 | 40.7919 | 35.8254 | 29.0618 | 36.782 | 41.8194 | 40.4511 | 46.0368 | 45.3239 | 42.3825 | 41.9156 | 42.5733 | 39.8943 | 39.6015 | 39.0344 | 38.4251 | 39.0307 | 40.1464 | 38.33 | 41.3675 | 40.8681 | 38.6264 | 42.1453 | 90.5252 | 90.2048 | 90.1876 | 93.028 | 45.0938 | 46.2754 | 41.4833 | 47.165 | 43.5872 | 44.4204 | 41.9185 | 44.3369 | 41.9694 | 43.9101 | 40.718 | 42.9999 | 43.0527 | 93.8977 | 94.1333 | 93.6111
2022-09-07 22:13 | 0:23 | 31.6452 | 30.3405 | 32.3517 | 39.7493 | 38.2083 | 37.8532 | 38.7332 | 36.6867 | 38.6589 | 38.2217 | 38.2042 | 39.6836 | 36.8312 | 38.1026 | 39.336 | 36.7909 | 37.815 | 37.6168 | 37.365 | 39.7493 | 34.6019 | 29.4346 | 36.1036 | 40.669 | 39.2951 | 44.129 | 43.5881 | 40.4504 | 40.2943 | 40.7867 | 38.8014 | 39.208 | 38.1794 | 38.5298 | 39.2875 | 39.3619 | 38.4297 | 40.167 | 40.1515 | 38.3672 | 45.7582 | 91.5929 | 91.0258 | 41.3337 | 93.9989 | 44.0641 | 45.2541 | 40.5932 | 45.4329 | 42.3619 | 43.136 | 41.2282 | 43.4246 | 40.9535 | 43.3693 | 40.1347 | 42.4038 | 42.5251 | 93.8663 | 94.1089 | 93.698
2022-09-07 22:13 | 0:23 | 31.7379 | 30.3397 | 32.4355 | 39.0745 | 38.2845 | 37.1613 | 38.8062 | 36.448 | 38.6269 | 37.805 | 38.2663 | 39.5724 | 36.5377 | 37.559 | 39.0562 | 36.7051 | 37.4968 | 37.3187 | 37.2882 | 39.3481 | 33.8185 | 29.1261 | 35.7008 | 40.3715 | 38.944 | 43.1195 | 42.9296 | 39.8731 | 39.6782 | 40.3543 | 38.2739 | 39.2405 | 37.8144 | 38.732 | 53.1554 | 38.8898 | 38.4251 | 39.6817 | 39.7542 | 38.4026 | 56.2204 | 92.4181 | 36.8978 | 40.0614 | 94.6996 | 43.573 | 44.6662 | 40.2435 | 44.2309 | 41.7582 | 42.7222 | 40.8499 | 42.9952 | 40.6357 | 43.0777 | 39.9752 | 41.9095 | 42.376 | 93.8357 | 94.0553 | 93.6911
2022-09-07 22:14 | 0:23 | 31.8339 | 30.3554 | 32.5351 | 38.8657 | 38.3632 | 36.901 | 38.699 | 36.4511 | 38.6549 | 37.6335 | 38.1212 | 39.8183 | 36.4513 | 37.4501 | 38.9397 | 36.6945 | 37.3188 | 37.2479 | 37.3914 | 39.2541 | 33.1732 | 28.8789 | 35.2683 | 40.1753 | 38.6127 | 42.8531 | 42.4198 | 39.7963 | 39.2109 | 40.057 | 37.9379 | 39.0431 | 37.5981 | 38.9016 | 48.2948 | 38.7684 | 38.5298 | 39.3994 | 39.6561 | 38.33 | 54.4134 | 37.552 | 36.525 | 38.8576 | 48.0767 | 43.1522 | 44.4259 | 40.0189 | 43.9209 | 41.5122 | 42.37 | 40.6013 | 42.8889 | 40.4487 | 42.8592 | 39.9496 | 41.7645 | 42.1734 | 93.7745 | 94.0139 | 93.5784
2022-09-07 22:14 | 0:24 | 31.8846 | 30.3344 | 32.6394 | 38.7447 | 38.4608 | 36.7416 | 38.7405 | 36.4463 | 38.686 | 37.4618 | 38.3902 | 39.8588 | 36.3552 | 37.2514 | 38.8479 | 36.6771 | 37.2762 | 37.1793 | 37.2179 | 39.1215 | 32.6918 | 28.7735 | 34.9184 | 39.9397 | 38.3819 | 42.7533 | 42.1453 | 39.3787 | 39.0307 | 39.9289 | 37.6389 | 39.0368 | 37.5811 | 39.2112 | 55.4797 | 38.7117 | 38.732 | 39.2087 | 39.4639 | 38.4297 | 59.0876 | 37.8254 | 36.8298 | 39.2581 | 37.5404 | 42.9764 | 44.2925 | 39.7722 | 43.5841 | 41.2385 | 42.0722 | 40.5186 | 42.7459 | 40.1744 | 42.7444 | 39.8445 | 41.4638 | 41.9829 | 93.7056 | 93.9532 | 93.5003
2022-09-07 22:14 | 0:24 | 31.9041 | 30.2651 | 32.6324 | 38.6299 | 38.5329 | 36.681 | 38.7933 | 36.4639 | 38.7483 | 37.4362 | 38.4479 | 39.8469 | 36.3492 | 37.1934 | 38.843 | 36.6938 | 37.1878 | 37.0776 | 37.2439 | 39.2592 | 32.3039 | 28.6573 | 34.6952 | 39.7331 | 38.3453 | 43.044 | 45.7582 | 41.1251 | 39.2875 | 40.4269 | 39.4872 | 38.9654 | 37.7856 | 39.4861 | 56.0872 | 38.6511 | 38.9016 | 39.2918 | 39.39 | 38.4251 | 57.4458 | 37.7495 | 37.2751 | 39.0611 | 38.0873 | 51.308 | 53.2341 | 45.3123 | 62.4681 | 47.114 | 62.2145 | 42.8729 | 47.5787 | 41.6793 | 49.0596 | 40.666 | 41.6582 | 45.7059 | 93.6181 | 93.877 | 93.4425
2022-09-07 22:14 | 0:24 | 31.8831 | 30.0591 | 32.6074 | 39.4422 | 38.6802 | 40.7638 | 39.3641 | 36.8171 | 38.8233 | 38.6868 | 39.0149 | 39.8628 | 36.6913 | 39.3324 | 39.5452 | 37.2895 | 38.1038 | 38.6084 | 38.0784 | 40.0845 | 32.1317 | 28.6808 | 35.0163 | 45.2036 | 52.2976 | 57.4575 | 56.2204 | 55.4767 | 53.1554 | 53.5671 | 49.773 | 41.8156 | 44.6354 | 39.7905 | 55.1051 | 41.0173 | 39.2112 | 46.3134 | 43.0635 | 38.5298 | 56.9979 | 35.257 | 37.5604 | 38.2767 | 38.0028 | 59.6266 | 62.3912 | 51.8454 | 66.1805 | 53.4913 | 62.2008 | 47.7156 | 52.0757 | 48.0176 | 48.1127 | 41.9548 | 45.9092 | 47.8022 | 93.5724 | 93.8002 | 93.4094
2022-09-07 22:14 | 0:24 | 31.9895 | 29.8595 | 32.7717 | 42.2441 | 38.9486 | 42.3475 | 39.9366 | 38.2768 | 39.246 | 39.8139 | 40.6712 | 40.1308 | 38.0235 | 40.6248 | 41.1053 | 38.0038 | 39.575 | 40.3374 | 38.9611 | 41.0348 | 32.8622 | 28.8031 | 36.1274 | 44.2213 | 45.9879 | 52.2358 | 54.4134 | 50.6463 | 48.2948 | 49.1584 | 46.8783 | 41.5941 | 42.6386 | 39.7906 | 47.9554 | 41.6803 | 39.4861 | 45.2137 | 43.2105 | 38.732 | 52.873 | 35.179 | 37.754 | 38.0611 | 38.042 | 59.2325 | 63.366 | 49.766 | 68.0878 | 52.9587 | 67.674 | 47.5688 | 54.4812 | 49.2943 | 54.8422 | 42.3265 | 45.852 | 47.8381 | 93.5203 | 93.7024 | 93.3951
2022-09-07 22:14 | 0:24 | 32.0905 | 29.723 | 32.7768 | 41.7061 | 39.0756 | 42.4982 | 39.8646 | 38.1915 | 39.3146 | 40.1964 | 40.5286 | 40.1688 | 38.0029 | 41.0795 | 40.915 | 38.5409 | 39.7248 | 40.6055 | 39.357 | 41.3804 | 33.9696 | 28.9081 | 37.191 | 46.4076 | 53.1208 | 53.1677 | 59.0876 | 54.5482 | 55.4797 | 50.8946 | 50.6052 | 43.0197 | 45.2332 | 39.989 | 45.2418 | 42.7165 | 39.7905 | 49.7258 | 44.7345 | 38.9016 | 50.9037 | 35.2566 | 37.8723 | 37.632 | 38.0402 | 77.3783 | 76.0013 | 71.2225 | 79.2845 | 55.0506 | 69.0417 | 50.4658 | 62.9163 | 50.2698 | 56.4512 | 43.2916 | 47.7975 | 50.1029 | 93.4187 | 93.6261 | 93.3026
2022-09-07 22:15 | 0:25 | 32.1024 | 29.7863 | 32.7444 | 42.546 | 39.2678 | 42.9458 | 40.2748 | 39.0328 | 39.5526 | 40.5298 | 41.2794 | 40.4186 | 38.6484 | 41.3344 | 41.2659 | 39.4665 | 40.3871 | 41.0284 | 39.934 | 41.7063 | 35.2138 | 29.0568 | 38.255 | 47.8346 | 47.6652 | 55.4573 | 57.4458 | 55.4451 | 56.0872 | 54.156 | 52.6849 | 44.4991 | 47.056 | 39.9274 | 44.1205 | 43.3581 | 39.7906 | 50.7885 | 45.9121 | 39.2112 | 50.0442 | 35.3002 | 38.0005 | 37.4486 | 38.0409 | 82.0258 | 80.5158 | 81.199 | 81.6532 | 58.0498 | 71.0562 | 51.7904 | 63.5651 | 49.1528 | 61.6564 | 44.1185 | 48.6878 | 49.8734 | 93.3334 | 93.5129 | 93.2641
2022-09-07 22:15 | 0:25 | 32.1055 | 29.8616 | 32.7038 | 42.7977 | 39.4387 | 43.6482 | 40.4229 | 39.088 | 39.7627 | 41.5874 | 41.4147 | 40.5577 | 38.7639 | 41.23 | 41.6151 | 40.3667 | 40.4599 | 40.9322 | 40.3469 | 42.3117 | 36.4811 | 29.3123 | 39.2511 | 48.0089 | 47.7782 | 55.0789 | 56.9979 | 55.2422 | 55.1051 | 54.5525 | 49.5468 | 44.6738 | 45.318 | 39.9096 | 44.16 | 45.3816 | 39.989 | 48.518 | 46.4836 | 39.4861 | 51.222 | 35.3758 | 38.1283 | 37.4387 | 38.0061 | 87.0004 | 86.9889 | 86.9206 | 85.5651 | 53.3909 | 57.8738 | 48.4324 | 53.4772 | 49.073 | 51.2919 | 44.1115 | 47.806 | 48.0623 | 93.1875 | 93.3701 | 93.0629
2022-09-07 22:15 | 0:25 | 32.1128 | 29.9182 | 32.7139 | 42.7953 | 39.5378 | 41.6938 | 40.1142 | 38.9892 | 39.8704 | 41.259 | 40.7516 | 40.5388 | 38.9057 | 41.7485 | 41.9448 | 39.133 | 40.4163 | 40.4606 | 40.0686 | 41.9095 | 37.4203 | 29.501 | 39.7576 | 45.4039 | 44.0888 | 51.6738 | 52.873 | 49.0599 | 47.9554 | 48.4842 | 44.9057 | 43.0112 | 42.3035 | 40.0943 | 52.2396 | 43.5134 | 39.9274 | 45.3372 | 43.5447 | 39.7905 | 53.5942 | 35.4366 | 38.1249 | 37.4639 | 37.9681 | 91.0356 | 90.2349 | 90.6847 | 89.2642 | 49.3092 | 53.5023 | 45.5435 | 49.8783 | 45.5876 | 48.8443 | 43.3289 | 46.6427 | 46.1495 | 93.0585 | 93.269 | 93.0262
2022-09-07 22:15 | 0:25 | 32.0141 | 29.9298 | 32.5934 | 41.4722 | 39.6196 | 39.8995 | 39.7229 | 38.1526 | 39.7981 | 39.8691 | 40.0476 | 40.4713 | 38.3272 | 40.6126 | 41.0522 | 38.6389 | 39.6665 | 39.2018 | 39.1818 | 41.2887 | 37.621 | 29.6514 | 39.5774 | 43.7767 | 42.8968 | 49.7065 | 50.9037 | 46.6128 | 45.2418 | 46.9155 | 43.4016 | 42.6201 | 40.8157 | 40.1118 | 48.799 | 42.3436 | 39.9096 | 44.0273 | 42.5519 | 39.7906 | 53.3863 | 35.4884 | 38.0872 | 37.4562 | 37.887 | 92.4291 | 92.0426 | 35.9266 | 90.6834 | 47.4691 | 51.4768 | 44.507 | 48.7294 | 44.5932 | 47.848 | 42.9047 | 46.1502 | 45.3872 | 92.9616 | 93.1606 | 93.0055
2022-09-07 22:15 | 0:25 | 31.8028 | 29.9354 | 32.4792 | 40.7344 | 39.7034 | 39.0972 | 39.7218 | 37.8535 | 39.7848 | 39.4444 | 39.7235 | 40.4487 | 37.9328 | 39.9232 | 41.0294 | 38.408 | 39.2136 | 38.9219 | 38.8383 | 40.9896 | 37.2847 | 29.7189 | 39.0492 | 43.0497 | 42.3856 | 48.9976 | 50.0442 | 45.73 | 44.1205 | 46.007 | 42.623 | 42.2701 | 40.5108 | 40.3657 | 49.151 | 41.7308 | 40.0943 | 43.3233 | 42.0654 | 39.989 | 54.6335 | 35.5572 | 38.0358 | 37.451 | 37.8204 | 34.5952 | 92.0274 | 34.5742 | 92.4627 | 46.5395 | 50.7871 | 44.2021 | 48.0693 | 44.049 | 47.423 | 42.7931 | 45.837 | 45.1806 | 92.8271 | 93.0763 | 92.8723
2022-09-07 22:15 | 0:25 | 31.6272 | 29.9402 | 32.3362 | 40.2712 | 39.7572 | 38.6402 | 39.6594 | 37.7227 | 39.7778 | 39.1574 | 39.6379 | 40.483 | 37.6786 | 39.7132 | 40.9171 | 38.2948 | 38.8136 | 38.5884 | 38.8686 | 40.6867 | 36.7383 | 29.7887 | 38.5182 | 42.6608 | 42.0273 | 48.5001 | 51.222 | 45.3022 | 44.16 | 45.7352 | 44.3687 | 42.2853 | 40.1382 | 40.6938 | 48.5902 | 41.4427 | 40.1118 | 43.0683 | 41.8937 | 39.9274 | 53.4249 | 35.585 | 38.0221 | 37.4213 | 37.7423 | 33.2069 | 93.5538 | 34.1717 | 92.7738 | 52.4205 | 67.2875 | 45.7931 | 49.7425 | 47.0009 | 57.4232 | 43.0928 | 45.5566 | 49.5173 | 92.7648 | 92.935 | 92.8147
2022-09-07 22:16 | 0:25 | 31.5055 | 29.9118 | 32.2386 | 40.597 | 39.8568 | 40.121 | 39.8112 | 37.8995 | 39.8687 | 39.5959 | 39.9324 | 40.5188 | 37.7252 | 39.853 | 40.6944 | 39.2662 | 39.0884 | 39.3614 | 39.4859 | 41.1795 | 36.3218 | 29.8385 | 38.565 | 47.1493 | 44.8224 | 54.9836 | 53.5942 | 53.6617 | 52.2396 | 54.1369 | 52.08 | 45.1034 | 45.5236 | 40.8447 | 46.392 | 43.5525 | 40.3657 | 49.27 | 44.9273 | 39.9096 | 51.2665 | 35.6477 | 38.0724 | 37.2283 | 37.6617 | 32.9779 | 94.4476 | 33.9445 | 92.7367 | 56.5896 | 69.637 | 52.4136 | 60.7918 | 49.8511 | 58.5903 | 45.0145 | 48.6653 | 49.4502 | 92.6846 | 92.8567 | 92.8113
2022-09-07 22:16 | 0:26 | 31.2469 | 30.0247 | 32.2505 | 42.3943 | 40.0141 | 42.2304 | 40.1733 | 38.8464 | 40.0618 | 40.9474 | 40.9734 | 40.7824 | 38.6685 | 40.8892 | 41.4456 | 39.8858 | 40.332 | 40.3667 | 40.1872 | 42.0528 | 36.7184 | 30.0075 | 39.2187 | 46.4187 | 43.8959 | 54.4132 | 53.3863 | 50.618 | 48.799 | 50.8429 | 47.9161 | 44.2144 | 42.9122 | 40.8034 | 45.2049 | 43.1875 | 40.6938 | 46.7385 | 44.7024 | 40.0943 | 50.0074 | 35.6667 | 38.1724 | 37.2346 | 37.6169 | 32.9957 | 93.8057 | 33.8269 | 94.0075 | 51.66 | 64.9889 | 47.7695 | 53.6047 | 47.4811 | 55.7584 | 44.0827 | 47.9942 | 48.3059 | 92.6005 | 92.7193 | 92.6393
2022-09-07 22:16 | 0:26 | 31.2478 | 30.0679 | 32.2273 | 42.0018 | 40.1119 | 40.7736 | 40.0298 | 38.5398 | 40.1564 | 40.504 | 40.3183 | 40.8002 | 38.705 | 41.3989 | 41.5011 | 39.6544 | 40.0163 | 40.6425 | 40.1971 | 41.8197 | 37.1346 | 30.1207 | 39.4964 | 48.1826 | 45.0416 | 56.6231 | 54.6335 | 52.5903 | 49.151 | 53.488 | 50.0706 | 44.8956 | 44.9237 | 40.8713 | 44.4047 | 43.0524 | 40.8447 | 47.7555 | 44.785 | 40.1118 | 49.5753 | 35.7264 | 38.3224 | 37.1189 | 37.5839 | 33.0613 | 93.6239 | 33.7979 | 93.9897 | 76.1313 | 77.3245 | 52.2343 | 61.7137 | 51.9266 | 57.8144 | 45.3136 | 50.3144 | 49.172 | 92.5127 | 92.5952 | 92.623
2022-09-07 22:16 | 0:26 | 31.192 | 30.0899 | 32.2335 | 42.6172 | 40.2458 | 42.3645 | 40.4428 | 39.2275 | 40.317 | 41.7644 | 41.3137 | 40.9296 | 39.1028 | 41.409 | 41.6463 | 39.761 | 40.8347 | 40.5607 | 40.5796 | 42.0786 | 37.664 | 30.2954 | 40.0546 | 46.9625 | 44.5054 | 55.8331 | 53.4249 | 50.3772 | 48.5902 | 50.7463 | 47.7625 | 44.6621 | 43.2824 | 40.8473 | 43.9912 | 43.6499 | 40.8034 | 46.8984 | 44.8011 | 40.3657 | 48.9214 | 35.7595 | 38.426 | 37.1808 | 37.549 | 33.095 | 93.6595 | 33.7946 | 93.6771 | 79.2858 | 80.257 | 47.9678 | 52.821 | 48.5217 | 51.2726 | 44.7928 | 48.3004 | 47.306 | 92.4178 | 92.4689 | 92.6034
2022-09-07 22:16 | 0:26 | 31.0952 | 30.1277 | 32.2 | 42.1786 | 40.3465 | 40.3279 | 40.2706 | 38.7839 | 40.3439 | 40.4016 | 40.4997 | 40.972 | 38.8608 | 41.7997 | 41.6519 | 39.3857 | 40.5217 | 40.2312 | 40.1286 | 41.9691 | 38.0101 | 30.4361 | 40.0415 | 44.8256 | 43.2464 | 51.2661 | 51.2665 | 47.4406 | 46.392 | 48.6634 | 45.111 | 43.5609 | 41.9296 | 40.6963 | 43.6369 | 42.9094 | 40.8713 | 45.3862 | 43.5481 | 40.6938 | 48.332 | 35.7709 | 38.4312 | 37.2046 | 37.5196 | 33.1986 | 93.7619 | 33.8253 | 94.4862 | 83.6575 | 83.9001 | 46.1744 | 49.8924 | 46.2889 | 49.7019 | 44.3364 | 47.1848 | 46.497 | 92.2773 | 92.3849 | 92.4027
2022-09-07 22:16 | 0:26 | 31.0017 | 30.0805 | 32.0868 | 41.2699 | 40.3777 | 39.1579 | 40.1951 | 38.5481 | 40.3468 | 39.9255 | 40.2696 | 40.9598 | 38.453 | 40.8382 | 41.5486 | 39.1534 | 39.5833 | 39.5363 | 39.8225 | 41.5513 | 37.809 | 30.4894 | 39.6513 | 44.039 | 42.8741 | 49.8134 | 50.0074 | 45.9123 | 45.2049 | 47.6313 | 44.1854 | 43.1158 | 41.1792 | 40.8447 | 48.4114 | 42.6245 | 40.8473 | 44.6844 | 43.077 | 40.8447 | 52.5984 | 35.7974 | 38.4455 | 37.2135 | 37.462 | 33.2502 | 92.6884 | 33.8635 | 92.7902 | 84.557 | 86.3624 | 45.2509 | 49.0524 | 45.1468 | 48.9582 | 44.025 | 46.7854 | 46.122 | 92.1457 | 92.2621 | 92.4031
2022-09-07 22:17 | 0:27 | 30.8466 | 30.0863 | 31.9813 | 40.8254 | 40.4532 | 38.8436 | 40.1619 | 38.3707 | 40.3629 | 39.6904 | 40.1669 | 41.0899 | 38.1687 | 40.5656 | 41.3026 | 39.0512 | 39.3517 | 39.4103 | 39.6417 | 41.3676 | 37.3267 | 30.5142 | 39.2446 | 43.6067 | 42.4235 | 49.227 | 49.5753 | 45.4294 | 44.4047 | 47.2143 | 43.6666 | 42.9914 | 41.077 | 41.0574 | 49.6015 | 42.2646 | 40.6963 | 44.2496 | 42.7464 | 40.8034 | 54.3372 | 35.8364 | 38.4253 | 37.246 | 37.4136 | 33.347 | 39.6883 | 33.8918 | 93.5644 | 89.2921 | 79.7805 | 44.9435 | 48.5558 | 44.9485 | 48.608 | 43.7779 | 46.5949 | 45.9673 | 92.164 | 92.287 | 92.4354
2022-09-07 22:17 | 0:27 | 29.8841 | 29.9761 | 31.7737 | 40.5802 | 40.5048 | 38.6957 | 40.045 | 38.2306 | 40.4277 | 39.6401 | 39.9947 | 41.242 | 38.0396 | 40.3206 | 41.0616 | 38.9635 | 39.1892 | 39.2998 | 39.5824 | 41.1775 | 36.8411 | 30.5386 | 38.9554 | 43.2886 | 42.302 | 48.4429 | 48.9214 | 44.8416 | 43.9912 | 47.145 | 43.3545 | 42.8597 | 40.7043 | 41.1916 | 50.1016 | 41.938 | 40.8447 | 43.9816 | 42.4288 | 40.8713 | 54.9443 | 35.8437 | 38.3684 | 37.2587 | 37.3596 | 33.3908 | 35.848 | 33.9378 | 40.3282 | 38.3071 | 34.6611 | 44.9761 | 48.2524 | 44.774 | 48.3287 | 43.6835 | 46.3253 | 45.8384 | 92.2912 | 92.3761 | 92.4762
2022-09-07 22:17 | 0:27 | 29.2701 | 29.8557 | 31.5956 | 40.4028 | 40.5885 | 38.3087 | 40.0952 | 38.2384 | 40.4461 | 39.5539 | 39.954 | 41.1533 | 38.0427 | 39.8873 | 41.1307 | 38.9059 | 39.0731 | 39.1051 | 39.4601 | 41.119 | 36.3222 | 30.5163 | 38.6418 | 43.1351 | 42.0348 | 47.869 | 48.332 | 44.4699 | 43.6369 | 47.004 | 43.1474 | 42.5428 | 40.5466 | 41.2208 | 47.2861 | 41.8824 | 41.0574 | 43.6364 | 42.3269 | 40.8473 | 51.5062 | 35.8594 | 38.336 | 37.2468 | 37.3089 | 33.4414 | 34.7794 | 33.9553 | 38.931 | 34.9394 | 33.6739 | 45.5829 | 49.3432 | 45.7542 | 55.4324 | 43.7291 | 45.8328 | 46.7778 | 92.3418 | 92.4523 | 92.607
2022-09-07 22:17 | 0:27 | 29.0895 | 29.7855 | 31.5031 | 40.3082 | 40.6343 | 38.7347 | 40.0883 | 38.2506 | 40.4875 | 39.5819 | 39.9384 | 41.0662 | 37.9299 | 40.2391 | 40.8145 | 39.099 | 39.0907 | 39.2605 | 39.6929 | 41.3813 | 35.9603 | 30.4679 | 38.6722 | 46.469 | 45.0948 | 54.2754 | 52.5984 | 50.1596 | 48.4114 | 51.4745 | 46.5944 | 44.6304 | 43.1466 | 41.1724 | 45.6203 | 41.9996 | 41.1916 | 46.3361 | 43.7356 | 40.6963 | 50.3473 | 35.8955 | 38.4276 | 37.1763 | 37.2956 | 33.5241 | 34.2486 | 34.0247 | 37.486 | 34.3114 | 33.3051 | 68.1802 | 73.816 | 52.5476 | 65.2017 | 45.6287 | 49.4821 | 48.4462 | 92.4076 | 92.5599 | 92.6599
2022-09-07 22:17 | 0:27 | 29.1428 | 29.7357 | 31.5356 | 41.6311 | 40.762 | 41.5875 | 40.6031 | 38.8148 | 40.6599 | 40.632 | 40.7061 | 41.21 | 38.5395 | 40.7858 | 41.3321 | 39.7005 | 39.9336 | 40.6832 | 40.303 | 42.0498 | 36.2883 | 30.5594 | 39.3494 | 47.8683 | 48.6654 | 56.9172 | 54.3372 | 52.1817 | 49.6015 | 52.4815 | 47.7836 | 45.3621 | 43.3933 | 41.1951 | 44.8543 | 42.9935 | 41.2208 | 47.5758 | 44.598 | 40.8447 | 49.3575 | 35.8971 | 38.6161 | 37.1016 | 37.3169 | 33.5544 | 33.9224 | 34.1133 | 36.6206 | 33.8714 | 33.0638 | 78.893 | 79.3872 | 51.1983 | 66.992 | 45.8765 | 50.9153 | 47.9104 | 92.5023 | 92.6839 | 92.6701
2022-09-07 22:17 | 0:27 | 29.5892 | 29.7499 | 31.6944 | 42.502 | 40.8859 | 42.5235 | 40.8549 | 39.3953 | 40.826 | 41.1013 | 41.3173 | 41.3341 | 39.1532 | 41.7832 | 42.083 | 40.0881 | 40.5801 | 41.3653 | 40.6728 | 42.5572 | 37.0245 | 30.6876 | 39.914 | 48.269 | 47.7155 | 57.8089 | 54.9443 | 52.1278 | 50.1016 | 52.3584 | 48.0916 | 45.4973 | 43.6661 | 41.2059 | 44.3932 | 43.231 | 41.1724 | 47.584 | 45.4164 | 41.0574 | 48.8181 | 35.9605 | 38.8107 | 37.136 | 37.3367 | 33.6048 | 33.6966 | 34.1814 | 35.9243 | 33.5603 | 32.9071 | 85.3801 | 84.7647 | 51.264 | 56.6356 | 45.9128 | 50.6078 | 47.7091 | 92.5646 | 92.7675 | 92.7379
2022-09-07 22:18 | 0:27 | 30.364 | 29.7855 | 31.8845 | 42.8139 | 40.9942 | 41.3042 | 40.9577 | 39.3871 | 40.9176 | 41.2164 | 40.9937 | 41.3852 | 39.359 | 42.3695 | 42.1766 | 39.8391 | 41.0019 | 40.9783 | 40.2033 | 42.6979 | 37.5845 | 30.7772 | 40.1079 | 45.3425 | 44.483 | 52.9682 | 51.5062 | 48.6938 | 47.2861 | 49.4653 | 45.1168 | 43.8882 | 42.2143 | 41.5259 | 44.7353 | 43.514 | 41.1951 | 45.8651 | 44.5191 | 41.1916 | 50.7762 | 35.9967 | 38.9318 | 37.2086 | 37.3563 | 33.6454 | 33.5217 | 34.2626 | 35.3847 | 33.3052 | 32.7795 | 90.714 | 88.314 | 46.7533 | 52.6502 | 45.2955 | 49.0214 | 47.2938 | 92.7251 | 92.8417 | 92.864
2022-09-07 22:18 | 0:28 | 30.9892 | 29.7525 | 32.0364 | 41.782 | 41.0011 | 39.5866 | 40.5152 | 38.8086 | 40.8943 | 40.3391 | 40.5873 | 41.4186 | 38.9316 | 40.9313 | 41.8603 | 39.6608 | 40.0752 | 40.1213 | 40.275 | 42.1762 | 37.633 | 30.7764 | 39.8286 | 44.3873 | 43.5113 | 50.2675 | 50.3473 | 46.6104 | 45.6203 | 48.3416 | 43.8194 | 43.4425 | 41.3866 | 41.8393 | 49.3021 | 43.0618 | 41.2059 | 45.0868 | 43.7103 | 41.2208 | 55.4192 | 36.0115 | 38.9417 | 37.224 | 37.3447 | 33.6772 | 33.389 | 34.3109 | 34.9535 | 33.1021 | 32.6599 | 92.4342 | 91.5922 | 45.7984 | 51.7924 | 45.1229 | 48.6875 | 47.0426 | 92.8339 | 92.9624 | 92.9329
2022-09-07 22:18 | 0:28 | 31.1002 | 29.6808 | 31.9638 | 41.0945 | 41.0526 | 39.0677 | 40.46 | 38.6494 | 40.9174 | 40.1401 | 40.3758 | 41.4103 | 38.5619 | 41.0231 | 41.5528 | 39.4626 | 39.7602 | 39.7455 | 40.0073 | 41.7724 | 37.3093 | 30.7769 | 39.483 | 43.8563 | 43.1101 | 49.3683 | 49.3575 | 46.0555 | 44.8543 | 48.0056 | 43.3207 | 43.3424 | 41.1585 | 41.7144 | 51.2427 | 42.6201 | 41.5259 | 44.602 | 43.2545 | 41.1724 | 56.5275 | 35.9983 | 38.944 | 37.2756 | 37.3138 | 33.7061 | 33.3056 | 34.3676 | 34.6372 | 32.9161 | 32.548 | 36.7172 | 93.7165 | 45.3543 | 51.3195 | 44.9234 | 48.4986 | 46.8432 | 92.8935 | 93.0556 | 92.9368
2022-09-07 22:18 | 0:28 | 30.8653 | 29.6986 | 31.7614 | 40.7531 | 41.1069 | 38.5887 | 40.5047 | 38.5266 | 40.9523 | 39.8734 | 40.3238 | 41.501 | 38.4058 | 40.815 | 41.5032 | 39.3707 | 39.5186 | 39.5964 | 39.8997 | 41.5376 | 36.8777 | 30.7796 | 39.151 | 43.5684 | 42.8715 | 48.9593 | 48.8181 | 45.4121 | 44.3932 | 47.3244 | 43.0623 | 42.9948 | 40.9945 | 41.6748 | 50.8242 | 42.4153 | 41.8393 | 44.246 | 42.9764 | 41.1951 | 56.3167 | 36.0072 | 38.928 | 37.2733 | 37.3017 | 33.7754 | 33.2281 | 34.4187 | 34.3525 | 32.7659 | 32.4616 | 34.3193 | 34.1542 | 45.0749 | 50.7061 | 44.8509 | 48.2503 | 46.7845 | 92.9626 | 93.243 | 93.0587
2022-09-07 22:18 | 0:28 | 30.0891 | 29.6455 | 31.5792 | 40.6136 | 41.1345 | 38.5628 | 40.56 | 38.4711 | 40.9776 | 39.8117 | 40.2635 | 41.519 | 38.3142 | 40.2462 | 41.2097 | 39.2889 | 39.4744 | 39.4222 | 39.8119 | 41.3711 | 36.4295 | 30.7073 | 38.8515 | 43.2434 | 42.5192 | 50.061 | 50.7762 | 46.5583 | 44.7353 | 47.8785 | 44.7028 | 42.9837 | 41.3099 | 41.6746 | 48.1563 | 42.0048 | 41.7144 | 44.2531 | 42.7454 | 41.2059 | 52.3886 | 36.0189 | 38.9164 | 37.287 | 37.2703 | 33.8046 | 33.1808 | 34.4582 | 34.1218 | 32.659 | 32.3854 | 33.8364 | 33.4742 | 46.2518 | 58.5343 | 45.3356 | 48.3285 | 47.2672 | 93.0519 | 93.3015 | 92.9999
2022-09-07 22:18 | 0:28 | 29.525 | 29.6355 | 31.4973 | 40.9547 | 41.2196 | 40.3743 | 40.6508 | 38.599 | 41.0346 | 40.4447 | 40.5639 | 41.5555 | 38.4287 | 40.7391 | 41.2342 | 39.9258 | 39.8092 | 40.288 | 40.4564 | 41.9331 | 36.1248 | 30.7294 | 38.9614 | 45.3118 | 46.3647 | 56.9184 | 55.4192 | 51.0099 | 49.3021 | 52.5645 | 48.4427 | 45.0391 | 43.8554 | 41.7912 | 46.9376 | 42.6141 | 41.6748 | 47.2833 | 44.2955 | 41.5259 | 50.8125 | 36.0598 | 39.0714 | 37.3215 | 37.2872 | 33.8407 | 33.158 | 34.5081 | 33.9593 | 32.6236 | 32.3492 | 33.749 | 33.1484 | 48.6927 | 53.3406 | 45.3038 | 72.9217 | 48.6776 | 93.2078 | 93.4241 | 93.1355
2022-09-07 22:19 | 0:29 | 29.4909 | 29.6589 | 31.6142 | 42.2472 | 41.3618 | 42.8602 | 41.0842 | 39.3527 | 41.2404 | 41.3077 | 41.7093 | 41.697 | 39.1158 | 41.84 | 41.8963 | 40.4567 | 40.6571 | 41.1235 | 40.8182 | 42.6228 | 36.2403 | 30.7809 | 39.3147 | 46.0064 | 49.5134 | 59.1234 | 56.5275 | 53.7054 | 51.2427 | 54.0683 | 48.6724 | 45.7884 | 44.8573 | 41.764 | 46.4569 | 43.448 | 41.6746 | 48.2212 | 45.1662 | 41.8393 | 50.2803 | 36.0833 | 39.1779 | 37.3743 | 37.3507 | 33.8224 | 33.1702 | 34.5722 | 33.7991 | 32.6732 | 32.3585 | 33.7172 | 32.9102 | 80.5261 | 52.6634 | 79.1176 | 83.2963 | 48.2196 | 93.2245 | 93.4877 | 93.1653
2022-09-07 22:19 | 0:29 | 30.4946 | 29.7075 | 32.038 | 43.1252 | 41.4745 | 44.2256 | 41.2612 | 39.9564 | 41.4165 | 41.7402 | 41.9384 | 41.8459 | 39.7126 | 42.553 | 42.6515 | 40.7992 | 41.2336 | 41.5659 | 41.2156 | 43.1381 | 36.5865 | 30.8445 | 39.6423 | 46.1378 | 47.93 | 58.4522 | 56.3167 | 53.021 | 50.8242 | 52.4955 | 47.7356 | 46.1008 | 44.1855 | 41.7773 | 46.0481 | 45.217 | 41.7912 | 48.2537 | 45.919 | 41.7144 | 49.878 | 36.118 | 39.5443 | 37.4613 | 37.402 | 33.8598 | 33.153 | 34.6471 | 33.6916 | 32.6882 | 32.3574 | 33.7816 | 32.7067 | 83.2396 | 48.73 | 83.037 | 84.0863 | 48.1045 | 93.3151 | 93.6014 | 93.2325
2022-09-07 22:19 | 0:29 | 31.2673 | 29.7827 | 32.278 | 43.1208 | 41.5405 | 41.8304 | 41.0111 | 39.5309 | 41.4652 | 41.4042 | 41.3685 | 41.821 | 39.8771 | 42.9158 | 42.8421 | 40.3864 | 41.3798 | 41.3498 | 41.1342 | 43.1591 | 36.8671 | 30.8482 | 39.6756 | 44.6177 | 44.9799 | 54.3967 | 52.3886 | 50.3022 | 48.1563 | 49.7342 | 45.7867 | 44.5052 | 42.8118 | 42.0613 | 49.2719 | 44.2156 | 41.764 | 46.4091 | 44.6995 | 41.6748 | 53.9722 | 36.1385 | 39.682 | 37.5369 | 37.4517 | 33.9117 | 33.1257 | 34.7201 | 33.6072 | 32.6219 | 32.3644 | 33.8472 | 32.5601 | 84.5458 | 47.668 | 85.5626 | 87.1206 | 48.6564 | 93.3949 | 93.6864 | 93.3331
2022-09-07 22:19 | 0:29 | 31.553 | 29.7588 | 32.3362 | 42.1718 | 41.587 | 40.0361 | 41.0198 | 39.0893 | 41.4202 | 40.6531 | 40.9824 | 41.7475 | 39.4583 | 42.1833 | 42.5844 | 40.1549 | 40.5361 | 41.0504 | 40.8093 | 42.7136 | 36.8586 | 30.8139 | 39.4515 | 43.9589 | 44.1706 | 52.1007 | 50.8125 | 48.7233 | 46.9376 | 48.1546 | 44.8441 | 44.0975 | 42.2432 | 42.576 | 51.4164 | 43.6419 | 41.7773 | 45.585 | 44.1372 | 41.6746 | 54.8709 | 36.1755 | 39.7439 | 37.5985 | 37.4382 | 33.9392 | 33.1457 | 34.7607 | 33.5332 | 32.5876 | 32.3334 | 33.8958 | 32.4475 | 86.9955 | 47.1896 | 46.3594 | 35.9466 | 47.9042 | 93.5437 | 93.7561 | 93.4534
2022-09-07 22:19 | 0:29 | 31.5993 | 29.7504 | 32.3604 | 41.5128 | 41.6332 | 39.2475 | 40.8863 | 38.9582 | 41.4244 | 40.4218 | 40.8641 | 41.8492 | 39.1918 | 42.1487 | 42.065 | 40.0184 | 40.1396 | 40.7656 | 40.6642 | 42.551 | 36.6433 | 30.7753 | 39.1998 | 43.4801 | 43.6992 | 51.4122 | 50.2803 | 48.099 | 46.4569 | 48.0504 | 44.3195 | 43.8511 | 41.6063 | 42.2619 | 48.545 | 43.3009 | 42.0613 | 45.0991 | 43.7943 | 41.7912 | 52.3999 | 36.1964 | 39.785 | 37.635 | 37.4555 | 33.9416 | 33.1802 | 34.8013 | 33.4729 | 32.5066 | 32.3165 | 33.9566 | 32.3358 | 36.8553 | 46.7254 | 35.0202 | 34.5177 | 47.5342 | 93.7205 | 93.7904 | 93.5197
2022-09-07 22:19 | 0:29 | 31.5903 | 29.7739 | 32.2907 | 41.4132 | 41.6495 | 39.4309 | 40.9185 | 38.8809 | 41.4539 | 40.3456 | 40.9058 | 41.797 | 38.9992 | 41.6333 | 42.0695 | 39.9644 | 40.0335 | 40.5754 | 40.611 | 42.1861 | 36.3025 | 30.7398 | 38.9076 | 43.1027 | 43.9109 | 51.032 | 49.878 | 48.5809 | 46.0481 | 47.9286 | 45.0055 | 43.8531 | 41.7736 | 42.8047 | 50.2036 | 43.0919 | 42.576 | 45.06 | 43.6503 | 41.764 | 55.6373 | 36.1935 | 39.8009 | 37.6591 | 37.46 | 33.982 | 33.1647 | 34.8475 | 33.4224 | 32.4601 | 32.307 | 34.0113 | 32.297 | 34.6028 | 46.1844 | 34.4058 | 33.8574 | 47.501 | 93.8334 | 93.827 | 93.6494
2022-09-07 22:20 | 0:29 | 31.3594 | 29.724 | 32.0956 | 41.4723 | 41.7537 | 41.0833 | 41.0871 | 38.9961 | 41.5321 | 40.8294 | 41.0221 | 41.896 | 38.8539 | 41.3618 | 41.6871 | 40.568 | 40.2672 | 40.828 | 40.8804 | 42.5018 | 35.9676 | 30.698 | 38.8407 | 45.0025 | 46.7131 | 57.3364 | 53.9722 | 51.9356 | 49.2719 | 52.7697 | 47.9711 | 45.9027 | 44.0616 | 46.8098 | 48.4105 | 43.8343 | 42.2619 | 47.3278 | 45.0339 | 41.7773 | 52.3092 | 36.1935 | 39.9685 | 37.6338 | 37.4873 | 34.0186 | 33.2099 | 34.9073 | 33.3391 | 32.479 | 32.2833 | 34.0507 | 32.2399 | 34.0824 | 45.5382 | 34.0165 | 33.7035 | 80.9013 | 93.9801 | 93.8783 | 93.7268
2022-09-07 22:20 | 0:30 | 31.1441 | 29.7808 | 32.06 | 42.8074 | 41.8538 | 42.4625 | 41.5219 | 39.7557 | 41.7163 | 41.5635 | 41.8915 | 42.0367 | 39.6281 | 42.3564 | 42.6107 | 40.7873 | 41.1429 | 41.638 | 41.3777 | 43.5555 | 35.9707 | 30.7278 | 39.0954 | 45.4123 | 48.9113 | 58.8621 | 54.8709 | 53.7078 | 51.4164 | 53.4402 | 48.2311 | 46.0597 | 45.0589 | 49.0227 | 61.8425 | 44.106 | 42.8047 | 48.2561 | 45.7986 | 42.0613 | 61.5013 | 36.2544 | 40.1918 | 37.7208 | 37.5362 | 34.0318 | 33.2186 | 34.9418 | 33.283 | 32.505 | 32.301 | 34.0964 | 32.1909 | 33.6597 | 45.7301 | 33.6125 | 33.469 | 85.7192 | 94.1138 | 93.9597 | 93.7814
2022-09-07 22:20 | 0:30 | 31.2498 | 29.8731 | 32.2558 | 43.4406 | 41.9652 | 42.2473 | 41.5748 | 39.8341 | 41.8135 | 41.9657 | 41.886 | 42.1082 | 40.085 | 43.0694 | 42.7772 | 40.7626 | 41.6632 | 41.7469 | 41.6246 | 43.6138 | 36.1907 | 30.7752 | 39.3515 | 44.6461 | 45.4857 | 55.8948 | 52.3999 | 50.4593 | 48.545 | 49.9507 | 46.0402 | 44.9974 | 43.1113 | 46.7811 | 67.1153 | 44.3329 | 46.8098 | 46.855 | 45.0584 | 42.576 | 60.4199 | 36.2825 | 40.3491 | 37.7985 | 37.5948 | 34.0695 | 33.226 | 35.023 | 33.259 | 32.5134 | 32.3646 | 34.1299 | 32.1449 | 33.3347 | 45.9842 | 33.3137 | 33.228 | 86.467 | 94.243 | 94.0922 | 93.8868
2022-09-07 22:20 | 0:30 | 31.4706 | 29.8739 | 32.406 | 42.4314 | 41.9769 | 41.1623 | 41.3079 | 39.4389 | 41.8018 | 41.2913 | 41.4319 | 42.1071 | 39.6242 | 42.5237 | 42.4817 | 40.796 | 40.9492 | 41.5447 | 41.5064 | 43.3767 | 36.3308 | 30.759 | 39.3009 | 44.5056 | 47.5752 | 57.2916 | 55.6373 | 52.6337 | 50.2036 | 52.3943 | 47.7145 | 46.0599 | 44.3204 | 45.5556 | 58.2818 | 43.9054 | 49.0227 | 47.6951 | 45.5209 | 42.2619 | 60.0842 | 36.3101 | 40.5162 | 37.8909 | 37.6121 | 34.0775 | 33.2485 | 35.0985 | 33.2427 | 32.5411 | 32.3719 | 34.1991 | 32.13 | 33.0884 | 79.3545 | 33.0599 | 33.0151 | 90.8913 | 94.3749 | 94.2687 | 93.9759
2022-09-07 22:20 | 0:30 | 31.562 | 29.9294 | 32.5243 | 43.0744 | 42.0696 | 41.6211 | 41.5738 | 39.8014 | 41.9106 | 41.8262 | 41.7923 | 42.2203 | 39.839 | 43.0966 | 42.7447 | 40.8378 | 41.4667 | 41.5354 | 41.6112 | 43.3569 | 36.3447 | 30.7501 | 39.2717 | 44.0693 | 45.2303 | 56.702 | 52.3092 | 55.5621 | 48.4105 | 58.9782 | 46.4519 | 47.8919 | 43.9452 | 45.0116 | 52.0066 | 44.0457 | 46.7811 | 51.1106 | 44.6925 | 42.8047 | 54.9031 | 36.3188 | 40.6537 | 37.9363 | 37.6495 | 34.1063 | 33.2599 | 35.1486 | 33.2213 | 32.5259 | 32.4079 | 34.1993 | 32.1397 | 32.9335 | 83.6291 | 32.8735 | 32.84 | 92.831 | 94.4765 | 94.4957 | 94.0976
2022-09-07 22:20 | 0:30 | 31.6542 | 30.0057 | 32.5654 | 43.1166 | 42.2159 | 42.5675 | 42.6816 | 40.2227 | 41.9382 | 42.5052 | 42.4331 | 42.323 | 40.2081 | 45.4896 | 43.7973 | 42.5018 | 41.8798 | 44.1279 | 42.819 | 43.8368 | 36.6305 | 30.8651 | 40.002 | 50.2568 | 75.6637 | 80.4938 | 61.5013 | 72.3856 | 61.8425 | 73.4047 | 55.3922 | 63.4955 | 51.5248 | 44.5396 | 50.2235 | 54.7049 | 45.5556 | 55.6456 | 46.6647 | 46.8098 | 53.463 | 36.3478 | 40.701 | 38.0194 | 37.6752 | 34.1288 | 33.2954 | 35.199 | 33.2042 | 32.5011 | 32.3977 | 34.2572 | 32.1171 | 32.7694 | 85.2057 | 32.7039 | 32.6835 | 92.9912 | 94.5994 | 94.619 | 94.1244
2022-09-07 22:21 | 0:31 | 31.7788 | 30.1267 | 32.8578 | 45.9134 | 42.7165 | 45.7201 | 43.9452 | 43.6574 | 42.9272 | 44.1259 | 46.4564 | 42.9628 | 42.2625 | 49.0911 | 44.9511 | 44.118 | 44.0867 | 47.4138 | 44.1331 | 45.8582 | 37.6499 | 31.0911 | 41.2767 | 52.4296 | 83.3055 | 83.4316 | 60.4199 | 73.9332 | 67.1153 | 74.6528 | 54.6513 | 66.7528 | 55.8913 | 47.1103 | 49.0973 | 59.3589 | 45.0116 | 57.114 | 49.7039 | 49.0227 | 52.5434 | 36.3843 | 40.7313 | 38.0617 | 37.6684 | 34.1632 | 33.274 | 35.2278 | 33.1785 | 32.487 | 32.3923 | 34.2605 | 32.1226 | 32.6628 | 87.5422 | 32.6256 | 32.6133 | 93.458 | 94.6996 | 94.7835 | 94.1908
2022-09-07 22:21 | 0:31 | 31.9074 | 30.2846 | 33.0928 | 47.7086 | 42.8992 | 47.1239 | 44.5247 | 43.3353 | 43.353 | 46.1085 | 46.7252 | 43.2632 | 43.7269 | 50.1249 | 45.2107 | 44.2566 | 45.7956 | 47.8253 | 44.6249 | 47.6493 | 38.9456 | 31.268 | 42.2441 | 47.4301 | 86.7014 | 82.221 | 60.0842 | 61.6014 | 58.2818 | 60.1676 | 52.5078 | 55.9504 | 49.6593 | 49.9808 | 63.9108 | 55.3711 | 44.5396 | 53.6431 | 48.428 | 46.7811 | 63.0387 | 36.4139 | 40.7405 | 38.1 | 37.6673 | 34.193 | 33.314 | 35.2587 | 33.1848 | 32.4424 | 32.3823 | 34.2866 | 32.1433 | 32.579 | 91.2801 | 32.5161 | 32.5156 | 94.2696 | 94.8327 | 94.8979 | 94.2981
2022-09-07 22:21 | 0:31 | 31.9944 | 30.3642 | 33.1226 | 46.2371 | 42.9094 | 43.2481 | 42.8964 | 41.5362 | 42.9565 | 43.0896 | 43.1997 | 43.1311 | 43.1877 | 45.9025 | 45.5659 | 43.1476 | 44.3206 | 44.6581 | 42.8254 | 46.6863 | 39.6332 | 31.3782 | 42.3747 | 46.8828 | 38.0847 | 66.2402 | 54.9031 | 54.9434 | 52.0066 | 54.7007 | 49.1181 | 51.7063 | 45.581 | 50.9431 | 76.2472 | 50.5967 | 47.1103 | 49.7046 | 47.4824 | 45.5556 | 81.3118 | 36.4434 | 40.7439 | 38.1594 | 37.6737 | 34.2107 | 33.3399 | 35.2978 | 33.1854 | 32.4395 | 32.3958 | 34.3265 | 32.1358 | 32.4992 | 88.3307 | 32.4259 | 32.4633 | 93.6853 | 95.0157 | 95.0494 | 94.3945
2022-09-07 22:21 | 0:31 | 32.0286 | 30.3696 | 33.0823 | 44.2497 | 42.9055 | 41.2777 | 41.9218 | 40.641 | 42.8123 | 41.8241 | 42.3908 | 42.8907 | 41.8348 | 44.229 | 45.4723 | 42.4853 | 42.5734 | 43.3064 | 42.0988 | 45.2535 | 39.6791 | 31.4513 | 42.0483 | 45.0178 | 34.824 | 77.9053 | 53.463 | 52.7659 | 50.2235 | 52.9634 | 47.7638 | 50.4243 | 44.6045 | 48.5222 | 76.3718 | 48.8596 | 49.9808 | 48.3676 | 46.8227 | 45.0116 | 81.177 | 36.4731 | 40.7099 | 38.1682 | 37.6844 | 34.2314 | 33.3617 | 35.3373 | 33.1517 | 32.4018 | 32.3906 | 34.3591 | 32.1491 | 32.4535 | 35.668 | 32.3859 | 32.412 | 35.5998 | 95.1343 | 95.1084 | 94.4482
2022-09-07 22:21 | 0:31 | 32.0581 | 30.3174 | 33.03 | 43.319 | 42.9603 | 40.7666 | 41.8217 | 40.2169 | 42.7381 | 41.3018 | 42.2824 | 42.9228 | 40.9515 | 43.9591 | 44.5853 | 42.1636 | 41.9534 | 42.7236 | 41.8487 | 44.4685 | 39.3016 | 31.451 | 41.5883 | 44.5717 | 34.2431 | 34.812 | 52.5434 | 51.5227 | 49.0973 | 52.5673 | 47.1517 | 49.471 | 44.1008 | 47.2514 | 82.455 | 47.6351 | 50.9431 | 47.6831 | 46.1555 | 44.5396 | 86.3733 | 36.5069 | 40.6891 | 38.2128 | 37.6576 | 34.2741 | 33.3776 | 35.3752 | 33.161 | 32.381 | 32.426 | 34.3639 | 32.1664 | 32.4163 | 34.5908 | 32.3252 | 32.3393 | 34.7097 | 95.1529 | 95.2106 | 94.4166
2022-09-07 22:21 | 0:31 | 32.0952 | 30.3182 | 33.0318 | 42.6838 | 42.9909 | 41.9336 | 42.0564 | 40.3372 | 42.7139 | 41.797 | 42.4122 | 42.9189 | 40.693 | 45.2403 | 44.1355 | 43.9872 | 41.8139 | 44.2484 | 43.3425 | 44.5648 | 38.8915 | 31.483 | 41.4412 | 50.7534 | 34.0118 | 33.9796 | 63.0387 | 71.432 | 63.9108 | 72.1753 | 55.9115 | 60.9918 | 53.6209 | 46.6031 | 83.7851 | 52.9283 | 48.5222 | 56.8826 | 48.1309 | 47.1103 | 35.6307 | 36.5371 | 40.6603 | 38.2273 | 37.6221 | 34.3046 | 33.4037 | 35.4012 | 33.161 | 32.3501 | 32.4031 | 34.4025 | 32.185 | 32.3736 | 34.195 | 32.2736 | 32.3107 | 34.3696 | 95.1488 | 95.1402 | 94.4544
2022-09-07 22:22 | 0:31 | 32.1669 | 30.4559 | 33.2219 | 45.6775 | 43.2607 | 46.548 | 43.9916 | 42.6049 | 43.1662 | 44.07 | 44.9888 | 43.4444 | 43.1677 | 48.5105 | 48.2063 | 46.8814 | 44.2979 | 47.4738 | 45.118 | 46.0655 | 39.1846 | 31.6672 | 42.3076 | 52.9849 | 33.8813 | 33.7045 | 81.3118 | 78.8683 | 76.2472 | 74.3517 | 75.3112 | 65.0858 | 55.8392 | 48.2253 | 88.7348 | 58.7269 | 47.2514 | 58.559 | 51.2055 | 49.9808 | 34.3281 | 36.5534 | 40.6991 | 38.2473 | 37.6267 | 34.3078 | 33.4199 | 35.4463 | 33.1624 | 32.3541 | 32.4568 | 34.4179 | 32.1791 | 32.3625 | 33.9947 | 32.2406 | 32.2954 | 34.199 | 94.9656 | 95.0439 | 94.3127
2022-09-07 22:22 | 0:32 | 32.2601 | 30.6012 | 33.347 | 46.3789 | 43.4323 | 47.0677 | 43.9273 | 43.1721 | 43.3997 | 44.8715 | 45.4015 | 43.6019 | 45.3606 | 49.0311 | 50.4019 | 48.3816 | 45.2173 | 48.6371 | 45.9304 | 47.5766 | 40.0321 | 31.8414 | 43.4905 | 53.8138 | 33.7814 | 33.601 | 81.177 | 80.4687 | 76.3718 | 73.0731 | 79.7257 | 68.2454 | 54.7225 | 50.2529 | 91.7879 | 61.4516 | 46.6031 | 59.7706 | 52.3871 | 50.9431 | 33.8913 | 36.5647 | 40.7515 | 38.2668 | 37.6112 | 34.365 | 33.444 | 35.47 | 33.1679 | 32.3657 | 32.4649 | 34.4231 | 32.2214 | 32.3516 | 33.8598 | 32.2065 | 32.3009 | 34.0575 | 94.7251 | 94.8539 | 94.1256
2022-09-07 22:22 | 0:32 | 32.384 | 30.701 | 33.4235 | 47.5452 | 43.541 | 44.915 | 43.4324 | 42.886 | 43.4879 | 44.6963 | 44.9176 | 43.8196 | 46.2262 | 48.3988 | 48.0672 | 47.0686 | 46.0621 | 47.1928 | 46.5589 | 48.5895 | 40.8914 | 32 | 44.0308 | 49.4462 | 33.7097 | 33.5271 | 86.3733 | 82.6873 | 82.455 | 61.8764 | 86.6909 | 58.9254 | 49.0028 | 50.499 | 92.8256 | 55.7931 | 48.2253 | 55.074 | 49.3937 | 48.5222 | 33.6618 | 36.6223 | 40.8202 | 38.2892 | 37.6071 | 34.3853 | 33.4706 | 35.4958 | 33.1627 | 32.3757 | 32.4725 | 34.442 | 32.2076 | 32.3436 | 33.7446 | 32.1928 | 32.282 | 33.9282 | 94.4835 | 94.5822 | 94.039
2022-09-07 22:22 | 0:32 | 32.4649 | 30.7219 | 33.4375 | 45.7252 | 43.5458 | 42.4608 | 42.7755 | 41.7074 | 43.4598 | 42.891 | 43.4231 | 43.6174 | 43.858 | 46.2714 | 46.8967 | 45.0983 | 44.2808 | 45.2776 | 43.9187 | 47.1721 | 41.1596 | 32.1356 | 43.7255 | 47.2696 | 33.6354 | 33.4676 | 35.6307 | 84.4387 | 83.7851 | 55.5928 | 90.9028 | 55.2755 | 46.4612 | 50.562 | 92.4965 | 51.8272 | 50.2529 | 51.7285 | 48.5107 | 47.2514 | 33.5288 | 36.6624 | 40.8203 | 38.3032 | 37.6046 | 34.4229 | 33.4885 | 35.5263 | 33.1812 | 32.3559 | 32.4852 | 34.4616 | 32.2501 | 32.3308 | 33.6638 | 32.1843 | 32.2653 | 33.8322 | 94.3072 | 94.3815 | 93.947
2022-09-07 22:22 | 0:32 | 32.5476 | 30.6985 | 33.4393 | 44.5382 | 43.5627 | 42.0311 | 42.5115 | 41.131 | 43.3906 | 42.3445 | 42.8719 | 43.5939 | 42.4722 | 44.7197 | 46.5367 | 44.2766 | 43.6508 | 44.1714 | 43.8959 | 45.9983 | 40.7932 | 32.1578 | 43.1068 | 46.1797 | 33.5712 | 33.4515 | 34.3281 | 37.6057 | 88.7348 | 53.1031 | 92.3757 | 53.8963 | 45.6968 | 49.3776 | 93.4116 | 50.0067 | 50.499 | 50.5783 | 47.8216 | 46.6031 | 33.463 | 36.7171 | 40.8004 | 38.3086 | 37.5864 | 34.4294 | 33.5199 | 35.5483 | 33.1639 | 32.3704 | 32.5099 | 34.4985 | 32.2674 | 32.3276 | 33.5798 | 32.1552 | 32.2581 | 33.7762 | 94.1502 | 94.1906 | 93.8804
2022-09-07 22:22 | 0:32 | 32.605 | 30.7474 | 33.4417 | 43.9551 | 43.5854 | 41.7007 | 42.5896 | 41.0362 | 43.3362 | 42.1894 | 42.8714 | 43.5445 | 42.0506 | 45.156 | 46.9646 | 44.2235 | 43.0801 | 43.9505 | 43.63 | 45.5767 | 40.207 | 32.1441 | 42.6147 | 48.5918 | 33.5469 | 33.4218 | 33.8913 | 36.8424 | 91.7879 | 67.3876 | 92.557 | 59.9584 | 50.5251 | 48.0853 | 93.2387 | 50.5259 | 50.562 | 57.3481 | 47.9577 | 48.2253 | 33.3987 | 36.7475 | 40.7714 | 38.342 | 37.5992 | 34.4679 | 33.5229 | 35.5881 | 33.1732 | 32.3886 | 32.5288 | 34.5046 | 32.2835 | 32.3258 | 33.5046 | 32.1372 | 32.2795 | 33.7315 | 94.0249 | 94.1531 | 93.8469
2022-09-07 22:23 | 0:32 | 32.6589 | 30.8037 | 33.5042 | 44.7469 | 43.6769 | 43.4988 | 43.0874 | 41.6378 | 43.4586 | 43.2017 | 43.6919 | 43.7336 | 43.2527 | 47.1646 | 46.5952 | 47.1431 | 44.305 | 46.735 | 45.705 | 47.6356 | 40.0333 | 32.2582 | 43.0227 | 52.0159 | 33.5176 | 33.446 | 33.6618 | 36.0627 | 92.8256 | 76.5427 | 93.3904 | 66.6051 | 55.4151 | 47.3875 | 92.1089 | 61.7582 | 49.3776 | 59.2588 | 52.4002 | 50.2529 | 33.3547 | 36.7904 | 40.7614 | 38.3498 | 37.5982 | 34.4779 | 33.5481 | 35.611 | 33.1644 | 32.4087 | 32.5586 | 34.5182 | 32.2922 | 32.3409 | 33.4648 | 32.1426 | 32.2626 | 33.7177 | 93.9343 | 94.0757 | 93.7956
2022-09-07 22:23 | 0:33 | 32.7956 | 30.8827 | 33.6326 | 46.0069 | 43.8466 | 44.7347 | 43.5482 | 42.7175 | 43.7432 | 43.7947 | 44.6718 | 43.9433 | 44.0941 | 48.6245 | 47.8351 | 47.5936 | 45.1301 | 47.4506 | 46.3172 | 48.6669 | 40.396 | 32.3565 | 43.7667 | 52.9276 | 33.4805 | 33.4763 | 33.5288 | 35.5951 | 92.4965 | 79.6562 | 94.1832 | 77.8257 | 71.1623 | 46.9575 | 37.9243 | 64.6411 | 48.0853 | 61.7972 | 54.781 | 50.499 | 33.2874 | 36.7923 | 40.8008 | 38.3588 | 37.5795 | 34.4985 | 33.565 | 35.6238 | 33.1819 | 32.4036 | 32.581 | 34.5623 | 32.3255 | 32.333 | 33.4479 | 32.1321 | 32.2722 | 33.6891 | 93.8672 | 94.0541 | 93.8276
2022-09-07 22:23 | 0:33 | 32.9745 | 30.9836 | 33.7631 | 46.2805 | 43.9697 | 44.8201 | 43.5792 | 42.6489 | 43.8549 | 44.1731 | 44.7404 | 43.9877 | 44.1903 | 48.9415 | 48.2948 | 47.2176 | 45.448 | 47.7616 | 46.8036 | 48.6475 | 40.9892 | 32.551 | 44.421 | 52.0365 | 33.4634 | 33.5129 | 33.463 | 35.0851 | 93.4116 | 82.4037 | 94.2717 | 80.8981 | 80.7805 | 46.6358 | 36.0268 | 66.2267 | 47.3875 | 59.6767 | 55.1597 | 50.562 | 33.2536 | 36.8274 | 40.8406 | 38.3627 | 37.5719 | 34.5493 | 33.576 | 35.6702 | 33.2066 | 32.4137 | 32.5979 | 34.5551 | 32.3334 | 32.3361 | 33.501 | 32.1124 | 32.2674 | 33.6975 | 93.8334 | 94.0579 | 93.8008
2022-09-07 22:23 | 0:33 | 33.0615 | 31.0602 | 33.8875 | 46.8919 | 44.006 | 44.3831 | 43.5747 | 42.8222 | 43.9777 | 44.844 | 44.7755 | 44.1246 | 44.2516 | 48.1504 | 47.4836 | 46.289 | 45.5657 | 46.9675 | 46.3479 | 48.0671 | 41.4211 | 32.7246 | 44.578 | 49.8586 | 33.4534 | 33.5721 | 33.3987 | 34.7276 | 93.2387 | 88.2193 | 93.745 | 78.9401 | 85.3594 | 48.6217 | 35.3112 | 58.3202 | 46.9575 | 55.7188 | 50.5712 | 49.3776 | 33.2382 | 36.878 | 40.8452 | 38.3811 | 37.5786 | 34.5672 | 33.5962 | 35.6732 | 33.1915 | 32.4284 | 32.6159 | 34.5895 | 32.3635 | 32.3712 | 33.5042 | 32.1069 | 32.307 | 33.6974 | 93.7952 | 93.9006 | 93.7414
2022-09-07 22:23 | 0:33 | 33.1551 | 31.0885 | 33.9237 | 45.6914 | 44.068 | 42.9944 | 43.4138 | 42.296 | 43.9542 | 43.5324 | 43.7966 | 44.0436 | 43.4744 | 46.8195 | 46.9458 | 45.3983 | 44.8006 | 46.1315 | 45.0553 | 47.3979 | 41.3049 | 32.7624 | 44.0552 | 47.5141 | 33.4639 | 33.5876 | 33.3547 | 34.4272 | 92.1089 | 36.9964 | 93.7826 | 80.006 | 88.7455 | 49.9559 | 34.9691 | 54.3693 | 46.6358 | 53.4983 | 49.3683 | 48.0853 | 33.2293 | 36.9395 | 40.8489 | 38.3805 | 37.5705 | 34.597 | 33.5948 | 35.7232 | 33.1938 | 32.4226 | 32.642 | 34.5887 | 32.3751 | 32.3783 | 33.5093 | 32.1163 | 32.2959 | 33.7179 | 93.7645 | 93.8307 | 93.6594
2022-09-07 22:23 | 0:33 | 33.2006 | 31.0887 | 33.9225 | 44.8856 | 44.1077 | 42.2906 | 43.3006 | 41.7502 | 43.9233 | 42.9746 | 43.4941 | 44.0516 | 42.7848 | 45.9854 | 46.3009 | 44.9437 | 44.1132 | 45.1304 | 44.6284 | 46.5707 | 40.7599 | 32.7601 | 43.3084 | 46.3633 | 33.4653 | 33.6174 | 33.2874 | 34.1633 | 37.9243 | 35.2576 | 93.6443 | 88.1487 | 90.6567 | 49.0735 | 34.6779 | 52.5039 | 48.6217 | 52.6298 | 48.9378 | 47.3875 | 33.2395 | 36.9359 | 40.8072 | 38.4134 | 37.5436 | 34.6296 | 33.6395 | 35.7294 | 33.1971 | 32.4324 | 32.663 | 34.6234 | 32.4003 | 32.4038 | 33.4744 | 32.1174 | 32.3033 | 33.7312 | 93.624 | 93.6955 | 93.564
2022-09-07 22:24 | 0:34 | 33.2036 | 31.1334 | 33.9612 | 44.5185 | 44.108 | 42.2588 | 43.273 | 41.5924 | 43.903 | 42.9471 | 43.3275 | 44.0693 | 42.3294 | 45.6852 | 45.7795 | 44.6032 | 43.8976 | 44.6575 | 44.2941 | 45.9699 | 40.0421 | 32.7218 | 42.5327 | 45.9519 | 33.4601 | 33.6695 | 33.2536 | 33.9608 | 36.0268 | 34.7573 | 91.7759 | 34.8826 | 91.939 | 48.5856 | 34.3857 | 51.3616 | 49.9559 | 51.8235 | 48.8365 | 46.9575 | 33.2949 | 36.9651 | 40.791 | 38.3973 | 37.5523 | 34.6367 | 33.6449 | 35.719 | 33.202 | 32.4611 | 32.7041 | 34.627 | 32.3852 | 32.4127 | 33.436 | 32.1016 | 32.3318 | 33.7448 | 93.5454 | 93.6365 | 93.523
2022-09-07 22:24 | 0:34 | 33.1421 | 31.1164 | 33.9596 | 44.2212 | 44.1379 | 41.9837 | 43.272 | 41.6236 | 43.9237 | 42.8851 | 43.2829 | 44.1203 | 42.1725 | 45.3719 | 45.9873 | 44.3997 | 43.3893 | 44.4799 | 44.151 | 45.9465 | 39.3994 | 32.6293 | 41.9896 | 45.4034 | 33.4584 | 33.6579 | 33.2382 | 33.7555 | 35.3112 | 34.4936 | 36.3126 | 33.604 | 91.2362 | 47.5427 | 34.1326 | 50.9591 | 49.0735 | 51.2723 | 48.5318 | 46.6358 | 33.3221 | 36.9969 | 40.7402 | 38.4143 | 37.5252 | 34.6589 | 33.6474 | 35.7564 | 33.2082 | 32.4867 | 32.7356 | 34.6448 | 32.4288 | 32.4263 | 33.4378 | 32.1045 | 32.3399 | 33.7758 | 93.453 | 93.6571 | 93.4796
2022-09-07 22:24 | 0:34 | 33.1009 | 31.1285 | 33.9258 | 44.2229 | 44.2008 | 41.9471 | 43.1774 | 41.5677 | 43.9582 | 43.1048 | 43.0399 | 44.1401 | 41.9103 | 45.9566 | 45.4905 | 44.3625 | 43.3081 | 44.774 | 44.3954 | 45.8443 | 38.8343 | 32.5962 | 41.8009 | 50.1574 | 33.4589 | 33.697 | 33.2293 | 33.6189 | 34.9691 | 34.5029 | 35.5091 | 33.28 | 90.9078 | 47.0039 | 33.9233 | 60.3153 | 48.5856 | 57.9647 | 49.1491 | 48.6217 | 33.3635 | 37.0345 | 40.6918 | 38.4046 | 37.5359 | 34.6823 | 33.683 | 35.7809 | 33.2049 | 32.5146 | 32.7618 | 34.657 | 32.4475 | 32.4321 | 33.4094 | 32.1032 | 32.3381 | 33.7827 | 93.3747 | 93.5596 | 93.4524
2022-09-07 22:24 | 0:34 | 33.0621 | 31.1747 | 33.9669 | 45.3462 | 44.3252 | 44.2511 | 43.5914 | 42.0483 | 44.105 | 43.769 | 44.1237 | 44.2949 | 43.0452 | 47.7422 | 46.8924 | 44.7917 | 44.8293 | 46.3614 | 45.3846 | 47.3308 | 38.8416 | 32.7097 | 42.2695 | 49.399 | 33.4675 | 33.7492 | 33.2395 | 33.5408 | 34.6779 | 34.5741 | 35.0969 | 33.0575 | 92.9346 | 46.438 | 33.7407 | 68.0645 | 47.5427 | 61.7621 | 53.671 | 49.9559 | 33.3754 | 37.0449 | 40.6929 | 38.3902 | 37.5364 | 34.6688 | 33.6796 | 35.7736 | 33.1674 | 32.5184 | 32.7625 | 34.6724 | 32.4491 | 32.4686 | 33.4331 | 32.1117 | 32.3406 | 33.7711 | 93.3066 | 93.4473 | 93.3643
2022-09-07 22:24 | 0:34 | 33.1125 | 31.2556 | 34.1051 | 46.4225 | 44.4337 | 45.3439 | 43.9029 | 42.7652 | 44.3241 | 44.371 | 44.7524 | 44.4387 | 43.7942 | 49.0441 | 46.9356 | 45.2481 | 45.3961 | 46.8794 | 45.5297 | 48.2763 | 39.1783 | 32.766 | 42.6028 | 49.2155 | 33.4674 | 33.8229 | 33.2949 | 33.4856 | 34.3857 | 34.5476 | 34.8542 | 32.9156 | 93.0211 | 47.5669 | 33.5804 | 78.3306 | 47.0039 | 66.2464 | 58.427 | 49.0735 | 33.4053 | 37.0692 | 40.7159 | 38.4221 | 37.5182 | 34.7247 | 33.6941 | 35.788 | 33.2009 | 32.5271 | 32.8138 | 34.674 | 32.4629 | 32.4569 | 33.4855 | 32.1163 | 32.3527 | 33.8428 | 93.234 | 93.3471 | 93.3002
2022-09-07 22:24 | 0:34 | 33.2994 | 31.3098 | 34.2621 | 47.0716 | 44.5605 | 45.2698 | 44.0084 | 42.9521 | 44.43 | 44.7077 | 44.9214 | 44.5753 | 44.2662 | 48.4832 | 46.7846 | 45.2103 | 45.4233 | 46.9197 | 45.0239 | 48.1997 | 39.498 | 32.8169 | 42.7479 | 48.8069 | 33.4722 | 33.8726 | 33.3221 | 33.4772 | 34.1326 | 34.4686 | 34.6059 | 32.8053 | 94.0195 | 47.1561 | 33.4667 | 82.591 | 46.438 | 57.6562 | 51.4849 | 48.5856 | 33.4421 | 37.102 | 40.7459 | 38.4118 | 37.4981 | 34.7467 | 33.7024 | 35.809 | 33.1775 | 32.5496 | 32.8035 | 34.683 | 32.5033 | 32.4877 | 33.5355 | 32.1137 | 32.3808 | 33.873 | 93.1573 | 93.2274 | 93.2317
2022-09-07 22:25 | 0:34 | 33.3984 | 31.2923 | 34.2839 | 46.1386 | 44.5292 | 43.6932 | 43.8398 | 42.4575 | 44.4122 | 43.9364 | 44.0195 | 44.4765 | 43.4729 | 47.7734 | 46.6183 | 44.6774 | 44.8863 | 46.2641 | 44.807 | 47.3358 | 39.5139 | 32.8035 | 42.4405 | 47.0378 | 33.4863 | 33.9257 | 33.3635 | 33.4399 | 33.9233 | 34.2864 | 34.3893 | 32.7169 | 48.1028 | 49.4063 | 33.359 | 87.0686 | 47.5669 | 53.9082 | 49.9929 | 47.5427 | 33.4699 | 37.131 | 40.7251 | 38.4179 | 37.4974 | 34.758 | 33.7286 | 35.8131 | 33.196 | 32.5906 | 32.8104 | 34.7062 | 32.5044 | 32.5273 | 33.543 | 32.1293 | 32.4127 | 33.9138 | 93.1445 | 93.1122 | 93.2737
2022-09-07 22:25 | 0:35 | 33.4061 | 31.3263 | 34.2636 | 45.1418 | 44.5427 | 43.0463 | 43.7195 | 42.1422 | 44.3689 | 43.5864 | 43.7327 | 44.4858 | 42.7601 | 46.439 | 46.4918 | 44.4169 | 43.9582 | 45.4372 | 44.6649 | 46.5407 | 39.1994 | 32.7452 | 41.9975 | 46.4249 | 33.5076 | 33.966 | 33.3754 | 33.3654 | 33.7407 | 34.1006 | 34.1875 | 32.671 | 34.6647 | 79.93 | 33.2698 | 35.5501 | 47.1561 | 52.842 | 49.5149 | 47.0039 | 33.5484 | 37.1671 | 40.7068 | 38.4162 | 37.4674 | 34.7809 | 33.7244 | 35.8584 | 33.2114 | 32.5878 | 32.8364 | 34.7327 | 32.5172 | 32.5409 | 33.5545 | 32.1407 | 32.4015 | 33.9266 | 93.0819 | 93.0533 | 93.1805
2022-09-07 22:25 | 0:35 | 33.2777 | 31.328 | 34.1814 | 44.6593 | 44.5572 | 42.6608 | 43.6901 | 42.0166 | 44.3239 | 43.636 | 43.4381 | 44.4275 | 42.3188 | 46.1462 | 45.8905 | 44.0842 | 43.664 | 44.9801 | 44.4222 | 46.0396 | 38.7457 | 32.6625 | 41.5815 | 45.4964 | 33.5202 | 33.9768 | 33.4053 | 33.3254 | 33.5804 | 33.9618 | 34.0019 | 32.6266 | 33.8282 | 83.8768 | 33.2209 | 34.3262 | 49.4063 | 62.967 | 52.7616 | 46.438 | 33.605 | 37.1957 | 40.6709 | 38.4287 | 37.4662 | 34.7967 | 33.7269 | 35.8475 | 33.1999 | 32.5984 | 32.8489 | 34.7144 | 32.5449 | 32.5654 | 33.5293 | 32.1569 | 32.416 | 33.9518 | 92.9308 | 92.8966 | 93.0997
2022-09-07 22:25 | 0:35 | 33.181 | 31.3297 | 34.1609 | 45.1247 | 44.6681 | 43.7751 | 43.9621 | 42.072 | 44.4173 | 44.0999 | 43.9145 | 44.5469 | 42.7978 | 47.9046 | 46.1412 | 44.36 | 43.9288 | 45.9575 | 44.7418 | 47.0454 | 38.336 | 32.6229 | 41.4823 | 47.5701 | 33.5322 | 34.0239 | 33.4421 | 33.2865 | 33.4667 | 34.0458 | 33.9015 | 32.6014 | 33.5144 | 88.1267 | 33.1662 | 33.917 | 79.93 | 76.444 | 58.0967 | 47.5669 | 33.6682 | 37.2237 | 40.6913 | 38.3974 | 37.4614 | 34.798 | 33.7713 | 35.8621 | 33.205 | 32.6142 | 32.8655 | 34.7287 | 32.5579 | 32.5738 | 33.5509 | 32.15 | 32.4452 | 33.988 | 92.8452 | 92.7564 | 93.0413
2022-09-07 22:25 | 0:35 | 33.2535 | 31.3742 | 34.2728 | 46.2176 | 44.8063 | 44.9095 | 44.1193 | 42.6879 | 44.6024 | 44.4854 | 44.5083 | 44.6859 | 43.4252 | 48.8225 | 46.6329 | 44.9067 | 44.8541 | 46.8707 | 44.4661 | 47.8254 | 38.2634 | 32.6546 | 70.6736 | 47.4164 | 33.556 | 34.0783 | 33.4699 | 33.2652 | 33.359 | 34.1768 | 33.8629 | 32.5734 | 65.4424 | 91.6001 | 33.1516 | 33.8661 | 83.8768 | 79.6126 | 52.6307 | 47.1561 | 33.73 | 37.2326 | 40.6985 | 38.3935 | 37.4593 | 34.8274 | 33.7646 | 35.875 | 33.2139 | 32.6237 | 32.9238 | 34.743 | 32.5597 | 32.5965 | 33.6276 | 32.1684 | 32.4512 | 34.0154 | 92.7349 | 92.6585 | 92.9885
2022-09-07 22:25 | 0:35 | 33.387 | 31.4063 | 34.2677 | 46.4916 | 44.891 | 45.1644 | 44.2741 | 43.153 | 44.7198 | 44.6585 | 44.882 | 44.7515 | 43.8004 | 48.9308 | 46.3716 | 44.9422 | 45.4606 | 47.2796 | 44.398 | 48.1058 | 38.3349 | 32.6355 | 78.713 | 47.0262 | 33.5715 | 34.136 | 33.5484 | 33.298 | 33.2698 | 34.2158 | 33.8292 | 32.5592 | 78.7566 | 38.4183 | 33.1066 | 33.7882 | 88.1267 | 81.5507 | 76.186 | 49.4063 | 33.7438 | 37.262 | 40.7412 | 38.4183 | 37.4631 | 34.8259 | 33.7734 | 35.8976 | 33.2159 | 32.6446 | 32.92 | 34.7502 | 32.5802 | 32.6107 | 33.683 | 32.154 | 32.4736 | 34.0423 | 92.5152 | 92.5222 | 92.8598
2022-09-07 22:26 | 0:36 | 33.521 | 31.4381 | 34.4149 | 46.7346 | 44.944 | 45.3283 | 44.5456 | 43.1239 | 44.8387 | 44.8385 | 44.9765 | 44.8213 | 43.8113 | 49.1282 | 46.8983 | 44.8809 | 45.0597 | 47.4242 | 44.5203 | 48.1144 | 38.3552 | 32.5935 | 86.6548 | 47.4279 | 33.6084 | 34.2334 | 33.605 | 33.3126 | 33.2209 | 34.2779 | 33.803 | 32.5719 | 81.438 | 37.0015 | 33.0689 | 33.6138 | 91.6001 | 84.4326 | 79.8465 | 79.93 | 33.7869 | 37.3186 | 40.7767 | 38.4243 | 37.4638 | 34.8529 | 33.782 | 35.9028 | 33.2208 | 32.6762 | 32.9368 | 34.7498 | 32.5986 | 32.624 | 33.743 | 32.1806 | 32.4945 | 34.0929 | 92.4136 | 92.448 | 92.7929
2022-09-07 22:26 | 0:36 | 33.6261 | 31.451 | 34.4811 | 46.6675 | 44.9824 | 45.2554 | 44.473 | 43.1631 | 44.911 | 44.8576 | 44.9312 | 44.8719 | 43.9757 | 49.2209 | 47.0931 | 44.9556 | 45.3693 | 47.4247 | 44.3499 | 48.4337 | 38.3837 | 32.5984 | 85.9365 | 47.3119 | 33.6208 | 34.2838 | 33.6682 | 33.2966 | 33.1662 | 34.3331 | 33.8119 | 32.5611 | 83.7687 | 36.5382 | 33.0686 | 33.4925 | 38.4183 | 87.1593 | 85.0999 | 83.8768 | 33.7922 | 37.353 | 40.8433 | 38.4103 | 37.4745 | 34.8997 | 33.7975 | 35.8999 | 33.2171 | 32.6632 | 32.976 | 34.7684 | 32.6192 | 32.6484 | 33.7869 | 32.1804 | 32.4964 | 34.1353 | 92.2398 | 92.2191 | 92.637
2022-09-07 22:26 | 0:36 | 33.7043 | 31.4981 | 34.5354 | 46.5404 | 45.0596 | 44.6262 | 44.4164 | 42.9623 | 44.8877 | 44.6669 | 44.6107 | 44.9005 | 43.8431 | 48.6638 | 47.1095 | 44.4235 | 45.123 | 46.9543 | 44.2316 | 47.8999 | 38.4173 | 32.6217 | 90.1807 | 46.8647 | 33.6634 | 34.3375 | 33.73 | 33.3011 | 33.1516 | 34.2782 | 33.7821 | 32.5668 | 87.3194 | 36.2853 | 33.0472 | 33.3681 | 37.0015 | 91.0793 | 43.1192 | 88.1267 | 33.8191 | 37.4328 | 40.8368 | 38.4331 | 37.4472 | 34.9136 | 33.8075 | 35.8901 | 33.2213 | 32.7129 | 33.0016 | 34.7773 | 32.6378 | 32.6781 | 33.8111 | 32.1807 | 32.5281 | 34.1624 | 92.1443 | 92.113 | 92.582
2022-09-07 22:26 | 0:36 | 33.6091 | 31.5193 | 34.4283 | 45.9755 | 45.0721 | 44.0879 | 44.2683 | 42.6904 | 44.875 | 44.462 | 44.1764 | 44.8891 | 43.4969 | 48.0639 | 46.6716 | 44.1696 | 44.8558 | 46.4635 | 44.117 | 47.565 | 38.3238 | 32.603 | 91.4956 | 46.4159 | 33.686 | 34.3749 | 33.7438 | 33.2942 | 33.1066 | 34.1566 | 33.7431 | 32.5799 | 39.829 | 36.12 | 33.0491 | 33.2529 | 36.5382 | 93.1124 | 38.1239 | 91.6001 | 33.858 | 37.4458 | 40.8254 | 38.4333 | 37.459 | 34.9289 | 33.8039 | 35.9122 | 33.2143 | 32.7341 | 33.0098 | 34.7834 | 32.6544 | 32.7029 | 33.8408 | 32.2161 | 32.5367 | 34.1927 | 92.0119 | 91.9922 | 92.4545
2022-09-07 22:26 | 0:36 | 33.5478 | 31.4676 | 34.3907 | 45.6029 | 45.1035 | 43.7185 | 44.3241 | 42.5402 | 44.8768 | 44.2652 | 44.0381 | 44.8713 | 43.3314 | 47.6875 | 46.4008 | 44.0352 | 44.5817 | 46.2901 | 44.1139 | 47.3277 | 38.1205 | 32.5315 | 93.93 | 45.883 | 33.7045 | 34.417 | 33.7869 | 33.257 | 33.0689 | 34.0838 | 33.6695 | 32.5771 | 37.7739 | 36.0132 | 33.0384 | 33.1677 | 36.2853 | 94.1743 | 37.3351 | 38.4183 | 33.9254 | 37.4824 | 40.8068 | 38.4416 | 37.4477 | 34.9307 | 33.8169 | 35.9398 | 33.229 | 32.7547 | 33.0188 | 34.7857 | 32.6684 | 32.7446 | 33.8464 | 32.2071 | 32.5565 | 34.2041 | 91.8396 | 91.8959 | 92.367
2022-09-07 22:26 | 0:36 | 33.5248 | 31.4875 | 34.3441 | 45.5989 | 45.0951 | 43.5269 | 44.2983 | 42.5546 | 44.8631 | 44.2422 | 44.0001 | 44.9058 | 43.0262 | 47.6357 | 46.4597 | 43.9047 | 44.4658 | 46.2943 | 44.0971 | 47.0608 | 37.8695 | 32.4813 | 95.3347 | 45.6473 | 33.72 | 34.4599 | 33.7922 | 33.2167 | 33.0686 | 33.9972 | 33.6043 | 32.5822 | 37.2067 | 35.9543 | 33.0449 | 33.1057 | 36.12 | 40.463 | 37.0066 | 37.0015 | 33.9496 | 37.512 | 40.785 | 38.4424 | 37.4545 | 34.934 | 33.8388 | 35.9219 | 33.2241 | 32.7687 | 33.0365 | 34.8024 | 32.6802 | 32.7398 | 33.8771 | 32.2343 | 32.5564 | 34.2352 | 91.7979 | 91.8338 | 92.3182
2022-09-07 22:27 | 0:36 | 33.4361 | 31.497 | 34.2668 | 45.4831 | 45.1592 | 43.7436 | 44.3093 | 42.4825 | 44.9289 | 44.3177 | 44.0252 | 44.9709 | 43.0402 | 48.0567 | 46.3128 | 43.9126 | 44.4823 | 46.3999 | 44.1919 | 47.1686 | 37.5908 | 32.4068 | 95.9707 | 45.4353 | 33.7352 | 34.5031 | 33.8191 | 33.147 | 33.0472 | 33.9994 | 33.5428 | 32.6139 | 36.9485 | 35.8925 | 33.0528 | 33.0758 | 36.0132 | 37.6677 | 36.8404 | 36.5382 | 34.0035 | 37.533 | 40.7528 | 38.4221 | 37.4439 | 34.9738 | 33.8486 | 35.945 | 33.2204 | 32.7737 | 33.0607 | 34.8067 | 32.6845 | 32.7469 | 33.88 | 32.2614 | 32.5599 | 34.2715 | 91.8231 | 91.8599 | 92.3199
2022-09-07 22:27 | 0:37 | 33.3826 | 31.5065 | 34.2334 | 46.4028 | 45.266 | 44.4634 | 44.597 | 42.9751 | 45.0326 | 44.7297 | 44.7838 | 45.1036 | 43.9103 | 49.9288 | 46.8152 | 44.4412 | 44.847 | 47.313 | 44.1079 | 48.0437 | 37.4 | 32.3747 | 96.2279 | 46.291 | 33.7527 | 34.564 | 33.858 | 33.1422 | 33.0491 | 34.1941 | 33.5533 | 32.6386 | 36.7889 | 35.8763 | 33.0349 | 33.0271 | 35.9543 | 37.083 | 36.7547 | 36.2853 | 34.0089 | 37.5558 | 40.7984 | 38.4154 | 37.4466 | 34.972 | 33.8669 | 35.937 | 33.2149 | 32.7932 | 33.0698 | 34.8246 | 32.6924 | 32.7754 | 33.9247 | 32.2492 | 32.6251 | 34.2844 | 91.85 | 91.9078 | 92.4292
2022-09-07 22:27 | 0:37 | 33.4979 | 31.556 | 34.3 | 46.8522 | 45.3287 | 44.6595 | 44.7585 | 43.1511 | 45.1366 | 45.1997 | 44.7766 | 45.2347 | 44.1648 | 49.4267 | 46.6962 | 44.7171 | 45.3066 | 47.2152 | 44.248 | 48.2448 | 37.3786 | 32.3596 | 96.3867 | 45.2054 | 33.7584 | 34.6202 | 33.9254 | 33.145 | 33.0384 | 34.2751 | 33.5722 | 32.6309 | 36.5985 | 35.8557 | 33.0475 | 33.0102 | 35.8925 | 36.6734 | 36.6612 | 36.12 | 34.0478 | 37.5729 | 40.8207 | 38.4265 | 37.4251 | 34.9961 | 33.8767 | 35.9674 | 33.2192 | 32.8064 | 33.0918 | 34.8195 | 32.7277 | 32.7911 | 33.9652 | 32.2716 | 32.6356 | 34.3198 | 91.9298 | 91.9733 | 92.5165
2022-09-07 22:27 | 0:37 | 33.4876 | 31.5285 | 34.2564 | 46.2139 | 45.2714 | 43.9203 | 44.6123 | 42.8364 | 45.1057 | 44.6641 | 44.1993 | 45.1366 | 43.6156 | 48.1258 | 46.7816 | 44.1125 | 44.9873 | 46.2688 | 44.0904 | 47.5793 | 37.3102 | 32.2792 | 95.5156 | 44.6263 | 33.7816 | 34.6735 | 33.9496 | 33.1408 | 33.0449 | 34.1746 | 33.5828 | 32.6663 | 36.4755 | 35.8658 | 33.0595 | 32.9927 | 35.8763 | 36.4309 | 36.6106 | 36.0132 | 34.0787 | 37.6134 | 40.8134 | 38.4246 | 37.4432 | 35.0215 | 33.9001 | 35.9629 | 33.2313 | 32.8315 | 33.1297 | 34.8271 | 32.7295 | 32.8083 | 33.9842 | 32.2787 | 32.6302 | 34.3374 | 92.0794 | 92.101 | 92.5816
2022-09-07 22:27 | 0:37 | 33.447 | 31.528 | 34.2187 | 45.3458 | 45.2987 | 43.5939 | 44.5087 | 42.5437 | 45.0519 | 44.2625 | 43.9699 | 45.1298 | 42.8862 | 47.0579 | 46.263 | 43.7426 | 44.435 | 45.4973 | 43.9899 | 48.5916 | 37.1208 | 32.1976 | 95.7039 | 44.2269 | 33.7968 | 34.7102 | 34.0035 | 33.1341 | 33.0528 | 34.0403 | 33.5595 | 32.6868 | 36.3821 | 35.8816 | 33.0647 | 32.9522 | 35.8557 | 36.2508 | 36.5943 | 35.9543 | 34.0963 | 37.6213 | 40.7949 | 38.4015 | 37.4178 | 35.009 | 33.8961 | 35.9762 | 33.2346 | 32.8529 | 33.1266 | 34.8288 | 32.733 | 32.8296 | 33.9612 | 32.3119 | 32.642 | 34.3712 | 92.1941 | 92.1687 | 92.6195
2022-09-07 22:27 | 0:37 | 33.3529 | 31.5518 | 34.2405 | 46.5277 | 45.5388 | 46.9197 | 45.6047 | 44.3113 | 45.3762 | 45.4796 | 46.4912 | 45.4095 | 60.3144 | 62.9762 | 64.0588 | 49.061 | 48.3319 | 57.9044 | 44.4149 | 62.1924 | 36.8393 | 32.1411 | 96.2383 | 44.0077 | 33.8265 | 34.7498 | 34.0089 | 33.1266 | 33.0349 | 33.9307 | 33.5132 | 32.7022 | 36.283 | 35.8943 | 33.0719 | 32.9451 | 35.8658 | 36.1393 | 36.6172 | 35.8925 | 34.118 | 37.6429 | 40.7608 | 38.3953 | 37.4234 | 35.0272 | 33.9023 | 35.9989 | 33.2219 | 32.8548 | 33.1495 | 34.8323 | 32.7632 | 32.8536 | 33.9756 | 32.3062 | 32.6561 | 34.3843 | 92.2868 | 92.2731 | 92.6165
2022-09-07 22:28 | 0:38 | 33.724 | 31.6101 | 34.5538 | 49.7842 | 46.0251 | 51.7688 | 47.7726 | 47.137 | 46.1777 | 48.1048 | 49.9398 | 45.9033 | 79.556 | 36.2739 | 81 | 78.3599 | 55.4695 | 65.8661 | 45.1675 | 54.6135 | 36.5742 | 32.1326 | 96.6679 | 43.9885 | 33.854 | 34.7901 | 34.0478 | 33.0938 | 33.0475 | 33.8951 | 33.4767 | 32.708 | 36.2238 | 35.8978 | 33.0709 | 32.923 | 35.8816 | 36.0333 | 36.6279 | 35.8763 | 34.1555 | 37.6942 | 40.734 | 38.4003 | 37.3956 | 35.0444 | 33.9124 | 35.9699 | 33.2073 | 32.9003 | 33.1571 | 34.8682 | 32.768 | 32.8796 | 34.0311 | 32.3306 | 32.672 | 34.4069 | 92.4047 | 92.3571 | 92.6978
2022-09-07 22:28 | 0:38 | 34.2249 | 31.6754 | 34.9012 | 51.0644 | 46.3481 | 53.2362 | 48.6182 | 49.2806 | 46.8591 | 49.8486 | 50.5864 | 46.4858 | 35.4725 | 35.2968 | 37.2033 | 35.6787 | 54.8076 | 65.1541 | 45.3555 | 54.7649 | 36.3464 | 32.0069 | 96.9195 | 43.9818 | 33.8478 | 34.8258 | 34.0787 | 33.0635 | 33.0595 | 33.8696 | 33.4563 | 32.7256 | 36.1561 | 35.9102 | 33.087 | 32.9141 | 35.8943 | 35.9414 | 36.6595 | 35.8557 | 34.1773 | 37.6745 | 40.7034 | 38.3918 | 37.3896 | 35.0566 | 33.9091 | 35.9773 | 33.205 | 32.9087 | 33.1516 | 34.8688 | 32.7805 | 32.8761 | 34.0903 | 32.3361 | 32.6532 | 34.4111 | 92.4844 | 92.5007 | 92.7724
2022-09-07 22:28 | 0:38 | 34.6613 | 31.7126 | 35.0938 | 51.8332 | 46.5192 | 53.8632 | 48.514 | 49.3662 | 47.2008 | 49.9685 | 51.75 | 46.7522 | 34.7869 | 35.069 | 35.2026 | 34.5256 | 52.5322 | 68.1896 | 49.1013 | 54.4347 | 36.1854 | 31.9849 | 97.1318 | 43.6977 | 33.8869 | 34.8923 | 34.0963 | 33.0516 | 33.0647 | 33.8243 | 33.415 | 32.7572 | 36.1244 | 35.9624 | 33.0945 | 32.9013 | 35.8978 | 35.8801 | 36.68 | 35.8658 | 34.2046 | 37.6966 | 40.7001 | 38.3833 | 37.397 | 35.0844 | 33.9057 | 35.9921 | 33.2021 | 32.8995 | 33.1646 | 34.8501 | 32.7792 | 32.9087 | 34.1311 | 32.358 | 32.6878 | 34.4431 | 92.5931 | 92.6304 | 92.8858
2022-09-07 22:28 | 0:38 | 35.0093 | 31.8188 | 35.3676 | 52.4185 | 46.9474 | 54.8792 | 48.8726 | 49.3548 | 47.7241 | 49.6309 | 52.5703 | 47.3224 | 34.5155 | 34.9954 | 34.6576 | 34.1894 | 81.6091 | 81.9255 | 81.1736 | 81.8686 | 36.0879 | 31.9303 | 97.2482 | 43.4354 | 33.9182 | 34.9132 | 34.118 | 33.0198 | 33.0719 | 33.8228 | 33.3956 | 32.7779 | 36.0902 | 35.9986 | 33.1041 | 32.8864 | 35.9102 | 35.8526 | 36.7325 | 35.8816 | 34.2587 | 37.7045 | 40.6764 | 38.3851 | 37.3861 | 35.0716 | 33.953 | 35.979 | 33.2092 | 32.9315 | 33.1886 | 34.8739 | 32.7834 | 32.9169 | 34.2006 | 32.3606 | 32.7079 | 34.5045 | 92.7434 | 92.7593 | 92.9578
2022-09-07 22:28 | 0:38 | 35.2779 | 31.846 | 35.4159 | 50.2288 | 46.8758 | 49.5967 | 46.9212 | 47.6062 | 47.4569 | 48.0632 | 48.2974 | 47.1893 | 34.33 | 34.9723 | 34.4602 | 33.9952 | 82.9885 | 83.1467 | 83.7353 | 83.3666 | 35.9633 | 31.8426 | 97.2694 | 43.248 | 33.9108 | 34.9723 | 34.1555 | 33.0227 | 33.0709 | 33.8025 | 33.3749 | 32.8015 | 36.0617 | 36.0371 | 33.1208 | 32.887 | 35.9624 | 35.817 | 36.7672 | 35.8943 | 34.2758 | 37.706 | 40.6455 | 38.3762 | 37.3771 | 35.0919 | 33.9357 | 35.9933 | 33.1821 | 32.9465 | 33.2076 | 34.8788 | 32.8072 | 32.9256 | 34.2061 | 32.3835 | 32.7274 | 34.5088 | 92.798 | 92.8618 | 92.9704
2022-09-07 22:28 | 0:38 | 35.2703 | 31.8776 | 35.3126 | 48.2816 | 46.941 | 48.4287 | 46.2308 | 46.5323 | 47.1732 | 47.2249 | 47.5748 | 46.7603 | 34.1786 | 34.9979 | 34.3325 | 33.8424 | 82.9536 | 83.9455 | 86.036 | 83.044 | 35.8582 | 31.7261 | 97.2655 | 42.9861 | 33.9303 | 35.0235 | 34.1773 | 33.0082 | 33.087 | 33.7394 | 33.3515 | 32.8167 | 36.0529 | 36.0599 | 33.1315 | 32.8858 | 35.9986 | 35.7601 | 36.8099 | 35.8978 | 34.3219 | 37.6892 | 40.6228 | 38.3707 | 37.3693 | 35.0926 | 33.9547 | 35.9881 | 33.2144 | 32.9635 | 33.232 | 34.8645 | 32.8207 | 32.9605 | 34.1899 | 32.3928 | 32.7364 | 34.5151 | 92.8637 | 92.9677 | 92.9952
2022-09-07 22:29 | 0:38 | 35.2647 | 31.8966 | 35.43 | 50.7848 | 47.4485 | 51.9582 | 48.8891 | 49.1733 | 48.3477 | 49.5193 | 51.5007 | 47.3757 | 34.0572 | 35.0743 | 34.2555 | 33.7415 | 89.932 | 85.9787 | 89.1758 | 86.1127 | 35.7551 | 31.6959 | 97.1868 | 42.9233 | 33.9415 | 35.0482 | 34.2046 | 33.0001 | 33.0945 | 33.728 | 33.3357 | 32.8597 | 36.0494 | 36.0992 | 33.136 | 32.8937 | 36.0371 | 35.7659 | 36.8356 | 35.9102 | 34.3337 | 37.7096 | 40.6287 | 38.363 | 37.3604 | 35.0913 | 33.9546 | 35.977 | 33.2025 | 32.9624 | 33.2486 | 34.8799 | 32.8066 | 32.9651 | 34.2126 | 32.4118 | 32.7508 | 34.5318 | 92.9261 | 93.1237 | 93.0588
2022-09-07 22:29 | 0:39 | 35.5574 | 31.9592 | 35.6494 | 51.0622 | 47.6805 | 52.5326 | 48.8402 | 49.9958 | 48.7302 | 49.7243 | 51.3832 | 47.8813 | 33.9699 | 35.1591 | 34.2018 | 33.696 | 93.7313 | 91.2638 | 93.1731 | 91.9514 | 35.6563 | 31.632 | 96.8627 | 42.7049 | 33.9497 | 35.0878 | 34.2587 | 33.0194 | 33.1041 | 33.7088 | 33.323 | 32.8839 | 36.0398 | 36.1161 | 33.1636 | 32.9001 | 36.0599 | 35.7541 | 36.8982 | 35.9624 | 34.3597 | 37.7204 | 40.5853 | 38.3704 | 37.3733 | 35.1202 | 33.9738 | 35.997 | 33.1978 | 32.9938 | 33.2515 | 34.8781 | 32.8394 | 33.0088 | 34.2252 | 32.4287 | 32.7669 | 34.551 | 92.9801 | 93.1695 | 93.0933
2022-09-07 22:29 | 0:39 | 35.5646 | 31.9672 | 35.5653 | 48.8041 | 47.5085 | 49.5977 | 47.2783 | 47.6129 | 47.91 | 48.1803 | 48.3291 | 47.561 | 33.9016 | 35.2304 | 34.1666 | 33.6374 | 94.7837 | 93.7275 | 94.6607 | 94.6987 | 35.5962 | 31.5379 | 96.6984 | 42.4974 | 33.982 | 35.1237 | 34.2758 | 32.9998 | 33.1208 | 33.7036 | 33.3101 | 32.9138 | 36.0481 | 36.1545 | 33.1968 | 32.9054 | 36.0992 | 35.7358 | 36.939 | 35.9986 | 34.3683 | 37.7104 | 40.5763 | 38.3676 | 37.3526 | 35.1205 | 33.9797 | 36.0057 | 33.1872 | 33.0124 | 33.2733 | 34.8825 | 32.8374 | 33.0086 | 34.2427 | 32.4239 | 32.7784 | 34.5806 | 93.1396 | 93.2389 | 93.1454
2022-09-07 22:29 | 0:39 | 35.3976 | 31.9651 | 35.3848 | 47.2851 | 47.4891 | 48.3791 | 46.7517 | 46.8916 | 47.7441 | 47.4014 | 47.6258 | 47.3042 | 33.8596 | 35.3199 | 34.1349 | 33.6108 | 95.625 | 94.537 | 95.565 | 40.2703 | 35.5039 | 31.5066 | 96.6145 | 42.4267 | 33.9873 | 35.1672 | 34.3219 | 32.999 | 33.1315 | 33.6828 | 33.2814 | 32.9357 | 36.0396 | 36.2063 | 33.2024 | 32.9171 | 36.1161 | 35.7258 | 36.9804 | 36.0371 | 34.4364 | 37.7323 | 40.5453 | 38.3558 | 37.3215 | 35.1422 | 33.9767 | 35.9987 | 33.1973 | 33.026 | 33.2977 | 34.9085 | 32.8714 | 33.0326 | 34.2449 | 32.4613 | 32.8081 | 34.6115 | 93.31 | 93.3597 | 93.2568
2022-09-07 22:29 | 0:39 | 35.1625 | 31.9622 | 35.1442 | 47.1841 | 47.4241 | 47.9776 | 46.6 | 46.471 | 47.5648 | 47.0423 | 47.2868 | 47.1898 | 33.8387 | 35.3934 | 34.1392 | 33.552 | 43.3724 | 40.1936 | 95.9066 | 38.2284 | 35.3815 | 31.4316 | 96.4707 | 42.2868 | 34.0047 | 35.1977 | 34.3337 | 33.0171 | 33.136 | 33.6362 | 33.2792 | 32.9863 | 36.057 | 36.2082 | 33.2166 | 32.9448 | 36.1545 | 35.7143 | 37.0125 | 36.0599 | 34.4735 | 37.7255 | 40.5275 | 38.3629 | 37.3379 | 35.1645 | 33.9763 | 36.0006 | 33.1983 | 33.0601 | 33.3003 | 34.8919 | 32.8779 | 33.0367 | 34.244 | 32.484 | 32.8057 | 34.6025 | 93.4446 | 93.4899 | 93.3618
2022-09-07 22:29 | 0:39 | 34.9182 | 31.9403 | 34.9614 | 47.0112 | 47.4868 | 47.5438 | 46.3564 | 46.0834 | 47.5053 | 46.7985 | 46.7871 | 47.0997 | 33.8409 | 35.4841 | 34.128 | 33.538 | 39.1821 | 40.7008 | 45.7853 | 37.7423 | 35.2273 | 31.3429 | 96.5245 | 42.288 | 33.9964 | 35.2257 | 34.3597 | 33.0119 | 33.1636 | 33.6205 | 33.2646 | 32.9866 | 36.0495 | 36.2486 | 33.2309 | 32.9514 | 36.2063 | 35.721 | 37.052 | 36.0992 | 34.5064 | 37.7204 | 40.5119 | 38.377 | 37.3127 | 35.1468 | 34.0231 | 35.9975 | 33.1893 | 33.0746 | 33.3163 | 34.896 | 32.8808 | 33.0577 | 34.2311 | 32.4792 | 32.8403 | 34.6229 | 93.5453 | 93.6112 | 93.4415
2022-09-07 22:30 | 0:40 | 34.7366 | 31.9617 | 34.8188 | 47.0753 | 47.4552 | 47.142 | 46.1 | 45.7933 | 47.3832 | 46.8688 | 46.5829 | 47.0057 | 33.833 | 35.572 | 34.1772 | 33.5271 | 38.4212 | 40.4438 | 43.0892 | 37.4892 | 35.0288 | 31.2984 | 96.445 | 41.9571 | 34.0315 | 35.2518 | 34.3683 | 33.0052 | 33.1968 | 33.5987 | 33.2539 | 33.0234 | 36.0717 | 36.2681 | 33.2493 | 32.9377 | 36.2082 | 35.7131 | 37.0718 | 36.1161 | 34.5353 | 37.7372 | 40.4693 | 38.3279 | 37.3167 | 35.1775 | 34.0161 | 36.0199 | 33.1923 | 33.0827 | 33.3295 | 34.9199 | 32.9046 | 33.0516 | 34.2205 | 32.491 | 32.8405 | 34.6518 | 93.7108 | 93.7678 | 93.5349
2022-09-07 22:30 | 0:40 | 34.5614 | 31.9141 | 34.7937 | 49.0542 | 47.7531 | 50.4958 | 47.8331 | 47.3107 | 47.818 | 48.3013 | 49.6903 | 47.3425 | 33.8341 | 35.6589 | 34.1739 | 33.5147 | 38.0952 | 39.8589 | 42.376 | 37.3177 | 34.8531 | 31.2927 | 96.4017 | 41.8518 | 34.0447 | 35.295 | 34.4364 | 32.9922 | 33.2024 | 33.6041 | 33.2401 | 33.047 | 36.0592 | 36.3013 | 33.254 | 32.9579 | 36.2486 | 35.6991 | 37.106 | 36.1545 | 34.5688 | 37.7288 | 40.4436 | 38.3476 | 37.3008 | 35.1766 | 34.0254 | 35.9927 | 33.2001 | 33.1017 | 33.349 | 34.9051 | 32.9064 | 33.0746 | 34.2668 | 32.5007 | 32.8392 | 34.6524 | 93.8633 | 93.924 | 93.5623
2022-09-07 22:30 | 0:40 | 34.8422 | 31.9697 | 35.0697 | 50.4352 | 67.0304 | 71.7873 | 68.963 | 57.3206 | 51.1769 | 58.5097 | 57.6166 | 50.5461 | 33.8207 | 35.7356 | 34.2026 | 33.5087 | 37.8596 | 39.4972 | 41.4214 | 37.143 | 34.7092 | 31.2628 | 96.3832 | 41.8662 | 34.0679 | 35.3145 | 34.4735 | 32.9937 | 33.2166 | 33.6057 | 33.2334 | 33.0645 | 36.0761 | 36.3495 | 33.2766 | 32.9752 | 36.2681 | 35.6762 | 37.1545 | 36.2063 | 34.5662 | 37.7299 | 40.4265 | 38.3162 | 37.2712 | 35.1868 | 34.0239 | 35.9985 | 33.2044 | 33.1258 | 33.3612 | 34.9102 | 32.9164 | 33.1097 | 34.2871 | 32.517 | 32.8805 | 34.6708 | 93.9773 | 94.1239 | 93.4972
2022-09-07 22:30 | 0:40 | 35.2958 | 32.0256 | 35.4648 | 50.2101 | 81.0753 | 81.0712 | 80.3619 | 63.727 | 53.6778 | 67.3495 | 58.5068 | 52.1048 | 33.856 | 35.7881 | 34.2531 | 33.5293 | 37.742 | 39.0793 | 40.6122 | 36.9538 | 34.6206 | 31.1673 | 96.3373 | 41.8434 | 34.089 | 35.3666 | 34.5064 | 33.0132 | 33.2309 | 33.6023 | 33.2184 | 33.0776 | 36.0868 | 36.3673 | 33.2888 | 32.9648 | 36.3013 | 35.6893 | 37.1809 | 36.2082 | 34.6324 | 37.7273 | 40.395 | 38.3125 | 37.2561 | 35.2115 | 34.0413 | 36.0161 | 33.2071 | 33.1403 | 33.3906 | 34.9118 | 32.9433 | 33.0997 | 34.3425 | 32.5292 | 32.8879 | 34.705 | 94.16 | 94.2712 | 93.7039
2022-09-07 22:30 | 0:40 | 35.6518 | 32.0095 | 35.6578 | 51.4296 | 89.3015 | 84.3355 | 83.7631 | 81.5157 | 51.3123 | 54.8137 | 52.6254 | 50.6008 | 33.86 | 35.837 | 34.2547 | 33.5178 | 37.6535 | 38.765 | 39.9749 | 36.8316 | 34.6 | 31.0473 | 96.2921 | 41.7431 | 34.1068 | 35.3993 | 34.5353 | 33.0123 | 33.2493 | 33.6118 | 33.2531 | 33.115 | 36.0942 | 36.3833 | 33.3368 | 32.9902 | 36.3495 | 35.7027 | 37.2073 | 36.2486 | 34.6459 | 37.7266 | 40.3683 | 38.3135 | 37.2695 | 35.1786 | 34.0427 | 35.9944 | 33.2114 | 33.1615 | 33.3567 | 34.9051 | 32.9419 | 33.1566 | 34.3859 | 32.5555 | 32.912 | 34.736 | 94.1753 | 94.4277 | 93.7418
2022-09-07 22:30 | 0:40 | 35.6567 | 32.0462 | 35.6647 | 49.9206 | 39.5712 | 85.7835 | 88.0056 | 82.2024 | 49.7401 | 51.3914 | 49.9837 | 49.4059 | 33.882 | 35.9017 | 34.307 | 33.5215 | 37.6114 | 38.4496 | 39.4583 | 36.731 | 34.6074 | 30.9976 | 96.1999 | 41.6021 | 34.1048 | 35.4526 | 34.5688 | 33.023 | 33.254 | 33.5981 | 33.2248 | 33.1352 | 36.115 | 36.3922 | 33.348 | 33.0116 | 36.3673 | 35.7056 | 37.2438 | 36.2681 | 34.6734 | 37.7179 | 40.3463 | 38.3002 | 37.2588 | 35.2086 | 34.0559 | 35.9939 | 33.2214 | 33.1867 | 33.3755 | 34.9333 | 32.9591 | 33.1468 | 34.4218 | 32.5611 | 32.9293 | 34.7719 | 94.3651 | 94.5961 | 93.9456
2022-09-07 22:31 | 0:40 | 35.5156 | 32.0331 | 35.4733 | 49.38 | 38.6202 | 35.7523 | 38.2515 | 86.1334 | 49.2281 | 50.3967 | 49.393 | 48.9913 | 33.904 | 35.9544 | 34.3543 | 33.5456 | 37.567 | 38.1904 | 39.0538 | 36.654 | 34.5866 | 30.9178 | 96.2381 | 41.42 | 34.1351 | 35.483 | 34.5662 | 33.0127 | 33.2766 | 33.5771 | 33.2494 | 33.1711 | 36.1377 | 36.4434 | 33.3307 | 33.0269 | 36.3833 | 35.7184 | 37.26 | 36.3013 | 34.7085 | 37.7355 | 40.3382 | 38.3171 | 37.2293 | 35.2075 | 34.0499 | 35.9935 | 33.2166 | 33.1856 | 33.4077 | 34.9381 | 32.9807 | 33.175 | 34.4509 | 32.5834 | 32.9459 | 34.7764 | 94.4754 | 94.7056 | 93.9627
2022-09-07 22:31 | 0:41 | 35.3203 | 32.0258 | 35.3618 | 49.3893 | 37.9084 | 35.2095 | 36.677 | 36.9537 | 48.9473 | 51.9715 | 49.1595 | 48.8329 | 33.9215 | 35.9919 | 34.3838 | 33.5489 | 37.566 | 37.9548 | 38.7102 | 36.5893 | 34.4842 | 30.8536 | 96.0821 | 41.419 | 34.1608 | 35.5192 | 34.6324 | 33.0165 | 33.2888 | 33.5881 | 33.2496 | 33.1942 | 36.1567 | 36.4646 | 33.3718 | 33.03 | 36.3922 | 35.7011 | 37.2724 | 36.3495 | 34.7147 | 37.7015 | 40.3101 | 38.2886 | 37.2101 | 35.2135 | 34.0832 | 36.0056 | 33.2122 | 33.198 | 33.4048 | 34.9253 | 32.9727 | 33.1811 | 34.4422 | 32.6008 | 32.9425 | 34.8076 | 94.6263 | 94.8155 | 94.059
2022-09-07 22:31 | 0:41 | 35.2961 | 32.1165 | 35.4374 | 49.3961 | 37.4711 | 34.8845 | 36.191 | 36.1022 | 52.5703 | 64.7242 | 57.5137 | 51.9371 | 33.9725 | 36.0609 | 34.4258 | 33.546 | 37.5782 | 37.7687 | 38.4813 | 36.538 | 34.381 | 30.7786 | 96.0009 | 41.2582 | 34.1694 | 35.5472 | 34.6459 | 33.0216 | 33.3368 | 33.601 | 33.2484 | 33.22 | 36.1649 | 36.4957 | 33.3742 | 33.0406 | 36.4434 | 35.703 | 37.3112 | 36.3673 | 34.7241 | 37.7257 | 40.2935 | 38.2785 | 37.2277 | 35.2125 | 34.0714 | 36.0309 | 33.2044 | 33.2238 | 33.4154 | 34.9161 | 32.9849 | 33.2209 | 34.4866 | 32.6069 | 32.9613 | 34.8217 | 94.7586 | 94.864 | 94.1795
2022-09-07 22:31 | 0:41 | 35.5442 | 32.1439 | 35.6182 | 49.982 | 37.0755 | 34.8352 | 35.7935 | 35.5474 | 53.7395 | 77.4926 | 58.375 | 52.2174 | 33.9815 | 36.0819 | 34.4856 | 33.5815 | 37.6145 | 37.594 | 38.3667 | 36.5251 | 34.3204 | 30.732 | 95.9276 | 41.2675 | 34.19 | 35.5735 | 34.6734 | 33.0331 | 33.348 | 33.5959 | 33.2608 | 33.2191 | 36.1788 | 36.518 | 33.3859 | 33.0715 | 36.4646 | 35.7115 | 37.3384 | 36.3833 | 34.7697 | 37.7147 | 40.2605 | 38.2907 | 37.213 | 35.2349 | 34.0808 | 35.9989 | 33.206 | 33.2276 | 33.4346 | 34.9229 | 32.98 | 33.2164 | 34.5192 | 32.6334 | 32.9781 | 34.8276 | 94.8415 | 94.9542 | 94.1776
2022-09-07 22:31 | 0:41 | 35.7571 | 32.1826 | 35.79 | 56.2546 | 36.8665 | 34.6915 | 35.5572 | 35.2285 | 54.6553 | 79.1748 | 62.8616 | 55.7847 | 34.021 | 36.1103 | 34.5297 | 33.6289 | 37.623 | 37.4567 | 38.2778 | 36.4944 | 34.3005 | 30.6831 | 91.4928 | 41.2926 | 34.2043 | 35.6257 | 34.7085 | 33.0547 | 33.3307 | 33.6237 | 33.2734 | 33.2568 | 36.2036 | 36.5353 | 33.4229 | 33.1042 | 36.4957 | 35.7092 | 37.3792 | 36.3922 | 34.7958 | 37.7122 | 40.2863 | 38.3097 | 37.1946 | 35.2211 | 34.1035 | 35.9957 | 33.2385 | 33.2604 | 33.4469 | 34.9663 | 33.0107 | 33.2378 | 34.6001 | 32.6375 | 32.9808 | 34.8658 | 94.842 | 94.994 | 94.2211
2022-09-07 22:31 | 0:41 | 36.239 | 32.2644 | 36.118 | 52.8016 | 36.5094 | 34.6359 | 35.3725 | 35.0436 | 56.5826 | 83.4469 | 73.8941 | 71.9826 | 34.0642 | 36.1676 | 34.606 | 33.6358 | 37.6842 | 37.3834 | 38.2609 | 36.4934 | 34.4268 | 30.6399 | 92.7124 | 41.8274 | 34.2336 | 35.6646 | 34.7147 | 33.0647 | 33.3718 | 33.6232 | 33.2867 | 33.2835 | 36.2305 | 36.5679 | 33.4303 | 33.1162 | 36.518 | 35.7137 | 37.3935 | 36.4434 | 34.8233 | 37.7091 | 40.3163 | 38.2954 | 37.2104 | 35.2247 | 34.0885 | 36.0171 | 33.2398 | 33.2703 | 33.4619 | 34.9583 | 33.0309 | 33.2708 | 34.6475 | 32.6482 | 33.0101 | 34.891 | 94.7417 | 94.9153 | 94.1476
2022-09-07 22:32 | 0:41 | 36.4496 | 32.3007 | 36.1058 | 50.8462 | 36.047 | 34.5815 | 35.1329 | 34.8634 | 78.1974 | 87.9788 | 80.2736 | 79.4561 | 34.1018 | 36.2151 | 34.6515 | 33.6741 | 37.686 | 37.2796 | 38.2398 | 36.4906 | 34.6968 | 30.653 | 93.8379 | 41.3437 | 34.2554 | 35.6928 | 34.7241 | 33.0819 | 33.3742 | 33.6211 | 33.2923 | 33.2966 | 36.2602 | 36.5636 | 33.4545 | 33.1422 | 36.5353 | 35.731 | 37.4225 | 36.4646 | 34.8653 | 37.7111 | 40.3434 | 38.3152 | 37.1752 | 35.2689 | 34.0856 | 36.0287 | 33.2441 | 33.2839 | 33.4657 | 34.9479 | 33.0433 | 33.2954 | 34.7052 | 32.667 | 33.0391 | 34.9308 | 94.5264 | 94.7192 | 93.9879
2022-09-07 22:32 | 0:42 | 36.4811 | 32.346 | 36.1687 | 51.0843 | 35.6792 | 34.5202 | 34.9324 | 34.7069 | 82.9554 | 91.426 | 85.5984 | 81.258 | 34.1223 | 36.2315 | 34.7166 | 33.7007 | 37.7191 | 37.2133 | 38.2153 | 36.5059 | 34.9082 | 30.7156 | 94.3791 | 41.3062 | 34.2697 | 35.7483 | 34.7697 | 33.101 | 33.3859 | 33.6465 | 33.3089 | 33.3105 | 36.2708 | 36.5939 | 33.47 | 33.1456 | 36.5679 | 35.732 | 37.4465 | 36.4957 | 34.8859 | 37.7254 | 40.3608 | 38.3284 | 37.1823 | 35.2464 | 34.0932 | 36.0427 | 33.2523 | 33.2843 | 33.4971 | 34.9701 | 33.0491 | 33.2912 | 34.7117 | 32.6882 | 33.039 | 34.9516 | 94.2863 | 94.4992 | 93.8567
2022-09-07 22:32 | 0:42 | 36.439 | 32.3651 | 36.1102 | 50.7161 | 35.4111 | 34.4672 | 34.7664 | 34.5933 | 89.9809 | 92.6616 | 93.9649 | 85.8441 | 34.152 | 36.2816 | 34.7592 | 33.7242 | 37.7658 | 37.1464 | 38.1511 | 36.5136 | 35.0321 | 30.7062 | 94.6143 | 41.1052 | 34.2798 | 35.7679 | 34.7958 | 33.0983 | 33.4229 | 33.6422 | 33.3126 | 33.3433 | 36.3031 | 36.6122 | 33.4833 | 33.1757 | 36.5636 | 35.7379 | 37.48 | 36.518 | 34.9184 | 37.6982 | 40.3331 | 38.3313 | 37.1614 | 35.2625 | 34.1103 | 36.0386 | 33.2614 | 33.2821 | 33.4974 | 34.9823 | 33.0427 | 33.3216 | 34.7841 | 32.7176 | 33.0592 | 34.9831 | 94.0679 | 94.2912 | 93.6896
2022-09-07 22:32 | 0:42 | 36.2785 | 32.3647 | 36.006 | 49.587 | 35.1969 | 34.4134 | 34.6557 | 34.5002 | 38.5649 | 92.466 | 36.8987 | 89.0849 | 34.1719 | 36.3136 | 34.773 | 33.7631 | 37.7934 | 37.1049 | 38.045 | 36.5338 | 35.041 | 30.6816 | 94.8691 | 41.324 | 34.2885 | 35.7961 | 34.8233 | 33.1305 | 33.4303 | 33.8533 | 33.3468 | 33.3803 | 36.3217 | 36.6337 | 33.5008 | 33.2193 | 36.5939 | 35.7496 | 37.496 | 36.5353 | 34.9192 | 37.6785 | 40.3537 | 38.3213 | 37.1567 | 35.2527 | 34.125 | 36.0395 | 33.2617 | 33.3198 | 33.514 | 34.959 | 33.0811 | 33.3356 | 34.7799 | 32.7332 | 33.0759 | 35.0038 | 93.9358 | 94.0869 | 93.6296
2022-09-07 22:32 | 0:42 | 36.1148 | 32.3572 | 35.9292 | 49.7179 | 35.0359 | 34.376 | 34.5639 | 34.4265 | 36.705 | 41.8815 | 36.2407 | 69.3096 | 34.2246 | 36.3226 | 34.8321 | 33.7806 | 37.8394 | 37.0575 | 37.9974 | 36.5166 | 35.1136 | 30.7078 | 94.9315 | 41.193 | 34.3008 | 35.8186 | 34.8653 | 33.1543 | 33.4545 | 33.8946 | 33.4164 | 33.4072 | 36.3276 | 36.6657 | 33.542 | 33.2122 | 36.6122 | 35.755 | 37.5282 | 36.5679 | 34.9555 | 37.68 | 40.321 | 38.3268 | 37.1506 | 35.2351 | 34.1369 | 36.0445 | 33.2441 | 33.338 | 33.5101 | 34.9699 | 33.0686 | 33.3509 | 34.7957 | 32.7321 | 33.0934 | 35.0335 | 93.8218 | 93.9633 | 93.5722
2022-09-07 22:32 | 0:42 | 35.9311 | 32.3786 | 35.785 | 49.3098 | 34.9188 | 34.347 | 34.4683 | 34.3535 | 36.317 | 40.6746 | 35.9198 | 37.9017 | 34.2489 | 36.3411 | 34.8914 | 33.8066 | 37.8711 | 37.0229 | 37.9357 | 36.5227 | 35.1116 | 30.6466 | 94.8095 | 40.9877 | 34.3277 | 35.8361 | 34.8859 | 33.1785 | 33.47 | 33.9038 | 33.4347 | 33.4316 | 36.3436 | 36.6765 | 33.5297 | 33.2429 | 36.6337 | 35.7705 | 37.5524 | 36.5636 | 34.9559 | 37.6989 | 40.3415 | 38.3381 | 37.1347 | 35.2477 | 34.1369 | 36.0348 | 33.2771 | 33.3492 | 33.5236 | 34.9546 | 33.0995 | 33.3916 | 34.8082 | 32.7729 | 33.1155 | 35.0516 | 93.6996 | 93.8272 | 93.4553
2022-09-07 22:33 | 0:43 | 35.6841 | 32.3549 | 35.679 | 48.8615 | 34.8188 | 34.3236 | 34.4289 | 34.2991 | 36.1291 | 40.0362 | 35.7645 | 36.9745 | 34.2705 | 36.379 | 34.925 | 33.8331 | 37.9036 | 36.9841 | 37.918 | 36.5556 | 35.0288 | 30.6085 | 94.7601 | 40.9053 | 34.3293 | 35.8728 | 34.9184 | 33.184 | 33.4833 | 33.8985 | 33.4604 | 33.4541 | 36.3763 | 36.7131 | 33.5649 | 33.2662 | 36.6657 | 35.7847 | 37.562 | 36.5939 | 34.9799 | 37.7007 | 40.3043 | 38.3225 | 37.1288 | 35.2727 | 34.162 | 36.0626 | 33.2769 | 33.3614 | 33.5428 | 34.9769 | 33.1035 | 33.4004 | 34.8303 | 32.7804 | 33.126 | 35.0543 | 93.6271 | 93.7543 | 93.4356
2022-09-07 22:33 | 0:43 | 35.452 | 32.313 | 35.58 | 49.6424 | 34.7257 | 34.2906 | 34.3537 | 34.2689 | 35.9996 | 38.7377 | 35.6618 | 36.5748 | 34.2982 | 36.4131 | 34.9775 | 33.87 | 37.9412 | 36.9411 | 37.9475 | 36.5624 | 34.9374 | 30.5909 | 94.692 | 40.7606 | 34.3581 | 35.887 | 34.9192 | 33.1895 | 33.5008 | 33.8762 | 33.4879 | 33.4658 | 36.3869 | 36.7159 | 33.5463 | 33.2897 | 36.6765 | 35.7736 | 37.5904 | 36.6122 | 34.993 | 37.6845 | 40.3102 | 38.3202 | 37.1276 | 35.2676 | 34.1694 | 36.0723 | 33.2803 | 33.3669 | 33.5439 | 34.9789 | 33.109 | 33.4033 | 34.8581 | 32.7645 | 33.1262 | 35.0736 | 93.5774 | 93.6701 | 93.3831
2022-09-07 22:33 | 0:43 | 35.2689 | 32.2756 | 35.4444 | 49.8386 | 34.6482 | 34.2952 | 34.3142 | 34.2519 | 35.8881 | 38.1616 | 35.519 | 36.2631 | 34.3312 | 36.4138 | 34.9994 | 33.889 | 37.9701 | 36.9062 | 37.9687 | 36.596 | 34.8479 | 30.5616 | 94.5994 | 40.806 | 34.3861 | 35.9147 | 34.9555 | 33.1884 | 33.542 | 33.8874 | 33.4947 | 33.4974 | 36.4084 | 36.7147 | 33.5868 | 33.2974 | 36.7131 | 35.7792 | 37.6116 | 36.6337 | 34.9938 | 37.6744 | 40.2929 | 38.3107 | 37.1065 | 35.2683 | 34.1579 | 36.0605 | 33.2754 | 33.3734 | 33.5403 | 34.9908 | 33.1309 | 33.4241 | 34.907 | 32.8015 | 33.1645 | 35.0995 | 93.4927 | 93.6062 | 93.3318
2022-09-07 22:33 | 0:43 | 35.1566 | 32.2915 | 35.3236 | 49.0744 | 34.6106 | 34.2647 | 34.2735 | 34.2173 | 35.7956 | 37.7349 | 35.4106 | 35.9942 | 34.3728 | 36.4439 | 35.0395 | 33.9069 | 38.0041 | 36.8949 | 37.8803 | 36.5984 | 34.7917 | 30.5057 | 94.5404 | 40.995 | 34.3747 | 35.9329 | 34.9559 | 33.2208 | 33.5297 | 33.8876 | 33.4859 | 33.5241 | 36.4248 | 36.7511 | 33.6135 | 33.3191 | 36.7159 | 35.8001 | 37.6399 | 36.6657 | 35.0211 | 37.6838 | 40.3008 | 38.3103 | 37.095 | 35.2631 | 34.1653 | 36.0438 | 33.2883 | 33.3909 | 33.5624 | 35.0007 | 33.1416 | 33.4529 | 34.9262 | 32.8128 | 33.1676 | 35.118 | 93.4713 | 93.5816 | 93.3318
2022-09-07 22:33 | 0:43 | 34.9657 | 32.2577 | 35.1703 | 47.753 | 34.5604 | 34.2546 | 34.2473 | 34.2061 | 35.7027 | 37.3594 | 35.2844 | 35.7931 | 34.3924 | 36.4592 | 35.0867 | 33.9418 | 38.0251 | 36.8804 | 37.8238 | 36.6281 | 34.7536 | 30.6581 | 95.0445 | 40.7238 | 34.4057 | 35.9749 | 34.9799 | 33.2179 | 33.5649 | 33.904 | 33.4904 | 33.5211 | 36.4387 | 36.7509 | 33.6138 | 33.3253 | 36.7147 | 35.8236 | 37.6635 | 36.6765 | 35.0384 | 37.668 | 40.2814 | 38.3255 | 37.0839 | 35.2552 | 34.1411 | 36.068 | 33.2905 | 33.3833 | 33.5502 | 34.9988 | 33.1213 | 33.4594 | 34.948 | 32.8325 | 33.2008 | 35.1281 | 93.3934 | 93.5477 | 93.284
2022-09-07 22:33 | 0:43 | 34.7263 | 32.171 | 35.0195 | 47.2523 | 34.5281 | 34.2552 | 34.2407 | 34.1816 | 35.6093 | 37.0543 | 35.1806 | 35.6045 | 34.4017 | 36.4847 | 35.101 | 33.9301 | 38.0463 | 36.8546 | 37.7544 | 36.633 | 34.6722 | 30.54 | 95.2016 | 40.6207 | 34.4078 | 35.9818 | 34.993 | 33.2455 | 33.5463 | 33.8731 | 33.484 | 33.5535 | 36.4497 | 36.7767 | 33.6437 | 33.3388 | 36.7511 | 35.8422 | 37.6645 | 36.7131 | 35.033 | 37.6646 | 40.2687 | 38.3186 | 37.0663 | 35.268 | 34.1699 | 36.0828 | 33.313 | 33.4245 | 33.5675 | 34.9877 | 33.1739 | 33.472 | 34.95 | 32.8672 | 33.201 | 35.1719 | 93.354 | 93.4603 | 93.2716
2022-09-07 22:34 | 0:43 | 34.452 | 32.1717 | 34.8649 | 46.974 | 34.4867 | 34.2471 | 34.1838 | 34.1594 | 35.5864 | 36.8063 | 35.0704 | 35.4776 | 34.4314 | 36.4973 | 35.1537 | 33.986 | 38.0674 | 36.8452 | 37.6887 | 36.6478 | 34.5641 | 30.4903 | 95.2671 | 40.3893 | 34.4338 | 36.0039 | 34.9938 | 33.2411 | 33.5868 | 33.858 | 33.5007 | 33.5652 | 36.4945 | 36.7842 | 33.6532 | 33.3557 | 36.7509 | 35.8377 | 37.6815 | 36.7159 | 35.0524 | 37.6885 | 40.2455 | 38.3026 | 37.0676 | 35.2555 | 34.1689 | 36.0523 | 33.2929 | 33.4324 | 33.6114 | 35.0005 | 33.1619 | 33.4772 | 34.9499 | 32.8589 | 33.1904 | 35.1732 | 93.2998 | 93.412 | 93.2533
2022-09-07 22:34 | 0:44 | 34.0469 | 32.1644 | 34.6649 | 46.4547 | 34.4593 | 34.232 | 34.1817 | 34.1581 | 35.5261 | 36.588 | 35.0028 | 35.3623 | 34.4578 | 36.5029 | 35.1871 | 34.0009 | 38.0818 | 36.8047 | 37.6375 | 36.6667 | 34.3807 | 30.3679 | 95.3241 | 40.444 | 34.4601 | 35.9994 | 35.0211 | 33.2398 | 33.6135 | 33.8325 | 33.4926 | 33.6006 | 36.4794 | 36.8092 | 33.6673 | 33.3757 | 36.7767 | 35.8341 | 37.6751 | 36.7147 | 35.0584 | 37.6835 | 40.2213 | 38.309 | 37.0641 | 35.272 | 34.172 | 36.0566 | 33.3229 | 33.4414 | 33.5856 | 35.0084 | 33.1634 | 33.4986 | 34.9249 | 32.8788 | 33.2358 | 35.1862 | 93.18 | 93.3087 | 93.1829
2022-09-07 22:34 | 0:44 | 33.7186 | 32.0928 | 34.45 | 46.4255 | 34.4269 | 34.2414 | 34.174 | 34.1555 | 35.4801 | 36.4277 | 34.9348 | 35.2635 | 34.4881 | 36.507 | 35.2127 | 34.0216 | 38.122 | 36.7804 | 37.5889 | 36.6439 | 34.227 | 30.2763 | 95.3573 | 40.2487 | 34.4605 | 36.0257 | 35.0384 | 33.2548 | 33.6138 | 33.8369 | 33.4728 | 33.5956 | 36.5051 | 36.81 | 33.6738 | 33.3702 | 36.7842 | 35.8446 | 37.7209 | 36.7511 | 35.0736 | 37.6665 | 40.2162 | 38.2916 | 37.0433 | 35.2744 | 34.1876 | 36.0623 | 33.2942 | 33.4496 | 33.6001 | 35.0167 | 33.2022 | 33.5332 | 34.9396 | 32.8883 | 33.2206 | 35.2071 | 93.139 | 93.2388 | 93.1392
2022-09-07 22:34 | 0:44 | 33.459 | 31.9805 | 34.2955 | 46.0251 | 34.404 | 34.2327 | 34.167 | 34.1414 | 35.4661 | 36.2635 | 34.8886 | 35.18 | 34.5136 | 36.5361 | 35.2386 | 34.0417 | 38.1173 | 36.75 | 37.5401 | 36.6613 | 34.0535 | 30.2386 | 95.4463 | 40.2769 | 34.458 | 36.0277 | 35.033 | 33.2442 | 33.6437 | 33.8308 | 33.4795 | 33.6281 | 36.5352 | 36.8344 | 33.6999 | 33.4074 | 36.8092 | 35.8672 | 37.7392 | 36.7509 | 35.1082 | 37.6656 | 40.1884 | 38.2858 | 37.0133 | 35.2697 | 34.1942 | 36.0698 | 33.3123 | 33.4664 | 33.5876 | 35.008 | 33.1936 | 33.5377 | 34.964 | 32.9071 | 33.2268 | 35.2359 | 93.032 | 93.137 | 93.0356
2022-09-07 22:34 | 0:44 | 33.4552 | 31.9704 | 34.1395 | 45.4667 | 34.368 | 34.2381 | 34.1543 | 34.14 | 35.4584 | 36.1414 | 34.8338 | 35.1351 | 34.5297 | 36.5618 | 35.2762 | 34.0738 | 38.1474 | 36.7275 | 37.5122 | 36.68 | 33.9026 | 30.1307 | 95.4996 | 40.1502 | 34.4777 | 36.0314 | 35.0524 | 33.258 | 33.6532 | 33.8449 | 33.477 | 33.6394 | 36.5388 | 36.861 | 33.7184 | 33.4178 | 36.81 | 35.8684 | 37.7463 | 36.7767 | 35.1164 | 37.6511 | 40.1605 | 38.2934 | 36.9964 | 35.2752 | 34.1751 | 36.0668 | 33.2992 | 33.46 | 33.6094 | 35.0115 | 33.2029 | 33.5465 | 34.9608 | 32.9054 | 33.2745 | 35.2424 | 92.9805 | 93.0695 | 92.9854
2022-09-07 22:34 | 0:44 | 33.1886 | 31.8787 | 33.9583 | 45.5433 | 34.3477 | 34.2432 | 34.1429 | 34.1465 | 35.4525 | 36.0455 | 34.8004 | 35.0569 | 34.5666 | 36.54 | 35.3082 | 34.1019 | 38.1548 | 36.7092 | 37.4549 | 36.6955 | 33.7491 | 30.0283 | 95.5358 | 40.0568 | 34.5082 | 36.0418 | 35.0584 | 33.2676 | 33.6673 | 33.8357 | 33.4816 | 33.646 | 36.568 | 36.8589 | 33.7351 | 33.4172 | 36.8344 | 35.8738 | 37.7652 | 36.7842 | 35.1224 | 37.6431 | 40.1424 | 38.2748 | 36.9815 | 35.2795 | 34.1694 | 36.0463 | 33.3285 | 33.4811 | 33.6294 | 35.0042 | 33.2167 | 33.5577 | 34.9709 | 32.9153 | 33.2858 | 35.2539 | 92.894 | 92.9698 | 92.9179
2022-09-07 22:35 | 0:45 | 33.2504 | 31.8254 | 33.978 | 45.2466 | 34.3323 | 34.2441 | 34.146 | 34.1462 | 35.4316 | 35.9483 | 34.7775 | 35.0195 | 34.5696 | 36.566 | 35.3431 | 34.1156 | 38.1785 | 36.6991 | 37.4383 | 36.7009 | 33.6128 | 29.9868 | 95.6273 | 40.0759 | 34.4958 | 36.0619 | 35.0736 | 33.271 | 33.6738 | 33.829 | 33.4929 | 33.6621 | 36.5841 | 36.8801 | 33.7274 | 33.4332 | 36.861 | 35.8874 | 37.7854 | 36.8092 | 35.1413 | 37.6359 | 40.1005 | 38.2844 | 36.9905 | 35.2486 | 34.1718 | 36.0631 | 33.3268 | 33.4795 | 33.6215 | 35.0323 | 33.2223 | 33.5871 | 34.9719 | 32.9543 | 33.2834 | 35.2594 | 92.7972 | 92.9045 | 92.8727
2022-09-07 22:35 | 0:45 | 33.4253 | 31.8006 | 34.0751 | 45.0788 | 34.3182 | 34.2336 | 34.1359 | 34.1295 | 35.452 | 35.8911 | 34.7609 | 34.9546 | 34.6118 | 36.5617 | 35.3585 | 34.1332 | 38.1941 | 36.6721 | 37.4075 | 36.7275 | 33.4969 | 29.9494 | 95.6079 | 39.8929 | 34.5036 | 36.0654 | 35.1082 | 33.2769 | 33.6999 | 33.8562 | 33.4913 | 33.6783 | 36.583 | 36.8994 | 33.7617 | 33.4246 | 36.8589 | 35.8896 | 37.7876 | 36.81 | 35.1546 | 37.6359 | 40.0796 | 38.2568 | 36.9763 | 35.2617 | 34.1716 | 36.0656 | 33.3347 | 33.5003 | 33.6543 | 35.0207 | 33.2309 | 33.5728 | 34.9897 | 32.9435 | 33.3066 | 35.2691 | 92.7201 | 92.7745 | 92.7816
2022-09-07 22:35 | 0:45 | 33.4948 | 31.7587 | 34.0863 | 44.8043 | 34.3193 | 34.2538 | 34.1541 | 34.1327 | 35.4289 | 35.8089 | 34.7286 | 34.9342 | 34.639 | 36.5783 | 35.404 | 34.1641 | 38.1957 | 36.6552 | 37.3879 | 36.7429 | 33.3731 | 29.8534 | 95.6877 | 39.9934 | 34.5329 | 36.083 | 35.1164 | 33.2774 | 33.7184 | 33.846 | 33.5023 | 33.6984 | 36.6045 | 36.9149 | 33.7735 | 33.4474 | 36.8801 | 35.9122 | 37.8217 | 36.8344 | 35.1625 | 37.6118 | 40.0319 | 38.2525 | 36.9523 | 35.2782 | 34.2 | 36.0599 | 33.3242 | 33.5029 | 33.6476 | 35.0067 | 33.2377 | 33.6104 | 35.0159 | 32.9576 | 33.3092 | 35.2785 | 92.5124 | 92.6418 | 92.6418
2022-09-07 22:35 | 0:45 | 33.5043 | 31.698 | 34.0562 | 44.7771 | 34.299 | 34.2758 | 34.1656 | 34.1526 | 35.433 | 35.7671 | 34.7193 | 34.9176 | 34.648 | 36.5763 | 35.4179 | 34.1865 | 38.2224 | 36.636 | 37.368 | 36.769 | 33.2391 | 29.8162 | 95.7727 | 39.8707 | 34.5465 | 36.0969 | 35.1224 | 33.2847 | 33.7351 | 33.866 | 33.5027 | 33.714 | 36.6168 | 36.9297 | 33.7901 | 33.4778 | 36.8994 | 35.9207 | 37.8286 | 36.861 | 35.1696 | 37.5897 | 40.0318 | 38.2297 | 36.9326 | 35.291 | 34.1799 | 36.0498 | 33.3268 | 33.5245 | 33.6673 | 35.0077 | 33.239 | 33.6138 | 35.0321 | 32.9807 | 33.3298 | 35.2897 | 92.4573 | 92.5341 | 92.7038
2022-09-07 22:35 | 0:45 | 33.4566 | 31.6419 | 33.9492 | 44.6433 | 34.3001 | 34.2927 | 34.1425 | 34.1635 | 35.4485 | 35.7073 | 34.721 | 34.9004 | 34.6625 | 36.5892 | 35.4491 | 34.2005 | 38.242 | 36.6311 | 37.3422 | 36.7645 | 33.1061 | 29.6737 | 95.8089 | 39.8097 | 34.5656 | 36.1159 | 35.1413 | 33.2875 | 33.7274 | 33.8728 | 33.4993 | 33.7415 | 36.6108 | 36.9264 | 33.8103 | 33.5 | 36.9149 | 35.9158 | 37.8475 | 36.8589 | 35.1961 | 37.6041 | 39.9838 | 38.2418 | 36.9505 | 35.2623 | 34.1876 | 36.0618 | 33.3364 | 33.5383 | 33.6576 | 35.0065 | 33.24 | 33.6123 | 35.0452 | 32.9697 | 33.3339 | 35.3197 | 92.3556 | 92.4255 | 92.6256
2022-09-07 22:35 | 0:45 | 33.3989 | 31.5654 | 33.9281 | 44.3881 | 34.2808 | 34.3072 | 34.15 | 34.1761 | 35.4745 | 35.6776 | 34.6985 | 34.8838 | 34.6855 | 36.6259 | 35.507 | 34.2427 | 38.2515 | 36.6234 | 37.3492 | 36.7978 | 33.0168 | 29.6145 | 95.9104 | 39.7525 | 34.5581 | 36.1272 | 35.1546 | 33.2948 | 33.7617 | 33.8705 | 33.499 | 33.7322 | 36.6452 | 36.9428 | 33.8296 | 33.5058 | 36.9297 | 35.9362 | 37.8531 | 36.8801 | 35.1898 | 37.5933 | 39.9571 | 38.2244 | 36.9171 | 35.265 | 34.1974 | 36.0495 | 33.3181 | 33.5318 | 33.6635 | 35.0089 | 33.2598 | 33.6379 | 35.0669 | 32.976 | 33.3493 | 35.3362 | 92.3119 | 92.281 | 92.484
2022-09-07 22:36 | 0:45 | 33.3838 | 31.5256 | 33.8712 | 44.2588 | 34.2758 | 34.3225 | 34.1741 | 34.185 | 35.4952 | 35.6474 | 34.6948 | 34.8722 | 34.7134 | 36.6103 | 35.5051 | 34.2868 | 38.2713 | 36.609 | 37.3311 | 36.8159 | 32.9423 | 29.5235 | 95.9911 | 39.7936 | 34.585 | 36.1403 | 35.1625 | 33.3061 | 33.7735 | 33.9021 | 33.5048 | 33.751 | 36.6695 | 36.9455 | 33.8359 | 33.5215 | 36.9264 | 35.9508 | 37.8744 | 36.8994 | 35.2319 | 37.5971 | 39.9333 | 38.2148 | 36.9237 | 35.2655 | 34.208 | 36.0496 | 33.3282 | 33.5423 | 33.683 | 35.0232 | 33.2735 | 33.6582 | 35.0771 | 32.9987 | 33.3674 | 35.3541 | 92.1952 | 92.0809 | 92.4014
2022-09-07 22:36 | 0:46 | 33.3463 | 31.5103 | 33.7946 | 44.187 | 34.2668 | 34.3348 | 34.1759 | 34.2016 | 35.5054 | 35.6111 | 34.6814 | 34.8519 | 34.7405 | 36.6193 | 35.5316 | 34.2969 | 38.2692 | 36.6226 | 37.3062 | 36.838 | 32.8875 | 29.5082 | 96.0675 | 39.5366 | 34.5905 | 36.1704 | 35.1696 | 33.3291 | 33.7901 | 33.887 | 33.5192 | 33.7737 | 36.6892 | 36.9561 | 33.8469 | 33.5218 | 36.9428 | 35.9599 | 37.8957 | 36.9149 | 35.2285 | 37.5704 | 39.8978 | 38.2034 | 36.8998 | 35.2744 | 34.21 | 36.0603 | 33.3338 | 33.5634 | 33.681 | 34.9942 | 33.2636 | 33.6758 | 35.0906 | 33.0307 | 33.3821 | 35.3644 | 91.9665 | 91.9506 | 92.2284
2022-09-07 22:36 | 0:46 | 33.3124 | 31.4629 | 33.7586 | 43.9665 | 34.2672 | 34.3541 | 34.1789 | 34.2227 | 35.5233 | 35.5872 | 34.681 | 34.8608 | 34.7465 | 36.6155 | 35.5556 | 34.3311 | 38.3027 | 36.6086 | 37.3062 | 36.8524 | 32.8554 | 29.507 | 96.112 | 39.5407 | 34.5922 | 36.1831 | 35.1961 | 33.3199 | 33.8103 | 33.915 | 33.5401 | 33.7878 | 36.7183 | 36.9748 | 33.8704 | 33.5383 | 36.9455 | 35.9724 | 37.898 | 36.9297 | 35.2315 | 37.5679 | 39.879 | 38.2039 | 36.8987 | 35.2666 | 34.2124 | 36.0544 | 33.3411 | 33.5542 | 33.702 | 35.0157 | 33.2973 | 33.6789 | 35.1149 | 33.0314 | 33.3963 | 35.373 | 91.8089 | 91.8635 | 92.2604
2022-09-07 22:36 | 0:46 | 33.2487 | 31.4173 | 33.7211 | 43.9176 | 34.2481 | 34.3539 | 34.1673 | 34.2363 | 35.5418 | 35.5628 | 34.6678 | 34.8336 | 34.7694 | 36.6181 | 35.5848 | 34.3516 | 38.3107 | 36.5815 | 37.2897 | 36.8743 | 32.8258 | 29.4449 | 96.1912 | 39.7085 | 34.6134 | 36.1869 | 35.1898 | 33.3398 | 33.8296 | 33.9039 | 33.5395 | 33.8092 | 36.7376 | 37.0005 | 33.88 | 33.5488 | 36.9561 | 35.983 | 37.919 | 36.9264 | 35.2297 | 37.5486 | 39.8497 | 38.1932 | 36.8796 | 35.2752 | 34.2193 | 36.0476 | 33.3321 | 33.5753 | 33.6862 | 35.0254 | 33.2958 | 33.6883 | 35.1582 | 33.0618 | 33.4024 | 35.3911 | 91.6522 | 91.7494 | 92.151
2022-09-07 22:36 | 0:46 | 33.2077 | 31.3671 | 33.6723 | 43.6094 | 34.229 | 34.391 | 34.1905 | 34.2381 | 35.5532 | 35.5539 | 34.6779 | 34.8456 | 34.7863 | 36.6211 | 35.619 | 34.371 | 38.3244 | 36.5869 | 37.282 | 36.8931 | 32.7717 | 29.3817 | 96.298 | 39.4438 | 34.6273 | 36.2048 | 35.2319 | 33.3495 | 33.8359 | 33.921 | 33.5545 | 33.8162 | 36.7477 | 37.0156 | 33.8767 | 33.569 | 36.9748 | 35.9898 | 37.9322 | 36.9428 | 35.2565 | 37.5582 | 39.7932 | 38.1867 | 36.8604 | 35.2766 | 34.2128 | 36.0607 | 33.3338 | 33.573 | 33.6995 | 35.0176 | 33.2915 | 33.7092 | 35.1526 | 33.0451 | 33.4353 | 35.3939 | 91.6296 | 91.7066 | 92.155
2022-09-07 22:36 | 0:46 | 33.1632 | 31.3403 | 33.6136 | 43.5963 | 34.2275 | 34.41 | 34.2088 | 34.2508 | 35.5745 | 35.5316 | 34.6986 | 34.8475 | 34.8125 | 36.6267 | 35.6552 | 34.3797 | 38.3308 | 36.5619 | 37.2614 | 36.9098 | 32.7276 | 29.3154 | 96.4209 | 39.5385 | 34.6265 | 36.2202 | 35.2285 | 33.3688 | 33.8469 | 33.9431 | 33.557 | 33.8207 | 36.7584 | 37.0184 | 33.8791 | 33.588 | 37.0005 | 36.0115 | 37.9393 | 36.9455 | 35.2614 | 37.5543 | 39.7976 | 38.1846 | 36.8481 | 35.2577 | 34.2114 | 36.0413 | 33.3296 | 33.5977 | 33.6952 | 35.0125 | 33.2957 | 33.7146 | 35.1702 | 33.0652 | 33.4303 | 35.4094 | 91.6277 | 91.7138 | 92.1458
2022-09-07 22:37 | 0:47 | 33.1505 | 31.3045 | 33.6081 | 43.6019 | 34.2441 | 34.4191 | 34.2196 | 34.254 | 35.5977 | 35.5132 | 34.6885 | 34.8449 | 34.8312 | 36.6472 | 35.6592 | 34.4243 | 38.3287 | 36.5654 | 37.2535 | 36.9322 | 32.6722 | 29.3084 | 96.5794 | 39.5016 | 34.6473 | 36.2431 | 35.2315 | 33.3753 | 33.8704 | 33.955 | 33.5701 | 33.8436 | 36.768 | 37.0135 | 33.882 | 33.6044 | 37.0156 | 36.031 | 37.9453 | 36.9561 | 35.2841 | 37.5179 | 39.7524 | 38.1816 | 36.8422 | 35.2724 | 34.2026 | 36.0425 | 33.3288 | 33.6061 | 33.7082 | 35.0072 | 33.3085 | 33.7304 | 35.182 | 33.0841 | 33.4476 | 35.4208 | 91.729 | 91.845 | 92.1355
2022-09-07 22:37 | 0:47 | 33.1256 | 31.2766 | 33.5515 | 43.4139 | 34.2281 | 34.4297 | 34.245 | 34.289 | 35.594 | 35.501 | 34.6833 | 34.8212 | 34.851 | 36.6492 | 35.6898 | 34.4392 | 38.359 | 36.5748 | 37.2475 | 36.929 | 32.6382 | 29.2619 | 96.6584 | 39.2609 | 34.6678 | 36.2553 | 35.2297 | 33.3839 | 33.88 | 33.942 | 33.5807 | 33.8671 | 36.7914 | 37.0407 | 33.9209 | 33.6206 | 37.0184 | 36.0307 | 37.9764 | 36.9748 | 35.291 | 37.4996 | 39.7213 | 38.1536 | 36.8295 | 35.2557 | 34.2281 | 36.0514 | 33.355 | 33.5963 | 33.7351 | 35.0168 | 33.3065 | 33.7562 | 35.2207 | 33.0904 | 33.4524 | 35.4308 | 91.8212 | 91.9276 | 92.2381
2022-09-07 22:37 | 0:47 | 33.0585 | 31.2129 | 33.5078 | 43.2179 | 34.2242 | 34.4732 | 34.2446 | 34.2963 | 35.6254 | 35.5035 | 34.6845 | 34.8454 | 34.8657 | 36.6308 | 35.7117 | 34.4704 | 38.3735 | 36.566 | 37.2514 | 36.9472 | 32.6095 | 29.2734 | 96.6618 | 39.3692 | 34.6527 | 36.2574 | 35.2565 | 33.3792 | 33.8767 | 33.9457 | 33.5856 | 33.8916 | 36.783 | 37.0464 | 33.9226 | 33.6274 | 37.0135 | 36.037 | 37.9695 | 37.0005 | 35.2881 | 37.4888 | 39.6933 | 38.1606 | 36.8202 | 35.2608 | 34.2196 | 36.0565 | 33.3464 | 33.6166 | 33.7169 | 35.0117 | 33.3235 | 33.7661 | 35.2298 | 33.1052 | 33.4567 | 35.4353 | 91.8786 | 92.0147 | 92.3002
2022-09-07 22:37 | 0:47 | 33.0046 | 31.1205 | 33.4547 | 43.1821 | 34.2305 | 34.4786 | 34.2706 | 34.3285 | 35.6433 | 35.4693 | 34.6855 | 34.8156 | 34.8903 | 36.6302 | 35.7265 | 34.4777 | 38.3567 | 36.5497 | 37.2293 | 36.9593 | 32.6177 | 29.1861 | 96.7808 | 39.4181 | 34.6872 | 36.2789 | 35.2614 | 33.4095 | 33.8791 | 33.9618 | 33.59 | 33.8912 | 36.8043 | 37.0451 | 33.9282 | 33.648 | 37.0407 | 36.0495 | 37.9815 | 37.0156 | 35.3066 | 37.492 | 39.6579 | 38.1315 | 36.8121 | 35.2745 | 34.2393 | 36.0446 | 33.3391 | 33.6338 | 33.7272 | 35.0104 | 33.3365 | 33.7587 | 35.2341 | 33.1195 | 33.4851 | 35.4604 | 91.9573 | 92.1471 | 92.2791
2022-09-07 22:37 | 0:47 | 32.957 | 31.0237 | 33.4378 | 43.1245 | 34.2152 | 34.5049 | 34.281 | 34.3347 | 35.6694 | 35.487 | 34.6826 | 34.8384 | 34.8999 | 36.6369 | 35.7468 | 34.5104 | 38.37 | 36.5762 | 37.2281 | 36.9654 | 32.6574 | 29.2445 | 96.7426 | 39.3092 | 34.7027 | 36.2945 | 35.2841 | 33.3876 | 33.882 | 33.9701 | 33.6074 | 33.8968 | 36.8138 | 37.0625 | 33.9522 | 33.6522 | 37.0464 | 36.0615 | 37.9939 | 37.0184 | 35.3085 | 37.4848 | 39.6412 | 38.1262 | 36.7935 | 35.2525 | 34.2456 | 36.0446 | 33.3604 | 33.6408 | 33.7311 | 35.0171 | 33.3359 | 33.7744 | 35.2678 | 33.1408 | 33.4857 | 35.4647 | 92.0647 | 92.2122 | 92.4066
2022-09-07 22:37 | 0:47 | 32.8891 | 30.8719 | 33.3446 | 42.983 | 34.2061 | 34.521 | 34.2869 | 34.3638 | 35.6841 | 35.4566 | 34.6918 | 34.8523 | 34.9049 | 36.6195 | 35.7794 | 34.5251 | 38.378 | 36.5468 | 37.2054 | 36.9979 | 32.745 | 29.1454 | 96.5891 | 39.2928 | 34.6985 | 36.3029 | 35.291 | 33.4074 | 33.9209 | 33.9924 | 33.6281 | 33.9113 | 36.8413 | 37.0761 | 33.9521 | 33.6658 | 37.0451 | 36.0815 | 37.9971 | 37.0135 | 35.3223 | 37.4748 | 39.6055 | 38.1269 | 36.7765 | 35.2619 | 34.2338 | 36.035 | 33.3469 | 33.6296 | 33.7401 | 34.9908 | 33.3294 | 33.7867 | 35.2851 | 33.1434 | 33.4789 | 35.4883 | 92.1667 | 92.3371 | 92.4635
2022-09-07 22:38 | 0:47 | 32.8446 | 30.8579 | 33.3363 | 42.9861 | 34.214 | 34.5659 | 34.2971 | 34.3666 | 35.6998 | 35.4443 | 34.6948 | 34.8482 | 34.9227 | 36.6428 | 35.7896 | 34.5599 | 38.3825 | 36.5371 | 37.2117 | 36.9806 | 32.855 | 29.1237 | 96.4733 | 39.3007 | 34.7158 | 36.3098 | 35.2881 | 33.4085 | 33.9226 | 33.986 | 33.6023 | 33.9481 | 36.8516 | 37.0906 | 33.9611 | 33.6824 | 37.0625 | 36.0677 | 38.0202 | 37.0407 | 35.3195 | 37.4608 | 39.5827 | 38.1033 | 36.7927 | 35.2754 | 34.2395 | 36.0258 | 33.3416 | 33.6538 | 33.7532 | 35.0195 | 33.3468 | 33.79 | 35.3112 | 33.1641 | 33.5092 | 35.4787 | 92.3154 | 92.4387 | 92.473
2022-09-07 22:38 | 0:48 | 32.7709 | 30.754 | 33.2423 | 42.7315 | 34.1999 | 34.5712 | 34.3209 | 34.3844 | 35.7186 | 35.4543 | 34.7033 | 34.8455 | 34.9358 | 36.6536 | 35.8196 | 34.5794 | 38.3821 | 36.523 | 37.2121 | 37.0165 | 32.949 | 29.0529 | 96.4061 | 39.1062 | 34.717 | 36.3401 | 35.3066 | 33.4373 | 33.9282 | 34.0115 | 33.6239 | 33.9332 | 36.874 | 37.0837 | 33.9904 | 33.7026 | 37.0761 | 36.0903 | 38.0374 | 37.0464 | 35.3446 | 37.4556 | 39.5483 | 38.093 | 36.775 | 35.2699 | 34.2214 | 36.0311 | 33.3559 | 33.6771 | 33.7452 | 35.0129 | 33.3391 | 33.8286 | 35.3074 | 33.1668 | 33.5613 | 35.4841 | 92.4261 | 92.6082 | 92.3898
2022-09-07 22:38 | 0:48 | 32.6649 | 30.6971 | 33.1987 | 42.6731 | 34.1934 | 34.6004 | 34.3423 | 34.4125 | 35.7372 | 35.4422 | 34.7022 | 34.8703 | 34.9553 | 36.6339 | 35.8316 | 34.6237 | 38.3931 | 36.5336 | 37.1875 | 37.0182 | 33.048 | 29.0483 | 96.3982 | 39.0688 | 34.7412 | 36.3598 | 35.3085 | 33.4335 | 33.9522 | 34.0089 | 33.6407 | 33.9458 | 36.8777 | 37.1092 | 33.9874 | 33.7115 | 37.0906 | 36.0901 | 38.0248 | 37.0451 | 35.3405 | 37.4203 | 39.513 | 38.0796 | 36.7578 | 35.2699 | 34.2347 | 36.0027 | 33.3651 | 33.6862 | 33.7674 | 35.0183 | 33.3879 | 33.8196 | 35.338 | 33.1725 | 33.5297 | 35.5126 | 92.5446 | 92.6799 | 92.5851
2022-09-07 22:38 | 0:48 | 32.5981 | 30.6075 | 33.1231 | 42.5307 | 34.1883 | 34.6261 | 34.3369 | 34.4119 | 35.7523 | 35.4317 | 34.7028 | 34.8655 | 34.9757 | 36.6404 | 35.8536 | 34.6211 | 38.4207 | 36.5385 | 37.1816 | 37.0468 | 33.0788 | 28.9917 | 96.3877 | 39.059 | 34.7425 | 36.3545 | 35.3223 | 33.4501 | 33.9521 | 34.0142 | 33.6486 | 33.9694 | 36.8996 | 37.1083 | 33.99 | 33.6985 | 37.0837 | 36.108 | 38.051 | 37.0625 | 35.3464 | 37.3941 | 39.4839 | 38.0505 | 36.7441 | 35.2457 | 34.2442 | 36.0136 | 33.3594 | 33.6999 | 33.7661 | 35.0336 | 33.3683 | 33.8131 | 35.3645 | 33.1915 | 33.5442 | 35.5027 | 92.6413 | 92.769 | 92.6609
2022-09-07 22:38 | 0:48 | 32.5165 | 30.5363 | 33.0506 | 42.539 | 34.2051 | 34.6312 | 34.3749 | 34.4436 | 35.7653 | 35.4419 | 34.7127 | 34.8668 | 34.9738 | 36.6427 | 35.8492 | 34.6385 | 38.4126 | 36.5305 | 37.1804 | 37.0363 | 33.1121 | 28.9072 | 96.3802 | 39.008 | 34.7308 | 36.3458 | 35.3195 | 33.4596 | 33.9611 | 34.0181 | 33.6505 | 33.9661 | 36.8858 | 37.1262 | 34.0191 | 33.7487 | 37.1092 | 36.1264 | 38.0336 | 37.0761 | 35.3675 | 37.3969 | 39.4384 | 38.0414 | 36.7505 | 35.2561 | 34.2492 | 36.013 | 33.3473 | 33.6852 | 33.7745 | 35.0238 | 33.3805 | 33.8319 | 35.3728 | 33.2097 | 33.5535 | 35.5175 | 92.738 | 92.8755 | 92.7608
2022-09-07 22:38 | 0:48 | 32.3534 | 30.4591 | 32.9371 | 42.4695 | 34.1804 | 34.6587 | 34.3766 | 34.4513 | 35.7892 | 35.4335 | 34.7278 | 34.879 | 35.0113 | 36.6325 | 35.8646 | 34.6596 | 38.4437 | 36.5284 | 37.1796 | 37.0602 | 33.1222 | 28.9233 | 96.3615 | 39.0414 | 34.7446 | 36.3912 | 35.3446 | 33.4787 | 33.9904 | 34.0245 | 33.6526 | 33.9789 | 36.9269 | 37.1228 | 34.0162 | 33.736 | 37.1083 | 36.1252 | 38.0528 | 37.0906 | 35.3597 | 37.4038 | 39.4225 | 38.0366 | 36.7151 | 35.2616 | 34.2607 | 36.0132 | 33.3468 | 33.7092 | 33.7803 | 35.0034 | 33.3519 | 33.8391 | 35.3789 | 33.2003 | 33.5755 | 35.5387 | 92.8752 | 92.9571 | 92.7654
2022-09-07 22:39 | 0:49 | 32.2241 | 30.43 | 32.8076 | 42.2329 | 34.1913 | 34.6875 | 34.386 | 34.465 | 35.7935 | 35.4091 | 34.7231 | 34.8775 | 35.0032 | 36.6315 | 35.896 | 34.6938 | 38.4313 | 36.509 | 37.1765 | 37.0739 | 33.0874 | 28.9001 | 96.304 | 38.9244 | 34.7498 | 36.3923 | 35.3405 | 33.4693 | 33.9874 | 34.0471 | 33.6778 | 34.0004 | 36.9156 | 37.1506 | 34.0286 | 33.7649 | 37.1262 | 36.1397 | 38.0666 | 37.0837 | 35.377 | 37.3689 | 39.4158 | 38.0244 | 36.7116 | 35.2391 | 34.2501 | 36.0118 | 33.3434 | 33.7433 | 33.7808 | 34.9921 | 33.3539 | 33.833 | 35.4222 | 33.2147 | 33.5817 | 35.539 | 92.9825 | 93.14 | 92.8898
2022-09-07 22:39 | 0:49 | 32.0318 | 30.3724 | 32.6409 | 42.4355 | 34.1774 | 34.7037 | 34.4087 | 34.4702 | 35.8347 | 35.4391 | 34.7473 | 34.8816 | 35.0366 | 36.6132 | 35.9175 | 34.6964 | 38.4372 | 36.5257 | 37.1679 | 37.0755 | 33.0144 | 28.7994 | 96.2786 | 38.943 | 34.7571 | 36.4062 | 35.3464 | 33.4853 | 33.99 | 34.0635 | 33.6843 | 34.0155 | 36.9482 | 37.1474 | 34.0189 | 33.7692 | 37.1228 | 36.1443 | 38.0729 | 37.1092 | 35.3748 | 37.3741 | 39.3645 | 38.0243 | 36.7135 | 35.2594 | 34.247 | 35.9973 | 33.3588 | 33.7093 | 33.7856 | 35.0095 | 33.3753 | 33.8693 | 35.4434 | 33.2297 | 33.5982 | 35.5487 | 93.143 | 93.2505 | 93.0046
2022-09-07 22:39 | 0:49 | 31.887 | 30.2846 | 32.437 | 42.2933 | 34.1743 | 34.733 | 34.4265 | 34.5232 | 35.8469 | 35.4325 | 34.7505 | 34.8742 | 35.0562 | 36.632 | 35.9197 | 34.7118 | 38.4537 | 36.5242 | 37.1588 | 37.0992 | 32.9414 | 28.7375 | 96.2738 | 38.8884 | 34.7944 | 36.4255 | 35.3675 | 33.4965 | 34.0191 | 34.0662 | 33.7003 | 34.0108 | 36.96 | 37.1536 | 34.0555 | 33.7877 | 37.1506 | 36.1715 | 38.0844 | 37.1083 | 35.3901 | 37.3616 | 39.3598 | 37.9961 | 36.7093 | 35.264 | 34.2614 | 36.0056 | 33.3667 | 33.7349 | 33.7835 | 35.018 | 33.383 | 33.8639 | 35.4585 | 33.2463 | 33.5985 | 35.5393 | 93.2705 | 93.3796 | 93.1111
2022-09-07 22:39 | 0:49 | 31.6682 | 30.1795 | 32.2875 | 42.1115 | 34.1864 | 34.7461 | 34.4393 | 34.5486 | 35.8744 | 35.428 | 34.7623 | 34.9063 | 35.0397 | 36.6238 | 35.9481 | 34.7435 | 38.4408 | 36.5286 | 37.1454 | 37.1418 | 32.8682 | 28.7779 | 96.1222 | 39.0858 | 34.7878 | 36.4327 | 35.3597 | 33.4997 | 34.0162 | 34.0752 | 33.7126 | 34.039 | 36.9661 | 37.168 | 34.0581 | 33.8069 | 37.1474 | 36.1904 | 38.0696 | 37.1262 | 35.4029 | 37.3481 | 39.3264 | 37.9957 | 36.7021 | 35.2602 | 34.2476 | 35.9858 | 33.346 | 33.7451 | 33.8026 | 34.9826 | 33.3709 | 33.8929 | 35.4656 | 33.2694 | 33.5896 | 35.5484 | 93.4095 | 93.5014 | 93.1699
2022-09-07 22:39 | 0:49 | 31.5392 | 30.1447 | 32.1648 | 42.0096 | 34.2002 | 34.7828 | 34.4589 | 34.5596 | 35.8854 | 35.446 | 34.7752 | 34.9218 | 35.0682 | 36.6199 | 35.9751 | 34.7658 | 38.4583 | 36.5106 | 37.1512 | 37.1275 | 32.7785 | 28.7627 | 95.8226 | 38.8525 | 34.802 | 36.4586 | 35.377 | 33.5121 | 34.0286 | 34.0923 | 33.7244 | 34.076 | 36.9651 | 37.1843 | 34.0669 | 33.8274 | 37.1536 | 36.169 | 38.1012 | 37.1228 | 35.4016 | 37.3378 | 39.3042 | 37.9675 | 36.6809 | 35.2444 | 34.2584 | 36.0098 | 33.3604 | 33.7495 | 33.8025 | 35.0147 | 33.4057 | 33.89 | 35.4639 | 33.2815 | 33.6327 | 35.5737 | 93.6037 | 93.7158 | 93.3098
2022-09-07 22:39 | 0:49 | 31.4133 | 30.0703 | 32.0924 | 41.9211 | 34.1699 | 34.81 | 34.4638 | 34.5644 | 35.8995 | 35.4196 | 34.7906 | 34.9206 | 35.0693 | 36.6151 | 35.972 | 34.7869 | 38.4499 | 36.5094 | 37.1664 | 37.1464 | 32.7485 | 28.7166 | 95.7251 | 38.6328 | 34.7886 | 36.457 | 35.3748 | 33.5311 | 34.0189 | 34.0754 | 33.7249 | 34.0549 | 37.0085 | 37.1873 | 34.0631 | 33.819 | 37.168 | 36.2105 | 38.1055 | 37.1506 | 35.4119 | 37.3309 | 39.2685 | 37.9688 | 36.6939 | 35.2458 | 34.2381 | 35.9913 | 33.3803 | 33.7525 | 33.7941 | 35.0036 | 33.4103 | 33.9195 | 35.5013 | 33.2861 | 33.6229 | 35.5694 | 93.7725 | 93.8693 | 93.4075
2022-09-07 22:40 | 0:50 | 31.2708 | 29.9592 | 31.9303 | 41.894 | 34.2031 | 34.8399 | 34.4721 | 34.5733 | 35.9221 | 35.4354 | 34.7881 | 34.9452 | 35.0884 | 36.6128 | 35.9922 | 34.815 | 38.4649 | 36.5072 | 37.1544 | 37.1583 | 32.656 | 28.5686 | 95.6364 | 38.8541 | 34.8096 | 36.4587 | 35.3901 | 33.537 | 34.0555 | 34.0935 | 33.7372 | 34.0917 | 37.0041 | 37.2139 | 34.0837 | 33.836 | 37.1843 | 36.202 | 38.1038 | 37.1474 | 35.4131 | 37.3147 | 39.2343 | 37.9551 | 36.6784 | 35.2474 | 34.2567 | 35.9793 | 33.3622 | 33.7797 | 33.8043 | 35.0137 | 33.4192 | 33.9019 | 35.5268 | 33.3101 | 33.6319 | 35.5827 | 93.951 | 93.9965 | 93.4546
2022-09-07 22:40 | 0:50 | 31.2417 | 29.9016 | 31.8032 | 41.613 | 34.1909 | 34.8478 | 34.4964 | 34.606 | 35.9447 | 35.4189 | 34.7986 | 34.961 | 35.1096 | 36.6107 | 36.0065 | 34.8345 | 38.4634 | 36.5127 | 37.1522 | 37.1816 | 32.6062 | 28.541 | 95.5554 | 38.6594 | 34.8343 | 36.4817 | 35.4029 | 33.5508 | 34.0581 | 34.1306 | 33.7327 | 34.0872 | 37.04 | 37.203 | 34.1013 | 33.8736 | 37.1873 | 36.2063 | 38.1279 | 37.1536 | 35.435 | 37.2899 | 39.2156 | 37.9537 | 36.6669 | 35.2334 | 34.2436 | 35.9924 | 33.3725 | 33.7994 | 33.7976 | 35.0097 | 33.4046 | 33.9007 | 35.5493 | 33.3315 | 33.662 | 35.5943 | 94.1166 | 94.2085 | 93.5282
2022-09-07 22:40 | 0:50 | 31.1916 | 29.8649 | 31.7396 | 41.8761 | 34.1977 | 34.871 | 34.5171 | 34.6185 | 35.9798 | 35.4357 | 34.8021 | 34.9629 | 35.1251 | 36.6001 | 36.0222 | 34.8359 | 38.4677 | 36.5236 | 37.1512 | 37.1884 | 32.5452 | 28.4383 | 95.4765 | 38.6465 | 34.8218 | 36.4882 | 35.4016 | 33.5751 | 34.0669 | 34.1311 | 33.7634 | 34.1101 | 37.0341 | 37.1977 | 34.1174 | 33.87 | 37.2139 | 36.2366 | 38.1282 | 37.168 | 35.4297 | 37.286 | 39.2141 | 37.9388 | 36.6465 | 35.2294 | 34.2836 | 35.9817 | 33.3777 | 33.7738 | 33.8305 | 34.9892 | 33.4106 | 33.9339 | 35.568 | 33.3321 | 33.6597 | 35.5981 | 94.239 | 94.328 | 93.6004
2022-09-07 22:40 | 0:50 | 30.5292 | 29.7544 | 31.5184 | 41.8312 | 34.1843 | 34.9154 | 34.5144 | 34.638 | 35.9841 | 35.4289 | 34.8061 | 34.9852 | 35.1209 | 36.6135 | 36.0516 | 34.8731 | 38.4761 | 36.5085 | 37.1592 | 37.2096 | 32.4896 | 28.3835 | 95.4353 | 38.6534 | 34.8377 | 36.5077 | 35.4119 | 33.5676 | 34.0631 | 34.1536 | 33.7745 | 34.1206 | 37.0398 | 37.1974 | 34.117 | 33.8818 | 37.203 | 36.2385 | 38.1276 | 37.1843 | 35.4559 | 37.2948 | 39.1695 | 37.9663 | 36.6305 | 35.2306 | 34.2485 | 35.9693 | 33.3863 | 33.7839 | 33.8234 | 35.0013 | 33.4008 | 33.9618 | 35.5867 | 33.3399 | 33.6782 | 35.6033 | 94.4445 | 94.467 | 93.7264
2022-09-07 22:40 | 0:50 | 29.0192 | 29.603 | 31.2629 | 41.5468 | 34.1914 | 34.9228 | 34.5452 | 34.6485 | 36.023 | 35.4383 | 34.8202 | 35.0079 | 35.1297 | 36.6097 | 36.0734 | 34.9053 | 38.4951 | 36.5181 | 37.1592 | 37.2084 | 32.4388 | 28.3307 | 95.3654 | 38.4696 | 34.8465 | 36.5117 | 35.4131 | 33.572 | 34.0837 | 34.1366 | 33.7786 | 34.1277 | 37.0543 | 37.2215 | 34.1282 | 33.9005 | 37.1977 | 36.2557 | 38.1392 | 37.1873 | 35.457 | 37.2522 | 39.1415 | 37.9458 | 36.6375 | 35.2376 | 34.2755 | 36.0099 | 33.3878 | 33.813 | 33.8531 | 34.9892 | 33.411 | 33.9672 | 35.5765 | 33.3445 | 33.691 | 35.6292 | 94.4308 | 94.59 | 93.6774
2022-09-07 22:40 | 0:50 | 28.6748 | 29.3972 | 31.045 | 41.6505 | 34.1724 | 34.9496 | 34.5724 | 34.6803 | 36.0391 | 35.4595 | 34.8445 | 34.9973 | 35.1461 | 36.5971 | 36.0695 | 34.9068 | 38.5032 | 36.5213 | 37.1522 | 37.2416 | 32.3734 | 28.1699 | 95.2596 | 38.3741 | 34.8642 | 36.531 | 35.435 | 33.5912 | 34.1013 | 34.1751 | 33.8084 | 34.1499 | 37.0816 | 37.2246 | 34.1225 | 33.9166 | 37.1974 | 36.2424 | 38.1742 | 37.2139 | 35.4565 | 37.2593 | 39.1339 | 37.9309 | 36.6142 | 35.2345 | 34.2769 | 35.9871 | 33.3805 | 33.8266 | 33.831 | 34.9988 | 33.4322 | 33.9895 | 35.6124 | 33.3719 | 33.694 | 35.6421 | 94.5468 | 94.7109 | 93.8912
2022-09-07 22:41 | 0:50 | 28.5711 | 29.2439 | 30.844 | 41.5813 | 34.1909 | 34.9656 | 34.5784 | 34.7009 | 36.0336 | 35.4402 | 34.8352 | 35.012 | 35.1597 | 36.6054 | 36.0915 | 34.9305 | 38.4872 | 36.5103 | 37.1512 | 37.25 | 32.3329 | 28.1644 | 95.2074 | 38.6503 | 34.8768 | 36.5372 | 35.4297 | 33.5977 | 34.1174 | 34.1633 | 33.7988 | 34.1535 | 37.094 | 37.2358 | 34.1506 | 33.9186 | 37.2215 | 36.2874 | 38.165 | 37.203 | 35.4725 | 37.2574 | 39.113 | 37.9236 | 36.6029 | 35.2358 | 34.2546 | 35.986 | 33.3873 | 33.8149 | 33.8455 | 34.9986 | 33.435 | 33.9837 | 35.6363 | 33.3918 | 33.7017 | 35.6507 | 94.7557 | 94.7824 | 93.9948
2022-09-07 22:41 | 0:51 | 28.638 | 29.0683 | 30.7466 | 41.4117 | 34.1904 | 34.974 | 34.5743 | 34.7299 | 36.0849 | 35.4519 | 34.8407 | 35.0361 | 35.178 | 36.5996 | 36.103 | 34.9605 | 38.4786 | 36.5335 | 37.1559 | 37.2679 | 32.2625 | 28.0345 | 95.1182 | 38.4832 | 34.8744 | 36.5495 | 35.4559 | 33.6217 | 34.117 | 34.1845 | 33.8084 | 34.1737 | 37.0949 | 37.2571 | 34.1612 | 33.9328 | 37.2246 | 36.3003 | 38.1582 | 37.1977 | 35.4783 | 37.2272 | 39.0929 | 37.9162 | 36.6114 | 35.2629 | 34.2713 | 35.9767 | 33.3929 | 33.8133 | 33.8248 | 35.0051 | 33.4352 | 33.9957 | 35.6333 | 33.4093 | 33.7308 | 35.6564 | 94.7825 | 94.9088 | 94.0287
2022-09-07 22:41 | 0:51 | 28.615 | 28.963 | 30.6091 | 41.4097 | 34.1856 | 35.0258 | 34.6039 | 34.7324 | 36.0979 | 35.4576 | 34.8669 | 35.0553 | 35.172 | 36.5967 | 36.1171 | 34.9914 | 38.5027 | 36.5358 | 37.1541 | 37.2747 | 32.2102 | 28.0081 | 95.0788 | 38.4579 | 34.8918 | 36.5536 | 35.457 | 33.6333 | 34.1282 | 34.1948 | 33.8377 | 34.186 | 37.1229 | 37.2507 | 34.1671 | 33.9576 | 37.2358 | 36.2907 | 38.1771 | 37.1974 | 35.4743 | 37.2084 | 39.0746 | 37.904 | 36.6069 | 35.2445 | 34.2808 | 35.9672 | 33.4077 | 33.8296 | 33.8488 | 35.0085 | 33.4628 | 33.9966 | 35.6406 | 33.4077 | 33.7454 | 35.658 | 94.8621 | 94.9514 | 94.1204
2022-09-07 22:41 | 0:51 | 28.2361 | 28.8484 | 30.4871 | 41.2895 | 34.1813 | 35.0432 | 34.628 | 34.7559 | 36.1123 | 35.4841 | 34.8537 | 35.0707 | 35.197 | 36.5924 | 36.1516 | 34.9685 | 38.5154 | 36.5515 | 37.1467 | 37.2922 | 32.1554 | 27.882 | 94.9439 | 38.4461 | 34.8884 | 36.5528 | 35.4565 | 33.633 | 34.1225 | 34.2011 | 33.8358 | 34.1795 | 37.136 | 37.2577 | 34.1904 | 33.9795 | 37.2571 | 36.3085 | 38.1914 | 37.2215 | 35.4763 | 37.2178 | 39.0531 | 37.8976 | 36.5891 | 35.2453 | 34.2697 | 35.9797 | 33.4006 | 33.8481 | 33.8434 | 35.0179 | 33.4436 | 34.0236 | 35.6574 | 33.4091 | 33.7635 | 35.6846 | 94.7669 | 94.929 | 94.0185
2022-09-07 22:41 | 0:51 | 28.5909 | 28.6879 | 30.3563 | 41.1365 | 34.1934 | 35.0763 | 34.6255 | 34.7783 | 36.1349 | 35.4865 | 34.8864 | 35.0694 | 35.2008 | 36.5979 | 36.1464 | 34.9973 | 38.5122 | 36.5305 | 37.1596 | 37.312 | 32.0834 | 27.7702 | 94.8105 | 38.4208 | 34.9028 | 36.5686 | 35.4725 | 33.6444 | 34.1506 | 34.2187 | 33.8494 | 34.2201 | 37.1638 | 37.2535 | 34.1861 | 33.9694 | 37.2507 | 36.3295 | 38.2019 | 37.2246 | 35.4874 | 37.2163 | 39.034 | 37.9073 | 36.5907 | 35.2255 | 34.2702 | 35.9749 | 33.4172 | 33.8657 | 33.8513 | 35.0023 | 33.4692 | 34.0582 | 35.6892 | 33.4249 | 33.7642 | 35.6786 | 94.5876 | 94.739 | 93.8214
2022-09-07 22:41 | 0:51 | 28.7567 | 28.6006 | 30.2873 | 41.2227 | 34.2045 | 35.0912 | 34.6594 | 34.7903 | 36.1579 | 35.4852 | 34.9029 | 35.0773 | 35.2222 | 36.5857 | 36.1785 | 35.0426 | 38.5252 | 36.5287 | 37.1759 | 37.3266 | 32.0467 | 27.8317 | 94.6674 | 38.5204 | 34.8979 | 36.5663 | 35.4783 | 33.6461 | 34.1612 | 34.2216 | 33.8533 | 34.213 | 37.1422 | 37.2513 | 34.2101 | 34.0076 | 37.2577 | 36.3461 | 38.2005 | 37.2358 | 35.4794 | 37.206 | 39.0105 | 37.9012 | 36.5778 | 35.2387 | 34.2941 | 35.9854 | 33.4492 | 33.8523 | 33.8397 | 35.0085 | 33.4682 | 34.0286 | 35.7152 | 33.4267 | 33.762 | 35.6857 | 94.3099 | 94.4795 | 93.6076
2022-09-07 22:42 | 0:52 | 28.059 | 28.4661 | 30.156 | 41.0615 | 34.1932 | 35.1212 | 34.6604 | 34.8088 | 36.1683 | 35.4913 | 34.9288 | 35.1215 | 35.2223 | 36.5913 | 36.1829 | 35.0367 | 38.5287 | 36.5361 | 37.1651 | 37.3448 | 32.0235 | 27.7113 | 94.4446 | 38.4091 | 34.9214 | 36.5609 | 35.4743 | 33.6635 | 34.1671 | 34.2301 | 33.8665 | 34.2176 | 37.1759 | 37.2655 | 34.2088 | 34.016 | 37.2535 | 36.3523 | 38.1941 | 37.2571 | 35.4873 | 37.2045 | 38.9997 | 37.8984 | 36.5559 | 35.2259 | 34.2716 | 35.9709 | 33.4274 | 33.8762 | 33.8629 | 34.9988 | 33.4688 | 34.046 | 35.7172 | 33.4629 | 33.7844 | 35.6961 | 94.1429 | 94.2476 | 93.6045
2022-09-07 22:42 | 0:52 | 28.3681 | 28.357 | 30.0754 | 40.8919 | 34.1944 | 35.1191 | 34.6775 | 34.83 | 36.1838 | 35.5028 | 34.9329 | 35.107 | 35.2328 | 36.5823 | 36.209 | 35.0685 | 38.521 | 36.5513 | 37.1695 | 37.3515 | 31.9834 | 27.5774 | 94.2232 | 38.1799 | 34.9136 | 36.5973 | 35.4763 | 33.6942 | 34.1904 | 34.2419 | 33.8792 | 34.2403 | 37.2028 | 37.267 | 34.2205 | 34.0127 | 37.2513 | 36.374 | 38.2221 | 37.2507 | 35.5122 | 37.169 | 38.953 | 37.8814 | 36.5379 | 35.2416 | 34.2783 | 35.9776 | 33.4247 | 33.8637 | 33.8828 | 35.0154 | 33.4417 | 34.0579 | 35.7217 | 33.4614 | 33.8086 | 35.7094 | 93.936 | 94.0959 | 93.4976
2022-09-07 22:42 | 0:52 | 27.9899 | 28.2317 | 29.9277 | 40.8114 | 34.203 | 35.1613 | 34.6891 | 34.8486 | 36.2193 | 35.5215 | 34.9226 | 35.1377 | 35.2448 | 36.5876 | 36.2043 | 35.085 | 38.5267 | 36.5459 | 37.1626 | 37.3458 | 31.9465 | 27.4438 | 94.0139 | 38.4138 | 34.9257 | 36.6121 | 35.4874 | 33.6782 | 34.1861 | 34.2705 | 33.8881 | 34.2449 | 37.2 | 37.2696 | 34.2262 | 34.0293 | 37.2655 | 36.3763 | 38.2263 | 37.2577 | 35.4884 | 37.1742 | 38.9535 | 37.8824 | 36.5183 | 35.215 | 34.2977 | 35.9639 | 33.4334 | 33.871 | 33.8613 | 35.0044 | 33.5015 | 34.0796 | 35.7405 | 33.4786 | 33.8103 | 35.7289 | 93.7993 | 94.005 | 93.4106
2022-09-07 22:42 | 0:52 | 27.8662 | 28.1378 | 29.8243 | 40.7815 | 34.2051 | 35.168 | 34.6988 | 34.8657 | 36.2212 | 35.5252 | 34.9412 | 35.1443 | 35.2485 | 36.5842 | 36.2264 | 35.087 | 38.5363 | 36.5518 | 37.1599 | 37.3664 | 31.9325 | 27.3709 | 93.8732 | 38.14 | 34.9471 | 36.6072 | 35.4794 | 33.7016 | 34.2101 | 34.2948 | 33.9036 | 34.2601 | 37.1792 | 37.2653 | 34.2592 | 34.0462 | 37.267 | 36.4047 | 38.243 | 37.2535 | 35.5005 | 37.1554 | 38.9399 | 37.8515 | 36.5072 | 35.2041 | 34.2801 | 35.9683 | 33.4498 | 33.8672 | 33.8656 | 35.0014 | 33.4798 | 34.0893 | 35.754 | 33.4815 | 33.8296 | 35.7166 | 93.7248 | 93.8936 | 93.3786
2022-09-07 22:42 | 0:52 | 27.4401 | 28.0333 | 29.6863 | 40.7567 | 34.203 | 35.184 | 34.706 | 34.8744 | 36.2394 | 35.5149 | 34.9563 | 35.1533 | 35.2728 | 36.575 | 36.2361 | 35.1039 | 38.5442 | 36.559 | 37.1797 | 37.3917 | 31.925 | 27.3834 | 93.7465 | 38.143 | 34.9604 | 36.6157 | 35.4873 | 33.6928 | 34.2088 | 34.2754 | 33.8988 | 34.2707 | 37.2237 | 37.2772 | 34.2463 | 34.0521 | 37.2696 | 36.4178 | 38.2561 | 37.2513 | 35.5096 | 37.154 | 38.9268 | 37.8584 | 36.4991 | 35.2456 | 34.2816 | 35.9549 | 33.4216 | 33.8886 | 33.8575 | 35.0305 | 33.4958 | 34.12 | 35.7752 | 33.5045 | 33.8193 | 35.7469 | 93.5791 | 93.8788 | 93.3303
2022-09-07 22:42 | 0:52 | 27.3002 | 27.8545 | 29.5554 | 40.7518 | 34.1897 | 35.2089 | 34.745 | 34.8909 | 36.2568 | 35.5325 | 34.9543 | 35.1707 | 35.2716 | 36.5789 | 36.2461 | 35.1292 | 38.5394 | 36.5549 | 37.1722 | 37.4081 | 31.8921 | 27.2929 | 93.5141 | 38.0267 | 34.958 | 36.6259 | 35.5122 | 33.7197 | 34.2205 | 34.3111 | 33.9201 | 34.2975 | 37.2229 | 37.2644 | 34.2544 | 34.0769 | 37.2653 | 36.4236 | 38.2529 | 37.2655 | 35.5383 | 37.14 | 38.9032 | 37.8699 | 36.4992 | 35.2128 | 34.3056 | 35.9576 | 33.4578 | 33.8856 | 33.8864 | 34.998 | 33.5172 | 34.1142 | 35.7833 | 33.5175 | 33.8545 | 35.7547 | 93.5347 | 93.8163 | 93.4071
2022-09-07 22:43 | 0:52 | 27.1642 | 27.7523 | 29.4328 | 40.7309 | 34.1962 | 35.2269 | 34.7514 | 34.9171 | 36.2727 | 35.5548 | 34.9638 | 35.1851 | 35.2849 | 36.5725 | 36.2569 | 35.1378 | 38.5472 | 36.5582 | 37.1895 | 37.4224 | 31.8391 | 27.2098 | 93.4158 | 38.1712 | 34.9815 | 36.621 | 35.4884 | 33.6992 | 34.2262 | 34.3094 | 33.9237 | 34.2871 | 37.2359 | 37.2748 | 34.2714 | 34.0485 | 37.2772 | 36.4345 | 38.2612 | 37.267 | 35.5273 | 37.1225 | 38.8784 | 37.8643 | 36.4974 | 35.2213 | 34.2752 | 35.9431 | 33.4704 | 33.9124 | 33.9007 | 34.9871 | 33.5028 | 34.1064 | 35.7942 | 33.5322 | 33.8495 | 35.777 | 93.5102 | 93.6816 | 93.2919
2022-09-07 22:43 | 0:53 | 27.5918 | 27.6057 | 29.3868 | 40.507 | 34.2067 | 35.2555 | 34.7563 | 34.9402 | 36.2853 | 35.5499 | 34.9759 | 35.2103 | 35.2823 | 36.5533 | 36.2638 | 35.154 | 38.5403 | 36.5551 | 37.1909 | 37.4327 | 31.8006 | 27.1082 | 93.4484 | 38.1216 | 34.991 | 36.6122 | 35.5005 | 33.7162 | 34.2592 | 34.3363 | 33.9253 | 34.2978 | 37.2385 | 37.2711 | 34.2742 | 34.0928 | 37.2644 | 36.4402 | 38.2659 | 37.2696 | 35.5135 | 37.1127 | 38.854 | 37.8623 | 36.4689 | 35.1926 | 34.2844 | 35.9529 | 33.4666 | 33.9074 | 33.8744 | 35.0255 | 33.517 | 34.1359 | 35.7877 | 33.5461 | 33.8573 | 35.7793 | 93.4572 | 93.6106 | 93.2799
2022-09-07 22:43 | 0:53 | 26.9879 | 27.5828 | 29.2765 | 40.5818 | 34.2221 | 35.2829 | 34.7722 | 34.9356 | 36.298 | 35.5513 | 34.9703 | 35.2079 | 35.2951 | 36.5576 | 36.2768 | 35.1614 | 38.5373 | 36.5677 | 37.1881 | 37.4528 | 31.7119 | 27.0929 | 93.509 | 38.0641 | 35.0173 | 36.6309 | 35.5096 | 33.7217 | 34.2463 | 34.3437 | 33.9398 | 34.3062 | 37.268 | 37.2795 | 34.2739 | 34.1151 | 37.2748 | 36.4633 | 38.2827 | 37.2653 | 35.5209 | 37.0971 | 38.8245 | 37.87 | 36.4749 | 35.2009 | 34.2897 | 35.969 | 33.4816 | 33.8943 | 33.8815 | 34.9896 | 33.5303 | 34.1497 | 35.8237 | 33.5541 | 33.874 | 35.7904 | 93.3529 | 93.5363 | 93.1997
2022-09-07 22:43 | 0:53 | 26.9254 | 27.3678 | 29.1447 | 40.5239 | 34.2083 | 35.2845 | 34.7802 | 34.963 | 36.3282 | 35.5621 | 34.9885 | 35.2277 | 35.2925 | 36.5497 | 36.3012 | 35.1839 | 38.5436 | 36.5569 | 37.1733 | 37.4819 | 31.657 | 27.0505 | 93.6392 | 37.9988 | 35.0023 | 36.6356 | 35.5383 | 33.7463 | 34.2544 | 34.3484 | 33.9427 | 34.3013 | 37.2785 | 37.2673 | 34.2889 | 34.1094 | 37.2711 | 36.4592 | 38.2727 | 37.2772 | 35.5188 | 37.1041 | 38.8191 | 37.8367 | 36.46 | 35.1987 | 34.3033 | 35.9665 | 33.4913 | 33.9217 | 33.886 | 34.9873 | 33.5256 | 34.1707 | 35.8353 | 33.5726 | 33.8868 | 35.796 | 93.3054 | 93.5326 | 93.2047
2022-09-07 22:43 | 0:53 | 26.8437 | 27.3073 | 29.0877 | 40.2742 | 34.219 | 35.311 | 34.822 | 34.9751 | 36.341 | 35.5778 | 34.9892 | 35.2388 | 35.328 | 36.5448 | 36.304 | 35.195 | 38.551 | 36.5686 | 37.189 | 37.4573 | 31.6183 | 26.8995 | 93.6779 | 38.0474 | 34.9978 | 36.6488 | 35.5273 | 33.7389 | 34.2714 | 34.3544 | 33.9451 | 34.3202 | 37.2912 | 37.2891 | 34.2905 | 34.1095 | 37.2795 | 36.4593 | 38.2753 | 37.2644 | 35.5305 | 37.0759 | 38.8072 | 37.8234 | 36.439 | 35.1999 | 34.2842 | 35.945 | 33.5038 | 33.9166 | 33.8962 | 35.0056 | 33.5278 | 34.1774 | 35.8329 | 33.5895 | 33.9091 | 35.8051 | 93.1924 | 93.4263 | 93.0851
2022-09-07 22:43 | 0:53 | 27.1882 | 27.2315 | 28.9965 | 40.3437 | 34.2141 | 35.2995 | 34.8075 | 34.9955 | 36.3693 | 35.5781 | 35.0113 | 35.2424 | 35.3053 | 36.5364 | 36.314 | 35.2018 | 38.5433 | 36.5663 | 37.1803 | 37.4849 | 31.5554 | 26.9139 | 93.7034 | 37.798 | 34.9971 | 36.6385 | 35.5135 | 33.7538 | 34.2742 | 34.3826 | 33.9587 | 34.3402 | 37.2696 | 37.2847 | 34.3047 | 34.1398 | 37.2673 | 36.4767 | 38.2998 | 37.2748 | 35.5224 | 37.0641 | 38.7884 | 37.8124 | 36.4335 | 35.1814 | 34.3052 | 35.9384 | 33.4745 | 33.9185 | 33.8956 | 35.0022 | 33.534 | 34.1726 | 35.8493 | 33.5746 | 33.8989 | 35.809 | 93.1879 | 93.3371 | 93.0598
2022-09-07 22:44 | 0:54 | 26.8277 | 27.0714 | 28.9036 | 40.323 | 34.2265 | 35.3434 | 34.8355 | 35.0058 | 36.3802 | 35.6086 | 35.0207 | 35.2437 | 35.3211 | 36.524 | 36.3268 | 35.2229 | 38.5385 | 36.5791 | 37.201 | 37.4915 | 31.497 | 26.8684 | 93.7337 | 37.7936 | 35.0142 | 36.6397 | 35.5209 | 33.7543 | 34.2739 | 34.384 | 33.9681 | 34.3335 | 37.2855 | 37.2716 | 34.3065 | 34.131 | 37.2891 | 36.4926 | 38.2967 | 37.2711 | 35.5259 | 37.068 | 38.7555 | 37.8224 | 36.432 | 35.1932 | 34.2758 | 35.9487 | 33.5099 | 33.9227 | 33.9024 | 35.0345 | 33.5534 | 34.1934 | 35.8426 | 33.595 | 33.9194 | 35.8253 | 93.1383 | 93.3143 | 93.0552
2022-09-07 22:44 | 0:54 | 26.483 | 26.9992 | 28.7444 | 40.409 | 34.2127 | 35.3371 | 34.8296 | 35.0196 | 36.3965 | 35.5957 | 35.0371 | 35.2757 | 35.3253 | 36.524 | 36.3327 | 35.2186 | 38.531 | 36.5841 | 37.1896 | 37.5009 | 31.4361 | 26.8076 | 93.8002 | 37.8075 | 35.0309 | 36.6644 | 35.5188 | 33.7604 | 34.2889 | 34.3924 | 33.9817 | 34.3512 | 37.291 | 37.2819 | 34.3131 | 34.143 | 37.2847 | 36.5043 | 38.3115 | 37.2795 | 35.5643 | 37.0435 | 38.7424 | 37.8134 | 36.4121 | 35.1572 | 34.2687 | 35.9427 | 33.5179 | 33.903 | 33.8984 | 34.9972 | 33.5425 | 34.2059 | 35.856 | 33.614 | 33.9392 | 35.8136 | 93.1301 | 93.3212 | 93.0429
2022-09-07 22:44 | 0:54 | 27.0783 | 26.9831 | 28.7531 | 40.3355 | 34.2231 | 35.3401 | 34.8466 | 35.0418 | 36.4068 | 35.6136 | 35.0268 | 35.2792 | 35.3145 | 36.5218 | 36.3449 | 35.2434 | 38.5511 | 36.5856 | 37.2107 | 37.5388 | 31.3744 | 26.7342 | 93.8064 | 37.8245 | 35.0427 | 36.6497 | 35.5305 | 33.7677 | 34.2905 | 34.4289 | 33.9824 | 34.3578 | 37.3039 | 37.2725 | 34.311 | 34.1389 | 37.2716 | 36.5234 | 38.316 | 37.2673 | 35.5529 | 37.0299 | 38.7227 | 37.8036 | 36.3929 | 35.1757 | 34.2787 | 35.9498 | 33.5125 | 33.9212 | 33.8903 | 35.0305 | 33.5555 | 34.2141 | 35.8723 | 33.618 | 33.9384 | 35.8315 | 93.1075 | 93.2784 | 92.9788
2022-09-07 22:44 | 0:54 | 26.4463 | 26.9431 | 28.6186 | 40.223 | 34.2227 | 35.385 | 34.8609 | 35.054 | 36.4215 | 35.6267 | 35.039 | 35.3016 | 35.3279 | 36.5067 | 36.3485 | 35.2497 | 38.552 | 36.586 | 37.1988 | 37.5235 | 31.326 | 26.6801 | 93.896 | 37.899 | 35.0263 | 36.6459 | 35.5224 | 33.7739 | 34.3047 | 34.415 | 33.9762 | 34.3749 | 37.2989 | 37.2814 | 34.345 | 34.1592 | 37.2819 | 36.5159 | 38.3218 | 37.2891 | 35.5236 | 37.0098 | 38.678 | 37.7953 | 36.3846 | 35.1677 | 34.282 | 35.9355 | 33.5108 | 33.9128 | 33.9038 | 35.0073 | 33.5644 | 34.2131 | 35.8633 | 33.597 | 33.9471 | 35.8516 | 93.0534 | 93.2322 | 92.9113
2022-09-07 22:44 | 0:54 | 26.2991 | 26.7264 | 28.494 | 40.133 | 34.2456 | 35.3956 | 34.8645 | 35.0725 | 36.4451 | 35.6335 | 35.0425 | 35.2967 | 35.3529 | 36.5164 | 36.3733 | 35.2795 | 38.5457 | 36.5901 | 37.1708 | 37.56 | 31.2599 | 26.5895 | 94.0001 | 37.9217 | 35.0703 | 36.6648 | 35.5259 | 33.8039 | 34.3065 | 34.4497 | 33.9845 | 34.3722 | 37.3237 | 37.2557 | 34.3329 | 34.1534 | 37.2725 | 36.5277 | 38.3359 | 37.2847 | 35.5378 | 37.0224 | 38.6892 | 37.7936 | 36.3693 | 35.1589 | 34.2954 | 35.9431 | 33.511 | 33.9197 | 33.9012 | 35.0033 | 33.5542 | 34.2234 | 35.8959 | 33.6263 | 33.9735 | 35.8464 | 92.9878 | 93.1377 | 92.8478
2022-09-07 22:44 | 0:54 | 26.2553 | 26.6813 | 28.4306 | 40.0676 | 34.2319 | 35.4247 | 34.8743 | 35.078 | 36.4612 | 35.6679 | 35.0557 | 35.3262 | 35.3384 | 36.5239 | 36.3875 | 35.288 | 38.5388 | 36.6052 | 37.1986 | 37.5657 | 31.1836 | 26.5651 | 94.1225 | 37.8259 | 35.0632 | 36.6581 | 35.5643 | 33.7989 | 34.3131 | 34.4632 | 34.0023 | 34.3882 | 37.3351 | 37.2791 | 34.3563 | 34.1678 | 37.2814 | 36.5365 | 38.3453 | 37.2716 | 35.5399 | 37.0085 | 38.68 | 37.7703 | 36.3579 | 35.1531 | 34.2804 | 35.946 | 33.529 | 33.9465 | 33.9083 | 35.0038 | 33.5541 | 34.2535 | 35.8969 | 33.6452 | 33.9533 | 35.8477 | 92.8959 | 93.0513 | 92.8062
2022-09-07 22:45 | 0:54 | 26.0629 | 26.5323 | 28.2898 | 40.1484 | 34.2317 | 35.4269 | 34.8854 | 35.092 | 36.4633 | 35.6772 | 35.0503 | 35.3158 | 35.344 | 36.5111 | 36.3863 | 35.3088 | 38.5346 | 36.585 | 37.2136 | 37.5665 | 31.1101 | 26.4406 | 94.1611 | 37.6713 | 35.0751 | 36.6734 | 35.5529 | 33.8082 | 34.311 | 34.4635 | 34.0172 | 34.3695 | 37.3555 | 37.2801 | 34.362 | 34.1759 | 37.2557 | 36.5496 | 38.3365 | 37.2819 | 35.5447 | 36.9798 | 38.6429 | 37.7798 | 36.3629 | 35.1572 | 34.2871 | 35.9287 | 33.5277 | 33.9447 | 33.8983 | 35.0019 | 33.5715 | 34.2498 | 35.9134 | 33.66 | 33.9735 | 35.867 | 92.8253 | 93.008 | 92.6702
2022-09-07 22:45 | 0:55 | 26.0281 | 26.5365 | 28.2189 | 40.1503 | 34.2436 | 35.4522 | 34.887 | 35.115 | 36.4691 | 35.6739 | 35.0459 | 35.3311 | 35.3489 | 36.4873 | 36.3977 | 35.3053 | 38.5388 | 36.596 | 37.2154 | 37.5816 | 31.0591 | 26.5481 | 94.2062 | 37.6288 | 35.0663 | 36.6594 | 35.5236 | 33.8161 | 34.345 | 34.475 | 34.0114 | 34.4003 | 37.3467 | 37.2706 | 34.3652 | 34.1791 | 37.2791 | 36.5447 | 38.3461 | 37.2725 | 35.5457 | 36.978 | 38.6334 | 37.7856 | 36.3323 | 35.1545 | 34.2888 | 35.9455 | 33.5526 | 33.9408 | 33.8894 | 34.9878 | 33.5818 | 34.2568 | 35.911 | 33.6518 | 33.9896 | 35.8648 | 92.7196 | 92.8913 | 92.6
2022-09-07 22:45 | 0:55 | 25.9883 | 26.3171 | 28.1195 | 39.8587 | 34.2428 | 35.4478 | 34.9132 | 35.1053 | 36.4785 | 35.6872 | 35.0768 | 35.3603 | 35.3478 | 36.4921 | 36.4158 | 35.3311 | 38.5414 | 36.5954 | 37.2133 | 37.598 | 31.0112 | 26.4609 | 94.3499 | 37.7358 | 35.0808 | 36.6741 | 35.5378 | 33.8145 | 34.3329 | 34.4924 | 34.0246 | 34.4196 | 37.3603 | 37.2858 | 34.3739 | 34.1954 | 37.2801 | 36.5475 | 38.3612 | 37.2814 | 35.5297 | 36.9697 | 38.6089 | 37.7628 | 36.3402 | 35.1606 | 34.2698 | 35.936 | 33.5361 | 33.9502 | 33.9251 | 34.984 | 33.5853 | 34.2638 | 35.9356 | 33.6649 | 34.005 | 35.8686 | 92.5455 | 92.7679 | 92.5698
2022-09-07 22:45 | 0:55 | 26.05 | 26.3395 | 28.0949 | 39.8238 | 34.2563 | 35.4695 | 34.9315 | 35.1194 | 36.4858 | 35.697 | 35.071 | 35.3574 | 35.3612 | 36.486 | 36.4331 | 35.3412 | 38.5381 | 36.608 | 37.2158 | 37.6033 | 30.9476 | 26.3966 | 94.4137 | 37.6328 | 35.0789 | 36.6819 | 35.5399 | 33.8295 | 34.3563 | 34.4971 | 34.029 | 34.3985 | 37.3724 | 37.2759 | 34.3915 | 34.1964 | 37.2706 | 36.5711 | 38.3758 | 37.2557 | 35.538 | 36.9496 | 38.5997 | 37.7551 | 36.321 | 35.1503 | 34.2699 | 35.9407 | 33.5275 | 33.9453 | 33.9148 | 34.9961 | 33.5737 | 34.2828 | 35.9579 | 33.6751 | 34.0054 | 35.8792 | 92.5041 | 92.6946 | 92.5387
2022-09-07 22:45 | 0:55 | 25.8397 | 26.3578 | 28.0012 | 39.9854 | 34.2738 | 35.4946 | 34.9457 | 35.1395 | 36.5207 | 35.7102 | 35.0884 | 35.379 | 35.3811 | 36.4752 | 36.4229 | 35.3425 | 38.5381 | 36.6123 | 37.217 | 37.6125 | 30.9172 | 26.3767 | 94.5571 | 37.6914 | 35.079 | 36.6759 | 35.5447 | 33.8492 | 34.362 | 34.5013 | 34.04 | 34.4346 | 37.3813 | 37.2789 | 34.3967 | 34.2144 | 37.2858 | 36.5911 | 38.382 | 37.2791 | 35.5594 | 36.9555 | 38.5659 | 37.752 | 36.3128 | 35.1538 | 34.3059 | 35.9091 | 33.5308 | 33.9575 | 33.9054 | 34.9783 | 33.5721 | 34.2761 | 35.9589 | 33.6806 | 34.0147 | 35.8602 | 92.3926 | 92.5536 | 92.4071
2022-09-07 22:45 | 0:55 | 25.7273 | 26.2103 | 27.8977 | 39.8569 | 34.2715 | 35.4908 | 34.9474 | 35.1652 | 36.5252 | 35.7193 | 35.0936 | 35.3942 | 35.3807 | 36.4735 | 36.4346 | 35.3509 | 38.5345 | 36.6151 | 37.2271 | 37.615 | 30.8529 | 26.293 | 94.6678 | 37.6691 | 35.099 | 36.6595 | 35.5457 | 33.8391 | 34.3652 | 34.5241 | 34.0304 | 34.409 | 37.3734 | 37.2857 | 34.4004 | 34.2044 | 37.2759 | 36.5937 | 38.38 | 37.2801 | 35.5395 | 36.9253 | 38.5615 | 37.7362 | 36.3042 | 35.1461 | 34.2773 | 35.925 | 33.5553 | 33.9736 | 33.8988 | 34.9906 | 33.5818 | 34.3026 | 35.9326 | 33.6969 | 34.0207 | 35.8799 | 92.2733 | 92.4345 | 92.42
2022-09-07 22:46 | 0:56 | 25.5525 | 26.096 | 27.8318 | 39.812 | 34.2699 | 35.5174 | 34.9485 | 35.1817 | 36.5531 | 35.7241 | 35.1023 | 35.3977 | 35.3617 | 36.4573 | 36.468 | 35.3602 | 38.5324 | 36.6284 | 37.2375 | 37.634 | 30.8026 | 26.1176 | 94.7488 | 37.6044 | 35.1064 | 36.6862 | 35.5297 | 33.8508 | 34.3739 | 34.5287 | 34.0456 | 34.4288 | 37.3866 | 37.2919 | 34.4108 | 34.2312 | 37.2789 | 36.6056 | 38.3802 | 37.2706 | 35.5475 | 36.9029 | 38.547 | 37.7088 | 36.2717 | 35.1386 | 34.2801 | 35.9277 | 33.5425 | 33.9372 | 33.919 | 34.9686 | 33.6013 | 34.31 | 35.959 | 33.699 | 34.0429 | 35.8928 | 92.1982 | 92.3605 | 92.2938
2022-09-07 22:46 | 0:56 | 25.5288 | 26.0686 | 27.7047 | 39.7362 | 34.2578 | 35.5235 | 34.9844 | 35.1953 | 36.5589 | 35.7226 | 35.0997 | 35.4015 | 35.3723 | 36.4796 | 36.4485 | 35.3811 | 38.5371 | 36.6264 | 37.219 | 37.6392 | 30.7849 | 26.0689 | 94.8724 | 37.5763 | 35.1172 | 36.6893 | 35.538 | 33.8474 | 34.3915 | 34.5451 | 34.0466 | 34.435 | 37.3919 | 37.2762 | 34.4129 | 34.2215 | 37.2857 | 36.5998 | 38.3625 | 37.2858 | 35.561 | 36.9023 | 38.533 | 37.7274 | 36.2754 | 35.1224 | 34.2726 | 35.9146 | 33.5617 | 33.9661 | 33.9215 | 34.9647 | 33.5998 | 34.3112 | 35.9712 | 33.7156 | 34.0352 | 35.8936 | 92.122 | 92.2279 | 92.3053
2022-09-07 22:46 | 0:56 | 25.4538 | 25.9018 | 27.627 | 39.5605 | 34.2823 | 35.5404 | 34.9787 | 35.1884 | 36.5599 | 35.7255 | 35.1053 | 35.4228 | 35.376 | 36.4345 | 36.4544 | 35.3911 | 38.5257 | 36.6247 | 37.2289 | 37.6413 | 30.7158 | 26.0075 | 95.0006 | 37.361 | 35.1143 | 36.6911 | 35.5594 | 33.8463 | 34.3967 | 34.5684 | 34.044 | 34.4209 | 37.4175 | 37.2839 | 34.4056 | 34.2549 | 37.2919 | 36.6225 | 38.3934 | 37.2759 | 35.5336 | 36.8819 | 38.4967 | 37.7047 | 36.2442 | 35.1527 | 34.2839 | 35.9272 | 33.5543 | 33.9613 | 33.9085 | 34.9793 | 33.6047 | 34.3197 | 35.9766 | 33.7126 | 34.0635 | 35.8951 | 92.0724 | 92.2028 | 92.2765
2022-09-07 22:46 | 0:56 | 25.3851 | 25.8404 | 27.5592 | 39.6592 | 34.2658 | 35.564 | 34.9853 | 35.2143 | 36.5771 | 35.7479 | 35.1033 | 35.4356 | 35.3699 | 36.4241 | 36.4754 | 35.4011 | 38.5278 | 36.6041 | 37.2224 | 37.6579 | 30.6889 | 26.0189 | 95.1147 | 37.6399 | 35.1136 | 36.6898 | 35.5395 | 33.8866 | 34.4004 | 34.5731 | 34.066 | 34.4272 | 37.4235 | 37.2832 | 34.4231 | 34.246 | 37.2762 | 36.6238 | 38.3932 | 37.2789 | 35.5469 | 36.8753 | 38.481 | 37.7056 | 36.2739 | 35.133 | 34.2796 | 35.9246 | 33.5622 | 33.9526 | 33.9102 | 34.9799 | 33.6078 | 34.3175 | 35.9752 | 33.7259 | 34.0544 | 35.8979 | 92.1653 | 92.2074 | 92.3422
2022-09-07 22:46 | 0:56 | 25.3625 | 25.8221 | 27.4719 | 39.6066 | 34.2695 | 35.5485 | 34.9895 | 35.213 | 36.6003 | 35.7367 | 35.1243 | 35.4403 | 35.4047 | 36.4419 | 36.4486 | 35.4183 | 38.5241 | 36.6293 | 37.2165 | 37.6534 | 30.6558 | 25.9316 | 95.215 | 37.5619 | 35.1143 | 36.6889 | 35.5475 | 33.8811 | 34.4108 | 34.5826 | 34.0688 | 34.4367 | 37.409 | 37.2931 | 34.4264 | 34.2458 | 37.2839 | 36.646 | 38.3873 | 37.2857 | 35.5603 | 36.8555 | 38.4517 | 37.6923 | 36.2556 | 35.1142 | 34.2776 | 35.8882 | 33.5482 | 33.9674 | 33.9173 | 34.9841 | 33.5959 | 34.3258 | 35.9842 | 33.7607 | 34.0514 | 35.893 | 92.1752 | 92.2798 | 92.3402
2022-09-07 22:46 | 0:56 | 25.2783 | 25.7252 | 27.3873 | 39.7389 | 34.2766 | 35.5884 | 35.0151 | 35.2318 | 36.5994 | 35.7661 | 35.1403 | 35.4691 | 35.3757 | 36.4202 | 36.4928 | 35.409 | 38.5308 | 36.622 | 37.2289 | 37.6659 | 30.6082 | 25.8213 | 95.3052 | 37.5463 | 35.1185 | 36.6988 | 35.561 | 33.8696 | 34.4129 | 34.5876 | 34.0797 | 34.4446 | 37.4232 | 37.2918 | 34.4259 | 34.267 | 37.2832 | 36.6218 | 38.4008 | 37.2919 | 35.5443 | 36.8481 | 38.4514 | 37.6803 | 36.2269 | 35.1312 | 34.2631 | 35.8832 | 33.5508 | 33.9713 | 33.9289 | 34.9804 | 33.5945 | 34.3206 | 35.9986 | 33.7516 | 34.061 | 35.9095 | 92.2355 | 92.355 | 92.3506
2022-09-07 22:47 | 0:56 | 25.2745 | 25.6298 | 27.3419 | 39.5986 | 34.2807 | 35.5995 | 35.009 | 35.2424 | 36.6205 | 35.7676 | 35.1397 | 35.4682 | 35.3814 | 36.4314 | 36.4907 | 35.4293 | 38.5194 | 36.638 | 37.2343 | 37.6802 | 30.5568 | 25.8437 | 95.4158 | 37.3111 | 35.1247 | 36.6922 | 35.5336 | 33.9088 | 34.4056 | 34.595 | 34.0958 | 34.4499 | 37.422 | 37.2849 | 34.4379 | 34.2823 | 37.2931 | 36.6389 | 38.407 | 37.2762 | 35.5633 | 36.8321 | 38.4335 | 37.6394 | 36.2143 | 35.0977 | 34.2957 | 35.8705 | 33.5332 | 33.9691 | 33.9194 | 34.989 | 33.6089 | 34.3381 | 36.011 | 33.7469 | 34.0688 | 35.8903 | 92.2882 | 92.4393 | 92.3498
2022-09-07 22:47 | 0:57 | 25.2032 | 25.6117 | 27.2537 | 39.5226 | 34.2829 | 35.6007 | 35.0139 | 35.2516 | 36.6454 | 35.7766 | 35.1464 | 35.4785 | 35.3943 | 36.4171 | 36.4681 | 35.4461 | 38.5179 | 36.6269 | 37.2486 | 37.6655 | 30.5447 | 25.7902 | 95.4741 | 37.4135 | 35.1428 | 36.6792 | 35.5469 | 33.9058 | 34.4231 | 34.5989 | 34.0812 | 34.462 | 37.4306 | 37.2914 | 34.4283 | 34.2753 | 37.2918 | 36.6531 | 38.4079 | 37.2839 | 35.5658 | 36.8235 | 38.4068 | 37.6442 | 36.2161 | 35.101 | 34.2739 | 35.8906 | 33.5587 | 33.9809 | 33.9035 | 34.9547 | 33.6026 | 34.3506 | 36.0292 | 33.7797 | 34.0953 | 35.8855 | 92.3746 | 92.5506 | 92.4634
2022-09-07 22:47 | 0:57 | 25.0741 | 25.486 | 27.1964 | 39.5376 | 34.2858 | 35.6109 | 35.0328 | 35.2519 | 36.6255 | 35.7837 | 35.1595 | 35.4854 | 35.3785 | 36.3972 | 36.4952 | 35.4418 | 38.5156 | 36.6282 | 37.2186 | 37.6612 | 30.4775 | 25.742 | 95.5339 | 37.3488 | 35.1388 | 36.6829 | 35.5603 | 33.9044 | 34.4264 | 34.6032 | 34.0859 | 34.4668 | 37.4272 | 37.2774 | 34.443 | 34.2902 | 37.2849 | 36.6443 | 38.4085 | 37.2832 | 35.5422 | 36.7925 | 38.3695 | 37.6352 | 36.2121 | 35.1035 | 34.2799 | 35.8747 | 33.5528 | 33.9668 | 33.9048 | 34.9511 | 33.5966 | 34.3233 | 36.0064 | 33.773 | 34.1124 | 35.8807 | 92.4448 | 92.6848 | 92.5314
2022-09-07 22:47 | 0:57 | 25.0574 | 25.4422 | 27.0957 | 39.3875 | 34.2754 | 35.6136 | 35.0414 | 35.2796 | 36.6148 | 35.7914 | 35.1467 | 35.4885 | 35.3959 | 36.3664 | 36.4899 | 35.4498 | 38.5105 | 36.6257 | 37.2512 | 37.6636 | 30.4555 | 25.6862 | 95.4342 | 37.4301 | 35.1337 | 36.6962 | 35.5443 | 33.9289 | 34.4259 | 34.6105 | 34.103 | 34.4723 | 37.4388 | 37.2802 | 34.4554 | 34.2893 | 37.2914 | 36.6588 | 38.407 | 37.2931 | 35.5605 | 36.7928 | 38.3662 | 37.6328 | 36.2121 | 35.0992 | 34.2844 | 35.8701 | 33.5733 | 33.9608 | 33.9271 | 34.9585 | 33.5899 | 34.345 | 36.0074 | 33.7757 | 34.1135 | 35.8858 | 92.5619 | 92.8307 | 92.6345
2022-09-07 22:47 | 0:57 | 24.9045 | 25.3348 | 27.0479 | 39.3159 | 34.2729 | 35.6342 | 35.0587 | 35.272 | 36.6278 | 35.79 | 35.1616 | 35.4896 | 35.3837 | 36.3735 | 36.4936 | 35.4576 | 38.5032 | 36.6327 | 37.2244 | 37.6776 | 30.3916 | 25.5844 | 95.3231 | 37.4093 | 35.1446 | 36.7038 | 35.5633 | 33.9253 | 34.4379 | 34.6303 | 34.1001 | 34.4852 | 37.4261 | 37.286 | 34.4551 | 34.3008 | 37.2774 | 36.6831 | 38.3922 | 37.2918 | 35.545 | 36.7857 | 38.3497 | 37.6018 | 36.1925 | 35.0683 | 34.2624 | 35.8682 | 33.5359 | 33.9731 | 33.9199 | 34.9606 | 33.5826 | 34.3438 | 36.0306 | 33.784 | 34.1211 | 35.8879 | 92.7396 | 92.9657 | 92.7849
2022-09-07 22:47 | 0:57 | 24.8838 | 25.285 | 26.9652 | 39.2502 | 34.2742 | 35.6539 | 35.0531 | 35.2856 | 36.6684 | 35.8175 | 35.1767 | 35.5015 | 35.3822 | 36.3709 | 36.5003 | 35.4736 | 38.4927 | 36.6216 | 37.2201 | 37.681 | 30.3473 | 25.5119 | 95.1757 | 37.2732 | 35.1531 | 36.6949 | 35.5658 | 33.9162 | 34.4283 | 34.6409 | 34.103 | 34.4695 | 37.4426 | 37.2941 | 34.4471 | 34.2975 | 37.2802 | 36.6872 | 38.4054 | 37.2849 | 35.571 | 36.7574 | 38.3451 | 37.5935 | 36.1994 | 35.0986 | 34.2751 | 35.8567 | 33.5418 | 33.9862 | 33.9125 | 34.9421 | 33.6081 | 34.3572 | 36.0342 | 33.8119 | 34.122 | 35.8671 | 92.9445 | 93.0949 | 92.8929
2022-09-07 22:48 | 0:58 | 24.7687 | 25.2643 | 26.9377 | 39.3584 | 34.279 | 35.6664 | 35.0746 | 35.3016 | 36.6531 | 35.8054 | 35.1725 | 35.5091 | 35.3936 | 36.3679 | 36.486 | 35.4626 | 38.4883 | 36.6401 | 37.2558 | 37.681 | 30.3329 | 25.4562 | 95.0602 | 37.2811 | 35.1618 | 36.708 | 35.5422 | 33.9257 | 34.443 | 34.6423 | 34.1039 | 34.4935 | 37.4413 | 37.2787 | 34.4768 | 34.3033 | 37.286 | 36.7052 | 38.4113 | 37.2914 | 35.5569 | 36.7683 | 38.3057 | 37.5967 | 36.1772 | 35.0992 | 34.2565 | 35.8486 | 33.5442 | 33.9912 | 33.9138 | 34.9695 | 33.5969 | 34.3531 | 36.0522 | 33.809 | 34.1393 | 35.8791 | 93.0614 | 93.1519 | 92.9911
2022-09-07 22:48 | 0:58 | 24.7342 | 25.1268 | 26.8625 | 39.3458 | 34.2921 | 35.692 | 35.0687 | 35.3055 | 36.6771 | 35.8224 | 35.1722 | 35.5533 | 35.3864 | 36.34 | 36.4858 | 35.4879 | 38.5055 | 36.6308 | 37.2418 | 37.7058 | 30.2835 | 25.4483 | 95.0438 | 37.3817 | 35.1679 | 36.7061 | 35.5605 | 33.9457 | 34.4554 | 34.6598 | 34.1189 | 34.49 | 37.453 | 37.2936 | 34.4907 | 34.3135 | 37.2941 | 36.6875 | 38.4101 | 37.2774 | 35.5647 | 36.7487 | 38.2835 | 37.5599 | 36.1869 | 35.0988 | 34.2668 | 35.8435 | 33.5501 | 33.9951 | 33.9119 | 34.9495 | 33.6111 | 34.3681 | 36.0415 | 33.8151 | 34.1425 | 35.8635 | 93.0984 | 93.3076 | 92.9366
2022-09-07 22:48 | 0:58 | 24.6663 | 25.1123 | 26.785 | 39.2198 | 34.2923 | 35.6851 | 35.1016 | 35.3233 | 36.6689 | 35.8249 | 35.1768 | 35.5521 | 35.3905 | 36.3585 | 36.5074 | 35.5076 | 38.4919 | 36.639 | 37.2502 | 37.7044 | 30.2525 | 25.3851 | 94.9624 | 37.3203 | 35.1461 | 36.6973 | 35.545 | 33.9499 | 34.4551 | 34.6559 | 34.1383 | 34.4871 | 37.4735 | 37.3027 | 34.4703 | 34.3139 | 37.2787 | 36.7016 | 38.4088 | 37.2802 | 35.5696 | 36.7231 | 38.2879 | 37.5804 | 36.1413 | 35.0545 | 34.2672 | 35.8516 | 33.565 | 33.989 | 33.9241 | 34.9534 | 33.5836 | 34.3577 | 36.0645 | 33.8379 | 34.1472 | 35.891 | 93.2367 | 93.4433 | 93.0981
2022-09-07 22:48 | 0:58 | 24.5411 | 24.9566 | 26.6887 | 39.1266 | 34.2882 | 35.7068 | 35.0974 | 35.3309 | 36.6891 | 35.8302 | 35.2164 | 35.5657 | 35.3931 | 36.3175 | 36.5076 | 35.4938 | 38.4917 | 36.6342 | 37.2468 | 37.6979 | 30.1932 | 25.3269 | 94.9843 | 37.192 | 35.1652 | 36.7359 | 35.571 | 33.9704 | 34.4471 | 34.6464 | 34.1324 | 34.5154 | 37.468 | 37.3076 | 34.4914 | 34.3214 | 37.2936 | 36.711 | 38.3983 | 37.286 | 35.5727 | 36.7403 | 38.2616 | 37.5568 | 36.1614 | 35.054 | 34.2799 | 35.845 | 33.5627 | 33.9928 | 33.9147 | 34.953 | 33.6136 | 34.396 | 36.0658 | 33.8308 | 34.1611 | 35.8875 | 93.3379 | 93.6024 | 93.0617
2022-09-07 22:48 | 0:58 | 24.5262 | 24.9509 | 26.6376 | 39.1036 | 34.2773 | 35.7171 | 35.0987 | 35.3409 | 36.69 | 35.8397 | 35.2116 | 35.5768 | 35.3926 | 36.3371 | 36.5245 | 35.523 | 38.4864 | 36.6583 | 37.2555 | 37.7141 | 30.1403 | 25.2275 | 94.9695 | 37.2504 | 35.1729 | 36.7063 | 35.5569 | 33.9631 | 34.4768 | 34.6814 | 34.1382 | 34.5113 | 37.4899 | 37.3083 | 34.491 | 34.3466 | 37.3027 | 36.7129 | 38.4168 | 37.2941 | 35.588 | 36.6942 | 38.2345 | 37.559 | 36.1544 | 35.0626 | 34.2705 | 35.8447 | 33.553 | 34.0125 | 33.9127 | 34.9558 | 33.6204 | 34.3854 | 36.0672 | 33.8534 | 34.1538 | 35.8709 | 93.5126 | 93.7939 | 93.2472
2022-09-07 22:48 | 0:58 | 24.426 | 24.8332 | 26.5777 | 39.0602 | 34.3011 | 35.7092 | 35.1142 | 35.3611 | 36.6981 | 35.8315 | 35.2215 | 35.5905 | 35.4127 | 36.2945 | 36.5453 | 35.5412 | 38.5034 | 36.6555 | 37.2428 | 37.7189 | 30.1081 | 25.22 | 94.9356 | 37.1253 | 35.1589 | 36.7218 | 35.5647 | 33.9612 | 34.4907 | 34.6874 | 34.138 | 34.5006 | 37.4737 | 37.3003 | 34.5043 | 34.3581 | 37.3076 | 36.733 | 38.4253 | 37.2787 | 35.5763 | 36.6997 | 38.2287 | 37.5472 | 36.145 | 35.0768 | 34.2509 | 35.8434 | 33.5528 | 33.9989 | 33.912 | 34.9504 | 33.6264 | 34.3841 | 36.0942 | 33.846 | 34.1542 | 35.8717 | 93.6632 | 93.9939 | 93.3664
2022-09-07 22:49 | 0:58 | 24.3734 | 24.7983 | 26.4928 | 39.2096 | 34.2873 | 35.7215 | 35.1072 | 35.3675 | 36.7195 | 35.8537 | 35.2407 | 35.5973 | 35.4154 | 36.3203 | 36.5115 | 35.5275 | 38.4832 | 36.6569 | 37.2769 | 37.7295 | 30.0605 | 25.1751 | 94.9135 | 37.2064 | 35.1827 | 36.7297 | 35.5696 | 33.9867 | 34.4703 | 34.7015 | 34.1388 | 34.5281 | 37.4947 | 37.2923 | 34.505 | 34.3612 | 37.3083 | 36.7332 | 38.4056 | 37.2936 | 35.5852 | 36.6724 | 38.2147 | 37.5549 | 36.1236 | 35.0718 | 34.2441 | 35.8199 | 33.559 | 34.0125 | 33.9182 | 34.9487 | 33.6144 | 34.3862 | 36.0798 | 33.8501 | 34.1741 | 35.8973 | 93.7999 | 94.1762 | 93.4239
2022-09-07 22:49 | 0:59 | 24.3515 | 24.7704 | 26.4581 | 39.0742 | 34.285 | 35.7498 | 35.1372 | 35.392 | 36.7359 | 35.8632 | 35.2399 | 35.6103 | 35.3942 | 36.2905 | 36.5359 | 35.5652 | 38.4771 | 36.6626 | 37.2684 | 37.7268 | 30.0371 | 25.1655 | 94.9169 | 37.2276 | 35.1957 | 36.7359 | 35.5727 | 33.9816 | 34.4914 | 34.6982 | 34.1712 | 34.5442 | 37.507 | 37.2977 | 34.5265 | 34.376 | 37.3003 | 36.7377 | 38.4024 | 37.3027 | 35.5998 | 36.6562 | 38.2068 | 37.552 | 36.1185 | 35.048 | 34.2727 | 35.8297 | 33.5467 | 34.0059 | 33.9251 | 34.9359 | 33.6161 | 34.3892 | 36.1157 | 33.8818 | 34.2029 | 35.8822 | 93.9468 | 94.3332 | 93.6084
2022-09-07 22:49 | 0:59 | 24.2412 | 24.6644 | 26.4082 | 39.1733 | 34.308 | 35.7606 | 35.1534 | 35.3896 | 36.7376 | 35.854 | 35.2358 | 35.6327 | 35.3897 | 36.301 | 36.5385 | 35.5699 | 38.4743 | 36.6664 | 37.2807 | 37.7351 | 30.0022 | 25.0484 | 94.8955 | 37.081 | 35.174 | 36.7282 | 35.588 | 33.9823 | 34.491 | 34.716 | 34.1646 | 34.5459 | 37.5031 | 37.3154 | 34.5198 | 34.3834 | 37.2923 | 36.7769 | 38.4227 | 37.3076 | 35.5832 | 36.6874 | 38.1822 | 37.5315 | 36.1241 | 35.0701 | 34.2737 | 35.8131 | 33.5478 | 34.0085 | 33.9194 | 34.9294 | 33.6095 | 34.4072 | 36.1173 | 33.8821 | 34.1747 | 35.8754 | 94.1665 | 94.5181 | 93.7448
2022-09-07 22:49 | 0:59 | 24.2626 | 24.5709 | 26.3067 | 39.0216 | 34.2966 | 35.7535 | 35.1489 | 35.386 | 36.738 | 35.8498 | 35.2641 | 35.6328 | 35.3956 | 36.3092 | 36.5339 | 35.5565 | 38.4574 | 36.6658 | 37.2814 | 37.7241 | 29.958 | 25.0302 | 94.8875 | 37.1539 | 35.1925 | 36.7454 | 35.5763 | 34.0002 | 34.5043 | 34.7437 | 34.1854 | 34.5526 | 37.5191 | 37.3063 | 34.5066 | 34.4042 | 37.2977 | 36.7548 | 38.4091 | 37.3083 | 35.5855 | 36.6624 | 38.1835 | 37.5184 | 36.087 | 35.0676 | 34.2456 | 35.8199 | 33.5576 | 34.0211 | 33.9409 | 34.9231 | 33.618 | 34.4111 | 36.1205 | 33.9102 | 34.2121 | 35.8847 | 94.3215 | 94.7225 | 93.8428
2022-09-07 22:49 | 0:59 | 24.199 | 24.5863 | 26.2869 | 38.8411 | 34.3176 | 35.7775 | 35.1875 | 35.4192 | 36.7686 | 35.8781 | 35.2693 | 35.6233 | 35.4255 | 36.2579 | 36.5393 | 35.5962 | 38.476 | 36.6859 | 37.288 | 37.7397 | 29.9108 | 24.9769 | 94.8551 | 37.0198 | 35.1929 | 36.7291 | 35.5852 | 34.0147 | 34.505 | 34.7348 | 34.1893 | 34.5506 | 37.5175 | 37.3077 | 34.5322 | 34.3839 | 37.3154 | 36.777 | 38.4292 | 37.3003 | 35.5871 | 36.6647 | 38.1439 | 37.5244 | 36.1081 | 35.0534 | 34.2665 | 35.8122 | 33.5596 | 34.0126 | 33.9193 | 34.9359 | 33.6221 | 34.4152 | 36.1189 | 33.9136 | 34.1978 | 35.882 | 94.4754 | 94.9481 | 93.9907
2022-09-07 22:49 | 0:59 | 24.1095 | 24.5734 | 26.2629 | 38.9545 | 34.3146 | 35.7794 | 35.1827 | 35.4119 | 36.7719 | 35.8922 | 35.2656 | 35.6544 | 35.411 | 36.2683 | 36.5488 | 35.5947 | 38.4736 | 36.677 | 37.2803 | 37.7277 | 29.9005 | 24.9807 | 94.8233 | 36.9463 | 35.2061 | 36.7486 | 35.5998 | 34.0248 | 34.5265 | 34.746 | 34.2057 | 34.5512 | 37.5141 | 37.2987 | 34.5436 | 34.3987 | 37.3063 | 36.7765 | 38.4373 | 37.2923 | 35.6011 | 36.6321 | 38.1435 | 37.516 | 36.093 | 35.0514 | 34.2408 | 35.8065 | 33.571 | 34.0124 | 33.9248 | 34.9442 | 33.6257 | 34.4224 | 36.1244 | 33.913 | 34.2125 | 35.8779 | 94.5624 | 95.1179 | 94.1139
2022-09-07 22:50 | 0:59 | 24.0868 | 24.5285 | 26.1989 | 38.9719 | 34.3094 | 35.8077 | 35.188 | 35.4299 | 36.7722 | 35.8772 | 35.2806 | 35.643 | 35.4097 | 36.255 | 36.542 | 35.6051 | 38.4845 | 36.6904 | 37.2797 | 37.7648 | 29.8723 | 24.9097 | 94.8101 | 36.7443 | 35.2145 | 36.747 | 35.5832 | 34.0222 | 34.5198 | 34.7553 | 34.2122 | 34.5749 | 37.5213 | 37.3194 | 34.541 | 34.4041 | 37.3077 | 36.7889 | 38.4294 | 37.2977 | 35.5886 | 36.6284 | 38.1219 | 37.5018 | 36.0818 | 35.0635 | 34.2359 | 35.804 | 33.5553 | 34.0358 | 33.9376 | 34.9264 | 33.621 | 34.4333 | 36.1455 | 33.9363 | 34.2384 | 35.8933 | 94.6681 | 95.2641 | 94.2175
2022-09-07 22:50 | 1:00 | 23.9564 | 24.3698 | 26.0782 | 38.8058 | 34.3116 | 35.8072 | 35.1944 | 35.4569 | 36.7883 | 35.9227 | 35.3057 | 35.6864 | 35.4224 | 36.2483 | 36.5617 | 35.6045 | 38.4874 | 36.7031 | 37.2841 | 37.7581 | 29.8003 | 24.8082 | 94.8264 | 36.9053 | 35.2173 | 36.7452 | 35.5855 | 34.0442 | 34.5066 | 34.7685 | 34.2205 | 34.5696 | 37.5364 | 37.3163 | 34.55 | 34.4204 | 37.2987 | 36.8143 | 38.4217 | 37.3154 | 35.6023 | 36.6148 | 38.097 | 37.4974 | 36.0753 | 35.0515 | 34.2427 | 35.8041 | 33.5698 | 34.0387 | 33.923 | 34.9217 | 33.6409 | 34.4299 | 36.1546 | 33.9239 | 34.2399 | 35.8844 | 94.8477 | 95.4015 | 94.345
2022-09-07 22:50 | 1:00 | 23.9805 | 24.3662 | 26.044 | 38.7391 | 34.3413 | 35.8244 | 35.197 | 35.4529 | 36.7848 | 35.9077 | 35.3217 | 35.6839 | 35.4141 | 36.2643 | 36.5654 | 35.6137 | 38.4718 | 36.6827 | 37.307 | 37.7765 | 29.7456 | 24.7863 | 94.6669 | 36.9844 | 35.2096 | 36.747 | 35.5871 | 34.0478 | 34.5322 | 34.7755 | 34.229 | 34.5739 | 37.5628 | 37.3163 | 34.5452 | 34.4063 | 37.3194 | 36.807 | 38.4326 | 37.3063 | 35.6049 | 36.6025 | 38.1106 | 37.4658 | 36.0796 | 35.048 | 34.2597 | 35.817 | 33.5667 | 34.0452 | 33.9136 | 34.9363 | 33.6204 | 34.4475 | 36.15 | 33.9549 | 34.2452 | 35.9062 | 94.9499 | 95.5261 | 94.3384
2022-09-07 22:50 | 1:00 | 23.8771 | 24.2634 | 26.0167 | 38.8082 | 34.3051 | 35.8324 | 35.2178 | 35.4727 | 36.7948 | 35.9204 | 35.3329 | 35.715 | 35.4067 | 36.2508 | 36.5609 | 35.6435 | 38.4647 | 36.7109 | 37.2895 | 37.7701 | 29.7146 | 24.7858 | 94.6035 | 36.8437 | 35.2377 | 36.77 | 35.6011 | 34.0486 | 34.5436 | 34.7853 | 34.2351 | 34.5776 | 37.5535 | 37.3183 | 34.5574 | 34.429 | 37.3163 | 36.8114 | 38.4305 | 37.3077 | 35.5973 | 36.5949 | 38.0978 | 37.4736 | 36.0702 | 35.0441 | 34.2649 | 35.7993 | 33.585 | 34.0318 | 33.9477 | 34.9371 | 33.6497 | 34.4432 | 36.1536 | 33.9518 | 34.2423 | 35.8895 | 95.1231 | 95.6375 | 94.4155
2022-09-07 22:50 | 1:00 | 23.8568 | 24.1877 | 25.9605 | 38.7903 | 34.3258 | 35.8485 | 35.224 | 35.4931 | 36.8103 | 35.9297 | 35.335 | 35.7256 | 35.4191 | 36.2356 | 36.576 | 35.6452 | 38.468 | 36.7234 | 37.3047 | 37.7796 | 29.6769 | 24.6523 | 94.5597 | 36.8551 | 35.2089 | 36.7581 | 35.5886 | 34.0513 | 34.541 | 34.795 | 34.2297 | 34.5873 | 37.5575 | 37.3164 | 34.5709 | 34.4337 | 37.3163 | 36.8216 | 38.4425 | 37.2987 | 35.5889 | 36.5941 | 38.062 | 37.4758 | 36.0534 | 35.0513 | 34.2463 | 35.801 | 33.5733 | 34.0646 | 33.9438 | 34.9224 | 33.6478 | 34.4393 | 36.158 | 33.9425 | 34.262 | 35.8989 | 95.1162 | 95.6613 | 94.3771
2022-09-07 22:50 | 1:00 | 23.8348 | 24.2291 | 25.9235 | 38.7363 | 34.3218 | 35.8421 | 35.2244 | 35.4875 | 36.8266 | 35.9323 | 35.3319 | 35.7503 | 35.4336 | 36.2268 | 36.581 | 35.6634 | 38.4578 | 36.7304 | 37.2973 | 37.7838 | 29.6339 | 24.6134 | 94.4704 | 36.9141 | 35.2267 | 36.7653 | 35.6023 | 34.0719 | 34.55 | 34.7888 | 34.2563 | 34.6085 | 37.569 | 37.3101 | 34.56 | 34.4484 | 37.3183 | 36.8338 | 38.4263 | 37.3194 | 35.6053 | 36.585 | 38.0663 | 37.4954 | 36.0613 | 35.0313 | 34.2596 | 35.7971 | 33.5886 | 34.0463 | 33.9284 | 34.9334 | 33.6447 | 34.45 | 36.1761 | 33.9842 | 34.2774 | 35.9121 | 95.2083 | 95.7177 | 94.4916
2022-09-07 22:51 | 1:01 | 23.7628 | 24.1249 | 25.8867 | 38.661 | 34.3171 | 35.8571 | 35.2302 | 35.4937 | 36.8185 | 35.9421 | 35.3355 | 35.7558 | 35.4251 | 36.2181 | 36.585 | 35.6679 | 38.4698 | 36.7249 | 37.3024 | 37.7731 | 29.6035 | 24.5591 | 94.4175 | 36.9267 | 35.2374 | 36.76 | 35.6049 | 34.0701 | 34.5452 | 34.8017 | 34.256 | 34.6016 | 37.5701 | 37.3087 | 34.5836 | 34.4604 | 37.3164 | 36.8387 | 38.4547 | 37.3163 | 35.59 | 36.5662 | 38.0462 | 37.4832 | 36.0279 | 35.0588 | 34.2392 | 35.7823 | 33.5692 | 34.0568 | 33.934 | 34.9381 | 33.6511 | 34.4864 | 36.1873 | 33.9749 | 34.2897 | 35.9166 | 95.1662 | 95.6006 | 94.4272
2022-09-07 22:51 | 1:01 | 23.6487 | 24.0643 | 25.7885 | 38.6693 | 34.3342 | 35.854 | 35.2456 | 35.5127 | 36.833 | 35.9451 | 35.3525 | 35.7807 | 35.453 | 36.1951 | 36.5948 | 35.6765 | 38.46 | 36.7277 | 37.322 | 37.7884 | 29.5424 | 24.4947 | 94.3228 | 36.7396 | 35.2345 | 36.7685 | 35.5973 | 34.0904 | 34.5574 | 34.813 | 34.2621 | 34.6114 | 37.5857 | 37.3238 | 34.5748 | 34.4699 | 37.3101 | 36.8612 | 38.4396 | 37.3163 | 35.592 | 36.5562 | 38.0419 | 37.4825 | 36.0332 | 35.0402 | 34.2548 | 35.7812 | 33.5806 | 34.0626 | 33.9492 | 34.9068 | 33.6209 | 34.4663 | 36.1933 | 33.9773 | 34.2816 | 35.9073 | 94.9221 | 95.3124 | 94.2206
2022-09-07 22:51 | 1:01 | 23.6552 | 24.0294 | 25.7353 | 38.628 | 34.3279 | 35.8701 | 35.2528 | 35.5204 | 36.8519 | 35.9798 | 35.3595 | 35.7759 | 35.434 | 36.1854 | 36.5845 | 35.6775 | 38.4787 | 36.7364 | 37.3303 | 37.8031 | 29.5079 | 24.4922 | 94.1845 | 36.8452 | 35.2426 | 36.7816 | 35.5889 | 34.0995 | 34.5709 | 34.8275 | 34.2756 | 34.633 | 37.5843 | 37.3103 | 34.5717 | 34.4565 | 37.3087 | 36.8609 | 38.4343 | 37.3183 | 35.6151 | 36.5692 | 38.0268 | 37.4627 | 36.0258 | 35.0482 | 34.2369 | 35.7812 | 33.5832 | 34.0607 | 33.9408 | 34.9333 | 33.6554 | 34.4791 | 36.1807 | 33.992 | 34.2895 | 35.9206 | 94.6675 | 95.0383 | 94.0497
2022-09-07 22:51 | 1:01 | 23.5643 | 23.9307 | 25.6746 | 38.7187 | 34.3595 | 35.8811 | 35.2617 | 35.5177 | 36.8431 | 35.9858 | 35.379 | 35.7866 | 35.4405 | 36.1875 | 36.5836 | 35.6943 | 38.4391 | 36.7242 | 37.3186 | 37.7894 | 29.4505 | 24.4246 | 93.9954 | 36.5187 | 35.2355 | 36.7709 | 35.6053 | 34.0814 | 34.56 | 34.824 | 34.2595 | 34.6125 | 37.5937 | 37.3244 | 34.5714 | 34.4759 | 37.3238 | 36.8823 | 38.4416 | 37.3164 | 35.6002 | 36.5568 | 38.0151 | 37.4511 | 36.0141 | 35.0233 | 34.248 | 35.7953 | 33.5935 | 34.0438 | 33.9363 | 34.9311 | 33.651 | 34.5018 | 36.1799 | 34.0234 | 34.2917 | 35.9148 | 94.4634 | 94.866 | 94.0439
2022-09-07 22:51 | 1:01 | 23.5151 | 23.9348 | 25.5858 | 38.5821 | 34.3311 | 35.8873 | 35.2706 | 35.5554 | 36.8618 | 35.9582 | 35.3708 | 35.7848 | 35.4191 | 36.188 | 36.5907 | 35.6892 | 38.4627 | 36.7547 | 37.3282 | 37.8178 | 29.4093 | 24.3818 | 93.8395 | 36.5764 | 35.2581 | 36.7631 | 35.59 | 34.0852 | 34.5836 | 34.8493 | 34.2832 | 34.6159 | 37.598 | 37.32 | 34.5946 | 34.4905 | 37.3103 | 36.8988 | 38.4496 | 37.3101 | 35.5927 | 36.5408 | 38.0038 | 37.4759 | 36.0046 | 34.9965 | 34.2543 | 35.7935 | 33.6013 | 34.056 | 33.9578 | 34.9346 | 33.6437 | 34.4964 | 36.2066 | 34.0016 | 34.3167 | 35.9153 | 94.3652 | 94.7042 | 93.8703
2022-09-07 22:51 | 1:01 | 23.454 | 23.8371 | 25.5704 | 38.4825 | 34.3515 | 35.9098 | 35.286 | 35.5626 | 36.865 | 35.974 | 35.3844 | 35.8053 | 35.4354 | 36.1874 | 36.5916 | 35.7253 | 38.4663 | 36.7469 | 37.34 | 37.7974 | 29.3747 | 24.2984 | 93.685 | 36.7522 | 35.2581 | 36.8036 | 35.592 | 34.0922 | 34.5748 | 34.8668 | 34.3015 | 34.6428 | 37.5912 | 37.321 | 34.5867 | 34.5039 | 37.3244 | 36.8936 | 38.4503 | 37.3087 | 35.6089 | 36.5302 | 37.9772 | 37.4606 | 35.9953 | 34.9948 | 34.2489 | 35.7935 | 33.6079 | 34.0585 | 33.9337 | 34.9098 | 33.6637 | 34.4993 | 36.1917 | 34.0202 | 34.3303 | 35.9155 | 94.2653 | 94.6399 | 93.7963
2022-09-07 22:52 | 1:01 | 23.4195 | 23.8212 | 25.5239 | 38.423 | 34.3449 | 35.9258 | 35.2905 | 35.5739 | 36.8761 | 36.0023 | 35.4113 | 35.81 | 35.4379 | 36.1583 | 36.591 | 35.7226 | 38.4441 | 36.7477 | 37.3026 | 37.8208 | 29.3328 | 24.2454 | 93.5362 | 36.6949 | 35.2608 | 36.7702 | 35.6151 | 34.1133 | 34.5717 | 34.8707 | 34.2904 | 34.6264 | 37.5895 | 37.3207 | 34.5942 | 34.5042 | 37.32 | 36.8935 | 38.452 | 37.3238 | 35.6033 | 36.5375 | 37.9722 | 37.4519 | 35.9895 | 35.0024 | 34.2232 | 35.8108 | 33.6078 | 34.0787 | 33.924 | 34.9115 | 33.6571 | 34.5191 | 36.2161 | 34.0261 | 34.3473 | 35.9282 | 94.1406 | 94.5521 | 93.8266
2022-09-07 22:52 | 1:02 | 23.304 | 23.6575 | 25.4241 | 38.441 | 34.3509 | 35.914 | 35.2952 | 35.5773 | 36.8745 | 35.9988 | 35.4133 | 35.8295 | 35.4396 | 36.1523 | 36.6008 | 35.7241 | 38.462 | 36.7633 | 37.3347 | 37.8189 | 29.2912 | 24.1839 | 93.3895 | 36.7686 | 35.2685 | 36.7641 | 35.6002 | 34.0982 | 34.5714 | 34.8896 | 34.3053 | 34.6463 | 37.6043 | 37.3071 | 34.6204 | 34.5121 | 37.321 | 36.8997 | 38.4419 | 37.3103 | 35.6097 | 36.5228 | 37.9437 | 37.4519 | 36.0006 | 34.9933 | 34.2526 | 35.7708 | 33.6208 | 34.0684 | 33.9293 | 34.9191 | 33.6503 | 34.5086 | 36.204 | 34.0245 | 34.3458 | 35.9156 | 94.0868 | 94.4165 | 93.6965
2022-09-07 22:52 | 1:02 | 23.4574 | 23.7744 | 25.4411 | 38.5012 | 34.3402 | 35.9324 | 35.3007 | 35.572 | 36.895 | 35.9848 | 35.4166 | 35.841 | 35.4318 | 36.1524 | 36.6071 | 35.7368 | 38.4544 | 36.7684 | 37.3342 | 37.8448 | 29.2383 | 24.1822 | 93.2492 | 36.6691 | 35.2591 | 36.7745 | 35.5927 | 34.1172 | 34.5946 | 34.877 | 34.3165 | 34.6489 | 37.6094 | 37.314 | 34.5911 | 34.5119 | 37.3207 | 36.9006 | 38.4614 | 37.3244 | 35.6261 | 36.5057 | 37.9514 | 37.442 | 35.9875 | 34.997 | 34.2423 | 35.7808 | 33.6073 | 34.0551 | 33.9473 | 34.912 | 33.6718 | 34.5358 | 36.2101 | 34.0545 | 34.3494 | 35.9068 | 93.9699 | 94.2638 | 93.6294
2022-09-07 22:52 | 1:02 | 23.2221 | 23.5783 | 25.3412 | 38.3566 | 34.3451 | 35.9417 | 35.3125 | 35.578 | 36.8982 | 36.023 | 35.4225 | 35.8492 | 35.4483 | 36.1433 | 36.6231 | 35.7263 | 38.4321 | 36.7982 | 37.3254 | 37.8327 | 29.1889 | 24.0881 | 93.1561 | 36.7246 | 35.276 | 36.7858 | 35.6089 | 34.1441 | 34.5867 | 34.886 | 34.3182 | 34.6519 | 37.6258 | 37.3099 | 34.6179 | 34.5374 | 37.3071 | 36.9074 | 38.4667 | 37.32 | 35.6087 | 36.5037 | 37.9416 | 37.4299 | 35.9686 | 34.9929 | 34.2381 | 35.7672 | 33.6077 | 34.0943 | 33.9365 | 34.9097 | 33.6693 | 34.5346 | 36.2238 | 34.0531 | 34.3602 | 35.9209 | 93.8837 | 94.1956 | 93.628
2022-09-07 22:52 | 1:02 | 23.2587 | 23.5657 | 25.2712 | 38.2929 | 34.3435 | 35.949 | 35.3076 | 35.5921 | 36.8911 | 36.0347 | 35.4218 | 35.8626 | 35.4317 | 36.1291 | 36.6042 | 35.7617 | 38.4373 | 36.7633 | 37.3595 | 37.8411 | 29.157 | 24.0658 | 93.057 | 36.5795 | 35.2845 | 36.7753 | 35.6033 | 34.1378 | 34.5942 | 34.8921 | 34.3171 | 34.6551 | 37.6319 | 37.2943 | 34.6217 | 34.5249 | 37.314 | 36.9075 | 38.4615 | 37.321 | 35.5986 | 36.4988 | 37.9266 | 37.4362 | 35.9679 | 34.9872 | 34.2279 | 35.7787 | 33.6392 | 34.0648 | 33.9396 | 34.9234 | 33.6726 | 34.5352 | 36.2311 | 34.059 | 34.3555 | 35.9423 | 93.8073 | 94.1587 | 93.575
2022-09-07 22:52 | 1:02 | 23.1272 | 23.4883 | 25.275 | 38.3199 | 34.3772 | 35.9478 | 35.3242 | 35.6001 | 36.925 | 36.0261 | 35.4221 | 35.8811 | 35.4484 | 36.119 | 36.6198 | 35.7505 | 38.4443 | 36.7799 | 37.3455 | 37.8494 | 29.1225 | 24.0537 | 93.0341 | 36.6084 | 35.28 | 36.7918 | 35.6097 | 34.152 | 34.6204 | 34.9068 | 34.3207 | 34.6721 | 37.6338 | 37.2906 | 34.6212 | 34.5339 | 37.3099 | 36.9293 | 38.4727 | 37.3207 | 35.5966 | 36.4732 | 37.9111 | 37.4105 | 35.9577 | 34.9684 | 34.2305 | 35.7641 | 33.6219 | 34.0662 | 33.9431 | 34.9311 | 33.6877 | 34.5489 | 36.2302 | 34.0834 | 34.3756 | 35.9343 | 93.8374 | 94.104 | 93.622
2022-09-07 22:53 | 1:03 | 23.077 | 23.4287 | 25.188 | 38.3081 | 34.3465 | 35.9677 | 35.3414 | 35.6182 | 36.9182 | 36.0425 | 35.4414 | 35.9 | 35.4513 | 36.1386 | 36.6104 | 35.768 | 38.4505 | 36.7985 | 37.3638 | 37.8719 | 29.0692 | 23.9533 | 93.0733 | 36.4883 | 35.284 | 36.7865 | 35.6261 | 34.1493 | 34.5911 | 34.9213 | 34.3182 | 34.6623 | 37.624 | 37.3026 | 34.6133 | 34.5297 | 37.2943 | 36.9492 | 38.4574 | 37.3071 | 35.6234 | 36.4683 | 37.9076 | 37.4217 | 35.9309 | 34.9755 | 34.2247 | 35.7474 | 33.6325 | 34.0729 | 33.9543 | 34.8976 | 33.6697 | 34.5673 | 36.2462 | 34.0814 | 34.3841 | 35.9504 | 93.8008 | 94.0389 | 93.5053
2022-09-07 22:53 | 1:03 | 23.0109 | 23.3606 | 25.1312 | 38.1887 | 34.3433 | 35.9821 | 35.3439 | 35.621 | 36.9292 | 36.0532 | 35.4533 | 35.9033 | 35.4409 | 36.1236 | 36.6425 | 35.7618 | 38.4253 | 36.7964 | 37.3721 | 37.844 | 29.018 | 23.9334 | 93.1959 | 36.6218 | 35.2856 | 36.7773 | 35.6087 | 34.164 | 34.6179 | 34.9326 | 34.3492 | 34.6738 | 37.6339 | 37.2733 | 34.6322 | 34.5451 | 37.2906 | 36.944 | 38.4721 | 37.314 | 35.6002 | 36.4707 | 37.8689 | 37.4149 | 35.9449 | 34.9562 | 34.2555 | 35.7399 | 33.6327 | 34.0823 | 33.9527 | 34.903 | 33.6802 | 34.5676 | 36.2338 | 34.0688 | 34.3972 | 35.9341 | 93.8088 | 94.041 | 93.6108
2022-09-07 22:53 | 1:03 | 23.0294 | 23.3718 | 25.1281 | 38.2118 | 34.3705 | 35.9679 | 35.3502 | 35.6268 | 36.9175 | 36.0563 | 35.4586 | 35.9143 | 35.4394 | 36.1055 | 36.628 | 35.786 | 38.4139 | 36.8055 | 37.369 | 37.8594 | 29.0138 | 23.9212 | 93.2467 | 36.4689 | 35.2873 | 36.7832 | 35.5986 | 34.1662 | 34.6217 | 34.9276 | 34.3301 | 34.6644 | 37.6421 | 37.2909 | 34.6568 | 34.5294 | 37.3026 | 36.9471 | 38.4748 | 37.3099 | 35.6011 | 36.4549 | 37.8761 | 37.4179 | 35.9305 | 34.9498 | 34.2319 | 35.7479 | 33.617 | 34.0935 | 33.9413 | 34.8989 | 33.687 | 34.5848 | 36.2373 | 34.0845 | 34.3958 | 35.9426 | 93.683 | 93.9224 | 93.4358
2022-09-07 22:53 | 1:03 | 22.9567 | 23.2632 | 25.07 | 38.2029 | 34.3646 | 35.9791 | 35.3579 | 35.629 | 36.9307 | 36.0431 | 35.4646 | 35.9166 | 35.4445 | 36.1063 | 36.621 | 35.7762 | 38.4314 | 36.7979 | 37.3603 | 37.8752 | 28.9371 | 23.8322 | 93.2961 | 36.4975 | 35.2878 | 36.7939 | 35.5966 | 34.1659 | 34.6212 | 34.9518 | 34.3513 | 34.6824 | 37.6388 | 37.2927 | 34.6314 | 34.5453 | 37.2733 | 36.961 | 38.4645 | 37.2943 | 35.5859 | 36.438 | 37.8548 | 37.4011 | 35.9163 | 34.955 | 34.2281 | 35.7503 | 33.6349 | 34.0793 | 33.9463 | 34.9209 | 33.6923 | 34.5872 | 36.2334 | 34.1057 | 34.3991 | 35.9437 | 93.5863 | 93.8319 | 93.3947
2022-09-07 22:53 | 1:03 | 22.8609 | 23.1794 | 25.002 | 38.2664 | 34.362 | 35.9943 | 35.3537 | 35.6374 | 36.9433 | 36.0791 | 35.4691 | 35.931 | 35.44 | 36.0944 | 36.6218 | 35.7607 | 38.419 | 36.8156 | 37.3673 | 37.8548 | 28.9 | 23.7901 | 93.3017 | 36.5756 | 35.2877 | 36.7809 | 35.6234 | 34.1729 | 34.6133 | 34.9595 | 34.343 | 34.6829 | 37.6564 | 37.2736 | 34.6417 | 34.5588 | 37.2909 | 36.9571 | 38.4703 | 37.2906 | 35.6007 | 36.4239 | 37.8478 | 37.3784 | 35.8882 | 34.9551 | 34.2245 | 35.7387 | 33.6287 | 34.0685 | 33.922 | 34.9004 | 33.698 | 34.5659 | 36.2305 | 34.1009 | 34.4194 | 35.9478 | 93.5205 | 93.7555 | 93.3242
2022-09-07 22:53 | 1:03 | 22.8972 | 23.2863 | 24.9757 | 38.2234 | 34.3466 | 35.9837 | 35.3702 | 35.6707 | 36.9348 | 36.0475 | 35.466 | 35.9325 | 35.4246 | 36.0609 | 36.6481 | 35.7789 | 38.414 | 36.8281 | 37.3636 | 37.8778 | 28.8604 | 23.8055 | 93.3325 | 36.4709 | 35.2869 | 36.7824 | 35.6002 | 34.1787 | 34.6322 | 34.9516 | 34.345 | 34.6881 | 37.6444 | 37.2911 | 34.6424 | 34.5371 | 37.2927 | 36.9661 | 38.4847 | 37.3026 | 35.6072 | 36.4102 | 37.8339 | 37.4087 | 35.8898 | 34.9432 | 34.2142 | 35.7541 | 33.6404 | 34.0778 | 33.9501 | 34.9028 | 33.6703 | 34.5987 | 36.2467 | 34.1249 | 34.4193 | 35.9457 | 93.4379 | 93.6665 | 93.2601
2022-09-07 22:54 | 1:03 | 22.7707 | 23.0977 | 24.906 | 38.1094 | 34.3689 | 36.0084 | 35.3808 | 35.6498 | 36.9567 | 36.0703 | 35.4798 | 35.9256 | 35.4313 | 36.0744 | 36.6452 | 35.7945 | 38.4104 | 36.8135 | 37.3776 | 37.8888 | 28.8048 | 23.695 | 93.3852 | 36.3702 | 35.3084 | 36.7684 | 35.6011 | 34.1803 | 34.6568 | 34.9632 | 34.3477 | 34.706 | 37.6391 | 37.2751 | 34.6631 | 34.5454 | 37.2736 | 36.9746 | 38.4947 | 37.2733 | 35.5883 | 36.4271 | 37.8259 | 37.3962 | 35.8757 | 34.9388 | 34.2182 | 35.741 | 33.6453 | 34.0895 | 33.9556 | 34.9088 | 33.6938 | 34.5909 | 36.2386 | 34.1153 | 34.4092 | 35.9565 | 93.3414 | 93.5802 | 93.201
2022-09-07 22:54 | 1:04 | 22.7764 | 23.1189 | 24.8955 | 38.0999 | 34.3664 | 35.9905 | 35.3739 | 35.6664 | 36.9435 | 36.0784 | 35.5053 | 35.9488 | 35.4372 | 36.0486 | 36.6649 | 35.8046 | 38.3997 | 36.845 | 37.3614 | 37.8935 | 28.7776 | 23.672 | 93.4856 | 36.3521 | 35.3165 | 36.7703 | 35.5859 | 34.184 | 34.6314 | 34.9853 | 34.345 | 34.6993 | 37.6629 | 37.249 | 34.6733 | 34.5652 | 37.2911 | 36.9824 | 38.4762 | 37.2909 | 35.5843 | 36.4026 | 37.8393 | 37.374 | 35.8823 | 34.9504 | 34.196 | 35.7174 | 33.6329 | 34.0897 | 33.9539 | 34.9048 | 33.6847 | 34.5954 | 36.2505 | 34.1503 | 34.4411 | 35.9573 | 93.3494 | 93.5268 | 93.2628
2022-09-07 22:54 | 1:04 | 22.7499 | 22.996 | 24.8184 | 38.0921 | 34.3686 | 36.0117 | 35.3927 | 35.6829 | 36.9554 | 36.1147 | 35.4892 | 35.9614 | 35.4351 | 36.0566 | 36.6491 | 35.8069 | 38.3933 | 36.8288 | 37.3833 | 37.8789 | 28.7235 | 23.652 | 93.5653 | 36.4833 | 35.3112 | 36.7749 | 35.6007 | 34.2166 | 34.6417 | 34.9872 | 34.3669 | 34.6923 | 37.6592 | 37.276 | 34.6637 | 34.5651 | 37.2751 | 36.9959 | 38.4828 | 37.2927 | 35.6033 | 36.3956 | 37.8132 | 37.3874 | 35.8672 | 34.9327 | 34.2163 | 35.7157 | 33.6479 | 34.072 | 33.9597 | 34.894 | 33.6808 | 34.609 | 36.262 | 34.1358 | 34.4246 | 35.9533 | 93.2576 | 93.4475 | 93.161
2022-09-07 22:54 | 1:04 | 22.7762 | 23.0502 | 24.7654 | 38.0401 | 34.3838 | 36.0038 | 35.3958 | 35.6726 | 36.9777 | 36.1104 | 35.4878 | 35.9635 | 35.4427 | 36.0372 | 36.6574 | 35.8081 | 38.3903 | 36.8023 | 37.3738 | 37.8956 | 28.6728 | 23.6327 | 93.6545 | 36.3799 | 35.3014 | 36.7687 | 35.6072 | 34.1897 | 34.6424 | 34.9958 | 34.3551 | 34.6914 | 37.661 | 37.2724 | 34.66 | 34.5615 | 37.249 | 36.9908 | 38.4874 | 37.2736 | 35.592 | 36.3863 | 37.7983 | 37.3676 | 35.8541 | 34.9213 | 34.2164 | 35.7227 | 33.6447 | 34.0823 | 33.9474 | 34.9044 | 33.686 | 34.6066 | 36.2428 | 34.1419 | 34.4277 | 35.9457 | 93.2188 | 93.3081 | 93.2131
2022-09-07 22:54 | 1:04 | 22.6461 | 22.9483 | 24.719 | 37.9769 | 34.3691 | 36.0067 | 35.3967 | 35.68 | 36.9788 | 36.1313 | 35.492 | 35.9916 | 35.4324 | 36.0145 | 36.6602 | 35.8155 | 38.3948 | 36.8345 | 37.3906 | 37.8947 | 28.6561 | 23.6336 | 93.7534 | 36.2563 | 35.3263 | 36.7644 | 35.5883 | 34.1916 | 34.6631 | 35.0018 | 34.3687 | 34.6931 | 37.6718 | 37.274 | 34.6825 | 34.5876 | 37.276 | 36.9895 | 38.4873 | 37.2911 | 35.582 | 36.38 | 37.7794 | 37.3764 | 35.868 | 34.9249 | 34.2036 | 35.7056 | 33.636 | 34.0837 | 33.9495 | 34.886 | 33.6883 | 34.619 | 36.2541 | 34.1742 | 34.4434 | 35.9545 | 93.0968 | 93.2055 | 93.0698
2022-09-07 22:54 | 1:04 | 22.6468 | 22.9787 | 24.7293 | 37.878 | 34.3882 | 36.0316 | 35.3928 | 35.6832 | 36.9737 | 36.1406 | 35.52 | 35.9809 | 35.4351 | 36.0381 | 36.6671 | 35.8208 | 38.3532 | 36.8326 | 37.3888 | 37.9216 | 28.5969 | 23.5618 | 93.8311 | 36.4206 | 35.321 | 36.7682 | 35.5843 | 34.2006 | 34.6733 | 35.0281 | 34.3696 | 34.7202 | 37.6786 | 37.2829 | 34.6632 | 34.5816 | 37.2724 | 36.9918 | 38.5031 | 37.2751 | 35.6028 | 36.3577 | 37.7744 | 37.3698 | 35.857 | 34.9298 | 34.1947 | 35.7116 | 33.6299 | 34.0675 | 33.9344 | 34.8903 | 33.7191 | 34.6177 | 36.2525 | 34.1504 | 34.4562 | 35.9553 | 92.9222 | 93.0551 | 92.8857
2022-09-07 22:55 | 1:05 | 22.638 | 22.969 | 24.7052 | 37.9607 | 34.3808 | 36.0126 | 35.4238 | 35.6882 | 36.9766 | 36.1574 | 35.5077 | 35.9873 | 35.4341 | 36.0309 | 36.6594 | 35.8183 | 38.3805 | 36.8319 | 37.3996 | 37.8918 | 28.5817 | 23.5479 | 93.8804 | 36.4688 | 35.3218 | 36.7424 | 35.6033 | 34.2013 | 34.6637 | 35.0258 | 34.3926 | 34.715 | 37.6616 | 37.2526 | 34.6688 | 34.5812 | 37.274 | 37.0182 | 38.483 | 37.249 | 35.5936 | 36.3296 | 37.7645 | 37.3403 | 35.8278 | 34.9312 | 34.1823 | 35.715 | 33.6565 | 34.0577 | 33.9147 | 34.9027 | 33.6891 | 34.6104 | 36.2784 | 34.1718 | 34.4756 | 35.9397 | 92.8556 | 92.9808 | 92.8863
2022-09-07 22:55 | 1:05 | 22.6103 | 22.8907 | 24.6773 | 38.0675 | 34.3751 | 36.0273 | 35.4148 | 35.7045 | 36.9797 | 36.1494 | 35.5091 | 36.0214 | 35.4342 | 36.0109 | 36.6517 | 35.832 | 38.3766 | 36.8485 | 37.4027 | 37.9008 | 28.5754 | 23.5057 | 93.9532 | 36.248 | 35.3176 | 36.7637 | 35.592 | 34.2163 | 34.66 | 35.0359 | 34.3752 | 34.7029 | 37.6753 | 37.2625 | 34.6771 | 34.5813 | 37.2829 | 37.0024 | 38.5036 | 37.276 | 35.5783 | 36.3454 | 37.7563 | 37.329 | 35.8148 | 34.903 | 34.1877 | 35.7037 | 33.6559 | 34.0819 | 33.9442 | 34.8658 | 33.7015 | 34.6278 | 36.2791 | 34.1823 | 34.4818 | 35.9359 | 92.7157 | 92.8583 | 92.7593
2022-09-07 22:55 | 1:05 | 22.5109 | 22.7804 | 24.6071 | 37.9956 | 34.395 | 36.0208 | 35.419 | 35.6981 | 36.9873 | 36.1684 | 35.509 | 36.0172 | 35.4324 | 35.9981 | 36.6698 | 35.8273 | 38.371 | 36.8376 | 37.4102 | 37.9138 | 28.5725 | 23.464 | 94.04 | 36.248 | 35.3374 | 36.752 | 35.582 | 34.2086 | 34.6825 | 35.0395 | 34.3877 | 34.7093 | 37.7149 | 37.2648 | 34.6687 | 34.5911 | 37.2526 | 37.0232 | 38.5025 | 37.2724 | 35.5722 | 36.3363 | 37.724 | 37.3452 | 35.8105 | 34.9278 | 34.1735 | 35.6975 | 33.6534 | 34.0743 | 33.9416 | 34.8938 | 33.6933 | 34.648 | 36.2801 | 34.1791 | 34.4855 | 35.9551 | 92.6374 | 92.77 | 92.8064
2022-09-07 22:55 | 1:05 | 22.6114 | 22.7981 | 24.5497 | 37.9899 | 34.3845 | 36.0328 | 35.4243 | 35.7283 | 37.0036 | 36.1638 | 35.5288 | 36.0138 | 35.4241 | 35.9935 | 36.6695 | 35.8413 | 38.3606 | 36.8553 | 37.4013 | 37.9234 | 28.5688 | 23.462 | 94.1508 | 36.3562 | 35.3204 | 36.7581 | 35.6028 | 34.2123 | 34.6632 | 35.0239 | 34.3907 | 34.7184 | 37.6921 | 37.264 | 34.6831 | 34.5908 | 37.2625 | 37.021 | 38.4903 | 37.274 | 35.5943 | 36.3073 | 37.7335 | 37.3451 | 35.8008 | 34.9166 | 34.178 | 35.6772 | 33.6522 | 34.063 | 33.9406 | 34.8989 | 33.7104 | 34.6285 | 36.27 | 34.1843 | 34.484 | 35.9458 | 92.5329 | 92.6968 | 92.6557
2022-09-07 22:55 | 1:05 | 22.529 | 22.7868 | 24.544 | 37.7906 | 34.4157 | 36.0401 | 35.455 | 35.7339 | 37.0059 | 36.1586 | 35.544 | 36.0261 | 35.4339 | 35.9782 | 36.6818 | 35.8384 | 38.361 | 36.8473 | 37.4161 | 37.9165 | 28.5839 | 23.4524 | 94.2745 | 36.3783 | 35.3208 | 36.7475 | 35.5936 | 34.221 | 34.6688 | 35.0472 | 34.3995 | 34.7024 | 37.6927 | 37.2539 | 34.6684 | 34.5985 | 37.2648 | 37.0294 | 38.4843 | 37.2829 | 35.5827 | 36.3169 | 37.7023 | 37.3207 | 35.7955 | 34.9144 | 34.2042 | 35.672 | 33.6676 | 34.0648 | 33.9433 | 34.8812 | 33.7058 | 34.6473 | 36.2866 | 34.1863 | 34.5153 | 35.9567 | 92.4273 | 92.5382 | 92.5763
2022-09-07 22:55 | 1:05 | 22.5266 | 22.7911 | 24.5042 | 37.9049 | 34.3896 | 36.0492 | 35.4412 | 35.7405 | 37.009 | 36.1672 | 35.5497 | 36.0358 | 35.4365 | 35.9699 | 36.684 | 35.8537 | 38.3501 | 36.8742 | 37.4114 | 37.9256 | 28.52 | 23.4173 | 94.3836 | 36.1997 | 35.3368 | 36.7651 | 35.5783 | 34.2384 | 34.6771 | 35.0581 | 34.3838 | 34.7126 | 37.7072 | 37.249 | 34.6904 | 34.6043 | 37.264 | 37.017 | 38.4975 | 37.2526 | 35.5708 | 36.294 | 37.6978 | 37.3207 | 35.8075 | 34.9102 | 34.1786 | 35.68 | 33.6588 | 34.0939 | 33.9416 | 34.8725 | 33.6798 | 34.6626 | 36.2887 | 34.2067 | 34.4859 | 35.9611 | 92.3264 | 92.408 | 92.507
2022-09-07 22:56 | 1:05 | 22.4466 | 22.7381 | 24.4629 | 37.7988 | 34.3979 | 36.0487 | 35.4416 | 35.7488 | 37.0162 | 36.1784 | 35.5438 | 36.0495 | 35.4184 | 35.9568 | 36.6698 | 35.8531 | 38.3449 | 36.8565 | 37.4144 | 37.926 | 28.4531 | 23.416 | 94.5263 | 36.1431 | 35.3386 | 36.7343 | 35.5722 | 34.2273 | 34.6687 | 35.0678 | 34.4014 | 34.7126 | 37.691 | 37.2542 | 34.7036 | 34.5971 | 37.2539 | 37.0423 | 38.4992 | 37.2625 | 35.5838 | 36.265 | 37.6642 | 37.3164 | 35.7897 | 34.8826 | 34.1873 | 35.6829 | 33.6554 | 34.1001 | 33.9416 | 34.8759 | 33.7029 | 34.6626 | 36.2802 | 34.2194 | 34.5125 | 35.9485 | 92.1597 | 92.293 | 92.3124
2022-09-07 22:56 | 1:06 | 22.4747 | 22.7069 | 24.4525 | 37.8036 | 34.402 | 36.0363 | 35.4609 | 35.7646 | 37.005 | 36.179 | 35.5375 | 36.062 | 35.4172 | 35.9581 | 36.6557 | 35.8362 | 38.3261 | 36.8556 | 37.4266 | 37.9305 | 28.3856 | 23.3656 | 94.6387 | 36.1325 | 35.3329 | 36.7372 | 35.5943 | 34.2126 | 34.6831 | 35.0823 | 34.4102 | 34.7155 | 37.6966 | 37.2349 | 34.6919 | 34.6018 | 37.249 | 37.0334 | 38.4991 | 37.2648 | 35.5811 | 36.2717 | 37.6589 | 37.3086 | 35.7665 | 34.903 | 34.1628 | 35.6672 | 33.663 | 34.0814 | 33.9278 | 34.8784 | 33.6883 | 34.647 | 36.2588 | 34.2013 | 34.5082 | 35.9367 | 92.1172 | 92.2621 | 92.3611
2022-09-07 22:56 | 1:06 | 22.4367 | 22.6915 | 24.4578 | 37.8012 | 34.4128 | 36.0462 | 35.4553 | 35.7572 | 37.002 | 36.1974 | 35.5427 | 36.0629 | 35.4286 | 35.952 | 36.6782 | 35.8705 | 38.3436 | 36.8571 | 37.4114 | 37.924 | 28.3543 | 23.368 | 94.7825 | 36.0654 | 35.3314 | 36.7484 | 35.5827 | 34.2379 | 34.6684 | 35.1028 | 34.4033 | 34.7252 | 37.694 | 37.2411 | 34.719 | 34.6063 | 37.2542 | 37.0329 | 38.4832 | 37.264 | 35.5709 | 36.2467 | 37.6474 | 37.2936 | 35.7671 | 34.8781 | 34.1627 | 35.6643 | 33.67 | 34.0878 | 33.9387 | 34.8616 | 33.7033 | 34.668 | 36.2807 | 34.2317 | 34.5358 | 35.9448 | 92.2856 | 92.3432 | 92.5796
2022-09-07 22:56 | 1:06 | 22.4199 | 22.6453 | 24.4146 | 37.7624 | 34.4126 | 36.0702 | 35.468 | 35.7656 | 37.0328 | 36.1981 | 35.5585 | 36.0578 | 35.4215 | 35.9323 | 36.6643 | 35.863 | 38.3447 | 36.8747 | 37.4218 | 37.9249 | 28.312 | 23.3443 | 94.8781 | 36.0683 | 35.3327 | 36.7588 | 35.5708 | 34.2333 | 34.6904 | 35.0863 | 34.4019 | 34.73 | 37.7179 | 37.2296 | 34.6885 | 34.627 | 37.2349 | 37.0468 | 38.5074 | 37.2539 | 35.5775 | 36.2514 | 37.6362 | 37.2875 | 35.747 | 34.8696 | 34.1692 | 35.6581 | 33.6489 | 34.0642 | 33.9394 | 34.8699 | 33.7005 | 34.6655 | 36.3022 | 34.2371 | 34.5165 | 35.9426 | 92.3652 | 92.4275 | 92.6457
2022-09-07 22:56 | 1:06 | 22.4225 | 22.6311 | 24.3736 | 37.8129 | 34.4018 | 36.056 | 35.4573 | 35.7578 | 37.0193 | 36.1992 | 35.5715 | 36.0844 | 35.4149 | 35.9263 | 36.6683 | 35.8729 | 38.3198 | 36.8687 | 37.4338 | 37.9328 | 28.2566 | 23.3592 | 94.948 | 36.0195 | 35.3371 | 36.7402 | 35.5838 | 34.2537 | 34.7036 | 35.1082 | 34.4122 | 34.737 | 37.7077 | 37.2062 | 34.7115 | 34.6308 | 37.2411 | 37.0562 | 38.4922 | 37.249 | 35.5907 | 36.2429 | 37.6141 | 37.2847 | 35.7513 | 34.8875 | 34.178 | 35.6514 | 33.6655 | 34.0741 | 33.9337 | 34.8711 | 33.701 | 34.6755 | 36.3086 | 34.2281 | 34.5131 | 35.9336 | 92.4022 | 92.5011 | 92.553
2022-09-07 22:56 | 1:06 | 22.3875 | 22.6235 | 24.3591 | 37.6452 | 34.4228 | 36.0611 | 35.4755 | 35.7498 | 37.0218 | 36.2097 | 35.5658 | 36.0807 | 35.4033 | 35.9036 | 36.6738 | 35.8788 | 38.3107 | 36.8807 | 37.4197 | 37.9406 | 28.2263 | 23.3434 | 95.0879 | 36.0206 | 35.3419 | 36.7562 | 35.5811 | 34.2618 | 34.6919 | 35.1058 | 34.4162 | 34.7236 | 37.6816 | 37.233 | 34.7007 | 34.6355 | 37.2296 | 37.0597 | 38.4777 | 37.2542 | 35.5731 | 36.249 | 37.6098 | 37.285 | 35.7585 | 34.8644 | 34.158 | 35.6289 | 33.658 | 34.0849 | 33.9345 | 34.8585 | 33.6839 | 34.6704 | 36.289 | 34.2348 | 34.5437 | 35.9444 | 92.4081 | 92.5719 | 92.6022
2022-09-07 22:57 | 1:07 | 22.3334 | 22.531 | 24.3159 | 37.8105 | 34.3824 | 36.0548 | 35.474 | 35.757 | 37.0272 | 36.2151 | 35.5715 | 36.1002 | 35.4115 | 35.8959 | 36.6626 | 35.8939 | 38.3193 | 36.8799 | 37.4298 | 37.9272 | 28.1935 | 23.2804 | 95.1513 | 36.1901 | 35.3434 | 36.7416 | 35.5709 | 34.262 | 34.719 | 35.1224 | 34.4485 | 34.7294 | 37.6968 | 37.224 | 34.6952 | 34.6127 | 37.2062 | 37.0666 | 38.4935 | 37.2349 | 35.5771 | 36.2164 | 37.6132 | 37.2569 | 35.7359 | 34.8592 | 34.1568 | 35.6415 | 33.6606 | 34.0983 | 33.9336 | 34.866 | 33.7095 | 34.6781 | 36.2955 | 34.2462 | 34.5393 | 35.9206 | 92.4906 | 92.6506 | 92.6806
2022-09-07 22:57 | 1:07 | 22.3647 | 22.552 | 24.3222 | 37.6404 | 34.3959 | 36.0564 | 35.4792 | 35.773 | 37.0282 | 36.2046 | 35.5796 | 36.1074 | 35.4139 | 35.8875 | 36.6624 | 35.8649 | 38.3027 | 36.8651 | 37.4231 | 37.9295 | 28.173 | 23.2552 | 95.1806 | 36.0455 | 35.3353 | 36.7496 | 35.5775 | 34.263 | 34.6885 | 35.102 | 34.4153 | 34.7411 | 37.6939 | 37.2275 | 34.6947 | 34.6257 | 37.233 | 37.0723 | 38.4785 | 37.2411 | 35.5572 | 36.2192 | 37.6039 | 37.2721 | 35.7385 | 34.8631 | 34.1442 | 35.6444 | 33.6513 | 34.0673 | 33.9183 | 34.8709 | 33.7029 | 34.6742 | 36.2947 | 34.2541 | 34.5508 | 35.9068 | 92.6018 | 92.7799 | 92.7031
2022-09-07 22:57 | 1:07 | 22.2372 | 22.4205 | 24.2156 | 37.6845 | 34.4124 | 36.0719 | 35.4708 | 35.7925 | 37.0401 | 36.2158 | 35.5839 | 36.1074 | 35.4028 | 35.8808 | 36.6696 | 35.887 | 38.3184 | 36.8855 | 37.429 | 37.9393 | 28.1175 | 23.2154 | 95.1167 | 36.0357 | 35.357 | 36.7536 | 35.5907 | 34.2716 | 34.7115 | 35.123 | 34.423 | 34.7371 | 37.7195 | 37.254 | 34.7075 | 34.644 | 37.224 | 37.0698 | 38.4899 | 37.2296 | 35.5555 | 36.1789 | 37.5824 | 37.2381 | 35.7306 | 34.8613 | 34.1378 | 35.6297 | 33.6401 | 34.0873 | 33.9353 | 34.8431 | 33.6778 | 34.6829 | 36.2957 | 34.258 | 34.5579 | 35.9053 | 92.7159 | 92.8731 | 92.7948
2022-09-07 22:57 | 1:07 | 22.2162 | 22.4128 | 24.2076 | 37.5534 | 34.4016 | 36.0858 | 35.5031 | 35.7825 | 37.0151 | 36.2161 | 35.5827 | 36.1004 | 35.3729 | 35.8791 | 36.6595 | 35.8909 | 38.3078 | 36.8924 | 37.4223 | 37.9264 | 28.0786 | 23.1662 | 94.9677 | 35.9341 | 35.3452 | 36.7424 | 35.5731 | 34.2684 | 34.7007 | 35.1171 | 34.4332 | 34.7493 | 37.6965 | 37.2275 | 34.7184 | 34.6311 | 37.2275 | 37.0788 | 38.4799 | 37.2062 | 35.5667 | 36.1759 | 37.5496 | 37.2494 | 35.7141 | 34.8518 | 34.1312 | 35.6211 | 33.6296 | 34.0929 | 33.9302 | 34.8454 | 33.6833 | 34.6754 | 36.2998 | 34.2639 | 34.5561 | 35.9115 | 92.7814 | 93.0017 | 92.7974
2022-09-07 22:57 | 1:07 | 22.1853 | 22.4343 | 24.1814 | 37.6095 | 34.4033 | 36.0777 | 35.5046 | 35.803 | 37.0391 | 36.2011 | 35.5786 | 36.1136 | 35.3733 | 35.8626 | 36.6537 | 35.879 | 38.2717 | 36.8922 | 37.4137 | 37.9135 | 28.0709 | 23.1032 | 94.8598 | 35.975 | 35.3297 | 36.7394 | 35.5771 | 34.2776 | 34.6952 | 35.1229 | 34.4358 | 34.7327 | 37.6949 | 37.2523 | 34.7153 | 34.6423 | 37.254 | 37.0671 | 38.471 | 37.233 | 35.5459 | 36.1583 | 37.551 | 37.2094 | 35.7048 | 34.8599 | 34.1397 | 35.613 | 33.6325 | 34.0782 | 33.9102 | 34.8288 | 33.6884 | 34.6556 | 36.3129 | 34.2756 | 34.5625 | 35.9049 | 92.9178 | 93.1158 | 92.9411
2022-09-07 22:57 | 1:07 | 22.0873 | 22.3902 | 24.1474 | 37.6419 | 34.4006 | 36.0871 | 35.5073 | 35.8031 | 37.0199 | 36.2213 | 35.5886 | 36.134 | 35.3792 | 35.8297 | 36.654 | 35.9018 | 38.2717 | 36.8808 | 37.4209 | 37.9073 | 28.0431 | 23.0957 | 94.7697 | 36.1162 | 35.3514 | 36.7429 | 35.5572 | 34.2701 | 34.6947 | 35.1356 | 34.4222 | 34.7488 | 37.7034 | 37.225 | 34.721 | 34.6392 | 37.2275 | 37.0823 | 38.4719 | 37.224 | 35.5715 | 36.1521 | 37.5399 | 37.2196 | 35.7126 | 34.8063 | 34.1438 | 35.6118 | 33.6496 | 34.0868 | 33.9022 | 34.8518 | 33.6799 | 34.667 | 36.3199 | 34.2802 | 34.5534 | 35.8824 | 92.9785 | 93.2351 | 92.9182
2022-09-07 22:58 | 1:08 | 22.144 | 22.3456 | 24.1342 | 37.5852 | 34.3608 | 36.0742 | 35.5076 | 35.7993 | 37.0301 | 36.2134 | 35.5977 | 36.126 | 35.3807 | 35.8391 | 36.6507 | 35.8932 | 38.2807 | 36.8863 | 37.4277 | 37.9284 | 28.0243 | 23.0235 | 94.7008 | 35.8833 | 35.3346 | 36.7346 | 35.5555 | 34.2772 | 34.7075 | 35.1314 | 34.4667 | 34.746 | 37.7094 | 37.2264 | 34.7101 | 34.6604 | 37.2523 | 37.0955 | 38.4735 | 37.2275 | 35.5806 | 36.1539 | 37.5264 | 37.1986 | 35.6977 | 34.8385 | 34.1391 | 35.591 | 33.6374 | 34.1037 | 33.9273 | 34.8328 | 33.6658 | 34.6559 | 36.2997 | 34.3007 | 34.5626 | 35.8903 | 93.1258 | 93.3491 | 93.0614
2022-09-07 22:58 | 1:08 | 22.1142 | 22.2991 | 24.0614 | 37.546 | 34.3946 | 36.0796 | 35.5192 | 35.7922 | 37.0523 | 36.2232 | 35.6285 | 36.1401 | 35.3667 | 35.8122 | 36.6427 | 35.8959 | 38.2766 | 36.8811 | 37.4284 | 37.9053 | 27.9909 | 23.012 | 94.6499 | 35.9365 | 35.3339 | 36.7233 | 35.5667 | 34.2816 | 34.7184 | 35.1398 | 34.4389 | 34.7377 | 37.7057 | 37.2413 | 34.7132 | 34.6449 | 37.225 | 37.0918 | 38.4624 | 37.254 | 35.5813 | 36.1461 | 37.4897 | 37.1928 | 35.7199 | 34.8324 | 34.1199 | 35.6086 | 33.6362 | 34.0772 | 33.929 | 34.8363 | 33.6854 | 34.6637 | 36.3112 | 34.2979 | 34.58 | 35.9079 | 93.2062 | 93.4487 | 93.0847
2022-09-07 22:58 | 1:08 | 22.047 | 22.2756 | 24.0248 | 37.6068 | 34.3921 | 36.0727 | 35.5115 | 35.7887 | 37.0445 | 36.2456 | 35.6351 | 36.139 | 35.3567 | 35.8116 | 36.6585 | 35.9106 | 38.2687 | 36.8899 | 37.4321 | 37.9211 | 27.9775 | 22.9952 | 94.6634 | 35.87 | 35.3321 | 36.7387 | 35.5459 | 34.2925 | 34.7153 | 35.1552 | 34.4562 | 34.7567 | 37.7144 | 37.2459 | 34.727 | 34.6425 | 37.2264 | 37.094 | 38.4627 | 37.2275 | 35.573 | 36.1431 | 37.4943 | 37.1961 | 35.6784 | 34.8381 | 34.1314 | 35.5894 | 33.6225 | 34.0847 | 33.9121 | 34.8327 | 33.6784 | 34.6605 | 36.3101 | 34.3125 | 34.593 | 35.8824 | 93.3238 | 93.5746 | 93.1727
2022-09-07 22:58 | 1:08 | 22.0368 | 22.2709 | 24.0116 | 37.4759 | 34.3832 | 36.0914 | 35.5373 | 35.8201 | 37.0466 | 36.2345 | 35.6392 | 36.1463 | 35.3448 | 35.8234 | 36.6469 | 35.9137 | 38.2698 | 36.8951 | 37.4491 | 37.9107 | 27.9543 | 22.9775 | 94.6337 | 35.9635 | 35.334 | 36.7499 | 35.5715 | 34.3093 | 34.721 | 35.148 | 34.4492 | 34.7418 | 37.7103 | 37.2383 | 34.7092 | 34.6711 | 37.2413 | 37.0952 | 38.4621 | 37.2523 | 35.5843 | 36.1476 | 37.4747 | 37.1802 | 35.6963 | 34.8394 | 34.1341 | 35.5932 | 33.6356 | 34.1038 | 33.9269 | 34.8312 | 33.6769 | 34.6563 | 36.3229 | 34.3201 | 34.5811 | 35.8625 | 93.4581 | 93.7299 | 93.3634
2022-09-07 22:58 | 1:08 | 22.1197 | 22.2945 | 24.0234 | 37.53 | 34.382 | 36.1059 | 35.5318 | 35.8297 | 37.0453 | 36.2437 | 35.6562 | 36.1748 | 35.3597 | 35.7955 | 36.6568 | 35.9188 | 38.2444 | 36.8951 | 37.4303 | 37.9288 | 27.9354 | 22.9835 | 94.6522 | 35.8263 | 35.3227 | 36.7345 | 35.5806 | 34.2986 | 34.7101 | 35.1625 | 34.4463 | 34.7473 | 37.7288 | 37.2338 | 34.7282 | 34.6651 | 37.2459 | 37.1001 | 38.4522 | 37.225 | 35.5747 | 36.1363 | 37.4713 | 37.1782 | 35.6908 | 34.8294 | 34.1374 | 35.5599 | 33.6281 | 34.1022 | 33.9246 | 34.8331 | 33.6788 | 34.6762 | 36.3231 | 34.3186 | 34.5763 | 35.8745 | 93.5649 | 93.8675 | 93.3795
2022-09-07 22:58 | 1:08 | 22.0393 | 22.2725 | 23.9997 | 37.4454 | 34.3957 | 36.1247 | 35.5334 | 35.8155 | 37.0545 | 36.2431 | 35.6495 | 36.1839 | 35.3601 | 35.8049 | 36.6466 | 35.9212 | 38.2502 | 36.8975 | 37.4292 | 37.9172 | 27.9078 | 22.8895 | 94.6487 | 35.8887 | 35.3441 | 36.7431 | 35.5813 | 34.3058 | 34.7132 | 35.1663 | 34.4663 | 34.7665 | 37.7142 | 37.2252 | 34.7356 | 34.6765 | 37.2383 | 37.1188 | 38.4661 | 37.2264 | 35.5575 | 36.1242 | 37.4765 | 37.1877 | 35.7036 | 34.8501 | 34.114 | 35.5745 | 33.6249 | 34.0972 | 33.9197 | 34.81 | 33.6867 | 34.6909 | 36.3094 | 34.3317 | 34.5918 | 35.8706 | 93.7319 | 94.0431 | 93.5087
2022-09-07 22:59 | 1:08 | 21.9513 | 22.1603 | 23.9402 | 37.4457 | 34.3792 | 36.0893 | 35.533 | 35.8384 | 37.0471 | 36.2504 | 35.6627 | 36.1822 | 35.3754 | 35.7754 | 36.6492 | 35.9333 | 38.2448 | 36.9039 | 37.443 | 37.9101 | 27.8935 | 22.8782 | 94.6022 | 35.768 | 35.3404 | 36.7404 | 35.573 | 34.3094 | 34.727 | 35.1655 | 34.4882 | 34.7808 | 37.7156 | 37.2268 | 34.739 | 34.6848 | 37.2338 | 37.108 | 38.4696 | 37.2413 | 35.5842 | 36.1291 | 37.4427 | 37.1749 | 35.6801 | 34.8056 | 34.137 | 35.569 | 33.6063 | 34.0947 | 33.8951 | 34.8166 | 33.6882 | 34.6906 | 36.3273 | 34.3172 | 34.5964 | 35.8653 | 93.8916 | 94.1843 | 93.5868
2022-09-07 22:59 | 1:09 | 21.9344 | 22.1905 | 23.889 | 37.3823 | 34.3905 | 36.1166 | 35.55 | 35.8415 | 37.0506 | 36.2555 | 35.6447 | 36.2027 | 35.3392 | 35.7486 | 36.6487 | 35.9214 | 38.2317 | 36.9111 | 37.4496 | 37.9324 | 27.8565 | 22.8395 | 94.5771 | 35.8742 | 35.346 | 36.7426 | 35.5843 | 34.2984 | 34.7092 | 35.1726 | 34.4993 | 34.7689 | 37.7485 | 37.2341 | 34.7452 | 34.6807 | 37.2252 | 37.101 | 38.462 | 37.2459 | 35.5794 | 36.0996 | 37.4646 | 37.1578 | 35.675 | 34.84 | 34.1138 | 35.554 | 33.6279 | 34.111 | 33.9219 | 34.8233 | 33.6789 | 34.6877 | 36.3279 | 34.3286 | 34.591 | 35.8723 | 94.0446 | 94.3507 | 93.7187
2022-09-07 22:59 | 1:09 | 21.892 | 22.1322 | 23.8696 | 37.3674 | 34.3833 | 36.1034 | 35.555 | 35.8397 | 37.0319 | 36.2618 | 35.6652 | 36.2066 | 35.3539 | 35.7509 | 36.6499 | 35.9308 | 38.2405 | 36.9376 | 37.4335 | 37.9222 | 27.8289 | 22.8066 | 94.5473 | 35.8065 | 35.33 | 36.7407 | 35.5747 | 34.3091 | 34.7282 | 35.1821 | 34.4984 | 34.784 | 37.7358 | 37.2315 | 34.7391 | 34.7018 | 37.2268 | 37.1227 | 38.439 | 37.2383 | 35.5813 | 36.0914 | 37.4182 | 37.1492 | 35.6683 | 34.8085 | 34.1059 | 35.5625 | 33.624 | 34.0954 | 33.9239 | 34.8103 | 33.6821 | 34.6996 | 36.3422 | 34.3339 | 34.618 | 35.8659 | 94.2016 | 94.4852 | 93.8132
2022-09-07 22:59 | 1:09 | 21.8629 | 22.1117 | 23.8421 | 37.3109 | 34.386 | 36.1196 | 35.5616 | 35.843 | 37.0711 | 36.2606 | 35.6699 | 36.2074 | 35.3611 | 35.7483 | 36.6444 | 35.9547 | 38.235 | 36.9286 | 37.4569 | 37.9135 | 27.8095 | 22.7603 | 94.4722 | 35.8661 | 35.3439 | 36.7684 | 35.5575 | 34.3263 | 34.7356 | 35.2036 | 34.4943 | 34.7717 | 37.7159 | 37.2206 | 34.7394 | 34.7124 | 37.2341 | 37.1218 | 38.453 | 37.2338 | 35.5673 | 36.0914 | 37.4159 | 37.1401 | 35.6615 | 34.7924 | 34.0959 | 35.5565 | 33.6264 | 34.1024 | 33.9119 | 34.8139 | 33.6901 | 34.696 | 36.3497 | 34.3419 | 34.6112 | 35.8571 | 94.377 | 94.6318 | 93.8329
2022-09-07 22:59 | 1:09 | 21.9019 | 22.1491 | 23.823 | 37.3592 | 34.3804 | 36.1133 | 35.57 | 35.8695 | 37.0552 | 36.2833 | 35.684 | 36.2313 | 35.3698 | 35.761 | 36.6431 | 35.9537 | 38.2297 | 36.9412 | 37.4342 | 37.9075 | 27.7836 | 22.7816 | 94.4712 | 35.9128 | 35.3568 | 36.7468 | 35.5842 | 34.3285 | 34.739 | 35.2049 | 34.4978 | 34.795 | 37.7191 | 37.2449 | 34.7249 | 34.7144 | 37.2315 | 37.1433 | 38.4439 | 37.2252 | 35.5738 | 36.0671 | 37.4111 | 37.1491 | 35.6487 | 34.8104 | 34.1056 | 35.541 | 33.6286 | 34.1097 | 33.909 | 34.8048 | 33.6897 | 34.7052 | 36.3445 | 34.3549 | 34.6316 | 35.8753 | 94.4833 | 94.8381 | 94.0905
2022-09-07 22:59 | 1:09 | 21.8114 | 22.0371 | 23.7935 | 37.2241 | 34.3916 | 36.1032 | 35.5835 | 35.8631 | 37.0675 | 36.2529 | 35.6854 | 36.2212 | 35.3399 | 35.7252 | 36.6403 | 35.9509 | 38.2224 | 36.9246 | 37.4596 | 37.9081 | 27.7641 | 22.7417 | 94.4171 | 35.9479 | 35.3598 | 36.7484 | 35.5794 | 34.3232 | 34.7452 | 35.1927 | 34.5079 | 34.7754 | 37.7557 | 37.2285 | 34.7507 | 34.7034 | 37.2206 | 37.1241 | 38.4503 | 37.2268 | 35.5669 | 36.0693 | 37.3974 | 37.1525 | 35.6604 | 34.8053 | 34.0854 | 35.5398 | 33.6217 | 34.1125 | 33.9053 | 34.8308 | 33.6743 | 34.7232 | 36.3222 | 34.3676 | 34.6354 | 35.8599 | 94.6768 | 95.0311 | 94.2011
2022-09-07 23:00 | 1:10 | 21.8376 | 22.0942 | 23.774 | 37.2707 | 34.3751 | 36.1289 | 35.5724 | 35.8793 | 37.0624 | 36.2841 | 35.7034 | 36.2372 | 35.3404 | 35.7166 | 36.6321 | 35.9509 | 38.2186 | 36.9425 | 37.4441 | 37.9096 | 27.756 | 22.7161 | 94.3598 | 35.9347 | 35.3588 | 36.7586 | 35.5813 | 34.3213 | 34.7391 | 35.2007 | 34.536 | 34.7805 | 37.7321 | 37.2406 | 34.7411 | 34.7094 | 37.2449 | 37.1234 | 38.4517 | 37.2341 | 35.5697 | 36.0576 | 37.3854 | 37.11 | 35.6585 | 34.8197 | 34.0793 | 35.5251 | 33.6336 | 34.1016 | 33.9312 | 34.7985 | 33.6689 | 34.7078 | 36.3518 | 34.336 | 34.6465 | 35.8581 | 94.8114 | 95.1949 | 94.3364
2022-09-07 23:00 | 1:10 | 21.7705 | 21.9955 | 23.7289 | 37.3652 | 34.3748 | 36.1187 | 35.5881 | 35.8667 | 37.0894 | 36.2576 | 35.7126 | 36.2446 | 35.3569 | 35.705 | 36.6384 | 35.9731 | 38.221 | 36.9496 | 37.4524 | 37.9058 | 27.7283 | 22.6349 | 94.2897 | 35.7936 | 35.3615 | 36.7494 | 35.5673 | 34.3423 | 34.7394 | 35.2123 | 34.5176 | 34.8127 | 37.7385 | 37.2347 | 34.7625 | 34.7064 | 37.2285 | 37.1391 | 38.4523 | 37.2315 | 35.5488 | 36.0493 | 37.375 | 37.1328 | 35.6407 | 34.7932 | 34.1095 | 35.5254 | 33.6307 | 34.1197 | 33.893 | 34.7922 | 33.7007 | 34.7254 | 36.3534 | 34.3661 | 34.6462 | 35.8583 | 94.9607 | 95.3523 | 94.3954
2022-09-07 23:00 | 1:10 | 21.7098 | 21.9547 | 23.6763 | 37.2178 | 34.3827 | 36.1352 | 35.5979 | 35.8912 | 37.0601 | 36.2677 | 35.725 | 36.2495 | 35.3628 | 35.7105 | 36.6543 | 35.9789 | 38.2246 | 36.9522 | 37.4633 | 37.9332 | 27.6881 | 22.6079 | 94.2705 | 35.7943 | 35.3595 | 36.7373 | 35.5738 | 34.3444 | 34.7249 | 35.2141 | 34.5139 | 34.7974 | 37.7425 | 37.2066 | 34.7513 | 34.7172 | 37.2406 | 37.1532 | 38.4484 | 37.2206 | 35.58 | 36.0506 | 37.3816 | 37.1423 | 35.6462 | 34.8023 | 34.08 | 35.5448 | 33.6431 | 34.1237 | 33.9121 | 34.8154 | 33.6644 | 34.7037 | 36.3652 | 34.3708 | 34.6571 | 35.8614 | 95.0045 | 95.4941 | 94.3994
2022-09-07 23:00 | 1:10 | 21.6852 | 21.9318 | 23.668 | 37.1869 | 34.3778 | 36.1244 | 35.5938 | 35.8839 | 37.067 | 36.2813 | 35.7209 | 36.2711 | 35.351 | 35.7225 | 36.6394 | 35.9626 | 38.211 | 36.9468 | 37.4691 | 37.928 | 27.6736 | 22.6011 | 94.2387 | 35.6897 | 35.3544 | 36.7362 | 35.5669 | 34.3327 | 34.7507 | 35.2336 | 34.5411 | 34.8203 | 37.7414 | 37.2238 | 34.7595 | 34.7272 | 37.2347 | 37.1511 | 38.4532 | 37.2449 | 35.5628 | 36.0237 | 37.3644 | 37.1342 | 35.6456 | 34.7904 | 34.0989 | 35.5338 | 33.6364 | 34.1221 | 33.8957 | 34.8031 | 33.6791 | 34.7132 | 36.3611 | 34.3688 | 34.6557 | 35.879 | 95.1343 | 95.6036 | 94.5449
2022-09-07 23:00 | 1:10 | 21.7663 | 21.9367 | 23.6005 | 37.2338 | 34.3774 | 36.148 | 35.5947 | 35.9071 | 37.0908 | 36.3051 | 35.7208 | 36.2867 | 35.3533 | 35.6799 | 36.6444 | 35.9581 | 38.2004 | 36.9772 | 37.4742 | 37.9198 | 27.6718 | 22.6417 | 94.179 | 35.744 | 35.3449 | 36.7381 | 35.5697 | 34.3435 | 34.7411 | 35.2387 | 34.5396 | 34.8199 | 37.7559 | 37.2285 | 34.7536 | 34.7452 | 37.2066 | 37.1724 | 38.4557 | 37.2285 | 35.5723 | 36.0296 | 37.3483 | 37.1492 | 35.6265 | 34.7751 | 34.101 | 35.5181 | 33.6424 | 34.1162 | 33.9254 | 34.7952 | 33.6978 | 34.7257 | 36.3663 | 34.3864 | 34.6671 | 35.8558 | 95.1552 | 95.6407 | 94.6266
2022-09-07 23:00 | 1:10 | 21.6933 | 21.941 | 23.6376 | 37.2703 | 34.39 | 36.136 | 35.5971 | 35.8934 | 37.0894 | 36.285 | 35.7364 | 36.2734 | 35.3502 | 35.6931 | 36.6501 | 35.9642 | 38.225 | 36.95 | 37.4635 | 37.93 | 27.6624 | 22.5766 | 94.089 | 35.7897 | 35.3573 | 36.7417 | 35.5488 | 34.337 | 34.7625 | 35.2566 | 34.5347 | 34.8281 | 37.7616 | 37.2384 | 34.7558 | 34.7214 | 37.2238 | 37.1457 | 38.4758 | 37.2406 | 35.5544 | 36.0165 | 37.357 | 37.1256 | 35.6321 | 34.7953 | 34.0844 | 35.5233 | 33.6532 | 34.1149 | 33.9116 | 34.8054 | 33.6798 | 34.7224 | 36.3715 | 34.3744 | 34.653 | 35.8637 | 95.1914 | 95.7477 | 94.5664
2022-09-07 23:01 | 1:10 | 21.6204 | 21.8372 | 23.56 | 37.2667 | 34.3799 | 36.1545 | 35.5996 | 35.9003 | 37.0904 | 36.3051 | 35.7347 | 36.3011 | 35.3439 | 35.6797 | 36.6215 | 35.9915 | 38.2116 | 36.952 | 37.4751 | 37.9278 | 27.6321 | 22.5092 | 93.9728 | 35.6617 | 35.3671 | 36.7372 | 35.58 | 34.3628 | 34.7513 | 35.2429 | 34.5541 | 34.8093 | 37.7489 | 37.2061 | 34.7602 | 34.72 | 37.2285 | 37.1648 | 38.4665 | 37.2347 | 35.5752 | 36.0346 | 37.3465 | 37.1369 | 35.6173 | 34.7918 | 34.0859 | 35.5062 | 33.6475 | 34.1277 | 33.9306 | 34.8211 | 33.6953 | 34.7422 | 36.3711 | 34.4045 | 34.6674 | 35.8436 | 95.1217 | 95.6156 | 94.5557
2022-09-07 23:01 | 1:11 | 21.4698 | 21.7793 | 23.5096 | 37.0819 | 34.3711 | 36.1543 | 35.6118 | 35.9107 | 37.1001 | 36.2957 | 35.7463 | 36.2941 | 35.346 | 35.6634 | 36.6632 | 35.9974 | 38.2078 | 36.978 | 37.4781 | 37.9402 | 27.5935 | 22.4794 | 93.8611 | 35.6551 | 35.3575 | 36.7456 | 35.5628 | 34.3739 | 34.7595 | 35.2517 | 34.5632 | 34.8216 | 37.7596 | 37.2293 | 34.772 | 34.7569 | 37.2384 | 37.1718 | 38.4374 | 37.2066 | 35.5713 | 36.0079 | 37.3358 | 37.1419 | 35.6023 | 34.7803 | 34.077 | 35.5168 | 33.6424 | 34.1233 | 33.9241 | 34.7992 | 33.6895 | 34.7471 | 36.3761 | 34.4117 | 34.6917 | 35.8635 | 94.9625 | 95.4012 | 94.3959
2022-09-07 23:01 | 1:11 | 21.5472 | 21.7882 | 23.4627 | 37.1042 | 34.3592 | 36.1556 | 35.6183 | 35.9072 | 37.1002 | 36.311 | 35.7581 | 36.322 | 35.3386 | 35.6401 | 36.636 | 36.0034 | 38.209 | 36.9871 | 37.4951 | 37.9224 | 27.5561 | 22.4161 | 93.7452 | 35.6892 | 35.3635 | 36.7496 | 35.5723 | 34.3651 | 34.7536 | 35.2737 | 34.5504 | 34.8253 | 37.755 | 37.2023 | 34.766 | 34.7429 | 37.2061 | 37.1879 | 38.4599 | 37.2238 | 35.5763 | 35.9987 | 37.3387 | 37.1087 | 35.6239 | 34.7664 | 34.0758 | 35.5334 | 33.6466 | 34.1014 | 33.9211 | 34.8026 | 33.6953 | 34.7462 | 36.3795 | 34.4193 | 34.6919 | 35.876 | 94.7116 | 95.0984 | 94.2398
2022-09-07 23:01 | 1:11 | 21.4383 | 21.6938 | 23.4238 | 37.124 | 34.3753 | 36.162 | 35.623 | 35.9109 | 37.0948 | 36.3222 | 35.753 | 36.3242 | 35.3577 | 35.6542 | 36.623 | 35.9929 | 38.1938 | 36.9846 | 37.4799 | 37.9308 | 27.5312 | 22.3699 | 93.5728 | 35.5959 | 35.3576 | 36.7711 | 35.5544 | 34.3741 | 34.7558 | 35.2472 | 34.5604 | 34.8197 | 37.7617 | 37.213 | 34.7769 | 34.7671 | 37.2293 | 37.1825 | 38.4396 | 37.2285 | 35.5708 | 35.9991 | 37.3167 | 37.1243 | 35.6043 | 34.7795 | 34.078 | 35.5155 | 33.6285 | 34.1295 | 33.94 | 34.804 | 33.7097 | 34.7646 | 36.373 | 34.426 | 34.691 | 35.8756 | 94.5681 | 94.8925 | 94.1256
2022-09-07 23:01 | 1:11 | 21.4046 | 21.6513 | 23.4136 | 37.1173 | 34.379 | 36.1735 | 35.6254 | 35.916 | 37.0955 | 36.3238 | 35.7621 | 36.321 | 35.3563 | 35.6397 | 36.644 | 36.004 | 38.1899 | 36.9846 | 37.4806 | 37.9342 | 27.5028 | 22.295 | 93.4152 | 35.617 | 35.3571 | 36.744 | 35.5752 | 34.3682 | 34.7602 | 35.2525 | 34.5731 | 34.8361 | 37.7754 | 37.2035 | 34.7584 | 34.7519 | 37.2023 | 37.1908 | 38.4555 | 37.2384 | 35.5462 | 35.9869 | 37.3019 | 37.1287 | 35.5861 | 34.7805 | 34.0669 | 35.5178 | 33.6439 | 34.1288 | 33.929 | 34.8057 | 33.6955 | 34.771 | 36.3922 | 34.4129 | 34.7061 | 35.8722 | 94.3893 | 94.7249 | 93.9295
2022-09-07 23:01 | 1:11 | 21.4472 | 21.6668 | 23.3458 | 37.1799 | 34.3739 | 36.1463 | 35.6223 | 35.9397 | 37.101 | 36.3261 | 35.7907 | 36.3285 | 35.3329 | 35.6476 | 36.6349 | 36.0142 | 38.1704 | 36.9776 | 37.4758 | 37.9273 | 27.5038 | 22.3121 | 93.2426 | 35.6689 | 35.3676 | 36.739 | 35.5713 | 34.384 | 34.772 | 35.2645 | 34.5765 | 34.8214 | 37.7711 | 37.2301 | 34.7621 | 34.7558 | 37.213 | 37.1883 | 38.4375 | 37.2061 | 35.5599 | 35.9943 | 37.3033 | 37.1219 | 35.5754 | 34.762 | 34.0862 | 35.5223 | 33.6482 | 34.1223 | 33.9219 | 34.8017 | 33.6751 | 34.7628 | 36.3749 | 34.4456 | 34.7075 | 35.8603 | 94.314 | 94.6042 | 93.9478
2022-09-07 23:02 | 1:12 | 21.356 | 21.5816 | 23.3051 | 37.1158 | 34.3625 | 36.1628 | 35.6255 | 35.9248 | 37.1162 | 36.3235 | 35.7667 | 36.3468 | 35.3248 | 35.622 | 36.6564 | 36.0097 | 38.1952 | 36.9896 | 37.4888 | 37.9231 | 27.481 | 22.2587 | 93.119 | 35.5973 | 35.3632 | 36.7325 | 35.5763 | 34.3875 | 34.766 | 35.2817 | 34.575 | 34.8538 | 37.7756 | 37.1946 | 34.7684 | 34.7879 | 37.2035 | 37.2061 | 38.4572 | 37.2293 | 35.565 | 35.9756 | 37.3022 | 37.131 | 35.5786 | 34.7479 | 34.0476 | 35.4884 | 33.6762 | 34.1367 | 33.939 | 34.8137 | 33.6981 | 34.7789 | 36.3705 | 34.4269 | 34.7192 | 35.8643 | 94.1828 | 94.4873 | 93.8631
2022-09-07 23:02 | 1:12 | 21.3628 | 21.6493 | 23.3346 | 37.063 | 34.3761 | 36.1385 | 35.6633 | 35.9437 | 37.1091 | 36.3383 | 35.7963 | 36.361 | 35.3504 | 35.5923 | 36.6525 | 36.0273 | 38.1868 | 36.9997 | 37.5015 | 37.9346 | 27.4577 | 22.2284 | 92.9398 | 35.6441 | 35.3589 | 36.7396 | 35.5708 | 34.3861 | 34.7769 | 35.2842 | 34.5706 | 34.8335 | 37.7766 | 37.2113 | 34.7943 | 34.7702 | 37.2301 | 37.2061 | 38.4457 | 37.2023 | 35.5525 | 35.9707 | 37.2787 | 37.1169 | 35.5816 | 34.746 | 34.0821 | 35.5005 | 33.6623 | 34.1436 | 33.9125 | 34.7889 | 33.7061 | 34.777 | 36.3815 | 34.4583 | 34.7308 | 35.8598 | 94.0937 | 94.368 | 93.813
2022-09-07 23:02 | 1:12 | 21.3047 | 21.5736 | 23.2623 | 37.0621 | 34.3713 | 36.1522 | 35.6482 | 35.9486 | 37.1099 | 36.3357 | 35.7932 | 36.3707 | 35.3291 | 35.6074 | 36.6428 | 36.0109 | 38.1872 | 36.9906 | 37.4972 | 37.9298 | 27.4226 | 22.1908 | 92.7793 | 35.516 | 35.3627 | 36.7365 | 35.5462 | 34.3931 | 34.7584 | 35.2916 | 34.5997 | 34.8386 | 37.7675 | 37.1983 | 34.7844 | 34.7891 | 37.1946 | 37.2064 | 38.444 | 37.213 | 35.5294 | 35.9591 | 37.2895 | 37.1381 | 35.5834 | 34.7281 | 34.0505 | 35.5023 | 33.6775 | 34.1098 | 33.9062 | 34.8082 | 33.6999 | 34.7794 | 36.3818 | 34.4344 | 34.7357 | 35.8716 | 94.0409 | 94.2598 | 93.7898
2022-09-07 23:02 | 1:12 | 21.2275 | 21.459 | 23.198 | 36.966 | 34.3649 | 36.1541 | 35.6576 | 35.9492 | 37.1137 | 36.3372 | 35.7769 | 36.3688 | 35.3316 | 35.5974 | 36.6389 | 36.0086 | 38.1826 | 36.9984 | 37.5109 | 37.9561 | 27.4214 | 22.1671 | 92.6899 | 35.3995 | 35.3783 | 36.7421 | 35.5599 | 34.3878 | 34.7621 | 35.283 | 34.5806 | 34.8381 | 37.7816 | 37.2094 | 34.7828 | 34.7753 | 37.2113 | 37.2093 | 38.4375 | 37.2035 | 35.5471 | 35.9517 | 37.2856 | 37.1029 | 35.5686 | 34.7575 | 34.0713 | 35.5048 | 33.6563 | 34.1161 | 33.9182 | 34.7892 | 33.6872 | 34.8125 | 36.3719 | 34.4681 | 34.7414 | 35.8741 | 94.0247 | 94.2411 | 93.7811
2022-09-07 23:02 | 1:12 | 21.2665 | 21.4539 | 23.1878 | 37.0409 | 34.3772 | 36.1562 | 35.6629 | 35.9574 | 37.1087 | 36.361 | 35.8113 | 36.3805 | 35.3276 | 35.5959 | 36.6248 | 36.028 | 38.1605 | 37.0052 | 37.5047 | 37.9568 | 27.4042 | 22.1258 | 92.7199 | 35.4206 | 35.3712 | 36.7376 | 35.565 | 34.3957 | 34.7684 | 35.308 | 34.5887 | 34.8501 | 37.7751 | 37.1844 | 34.767 | 34.797 | 37.1983 | 37.2071 | 38.4583 | 37.2301 | 35.5568 | 35.9655 | 37.276 | 37.1198 | 35.5651 | 34.7191 | 34.0793 | 35.5067 | 33.6687 | 34.1445 | 33.9244 | 34.8026 | 33.6958 | 34.7912 | 36.3801 | 34.4743 | 34.752 | 35.8768 | 93.9068 | 94.1592 | 93.6466
2022-09-07 23:02 | 1:12 | 21.3529 | 21.535 | 23.1737 | 37.0506 | 34.3707 | 36.1582 | 35.6583 | 35.9545 | 37.1194 | 36.3603 | 35.8131 | 36.3719 | 35.314 | 35.5736 | 36.6306 | 36.0406 | 38.1748 | 37.0116 | 37.5234 | 37.9416 | 27.3739 | 22.1851 | 92.8266 | 35.548 | 35.3761 | 36.7312 | 35.5525 | 34.3913 | 34.7943 | 35.3114 | 34.5897 | 34.854 | 37.7838 | 37.1918 | 34.7907 | 34.7853 | 37.2094 | 37.2238 | 38.459 | 37.1946 | 35.5334 | 35.9377 | 37.266 | 37.1329 | 35.5571 | 34.7325 | 34.0577 | 35.4837 | 33.6806 | 34.1376 | 33.9423 | 34.8167 | 33.7138 | 34.7812 | 36.376 | 34.478 | 34.7411 | 35.8816 | 93.8519 | 94.118 | 93.6057
2022-09-07 23:03 | 1:12 | 21.2272 | 21.434 | 23.1599 | 36.9701 | 34.3638 | 36.157 | 35.6789 | 35.9604 | 37.1084 | 36.3828 | 35.8175 | 36.389 | 35.3364 | 35.5759 | 36.6406 | 36.0358 | 38.1531 | 37.0205 | 37.4996 | 37.9447 | 27.331 | 22.1675 | 92.9347 | 35.5307 | 35.374 | 36.7465 | 35.5294 | 34.4034 | 34.7844 | 35.3161 | 34.5942 | 34.8602 | 37.7898 | 37.1945 | 34.7874 | 34.7901 | 37.1844 | 37.2289 | 38.4616 | 37.2113 | 35.5418 | 35.9468 | 37.2594 | 37.0996 | 35.5612 | 34.7152 | 34.06 | 35.4954 | 33.6634 | 34.128 | 33.928 | 34.7895 | 33.7133 | 34.8173 | 36.3819 | 34.5099 | 34.7622 | 35.8751 | 93.7904 | 94.017 | 93.6697
2022-09-07 23:03 | 1:13 | 21.1646 | 21.4056 | 23.1077 | 36.9452 | 34.3669 | 36.1425 | 35.6831 | 35.9468 | 37.1089 | 36.3653 | 35.8205 | 36.4036 | 35.3175 | 35.5581 | 36.6446 | 36.0365 | 38.1342 | 37.0421 | 37.5175 | 37.9319 | 27.3184 | 22.1278 | 93.0368 | 35.3647 | 35.3737 | 36.7321 | 35.5471 | 34.4098 | 34.7828 | 35.3195 | 34.6022 | 34.8599 | 37.7817 | 37.1891 | 34.7828 | 34.7912 | 37.1918 | 37.2211 | 38.4451 | 37.1983 | 35.5373 | 35.9219 | 37.2381 | 37.1115 | 35.5273 | 34.7345 | 34.0418 | 35.4722 | 33.6776 | 34.1517 | 33.9109 | 34.7897 | 33.7009 | 34.8129 | 36.3774 | 34.4776 | 34.7678 | 35.8726 | 93.7087 | 93.8865 | 93.6193
2022-09-07 23:03 | 1:13 | 21.0725 | 21.2863 | 23.053 | 36.938 | 34.3586 | 36.1578 | 35.6735 | 35.9809 | 37.1333 | 36.3732 | 35.8414 | 36.3903 | 35.3098 | 35.5592 | 36.6613 | 36.0252 | 38.1307 | 37.0367 | 37.5246 | 37.9755 | 27.2625 | 22.0638 | 93.0575 | 35.4234 | 35.3599 | 36.7118 | 35.5568 | 34.3865 | 34.767 | 35.3223 | 34.5931 | 34.8642 | 37.7766 | 37.1816 | 34.7884 | 34.7835 | 37.1945 | 37.2292 | 38.4386 | 37.2094 | 35.542 | 35.9198 | 37.2601 | 37.1167 | 35.529 | 34.7413 | 34.0554 | 35.4795 | 33.6772 | 34.1367 | 33.9057 | 34.7791 | 33.7285 | 34.8141 | 36.3585 | 34.4801 | 34.7747 | 35.8892 | 93.6203 | 93.7423 | 93.5961
2022-09-07 23:03 | 1:13 | 21.1202 | 21.2898 | 23.0101 | 36.9916 | 34.36 | 36.1461 | 35.6667 | 35.9573 | 37.1414 | 36.3713 | 35.8478 | 36.4222 | 35.3292 | 35.5622 | 36.6623 | 36.007 | 38.1312 | 37.0079 | 37.5173 | 37.9527 | 27.2573 | 22.0339 | 93.0862 | 35.5523 | 35.3685 | 36.7438 | 35.5334 | 34.3993 | 34.7907 | 35.3334 | 34.6222 | 34.8642 | 37.7937 | 37.1838 | 34.7861 | 34.7997 | 37.1891 | 37.2275 | 38.4509 | 37.1844 | 35.5389 | 35.8988 | 37.2327 | 37.1098 | 35.5245 | 34.7311 | 34.0438 | 35.4806 | 33.6819 | 34.1245 | 33.9035 | 34.792 | 33.6885 | 34.826 | 36.3764 | 34.4911 | 34.7736 | 35.8848 | 93.5605 | 93.6087 | 93.5418
2022-09-07 23:03 | 1:13 | 21.0231 | 21.254 | 22.9856 | 36.9476 | 34.3712 | 36.1684 | 35.6642 | 35.9711 | 37.1166 | 36.3794 | 35.8454 | 36.4141 | 35.303 | 35.5334 | 36.6488 | 36.0323 | 38.1284 | 37.0185 | 37.5135 | 37.9621 | 27.2378 | 22.0016 | 93.1449 | 35.3246 | 35.3686 | 36.7174 | 35.5418 | 34.42 | 34.7874 | 35.3247 | 34.6165 | 34.8453 | 37.7869 | 37.1593 | 34.7831 | 34.7987 | 37.1816 | 37.2424 | 38.4511 | 37.1918 | 35.5329 | 35.902 | 37.2282 | 37.0944 | 35.4992 | 34.7178 | 34.0348 | 35.4886 | 33.6923 | 34.1273 | 33.9276 | 34.8002 | 33.6893 | 34.8291 | 36.3879 | 34.4891 | 34.7782 | 35.8654 | 93.5196 | 93.5407 | 93.5748
2022-09-07 23:03 | 1:13 | 21.0332 | 21.267 | 22.9439 | 36.8041 | 34.342 | 36.1528 | 35.689 | 35.978 | 37.115 | 36.3995 | 35.8471 | 36.4244 | 35.2941 | 35.5337 | 36.6364 | 36.0431 | 38.1135 | 37.0163 | 37.513 | 37.9575 | 27.199 | 21.9948 | 93.184 | 35.4092 | 35.3896 | 36.7067 | 35.5373 | 34.4061 | 34.7828 | 35.3505 | 34.6059 | 34.8512 | 37.782 | 37.1599 | 34.7809 | 34.7954 | 37.1838 | 37.2518 | 38.4442 | 37.1945 | 35.5278 | 35.8946 | 37.2208 | 37.0893 | 35.513 | 34.6982 | 34.0285 | 35.458 | 33.7061 | 34.1374 | 33.9054 | 34.7958 | 33.7119 | 34.8462 | 36.3757 | 34.5038 | 34.7889 | 35.8582 | 93.463 | 93.4168 | 93.4725
2022-09-07 23:04 | 1:14 | 21.0302 | 21.2668 | 22.9702 | 36.9654 | 34.3473 | 36.1555 | 35.6678 | 35.9819 | 37.1109 | 36.4087 | 35.8471 | 36.4239 | 35.3079 | 35.5264 | 36.6467 | 36.0549 | 38.1231 | 37.0229 | 37.519 | 37.9619 | 27.1312 | 21.961 | 93.2496 | 35.4466 | 35.3714 | 36.6911 | 35.542 | 34.404 | 34.7884 | 35.3385 | 34.6072 | 34.8528 | 37.7796 | 37.1672 | 34.7956 | 34.8084 | 37.1593 | 37.2422 | 38.4557 | 37.1891 | 35.5356 | 35.8726 | 37.189 | 37.0938 | 35.5168 | 34.7099 | 34.0443 | 35.452 | 33.6778 | 34.1241 | 33.9131 | 34.8047 | 33.7014 | 34.8265 | 36.3909 | 34.513 | 34.7794 | 35.8802 | 93.4497 | 93.2818 | 93.41
2022-09-07 23:04 | 1:14 | 21.0713 | 21.2076 | 22.913 | 36.9501 | 34.3626 | 36.155 | 35.6908 | 36.0026 | 37.1251 | 36.4368 | 35.8482 | 36.4204 | 35.2886 | 35.4981 | 36.6343 | 36.0438 | 38.1053 | 37.0406 | 37.5374 | 37.9559 | 27.161 | 21.9934 | 93.4352 | 35.3306 | 35.3793 | 36.7099 | 35.5389 | 34.4164 | 34.7861 | 35.3413 | 34.608 | 34.8618 | 37.7843 | 37.1654 | 34.8116 | 34.7883 | 37.1599 | 37.2437 | 38.4399 | 37.1816 | 35.5127 | 35.8714 | 37.1947 | 37.0922 | 35.5222 | 34.7051 | 34.0261 | 35.4733 | 33.6792 | 34.1315 | 33.9047 | 34.7818 | 33.6832 | 34.8205 | 36.382 | 34.5167 | 34.7988 | 35.8655 | 93.2503 | 93.1925 | 93.3083
2022-09-07 23:04 | 1:14 | 21.0282 | 21.2007 | 22.8978 | 36.9185 | 34.3498 | 36.1659 | 35.6935 | 35.9613 | 37.1343 | 36.4076 | 35.8571 | 36.4356 | 35.2901 | 35.5055 | 36.647 | 36.0411 | 38.1063 | 37.038 | 37.5199 | 37.9846 | 27.1087 | 21.9702 | 93.5088 | 35.378 | 35.3849 | 36.7083 | 35.5329 | 34.4237 | 34.7831 | 35.3662 | 34.5985 | 34.8446 | 37.7725 | 37.1647 | 34.7956 | 34.8053 | 37.1672 | 37.2326 | 38.4575 | 37.1838 | 35.5323 | 35.8681 | 37.1842 | 37.1081 | 35.4951 | 34.6964 | 34.0172 | 35.4512 | 33.6889 | 34.1337 | 33.9207 | 34.785 | 33.7024 | 34.8517 | 36.3974 | 34.5343 | 34.8075 | 35.8634 | 93.1301 | 93.096 | 93.2412
2022-09-07 23:04 | 1:14 | 20.9551 | 21.151 | 22.8508 | 36.8743 | 34.3449 | 36.1532 | 35.6886 | 35.9935 | 37.1356 | 36.4221 | 35.8586 | 36.443 | 35.2953 | 35.4945 | 36.6436 | 36.0401 | 38.1146 | 37.0377 | 37.526 | 37.9695 | 27.0697 | 21.9107 | 93.5027 | 35.3578 | 35.3813 | 36.6979 | 35.5278 | 34.4267 | 34.7809 | 35.3557 | 34.607 | 34.8674 | 37.7945 | 37.1217 | 34.7975 | 34.7859 | 37.1654 | 37.2427 | 38.4375 | 37.1593 | 35.5041 | 35.8738 | 37.1615 | 37.0759 | 35.4866 | 34.6708 | 34.0246 | 35.4425 | 33.72 | 34.1201 | 33.9146 | 34.7822 | 33.7131 | 34.8389 | 36.4145 | 34.525 | 34.7955 | 35.8731 | 92.9763 | 92.9749 | 93.1326
2022-09-07 23:04 | 1:14 | 20.8811 | 21.0938 | 22.8243 | 36.8412 | 34.3359 | 36.1446 | 35.6866 | 36.0011 | 37.1406 | 36.4408 | 35.8578 | 36.4496 | 35.282 | 35.4831 | 36.6393 | 36.0538 | 38.1008 | 37.034 | 37.5329 | 37.9657 | 27.0306 | 21.8752 | 93.5994 | 35.373 | 35.3878 | 36.6973 | 35.5356 | 34.4257 | 34.7956 | 35.3733 | 34.6134 | 34.8621 | 37.7906 | 37.1675 | 34.8034 | 34.8136 | 37.1647 | 37.2415 | 38.4408 | 37.1599 | 35.5086 | 35.8624 | 37.1623 | 37.0874 | 35.4772 | 34.6991 | 34.0231 | 35.4367 | 33.7031 | 34.1163 | 33.8978 | 34.7845 | 33.7029 | 34.8504 | 36.4023 | 34.5294 | 34.8235 | 35.8701 | 92.8937 | 92.8745 | 93.0767
2022-09-07 23:04 | 1:14 | 20.8848 | 21.1136 | 22.8065 | 36.9055 | 34.3668 | 36.1476 | 35.7157 | 36.002 | 37.1347 | 36.4546 | 35.8777 | 36.4774 | 35.2796 | 35.4828 | 36.6611 | 36.0633 | 38.1047 | 37.0574 | 37.5358 | 37.9654 | 27.0192 | 21.8693 | 93.633 | 35.3601 | 35.3804 | 36.6908 | 35.5127 | 34.4209 | 34.8116 | 35.378 | 34.6193 | 34.8705 | 37.8003 | 37.1463 | 34.8061 | 34.7966 | 37.1217 | 37.2567 | 38.451 | 37.1672 | 35.5034 | 35.8423 | 37.1621 | 37.0811 | 35.4763 | 34.6699 | 34.0068 | 35.4491 | 33.6861 | 34.1127 | 33.9115 | 34.7813 | 33.696 | 34.8581 | 36.3935 | 34.5565 | 34.8113 | 35.8697 | 92.8152 | 92.7831 | 93.0315
2022-09-07 23:05 | 1:14 | 20.9985 | 21.1004 | 22.7649 | 36.8612 | 34.357 | 36.1478 | 35.699 | 36.0038 | 37.1482 | 36.4369 | 35.8747 | 36.4467 | 35.2691 | 35.4656 | 36.6428 | 36.0464 | 38.1083 | 37.0468 | 37.5389 | 37.9718 | 26.9902 | 21.9185 | 93.6827 | 35.3969 | 35.3775 | 36.6987 | 35.5323 | 34.4276 | 34.7956 | 35.3982 | 34.6254 | 34.8606 | 37.7928 | 37.1439 | 34.807 | 34.8014 | 37.1675 | 37.2653 | 38.4601 | 37.1654 | 35.5086 | 35.8312 | 37.1365 | 37.0701 | 35.4668 | 34.6918 | 34.0185 | 35.432 | 33.7018 | 34.1145 | 33.917 | 34.7559 | 33.6964 | 34.8619 | 36.3907 | 34.5423 | 34.8285 | 35.8712 | 92.7104 | 92.6865 | 92.9654
2022-09-07 23:05 | 1:15 | 20.9374 | 21.1658 | 22.7817 | 36.8384 | 34.3492 | 36.1356 | 35.7061 | 36.005 | 37.1495 | 36.4544 | 35.8917 | 36.4734 | 35.2774 | 35.4711 | 36.6316 | 36.0583 | 38.0862 | 37.0502 | 37.5345 | 37.9706 | 26.985 | 21.8992 | 93.7467 | 35.1998 | 35.3829 | 36.7032 | 35.5041 | 34.4256 | 34.7975 | 35.3874 | 34.6174 | 34.8432 | 37.7916 | 37.1466 | 34.7984 | 34.8078 | 37.1463 | 37.2577 | 38.4282 | 37.1647 | 35.5208 | 35.8371 | 37.1517 | 37.0722 | 35.4642 | 34.6686 | 34.0146 | 35.451 | 33.6794 | 34.1192 | 33.8987 | 34.7482 | 33.71 | 34.8756 | 36.4007 | 34.5393 | 34.8254 | 35.8489 | 92.5665 | 92.595 | 92.8478
2022-09-07 23:05 | 1:15 | 20.8847 | 21.1118 | 22.7975 | 37.0451 | 34.3553 | 36.1544 | 35.694 | 36.0005 | 37.1554 | 36.4251 | 35.8772 | 36.4813 | 35.259 | 35.4387 | 36.6338 | 36.0442 | 38.0885 | 37.0581 | 37.5551 | 37.9764 | 26.9484 | 21.8589 | 93.8378 | 35.3696 | 35.3654 | 36.683 | 35.5086 | 34.4244 | 34.8034 | 35.3744 | 34.6194 | 34.8581 | 37.7927 | 37.1367 | 34.8081 | 34.7917 | 37.1439 | 37.2639 | 38.4366 | 37.1217 | 35.4999 | 35.7911 | 37.1561 | 37.0511 | 35.4668 | 34.6638 | 33.99 | 35.4339 | 33.6941 | 34.1218 | 33.8986 | 34.7604 | 33.7357 | 34.8772 | 36.3942 | 34.5507 | 34.8261 | 35.8645 | 92.5057 | 92.4641 | 92.7663
2022-09-07 23:05 | 1:15 | 20.8722 | 21.0831 | 22.7285 | 36.8408 | 34.3472 | 36.1598 | 35.7133 | 36.0236 | 37.1393 | 36.4616 | 35.9148 | 36.4702 | 35.2708 | 35.4402 | 36.6308 | 36.0686 | 38.0858 | 37.065 | 37.5259 | 37.9888 | 26.9343 | 21.8257 | 94.0028 | 35.313 | 35.3799 | 36.689 | 35.5034 | 34.4493 | 34.8061 | 35.3908 | 34.626 | 34.8744 | 37.7989 | 37.154 | 34.8148 | 34.8198 | 37.1466 | 37.2683 | 38.4546 | 37.1675 | 35.4963 | 35.8032 | 37.138 | 37.0621 | 35.4492 | 34.6696 | 33.9962 | 35.4313 | 33.6779 | 34.1249 | 33.9085 | 34.7623 | 33.7089 | 34.8867 | 36.4144 | 34.5588 | 34.8428 | 35.8676 | 92.3618 | 92.3226 | 92.7219
2022-09-07 23:05 | 1:15 | 20.911 | 21.1296 | 22.7322 | 36.7983 | 34.3404 | 36.1437 | 35.7071 | 36.0221 | 37.1598 | 36.4483 | 35.8808 | 36.4771 | 35.2739 | 35.4139 | 36.6433 | 36.0654 | 38.0622 | 37.0597 | 37.5251 | 37.9815 | 26.924 | 21.851 | 94.046 | 35.3761 | 35.3681 | 36.6993 | 35.5086 | 34.4541 | 34.807 | 35.4012 | 34.6279 | 34.8605 | 37.7892 | 37.1418 | 34.806 | 34.8128 | 37.1367 | 37.2665 | 38.4445 | 37.1463 | 35.5052 | 35.8205 | 37.1246 | 37.0234 | 35.4508 | 34.6471 | 33.9964 | 35.4166 | 33.6916 | 34.102 | 33.9241 | 34.7615 | 33.7087 | 34.8641 | 36.389 | 34.5676 | 34.8603 | 35.8453 | 92.2516 | 92.1626 | 92.6353
2022-09-07 23:05 | 1:15 | 20.8995 | 21.1543 | 22.7403 | 36.7587 | 34.3489 | 36.1491 | 35.7149 | 36.0245 | 37.1556 | 36.471 | 35.8801 | 36.4861 | 35.2535 | 35.4264 | 36.6272 | 36.0574 | 38.0687 | 37.06 | 37.5393 | 37.9452 | 26.9252 | 21.8514 | 94.1858 | 35.2999 | 35.3477 | 36.6605 | 35.5208 | 34.4453 | 34.7984 | 35.4192 | 34.6383 | 34.8595 | 37.7931 | 37.1411 | 34.808 | 34.8229 | 37.154 | 37.2493 | 38.4425 | 37.1439 | 35.5084 | 35.7983 | 37.1147 | 37.0369 | 35.4151 | 34.6504 | 33.9926 | 35.4084 | 33.6839 | 34.1203 | 33.8853 | 34.7544 | 33.7188 | 34.8792 | 36.3962 | 34.571 | 34.8564 | 35.8618 | 92.1452 | 92.091 | 92.5945
2022-09-07 23:06 | 1:15 | 20.9877 | 21.179 | 22.7683 | 36.7484 | 34.3355 | 36.1449 | 35.7197 | 36.0117 | 37.1423 | 36.4797 | 35.9108 | 36.4964 | 35.2445 | 35.4042 | 36.6414 | 36.0562 | 38.0595 | 37.068 | 37.5481 | 37.9779 | 26.9115 | 21.8659 | 94.2736 | 35.1235 | 35.379 | 36.6672 | 35.4999 | 34.4287 | 34.8081 | 35.4085 | 34.6245 | 34.8723 | 37.7916 | 37.1241 | 34.8111 | 34.8111 | 37.1418 | 37.2769 | 38.4369 | 37.1466 | 35.4751 | 35.7984 | 37.1059 | 37.0543 | 35.447 | 34.6548 | 33.9945 | 35.4066 | 33.6928 | 34.128 | 33.9096 | 34.7354 | 33.7033 | 34.8772 | 36.3858 | 34.5709 | 34.8572 | 35.8484 | 91.942 | 91.9277 | 92.5139
2022-09-07 23:06 | 1:16 | 20.8563 | 21.0159 | 22.6997 | 36.7093 | 34.3606 | 36.15 | 35.7263 | 36.013 | 37.1416 | 36.481 | 35.891 | 36.4966 | 35.2527 | 35.3962 | 36.6231 | 36.0597 | 38.0621 | 37.0634 | 37.5453 | 37.9644 | 26.9032 | 21.8091 | 94.4289 | 35.2995 | 35.3646 | 36.6763 | 35.4963 | 34.4579 | 34.8148 | 35.4055 | 34.6293 | 34.8699 | 37.8021 | 37.1223 | 34.7992 | 34.8118 | 37.1411 | 37.279 | 38.4352 | 37.1367 | 35.4909 | 35.7882 | 37.0888 | 37.0397 | 35.4418 | 34.6541 | 33.977 | 35.403 | 33.6851 | 34.1062 | 33.8906 | 34.77 | 33.7151 | 34.8809 | 36.4066 | 34.5738 | 34.8427 | 35.8471 | 91.915 | 91.9322 | 92.4873
2022-09-07 23:06 | 1:16 | 20.8306 | 20.9456 | 22.6276 | 36.6487 | 34.3487 | 36.151 | 35.7252 | 36.0197 | 37.1411 | 36.4761 | 35.8996 | 36.5164 | 35.2238 | 35.3978 | 36.6339 | 36.058 | 38.0362 | 37.0622 | 37.5258 | 37.9691 | 26.8773 | 21.7673 | 94.5637 | 35.2617 | 35.382 | 36.668 | 35.5052 | 34.4555 | 34.806 | 35.4103 | 34.6396 | 34.8813 | 37.7819 | 37.1069 | 34.8059 | 34.8128 | 37.1241 | 37.2807 | 38.4417 | 37.154 | 35.4896 | 35.7726 | 37.0727 | 37.0261 | 35.4326 | 34.6311 | 33.9646 | 35.3999 | 33.6925 | 34.1321 | 33.9248 | 34.7476 | 33.7069 | 34.8776 | 36.3883 | 34.5808 | 34.8594 | 35.8371 | 92.0816 | 91.9358 | 92.4753
2022-09-07 23:06 | 1:16 | 20.7765 | 20.9385 | 22.5741 | 36.7454 | 34.3413 | 36.1403 | 35.7273 | 36.0318 | 37.1369 | 36.4799 | 35.9085 | 36.5099 | 35.2311 | 35.3719 | 36.6215 | 36.0603 | 38.0493 | 37.0745 | 37.5384 | 37.95 | 26.8469 | 21.7393 | 94.6495 | 35.3059 | 35.3854 | 36.6648 | 35.5084 | 34.4241 | 34.808 | 35.419 | 34.641 | 34.8786 | 37.8021 | 37.1151 | 34.8065 | 34.8211 | 37.1223 | 37.2639 | 38.434 | 37.1418 | 35.4867 | 35.774 | 37.0702 | 37.0293 | 35.4307 | 34.6342 | 33.9858 | 35.4006 | 33.6767 | 34.0972 | 33.9043 | 34.7538 | 33.688 | 34.8813 | 36.3928 | 34.5935 | 34.8601 | 35.8162 | 92.1096 | 91.984 | 92.5077
2022-09-07 23:06 | 1:16 | 20.9172 | 20.9918 | 22.6292 | 36.669 | 34.3407 | 36.1309 | 35.7207 | 36.0358 | 37.1575 | 36.4856 | 35.9153 | 36.5104 | 35.2209 | 35.3794 | 36.6173 | 36.0573 | 38.0445 | 37.0683 | 37.5387 | 37.9557 | 26.8315 | 21.808 | 94.754 | 35.1124 | 35.3869 | 36.6696 | 35.4751 | 34.4483 | 34.8111 | 35.4268 | 34.6442 | 34.8755 | 37.7848 | 37.1067 | 34.8094 | 34.8136 | 37.1069 | 37.2645 | 38.4292 | 37.1411 | 35.4729 | 35.7647 | 37.063 | 37.0155 | 35.4154 | 34.6426 | 33.9765 | 35.4014 | 33.6658 | 34.1126 | 33.8876 | 34.7406 | 33.6964 | 34.8678 | 36.3908 | 34.5866 | 34.8736 | 35.8292 | 92.1098 | 92.1225 | 92.6804
2022-09-07 23:06 | 1:16 | 20.8514 | 21.0138 | 22.6171 | 36.7676 | 34.3516 | 36.1675 | 35.7321 | 36.0251 | 37.1606 | 36.4932 | 35.9134 | 36.53 | 35.2292 | 35.3528 | 36.621 | 36.0564 | 38.0307 | 37.0498 | 37.5438 | 37.9776 | 26.8419 | 21.8121 | 94.8319 | 35.2081 | 35.3627 | 36.6722 | 35.4909 | 34.4492 | 34.7992 | 35.4321 | 34.6621 | 34.8685 | 37.7803 | 37.1105 | 34.7937 | 34.8239 | 37.1151 | 37.2743 | 38.4378 | 37.1241 | 35.4628 | 35.7487 | 37.0423 | 37.0083 | 35.4104 | 34.6248 | 33.9623 | 35.3802 | 33.6634 | 34.1098 | 33.8856 | 34.7483 | 33.6968 | 34.8713 | 36.397 | 34.5987 | 34.8417 | 35.814 | 92.2136 | 92.1658 | 92.6781
2022-09-07 23:07 | 1:16 | 20.8701 | 21.0281 | 22.6394 | 36.6757 | 34.3268 | 36.1667 | 35.7441 | 36.0506 | 37.1446 | 36.4914 | 35.9052 | 36.5313 | 35.2264 | 35.332 | 36.6087 | 36.0476 | 38.0318 | 37.0729 | 37.5328 | 37.9651 | 26.8482 | 21.7944 | 94.8976 | 35.1697 | 35.3524 | 36.6586 | 35.4896 | 34.4441 | 34.8059 | 35.446 | 34.6305 | 34.858 | 37.7693 | 37.0932 | 34.8055 | 34.8212 | 37.1067 | 37.2717 | 38.3964 | 37.1223 | 35.4711 | 35.74 | 37.0381 | 36.9935 | 35.4043 | 34.61 | 33.9535 | 35.3683 | 33.6738 | 34.125 | 33.8875 | 34.7431 | 33.6858 | 34.873 | 36.3909 | 34.6031 | 34.8814 | 35.81 | 92.2567 | 92.2436 | 92.6767
2022-09-07 23:07 | 1:17 | 20.7628 | 20.942 | 22.6041 | 36.7015 | 34.3351 | 36.1446 | 35.7323 | 36.0392 | 37.1463 | 36.4808 | 35.934 | 36.5207 | 35.2114 | 35.3361 | 36.5973 | 36.0851 | 38.0231 | 37.063 | 37.5323 | 37.9528 | 26.8253 | 21.7105 | 94.9461 | 35.2296 | 35.3557 | 36.6589 | 35.4867 | 34.4297 | 34.8065 | 35.4244 | 34.6534 | 34.8809 | 37.7999 | 37.1217 | 34.7818 | 34.8167 | 37.1105 | 37.25 | 38.4188 | 37.1069 | 35.4658 | 35.7482 | 37.0464 | 36.9973 | 35.3845 | 34.6115 | 33.9357 | 35.3456 | 33.6653 | 34.1052 | 33.8972 | 34.7501 | 33.6932 | 34.8577 | 36.3872 | 34.5993 | 34.8651 | 35.8 | 92.3917 | 92.403 | 92.7721
2022-09-07 23:07 | 1:17 | 20.7154 | 20.9016 | 22.556 | 36.6772 | 34.3358 | 36.1309 | 35.7356 | 36.0354 | 37.1385 | 36.4876 | 35.9248 | 36.5298 | 35.2032 | 35.345 | 36.5921 | 36.0482 | 38.0028 | 37.0712 | 37.5393 | 37.9411 | 26.8024 | 21.685 | 94.8577 | 35.044 | 35.355 | 36.6468 | 35.4729 | 34.45 | 34.8094 | 35.4459 | 34.6376 | 34.8785 | 37.7724 | 37.0926 | 34.7975 | 34.8043 | 37.0932 | 37.2815 | 38.407 | 37.1151 | 35.4689 | 35.7176 | 37.0288 | 36.9771 | 35.3982 | 34.6114 | 33.9641 | 35.3565 | 33.6549 | 34.1162 | 33.8765 | 34.7376 | 33.6833 | 34.8779 | 36.3983 | 34.5943 | 34.8694 | 35.804 | 92.4775 | 92.5333 | 92.8074
2022-09-07 23:07 | 1:17 | 20.7695 | 20.937 | 22.5555 | 36.6945 | 34.3329 | 36.1375 | 35.7376 | 36.0241 | 37.14 | 36.4853 | 35.935 | 36.5204 | 35.1975 | 35.3125 | 36.5898 | 36.0554 | 37.9903 | 37.0588 | 37.544 | 37.9543 | 26.7986 | 21.6829 | 94.7235 | 35.2007 | 35.3512 | 36.651 | 35.4628 | 34.4405 | 34.7937 | 35.4328 | 34.656 | 34.8678 | 37.7807 | 37.1126 | 34.8245 | 34.8209 | 37.1217 | 37.2731 | 38.4122 | 37.1067 | 35.4805 | 35.6909 | 37.0007 | 36.9813 | 35.4006 | 34.6103 | 33.9243 | 35.3632 | 33.6551 | 34.1128 | 33.8927 | 34.7434 | 33.6843 | 34.8746 | 36.3926 | 34.6032 | 34.8829 | 35.8056 | 92.5087 | 92.5973 | 92.8099
2022-09-07 23:07 | 1:17 | 20.7337 | 20.8806 | 22.5194 | 36.7706 | 34.3095 | 36.1295 | 35.7363 | 36.0417 | 37.1341 | 36.4841 | 35.9237 | 36.5219 | 35.184 | 35.3054 | 36.5838 | 36.0581 | 37.9819 | 37.0604 | 37.5442 | 37.9508 | 26.7924 | 21.6416 | 94.5795 | 35.1102 | 35.3392 | 36.6425 | 35.4711 | 34.4533 | 34.8055 | 35.4329 | 34.6663 | 34.8586 | 37.7979 | 37.0983 | 34.8093 | 34.8282 | 37.0926 | 37.2562 | 38.3891 | 37.1105 | 35.4832 | 35.6801 | 36.9937 | 36.962 | 35.3849 | 34.6258 | 33.9229 | 35.3374 | 33.6481 | 34.0958 | 33.8798 | 34.7247 | 33.6732 | 34.8708 | 36.3858 | 34.5981 | 34.9002 | 35.7723 | 92.6667 | 92.6775 | 92.9222
2022-09-07 23:07 | 1:17 | 20.757 | 20.8844 | 22.4846 | 36.6532 | 34.3165 | 36.1217 | 35.7651 | 36.0396 | 37.1335 | 36.4859 | 35.9341 | 36.532 | 35.182 | 35.3007 | 36.5919 | 36.0557 | 37.9881 | 37.054 | 37.5249 | 37.9228 | 26.7861 | 21.6554 | 94.5092 | 35.0087 | 35.3626 | 36.6481 | 35.4658 | 34.4418 | 34.7818 | 35.4452 | 34.6484 | 34.8697 | 37.7664 | 37.0948 | 34.816 | 34.8186 | 37.1126 | 37.2888 | 38.3925 | 37.0932 | 35.4657 | 35.6944 | 36.9879 | 36.9564 | 35.3808 | 34.5774 | 33.9352 | 35.3401 | 33.6478 | 34.0984 | 33.8804 | 34.7386 | 33.6672 | 34.8731 | 36.3944 | 34.6427 | 34.8979 | 35.7747 | 92.8123 | 92.8182 | 93.0659
2022-09-07 23:08 | 1:17 | 20.719 | 20.8972 | 22.4849 | 36.5511 | 34.3387 | 36.1246 | 35.7422 | 36.0331 | 37.1256 | 36.5017 | 35.9383 | 36.5487 | 35.1827 | 35.2908 | 36.5758 | 36.0466 | 37.9793 | 37.0537 | 37.543 | 37.9398 | 26.7714 | 21.6531 | 94.4289 | 35.1784 | 35.3547 | 36.6318 | 35.4689 | 34.4566 | 34.7975 | 35.4188 | 34.6709 | 34.8784 | 37.7645 | 37.1217 | 34.8127 | 34.8205 | 37.0983 | 37.2703 | 38.3833 | 37.1217 | 35.4715 | 35.6864 | 36.9871 | 36.9622 | 35.3738 | 34.5961 | 33.9193 | 35.3264 | 33.652 | 34.1127 | 33.8702 | 34.7174 | 33.6676 | 34.8626 | 36.4083 | 34.623 | 34.9119 | 35.7679 | 92.8558 | 92.9302 | 93.0496
2022-09-07 23:08 | 1:18 | 20.844 | 20.9813 | 22.5288 | 36.6587 | 34.3154 | 36.1256 | 35.7487 | 36.0372 | 37.1198 | 36.501 | 35.9382 | 36.5546 | 35.1701 | 35.2645 | 36.5617 | 36.0614 | 37.9706 | 37.0595 | 37.5348 | 37.9404 | 26.7777 | 21.6661 | 94.4425 | 35.0091 | 35.3558 | 36.6489 | 35.4805 | 34.4571 | 34.8245 | 35.4566 | 34.6366 | 34.8641 | 37.7881 | 37.1126 | 34.8065 | 34.8085 | 37.0948 | 37.2679 | 38.3959 | 37.0926 | 35.4718 | 35.6715 | 36.9647 | 36.9473 | 35.3664 | 34.6137 | 33.9211 | 35.3147 | 33.6528 | 34.1 | 33.875 | 34.712 | 33.6741 | 34.8622 | 36.4041 | 34.6308 | 34.904 | 35.7811 | 92.9762 | 93.0066 | 93.1584
2022-09-07 23:08 | 1:18 | 20.6861 | 20.9394 | 22.5197 | 36.633 | 34.3059 | 36.1349 | 35.7653 | 36.0402 | 37.1219 | 36.5007 | 35.9506 | 36.5597 | 35.1929 | 35.2548 | 36.5872 | 36.0768 | 37.9587 | 37.0744 | 37.5352 | 37.9187 | 26.778 | 21.6689 | 94.4455 | 35.0939 | 35.349 | 36.6608 | 35.4832 | 34.4462 | 34.8093 | 35.4475 | 34.6673 | 34.8657 | 37.7885 | 37.1075 | 34.7964 | 34.823 | 37.1217 | 37.2684 | 38.3746 | 37.1126 | 35.4825 | 35.6771 | 36.9566 | 36.9529 | 35.3709 | 34.6185 | 33.9113 | 35.3144 | 33.637 | 34.0992 | 33.8808 | 34.7162 | 33.6867 | 34.884 | 36.4009 | 34.6368 | 34.8865 | 35.7399 | 93.0703 | 93.117 | 93.1922
2022-09-07 23:08 | 1:18 | 20.757 | 20.9655 | 22.4896 | 36.6007 | 34.3065 | 36.1288 | 35.7685 | 36.0548 | 37.1253 | 36.4948 | 35.9805 | 36.5562 | 35.1694 | 35.2351 | 36.5968 | 36.0839 | 37.9755 | 37.0576 | 37.5147 | 37.9325 | 26.7753 | 21.6263 | 94.5299 | 34.9714 | 35.3533 | 36.6413 | 35.4657 | 34.4819 | 34.816 | 35.4441 | 34.6623 | 34.8821 | 37.7746 | 37.1142 | 34.8183 | 34.8296 | 37.1126 | 37.2659 | 38.3699 | 37.0983 | 35.4776 | 35.6599 | 36.9502 | 36.9305 | 35.3749 | 34.5796 | 33.9119 | 35.3056 | 33.6122 | 34.1299 | 33.8825 | 34.7047 | 33.6513 | 34.8679 | 36.4051 | 34.6136 | 34.9101 | 35.7569 | 93.2223 | 93.2152 | 93.2823
2022-09-07 23:08 | 1:18 | 20.7762 | 20.8956 | 22.4762 | 36.5459 | 34.325 | 36.1392 | 35.7669 | 36.0521 | 37.1367 | 36.5095 | 35.9691 | 36.5821 | 35.1728 | 35.2301 | 36.5702 | 36.0795 | 37.9565 | 37.0799 | 37.5315 | 37.9179 | 26.7882 | 21.6988 | 94.3953 | 35.0399 | 35.3412 | 36.6251 | 35.4715 | 34.4387 | 34.8127 | 35.4447 | 34.679 | 34.8644 | 37.7642 | 37.1018 | 34.8381 | 34.8335 | 37.1075 | 37.266 | 38.3742 | 37.0948 | 35.4444 | 35.6663 | 36.9517 | 36.9195 | 35.3699 | 34.5865 | 33.8909 | 35.333 | 33.6402 | 34.1096 | 33.8722 | 34.7139 | 33.654 | 34.8592 | 36.394 | 34.6379 | 34.8974 | 35.7319 | 93.4197 | 93.3887 | 93.4113
2022-09-07 23:08 | 1:18 | 20.747 | 20.8943 | 22.4875 | 36.68 | 34.2999 | 36.13 | 35.7677 | 36.0369 | 37.125 | 36.5148 | 35.965 | 36.572 | 35.1521 | 35.2276 | 36.562 | 36.0724 | 37.9522 | 37.0534 | 37.5341 | 37.9265 | 26.7763 | 21.6603 | 94.3273 | 35.027 | 35.3445 | 36.635 | 35.4718 | 34.4522 | 34.8065 | 35.4437 | 34.6785 | 34.8751 | 37.7949 | 37.1251 | 34.8027 | 34.8212 | 37.1142 | 37.2766 | 38.3812 | 37.1217 | 35.479 | 35.6598 | 36.9264 | 36.9308 | 35.3676 | 34.6034 | 33.9167 | 35.304 | 33.6158 | 34.1239 | 33.8827 | 34.7011 | 33.6508 | 34.8421 | 36.4054 | 34.6333 | 34.8957 | 35.736 | 93.5635 | 93.5622 | 93.4899
2022-09-07 23:09 | 1:19 | 20.7471 | 20.8772 | 22.4411 | 36.5738 | 34.305 | 36.125 | 35.7698 | 36.0636 | 37.108 | 36.5129 | 35.9837 | 36.5715 | 35.1441 | 35.222 | 36.5795 | 36.0801 | 37.9573 | 37.0766 | 37.531 | 37.9289 | 26.7554 | 21.6344 | 94.2975 | 34.8751 | 35.3456 | 36.6248 | 35.4825 | 34.46 | 34.7964 | 35.4561 | 34.6885 | 34.876 | 37.7926 | 37.1075 | 34.8189 | 34.8436 | 37.1018 | 37.2816 | 38.373 | 37.1126 | 35.459 | 35.6231 | 36.9301 | 36.9096 | 35.3479 | 34.6082 | 33.9023 | 35.2874 | 33.6305 | 34.1306 | 33.8725 | 34.7127 | 33.6606 | 34.8725 | 36.4027 | 34.6406 | 34.9237 | 35.7393 | 93.7393 | 93.7011 | 93.5797
2022-09-07 23:09 | 1:19 | 20.6546 | 20.8422 | 22.4143 | 36.537 | 34.3044 | 36.1306 | 35.7833 | 36.0569 | 37.1188 | 36.5019 | 35.9843 | 36.5887 | 35.1814 | 35.2141 | 36.5651 | 36.0817 | 37.9387 | 37.0645 | 37.5227 | 37.9184 | 26.7214 | 21.5887 | 94.3429 | 35.086 | 35.3521 | 36.6421 | 35.4776 | 34.4818 | 34.8183 | 35.4578 | 34.6827 | 34.8865 | 37.7752 | 37.0913 | 34.8188 | 34.8443 | 37.1251 | 37.2925 | 38.383 | 37.1075 | 35.4627 | 35.6538 | 36.9218 | 36.9236 | 35.3562 | 34.5996 | 33.9009 | 35.2886 | 33.6223 | 34.1157 | 33.8689 | 34.689 | 33.6712 | 34.8697 | 36.4121 | 34.64 | 34.9277 | 35.7298 | 93.8861 | 93.8296 | 93.6746
2022-09-07 23:09 | 1:19 | 20.6651 | 20.8467 | 22.415 | 36.5648 | 34.3079 | 36.1376 | 35.7764 | 36.0795 | 37.1273 | 36.5145 | 35.9873 | 36.5984 | 35.154 | 35.2091 | 36.5871 | 36.0953 | 37.9525 | 37.0619 | 37.5299 | 37.9206 | 26.7047 | 21.5759 | 94.2461 | 35.1157 | 35.3434 | 36.6616 | 35.4444 | 34.474 | 34.8381 | 35.4606 | 34.6885 | 34.8713 | 37.7992 | 37.083 | 34.8011 | 34.8466 | 37.1075 | 37.2882 | 38.3788 | 37.1142 | 35.4547 | 35.6278 | 36.9202 | 36.928 | 35.3589 | 34.5618 | 33.8831 | 35.2773 | 33.639 | 34.1288 | 33.8792 | 34.6818 | 33.6524 | 34.8626 | 36.4025 | 34.6534 | 34.9165 | 35.7363 | 94.0368 | 94.0358 | 93.7885
2022-09-07 23:09 | 1:19 | 20.7063 | 20.9099 | 22.452 | 36.697 | 34.3 | 36.1275 | 35.7906 | 36.0656 | 37.1205 | 36.5292 | 36.007 | 36.6223 | 35.163 | 35.1858 | 36.5658 | 36.0908 | 37.9442 | 37.0901 | 37.5295 | 37.9144 | 26.7118 | 21.5798 | 94.208 | 34.9812 | 35.3447 | 36.6369 | 35.479 | 34.5064 | 34.8027 | 35.4657 | 34.7131 | 34.8945 | 37.808 | 37.0978 | 34.8019 | 34.8609 | 37.0913 | 37.3064 | 38.3564 | 37.1018 | 35.4679 | 35.6287 | 36.9108 | 36.9333 | 35.3415 | 34.5514 | 33.8726 | 35.271 | 33.6381 | 34.1324 | 33.8739 | 34.6939 | 33.6624 | 34.8878 | 36.4006 | 34.6653 | 34.9235 | 35.7305 | 94.2399 | 94.174 | 93.8594
2022-09-07 23:09 | 1:19 | 20.6642 | 20.8525 | 22.3943 | 36.6085 | 34.3094 | 36.1397 | 35.7786 | 36.0717 | 37.1327 | 36.5221 | 36.0248 | 36.6187 | 35.1501 | 35.1955 | 36.5658 | 36.0837 | 37.9312 | 37.0833 | 37.532 | 37.9186 | 26.6775 | 21.579 | 94.1705 | 35.0298 | 35.3393 | 36.6407 | 35.459 | 34.4737 | 34.8189 | 35.4688 | 34.6926 | 34.8977 | 37.8 | 37.1083 | 34.8117 | 34.8681 | 37.083 | 37.2839 | 38.3708 | 37.1251 | 35.4704 | 35.6167 | 36.928 | 36.9252 | 35.3496 | 34.5727 | 33.9086 | 35.2789 | 33.6272 | 34.1159 | 33.8617 | 34.7146 | 33.6624 | 34.8873 | 36.4122 | 34.6706 | 34.9283 | 35.7233 | 94.389 | 94.3038 | 93.9795
2022-09-07 23:09 | 1:19 | 20.6072 | 20.7536 | 22.3645 | 36.6009 | 34.309 | 36.1404 | 35.7861 | 36.0896 | 37.137 | 36.5359 | 36.0138 | 36.6229 | 35.1654 | 35.1847 | 36.5622 | 36.0926 | 37.9217 | 37.0724 | 37.5224 | 37.9105 | 26.6556 | 21.5176 | 94.123 | 35.0145 | 35.3631 | 36.6428 | 35.4627 | 34.4754 | 34.8188 | 35.4932 | 34.7192 | 34.8906 | 37.7972 | 37.1022 | 34.8244 | 34.8485 | 37.0978 | 37.2866 | 38.3654 | 37.1075 | 35.461 | 35.6153 | 36.8871 | 36.9329 | 35.3476 | 34.5686 | 33.8953 | 35.2675 | 33.6325 | 34.1243 | 33.8792 | 34.7029 | 33.663 | 34.9001 | 36.4221 | 34.6662 | 34.9443 | 35.7339 | 94.5638 | 94.4912 | 94.1115
2022-09-07 23:10 | 1:19 | 20.5321 | 20.7247 | 22.3194 | 36.5531 | 34.2916 | 36.1243 | 35.7882 | 36.0727 | 37.1384 | 36.5333 | 36.0342 | 36.6289 | 35.1538 | 35.1669 | 36.5512 | 36.0994 | 37.9203 | 37.0876 | 37.5331 | 37.9215 | 26.6155 | 21.5116 | 94.0417 | 35.0867 | 35.3664 | 36.6465 | 35.4547 | 34.473 | 34.8011 | 35.4704 | 34.7225 | 34.8914 | 37.801 | 37.1099 | 34.8261 | 34.8519 | 37.1083 | 37.3096 | 38.3567 | 37.0913 | 35.456 | 35.6261 | 36.9119 | 36.9098 | 35.3389 | 34.5667 | 33.8916 | 35.2632 | 33.6509 | 34.1269 | 33.8921 | 34.6906 | 33.6643 | 34.8783 | 36.4108 | 34.6731 | 34.9371 | 35.7366 | 94.6477 | 94.6667 | 94.1892
2022-09-07 23:10 | 1:20 | 20.5875 | 20.7666 | 22.3254 | 36.5737 | 34.2849 | 36.1143 | 35.7803 | 36.0715 | 37.1342 | 36.5528 | 36.0208 | 36.621 | 35.1501 | 35.1699 | 36.5674 | 36.0908 | 37.9328 | 37.0954 | 37.5257 | 37.927 | 26.5969 | 21.4783 | 93.9189 | 34.9399 | 35.3396 | 36.6426 | 35.4679 | 34.4861 | 34.8019 | 35.4855 | 34.7148 | 34.9007 | 37.8025 | 37.0871 | 34.8133 | 34.8588 | 37.1022 | 37.3011 | 38.3494 | 37.083 | 35.4506 | 35.5945 | 36.902 | 36.8997 | 35.3533 | 34.5439 | 33.875 | 35.2731 | 33.6495 | 34.1411 | 33.8652 | 34.6736 | 33.6456 | 34.8856 | 36.4271 | 34.6853 | 34.9478 | 35.7283 | 94.8354 | 94.7595 | 94.2119
2022-09-07 23:10 | 1:20 | 20.5875 | 20.7642 | 22.3045 | 36.4995 | 34.2966 | 36.1305 | 35.7965 | 36.0768 | 37.1357 | 36.5354 | 36.0366 | 36.6437 | 35.1416 | 35.1635 | 36.5482 | 36.0932 | 37.9215 | 37.0673 | 37.5391 | 37.915 | 26.5992 | 21.4595 | 93.9034 | 35.0749 | 35.3565 | 36.6312 | 35.4704 | 34.4897 | 34.8117 | 35.4897 | 34.7269 | 34.9156 | 37.8005 | 37.0944 | 34.8068 | 34.8731 | 37.1099 | 37.2916 | 38.3638 | 37.0978 | 35.4496 | 35.6026 | 36.9141 | 36.9148 | 35.3315 | 34.5381 | 33.8813 | 35.2715 | 33.6296 | 34.1373 | 33.8798 | 34.6912 | 33.6453 | 34.9026 | 36.4331 | 34.6853 | 34.9495 | 35.7226 | 94.9154 | 94.8829 | 94.3007
2022-09-07 23:10 | 1:20 | 20.5526 | 20.6994 | 22.2776 | 36.4587 | 34.3091 | 36.1139 | 35.7866 | 36.0941 | 37.1237 | 36.5563 | 36.0542 | 36.6361 | 35.1241 | 35.1645 | 36.5549 | 36.1018 | 37.9453 | 37.0796 | 37.548 | 37.9156 | 26.5738 | 21.4405 | 93.9578 | 34.9365 | 35.351 | 36.6338 | 35.461 | 34.4985 | 34.8244 | 35.4821 | 34.7144 | 34.9033 | 37.7968 | 37.0794 | 34.8035 | 34.8831 | 37.0871 | 37.3001 | 38.368 | 37.1083 | 35.4451 | 35.584 | 36.9017 | 36.9335 | 35.3325 | 34.5221 | 33.8884 | 35.2468 | 33.6325 | 34.1533 | 33.8709 | 34.6679 | 33.6606 | 34.9219 | 36.4203 | 34.7061 | 34.9699 | 35.7223 | 94.9986 | 94.9972 | 94.3734
2022-09-07 23:10 | 1:20 | 20.5246 | 20.7117 | 22.2631 | 36.4961 | 34.2837 | 36.1272 | 35.8076 | 36.0951 | 37.1334 | 36.5548 | 36.0488 | 36.6379 | 35.1508 | 35.1522 | 36.5704 | 36.13 | 37.9105 | 37.0898 | 37.5279 | 37.9273 | 26.5475 | 21.4322 | 93.8674 | 34.9442 | 35.3255 | 36.6462 | 35.456 | 34.4841 | 34.8261 | 35.4911 | 34.7384 | 34.9031 | 37.8039 | 37.0972 | 34.8116 | 34.8721 | 37.0944 | 37.3184 | 38.3453 | 37.1022 | 35.4585 | 35.6061 | 36.8768 | 36.9149 | 35.3311 | 34.546 | 33.8867 | 35.2482 | 33.6328 | 34.1295 | 33.878 | 34.6937 | 33.6448 | 34.9168 | 36.4154 | 34.6929 | 34.9469 | 35.7168 | 95.1 | 95.022 | 94.4547
2022-09-07 23:10 | 1:20 | 20.5065 | 20.7025 | 22.2755 | 36.505 | 34.2953 | 36.1373 | 35.8095 | 36.0891 | 37.136 | 36.5531 | 36.0354 | 36.6634 | 35.145 | 35.1415 | 36.5361 | 36.1161 | 37.9097 | 37.0721 | 37.5359 | 37.9194 | 26.5336 | 21.4043 | 93.6545 | 35.0462 | 35.3389 | 36.6438 | 35.4506 | 34.4966 | 34.8133 | 35.4952 | 34.7394 | 34.8918 | 37.8047 | 37.0919 | 34.8348 | 34.8636 | 37.0794 | 37.3148 | 38.3447 | 37.1099 | 35.4527 | 35.5909 | 36.881 | 36.9108 | 35.3272 | 34.5376 | 33.8844 | 35.2418 | 33.6333 | 34.1397 | 33.8819 | 34.6898 | 33.6649 | 34.9057 | 36.4119 | 34.6927 | 34.9644 | 35.7203 | 95.0901 | 95.089 | 94.4377
2022-09-07 23:11 | 1:21 | 20.4871 | 20.6441 | 22.2424 | 36.5876 | 34.2721 | 36.1368 | 35.8061 | 36.1347 | 37.1313 | 36.5797 | 36.0822 | 36.6509 | 35.1419 | 35.1171 | 36.5501 | 36.1204 | 37.9244 | 37.0756 | 37.5543 | 37.9161 | 26.5289 | 21.3845 | 93.5253 | 34.8117 | 35.3608 | 36.648 | 35.4496 | 34.4942 | 34.8068 | 35.5104 | 34.7581 | 34.9059 | 37.7958 | 37.077 | 34.8235 | 34.87 | 37.0972 | 37.3319 | 38.3656 | 37.0871 | 35.4506 | 35.5687 | 36.8768 | 36.9168 | 35.3322 | 34.5343 | 33.8745 | 35.2391 | 33.6378 | 34.1275 | 33.8803 | 34.6803 | 33.6672 | 34.9252 | 36.4199 | 34.7079 | 34.974 | 35.7415 | 94.9783 | 95.0921 | 94.3328
2022-09-07 23:11 | 1:21 | 20.4514 | 20.613 | 22.2205 | 36.6412 | 34.2951 | 36.1226 | 35.8165 | 36.0999 | 37.1262 | 36.571 | 36.0796 | 36.6698 | 35.1048 | 35.109 | 36.5452 | 36.1247 | 37.9042 | 37.0955 | 37.558 | 37.9041 | 26.5225 | 21.3264 | 93.4883 | 34.8915 | 35.3456 | 36.6363 | 35.4451 | 34.4906 | 34.8035 | 35.4806 | 34.7431 | 34.9142 | 37.8141 | 37.083 | 34.8238 | 34.8803 | 37.0919 | 37.3246 | 38.3485 | 37.0944 | 35.4633 | 35.5777 | 36.8798 | 36.9035 | 35.3037 | 34.5172 | 33.8375 | 35.2644 | 33.6513 | 34.1165 | 33.8521 | 34.6962 | 33.6581 | 34.9062 | 36.4352 | 34.7143 | 34.9745 | 35.7174 | 94.7874 | 94.8837 | 94.1692
2022-09-07 23:11 | 1:21 | 20.3519 | 20.5224 | 22.1503 | 36.556 | 34.2905 | 36.1479 | 35.8161 | 36.0993 | 37.1298 | 36.5891 | 36.0641 | 36.6625 | 35.119 | 35.1162 | 36.5305 | 36.1255 | 37.8902 | 37.0911 | 37.5532 | 37.9226 | 26.4852 | 21.2913 | 93.4222 | 34.8558 | 35.3434 | 36.6415 | 35.4585 | 34.4885 | 34.8116 | 35.5019 | 34.762 | 34.9072 | 37.794 | 37.0795 | 34.8235 | 34.868 | 37.077 | 37.3148 | 38.3705 | 37.0794 | 35.4557 | 35.577 | 36.8828 | 36.9369 | 35.2919 | 34.5204 | 33.8475 | 35.2537 | 33.6487 | 34.1456 | 33.8755 | 34.6868 | 33.6633 | 34.9371 | 36.419 | 34.7273 | 34.9762 | 35.7369 | 94.586 | 94.692 | 94.0454
2022-09-07 23:11 | 1:21 | 20.4476 | 20.5532 | 22.1337 | 36.5905 | 34.2849 | 36.1351 | 35.8158 | 36.1176 | 37.1377 | 36.5907 | 36.0523 | 36.6771 | 35.12 | 35.0812 | 36.5432 | 36.117 | 37.8898 | 37.1071 | 37.5382 | 37.915 | 26.4754 | 21.2564 | 93.207 | 34.849 | 35.3427 | 36.6281 | 35.4527 | 34.5127 | 34.8348 | 35.5027 | 34.7627 | 34.932 | 37.7951 | 37.0712 | 34.8144 | 34.8823 | 37.083 | 37.3169 | 38.3485 | 37.0972 | 35.4541 | 35.569 | 36.8689 | 36.9088 | 35.3071 | 34.517 | 33.8685 | 35.2352 | 33.6602 | 34.144 | 33.8858 | 34.6643 | 33.6579 | 34.9307 | 36.4025 | 34.7146 | 34.9798 | 35.7138 | 94.3453 | 94.4656 | 93.9345
2022-09-07 23:11 | 1:21 | 20.3054 | 20.4959 | 22.1058 | 36.5948 | 34.2921 | 36.1216 | 35.805 | 36.1154 | 37.1324 | 36.5835 | 36.0834 | 36.6854 | 35.1245 | 35.1058 | 36.5489 | 36.116 | 37.8922 | 37.0919 | 37.5448 | 37.905 | 26.445 | 21.2353 | 93.1482 | 34.9048 | 35.3358 | 36.6276 | 35.4506 | 34.5059 | 34.8235 | 35.5101 | 34.756 | 34.9415 | 37.8009 | 37.0707 | 34.8369 | 34.8756 | 37.0795 | 37.3328 | 38.3472 | 37.0919 | 35.4323 | 35.5638 | 36.8687 | 36.8807 | 35.3082 | 34.5293 | 33.823 | 35.2417 | 33.6618 | 34.1293 | 33.8573 | 34.6818 | 33.6495 | 34.9255 | 36.4147 | 34.7173 | 34.9696 | 35.719 | 94.1864 | 94.3109 | 93.8496
2022-09-07 23:11 | 1:21 | 20.2255 | 20.4001 | 22.0577 | 36.4835 | 34.2955 | 36.1176 | 35.8114 | 36.1054 | 37.1485 | 36.6022 | 36.075 | 36.7005 | 35.1177 | 35.0735 | 36.547 | 36.1376 | 37.9042 | 37.0898 | 37.5684 | 37.928 | 26.4165 | 21.1569 | 92.9207 | 34.8121 | 35.332 | 36.636 | 35.4633 | 34.4977 | 34.8238 | 35.5178 | 34.7588 | 34.9346 | 37.8067 | 37.0865 | 34.8297 | 34.8886 | 37.0712 | 37.3266 | 38.3385 | 37.077 | 35.436 | 35.5469 | 36.8674 | 36.9075 | 35.2762 | 34.5304 | 33.8584 | 35.2247 | 33.6469 | 34.1449 | 33.8631 | 34.6579 | 33.6695 | 34.9312 | 36.4307 | 34.7242 | 34.9972 | 35.7117 | 94.0348 | 94.2503 | 93.7769
2022-09-07 23:12 | 1:21 | 20.203 | 20.3936 | 22.0214 | 36.4356 | 34.2916 | 36.1354 | 35.8079 | 36.1226 | 37.1388 | 36.5986 | 36.0858 | 36.7091 | 35.1052 | 35.0781 | 36.5464 | 36.1244 | 37.9043 | 37.1213 | 37.5648 | 37.9109 | 26.3848 | 21.1269 | 92.7457 | 35.0207 | 35.3587 | 36.6325 | 35.4557 | 34.5009 | 34.8235 | 35.5191 | 34.7496 | 34.9327 | 37.8118 | 37.0707 | 34.8135 | 34.8854 | 37.0707 | 37.3476 | 38.3527 | 37.083 | 35.4424 | 35.5324 | 36.8458 | 36.913 | 35.3013 | 34.4922 | 33.8409 | 35.2289 | 33.6385 | 34.136 | 33.8695 | 34.6499 | 33.6688 | 34.9356 | 36.4167 | 34.7344 | 35.0063 | 35.7276 | 93.91 | 94.1418 | 93.6697
2022-09-07 23:12 | 1:22 | 20.1895 | 20.3266 | 21.9875 | 36.3837 | 34.2872 | 36.1096 | 35.7978 | 36.1207 | 37.1339 | 36.5889 | 36.08 | 36.7045 | 35.1098 | 35.0879 | 36.5369 | 36.1256 | 37.8941 | 37.1222 | 37.5513 | 37.9126 | 26.3772 | 21.1107 | 92.5207 | 34.9054 | 35.3484 | 36.6229 | 35.4541 | 34.4842 | 34.8144 | 35.518 | 34.7652 | 34.9221 | 37.8068 | 37.0612 | 34.8324 | 34.8896 | 37.0865 | 37.3512 | 38.3426 | 37.0795 | 35.4289 | 35.5269 | 36.8375 | 36.8964 | 35.2836 | 34.516 | 33.8206 | 35.2304 | 33.6455 | 34.1296 | 33.8625 | 34.6788 | 33.6588 | 34.9457 | 36.4213 | 34.7443 | 35.0087 | 35.7193 | 93.8845 | 94.0323 | 93.6451
2022-09-07 23:12 | 1:22 | 20.1641 | 20.3293 | 21.9728 | 36.3867 | 34.2847 | 36.125 | 35.8254 | 36.128 | 37.1395 | 36.6109 | 36.0946 | 36.7009 | 35.0885 | 35.0521 | 36.5301 | 36.1355 | 37.8759 | 37.1088 | 37.5657 | 37.9344 | 26.3389 | 21.096 | 92.3934 | 34.7497 | 35.3443 | 36.622 | 35.4323 | 34.4986 | 34.8369 | 35.5239 | 34.7677 | 34.9244 | 37.8 | 37.0532 | 34.8281 | 34.8954 | 37.0707 | 37.3262 | 38.3334 | 37.0712 | 35.4233 | 35.5123 | 36.8467 | 36.9202 | 35.2683 | 34.5185 | 33.8186 | 35.2325 | 33.6616 | 34.1199 | 33.8735 | 34.6657 | 33.6761 | 34.943 | 36.419 | 34.747 | 35.007 | 35.7229 | 93.8029 | 93.9083 | 93.6312
2022-09-07 23:12 | 1:22 | 20.1581 | 20.3433 | 21.9643 | 36.3446 | 34.3005 | 36.117 | 35.8167 | 36.1131 | 37.1334 | 36.6151 | 36.1046 | 36.7234 | 35.0874 | 35.0601 | 36.5403 | 36.1407 | 37.8822 | 37.1284 | 37.5547 | 37.9278 | 26.3307 | 21.063 | 92.5084 | 34.8399 | 35.346 | 36.6214 | 35.436 | 34.506 | 34.8297 | 35.5436 | 34.7821 | 34.9356 | 37.8043 | 37.0634 | 34.8131 | 34.9032 | 37.0612 | 37.3365 | 38.3484 | 37.0707 | 35.4193 | 35.5227 | 36.856 | 36.9133 | 35.2829 | 34.5152 | 33.8334 | 35.2275 | 33.6636 | 34.1335 | 33.8694 | 34.6633 | 33.6633 | 34.9449 | 36.4286 | 34.771 | 35.023 | 35.7243 | 93.71 | 93.7993 | 93.624
2022-09-07 23:12 | 1:22 | 20.187 | 20.3585 | 21.9752 | 36.4618 | 34.2857 | 36.1216 | 35.8222 | 36.1285 | 37.1192 | 36.6203 | 36.1078 | 36.7156 | 35.0947 | 35.0567 | 36.5239 | 36.1288 | 37.8715 | 37.1174 | 37.5522 | 37.9217 | 26.3057 | 21.0657 | 92.6416 | 34.9412 | 35.344 | 36.621 | 35.4424 | 34.5187 | 34.8135 | 35.5365 | 34.7792 | 34.925 | 37.7925 | 37.0415 | 34.8299 | 34.8808 | 37.0532 | 37.3308 | 38.3387 | 37.0865 | 35.4165 | 35.5189 | 36.843 | 36.8984 | 35.2515 | 34.4892 | 33.8272 | 35.2263 | 33.633 | 34.1209 | 33.8603 | 34.6579 | 33.6589 | 34.9567 | 36.4066 | 34.7358 | 35.0092 | 35.7211 | 93.6783 | 93.7811 | 93.5624
2022-09-07 23:12 | 1:22 | 20.1599 | 20.3594 | 21.9798 | 36.4106 | 34.2879 | 36.1181 | 35.8153 | 36.1398 | 37.1233 | 36.6381 | 36.1012 | 36.7144 | 35.086 | 35.0314 | 36.5489 | 36.1265 | 37.8694 | 37.1256 | 37.5533 | 37.9164 | 26.2997 | 21.0686 | 92.7185 | 34.8657 | 35.3252 | 36.6119 | 35.4289 | 34.4958 | 34.8324 | 35.5215 | 34.7727 | 34.9344 | 37.8149 | 37.0625 | 34.8335 | 34.8978 | 37.0634 | 37.3485 | 38.3434 | 37.0707 | 35.4031 | 35.5255 | 36.8269 | 36.9036 | 35.239 | 34.4745 | 33.8122 | 35.2179 | 33.6595 | 34.1237 | 33.8574 | 34.6636 | 33.6799 | 34.9822 | 36.4344 | 34.7609 | 35.0098 | 35.7296 | 93.5992 | 93.6894 | 93.5436
2022-09-07 23:13 | 1:23 | 20.1685 | 20.2984 | 21.9266 | 36.3965 | 34.2677 | 36.1125 | 35.7968 | 36.1146 | 37.1636 | 36.618 | 36.1163 | 36.7309 | 35.0935 | 35.0427 | 36.5331 | 36.1273 | 37.8729 | 37.1179 | 37.5427 | 37.9049 | 26.27 | 21.0291 | 92.7814 | 34.8335 | 35.3209 | 36.6076 | 35.4233 | 34.4985 | 34.8281 | 35.5435 | 34.7778 | 34.932 | 37.818 | 37.0296 | 34.8366 | 34.892 | 37.0415 | 37.3302 | 38.3432 | 37.0612 | 35.4072 | 35.5077 | 36.8096 | 36.9025 | 35.2594 | 34.5097 | 33.7958 | 35.2109 | 33.6418 | 34.1289 | 33.8806 | 34.6612 | 33.6513 | 34.9735 | 36.423 | 34.7734 | 35.029 | 35.7113 | 93.5142 | 93.6633 | 93.4113
2022-09-07 23:13 | 1:23 | 20.1634 | 20.3269 | 21.9241 | 36.3596 | 34.2868 | 36.1 | 35.8123 | 36.1323 | 37.1358 | 36.6386 | 36.1092 | 36.7297 | 35.0969 | 35.0181 | 36.5237 | 36.1321 | 37.8564 | 37.1086 | 37.5616 | 37.9174 | 26.239 | 21.0351 | 92.9418 | 34.9057 | 35.3041 | 36.6009 | 35.4193 | 34.5171 | 34.8131 | 35.5184 | 34.7554 | 34.9224 | 37.7987 | 37.0698 | 34.8216 | 34.8813 | 37.0625 | 37.3518 | 38.3218 | 37.0532 | 35.4203 | 35.5091 | 36.824 | 36.8975 | 35.2586 | 34.4643 | 33.8175 | 35.1942 | 33.6532 | 34.1328 | 33.8665 | 34.6668 | 33.6721 | 34.95 | 36.4184 | 34.7639 | 35.0233 | 35.6981 | 93.4417 | 93.5464 | 93.3305
2022-09-07 23:13 | 1:23 | 20.1118 | 20.246 | 21.9003 | 36.435 | 34.2704 | 36.1242 | 35.8212 | 36.1355 | 37.1438 | 36.6383 | 36.1106 | 36.7404 | 35.085 | 35.0142 | 36.5265 | 36.1511 | 37.8513 | 37.1109 | 37.5565 | 37.9118 | 26.2071 | 21.0065 | 92.8985 | 34.7451 | 35.3311 | 36.5864 | 35.4165 | 34.5187 | 34.8299 | 35.5455 | 34.769 | 34.9159 | 37.8055 | 37.0416 | 34.8114 | 34.8873 | 37.0296 | 37.3343 | 38.3263 | 37.0634 | 35.4079 | 35.504 | 36.7943 | 36.8901 | 35.2431 | 34.4781 | 33.8098 | 35.1924 | 33.6557 | 34.1272 | 33.8514 | 34.6661 | 33.6786 | 34.9617 | 36.4004 | 34.7763 | 35.0346 | 35.7056 | 93.3471 | 93.4981 | 93.3315
2022-09-07 23:13 | 1:23 | 20.076 | 20.1901 | 21.916 | 36.4492 | 34.2728 | 36.1107 | 35.8141 | 36.1222 | 37.1228 | 36.6404 | 36.1094 | 36.7442 | 35.0662 | 34.9896 | 36.5194 | 36.1225 | 37.8408 | 37.109 | 37.5627 | 37.9173 | 26.1732 | 20.9678 | 92.9417 | 34.8009 | 35.3227 | 36.5766 | 35.4031 | 34.5071 | 34.8335 | 35.5403 | 34.7786 | 34.9261 | 37.8044 | 37.0334 | 34.8234 | 34.9098 | 37.0698 | 37.3473 | 38.3129 | 37.0415 | 35.3947 | 35.4961 | 36.7932 | 36.8904 | 35.244 | 34.4656 | 33.8102 | 35.2034 | 33.6666 | 34.1242 | 33.8499 | 34.6704 | 33.6484 | 34.9626 | 36.4104 | 34.7716 | 35.0426 | 35.7279 | 93.22 | 93.4553 | 93.2801
2022-09-07 23:13 | 1:23 | 20.0326 | 20.1879 | 21.8986 | 36.3683 | 34.2645 | 36.1057 | 35.8166 | 36.1244 | 37.1432 | 36.6595 | 36.1267 | 36.7212 | 35.0734 | 35.0015 | 36.5316 | 36.1356 | 37.8361 | 37.1161 | 37.5516 | 37.9188 | 26.107 | 20.9666 | 92.9672 | 34.7835 | 35.331 | 36.599 | 35.4072 | 34.5145 | 34.8366 | 35.5429 | 34.7673 | 34.9348 | 37.8099 | 37.0357 | 34.8143 | 34.8904 | 37.0416 | 37.3386 | 38.3281 | 37.0625 | 35.3922 | 35.4905 | 36.7979 | 36.8917 | 35.255 | 34.4628 | 33.7905 | 35.2017 | 33.6463 | 34.1107 | 33.8522 | 34.6653 | 33.6819 | 34.9566 | 36.3983 | 34.7832 | 35.0348 | 35.7206 | 93.156 | 93.3458 | 93.1952
2022-09-07 23:13 | 1:23 | 20.0201 | 20.1736 | 21.8282 | 36.3272 | 34.2858 | 36.1017 | 35.8089 | 36.1425 | 37.1172 | 36.6696 | 36.0954 | 36.7616 | 35.0634 | 34.9865 | 36.5169 | 36.1241 | 37.846 | 37.1144 | 37.5542 | 37.9223 | 26.0949 | 20.9835 | 93.1139 | 34.8351 | 35.3267 | 36.581 | 35.4203 | 34.5004 | 34.8216 | 35.5545 | 34.7719 | 34.9337 | 37.8137 | 37.0301 | 34.8288 | 34.898 | 37.0334 | 37.3293 | 38.3355 | 37.0296 | 35.3839 | 35.4825 | 36.7784 | 36.9032 | 35.2326 | 34.4707 | 33.8059 | 35.1863 | 33.6589 | 34.1166 | 33.8488 | 34.6602 | 33.6576 | 34.9897 | 36.4067 | 34.7713 | 35.0472 | 35.7165 | 93.0351 | 93.2319 | 93.1643
2022-09-07 23:14 | 1:23 | 20.0162 | 20.1958 | 21.8471 | 36.3567 | 34.273 | 36.111 | 35.815 | 36.1302 | 37.1331 | 36.6718 | 36.1276 | 36.7398 | 35.0627 | 34.9799 | 36.5328 | 36.1394 | 37.8244 | 37.1178 | 37.5701 | 37.9024 | 26.0681 | 20.9238 | 93.2808 | 34.7924 | 35.3293 | 36.5669 | 35.4079 | 34.5058 | 34.8114 | 35.5758 | 34.7791 | 34.9248 | 37.8024 | 37.0264 | 34.8177 | 34.8822 | 37.0357 | 37.3449 | 38.3201 | 37.0698 | 35.3897 | 35.4749 | 36.7718 | 36.8775 | 35.2161 | 34.44 | 33.7875 | 35.181 | 33.6597 | 34.1107 | 33.8583 | 34.6577 | 33.6471 | 34.9599 | 36.4101 | 34.7821 | 35.0362 | 35.7141 | 92.9592 | 93.075 | 93.0887
2022-09-07 23:14 | 1:24 | 20.0069 | 20.1787 | 21.8644 | 36.3226 | 34.2806 | 36.0855 | 35.8113 | 36.1247 | 37.1381 | 36.6841 | 36.1228 | 36.766 | 35.0661 | 34.9719 | 36.5294 | 36.1353 | 37.8304 | 37.1085 | 37.5691 | 37.9243 | 26.0431 | 20.8985 | 93.2785 | 34.6217 | 35.3389 | 36.5605 | 35.3947 | 34.5082 | 34.8234 | 35.5582 | 34.7855 | 34.9387 | 37.8092 | 37.0427 | 34.8182 | 34.8946 | 37.0301 | 37.3507 | 38.3385 | 37.0416 | 35.3942 | 35.4682 | 36.7584 | 36.861 | 35.2068 | 34.4601 | 33.7836 | 35.1885 | 33.6538 | 34.1212 | 33.8505 | 34.6584 | 33.6783 | 34.9732 | 36.41 | 34.7798 | 35.0416 | 35.7049 | 92.7798 | 93.0042 | 92.8591
2022-09-07 23:14 | 1:24 | 20.0218 | 20.1389 | 21.8952 | 36.4355 | 34.2557 | 36.0932 | 35.8133 | 36.1421 | 37.1605 | 36.6843 | 36.1171 | 36.7566 | 35.05 | 34.9677 | 36.5132 | 36.1346 | 37.8194 | 37.1114 | 37.5715 | 37.9311 | 26.0293 | 20.897 | 93.421 | 34.7854 | 35.3306 | 36.5815 | 35.3922 | 34.5099 | 34.8143 | 35.568 | 34.7847 | 34.9408 | 37.8119 | 37.0215 | 34.8113 | 34.8839 | 37.0264 | 37.3533 | 38.3192 | 37.0334 | 35.3814 | 35.4558 | 36.7778 | 36.866 | 35.223 | 34.4381 | 33.7641 | 35.1591 | 33.6719 | 34.1103 | 33.8491 | 34.6534 | 33.6701 | 35.007 | 36.4121 | 34.7917 | 35.0678 | 35.6965 | 92.7698 | 92.8853 | 92.9308
2022-09-07 23:14 | 1:24 | 19.9904 | 20.1413 | 21.9217 | 36.4087 | 34.2722 | 36.0835 | 35.8176 | 36.1346 | 37.1399 | 36.6857 | 36.1224 | 36.7546 | 35.0541 | 34.9432 | 36.5222 | 36.1291 | 37.8079 | 37.1184 | 37.5626 | 37.9101 | 25.99 | 20.8989 | 93.4405 | 34.6848 | 35.3352 | 36.5643 | 35.3839 | 34.5001 | 34.8288 | 35.5734 | 34.778 | 34.9346 | 37.8077 | 37.0171 | 34.8148 | 34.8835 | 37.0427 | 37.348 | 38.3371 | 37.0357 | 35.3931 | 35.4525 | 36.7609 | 36.8917 | 35.1959 | 34.4267 | 33.7774 | 35.1842 | 33.656 | 34.1173 | 33.8492 | 34.6598 | 33.6598 | 35 | 36.437 | 34.7961 | 35.0411 | 35.7077 | 92.6419 | 92.7555 | 92.8225
2022-09-07 23:14 | 1:24 | 19.9941 | 20.1423 | 21.8497 | 36.4267 | 34.2591 | 36.0772 | 35.8254 | 36.1343 | 37.1335 | 36.6908 | 36.1315 | 36.7553 | 35.0451 | 34.9643 | 36.5154 | 36.1298 | 37.7955 | 37.1142 | 37.568 | 37.9175 | 25.9733 | 20.9014 | 93.5463 | 34.8353 | 35.3212 | 36.5339 | 35.3897 | 34.5241 | 34.8177 | 35.5559 | 34.7658 | 34.9213 | 37.7903 | 37.0209 | 34.8335 | 34.8968 | 37.0215 | 37.3531 | 38.3456 | 37.0301 | 35.3883 | 35.4612 | 36.7319 | 36.8719 | 35.1966 | 34.4321 | 33.7785 | 35.1809 | 33.6452 | 34.1123 | 33.8358 | 34.6429 | 33.6558 | 35.0121 | 36.4156 | 34.7898 | 35.0623 | 35.6991 | 92.5348 | 92.6217 | 92.767
2022-09-07 23:14 | 1:24 | 19.9668 | 20.1055 | 21.8585 | 36.3055 | 34.2763 | 36.0812 | 35.8214 | 36.1274 | 37.144 | 36.7049 | 36.1175 | 36.7827 | 35.0311 | 34.9433 | 36.4973 | 36.1263 | 37.7982 | 37.1244 | 37.5652 | 37.9315 | 25.9526 | 20.8779 | 93.6024 | 34.7153 | 35.3142 | 36.5659 | 35.3942 | 34.5227 | 34.8182 | 35.5769 | 34.7878 | 34.9181 | 37.7938 | 37.0077 | 34.8303 | 34.8946 | 37.0171 | 37.3446 | 38.3446 | 37.0264 | 35.3707 | 35.4392 | 36.7433 | 36.852 | 35.19 | 34.4908 | 33.7557 | 35.1658 | 33.6645 | 34.1012 | 33.8502 | 34.6496 | 33.6487 | 34.9811 | 36.4072 | 34.8045 | 35.0629 | 35.7012 | 92.4242 | 92.5542 | 92.6132
2022-09-07 23:15 | 1:24 | 19.9102 | 20.0331 | 21.777 | 36.2739 | 34.2783 | 36.0648 | 35.8109 | 36.1294 | 37.1372 | 36.7097 | 36.136 | 36.7596 | 35.053 | 34.9294 | 36.5154 | 36.1275 | 37.8024 | 37.121 | 37.5638 | 37.9186 | 25.9263 | 20.832 | 93.6587 | 34.5819 | 35.3156 | 36.5496 | 35.3814 | 34.5015 | 34.8113 | 35.5717 | 34.7727 | 34.9288 | 37.7941 | 37.0093 | 34.824 | 34.8779 | 37.0209 | 37.3391 | 38.3135 | 37.0427 | 35.384 | 35.4275 | 36.7079 | 36.855 | 35.1831 | 34.4978 | 33.7754 | 35.1525 | 33.6484 | 34.1059 | 33.8361 | 34.6538 | 33.667 | 34.9875 | 36.4125 | 34.8052 | 35.0887 | 35.694 | 92.3308 | 92.4327 | 92.6075
2022-09-07 23:15 | 1:25 | 19.9034 | 20.0383 | 21.8102 | 36.2246 | 34.2576 | 36.0837 | 35.8256 | 36.1525 | 37.1354 | 36.7265 | 36.1374 | 36.7696 | 35.0368 | 34.9112 | 36.4992 | 36.1358 | 37.7913 | 37.1359 | 37.5593 | 37.9185 | 25.8942 | 20.8128 | 93.8822 | 34.8139 | 35.3096 | 36.5702 | 35.3931 | 34.4991 | 34.8148 | 35.5879 | 34.7888 | 34.9374 | 37.7978 | 36.999 | 34.8288 | 34.8979 | 37.0077 | 37.359 | 38.331 | 37.0215 | 35.3745 | 35.4135 | 36.7283 | 36.843 | 35.1776 | 34.4957 | 33.7448 | 35.1545 | 33.6422 | 34.1026 | 33.8528 | 34.6635 | 33.644 | 34.9945 | 36.408 | 34.8098 | 35.0749 | 35.6908 | 92.1946 | 92.3263 | 92.4998
2022-09-07 23:15 | 1:25 | 19.9032 | 20.0086 | 21.8506 | 36.3412 | 34.2775 | 36.061 | 35.825 | 36.1467 | 37.1313 | 36.7325 | 36.1324 | 36.7954 | 35.0321 | 34.9058 | 36.5102 | 36.1344 | 37.7994 | 37.1208 | 37.5715 | 37.913 | 25.8525 | 20.8218 | 93.9927 | 34.6394 | 35.3224 | 36.5534 | 35.3883 | 34.5262 | 34.8335 | 35.5728 | 34.7817 | 34.9322 | 37.7995 | 37.005 | 34.8075 | 34.8829 | 37.0093 | 37.3493 | 38.318 | 37.0171 | 35.3702 | 35.4133 | 36.7107 | 36.8685 | 35.1636 | 34.4833 | 33.7565 | 35.1671 | 33.6566 | 34.0925 | 33.833 | 34.6395 | 33.6442 | 35.0073 | 36.4112 | 34.8169 | 35.0758 | 35.699 | 92.0955 | 92.1616 | 92.4211
2022-09-07 23:15 | 1:25 | 19.9363 | 20.0398 | 21.8952 | 36.318 | 34.2737 | 36.0745 | 35.8314 | 36.1343 | 37.1298 | 36.7447 | 36.118 | 36.7735 | 35.0147 | 34.8843 | 36.5121 | 36.1283 | 37.7724 | 37.1367 | 37.5666 | 37.9309 | 25.8758 | 20.8618 | 94.1094 | 34.5489 | 35.3175 | 36.5505 | 35.3707 | 34.5203 | 34.8303 | 35.571 | 34.7829 | 34.9342 | 37.7859 | 37 | 34.8176 | 34.8961 | 36.999 | 37.3571 | 38.3026 | 37.0209 | 35.366 | 35.4173 | 36.7308 | 36.86 | 35.1501 | 34.4959 | 33.7483 | 35.1493 | 33.6453 | 34.1005 | 33.8495 | 34.6448 | 33.6419 | 34.9894 | 36.3978 | 34.8156 | 35.0793 | 35.6951 | 91.9786 | 92.0818 | 92.361
2022-09-07 23:15 | 1:25 | 20.0015 | 20.1188 | 21.8878 | 36.3365 | 34.2918 | 36.0752 | 35.829 | 36.1383 | 37.1374 | 36.7288 | 36.1372 | 36.7841 | 34.9904 | 34.8759 | 36.5167 | 36.1269 | 37.7826 | 37.1451 | 37.5601 | 37.9265 | 25.8668 | 20.8841 | 94.1772 | 34.6331 | 35.3125 | 36.5479 | 35.384 | 34.5202 | 34.824 | 35.6099 | 34.7834 | 34.9372 | 37.8124 | 36.9963 | 34.8349 | 34.8933 | 37.005 | 37.3606 | 38.3251 | 37.0077 | 35.3458 | 35.4186 | 36.7151 | 36.8507 | 35.1569 | 34.4665 | 33.7289 | 35.1446 | 33.6379 | 34.0881 | 33.8625 | 34.6585 | 33.6537 | 34.9973 | 36.4151 | 34.8088 | 35.0909 | 35.6835 | 91.8255 | 91.898 | 92.2265
2022-09-07 23:15 | 1:25 | 19.9546 | 20.0744 | 21.9718 | 36.182 | 34.2492 | 36.0512 | 35.8258 | 36.1347 | 37.1377 | 36.7489 | 36.1208 | 36.7916 | 35.0216 | 34.8904 | 36.5077 | 36.1343 | 37.7696 | 37.1453 | 37.587 | 37.9108 | 25.8377 | 20.8339 | 94.3678 | 34.752 | 35.3059 | 36.5535 | 35.3745 | 34.5101 | 34.8288 | 35.6159 | 34.7931 | 34.9199 | 37.7979 | 36.9955 | 34.8341 | 34.8822 | 37 | 37.3486 | 38.3105 | 37.0093 | 35.3544 | 35.3915 | 36.6973 | 36.8123 | 35.1452 | 34.4603 | 33.7391 | 35.1477 | 33.6611 | 34.0859 | 33.8327 | 34.6288 | 33.6574 | 35.0082 | 36.4245 | 34.8172 | 35.1024 | 35.6925 | 91.7033 | 91.7995 | 92.19
2022-09-07 23:16 | 1:26 | 19.8883 | 20.0508 | 21.8454 | 36.2968 | 34.2589 | 36.067 | 35.8212 | 36.1265 | 37.1384 | 36.7436 | 36.1431 | 36.795 | 35.0068 | 34.8858 | 36.4924 | 36.1443 | 37.7664 | 37.1316 | 37.5779 | 37.9079 | 25.8229 | 20.7979 | 94.4186 | 34.5796 | 35.311 | 36.5682 | 35.3702 | 34.5173 | 34.8075 | 35.5972 | 34.7832 | 34.9363 | 37.7829 | 36.9992 | 34.8139 | 34.8943 | 36.9963 | 37.352 | 38.3339 | 36.999 | 35.3709 | 35.4053 | 36.6951 | 36.854 | 35.1542 | 34.4801 | 33.748 | 35.1235 | 33.6484 | 34.0977 | 33.8325 | 34.623 | 33.6536 | 35.0213 | 36.4078 | 34.8397 | 35.1023 | 35.6828 | 91.5775 | 91.7758 | 92.0211
2022-09-07 23:16 | 1:26 | 19.8558 | 20.0407 | 21.8255 | 36.2974 | 34.2684 | 36.0745 | 35.8362 | 36.1341 | 37.1313 | 36.7511 | 36.1509 | 36.79 | 35.0035 | 34.8772 | 36.5009 | 36.1384 | 37.7693 | 37.1444 | 37.566 | 37.9174 | 25.7936 | 20.7726 | 94.5554 | 34.7136 | 35.3208 | 36.5352 | 35.366 | 34.5078 | 34.8176 | 35.6041 | 34.7831 | 34.9479 | 37.7908 | 36.983 | 34.8226 | 34.8789 | 36.9955 | 37.3449 | 38.3036 | 37.005 | 35.3641 | 35.3755 | 36.684 | 36.8343 | 35.1383 | 34.4601 | 33.7309 | 35.1358 | 33.6544 | 34.0939 | 33.8386 | 34.6294 | 33.649 | 34.993 | 36.4034 | 34.8392 | 35.0839 | 35.6656 | 91.6526 | 91.7941 | 92.2045
2022-09-07 23:16 | 1:26 | 19.8679 | 20.0106 | 21.8305 | 36.2692 | 34.2605 | 36.0746 | 35.8389 | 36.155 | 37.1293 | 36.7763 | 36.1371 | 36.79 | 34.9945 | 34.8496 | 36.4788 | 36.1357 | 37.7456 | 37.1347 | 37.5607 | 37.9145 | 25.7915 | 20.7702 | 94.6028 | 34.6748 | 35.3025 | 36.521 | 35.3458 | 34.5048 | 34.8349 | 35.5942 | 34.78 | 34.9106 | 37.7776 | 37.0008 | 34.8141 | 34.8883 | 36.9992 | 37.3378 | 38.2973 | 37 | 35.3315 | 35.38 | 36.6833 | 36.8344 | 35.139 | 34.469 | 33.736 | 35.1286 | 33.6533 | 34.1071 | 33.8251 | 34.6195 | 33.6276 | 34.9985 | 36.3964 | 34.8274 | 35.1018 | 35.674 | 91.6904 | 91.8828 | 92.1892
2022-09-07 23:16 | 1:26 | 19.8643 | 19.9919 | 21.7375 | 36.2089 | 34.261 | 36.0707 | 35.8243 | 36.1374 | 37.1196 | 36.7659 | 36.1489 | 36.8079 | 34.9951 | 34.8495 | 36.4811 | 36.1248 | 37.7549 | 37.1276 | 37.554 | 37.8989 | 25.7567 | 20.7608 | 94.7413 | 34.6702 | 35.2822 | 36.5361 | 35.3544 | 34.5135 | 34.8341 | 35.597 | 34.7637 | 34.9205 | 37.7831 | 36.9958 | 34.8054 | 34.8842 | 36.983 | 37.3473 | 38.312 | 36.9963 | 35.3572 | 35.3918 | 36.6721 | 36.8192 | 35.1437 | 34.4537 | 33.7301 | 35.127 | 33.6362 | 34.1034 | 33.8426 | 34.6224 | 33.6354 | 34.9993 | 36.411 | 34.8355 | 35.1075 | 35.6463 | 91.7607 | 91.9368 | 92.2214
2022-09-07 23:16 | 1:26 | 19.9125 | 20.0287 | 21.7914 | 36.2613 | 34.2633 | 36.0609 | 35.8328 | 36.1659 | 37.1107 | 36.7831 | 36.1481 | 36.7985 | 34.9832 | 34.8396 | 36.4802 | 36.1372 | 37.7515 | 37.1307 | 37.564 | 37.9003 | 25.7636 | 20.7967 | 94.785 | 34.5181 | 35.3042 | 36.5251 | 35.3709 | 34.5093 | 34.8139 | 35.6189 | 34.7969 | 34.9299 | 37.7872 | 36.9937 | 34.7933 | 34.8859 | 37.0008 | 37.3412 | 38.2956 | 36.9955 | 35.3641 | 35.3537 | 36.6585 | 36.8184 | 35.1328 | 34.4765 | 33.7085 | 35.0956 | 33.6414 | 34.0963 | 33.8213 | 34.634 | 33.6404 | 34.9996 | 36.4068 | 34.8404 | 35.0974 | 35.6521 | 91.7786 | 92.0197 | 92.2091
2022-09-07 23:16 | 1:26 | 19.8635 | 19.9965 | 21.8636 | 36.2326 | 34.2616 | 36.0636 | 35.837 | 36.1354 | 37.1109 | 36.7623 | 36.1478 | 36.8361 | 34.9732 | 34.8355 | 36.491 | 36.1218 | 37.7378 | 37.1165 | 37.5822 | 37.9049 | 25.7379 | 20.7693 | 94.8627 | 34.5765 | 35.3048 | 36.5103 | 35.3641 | 34.5165 | 34.8226 | 35.6121 | 34.7897 | 34.9266 | 37.7932 | 36.9644 | 34.8078 | 34.8878 | 36.9958 | 37.3453 | 38.2881 | 36.9992 | 35.3589 | 35.3566 | 36.6718 | 36.8049 | 35.1407 | 34.4607 | 33.6868 | 35.1174 | 33.6258 | 34.1158 | 33.8389 | 34.6246 | 33.6305 | 34.9893 | 36.4072 | 34.8349 | 35.1075 | 35.6481 | 91.8848 | 92.1979 | 92.3455
2022-09-07 23:17 | 1:26 | 19.8545 | 19.9367 | 21.7936 | 36.1955 | 34.2425 | 36.0579 | 35.8548 | 36.1621 | 37.127 | 36.7749 | 36.1503 | 36.8172 | 34.9525 | 34.8128 | 36.4805 | 36.1376 | 37.7335 | 37.1321 | 37.5777 | 37.8992 | 25.7227 | 20.7484 | 94.8996 | 34.5103 | 35.2815 | 36.5139 | 35.3315 | 34.5012 | 34.8141 | 35.5887 | 34.7896 | 34.9123 | 37.7951 | 36.9959 | 34.8061 | 34.8846 | 36.9937 | 37.3331 | 38.2952 | 36.983 | 35.3364 | 35.3618 | 36.6581 | 36.7917 | 35.1077 | 34.4725 | 33.719 | 35.0921 | 33.6061 | 34.0978 | 33.8268 | 34.6351 | 33.6056 | 35.0025 | 36.4166 | 34.847 | 35.1103 | 35.643 | 92.0388 | 92.3117 | 92.4329
2022-09-07 23:17 | 1:27 | 19.8145 | 19.9278 | 21.7618 | 36.2466 | 34.245 | 36.0306 | 35.842 | 36.1523 | 37.1223 | 36.7723 | 36.1756 | 36.7998 | 34.9646 | 34.797 | 36.4764 | 36.14 | 37.7321 | 37.1092 | 37.559 | 37.8798 | 25.71 | 20.6884 | 94.851 | 34.6376 | 35.2781 | 36.5304 | 35.3572 | 34.5129 | 34.8054 | 35.5931 | 34.7798 | 34.9187 | 37.7773 | 36.9873 | 34.801 | 34.9064 | 36.9644 | 37.3437 | 38.2788 | 37.0008 | 35.3396 | 35.3382 | 36.6529 | 36.7962 | 35.1129 | 34.462 | 33.6809 | 35.0962 | 33.615 | 34.1039 | 33.7959 | 34.6127 | 33.6312 | 34.9993 | 36.3959 | 34.8407 | 35.1036 | 35.6322 | 92.1234 | 92.3525 | 92.5234
2022-09-07 23:17 | 1:27 | 19.8083 | 19.9324 | 21.7854 | 36.1259 | 34.2344 | 36.0461 | 35.841 | 36.157 | 37.1053 | 36.7756 | 36.1604 | 36.8157 | 34.9492 | 34.7795 | 36.4636 | 36.117 | 37.7131 | 37.1136 | 37.5702 | 37.8699 | 25.7029 | 20.6913 | 94.6739 | 34.5212 | 35.2567 | 36.5088 | 35.3641 | 34.5048 | 34.7933 | 35.6087 | 34.7817 | 34.9138 | 37.7686 | 36.9781 | 34.8037 | 34.8914 | 36.9959 | 37.3341 | 38.2769 | 36.9958 | 35.338 | 35.3278 | 36.6318 | 36.7905 | 35.1103 | 34.4569 | 33.6838 | 35.1026 | 33.6136 | 34.0886 | 33.8306 | 34.6099 | 33.6202 | 34.9833 | 36.403 | 34.8208 | 35.1046 | 35.6101 | 92.245 | 92.4711 | 92.5225
2022-09-07 23:17 | 1:27 | 19.8154 | 19.9478 | 21.864 | 36.2565 | 34.2458 | 36.0454 | 35.8291 | 36.1403 | 37.1046 | 36.7875 | 36.155 | 36.7937 | 34.9619 | 34.7642 | 36.4503 | 36.1139 | 37.6974 | 37.1091 | 37.5767 | 37.8565 | 25.7257 | 20.6474 | 94.5055 | 34.5084 | 35.2769 | 36.5062 | 35.3589 | 34.5095 | 34.8078 | 35.5968 | 34.7966 | 34.9173 | 37.7713 | 36.9573 | 34.8012 | 34.8683 | 36.9873 | 37.3333 | 38.2637 | 36.9937 | 35.3316 | 35.3349 | 36.6175 | 36.77 | 35.1172 | 34.4577 | 33.6883 | 35.0694 | 33.5915 | 34.0968 | 33.8223 | 34.5942 | 33.6221 | 34.9839 | 36.4083 | 34.8598 | 35.1177 | 35.609 | 92.3902 | 92.6036 | 92.5979
2022-09-07 23:17 | 1:27 | 19.8431 | 19.9921 | 21.8021 | 36.1819 | 34.2293 | 36.0387 | 35.8476 | 36.1453 | 37.0988 | 36.784 | 36.1536 | 36.7926 | 34.9474 | 34.7534 | 36.4462 | 36.1201 | 37.705 | 37.1389 | 37.5578 | 37.8524 | 25.7098 | 20.6626 | 94.3539 | 34.5324 | 35.2753 | 36.5221 | 35.3364 | 34.5147 | 34.8061 | 35.6093 | 34.7816 | 34.9037 | 37.7703 | 36.967 | 34.8047 | 34.8868 | 36.9781 | 37.3411 | 38.2507 | 36.9644 | 35.3341 | 35.31 | 36.5995 | 36.7649 | 35.1085 | 34.4593 | 33.6807 | 35.0781 | 33.609 | 34.1002 | 33.8192 | 34.5904 | 33.6138 | 34.9867 | 36.4025 | 34.8447 | 35.0997 | 35.6021 | 92.5253 | 92.7284 | 92.7457
2022-09-07 23:17 | 1:27 | 19.7888 | 19.9216 | 21.8195 | 36.1789 | 34.2293 | 36.0433 | 35.8535 | 36.1414 | 37.1028 | 36.7689 | 36.1673 | 36.812 | 34.9406 | 34.7552 | 36.4413 | 36.1307 | 37.6986 | 37.1192 | 37.55 | 37.8679 | 25.7363 | 20.6387 | 94.4026 | 34.5595 | 35.2685 | 36.5156 | 35.3396 | 34.526 | 34.801 | 35.6079 | 34.7945 | 34.9141 | 37.7808 | 36.9646 | 34.8046 | 34.8939 | 36.9573 | 37.3293 | 38.2645 | 36.9959 | 35.3108 | 35.3111 | 36.5984 | 36.7485 | 35.0778 | 34.4451 | 33.6724 | 35.0708 | 33.5853 | 34.1026 | 33.8055 | 34.5963 | 33.6165 | 34.9978 | 36.4116 | 34.8724 | 35.1072 | 35.6066 | 92.6699 | 92.7823 | 92.8043
2022-09-07 23:18 | 1:28 | 19.7821 | 19.9286 | 21.8489 | 36.1315 | 34.2274 | 36.0314 | 35.8539 | 36.142 | 37.0969 | 36.7788 | 36.1658 | 36.8247 | 34.9444 | 34.7563 | 36.4325 | 36.1295 | 37.6964 | 37.1292 | 37.5305 | 37.8609 | 25.7232 | 20.6323 | 94.4402 | 34.6199 | 35.2589 | 36.5131 | 35.338 | 34.5112 | 34.8037 | 35.6121 | 34.8049 | 34.9177 | 37.7846 | 36.9788 | 34.7964 | 34.8922 | 36.967 | 37.3445 | 38.2407 | 36.9873 | 35.3362 | 35.3034 | 36.5886 | 36.749 | 35.0944 | 34.4578 | 33.6771 | 35.0427 | 33.5788 | 34.0938 | 33.8223 | 34.5804 | 33.6028 | 34.9761 | 36.4234 | 34.868 | 35.1025 | 35.5822 | 92.6911 | 92.9202 | 92.8409
2022-09-07 23:18 | 1:28 | 19.8143 | 19.9611 | 21.7551 | 36.1393 | 34.2058 | 36.0422 | 35.8495 | 36.1365 | 37.1006 | 36.7982 | 36.17 | 36.826 | 34.9294 | 34.7198 | 36.4339 | 36.1312 | 37.6833 | 37.1242 | 37.5622 | 37.8563 | 25.7201 | 20.6633 | 94.3947 | 34.4901 | 35.2651 | 36.5028 | 35.3316 | 34.5078 | 34.8012 | 35.6061 | 34.7918 | 34.9284 | 37.7599 | 36.9481 | 34.7897 | 34.8796 | 36.9646 | 37.328 | 38.2583 | 36.9781 | 35.343 | 35.2859 | 36.6076 | 36.7479 | 35.1079 | 34.4566 | 33.6677 | 35.0619 | 33.5746 | 34.097 | 33.7874 | 34.5973 | 33.6093 | 34.9802 | 36.4013 | 34.8522 | 35.1273 | 35.5852 | 92.8913 | 93.0235 | 92.8755
2022-09-07 23:18 | 1:28 | 19.8152 | 19.9694 | 21.7097 | 36.2062 | 34.2118 | 36.0329 | 35.8575 | 36.1614 | 37.1053 | 36.7922 | 36.1755 | 36.8356 | 34.938 | 34.7292 | 36.427 | 36.1228 | 37.6789 | 37.1196 | 37.5647 | 37.8503 | 25.7081 | 20.6472 | 94.3134 | 34.6334 | 35.2595 | 36.4942 | 35.3341 | 34.53 | 34.8047 | 35.5954 | 34.7918 | 34.9125 | 37.7775 | 36.9677 | 34.8206 | 34.9072 | 36.9788 | 37.3304 | 38.257 | 36.9573 | 35.3169 | 35.289 | 36.5888 | 36.7406 | 35.08 | 34.4468 | 33.6687 | 35.0376 | 33.5666 | 34.1029 | 33.8217 | 34.5784 | 33.6041 | 34.9967 | 36.4012 | 34.8753 | 35.1118 | 35.5789 | 93.0571 | 93.1324 | 93.0008
2022-09-07 23:18 | 1:28 | 19.7583 | 19.9232 | 21.6707 | 36.2429 | 34.221 | 36.0321 | 35.8585 | 36.1316 | 37.0885 | 36.8131 | 36.1643 | 36.8294 | 34.9093 | 34.7255 | 36.4243 | 36.1293 | 37.6864 | 37.1163 | 37.5575 | 37.8635 | 25.7224 | 20.633 | 94.2744 | 34.3686 | 35.2518 | 36.5131 | 35.3108 | 34.5261 | 34.8046 | 35.6086 | 34.7984 | 34.9337 | 37.7733 | 36.9689 | 34.797 | 34.8868 | 36.9481 | 37.3435 | 38.2452 | 36.967 | 35.3432 | 35.2898 | 36.5722 | 36.7323 | 35.0829 | 34.4566 | 33.6475 | 35.0576 | 33.5704 | 34.101 | 33.8206 | 34.5747 | 33.5937 | 34.9855 | 36.4109 | 34.8634 | 35.097 | 35.5834 | 93.214 | 93.312 | 93.1337
2022-09-07 23:18 | 1:28 | 19.8165 | 19.9571 | 21.7724 | 36.0919 | 34.2168 | 36.0288 | 35.8681 | 36.145 | 37.1043 | 36.8071 | 36.1892 | 36.8292 | 34.926 | 34.7028 | 36.4231 | 36.1299 | 37.6706 | 37.1428 | 37.5736 | 37.8606 | 25.7142 | 20.6228 | 94.2322 | 34.3756 | 35.257 | 36.4916 | 35.3362 | 34.5184 | 34.7964 | 35.6009 | 34.8135 | 34.9364 | 37.7651 | 36.9826 | 34.811 | 34.9012 | 36.9677 | 37.3468 | 38.2273 | 36.9646 | 35.3303 | 35.2738 | 36.5815 | 36.7293 | 35.0872 | 34.4503 | 33.6625 | 35.0551 | 33.582 | 34.0967 | 33.8082 | 34.5758 | 33.5888 | 35.0025 | 36.4124 | 34.8511 | 35.1228 | 35.5862 | 93.335 | 93.4525 | 93.1194
2022-09-07 23:18 | 1:28 | 19.832 | 19.968 | 21.7041 | 36.1536 | 34.2081 | 36.029 | 35.849 | 36.1574 | 37.1001 | 36.8192 | 36.1889 | 36.8445 | 34.917 | 34.6739 | 36.4072 | 36.1427 | 37.6824 | 37.1287 | 37.5761 | 37.8409 | 25.7132 | 20.6429 | 94.1979 | 34.6189 | 35.2499 | 36.4876 | 35.343 | 34.5276 | 34.7897 | 35.6121 | 34.8213 | 34.9154 | 37.7633 | 36.9637 | 34.7999 | 34.882 | 36.9689 | 37.3507 | 38.2392 | 36.9788 | 35.3366 | 35.2679 | 36.5721 | 36.7355 | 35.0938 | 34.4472 | 33.6573 | 35.0467 | 33.5776 | 34.0987 | 33.7996 | 34.5725 | 33.6046 | 34.9742 | 36.4127 | 34.8801 | 35.1001 | 35.5583 | 93.5244 | 93.6239 | 93.2815
2022-09-07 23:19 | 1:28 | 19.7826 | 19.8996 | 21.7127 | 36.1786 | 34.2366 | 36.0127 | 35.8678 | 36.138 | 37.105 | 36.831 | 36.2012 | 36.8476 | 34.9021 | 34.6825 | 36.4029 | 36.1341 | 37.6563 | 37.1295 | 37.5456 | 37.8659 | 25.6733 | 20.6205 | 94.2184 | 34.5397 | 35.2552 | 36.4984 | 35.3169 | 34.5172 | 34.8206 | 35.6105 | 34.8327 | 34.9211 | 37.7704 | 36.9668 | 34.8186 | 34.9008 | 36.9826 | 37.344 | 38.2363 | 36.9481 | 35.329 | 35.2666 | 36.575 | 36.7406 | 35.087 | 34.4433 | 33.669 | 35.0195 | 33.562 | 34.0936 | 33.8084 | 34.5874 | 33.5656 | 34.9966 | 36.404 | 34.88 | 35.1223 | 35.5692 | 93.6889 | 93.8249 | 93.3633
2022-09-07 23:19 | 1:29 | 19.7217 | 19.8368 | 21.6575 | 36.119 | 34.1915 | 36.0294 | 35.8693 | 36.1687 | 37.1099 | 36.8202 | 36.2009 | 36.8458 | 34.9083 | 34.6846 | 36.4269 | 36.1196 | 37.6565 | 37.1407 | 37.5525 | 37.8327 | 25.6544 | 20.5786 | 94.2177 | 34.4001 | 35.2594 | 36.5013 | 35.3432 | 34.5349 | 34.797 | 35.6354 | 34.8302 | 34.92 | 37.7703 | 36.9647 | 34.8073 | 34.9095 | 36.9637 | 37.3702 | 38.2278 | 36.9677 | 35.3157 | 35.2429 | 36.5591 | 36.7227 | 35.0769 | 34.4488 | 33.6317 | 35.0233 | 33.5603 | 34.0966 | 33.8053 | 34.5799 | 33.5857 | 34.9917 | 36.4294 | 34.8596 | 35.1208 | 35.5484 | 93.8397 | 94.0897 | 93.5188
2022-09-07 23:19 | 1:29 | 19.7418 | 19.8853 | 21.602 | 36.038 | 34.2127 | 36.0161 | 35.8532 | 36.168 | 37.093 | 36.8292 | 36.1998 | 36.8773 | 34.9127 | 34.6813 | 36.4066 | 36.1362 | 37.686 | 37.1419 | 37.5364 | 37.8741 | 25.6521 | 20.5741 | 94.1401 | 34.392 | 35.2703 | 36.5129 | 35.3303 | 34.5088 | 34.811 | 35.6281 | 34.829 | 34.9342 | 37.7845 | 36.9646 | 34.8067 | 34.901 | 36.9668 | 37.3346 | 38.2325 | 36.9689 | 35.3278 | 35.2408 | 36.5382 | 36.7438 | 35.0769 | 34.4307 | 33.6446 | 35.0221 | 33.5741 | 34.0977 | 33.7991 | 34.5686 | 33.5898 | 34.9781 | 36.3922 | 34.886 | 35.1562 | 35.5498 | 94.1017 | 94.2172 | 93.7217
2022-09-07 23:19 | 1:29 | 19.7412 | 19.8609 | 21.6743 | 36.1171 | 34.2219 | 36.0148 | 35.857 | 36.1658 | 37.0932 | 36.8407 | 36.2141 | 36.8663 | 34.8952 | 34.6676 | 36.4232 | 36.1291 | 37.6686 | 37.1484 | 37.5525 | 37.868 | 25.6232 | 20.5646 | 94.1583 | 34.5531 | 35.2432 | 36.4903 | 35.3366 | 34.5318 | 34.7999 | 35.6259 | 34.8248 | 34.9272 | 37.7868 | 36.9652 | 34.8087 | 34.898 | 36.9647 | 37.3502 | 38.2344 | 36.9826 | 35.3067 | 35.2391 | 36.5484 | 36.7176 | 35.0765 | 34.4567 | 33.637 | 35.0127 | 33.5632 | 34.0829 | 33.8028 | 34.572 | 33.5907 | 34.9999 | 36.4154 | 34.8941 | 35.1138 | 35.5437 | 94.152 | 94.3978 | 93.6039
2022-09-07 23:19 | 1:29 | 19.711 | 19.8273 | 21.671 | 36.1759 | 34.2135 | 36.0164 | 35.8709 | 36.1528 | 37.0917 | 36.8199 | 36.2189 | 36.8663 | 34.9068 | 34.669 | 36.4172 | 36.1337 | 37.6463 | 37.1526 | 37.5643 | 37.8427 | 25.6043 | 20.5298 | 94.0666 | 34.3825 | 35.2574 | 36.4936 | 35.329 | 34.5088 | 34.8186 | 35.6248 | 34.8201 | 34.9272 | 37.7649 | 36.9698 | 34.8156 | 34.9078 | 36.9646 | 37.3621 | 38.2413 | 36.9637 | 35.3056 | 35.2278 | 36.5417 | 36.7248 | 35.0739 | 34.4334 | 33.6382 | 35.03 | 33.5584 | 34.0864 | 33.7889 | 34.5638 | 33.5859 | 34.9998 | 36.4081 | 34.8974 | 35.1362 | 35.5491 | 94.3647 | 94.4901 | 93.784
2022-09-07 23:19 | 1:29 | 19.7061 | 19.8396 | 21.6805 | 36.1938 | 34.1784 | 36.0387 | 35.8608 | 36.1737 | 37.1005 | 36.8387 | 36.2163 | 36.8551 | 34.8871 | 34.6677 | 36.4093 | 36.1428 | 37.6495 | 37.1467 | 37.5487 | 37.8572 | 25.5742 | 20.5057 | 94.0679 | 34.379 | 35.2253 | 36.4874 | 35.3157 | 34.5225 | 34.8073 | 35.6295 | 34.8448 | 34.915 | 37.7942 | 36.9635 | 34.8069 | 34.9168 | 36.9652 | 37.342 | 38.2284 | 36.9668 | 35.3113 | 35.2282 | 36.5386 | 36.7316 | 35.0733 | 34.4463 | 33.6333 | 35.0335 | 33.5909 | 34.1142 | 33.7923 | 34.5585 | 33.5887 | 35.0073 | 36.4135 | 34.8866 | 35.1448 | 35.5278 | 94.4822 | 94.6658 | 93.8203
2022-09-07 23:20 | 1:30 | 19.6574 | 19.7694 | 21.6686 | 36.1886 | 34.2059 | 36.0203 | 35.8509 | 36.1861 | 37.0912 | 36.8346 | 36.2403 | 36.8826 | 34.8818 | 34.6486 | 36.3859 | 36.1431 | 37.6461 | 37.1356 | 37.5527 | 37.8466 | 25.5656 | 20.5011 | 94.1343 | 34.4251 | 35.2238 | 36.5098 | 35.3278 | 34.5342 | 34.8067 | 35.6293 | 34.8536 | 34.9239 | 37.778 | 36.951 | 34.8045 | 34.888 | 36.9698 | 37.3364 | 38.2107 | 36.9647 | 35.3201 | 35.2181 | 36.5377 | 36.7147 | 35.0588 | 34.4521 | 33.6409 | 35.0088 | 33.575 | 34.1351 | 33.7914 | 34.5711 | 33.6045 | 35.0078 | 36.4137 | 34.8891 | 35.1608 | 35.5579 | 94.6362 | 94.7621 | 93.9889
2022-09-07 23:20 | 1:30 | 19.6244 | 19.7765 | 21.6806 | 36.133 | 34.1933 | 36.004 | 35.8524 | 36.1689 | 37.0889 | 36.8393 | 36.2477 | 36.8956 | 34.8776 | 34.6692 | 36.4049 | 36.1466 | 37.6439 | 37.1437 | 37.5568 | 37.8586 | 25.57 | 20.468 | 94.0515 | 34.5319 | 35.2455 | 36.4856 | 35.3067 | 34.5182 | 34.8087 | 35.6294 | 34.852 | 34.9279 | 37.7914 | 36.9473 | 34.7998 | 34.9116 | 36.9635 | 37.3588 | 38.2377 | 36.9646 | 35.3261 | 35.2336 | 36.536 | 36.7304 | 35.0551 | 34.4561 | 33.6287 | 35.0157 | 33.5717 | 34.0948 | 33.7774 | 34.5832 | 33.5892 | 35.0041 | 36.4164 | 34.8958 | 35.1463 | 35.5634 | 94.7619 | 94.8727 | 94.1228
2022-09-07 23:20 | 1:30 | 19.6126 | 19.7559 | 21.6097 | 36.0829 | 34.1998 | 36.0041 | 35.8631 | 36.1524 | 37.0984 | 36.8493 | 36.2316 | 36.9068 | 34.894 | 34.6198 | 36.3868 | 36.1554 | 37.6407 | 37.1445 | 37.5407 | 37.839 | 25.5237 | 20.4625 | 93.8831 | 34.4331 | 35.2613 | 36.4999 | 35.3056 | 34.5397 | 34.8156 | 35.6283 | 34.8494 | 34.9523 | 37.7644 | 36.9501 | 34.809 | 34.9158 | 36.951 | 37.3602 | 38.225 | 36.9652 | 35.3381 | 35.2131 | 36.5192 | 36.7272 | 35.0505 | 34.4321 | 33.6252 | 35.0227 | 33.5699 | 34.1088 | 33.7781 | 34.5784 | 33.5894 | 35.007 | 36.4144 | 34.9048 | 35.1527 | 35.5606 | 94.8769 | 94.9841 | 94.0641
2022-09-07 23:20 | 1:30 | 19.6262 | 19.7511 | 21.6413 | 36.0107 | 34.2096 | 36.0077 | 35.8737 | 36.1754 | 37.0831 | 36.8448 | 36.2419 | 36.8962 | 34.8805 | 34.6398 | 36.4027 | 36.1539 | 37.658 | 37.14 | 37.5699 | 37.8362 | 25.5349 | 20.4587 | 93.76 | 34.3956 | 35.2533 | 36.5002 | 35.3113 | 34.5289 | 34.8069 | 35.645 | 34.845 | 34.9368 | 37.7666 | 36.9807 | 34.8037 | 34.9226 | 36.9473 | 37.3439 | 38.2164 | 36.9698 | 35.3181 | 35.2135 | 36.5289 | 36.7288 | 35.043 | 34.439 | 33.606 | 34.9948 | 33.5709 | 34.0921 | 33.8038 | 34.5502 | 33.575 | 35.0057 | 36.3997 | 34.9129 | 35.179 | 35.5441 | 95.0045 | 95.0639 | 94.256
2022-09-07 23:20 | 1:30 | 19.6029 | 19.746 | 21.6408 | 36.0621 | 34.1923 | 36.0264 | 35.8732 | 36.1653 | 37.098 | 36.8517 | 36.2394 | 36.9115 | 34.8761 | 34.6084 | 36.4186 | 36.1376 | 37.642 | 37.1634 | 37.5865 | 37.8311 | 25.5129 | 20.4248 | 93.6391 | 34.4781 | 35.2416 | 36.476 | 35.3201 | 34.5264 | 34.8045 | 35.6386 | 34.8526 | 34.9371 | 37.776 | 36.9499 | 34.8105 | 34.9143 | 36.9501 | 37.358 | 38.2234 | 36.9635 | 35.3151 | 35.2171 | 36.504 | 36.7182 | 35.0364 | 34.4377 | 33.6056 | 34.9807 | 33.5631 | 34.116 | 33.797 | 34.5733 | 33.5856 | 35.0245 | 36.408 | 34.9225 | 35.1664 | 35.547 | 94.9779 | 95.1413 | 94.1716
2022-09-07 23:20 | 1:30 | 19.6069 | 19.7436 | 21.6367 | 36.08 | 34.1778 | 36.0073 | 35.8701 | 36.1796 | 37.0883 | 36.8602 | 36.2396 | 36.9163 | 34.8803 | 34.6314 | 36.4021 | 36.1608 | 37.6433 | 37.1562 | 37.5689 | 37.8398 | 25.4871 | 20.4278 | 93.5599 | 34.4411 | 35.2454 | 36.4797 | 35.3261 | 34.5346 | 34.7998 | 35.6403 | 34.8678 | 34.9482 | 37.771 | 36.9605 | 34.8105 | 34.9227 | 36.9807 | 37.3692 | 38.2342 | 36.951 | 35.3209 | 35.1999 | 36.5068 | 36.6965 | 35.0351 | 34.4175 | 33.6033 | 34.9989 | 33.5848 | 34.1016 | 33.7863 | 34.5664 | 33.5922 | 35.0072 | 36.4073 | 34.9087 | 35.1551 | 35.5417 | 94.9502 | 95.068 | 94.1496
2022-09-07 23:21 | 1:30 | 19.5635 | 19.7077 | 21.6359 | 35.9965 | 34.1852 | 36.0205 | 35.885 | 36.1656 | 37.0927 | 36.8545 | 36.2374 | 36.9233 | 34.8687 | 34.625 | 36.3857 | 36.1634 | 37.6356 | 37.1589 | 37.5731 | 37.8473 | 25.4669 | 20.3604 | 93.4318 | 34.512 | 35.2126 | 36.489 | 35.3381 | 34.5462 | 34.809 | 35.6574 | 34.8486 | 34.9345 | 37.7901 | 36.9548 | 34.8068 | 34.9343 | 36.9499 | 37.3449 | 38.229 | 36.9473 | 35.2958 | 35.1918 | 36.5307 | 36.7228 | 35.0414 | 34.4455 | 33.6025 | 35.0035 | 33.587 | 34.0897 | 33.7819 | 34.571 | 33.5739 | 35.0036 | 36.4218 | 34.9192 | 35.1825 | 35.5377 | 94.7116 | 94.8839 | 93.9065
2022-09-07 23:21 | 1:31 | 19.5706 | 19.6992 | 21.6298 | 36.0336 | 34.1835 | 35.9958 | 35.8743 | 36.1778 | 37.0806 | 36.8572 | 36.2422 | 36.9118 | 34.8746 | 34.5933 | 36.3844 | 36.1577 | 37.6309 | 37.1559 | 37.5671 | 37.8218 | 25.4395 | 20.3333 | 93.2435 | 34.4352 | 35.2254 | 36.4832 | 35.3181 | 34.5284 | 34.8037 | 35.6422 | 34.8661 | 34.9325 | 37.7814 | 36.9549 | 34.7865 | 34.9239 | 36.9605 | 37.3633 | 38.1988 | 36.9501 | 35.2996 | 35.2049 | 36.5198 | 36.7251 | 35.0338 | 34.4333 | 33.6084 | 34.983 | 33.5793 | 34.1101 | 33.7881 | 34.5414 | 33.5807 | 35.0269 | 36.4272 | 34.9264 | 35.1592 | 35.5242 | 94.4594 | 94.6212 | 93.7898
2022-09-07 23:21 | 1:31 | 19.5019 | 19.6139 | 21.5745 | 36.0176 | 34.1891 | 36.0159 | 35.8733 | 36.1887 | 37.0853 | 36.8499 | 36.2444 | 36.9172 | 34.8516 | 34.5871 | 36.411 | 36.1627 | 37.6238 | 37.1632 | 37.573 | 37.8396 | 25.4466 | 20.3083 | 93.1258 | 34.3802 | 35.2262 | 36.483 | 35.3151 | 34.5297 | 34.8105 | 35.663 | 34.838 | 34.9538 | 37.7831 | 36.9436 | 34.7961 | 34.9328 | 36.9548 | 37.3734 | 38.2426 | 36.9807 | 35.3116 | 35.1988 | 36.5037 | 36.7461 | 35.0114 | 34.4184 | 33.5832 | 34.9834 | 33.579 | 34.0933 | 33.7946 | 34.5408 | 33.5776 | 35.0318 | 36.4063 | 34.9263 | 35.163 | 35.537 | 94.1806 | 94.4029 | 93.6082
2022-09-07 23:21 | 1:31 | 19.4783 | 19.5819 | 21.5666 | 35.9899 | 34.1527 | 36.0095 | 35.8869 | 36.1912 | 37.0883 | 36.8522 | 36.2612 | 36.914 | 34.8528 | 34.5915 | 36.3807 | 36.1624 | 37.6318 | 37.1483 | 37.5623 | 37.8357 | 25.4264 | 20.2633 | 92.9776 | 34.583 | 35.2189 | 36.4846 | 35.3209 | 34.5234 | 34.8105 | 35.6398 | 34.8661 | 34.9507 | 37.7732 | 36.932 | 34.795 | 34.9377 | 36.9549 | 37.3715 | 38.2035 | 36.9499 | 35.3057 | 35.1786 | 36.5204 | 36.7174 | 35.0257 | 34.4355 | 33.5923 | 34.9756 | 33.5758 | 34.1185 | 33.7684 | 34.5401 | 33.5802 | 35.0425 | 36.4067 | 34.9205 | 35.19 | 35.5398 | 94.0422 | 94.1526 | 93.5132
2022-09-07 23:21 | 1:31 | 19.4563 | 19.5133 | 21.4972 | 35.9781 | 34.1714 | 36.0074 | 35.8818 | 36.1772 | 37.101 | 36.8784 | 36.2716 | 36.9399 | 34.8535 | 34.5883 | 36.3917 | 36.1653 | 37.6132 | 37.1723 | 37.5835 | 37.8474 | 25.4118 | 20.2479 | 92.8489 | 34.5532 | 35.21 | 36.4839 | 35.2958 | 34.5268 | 34.8068 | 35.6366 | 34.8726 | 34.9522 | 37.7888 | 36.9508 | 34.8121 | 34.9318 | 36.9436 | 37.3602 | 38.2084 | 36.9605 | 35.3033 | 35.1892 | 36.4978 | 36.7251 | 35.0087 | 34.4332 | 33.5879 | 34.9757 | 33.5763 | 34.113 | 33.7995 | 34.5549 | 33.5851 | 35.0526 | 36.4119 | 34.9421 | 35.1633 | 35.5399 | 93.9086 | 94.0656 | 93.4307
2022-09-07 23:21 | 1:31 | 19.4372 | 19.5881 | 21.4786 | 36.0676 | 34.1788 | 35.9912 | 35.8783 | 36.1923 | 37.0845 | 36.8679 | 36.2691 | 36.9449 | 34.856 | 34.5718 | 36.3835 | 36.1532 | 37.5967 | 37.1669 | 37.5873 | 37.8458 | 25.3826 | 20.232 | 92.7058 | 34.4787 | 35.2132 | 36.4849 | 35.2996 | 34.5562 | 34.7865 | 35.6504 | 34.8667 | 34.9398 | 37.7863 | 36.9384 | 34.7942 | 34.935 | 36.932 | 37.3627 | 38.1992 | 36.9548 | 35.3226 | 35.1658 | 36.4899 | 36.7318 | 35.0159 | 34.4265 | 33.6079 | 34.9759 | 33.5895 | 34.0977 | 33.801 | 34.5453 | 33.5796 | 35.0583 | 36.4186 | 34.9468 | 35.1866 | 35.5394 | 93.7223 | 93.9321 | 93.3809
2022-09-07 23:22 | 1:32 | 19.4291 | 19.5407 | 21.4011 | 36.0499 | 34.1669 | 35.9875 | 35.8844 | 36.1889 | 37.104 | 36.8675 | 36.276 | 36.9389 | 34.8478 | 34.5482 | 36.3726 | 36.1656 | 37.5907 | 37.1748 | 37.5833 | 37.826 | 25.3741 | 20.152 | 92.6232 | 34.3654 | 35.2187 | 36.4839 | 35.3116 | 34.531 | 34.7961 | 35.6591 | 34.8749 | 34.9635 | 37.7941 | 36.9387 | 34.8136 | 34.8971 | 36.9508 | 37.3642 | 38.2316 | 36.9549 | 35.3157 | 35.1678 | 36.4983 | 36.7218 | 35.0024 | 34.4158 | 33.5731 | 34.9716 | 33.5724 | 34.09 | 33.7724 | 34.553 | 33.5822 | 35.028 | 36.4153 | 34.9526 | 35.1948 | 35.5433 | 93.6636 | 93.8253 | 93.2976
2022-09-07 23:22 | 1:32 | 19.3102 | 19.4994 | 21.3189 | 35.9823 | 34.1631 | 35.9953 | 35.8806 | 36.1767 | 37.0962 | 36.8659 | 36.2806 | 36.9518 | 34.8487 | 34.5585 | 36.3755 | 36.173 | 37.6015 | 37.1799 | 37.578 | 37.8363 | 25.36 | 20.0913 | 92.5132 | 34.34 | 35.2115 | 36.4788 | 35.3057 | 34.5217 | 34.795 | 35.6474 | 34.8739 | 34.9547 | 37.7851 | 36.9447 | 34.7928 | 34.9353 | 36.9384 | 37.3668 | 38.2026 | 36.9436 | 35.2776 | 35.183 | 36.4868 | 36.7189 | 35.0001 | 34.4145 | 33.5779 | 34.9865 | 33.5735 | 34.1129 | 33.7863 | 34.5714 | 33.5815 | 35.0455 | 36.3907 | 34.9471 | 35.1971 | 35.5256 | 93.5388 | 93.7502 | 93.2354
2022-09-07 23:22 | 1:32 | 19.3533 | 19.5066 | 21.389 | 35.9005 | 34.1544 | 35.9951 | 35.8862 | 36.2055 | 37.0902 | 36.886 | 36.2685 | 36.9686 | 34.8338 | 34.5374 | 36.3742 | 36.1579 | 37.6101 | 37.1965 | 37.5777 | 37.8423 | 25.3582 | 20.1179 | 92.408 | 34.2484 | 35.2121 | 36.4782 | 35.3033 | 34.535 | 34.8121 | 35.668 | 34.8687 | 34.9562 | 37.7899 | 36.9182 | 34.7859 | 34.9159 | 36.9387 | 37.3625 | 38.2146 | 36.932 | 35.2815 | 35.1462 | 36.5003 | 36.7264 | 34.9887 | 34.4145 | 33.5719 | 34.9518 | 33.5833 | 34.1108 | 33.7842 | 34.5393 | 33.5852 | 35.0479 | 36.4022 | 34.9499 | 35.2067 | 35.5356 | 93.4774 | 93.6867 | 93.2042
2022-09-07 23:22 | 1:32 | 19.3825 | 19.5337 | 21.3878 | 35.9782 | 34.1794 | 35.9949 | 35.886 | 36.1915 | 37.0789 | 36.8724 | 36.2979 | 36.9592 | 34.8418 | 34.5519 | 36.3785 | 36.17 | 37.5953 | 37.1656 | 37.584 | 37.8316 | 25.3609 | 20.1459 | 92.4824 | 34.434 | 35.2005 | 36.4734 | 35.3226 | 34.5384 | 34.7942 | 35.6649 | 34.8794 | 34.9472 | 37.789 | 36.9304 | 34.8035 | 34.9326 | 36.9447 | 37.3575 | 38.2167 | 36.9508 | 35.2807 | 35.1655 | 36.489 | 36.7106 | 34.9975 | 34.4227 | 33.5799 | 34.9567 | 33.5875 | 34.1055 | 33.7948 | 34.5537 | 33.5824 | 35.0579 | 36.417 | 34.9454 | 35.2 | 35.5363 | 93.4657 | 93.624 | 93.2248
2022-09-07 23:22 | 1:32 | 19.368 | 19.5127 | 21.3769 | 36.0379 | 34.145 | 35.9976 | 35.8701 | 36.201 | 37.1022 | 36.8902 | 36.2917 | 36.9632 | 34.8365 | 34.5365 | 36.3605 | 36.1808 | 37.6109 | 37.1814 | 37.5743 | 37.8349 | 25.3641 | 20.1396 | 92.5171 | 34.2778 | 35.2162 | 36.4395 | 35.3157 | 34.5386 | 34.8136 | 35.6701 | 34.8757 | 34.939 | 37.7874 | 36.9258 | 34.791 | 34.9326 | 36.9182 | 37.3607 | 38.2318 | 36.9384 | 35.2701 | 35.1567 | 36.4772 | 36.7218 | 34.977 | 34.4188 | 33.5658 | 34.9633 | 33.5704 | 34.063 | 33.785 | 34.5397 | 33.5755 | 35.0651 | 36.4128 | 34.9613 | 35.2125 | 35.5353 | 93.4357 | 93.5798 | 93.2233
2022-09-07 23:22 | 1:32 | 19.3108 | 19.4616 | 21.26 | 35.9416 | 34.1437 | 35.9772 | 35.881 | 36.1989 | 37.0777 | 36.8971 | 36.28 | 36.9664 | 34.8296 | 34.5112 | 36.3647 | 36.1575 | 37.6063 | 37.1924 | 37.5741 | 37.8433 | 25.3187 | 20.1141 | 92.6263 | 34.2299 | 35.2189 | 36.449 | 35.2776 | 34.5328 | 34.7928 | 35.6756 | 34.8604 | 34.9601 | 37.7749 | 36.9027 | 34.8075 | 34.9392 | 36.9304 | 37.3608 | 38.2088 | 36.9387 | 35.268 | 35.1667 | 36.4528 | 36.7088 | 34.9826 | 34.3866 | 33.5448 | 34.9582 | 33.5855 | 34.084 | 33.785 | 34.546 | 33.5772 | 35.0618 | 36.4038 | 34.9618 | 35.2181 | 35.5402 | 93.3705 | 93.5376 | 93.211
2022-09-07 23:23 | 1:32 | 19.3002 | 19.4421 | 21.2823 | 35.8871 | 34.1348 | 35.977 | 35.8951 | 36.1905 | 37.0889 | 36.8926 | 36.3075 | 36.9628 | 34.8146 | 34.5138 | 36.3822 | 36.1727 | 37.5852 | 37.1762 | 37.5862 | 37.8586 | 25.2952 | 20.0836 | 92.7318 | 34.2885 | 35.2128 | 36.4566 | 35.2815 | 34.5272 | 34.7859 | 35.6604 | 34.8652 | 34.9428 | 37.7756 | 36.9178 | 34.7722 | 34.931 | 36.9258 | 37.3685 | 38.1971 | 36.9447 | 35.273 | 35.146 | 36.4785 | 36.723 | 34.9733 | 34.4416 | 33.5501 | 34.9626 | 33.5573 | 34.1007 | 33.7833 | 34.5361 | 33.5933 | 35.049 | 36.4059 | 34.9665 | 35.2218 | 35.5471 | 93.2856 | 93.4421 | 93.078
2022-09-07 23:23 | 1:33 | 19.2829 | 19.397 | 21.2563 | 35.9785 | 34.1532 | 35.9757 | 35.8831 | 36.2045 | 37.0801 | 36.9056 | 36.3066 | 36.9683 | 34.8071 | 34.4933 | 36.3625 | 36.1511 | 37.5887 | 37.1855 | 37.5849 | 37.8333 | 25.2321 | 20.059 | 92.8722 | 34.2607 | 35.2088 | 36.4414 | 35.2807 | 34.5163 | 34.8035 | 35.6655 | 34.8665 | 34.9713 | 37.787 | 36.9036 | 34.8016 | 34.9243 | 36.9027 | 37.3701 | 38.1902 | 36.9182 | 35.2514 | 35.1283 | 36.4717 | 36.7085 | 34.9713 | 34.4127 | 33.5571 | 34.9392 | 33.5679 | 34.1057 | 33.7564 | 34.5429 | 33.584 | 35.0693 | 36.4019 | 34.9823 | 35.2162 | 35.5329 | 93.1806 | 93.3497 | 92.9942
2022-09-07 23:23 | 1:33 | 19.2314 | 19.3597 | 21.1881 | 35.7688 | 34.1322 | 35.9606 | 35.8806 | 36.1945 | 37.057 | 36.902 | 36.2891 | 36.9419 | 34.8053 | 34.4938 | 36.3317 | 36.1478 | 37.5706 | 37.1945 | 37.5716 | 37.8422 | 25.2022 | 20.0362 | 92.8068 | 34.2809 | 35.1886 | 36.4315 | 35.2701 | 34.5296 | 34.791 | 35.6709 | 34.8672 | 34.9434 | 37.7824 | 36.902 | 34.7971 | 34.9367 | 36.9178 | 37.3476 | 38.1961 | 36.9304 | 35.2472 | 35.1248 | 36.4743 | 36.7045 | 34.9828 | 34.4259 | 33.5224 | 34.9438 | 33.5698 | 34.0734 | 33.7746 | 34.5575 | 33.5804 | 35.0533 | 36.4078 | 34.9832 | 35.2285 | 35.528 | 93.1186 | 93.3003 | 93.0242
2022-09-07 23:23 | 1:33 | 19.2337 | 19.3341 | 21.1922 | 35.841 | 34.1581 | 35.9583 | 35.877 | 36.1775 | 37.0939 | 36.9022 | 36.2874 | 36.9726 | 34.8086 | 34.4716 | 36.3475 | 36.1587 | 37.5729 | 37.1843 | 37.5809 | 37.8225 | 25.1636 | 20.0241 | 92.8876 | 34.2993 | 35.1833 | 36.4455 | 35.268 | 34.515 | 34.8075 | 35.6799 | 34.8687 | 34.9498 | 37.7782 | 36.9217 | 34.7807 | 34.9113 | 36.9036 | 37.3624 | 38.1945 | 36.9258 | 35.2527 | 35.133 | 36.4478 | 36.6881 | 34.9669 | 34.4147 | 33.5406 | 34.9439 | 33.5786 | 34.0947 | 33.7684 | 34.5461 | 33.5824 | 35.0558 | 36.3939 | 34.9659 | 35.227 | 35.5344 | 93.0431 | 93.2274 | 92.9733
2022-09-07 23:23 | 1:33 | 19.2486 | 19.3491 | 21.1766 | 35.8639 | 34.1412 | 35.9643 | 35.8723 | 36.1825 | 37.0943 | 36.8985 | 36.3025 | 36.9759 | 34.8064 | 34.4677 | 36.3508 | 36.1599 | 37.5501 | 37.1728 | 37.5755 | 37.8267 | 25.1375 | 20.0453 | 92.947 | 34.2896 | 35.1936 | 36.4331 | 35.273 | 34.533 | 34.7722 | 35.6897 | 34.8803 | 34.9231 | 37.7698 | 36.8896 | 34.7942 | 34.9141 | 36.902 | 37.3625 | 38.1951 | 36.9027 | 35.2691 | 35.117 | 36.4459 | 36.6979 | 34.9395 | 34.406 | 33.5191 | 34.9316 | 33.5835 | 34.0711 | 33.7565 | 34.5356 | 33.567 | 35.0735 | 36.3934 | 34.9606 | 35.2144 | 35.5214 | 92.9372 | 93.139 | 92.841
2022-09-07 23:23 | 1:33 | 19.2297 | 19.3224 | 21.2102 | 35.8455 | 34.1441 | 35.9592 | 35.8676 | 36.193 | 37.0717 | 36.9145 | 36.2981 | 36.986 | 34.7993 | 34.4634 | 36.3518 | 36.1612 | 37.5584 | 37.1797 | 37.5915 | 37.8389 | 25.1261 | 20.0138 | 93.0026 | 34.2304 | 35.2269 | 36.4372 | 35.2514 | 34.5256 | 34.8016 | 35.6763 | 34.8549 | 34.9364 | 37.7645 | 36.8945 | 34.8003 | 34.9261 | 36.9217 | 37.3643 | 38.2008 | 36.9178 | 35.2475 | 35.1113 | 36.4463 | 36.6986 | 34.9231 | 34.4066 | 33.5277 | 34.9258 | 33.5661 | 34.0691 | 33.7555 | 34.5199 | 33.5687 | 35.0543 | 36.398 | 34.9759 | 35.2067 | 35.5119 | 92.7796 | 93.0747 | 92.8133
2022-09-07 23:24 | 1:33 | 19.2592 | 19.3664 | 21.2464 | 35.9462 | 34.1391 | 35.9519 | 35.8701 | 36.1751 | 37.0715 | 36.9125 | 36.315 | 36.9769 | 34.8022 | 34.4619 | 36.3511 | 36.1493 | 37.5594 | 37.1871 | 37.5753 | 37.8375 | 25.0952 | 20.0224 | 93.0898 | 34.2894 | 35.1932 | 36.4217 | 35.2472 | 34.5118 | 34.7971 | 35.6828 | 34.8543 | 34.9408 | 37.7572 | 36.879 | 34.7869 | 34.9233 | 36.8896 | 37.3521 | 38.2075 | 36.9036 | 35.2417 | 35.107 | 36.4258 | 36.7009 | 34.933 | 34.4136 | 33.5171 | 34.9323 | 33.5715 | 34.0931 | 33.7593 | 34.5314 | 33.5597 | 35.0593 | 36.3865 | 34.9631 | 35.2252 | 35.5234 | 92.6902 | 93.0215 | 92.7911
2022-09-07 23:24 | 1:34 | 19.2176 | 19.3364 | 21.2162 | 35.8929 | 34.1438 | 35.953 | 35.867 | 36.2085 | 37.0692 | 36.9191 | 36.313 | 36.9669 | 34.7786 | 34.4671 | 36.3657 | 36.1576 | 37.5353 | 37.1852 | 37.5823 | 37.842 | 25.0542 | 19.9734 | 93.145 | 34.1354 | 35.1987 | 36.4316 | 35.2527 | 34.5328 | 34.7807 | 35.688 | 34.872 | 34.9483 | 37.7503 | 36.8906 | 34.8061 | 34.9176 | 36.8945 | 37.361 | 38.1982 | 36.902 | 35.2585 | 35.0838 | 36.4408 | 36.662 | 34.8997 | 34.3965 | 33.5348 | 34.9339 | 33.5729 | 34.0576 | 33.7655 | 34.5304 | 33.5743 | 35.075 | 36.3779 | 34.9728 | 35.229 | 35.5359 | 92.6435 | 92.8723 | 92.6982
2022-09-07 23:24 | 1:34 | 19.1913 | 19.2971 | 21.1795 | 35.8566 | 34.1412 | 35.9491 | 35.8618 | 36.184 | 37.0944 | 36.9151 | 36.3125 | 36.9761 | 34.7942 | 34.4423 | 36.35 | 36.1693 | 37.5449 | 37.1876 | 37.5801 | 37.8336 | 25.0485 | 19.9442 | 93.231 | 34.3204 | 35.1814 | 36.4169 | 35.2691 | 34.526 | 34.7942 | 35.6682 | 34.8744 | 34.9447 | 37.7715 | 36.8921 | 34.7816 | 34.9262 | 36.879 | 37.3564 | 38.196 | 36.9217 | 35.2372 | 35.0856 | 36.4471 | 36.6904 | 34.9427 | 34.4198 | 33.5048 | 34.9266 | 33.5769 | 34.0717 | 33.7479 | 34.5431 | 33.5697 | 35.0852 | 36.4016 | 34.9778 | 35.2401 | 35.5098 | 92.5115 | 92.7804 | 92.6105
2022-09-07 23:24 | 1:34 | 19.2091 | 19.3407 | 21.2239 | 35.8658 | 34.1131 | 35.9559 | 35.8674 | 36.1911 | 37.0828 | 36.9323 | 36.3186 | 36.9664 | 34.7868 | 34.4405 | 36.3361 | 36.1395 | 37.5485 | 37.1886 | 37.5785 | 37.8249 | 24.9985 | 19.9849 | 93.3987 | 34.2212 | 35.1823 | 36.4274 | 35.2475 | 34.5221 | 34.8003 | 35.6938 | 34.8705 | 34.9592 | 37.7732 | 36.8808 | 34.7981 | 34.9118 | 36.8906 | 37.3656 | 38.1956 | 36.8896 | 35.2543 | 35.0759 | 36.4233 | 36.684 | 34.9141 | 34.4169 | 33.5235 | 34.9225 | 33.5717 | 34.0769 | 33.7626 | 34.5175 | 33.5517 | 35.0763 | 36.3888 | 34.989 | 35.2476 | 35.5242 | 92.419 | 92.6504 | 92.4787
2022-09-07 23:24 | 1:34 | 19.1728 | 19.2788 | 21.1473 | 35.8994 | 34.1151 | 35.9443 | 35.8692 | 36.1792 | 37.0769 | 36.92 | 36.3134 | 36.9785 | 34.7797 | 34.4162 | 36.3352 | 36.1657 | 37.5359 | 37.1832 | 37.5778 | 37.8406 | 24.9972 | 19.9429 | 93.5427 | 34.254 | 35.1955 | 36.4133 | 35.2417 | 34.5318 | 34.7869 | 35.7088 | 34.8563 | 34.9424 | 37.7668 | 36.8748 | 34.7995 | 34.9047 | 36.8921 | 37.3635 | 38.1913 | 36.8945 | 35.2291 | 35.0832 | 36.405 | 36.6837 | 34.923 | 34.4241 | 33.5136 | 34.9007 | 33.5776 | 34.0654 | 33.7671 | 34.5251 | 33.565 | 35.0731 | 36.3931 | 34.9735 | 35.2333 | 35.5153 | 92.3276 | 92.5409 | 92.5012
2022-09-07 23:24 | 1:34 | 19.1535 | 19.228 | 21.2132 | 35.8802 | 34.1135 | 35.9418 | 35.8836 | 36.1774 | 37.0832 | 36.9222 | 36.3058 | 36.9863 | 34.7757 | 34.4326 | 36.3415 | 36.1458 | 37.5405 | 37.1941 | 37.5782 | 37.8281 | 24.963 | 19.9366 | 93.579 | 34.2172 | 35.1923 | 36.4126 | 35.2585 | 34.5285 | 34.8061 | 35.6989 | 34.8816 | 34.9338 | 37.7791 | 36.8689 | 34.7746 | 34.9193 | 36.8808 | 37.3593 | 38.2067 | 36.879 | 35.2341 | 35.0618 | 36.4221 | 36.6816 | 34.9133 | 34.4261 | 33.4983 | 34.9089 | 33.5654 | 34.0622 | 33.756 | 34.5003 | 33.5662 | 35.0729 | 36.397 | 34.9932 | 35.2446 | 35.5164 | 92.2006 | 92.4217 | 92.3717
2022-09-07 23:25 | 1:34 | 19.1285 | 19.302 | 21.176 | 35.8033 | 34.1055 | 35.9274 | 35.8733 | 36.195 | 37.0777 | 36.9288 | 36.3152 | 36.9972 | 34.7642 | 34.4126 | 36.361 | 36.168 | 37.516 | 37.1725 | 37.5811 | 37.8301 | 24.9639 | 19.9238 | 93.6624 | 34.2113 | 35.1904 | 36.4147 | 35.2372 | 34.5327 | 34.7816 | 35.6858 | 34.8905 | 34.9464 | 37.7555 | 36.8824 | 34.7655 | 34.9108 | 36.8748 | 37.3666 | 38.2016 | 36.8906 | 35.2311 | 35.0585 | 36.4058 | 36.6741 | 34.8977 | 34.409 | 33.5159 | 34.9118 | 33.5695 | 34.0694 | 33.7687 | 34.5143 | 33.5637 | 35.105 | 36.3858 | 35.0078 | 35.2443 | 35.5104 | 92.0526 | 92.2835 | 92.1421
2022-09-07 23:25 | 1:35 | 19.1636 | 19.3203 | 21.1831 | 35.8972 | 34.1123 | 35.9276 | 35.8614 | 36.166 | 37.0675 | 36.9318 | 36.3087 | 36.9919 | 34.7564 | 34.4161 | 36.3372 | 36.1496 | 37.5287 | 37.19 | 37.5825 | 37.8434 | 24.9399 | 19.9569 | 93.7087 | 34.2024 | 35.1865 | 36.4063 | 35.2543 | 34.5033 | 34.7981 | 35.687 | 34.8674 | 34.9203 | 37.7602 | 36.8551 | 34.7936 | 34.9235 | 36.8689 | 37.3615 | 38.1877 | 36.8921 | 35.214 | 35.0488 | 36.3923 | 36.6734 | 34.9009 | 34.4133 | 33.5185 | 34.8882 | 33.5903 | 34.0706 | 33.7431 | 34.5166 | 33.5547 | 35.0949 | 36.3931 | 34.9889 | 35.2445 | 35.4848 | 91.9347 | 92.1704 | 92.1652
2022-09-07 23:25 | 1:35 | 19.1566 | 19.2698 | 21.1746 | 35.8589 | 34.1141 | 35.9263 | 35.8802 | 36.194 | 37.0896 | 36.9605 | 36.3235 | 36.9956 | 34.7696 | 34.3934 | 36.3424 | 36.1264 | 37.5114 | 37.1773 | 37.5807 | 37.8453 | 24.9246 | 19.9257 | 93.8201 | 34.1986 | 35.1957 | 36.3958 | 35.2291 | 34.52 | 34.7995 | 35.6976 | 34.8767 | 34.9346 | 37.754 | 36.8536 | 34.7689 | 34.9265 | 36.8824 | 37.3544 | 38.1878 | 36.8808 | 35.21 | 35.0743 | 36.4046 | 36.6793 | 34.8756 | 34.4082 | 33.518 | 34.903 | 33.5707 | 34.0518 | 33.7338 | 34.5056 | 33.5727 | 35.0932 | 36.391 | 35.0036 | 35.238 | 35.5005 | 91.7803 | 92.0216 | 92.1941
2022-09-07 23:25 | 1:35 | 19.1246 | 19.2598 | 21.1497 | 35.8035 | 34.1375 | 35.9104 | 35.8735 | 36.2088 | 37.0814 | 36.9324 | 36.3346 | 37.0109 | 34.7674 | 34.3745 | 36.3306 | 36.148 | 37.526 | 37.1829 | 37.5805 | 37.8363 | 24.9229 | 19.9245 | 93.9035 | 34.1306 | 35.1736 | 36.38 | 35.2341 | 34.5339 | 34.7746 | 35.6869 | 34.8561 | 34.9315 | 37.7592 | 36.8699 | 34.7791 | 34.9262 | 36.8551 | 37.3442 | 38.1932 | 36.8748 | 35.2125 | 35.0417 | 36.3849 | 36.6764 | 34.8776 | 34.4096 | 33.5084 | 34.8854 | 33.5582 | 34.0539 | 33.7531 | 34.5338 | 33.5572 | 35.0812 | 36.3988 | 34.9988 | 35.2456 | 35.495 | 91.7497 | 91.9295 | 92.1633
2022-09-07 23:25 | 1:35 | 19.1047 | 19.2699 | 21.1224 | 35.8815 | 34.1129 | 35.9254 | 35.8661 | 36.2001 | 37.0722 | 36.9623 | 36.3257 | 36.9959 | 34.7389 | 34.3784 | 36.3175 | 36.1409 | 37.5039 | 37.1957 | 37.5888 | 37.8406 | 24.9036 | 19.8907 | 94.1345 | 34.1365 | 35.1776 | 36.3716 | 35.2311 | 34.5316 | 34.7655 | 35.7041 | 34.8749 | 34.9301 | 37.7542 | 36.861 | 34.7735 | 34.9189 | 36.8536 | 37.3375 | 38.1808 | 36.8689 | 35.2297 | 35.045 | 36.3809 | 36.6635 | 34.8573 | 34.4053 | 33.4799 | 34.8865 | 33.56 | 34.0552 | 33.7454 | 34.4965 | 33.5731 | 35.0862 | 36.3857 | 35.0241 | 35.2517 | 35.4906 | 91.6132 | 91.7977 | 92.0892
2022-09-07 23:25 | 1:35 | 19.049 | 19.2347 | 21.1197 | 35.8903 | 34.0918 | 35.9109 | 35.8651 | 36.1983 | 37.0723 | 36.9451 | 36.3175 | 37.014 | 34.7534 | 34.3686 | 36.3138 | 36.1425 | 37.5041 | 37.1803 | 37.5634 | 37.8396 | 24.87 | 19.9376 | 94.2678 | 34.2096 | 35.1785 | 36.3956 | 35.214 | 34.5117 | 34.7936 | 35.73 | 34.8698 | 34.9398 | 37.7632 | 36.8585 | 34.7728 | 34.9153 | 36.8699 | 37.3603 | 38.1886 | 36.8824 | 35.2067 | 35.0427 | 36.3763 | 36.6719 | 34.857 | 34.4288 | 33.487 | 34.8729 | 33.5658 | 34.0462 | 33.7398 | 34.4834 | 33.5588 | 35.0996 | 36.3883 | 35.0101 | 35.2413 | 35.4787 | 91.508 | 91.718 | 92.0624
2022-09-07 23:26 | 1:35 | 19.1493 | 19.3445 | 21.1588 | 35.8819 | 34.0949 | 35.9032 | 35.8697 | 36.1972 | 37.0605 | 36.9376 | 36.3255 | 37.0032 | 34.7487 | 34.3733 | 36.3148 | 36.1255 | 37.5091 | 37.155 | 37.584 | 37.8296 | 24.8666 | 19.9194 | 94.3326 | 34.1685 | 35.1716 | 36.3802 | 35.21 | 34.5266 | 34.7689 | 35.7018 | 34.8717 | 34.9271 | 37.7599 | 36.8563 | 34.7702 | 34.9192 | 36.861 | 37.3621 | 38.1873 | 36.8551 | 35.2265 | 35.0248 | 36.3851 | 36.6645 | 34.8554 | 34.4007 | 33.4613 | 34.8835 | 33.5548 | 34.0505 | 33.7477 | 34.491 | 33.5545 | 35.0869 | 36.3898 | 35.0201 | 35.2534 | 35.4836 | 91.4342 | 91.6715 | 91.996
2022-09-07 23:26 | 1:36 | 19.0584 | 19.2105 | 21.1476 | 35.8531 | 34.0928 | 35.9096 | 35.8719 | 36.2119 | 37.0721 | 36.9537 | 36.3408 | 37.0075 | 34.7345 | 34.3694 | 36.3131 | 36.1282 | 37.514 | 37.184 | 37.5901 | 37.8305 | 24.8435 | 19.8615 | 94.5238 | 34.1025 | 35.1741 | 36.3916 | 35.2125 | 34.5134 | 34.7791 | 35.7134 | 34.8577 | 34.9501 | 37.752 | 36.843 | 34.7643 | 34.8954 | 36.8585 | 37.3569 | 38.1763 | 36.8536 | 35.2097 | 35.0157 | 36.3659 | 36.6544 | 34.8589 | 34.4162 | 33.457 | 34.8604 | 33.5291 | 34.0351 | 33.7456 | 34.5041 | 33.565 | 35.0756 | 36.3754 | 35.0027 | 35.2595 | 35.4723 | 91.5216 | 91.7437 | 92.1216
2022-09-07 23:26 | 1:36 | 19.0447 | 19.1898 | 21.0722 | 35.8682 | 34.0842 | 35.9303 | 35.8699 | 36.1945 | 37.0748 | 36.9427 | 36.337 | 37.0002 | 34.7293 | 34.3556 | 36.3104 | 36.1379 | 37.4997 | 37.1889 | 37.5848 | 37.8193 | 24.8109 | 19.8759 | 94.5973 | 34.1331 | 35.174 | 36.3838 | 35.2297 | 34.5218 | 34.7735 | 35.7133 | 34.8597 | 34.9352 | 37.7594 | 36.8481 | 34.7879 | 34.901 | 36.8563 | 37.3436 | 38.1614 | 36.8699 | 35.2006 | 35.0133 | 36.3421 | 36.6379 | 34.8416 | 34.4172 | 33.4582 | 34.8552 | 33.5263 | 34.046 | 33.7282 | 34.492 | 33.5389 | 35.0877 | 36.3812 | 34.9997 | 35.2636 | 35.4753 | 91.6677 | 91.8111 | 92.1924
2022-09-07 23:26 | 1:36 | 19.0579 | 19.2128 | 21.0634 | 35.8724 | 34.0846 | 35.9087 | 35.8691 | 36.1827 | 37.0776 | 36.9598 | 36.3431 | 37.0055 | 34.7299 | 34.3453 | 36.2997 | 36.1393 | 37.4795 | 37.1728 | 37.5693 | 37.833 | 24.783 | 19.8433 | 94.6161 | 34.1351 | 35.1595 | 36.3992 | 35.2067 | 34.5175 | 34.7728 | 35.7097 | 34.8728 | 34.9337 | 37.7541 | 36.8563 | 34.7591 | 34.9013 | 36.843 | 37.3544 | 38.1816 | 36.861 | 35.1992 | 34.9952 | 36.3679 | 36.6261 | 34.8626 | 34.4061 | 33.4852 | 34.8555 | 33.5424 | 34.0355 | 33.7486 | 34.4922 | 33.5472 | 35.0935 | 36.3651 | 35.0156 | 35.2652 | 35.4599 | 91.7946 | 91.9291 | 92.1846
2022-09-07 23:26 | 1:36 | 19.09 | 19.2158 | 21.0277 | 35.9079 | 34.0862 | 35.9033 | 35.8824 | 36.1958 | 37.0611 | 36.956 | 36.3142 | 37.0288 | 34.7147 | 34.3176 | 36.294 | 36.1409 | 37.4655 | 37.1896 | 37.5648 | 37.8217 | 24.7817 | 19.8684 | 94.7113 | 34.1274 | 35.1408 | 36.3876 | 35.2265 | 34.5345 | 34.7702 | 35.7006 | 34.8715 | 34.9473 | 37.7488 | 36.8333 | 34.7467 | 34.9162 | 36.8481 | 37.3598 | 38.1531 | 36.8585 | 35.1962 | 35.005 | 36.348 | 36.6312 | 34.8551 | 34.4011 | 33.4471 | 34.8655 | 33.5231 | 34.0627 | 33.7448 | 34.486 | 33.5518 | 35.1041 | 36.36 | 35.0072 | 35.2657 | 35.457 | 91.8863 | 92.0339 | 92.2774
2022-09-07 23:26 | 1:36 | 19.0875 | 19.217 | 21.0261 | 35.8368 | 34.07 | 35.9037 | 35.8866 | 36.2119 | 37.0851 | 36.9492 | 36.3383 | 37.0118 | 34.701 | 34.3125 | 36.2955 | 36.1294 | 37.4597 | 37.1786 | 37.5704 | 37.8075 | 24.7741 | 19.8458 | 94.8103 | 34.1969 | 35.1513 | 36.3579 | 35.2097 | 34.507 | 34.7643 | 35.7082 | 34.8568 | 34.9298 | 37.7378 | 36.8488 | 34.7592 | 34.8957 | 36.8563 | 37.3426 | 38.1613 | 36.8563 | 35.1963 | 34.999 | 36.3475 | 36.6024 | 34.838 | 34.4159 | 33.4456 | 34.8491 | 33.5227 | 34.0701 | 33.7303 | 34.4831 | 33.5341 | 35.0856 | 36.3768 | 35.0256 | 35.2846 | 35.4531 | 91.9874 | 92.1472 | 92.3226
2022-09-07 23:27 | 1:37 | 19.0899 | 19.2231 | 21.0114 | 35.836 | 34.083 | 35.8839 | 35.8803 | 36.1988 | 37.0592 | 36.9705 | 36.3373 | 37.0095 | 34.703 | 34.3175 | 36.2926 | 36.1377 | 37.4628 | 37.1674 | 37.5763 | 37.8 | 24.7856 | 19.8969 | 94.7262 | 34.2193 | 35.1347 | 36.3741 | 35.2006 | 34.5115 | 34.7879 | 35.7096 | 34.8694 | 34.9263 | 37.7383 | 36.8487 | 34.7688 | 34.8909 | 36.8333 | 37.3427 | 38.1391 | 36.843 | 35.1728 | 34.9734 | 36.3458 | 36.6299 | 34.8248 | 34.418 | 33.4417 | 34.8392 | 33.5112 | 34.0318 | 33.7188 | 34.4738 | 33.5243 | 35.0687 | 36.3607 | 35.0077 | 35.2543 | 35.4391 | 92.2048 | 92.2352 | 92.4303
2022-09-07 23:27 | 1:37 | 19.086 | 19.2526 | 21.0349 | 35.9026 | 34.056 | 35.8959 | 35.8728 | 36.1731 | 37.0728 | 36.942 | 36.337 | 37.0081 | 34.6925 | 34.3062 | 36.2906 | 36.1319 | 37.4523 | 37.1758 | 37.576 | 37.8113 | 24.8008 | 19.846 | 94.6435 | 34.0241 | 35.1402 | 36.374 | 35.1992 | 34.503 | 34.7591 | 35.6967 | 34.8669 | 34.9199 | 37.7486 | 36.8365 | 34.7423 | 34.8985 | 36.8488 | 37.3418 | 38.1451 | 36.8481 | 35.1918 | 34.9528 | 36.3233 | 36.598 | 34.8397 | 34.4385 | 33.4199 | 34.8411 | 33.5197 | 34.0551 | 33.726 | 34.4733 | 33.5464 | 35.0658 | 36.3759 | 35.0146 | 35.2763 | 35.4323 | 92.27 | 92.4228 | 92.4135
2022-09-07 23:27 | 1:37 | 19.0186 | 19.1675 | 21.0077 | 35.755 | 34.0633 | 35.8934 | 35.8836 | 36.1881 | 37.0699 | 36.9459 | 36.334 | 37.0133 | 34.6835 | 34.3088 | 36.2699 | 36.12 | 37.4429 | 37.1653 | 37.5628 | 37.7839 | 24.7829 | 19.7578 | 94.5279 | 34.0529 | 35.1386 | 36.3575 | 35.1962 | 34.5142 | 34.7467 | 35.7004 | 34.8811 | 34.932 | 37.7354 | 36.8381 | 34.7583 | 34.9071 | 36.8487 | 37.3345 | 38.1428 | 36.8563 | 35.1682 | 34.9797 | 36.3198 | 36.6098 | 34.8169 | 34.423 | 33.4382 | 34.8197 | 33.5139 | 34.0393 | 33.7211 | 34.4754 | 33.5438 | 35.0777 | 36.3699 | 35.0315 | 35.2595 | 35.4284 | 92.4437 | 92.6234 | 92.5148
2022-09-07 23:27 | 1:37 | 18.9902 | 19.1425 | 20.9351 | 35.9228 | 34.0471 | 35.8768 | 35.8822 | 36.1898 | 37.0664 | 36.9619 | 36.3331 | 37.018 | 34.6771 | 34.2682 | 36.2667 | 36.134 | 37.4458 | 37.1693 | 37.5582 | 37.7794 | 24.7771 | 19.7604 | 94.3388 | 34.1636 | 35.1385 | 36.3525 | 35.1963 | 34.5114 | 34.7592 | 35.6965 | 34.8636 | 34.9281 | 37.7325 | 36.8526 | 34.7554 | 34.9032 | 36.8365 | 37.3344 | 38.1395 | 36.8333 | 35.1816 | 34.9525 | 36.3133 | 36.5838 | 34.819 | 34.4348 | 33.4299 | 34.8073 | 33.5055 | 34.0227 | 33.7191 | 34.4773 | 33.5162 | 35.071 | 36.3781 | 35.0395 | 35.2612 | 35.4182 | 92.6674 | 92.8216 | 92.6828
2022-09-07 23:27 | 1:37 | 19.0631 | 19.2118 | 20.9953 | 35.8114 | 34.039 | 35.8822 | 35.8731 | 36.1784 | 37.0327 | 36.9317 | 36.3349 | 37.0112 | 34.6755 | 34.2789 | 36.2692 | 36.1269 | 37.4367 | 37.1755 | 37.5588 | 37.7904 | 24.8162 | 19.8207 | 94.259 | 34.0348 | 35.1416 | 36.3455 | 35.1728 | 34.5095 | 34.7688 | 35.7184 | 34.8554 | 34.9198 | 37.7466 | 36.8471 | 34.7558 | 34.9062 | 36.8381 | 37.3365 | 38.1354 | 36.8488 | 35.1897 | 34.9376 | 36.3008 | 36.5973 | 34.8086 | 34.426 | 33.4175 | 34.8267 | 33.5065 | 34.0143 | 33.723 | 34.454 | 33.5052 | 35.0475 | 36.3611 | 35.0389 | 35.2507 | 35.4212 | 92.9184 | 93.0659 | 92.8819
2022-09-07 23:27 | 1:37 | 18.9965 | 19.152 | 20.9762 | 35.8577 | 34.0386 | 35.8715 | 35.8624 | 36.1974 | 37.0394 | 36.9436 | 36.3514 | 37.0185 | 34.6828 | 34.2653 | 36.2717 | 36.1353 | 37.4477 | 37.1692 | 37.5707 | 37.7815 | 24.8328 | 19.7582 | 94.2423 | 34.0864 | 35.1249 | 36.3576 | 35.1918 | 34.4988 | 34.7423 | 35.6955 | 34.8774 | 34.9226 | 37.743 | 36.8553 | 34.7557 | 34.912 | 36.8526 | 37.3197 | 38.1437 | 36.8487 | 35.182 | 34.9374 | 36.2842 | 36.5871 | 34.8166 | 34.422 | 33.4147 | 34.7906 | 33.4924 | 34.0412 | 33.71 | 34.4752 | 33.5059 | 35.062 | 36.3671 | 35.0323 | 35.2753 | 35.3982 | 93.06 | 93.2599 | 92.9695
2022-09-07 23:28 | 1:37 | 19.0205 | 19.1447 | 20.9557 | 35.8947 | 34.0471 | 35.8582 | 35.8873 | 36.1945 | 37.0527 | 36.9329 | 36.3468 | 37.0001 | 34.6595 | 34.2469 | 36.2706 | 36.1149 | 37.4283 | 37.1695 | 37.5474 | 37.7735 | 24.8252 | 19.7683 | 94.2194 | 34.1453 | 35.118 | 36.3561 | 35.1682 | 34.5079 | 34.7583 | 35.6914 | 34.8695 | 34.9146 | 37.742 | 36.8449 | 34.7587 | 34.9055 | 36.8471 | 37.3465 | 38.1296 | 36.8365 | 35.181 | 34.9372 | 36.285 | 36.5769 | 34.7966 | 34.4314 | 34.4908 | 34.8073 | 33.4983 | 34.0322 | 33.7063 | 34.4529 | 33.5146 | 35.0661 | 36.3731 | 35.0303 | 35.2697 | 35.3883 | 93.2364 | 93.4784 | 93.0311
2022-09-07 23:28 | 1:38 | 19.0265 | 19.1743 | 20.9585 | 35.8635 | 34.0365 | 35.8617 | 35.8742 | 36.1745 | 37.0583 | 36.9475 | 36.3573 | 37.0324 | 34.6518 | 34.2311 | 36.264 | 36.1189 | 37.4251 | 37.1533 | 37.5693 | 37.769 | 24.8352 | 19.7639 | 94.2016 | 33.9157 | 35.1215 | 36.3545 | 35.1816 | 34.509 | 34.7554 | 35.7054 | 34.8778 | 34.9139 | 37.7317 | 36.8315 | 34.7592 | 34.9003 | 36.8553 | 37.3511 | 38.1149 | 36.8381 | 35.1885 | 34.9295 | 36.2726 | 36.564 | 34.8027 | 34.4409 | 34.4978 | 34.8075 | 33.49 | 34.0375 | 33.7087 | 34.4479 | 33.5011 | 35.0825 | 36.3733 | 35.0427 | 35.2666 | 35.4005 | 93.3317 | 93.6512 | 93.0267
2022-09-07 23:28 | 1:38 | 19.061 | 19.1734 | 20.9063 | 35.9559 | 34.0247 | 35.8677 | 35.8845 | 36.1906 | 37.0419 | 36.9485 | 36.3645 | 37.0289 | 34.647 | 34.2259 | 36.2457 | 36.1204 | 37.4063 | 37.1679 | 37.5585 | 37.7912 | 24.8256 | 19.7791 | 94.1601 | 34.0716 | 35.1066 | 36.3489 | 35.1897 | 34.5005 | 34.7558 | 35.6983 | 34.8748 | 34.9208 | 37.7237 | 36.8278 | 34.7533 | 34.9135 | 36.8449 | 37.3369 | 38.1282 | 36.8526 | 35.1926 | 34.9188 | 36.285 | 36.5567 | 34.8009 | 34.4174 | 34.4957 | 34.787 | 33.4811 | 34.0134 | 33.7146 | 34.458 | 33.4916 | 35.0672 | 36.3652 | 35.0308 | 35.2587 | 35.3768 | 93.5367 | 93.8953 | 93.2835
2022-09-07 23:28 | 1:38 | 19.0048 | 19.1554 | 20.9308 | 35.868 | 34.0178 | 35.8721 | 35.8865 | 36.1975 | 37.0629 | 36.9461 | 36.3745 | 37.0508 | 34.6633 | 34.2306 | 36.2554 | 36.1157 | 37.4125 | 37.1579 | 37.5597 | 37.7585 | 24.807 | 19.7356 | 94.1808 | 34.1025 | 35.0986 | 36.3561 | 35.182 | 34.5129 | 34.7557 | 35.6927 | 34.8878 | 34.9343 | 37.7302 | 36.8486 | 34.7476 | 34.8998 | 36.8315 | 37.3337 | 38.1247 | 36.8471 | 35.1686 | 34.9243 | 36.268 | 36.5757 | 34.8088 | 34.4221 | 34.4833 | 34.7973 | 33.4893 | 34.0206 | 33.6959 | 34.4273 | 33.492 | 35.0683 | 36.3614 | 35.045 | 35.2706 | 35.3955 | 93.7011 | 94.0969 | 93.398
2022-09-07 23:28 | 1:38 | 19.0123 | 19.1622 | 20.9071 | 35.9196 | 34.0115 | 35.8606 | 35.8912 | 36.1966 | 37.0465 | 36.9655 | 36.369 | 37.0205 | 34.6331 | 34.215 | 36.2415 | 36.1265 | 37.4193 | 37.1664 | 37.574 | 37.7612 | 24.8257 | 19.7785 | 94.1496 | 34.0313 | 35.1109 | 36.362 | 35.181 | 34.513 | 34.7587 | 35.6921 | 34.8805 | 34.9236 | 37.7345 | 36.8363 | 34.7439 | 34.9098 | 36.8278 | 37.333 | 38.1216 | 36.8553 | 35.1719 | 34.9051 | 36.2495 | 36.5433 | 34.8079 | 34.4384 | 34.4959 | 34.7842 | 33.4963 | 34.0309 | 33.7099 | 34.439 | 33.4945 | 35.0759 | 36.3627 | 35.0653 | 35.2834 | 35.3692 | 93.9856 | 94.3292 | 93.5787
2022-09-07 23:28 | 1:38 | 19.005 | 19.155 | 20.8635 | 35.8146 | 34.0111 | 35.8665 | 35.8718 | 36.1864 | 37.0547 | 36.9676 | 36.385 | 37.0509 | 34.639 | 34.2013 | 36.231 | 36.1104 | 37.4349 | 37.1756 | 37.5722 | 37.7716 | 24.8172 | 19.7489 | 94.1551 | 34.1153 | 35.1065 | 36.3726 | 35.1885 | 34.5086 | 34.7592 | 35.6922 | 34.8942 | 34.9313 | 37.7379 | 36.837 | 34.7627 | 34.9071 | 36.8486 | 37.3466 | 38.1218 | 36.8449 | 35.175 | 34.8848 | 36.2665 | 36.5629 | 34.783 | 34.4187 | 34.4665 | 34.8081 | 33.4843 | 34.0425 | 33.702 | 34.446 | 33.4985 | 35.0605 | 36.3704 | 35.031 | 35.2779 | 35.3785 | 94.1314 | 94.5209 | 93.6541
2022-09-07 23:29 | 1:39 | 19.0422 | 19.1763 | 20.8433 | 35.8731 | 34.0102 | 35.8683 | 35.8915 | 36.1801 | 37.0465 | 36.9552 | 36.3774 | 37.0244 | 34.6461 | 34.1878 | 36.2235 | 36.1415 | 37.4021 | 37.1757 | 37.5716 | 37.769 | 24.7952 | 19.7206 | 94.111 | 34.1053 | 35.0934 | 36.3482 | 35.1926 | 34.5105 | 34.7533 | 35.7081 | 34.8853 | 34.9285 | 37.7221 | 36.8467 | 34.7517 | 34.9189 | 36.8363 | 37.3288 | 38.1022 | 36.8315 | 35.1756 | 34.8875 | 36.2427 | 36.5472 | 34.7946 | 34.4511 | 34.4603 | 34.7771 | 33.4575 | 34.0425 | 33.7215 | 34.4459 | 33.4904 | 35.0722 | 36.3691 | 35.0565 | 35.2781 | 35.3693 | 94.2949 | 94.7235 | 93.7193
2022-09-07 23:29 | 1:39 | 19.0171 | 19.1478 | 20.8745 | 35.8711 | 34.0101 | 35.8621 | 35.8651 | 36.1784 | 37.041 | 36.9653 | 36.3813 | 37.0339 | 34.6274 | 34.2101 | 36.2263 | 36.1504 | 37.4058 | 37.186 | 37.5534 | 37.754 | 24.7817 | 19.7113 | 94.0047 | 34.0336 | 35.1125 | 36.3506 | 35.1686 | 34.5116 | 34.7476 | 35.6994 | 34.8702 | 34.9257 | 37.7362 | 36.8487 | 34.7375 | 34.9254 | 36.837 | 37.336 | 38.1282 | 36.8278 | 35.1805 | 34.8966 | 36.2377 | 36.5504 | 34.795 | 34.4283 | 34.4801 | 34.7705 | 33.465 | 34.0147 | 33.7064 | 34.4533 | 33.4641 | 35.0781 | 36.373 | 35.0435 | 35.283 | 35.3549 | 94.4943 | 94.9472 | 93.8339
2022-09-07 23:29 | 1:39 | 18.9569 | 19.1032 | 20.8661 | 35.8667 | 34.0074 | 35.8548 | 35.8965 | 36.1814 | 37.0426 | 36.9735 | 36.3901 | 37.0483 | 34.6236 | 34.1955 | 36.2249 | 36.1293 | 37.4113 | 37.1701 | 37.5614 | 37.7585 | 24.7646 | 19.6968 | 93.9646 | 34.0669 | 35.1039 | 36.3383 | 35.1719 | 34.5071 | 34.7439 | 35.7066 | 34.9107 | 34.9369 | 37.7412 | 36.8511 | 34.7443 | 34.9071 | 36.8467 | 37.334 | 38.1117 | 36.8486 | 35.1692 | 34.8882 | 36.2505 | 36.5548 | 34.7959 | 34.4471 | 34.4601 | 34.7688 | 33.4682 | 34.0333 | 33.7082 | 34.4469 | 33.4923 | 35.0743 | 36.3771 | 35.0522 | 35.286 | 35.3634 | 94.5889 | 95.0899 | 94.0409
2022-09-07 23:29 | 1:39 | 18.9775 | 19.1351 | 20.8587 | 35.8339 | 33.9986 | 35.8634 | 35.8912 | 36.2087 | 37.0492 | 36.9625 | 36.3852 | 37.0594 | 34.6128 | 34.1819 | 36.2316 | 36.1357 | 37.4091 | 37.1588 | 37.5535 | 37.7547 | 24.7678 | 19.718 | 93.9093 | 34.0593 | 35.0946 | 36.3544 | 35.175 | 34.5257 | 34.7627 | 35.7078 | 34.8927 | 34.9209 | 37.7386 | 36.8589 | 34.759 | 34.9105 | 36.8487 | 37.3376 | 38.1182 | 36.8363 | 35.1727 | 34.8682 | 36.2359 | 36.544 | 34.7884 | 34.4458 | 34.469 | 34.7545 | 33.4702 | 34.0405 | 33.7001 | 34.4251 | 33.4746 | 35.0642 | 36.373 | 35.0475 | 35.2775 | 35.3681 | 94.8134 | 95.2417 | 94.1597
2022-09-07 23:29 | 1:39 | 18.9506 | 19.0951 | 20.8576 | 35.9554 | 34.0019 | 35.8555 | 35.8827 | 36.1972 | 37.0492 | 36.9709 | 36.3967 | 37.0563 | 34.6308 | 34.1595 | 36.2149 | 36.1348 | 37.3914 | 37.1734 | 37.5496 | 37.7612 | 24.7414 | 19.6888 | 93.9142 | 34.095 | 35.097 | 36.3395 | 35.1756 | 34.5123 | 34.7517 | 35.7022 | 34.908 | 34.9154 | 37.7298 | 36.85 | 34.7807 | 34.8978 | 36.8511 | 37.3425 | 38.1083 | 36.837 | 35.1665 | 34.8848 | 36.2217 | 36.5487 | 34.7824 | 34.4488 | 34.4537 | 34.7573 | 33.4844 | 34.0284 | 33.6761 | 34.4276 | 33.4822 | 35.0817 | 36.3774 | 35.0699 | 35.2854 | 35.3651 | 94.9035 | 95.3746 | 94.2116
2022-09-07 23:29 | 1:39 | 18.8802 | 19.0428 | 20.8584 | 35.8432 | 33.9884 | 35.8493 | 35.8938 | 36.1849 | 37.0475 | 36.9826 | 36.3986 | 37.0626 | 34.6177 | 34.184 | 36.2176 | 36.1508 | 37.3933 | 37.1873 | 37.5545 | 37.7727 | 24.7329 | 19.6494 | 93.8873 | 34.0699 | 35.0863 | 36.3477 | 35.1805 | 34.5263 | 34.7375 | 35.7035 | 34.9054 | 34.9323 | 37.7246 | 36.8521 | 34.7538 | 34.9106 | 36.8589 | 37.3278 | 38.136 | 36.8467 | 35.1629 | 34.8824 | 36.2215 | 36.5401 | 34.7562 | 34.4568 | 34.4765 | 34.7512 | 33.4646 | 34.0219 | 33.7087 | 34.4412 | 33.4879 | 35.0924 | 36.3837 | 35.0621 | 35.3085 | 35.3557 | 95.0205 | 95.4954 | 94.2769
2022-09-07 23:30 | 1:39 | 18.8975 | 19.0749 | 20.8397 | 35.8388 | 34.0057 | 35.8691 | 35.8957 | 36.2124 | 37.0478 | 36.9962 | 36.3957 | 37.0624 | 34.5856 | 34.1522 | 36.204 | 36.138 | 37.3968 | 37.1637 | 37.5699 | 37.7582 | 24.7205 | 19.6546 | 93.7947 | 33.9698 | 35.0922 | 36.3492 | 35.1692 | 34.5048 | 34.7443 | 35.7227 | 34.9002 | 34.9404 | 37.7344 | 36.8433 | 34.7525 | 34.9091 | 36.85 | 37.3374 | 38.0986 | 36.8487 | 35.1764 | 34.8709 | 36.2338 | 36.5411 | 34.7538 | 34.4473 | 34.4607 | 34.7491 | 33.465 | 34.0212 | 33.7021 | 34.423 | 33.4851 | 35.0885 | 36.3761 | 35.0708 | 35.3046 | 35.3589 | 95.1064 | 95.5845 | 94.348
2022-09-07 23:30 | 1:40 | 19.0042 | 19.1192 | 20.8539 | 35.713 | 34.0014 | 35.832 | 35.8946 | 36.1911 | 37.0426 | 36.9806 | 36.3959 | 37.083 | 34.605 | 34.1553 | 36.2266 | 36.1316 | 37.4068 | 37.1794 | 37.5472 | 37.7526 | 24.7242 | 19.7185 | 93.7399 | 34.0327 | 35.09 | 36.3259 | 35.1727 | 34.513 | 34.759 | 35.7203 | 34.9043 | 34.9352 | 37.7386 | 36.8286 | 34.7472 | 34.925 | 36.8521 | 37.3637 | 38.0874 | 36.8511 | 35.1703 | 34.8588 | 36.2234 | 36.5442 | 34.7267 | 34.4623 | 34.4725 | 34.7485 | 33.4694 | 34.0425 | 33.7128 | 34.4141 | 33.4804 | 35.0658 | 36.3633 | 35.0747 | 35.2965 | 35.3604 | 95.183 | 95.6654 | 94.4414
2022-09-07 23:30 | 1:40 | 18.8861 | 19.0644 | 20.8007 | 35.6638 | 33.9758 | 35.8503 | 35.8993 | 36.2039 | 37.0383 | 36.9937 | 36.4028 | 37.0794 | 34.6002 | 34.1534 | 36.2086 | 36.1181 | 37.3739 | 37.1757 | 37.5496 | 37.7426 | 24.7002 | 19.6389 | 93.6404 | 33.9234 | 35.0932 | 36.335 | 35.1665 | 34.4996 | 34.7807 | 35.7175 | 34.9138 | 34.9455 | 37.7358 | 36.8226 | 34.7518 | 34.9219 | 36.8433 | 37.3533 | 38.0884 | 36.8589 | 35.1773 | 34.8697 | 36.2178 | 36.5234 | 34.7693 | 34.4505 | 34.462 | 34.7461 | 33.4992 | 34.0286 | 33.6829 | 34.4382 | 33.4847 | 35.0756 | 36.3821 | 35.0653 | 35.2845 | 35.3561 | 95.2449 | 95.705 | 94.3598
2022-09-07 23:30 | 1:40 | 18.9051 | 19.0394 | 20.7782 | 35.888 | 33.9744 | 35.8354 | 35.8933 | 36.2116 | 37.0575 | 36.9771 | 36.4085 | 37.0891 | 34.5885 | 34.1371 | 36.1925 | 36.1126 | 37.3894 | 37.1584 | 37.5613 | 37.7491 | 24.6564 | 19.6061 | 93.6728 | 33.9807 | 35.091 | 36.3335 | 35.1629 | 34.5015 | 34.7538 | 35.7189 | 34.9184 | 34.9313 | 37.7235 | 36.8279 | 34.7467 | 34.9269 | 36.8286 | 37.338 | 38.1024 | 36.85 | 35.1716 | 34.8537 | 36.2178 | 36.5527 | 34.7719 | 34.4601 | 34.4569 | 34.7557 | 33.4624 | 34.0351 | 33.6796 | 34.424 | 33.4727 | 35.0853 | 36.395 | 35.0799 | 35.3085 | 35.3523 | 95.1504 | 95.5819 | 94.3348
2022-09-07 23:30 | 1:40 | 18.8017 | 18.9455 | 20.7493 | 35.7556 | 33.9822 | 35.8583 | 35.9105 | 36.2013 | 37.0433 | 36.9817 | 36.4134 | 37.0829 | 34.6053 | 34.1244 | 36.2076 | 36.1377 | 37.3836 | 37.1855 | 37.569 | 37.7742 | 24.6334 | 19.5293 | 93.7175 | 33.8866 | 35.0751 | 36.3304 | 35.1764 | 34.5163 | 34.7525 | 35.721 | 34.9249 | 34.951 | 37.7498 | 36.8303 | 34.7571 | 34.9048 | 36.8226 | 37.3256 | 38.0828 | 36.8521 | 35.1612 | 34.8482 | 36.2201 | 36.5418 | 34.7403 | 34.4486 | 34.4577 | 34.7379 | 33.4611 | 34.0164 | 33.6874 | 34.4321 | 33.4663 | 35.0934 | 36.379 | 35.0748 | 35.3025 | 35.3539 | 94.89 | 95.3334 | 94.1662
2022-09-07 23:30 | 1:40 | 18.7664 | 18.9059 | 20.727 | 35.8283 | 33.9781 | 35.8496 | 35.8958 | 36.1901 | 37.0453 | 36.9909 | 36.4129 | 37.0687 | 34.5905 | 34.1253 | 36.2077 | 36.1397 | 37.3811 | 37.1794 | 37.5552 | 37.7478 | 24.6286 | 19.4755 | 93.6088 | 34.0947 | 35.081 | 36.3326 | 35.1703 | 34.5138 | 34.7472 | 35.7069 | 34.9244 | 34.9582 | 37.7514 | 36.836 | 34.7558 | 34.9372 | 36.8279 | 37.3474 | 38.0869 | 36.8433 | 35.167 | 34.8581 | 36.2225 | 36.5558 | 34.7522 | 34.4761 | 34.4593 | 34.7531 | 33.4758 | 34.0299 | 33.6995 | 34.4223 | 33.4863 | 35.0914 | 36.3678 | 35.0893 | 35.2989 | 35.3533 | 94.7161 | 95.0959 | 93.9536
2022-09-07 23:31 | 1:41 | 18.8096 | 18.9667 | 20.7825 | 35.8274 | 33.9732 | 35.8256 | 35.8935 | 36.2069 | 37.0587 | 37.0095 | 36.4199 | 37.0856 | 34.6018 | 34.131 | 36.2118 | 36.1281 | 37.3779 | 37.1921 | 37.5615 | 37.7516 | 24.6427 | 19.5296 | 93.3889 | 34.0546 | 35.0755 | 36.3322 | 35.1773 | 34.504 | 34.7518 | 35.7107 | 34.9128 | 34.9422 | 37.7449 | 36.8145 | 34.7403 | 34.9243 | 36.8303 | 37.3471 | 38.0895 | 36.8286 | 35.154 | 34.8354 | 36.2069 | 36.5127 | 34.7533 | 34.4657 | 34.4451 | 34.7553 | 33.4677 | 34.0338 | 33.7053 | 34.4243 | 33.462 | 35.08 | 36.3733 | 35.0934 | 35.3072 | 35.3467 | 94.4557 | 94.8382 | 93.8456
2022-09-07 23:31 | 1:41 | 18.7615 | 18.924 | 20.7209 | 35.8041 | 33.9617 | 35.833 | 35.9044 | 36.198 | 37.0585 | 36.9923 | 36.4122 | 37.0945 | 34.5851 | 34.1199 | 36.1913 | 36.1231 | 37.383 | 37.1791 | 37.568 | 37.7727 | 24.643 | 19.4604 | 93.3485 | 33.998 | 35.0694 | 36.3476 | 35.1716 | 34.5303 | 34.7467 | 35.71 | 34.9163 | 34.9529 | 37.746 | 36.827 | 34.7482 | 34.9251 | 36.836 | 37.3275 | 38.098 | 36.8226 | 35.1465 | 34.8449 | 36.2145 | 36.5511 | 34.7423 | 34.469 | 34.4578 | 34.7289 | 33.4639 | 34.0431 | 33.6996 | 34.4428 | 33.4735 | 35.086 | 36.3551 | 35.1052 | 35.3086 | 35.3411 | 94.2458 | 94.6554 | 93.6755
2022-09-07 23:31 | 1:41 | 18.6937 | 18.8189 | 20.678 | 35.745 | 33.9721 | 35.8237 | 35.9015 | 36.2073 | 37.0517 | 36.9967 | 36.4309 | 37.1102 | 34.6085 | 34.08 | 36.1894 | 36.1447 | 37.3755 | 37.1968 | 37.5629 | 37.7672 | 24.6051 | 19.4143 | 93.1285 | 33.9371 | 35.0816 | 36.3388 | 35.1612 | 34.518 | 34.7571 | 35.7182 | 34.9228 | 34.9526 | 37.7354 | 36.8234 | 34.749 | 34.9391 | 36.8145 | 37.3546 | 38.0801 | 36.8279 | 35.1689 | 34.8541 | 36.1935 | 36.5312 | 34.7276 | 34.4839 | 34.4566 | 34.7357 | 33.4889 | 34.0306 | 33.7012 | 34.431 | 33.4699 | 35.0944 | 36.3625 | 35.0949 | 35.3084 | 35.349 | 94.1995 | 94.5349 | 93.7113
2022-09-07 23:31 | 1:41 | 18.6864 | 18.7956 | 20.6466 | 35.6893 | 33.9681 | 35.8218 | 35.8857 | 36.224 | 37.0379 | 36.9909 | 36.4413 | 37.1021 | 34.57 | 34.0912 | 36.1892 | 36.1401 | 37.3897 | 37.1862 | 37.5777 | 37.7541 | 24.596 | 19.3841 | 92.9373 | 33.8381 | 35.0597 | 36.329 | 35.167 | 34.5359 | 34.7558 | 35.7152 | 34.9295 | 34.9669 | 37.7382 | 36.8176 | 34.7517 | 34.92 | 36.827 | 37.3453 | 38.098 | 36.8303 | 35.1516 | 34.8343 | 36.1871 | 36.5212 | 34.7242 | 34.4885 | 34.4468 | 34.7237 | 33.4847 | 34.0126 | 33.679 | 34.4253 | 33.4618 | 35.0941 | 36.3626 | 35.0869 | 35.3122 | 35.3447 | 94.1419 | 94.4627 | 93.7299
2022-09-07 23:31 | 1:41 | 18.6486 | 18.7678 | 20.6197 | 35.6539 | 33.9642 | 35.8411 | 35.9056 | 36.2235 | 37.0354 | 37.0066 | 36.4394 | 37.1087 | 34.5786 | 34.0883 | 36.1955 | 36.1293 | 37.3774 | 37.1882 | 37.5631 | 37.7647 | 24.5899 | 19.4126 | 92.6176 | 33.8493 | 35.0745 | 36.3414 | 35.154 | 34.5207 | 34.7403 | 35.7224 | 34.9382 | 34.9569 | 37.7382 | 36.8259 | 34.7488 | 34.922 | 36.8234 | 37.337 | 38.0827 | 36.836 | 35.1401 | 34.8181 | 36.2024 | 36.5476 | 34.7103 | 34.4627 | 34.4566 | 34.7178 | 33.4546 | 34.0255 | 33.6902 | 34.4278 | 33.4722 | 35.1078 | 36.364 | 35.0999 | 35.3028 | 35.3552 | 94.0327 | 94.3529 | 93.706
2022-09-07 23:31 | 1:41 | 18.6282 | 18.7986 | 20.6396 | 35.7229 | 33.9593 | 35.8228 | 35.8903 | 36.2145 | 37.05 | 37.0124 | 36.4332 | 37.1013 | 34.575 | 34.0708 | 36.177 | 36.1221 | 37.3601 | 37.1906 | 37.5694 | 37.7452 | 24.5789 | 19.3547 | 92.4225 | 33.9597 | 35.0731 | 36.3263 | 35.1465 | 34.5161 | 34.7482 | 35.7288 | 34.9368 | 34.9493 | 37.7466 | 36.8201 | 34.7351 | 34.9424 | 36.8176 | 37.3479 | 38.0738 | 36.8145 | 35.1523 | 34.8089 | 36.2024 | 36.5346 | 34.7227 | 34.4792 | 34.4503 | 34.7446 | 33.4801 | 34.0521 | 33.6881 | 34.4093 | 33.4715 | 35.1035 | 36.369 | 35.1134 | 35.318 | 35.3348 | 93.9855 | 94.2834 | 93.727
2022-09-07 23:32 | 1:41 | 18.6535 | 18.7772 | 20.5973 | 35.7503 | 33.9695 | 35.8376 | 35.8922 | 36.2065 | 37.0495 | 37.0077 | 36.4402 | 37.1153 | 34.5598 | 34.0723 | 36.1715 | 36.1092 | 37.3535 | 37.1879 | 37.5632 | 37.7562 | 24.5677 | 19.3514 | 92.4032 | 33.7473 | 35.0593 | 36.3195 | 35.1689 | 34.5038 | 34.749 | 35.7153 | 34.9324 | 34.9441 | 37.7536 | 36.7995 | 34.7214 | 34.9451 | 36.8259 | 37.3425 | 38.0794 | 36.827 | 35.1446 | 34.8247 | 36.2098 | 36.5458 | 34.7182 | 34.484 | 34.4472 | 34.7288 | 33.4629 | 34.0005 | 33.697 | 34.4137 | 33.4894 | 35.1117 | 36.3631 | 35.1045 | 35.3547 | 35.3353 | 93.8916 | 94.1816 | 93.6313
2022-09-07 23:32 | 1:42 | 18.553 | 18.7207 | 20.571 | 35.6754 | 33.9573 | 35.8341 | 35.8901 | 36.223 | 37.062 | 37.015 | 36.449 | 37.1235 | 34.5592 | 34.0606 | 36.1809 | 36.1345 | 37.3659 | 37.1988 | 37.5756 | 37.7629 | 24.5463 | 19.3106 | 92.4129 | 33.8177 | 35.0711 | 36.3389 | 35.1516 | 34.5267 | 34.7517 | 35.7317 | 34.9268 | 34.9585 | 37.7442 | 36.8061 | 34.7459 | 34.9469 | 36.8201 | 37.3471 | 38.0859 | 36.8234 | 35.1425 | 34.8091 | 36.1796 | 36.5393 | 34.7 | 34.4718 | 34.4433 | 34.7193 | 33.4569 | 34.0191 | 33.6782 | 34.435 | 33.474 | 35.1241 | 36.3561 | 35.0971 | 35.3269 | 35.3427 | 93.8599 | 94.0982 | 93.5591
2022-09-07 23:32 | 1:42 | 18.6027 | 18.718 | 20.5555 | 35.666 | 33.9559 | 35.8277 | 35.8947 | 36.2311 | 37.027 | 37.0273 | 36.4476 | 37.1224 | 34.5593 | 34.066 | 36.1859 | 36.1351 | 37.3738 | 37.1947 | 37.5748 | 37.7647 | 24.708 | 19.3171 | 92.4786 | 33.8519 | 35.0515 | 36.3233 | 35.1401 | 34.5139 | 34.7488 | 35.7337 | 34.9445 | 34.9619 | 37.7569 | 36.7933 | 34.7356 | 34.9416 | 36.7995 | 37.3679 | 38.0887 | 36.8176 | 35.1186 | 34.8118 | 36.1864 | 36.5433 | 34.6905 | 34.4673 | 34.4488 | 34.7284 | 33.4963 | 34.0288 | 33.7089 | 34.4189 | 33.4576 | 35.1104 | 36.3753 | 35.1127 | 35.342 | 35.3282 | 93.7557 | 94.0802 | 93.439
2022-09-07 23:32 | 1:42 | 18.6302 | 18.7313 | 20.5649 | 35.7131 | 33.9373 | 35.8173 | 35.8787 | 36.2296 | 37.06 | 37.0234 | 36.4401 | 37.1332 | 34.563 | 34.0908 | 36.1883 | 36.1226 | 37.333 | 37.2088 | 37.5681 | 37.7549 | 24.6688 | 19.3429 | 92.5553 | 33.9224 | 35.0679 | 36.3196 | 35.1523 | 34.5193 | 34.7351 | 35.7334 | 34.9496 | 34.9315 | 37.7453 | 36.8038 | 34.7402 | 34.9341 | 36.8061 | 37.3379 | 38.0816 | 36.8259 | 35.1438 | 34.8059 | 36.1972 | 36.537 | 34.6965 | 34.5022 | 34.4307 | 34.7217 | 33.4715 | 34.0197 | 33.6816 | 34.4238 | 33.4724 | 35.1095 | 36.373 | 35.1089 | 35.3297 | 35.3352 | 93.7405 | 94.0403 | 93.4817
2022-09-07 23:32 | 1:42 | 18.6486 | 18.7848 | 20.6026 | 35.5842 | 33.939 | 35.8188 | 35.8926 | 36.2081 | 37.0524 | 37.0243 | 36.4646 | 37.1019 | 34.5562 | 34.0568 | 36.1876 | 36.1281 | 37.3586 | 37.1948 | 37.5698 | 37.7652 | 24.6038 | 19.3812 | 92.6489 | 33.9593 | 35.0701 | 36.3041 | 35.1446 | 34.4997 | 34.7214 | 35.7329 | 34.9168 | 34.9323 | 37.743 | 36.8037 | 34.7284 | 34.936 | 36.7933 | 37.3262 | 38.0746 | 36.8201 | 35.121 | 34.8059 | 36.1857 | 36.5583 | 34.6916 | 34.4804 | 34.4567 | 34.7167 | 33.488 | 34.0275 | 33.6823 | 34.4149 | 33.472 | 35.1195 | 36.3613 | 35.1247 | 35.3481 | 35.3434 | 93.696 | 93.9826 | 93.4251
2022-09-07 23:32 | 1:42 | 18.6073 | 18.7756 | 20.5776 | 35.6226 | 33.9422 | 35.832 | 35.8834 | 36.2149 | 37.048 | 37.0197 | 36.4372 | 37.1245 | 34.5428 | 34.033 | 36.1733 | 36.1302 | 37.3657 | 37.1974 | 37.5777 | 37.7551 | 24.5459 | 19.3265 | 92.7285 | 34.0048 | 35.049 | 36.3202 | 35.1425 | 34.5109 | 34.7459 | 35.7303 | 34.9163 | 34.9574 | 37.7395 | 36.7879 | 34.7373 | 34.9433 | 36.8038 | 37.3563 | 38.0799 | 36.7995 | 35.1242 | 34.8056 | 36.1545 | 36.5277 | 34.6845 | 34.4997 | 34.4334 | 34.7196 | 33.4776 | 33.9832 | 33.668 | 34.4152 | 33.4677 | 35.1328 | 36.3526 | 35.1086 | 35.3418 | 35.3491 | 93.6723 | 93.8973 | 93.4145
2022-09-07 23:33 | 1:43 | 18.5776 | 18.7299 | 20.5517 | 35.6578 | 33.9448 | 35.8229 | 35.9111 | 36.2135 | 37.0517 | 37.0399 | 36.4433 | 37.1231 | 34.534 | 34.0328 | 36.1724 | 36.1236 | 37.3622 | 37.1804 | 37.5665 | 37.7482 | 24.4942 | 19.3193 | 92.8519 | 33.8307 | 35.0541 | 36.3109 | 35.1186 | 34.5149 | 34.7356 | 35.7216 | 34.9322 | 34.9415 | 37.73 | 36.7855 | 34.736 | 34.928 | 36.8037 | 37.3556 | 38.0686 | 36.8061 | 35.126 | 34.8031 | 36.1579 | 36.5321 | 34.6699 | 34.4834 | 34.4463 | 34.7077 | 33.4487 | 34.0105 | 33.6742 | 34.4109 | 33.4684 | 35.1107 | 36.341 | 35.1076 | 35.3372 | 35.3088 | 93.5506 | 93.7867 | 93.3504
2022-09-07 23:33 | 1:43 | 18.5329 | 18.6791 | 20.5238 | 35.67 | 33.9292 | 35.8055 | 35.8886 | 36.2024 | 37.0398 | 37.0263 | 36.4446 | 37.1159 | 34.5528 | 34.0339 | 36.151 | 36.1267 | 37.3441 | 37.1907 | 37.5594 | 37.7375 | 24.4538 | 19.2658 | 92.8712 | 33.8512 | 35.0588 | 36.2899 | 35.1438 | 34.4878 | 34.7402 | 35.721 | 34.9351 | 34.94 | 37.7525 | 36.7752 | 34.7298 | 34.9398 | 36.7879 | 37.3355 | 38.0762 | 36.7933 | 35.1125 | 34.7666 | 36.1407 | 36.5224 | 34.6767 | 34.5132 | 34.4521 | 34.6884 | 33.4772 | 34.0051 | 33.67 | 34.3992 | 33.4557 | 35.1317 | 36.355 | 35.1017 | 35.3426 | 35.3303 | 93.4687 | 93.7097 | 93.2883
2022-09-07 23:33 | 1:43 | 18.484 | 18.6397 | 20.4923 | 35.6942 | 33.9432 | 35.7854 | 35.887 | 36.2023 | 37.0521 | 37.0403 | 36.4505 | 37.1171 | 34.5243 | 34.0368 | 36.1543 | 36.109 | 37.3288 | 37.184 | 37.5599 | 37.7367 | 24.3647 | 19.2709 | 92.8129 | 33.8772 | 35.0323 | 36.2938 | 35.121 | 34.5016 | 34.7284 | 35.73 | 34.9186 | 34.9416 | 37.7227 | 36.7725 | 34.7268 | 34.913 | 36.7855 | 37.3449 | 38.0828 | 36.8038 | 35.1068 | 34.7708 | 36.1603 | 36.4972 | 34.657 | 34.4918 | 34.4561 | 34.7109 | 33.4555 | 34.0045 | 33.6608 | 34.406 | 33.4536 | 35.1261 | 36.3441 | 35.1155 | 35.342 | 35.3106 | 93.4765 | 93.6298 | 93.3342
2022-09-07 23:33 | 1:43 | 18.5566 | 18.6777 | 20.5262 | 35.5611 | 33.924 | 35.799 | 35.9015 | 36.2168 | 37.0374 | 37.0532 | 36.451 | 37.1157 | 34.5245 | 34.0191 | 36.1829 | 36.1162 | 37.3181 | 37.1928 | 37.5659 | 37.7356 | 24.3426 | 19.3133 | 92.8697 | 33.7559 | 35.0444 | 36.3087 | 35.1242 | 34.5054 | 34.7373 | 35.7341 | 34.9316 | 34.9416 | 37.7344 | 36.7841 | 34.7259 | 34.9226 | 36.7752 | 37.3447 | 38.0938 | 36.8037 | 35.1108 | 34.7647 | 36.1415 | 36.5072 | 34.6541 | 34.5001 | 34.4321 | 34.7056 | 33.456 | 33.9906 | 33.6632 | 34.4006 | 33.4639 | 35.113 | 36.3317 | 35.1091 | 35.3431 | 35.3255 | 93.3772 | 93.5467 | 93.1949
2022-09-07 23:33 | 1:43 | 18.525 | 18.6817 | 20.5574 | 35.678 | 33.8957 | 35.7894 | 35.8891 | 36.215 | 37.0541 | 37.0578 | 36.4492 | 37.115 | 34.5521 | 33.9889 | 36.1803 | 36.1307 | 37.3316 | 37.19 | 37.5623 | 37.7581 | 24.3077 | 19.2472 | 92.9508 | 33.9425 | 35.0507 | 36.2891 | 35.126 | 34.4937 | 34.736 | 35.7321 | 34.9195 | 34.9483 | 37.7313 | 36.794 | 34.7345 | 34.9227 | 36.7725 | 37.3329 | 38.0809 | 36.7879 | 35.1177 | 34.7583 | 36.1458 | 36.5132 | 34.6515 | 34.4813 | 34.439 | 34.6739 | 33.459 | 33.9834 | 33.6531 | 34.3909 | 33.4494 | 35.131 | 36.3419 | 35.1184 | 35.3361 | 35.3382 | 93.2595 | 93.4712 | 93.1539
2022-09-07 23:33 | 1:43 | 18.4536 | 18.621 | 20.5109 | 35.6401 | 33.9044 | 35.7894 | 35.8965 | 36.2051 | 37.0359 | 37.0483 | 36.4324 | 37.1375 | 34.5086 | 33.9996 | 36.153 | 36.1137 | 37.3213 | 37.1893 | 37.5688 | 37.7418 | 24.2772 | 19.2331 | 93.1108 | 33.9282 | 35.0515 | 36.2803 | 35.1125 | 34.4979 | 34.7298 | 35.7456 | 34.9283 | 34.9374 | 37.7291 | 36.7721 | 34.7291 | 34.9182 | 36.7841 | 37.329 | 38.0893 | 36.7855 | 35.1092 | 34.7672 | 36.1338 | 36.5212 | 34.6478 | 34.5003 | 34.4377 | 34.676 | 33.4813 | 33.983 | 33.6651 | 34.3977 | 33.4514 | 35.1248 | 36.3481 | 35.1209 | 35.3481 | 35.3087 | 93.1363 | 93.348 | 93.0651
2022-09-07 23:34 | 1:43 | 18.5116 | 18.6388 | 20.5021 | 35.6121 | 33.9076 | 35.7788 | 35.8845 | 36.2076 | 37.049 | 37.0482 | 36.4615 | 37.1286 | 34.522 | 33.9828 | 36.1587 | 36.1224 | 37.3246 | 37.1824 | 37.5527 | 37.754 | 24.2672 | 19.2696 | 93.2223 | 33.8316 | 35.0332 | 36.2761 | 35.1068 | 34.4957 | 34.7268 | 35.7302 | 34.9102 | 34.9186 | 37.724 | 36.7661 | 34.7311 | 34.9297 | 36.794 | 37.3335 | 38.0738 | 36.7752 | 35.1147 | 34.7736 | 36.1371 | 36.5007 | 34.6314 | 34.5073 | 34.4175 | 34.6795 | 33.4687 | 33.9811 | 33.6389 | 34.4003 | 33.4502 | 35.1255 | 36.3404 | 35.1324 | 35.3444 | 35.3112 | 93.0788 | 93.3104 | 93.0428
2022-09-07 23:34 | 1:44 | 18.4973 | 18.6638 | 20.5422 | 35.595 | 33.9127 | 35.7697 | 35.8744 | 36.208 | 37.0317 | 37.0558 | 36.4609 | 37.1227 | 34.5006 | 33.9899 | 36.1482 | 36.127 | 37.3232 | 37.193 | 37.5495 | 37.7599 | 24.2364 | 19.2025 | 93.2118 | 33.8707 | 35.0289 | 36.2794 | 35.1108 | 34.4824 | 34.7259 | 35.7353 | 34.9261 | 34.9308 | 37.7315 | 36.7536 | 34.7329 | 34.9278 | 36.7721 | 37.3295 | 38.0726 | 36.7725 | 35.096 | 34.7531 | 36.1066 | 36.4868 | 34.6371 | 34.4845 | 34.4455 | 34.6762 | 33.456 | 34.0064 | 33.6718 | 34.384 | 33.4518 | 35.1327 | 36.3495 | 35.1337 | 35.3415 | 35.294 | 92.9725 | 93.1495 | 92.8616
2022-09-07 23:34 | 1:44 | 18.5159 | 18.6391 | 20.4997 | 35.5444 | 33.9029 | 35.7748 | 35.9095 | 36.2031 | 37.0327 | 37.0493 | 36.4488 | 37.1403 | 34.5173 | 33.968 | 36.1534 | 36.1158 | 37.311 | 37.1798 | 37.5565 | 37.7656 | 24.2313 | 19.2378 | 93.2547 | 33.9182 | 35.0197 | 36.2632 | 35.1177 | 34.4866 | 34.7345 | 35.7396 | 34.9143 | 34.9226 | 37.7201 | 36.7433 | 34.7436 | 34.9452 | 36.7661 | 37.3249 | 38.0625 | 36.7841 | 35.0969 | 34.7237 | 36.1116 | 36.5006 | 34.6189 | 34.524 | 34.4333 | 34.6927 | 33.4764 | 33.9866 | 33.6529 | 34.4059 | 33.4318 | 35.1386 | 36.3509 | 35.137 | 35.3486 | 35.3173 | 92.8667 | 93.0377 | 92.8665
2022-09-07 23:34 | 1:44 | 18.5147 | 18.6555 | 20.4883 | 35.6074 | 33.9064 | 35.7742 | 35.8712 | 36.2069 | 37.0616 | 37.0639 | 36.462 | 37.1504 | 34.5043 | 33.9801 | 36.1659 | 36.1148 | 37.3208 | 37.164 | 37.5559 | 37.733 | 24.2281 | 19.2324 | 93.3478 | 33.8366 | 35.0423 | 36.2806 | 35.1092 | 34.5099 | 34.7291 | 35.7601 | 34.9172 | 34.9361 | 37.7186 | 36.7506 | 34.7281 | 34.9121 | 36.7536 | 37.325 | 38.0918 | 36.794 | 35.0924 | 34.7439 | 36.1125 | 36.4818 | 34.6204 | 34.5103 | 34.4184 | 34.676 | 33.4494 | 33.9772 | 33.665 | 34.4082 | 33.4489 | 35.1523 | 36.3428 | 35.1282 | 35.3582 | 35.3028 | 92.6914 | 92.924 | 92.6823
2022-09-07 23:34 | 1:44 | 18.5203 | 18.6519 | 20.4885 | 35.5638 | 33.8948 | 35.7451 | 35.8729 | 36.2138 | 37.0411 | 37.0643 | 36.4531 | 37.1538 | 34.4907 | 33.9485 | 36.1476 | 36.107 | 37.2921 | 37.1711 | 37.5466 | 37.7485 | 24.2004 | 19.2431 | 93.4644 | 33.6606 | 35.0273 | 36.2626 | 35.1147 | 34.5097 | 34.7311 | 35.7482 | 34.9159 | 34.9107 | 37.7189 | 36.7671 | 34.7303 | 34.9097 | 36.7433 | 37.3451 | 38.0716 | 36.7721 | 35.0856 | 34.7227 | 36.1229 | 36.4887 | 34.5997 | 34.5049 | 34.4355 | 34.6563 | 33.453 | 33.9636 | 33.656 | 34.3963 | 33.4256 | 35.1164 | 36.3494 | 35.1356 | 35.3634 | 35.303 | 92.5834 | 92.7941 | 92.5917
2022-09-07 23:34 | 1:44 | 18.4222 | 18.5938 | 20.4404 | 35.5722 | 33.8888 | 35.7806 | 35.8846 | 36.2227 | 37.045 | 37.066 | 36.4512 | 37.1348 | 34.4998 | 33.9405 | 36.1484 | 36.1058 | 37.2957 | 37.1748 | 37.5471 | 37.7474 | 24.1885 | 19.1642 | 93.5077 | 33.93 | 35.0103 | 36.2648 | 35.096 | 34.4938 | 34.7329 | 35.7594 | 34.8993 | 34.9483 | 37.7375 | 36.7538 | 34.7302 | 34.902 | 36.7506 | 37.3433 | 38.0767 | 36.7661 | 35.0892 | 34.7175 | 36.1158 | 36.4656 | 34.6202 | 34.4975 | 34.4332 | 34.6665 | 33.4835 | 33.9637 | 33.6179 | 34.3982 | 33.4362 | 35.1345 | 36.339 | 35.1481 | 35.3617 | 35.3025 | 92.4665 | 92.6927 | 92.5349
2022-09-07 23:35 | 1:44 | 18.4102 | 18.561 | 20.4396 | 35.6239 | 33.8787 | 35.758 | 35.8955 | 36.2122 | 37.0176 | 37.0861 | 36.4564 | 37.1303 | 34.4938 | 33.9404 | 36.1264 | 36.0883 | 37.2969 | 37.1829 | 37.5688 | 37.758 | 24.1647 | 19.1479 | 93.4567 | 33.8297 | 35.0288 | 36.258 | 35.0969 | 34.4846 | 34.7436 | 35.7495 | 34.9231 | 34.9205 | 37.7233 | 36.7761 | 34.7207 | 34.9206 | 36.7671 | 37.3529 | 38.0769 | 36.7536 | 35.0895 | 34.7173 | 36.0845 | 36.4879 | 34.5961 | 34.4876 | 34.4265 | 34.649 | 33.4313 | 33.9703 | 33.6501 | 34.3698 | 33.4591 | 35.138 | 36.3407 | 35.1333 | 35.3476 | 35.3137 | 92.3749 | 92.5694 | 92.4409
2022-09-07 23:35 | 1:45 | 18.4329 | 18.5751 | 20.4237 | 35.5295 | 33.8738 | 35.7642 | 35.9041 | 36.1822 | 37.0397 | 37.0852 | 36.4558 | 37.1504 | 34.4995 | 33.9157 | 36.1386 | 36.092 | 37.2692 | 37.1789 | 37.5824 | 37.7413 | 24.1459 | 19.1369 | 93.5817 | 33.8692 | 35.0127 | 36.2463 | 35.0924 | 34.4927 | 34.7281 | 35.7554 | 34.928 | 34.9243 | 37.7175 | 36.7517 | 34.7066 | 34.9144 | 36.7538 | 37.3349 | 38.0651 | 36.7433 | 35.0874 | 34.7042 | 36.1071 | 36.4798 | 34.5994 | 34.5055 | 34.4158 | 34.662 | 33.4545 | 33.9882 | 33.6477 | 34.3825 | 33.4112 | 35.1462 | 36.3268 | 35.1291 | 35.3555 | 35.2869 | 92.2814 | 92.4168 | 92.3835
2022-09-07 23:35 | 1:45 | 18.4714 | 18.614 | 20.4533 | 35.6148 | 33.8808 | 35.7399 | 35.8833 | 36.2215 | 37.0408 | 37.0785 | 36.4481 | 37.1471 | 34.4757 | 33.9279 | 36.1189 | 36.1119 | 37.3058 | 37.1763 | 37.5537 | 37.7479 | 24.1303 | 19.2017 | 93.752 | 33.942 | 35.0062 | 36.2359 | 35.0856 | 34.4951 | 34.7303 | 35.745 | 34.9333 | 34.9444 | 37.7231 | 36.748 | 34.7394 | 34.9066 | 36.7761 | 37.3379 | 38.0554 | 36.7506 | 35.0667 | 34.6874 | 36.1013 | 36.4702 | 34.6056 | 34.5152 | 34.4145 | 34.6438 | 33.4407 | 33.9625 | 33.6246 | 34.3907 | 33.4253 | 35.154 | 36.3363 | 35.1455 | 35.3614 | 35.2949 | 92.1556 | 92.2895 | 92.3486
2022-09-07 23:35 | 1:45 | 18.5107 | 18.6312 | 20.4465 | 35.6938 | 33.8859 | 35.7614 | 35.9024 | 36.2218 | 37.0381 | 37.074 | 36.4592 | 37.1512 | 34.4515 | 33.9209 | 36.1329 | 36.1065 | 37.2975 | 37.1701 | 37.556 | 37.7463 | 24.1507 | 19.2445 | 93.8556 | 33.7159 | 35.0224 | 36.2732 | 35.0892 | 34.4865 | 34.7302 | 35.7459 | 34.9117 | 34.9374 | 37.7119 | 36.7509 | 34.7175 | 34.9156 | 36.7517 | 37.3219 | 38.0479 | 36.7671 | 35.0933 | 34.668 | 36.0833 | 36.4717 | 34.615 | 34.511 | 34.4145 | 34.6352 | 33.4326 | 33.9769 | 33.6154 | 34.378 | 33.4303 | 35.1362 | 36.3351 | 35.1466 | 35.3705 | 35.2987 | 92.0038 | 92.1742 | 92.1612
2022-09-07 23:35 | 1:45 | 18.494 | 18.6547 | 20.4468 | 35.5311 | 33.8731 | 35.7606 | 35.8876 | 36.2113 | 37.0304 | 37.0826 | 36.4776 | 37.152 | 34.4598 | 33.9068 | 36.1311 | 36.0911 | 37.2826 | 37.1799 | 37.5431 | 37.7573 | 24.1287 | 19.2198 | 93.9497 | 33.7975 | 35.0115 | 36.2447 | 35.0895 | 34.4988 | 34.7207 | 35.7568 | 34.9302 | 34.9484 | 37.7317 | 36.7308 | 34.7133 | 34.898 | 36.748 | 37.3191 | 38.045 | 36.7538 | 35.0692 | 34.7082 | 36.0901 | 36.4724 | 34.5698 | 34.4948 | 34.4227 | 34.6292 | 33.4356 | 33.965 | 33.6372 | 34.395 | 33.4259 | 35.133 | 36.3378 | 35.1353 | 35.3726 | 35.2653 | 91.9855 | 92.1855 | 92.146
2022-09-07 23:35 | 1:45 | 18.4657 | 18.619 | 20.4886 | 35.5027 | 33.8632 | 35.7465 | 35.8901 | 36.2269 | 37.0348 | 37.0868 | 36.4689 | 37.1543 | 34.4501 | 33.8916 | 36.1255 | 36.0944 | 37.2706 | 37.1777 | 37.5536 | 37.7314 | 24.1263 | 19.2034 | 94.0758 | 33.7526 | 35.0111 | 36.2412 | 35.0874 | 34.4883 | 34.7066 | 35.7625 | 34.911 | 34.9294 | 37.7226 | 36.7364 | 34.729 | 34.9096 | 36.7509 | 37.3251 | 38.058 | 36.7761 | 35.0742 | 34.6632 | 36.0728 | 36.4723 | 34.5545 | 34.5159 | 34.4188 | 34.642 | 33.4275 | 33.9764 | 33.6378 | 34.3884 | 33.4229 | 35.1654 | 36.319 | 35.1558 | 35.3686 | 35.2765 | 92.0368 | 92.2425 | 92.2299
2022-09-07 23:36 | 1:46 | 18.4659 | 18.5913 | 20.4418 | 35.5799 | 33.8733 | 35.757 | 35.8885 | 36.2087 | 37.0201 | 37.0893 | 36.4589 | 37.155 | 34.4295 | 33.874 | 36.1154 | 36.0906 | 37.2623 | 37.1708 | 37.567 | 37.7401 | 24.1092 | 19.1874 | 94.1516 | 33.6385 | 35.0074 | 36.2397 | 35.0667 | 34.4821 | 34.7394 | 35.7634 | 34.9177 | 34.938 | 37.7133 | 36.7398 | 34.7074 | 34.9086 | 36.7308 | 37.3302 | 38.0496 | 36.7517 | 35.0699 | 34.6776 | 36.0821 | 36.4605 | 34.5643 | 34.5105 | 34.3866 | 34.6429 | 33.416 | 33.9577 | 33.6272 | 34.3786 | 33.4319 | 35.1296 | 36.3329 | 35.1592 | 35.3645 | 35.2765 | 92.1097 | 92.3595 | 92.3023
2022-09-07 23:36 | 1:46 | 18.4712 | 18.6102 | 20.44 | 35.6056 | 33.8532 | 35.7563 | 35.897 | 36.2043 | 37.0209 | 37.0942 | 36.4794 | 37.1354 | 34.4393 | 33.8862 | 36.114 | 36.0947 | 37.2626 | 37.1912 | 37.5581 | 37.7264 | 24.0874 | 19.2028 | 94.0775 | 33.6896 | 34.9972 | 36.221 | 35.0933 | 34.4886 | 34.7175 | 35.754 | 34.8891 | 34.94 | 37.7149 | 36.7364 | 34.7073 | 34.9025 | 36.7364 | 37.3267 | 38.0478 | 36.748 | 35.0589 | 34.6614 | 36.0667 | 36.4345 | 34.5665 | 34.5205 | 34.4416 | 34.6132 | 34.4908 | 33.9536 | 33.6429 | 34.3713 | 33.4207 | 35.1253 | 36.3193 | 35.1549 | 35.363 | 35.272 | 92.1715 | 92.4161 | 92.3818
2022-09-07 23:36 | 1:46 | 18.5188 | 18.6504 | 20.4431 | 35.5955 | 33.8673 | 35.7216 | 35.882 | 36.194 | 37.0489 | 37.0948 | 36.465 | 37.1542 | 34.4375 | 33.8699 | 36.1105 | 36.1019 | 37.2634 | 37.1795 | 37.5592 | 37.7451 | 24.0725 | 19.2354 | 94.2027 | 33.8953 | 34.9921 | 36.2283 | 35.0692 | 34.4756 | 34.7133 | 35.7548 | 34.9272 | 34.9256 | 37.7093 | 36.7288 | 34.7001 | 34.8942 | 36.7398 | 37.3317 | 38.0317 | 36.7509 | 35.0636 | 34.6712 | 36.0623 | 36.4673 | 34.5485 | 34.524 | 34.4127 | 34.5959 | 34.4978 | 33.9539 | 33.6216 | 34.3619 | 34.4908 | 35.152 | 36.3145 | 35.1555 | 35.3719 | 35.2539 | 92.2618 | 92.5038 | 92.3887
2022-09-07 23:36 | 1:46 | 18.5116 | 18.6398 | 20.4304 | 35.4947 | 33.8689 | 35.7348 | 35.8838 | 36.2198 | 37.0409 | 37.0855 | 36.4565 | 37.1669 | 34.44 | 33.8585 | 36.0943 | 36.097 | 37.2738 | 37.1617 | 37.5551 | 37.7327 | 24.0655 | 19.231 | 94.3325 | 33.9483 | 34.9969 | 36.2208 | 35.0742 | 34.4834 | 34.729 | 35.7541 | 34.9218 | 34.9215 | 37.6969 | 36.7313 | 34.704 | 34.8964 | 36.7364 | 37.3274 | 38.0642 | 36.7308 | 35.0536 | 34.6509 | 36.056 | 36.4557 | 34.5602 | 34.5166 | 34.4259 | 34.6017 | 34.4957 | 33.965 | 33.618 | 34.3871 | 34.4978 | 35.138 | 36.3325 | 35.1583 | 35.3623 | 35.242 | 92.3816 | 92.6237 | 92.4838
2022-09-07 23:36 | 1:46 | 18.4402 | 18.6246 | 20.4029 | 35.608 | 33.8443 | 35.7135 | 35.9017 | 36.2297 | 37.0243 | 37.074 | 36.4709 | 37.1345 | 34.4191 | 33.8649 | 36.1107 | 36.0866 | 37.2594 | 37.1574 | 37.528 | 37.71 | 24.041 | 19.1841 | 94.2318 | 33.8412 | 34.9875 | 36.2339 | 35.0699 | 34.4774 | 34.7074 | 35.7542 | 34.9178 | 34.9318 | 37.7137 | 36.7409 | 34.7022 | 34.92 | 36.7288 | 37.3113 | 38.0346 | 36.7364 | 35.0479 | 34.6369 | 36.06 | 36.458 | 34.5476 | 34.5186 | 34.4147 | 34.6053 | 34.4833 | 33.9701 | 33.6302 | 34.3556 | 34.4957 | 35.1302 | 36.3154 | 35.156 | 35.3741 | 35.2452 | 92.4759 | 92.727 | 92.512
2022-09-07 23:36 | 1:46 | 18.4192 | 18.5739 | 20.3944 | 35.5092 | 33.8532 | 35.6982 | 35.8857 | 36.2116 | 37.0313 | 37.0925 | 36.4629 | 37.157 | 34.4533 | 33.8495 | 36.0961 | 36.1064 | 37.2594 | 37.1615 | 37.5378 | 37.7216 | 24.0345 | 19.2216 | 94.3066 | 33.7729 | 34.9708 | 36.201 | 35.0589 | 34.4796 | 34.7073 | 35.7562 | 34.9158 | 34.9234 | 37.7204 | 36.7347 | 34.7081 | 34.8937 | 36.7313 | 37.3103 | 38.0213 | 36.7398 | 35.0609 | 34.6278 | 36.0371 | 36.4226 | 34.5555 | 34.5311 | 34.406 | 34.6062 | 34.4959 | 33.9623 | 33.6025 | 34.3519 | 34.4833 | 35.1249 | 36.3043 | 35.1568 | 35.3627 | 35.2277 | 92.594 | 92.8688 | 92.6813
2022-09-07 23:37 | 1:46 | 18.447 | 18.5955 | 20.3946 | 35.6687 | 33.8386 | 35.7152 | 35.8969 | 36.207 | 37.0225 | 37.0795 | 36.4594 | 37.1603 | 34.4199 | 33.8319 | 36.0752 | 36.0849 | 37.2439 | 37.1573 | 37.5325 | 37.7085 | 24.0074 | 19.1087 | 94.1817 | 33.8294 | 34.9616 | 36.213 | 35.0636 | 34.4829 | 34.7001 | 35.7622 | 34.9207 | 34.9171 | 37.712 | 36.7219 | 34.7023 | 34.9004 | 36.7409 | 37.2939 | 38.0376 | 36.7364 | 35.039 | 34.6192 | 36.0324 | 36.4146 | 34.5146 | 34.529 | 34.4066 | 34.5986 | 34.4665 | 33.9634 | 33.6017 | 34.3504 | 34.4959 | 35.1223 | 36.3252 | 35.1649 | 35.3649 | 35.2187 | 92.7258 | 93.0039 | 92.8004
2022-09-07 23:37 | 1:47 | 18.3555 | 18.4824 | 20.3724 | 35.5298 | 33.8264 | 35.7195 | 35.8985 | 36.2016 | 37.0095 | 37.0816 | 36.4591 | 37.1589 | 34.4071 | 33.8186 | 36.0843 | 36.0688 | 37.22 | 37.1618 | 37.5159 | 37.721 | 23.9982 | 19.0476 | 94.2376 | 33.7616 | 34.9621 | 36.2148 | 35.0536 | 34.4857 | 34.704 | 35.7359 | 34.9061 | 34.9058 | 37.6977 | 36.7117 | 34.689 | 34.8769 | 36.7347 | 37.298 | 38.0218 | 36.7288 | 35.0565 | 34.6244 | 36.0349 | 36.4104 | 34.5361 | 34.515 | 34.4136 | 34.5776 | 34.4603 | 33.943 | 33.6112 | 34.3625 | 34.4665 | 35.1245 | 36.3147 | 35.1716 | 35.3682 | 35.2273 | 92.8096 | 93.1003 | 92.7818
2022-09-07 23:37 | 1:47 | 18.322 | 18.4731 | 20.3254 | 35.5981 | 33.8248 | 35.6881 | 35.8932 | 36.199 | 37.0176 | 37.0806 | 36.4629 | 37.1713 | 34.4078 | 33.8181 | 36.0843 | 36.0844 | 37.2088 | 37.1799 | 37.5365 | 37.7143 | 23.9927 | 19.0679 | 94.0755 | 33.6739 | 34.9649 | 36.2202 | 35.0479 | 34.4651 | 34.7022 | 35.7438 | 34.9185 | 34.9131 | 37.7011 | 36.7259 | 34.6717 | 34.9036 | 36.7219 | 37.3073 | 38.0087 | 36.7313 | 35.0127 | 34.6304 | 36.0303 | 36.3939 | 34.5291 | 34.5234 | 34.3965 | 34.5847 | 34.4801 | 33.9536 | 33.6117 | 34.3527 | 34.4603 | 35.1226 | 36.3103 | 35.1638 | 35.3669 | 35.2124 | 92.9223 | 93.216 | 92.9058
2022-09-07 23:37 | 1:47 | 18.3751 | 18.5386 | 20.3302 | 35.5319 | 33.8103 | 35.6962 | 35.8904 | 36.2141 | 37.0235 | 37.087 | 36.4723 | 37.1457 | 34.3955 | 33.8035 | 36.0611 | 36.091 | 37.226 | 37.1608 | 37.5351 | 37.7069 | 24.0108 | 19.0719 | 94.054 | 33.724 | 34.9455 | 36.207 | 35.0609 | 34.4617 | 34.7081 | 35.7565 | 34.9265 | 34.9071 | 37.6755 | 36.7283 | 34.7 | 34.8921 | 36.7117 | 37.2999 | 38.0236 | 36.7409 | 35.0348 | 34.5989 | 35.9973 | 36.398 | 34.5305 | 34.5235 | 34.4198 | 34.5523 | 34.4601 | 33.9531 | 33.5968 | 34.3453 | 34.4801 | 35.1195 | 36.2993 | 35.1374 | 35.3542 | 35.2142 | 93.0114 | 93.3345 | 92.9724
2022-09-07 23:37 | 1:47 | 18.3826 | 18.5483 | 20.3366 | 35.4442 | 33.816 | 35.684 | 35.8989 | 36.1867 | 37.0095 | 37.0829 | 36.4772 | 37.1703 | 34.3994 | 33.7984 | 36.0699 | 36.066 | 37.2087 | 37.1617 | 37.5313 | 37.6912 | 24.0417 | 19.0572 | 93.9193 | 33.7839 | 34.9596 | 36.2067 | 35.039 | 34.4656 | 34.7023 | 35.7433 | 34.907 | 34.8995 | 37.6836 | 36.7293 | 34.6973 | 34.892 | 36.7259 | 37.3139 | 38.0261 | 36.7347 | 35.0423 | 34.5856 | 36.0191 | 36.4018 | 34.5074 | 34.5212 | 34.4169 | 34.5732 | 34.469 | 33.9453 | 33.607 | 34.3434 | 34.4601 | 35.0994 | 36.3044 | 35.1621 | 35.3771 | 35.2015 | 93.1396 | 93.4437 | 93.074
2022-09-07 23:37 | 1:47 | 18.363 | 18.549 | 20.3498 | 35.5814 | 33.8193 | 35.7015 | 35.879 | 36.1893 | 37.013 | 37.073 | 36.4731 | 37.1699 | 34.3788 | 33.7803 | 36.0662 | 36.0904 | 37.2018 | 37.1547 | 37.523 | 37.685 | 24.0302 | 19.0793 | 93.8714 | 33.8495 | 34.9528 | 36.2109 | 35.0565 | 34.4848 | 34.689 | 35.7443 | 34.9235 | 34.8999 | 37.7079 | 36.7261 | 34.6772 | 34.8906 | 36.7283 | 37.3028 | 38.021 | 36.7219 | 35.0435 | 34.6083 | 35.9907 | 36.3785 | 34.5192 | 34.5264 | 34.4241 | 34.5668 | 34.4537 | 33.9588 | 33.5972 | 34.3425 | 34.469 | 35.1138 | 36.3165 | 35.1586 | 35.3834 | 35.1934 | 93.2959 | 93.6119 | 93.1459
2022-09-07 23:38 | 1:48 | 18.3409 | 18.4957 | 20.2968 | 35.4622 | 33.818 | 35.6806 | 35.8851 | 36.1989 | 37.0023 | 37.0904 | 36.4729 | 37.1668 | 34.3912 | 33.7764 | 36.0665 | 36.0813 | 37.2075 | 37.1454 | 37.5123 | 37.6889 | 24.0498 | 19.0255 | 93.7876 | 33.7707 | 34.95 | 36.1935 | 35.0127 | 34.4742 | 34.6717 | 35.738 | 34.913 | 34.915 | 37.697 | 36.7191 | 34.7058 | 34.8954 | 36.7293 | 37.2962 | 38.0126 | 36.7117 | 35.0339 | 34.5968 | 36.005 | 36.3752 | 34.5196 | 34.532 | 34.4261 | 34.5546 | 34.4765 | 33.9451 | 33.5876 | 34.3384 | 34.4537 | 35.1084 | 36.3108 | 35.1594 | 35.3759 | 35.1883 | 93.4047 | 93.7582 | 93.2225
2022-09-07 23:38 | 1:48 | 18.3076 | 18.4694 | 20.3191 | 35.4453 | 33.8016 | 35.6798 | 35.8931 | 36.2014 | 37.0129 | 37.0929 | 36.489 | 37.18 | 34.3805 | 33.7638 | 36.0514 | 36.0841 | 37.1933 | 37.1626 | 37.5002 | 37.686 | 24.0549 | 18.9732 | 93.877 | 33.7105 | 34.951 | 36.1992 | 35.0348 | 34.4873 | 34.7 | 35.7314 | 34.8963 | 34.9097 | 37.6936 | 36.7195 | 34.7019 | 34.8945 | 36.7261 | 37.2985 | 38.0003 | 36.7259 | 35.0392 | 34.5862 | 35.9764 | 36.3814 | 34.4901 | 34.5422 | 34.409 | 34.5664 | 34.4607 | 33.9436 | 33.6025 | 34.3456 | 34.4765 | 35.1122 | 36.295 | 35.1673 | 35.3941 | 35.1802 | 93.5561 | 93.9242 | 93.3127
2022-09-07 23:38 | 1:48 | 18.3501 | 18.484 | 20.3401 | 35.577 | 33.7949 | 35.6863 | 35.8715 | 36.1938 | 37.0072 | 37.0805 | 36.4619 | 37.1712 | 34.3789 | 33.7787 | 36.0425 | 36.0868 | 37.201 | 37.1623 | 37.5102 | 37.6951 | 24.0431 | 19.0213 | 93.7157 | 33.8071 | 34.9509 | 36.195 | 35.0423 | 34.4638 | 34.6973 | 35.7444 | 34.9136 | 34.9103 | 37.6875 | 36.7171 | 34.6904 | 34.8925 | 36.7191 | 37.3005 | 38.0122 | 36.7283 | 35.0476 | 34.5682 | 35.988 | 36.378 | 34.5096 | 34.5447 | 34.4133 | 34.5567 | 34.4725 | 33.9386 | 33.6023 | 34.3554 | 34.4607 | 35.0968 | 36.3075 | 35.178 | 35.3555 | 35.1807 | 93.7347 | 94.1329 | 93.4656
2022-09-07 23:38 | 1:48 | 18.3788 | 18.5143 | 20.3299 | 35.4853 | 33.7836 | 35.6895 | 35.8851 | 36.1829 | 37.0001 | 37.0742 | 36.4846 | 37.1824 | 34.3841 | 33.762 | 36.0476 | 36.0883 | 37.2046 | 37.1482 | 37.5023 | 37.6793 | 24.0725 | 19.0148 | 93.6996 | 33.7489 | 34.9471 | 36.2002 | 35.0435 | 34.4769 | 34.6772 | 35.7457 | 34.924 | 34.9184 | 37.6752 | 36.7206 | 34.6999 | 34.891 | 36.7195 | 37.3012 | 38.0024 | 36.7293 | 35.0433 | 34.5639 | 35.9804 | 36.3805 | 34.5187 | 34.5512 | 34.4082 | 34.5411 | 34.462 | 33.9464 | 33.6067 | 34.3309 | 34.4725 | 35.1225 | 36.3162 | 35.1844 | 35.3689 | 35.1508 | 93.8805 | 94.3357 | 93.5554
2022-09-07 23:38 | 1:48 | 18.3883 | 18.5419 | 20.3546 | 35.4432 | 33.7873 | 35.6647 | 35.9034 | 36.2003 | 37.0138 | 37.0953 | 36.5042 | 37.1763 | 34.3563 | 33.7567 | 36.0532 | 36.0759 | 37.1956 | 37.1524 | 37.5319 | 37.7008 | 24.0506 | 19.0384 | 93.7515 | 33.7478 | 34.9426 | 36.1826 | 35.0339 | 34.4759 | 34.7058 | 35.7367 | 34.9213 | 34.9191 | 37.7014 | 36.7317 | 34.6891 | 34.9135 | 36.7171 | 37.2874 | 37.9859 | 36.7261 | 35.0519 | 34.5809 | 35.9807 | 36.3642 | 34.5134 | 34.5315 | 34.4096 | 34.5513 | 34.4569 | 33.9492 | 33.5897 | 34.3487 | 34.462 | 35.119 | 36.3026 | 35.1841 | 35.3736 | 35.169 | 94.1034 | 94.5225 | 93.7563
2022-09-07 23:38 | 1:48 | 18.3362 | 18.4895 | 20.3081 | 35.4987 | 33.7729 | 35.6742 | 35.8971 | 36.1986 | 36.9907 | 37.0999 | 36.4962 | 37.1792 | 34.3718 | 33.734 | 36.0376 | 36.0779 | 37.1998 | 37.1601 | 37.5254 | 37.68 | 24.0318 | 18.9736 | 93.6841 | 33.5154 | 34.9305 | 36.1923 | 35.0392 | 34.465 | 34.7019 | 35.745 | 34.929 | 34.9113 | 37.6892 | 36.7303 | 34.687 | 34.9035 | 36.7206 | 37.2844 | 37.9913 | 36.7191 | 35.0218 | 34.5648 | 35.9659 | 36.3592 | 34.4937 | 34.5338 | 34.4053 | 34.5454 | 34.4577 | 33.9393 | 33.5858 | 34.3237 | 34.4569 | 35.1121 | 36.3121 | 35.1708 | 35.3526 | 35.1786 | 94.2758 | 94.7292 | 93.8794
2022-09-07 23:39 | 1:48 | 18.3386 | 18.4697 | 20.2864 | 35.4303 | 33.7908 | 35.6557 | 35.8922 | 36.2031 | 37.0059 | 37.084 | 36.4941 | 37.1666 | 34.3655 | 33.738 | 36.0144 | 36.0734 | 37.1878 | 37.1557 | 37.5149 | 37.6677 | 24.0459 | 19.0374 | 93.7476 | 33.5653 | 34.9269 | 36.1954 | 35.0476 | 34.4535 | 34.6904 | 35.7522 | 34.9273 | 34.9176 | 37.6835 | 36.706 | 34.6884 | 34.9039 | 36.7317 | 37.3067 | 37.9808 | 36.7195 | 35.0218 | 34.5598 | 35.9714 | 36.3789 | 34.4784 | 34.5333 | 34.4288 | 34.5347 | 34.4593 | 33.9288 | 33.5973 | 34.3219 | 34.4577 | 35.1183 | 36.3055 | 35.1893 | 35.3659 | 35.1709 | 94.411 | 94.8865 | 94.0291
2022-09-07 23:39 | 1:49 | 18.3299 | 18.4882 | 20.317 | 35.5418 | 33.771 | 35.6816 | 35.8981 | 36.1959 | 37.0074 | 37.0987 | 36.5025 | 37.1802 | 34.3551 | 33.7489 | 36.0366 | 36.0693 | 37.1852 | 37.1432 | 37.5102 | 37.6826 | 24.0486 | 19.0035 | 93.7023 | 33.6112 | 34.9332 | 36.2097 | 35.0433 | 34.4772 | 34.6999 | 35.7575 | 34.9168 | 34.9168 | 37.7016 | 36.7489 | 34.686 | 34.8879 | 36.7303 | 37.3069 | 37.9926 | 36.7171 | 35.0435 | 34.5524 | 35.9603 | 36.3719 | 34.4804 | 34.538 | 34.4007 | 34.5276 | 34.4451 | 33.935 | 33.5871 | 34.3188 | 34.4593 | 35.1132 | 36.3165 | 35.1891 | 35.386 | 35.1593 | 94.6159 | 95.0879 | 94.0592
2022-09-07 23:39 | 1:49 | 18.3348 | 18.4838 | 20.308 | 35.5723 | 33.7713 | 35.6663 | 35.8926 | 36.2081 | 37.0046 | 37.0943 | 36.4894 | 37.1991 | 34.3581 | 33.7293 | 36.0433 | 36.0839 | 37.1944 | 37.1596 | 37.5214 | 37.6864 | 24.0261 | 19.0343 | 93.5902 | 33.7757 | 34.9251 | 36.2038 | 35.0519 | 34.4652 | 34.6891 | 35.7535 | 34.9131 | 34.911 | 37.6818 | 36.7447 | 34.6823 | 34.9046 | 36.706 | 37.2914 | 38.0078 | 36.7206 | 35.035 | 34.5477 | 35.954 | 36.3687 | 34.4781 | 34.5456 | 34.4162 | 34.5282 | 34.4578 | 33.9442 | 33.5944 | 34.316 | 34.4451 | 35.1204 | 36.3193 | 35.1775 | 35.3935 | 35.1655 | 94.8182 | 95.2204 | 94.2523
2022-09-07 23:39 | 1:49 | 18.321 | 18.4754 | 20.2699 | 35.4824 | 33.7757 | 35.6817 | 35.9038 | 36.1855 | 37.0084 | 37.0867 | 36.5099 | 37.1844 | 34.3535 | 33.6947 | 36.0229 | 36.0656 | 37.1984 | 37.1518 | 37.5134 | 37.6864 | 24.026 | 18.9934 | 93.4438 | 33.8036 | 34.9492 | 36.196 | 35.0218 | 34.4648 | 34.687 | 35.7522 | 34.9338 | 34.9202 | 37.684 | 36.7186 | 34.6903 | 34.9063 | 36.7489 | 37.2955 | 38.0089 | 36.7317 | 35.033 | 34.552 | 35.9487 | 36.3673 | 34.4774 | 34.5389 | 34.4172 | 34.5335 | 34.4566 | 33.9476 | 33.59 | 34.3165 | 34.4578 | 35.1161 | 36.3192 | 35.1954 | 35.3882 | 35.1532 | 94.896 | 95.3834 | 94.2619
2022-09-07 23:39 | 1:49 | 18.1953 | 18.4001 | 20.2284 | 35.5138 | 33.763 | 35.6675 | 35.9014 | 36.1881 | 36.99 | 37.0998 | 36.5146 | 37.2064 | 34.3406 | 33.693 | 36.034 | 36.0687 | 37.1881 | 37.1692 | 37.5227 | 37.673 | 24.0055 | 18.9176 | 93.4428 | 33.652 | 34.9212 | 36.1744 | 35.0218 | 34.4629 | 34.6884 | 35.7362 | 34.9322 | 34.9182 | 37.6901 | 36.7365 | 34.6791 | 34.9167 | 36.7447 | 37.2926 | 37.9886 | 36.7303 | 35.0497 | 34.545 | 35.9562 | 36.3593 | 34.4566 | 34.558 | 34.4061 | 34.5161 | 34.4468 | 33.9515 | 33.591 | 34.3169 | 34.4566 | 35.0998 | 36.3298 | 35.196 | 35.3847 | 35.1648 | 95.0503 | 95.4924 | 94.3729
2022-09-07 23:39 | 1:49 | 18.251 | 18.3907 | 20.2077 | 35.5145 | 33.7719 | 35.6566 | 35.8963 | 36.1793 | 36.9955 | 37.0981 | 36.5102 | 37.2135 | 34.3464 | 33.7098 | 36.023 | 36.0726 | 37.1869 | 37.1807 | 37.5227 | 37.6757 | 23.9959 | 18.9506 | 93.4315 | 33.7346 | 34.9219 | 36.2124 | 35.0435 | 34.4638 | 34.686 | 35.7679 | 34.933 | 34.9282 | 37.6895 | 36.7215 | 34.6793 | 34.9021 | 36.7186 | 37.3117 | 37.9881 | 36.706 | 35.0306 | 34.5375 | 35.9524 | 36.3434 | 34.4717 | 34.5571 | 34.4011 | 34.5237 | 34.4566 | 33.9507 | 33.5809 | 34.3377 | 34.4468 | 35.1024 | 36.2921 | 35.1993 | 35.378 | 35.1519 | 95.1672 | 95.5786 | 94.4188
2022-09-07 23:40 | 1:50 | 18.2507 | 18.4325 | 20.2164 | 35.4179 | 33.7785 | 35.6645 | 35.8976 | 36.1942 | 36.999 | 37.124 | 36.511 | 37.1917 | 34.3373 | 33.6883 | 36.0416 | 36.0784 | 37.1926 | 37.173 | 37.513 | 37.6818 | 23.982 | 18.9567 | 93.3025 | 33.5133 | 34.9231 | 36.1975 | 35.035 | 34.4716 | 34.6823 | 35.7356 | 34.9343 | 34.9197 | 37.7034 | 36.7087 | 34.6739 | 34.9142 | 36.7365 | 37.3048 | 37.9957 | 36.7489 | 35.0292 | 34.5444 | 35.9629 | 36.3564 | 34.4547 | 34.5525 | 34.4159 | 34.542 | 34.4503 | 33.9251 | 33.5778 | 34.3139 | 34.4566 | 35.1292 | 36.301 | 35.1983 | 35.3961 | 35.1543 | 95.1553 | 95.6673 | 94.5202
2022-09-07 23:40 | 1:50 | 18.2426 | 18.4059 | 20.2264 | 35.5207 | 33.7522 | 35.6434 | 35.9111 | 36.2049 | 37.0118 | 37.1122 | 36.5185 | 37.2128 | 34.3587 | 33.7038 | 36.0221 | 36.0636 | 37.193 | 37.1453 | 37.5293 | 37.6828 | 23.9612 | 18.9116 | 93.3168 | 33.6669 | 34.9239 | 36.1853 | 35.033 | 34.4751 | 34.6903 | 35.7566 | 34.9409 | 34.931 | 37.699 | 36.7244 | 34.6867 | 34.9181 | 36.7215 | 37.295 | 37.9806 | 36.7447 | 35.0204 | 34.5367 | 35.9515 | 36.3378 | 34.4655 | 34.5464 | 34.418 | 34.5176 | 34.4472 | 33.946 | 33.5779 | 34.322 | 34.4503 | 35.1262 | 36.3003 | 35.2019 | 35.3926 | 35.1584 | 95.3366 | 95.7839 | 94.5706
2022-09-07 23:40 | 1:50 | 18.1944 | 18.3437 | 20.1742 | 35.3871 | 33.7691 | 35.669 | 35.9051 | 36.2083 | 37.0018 | 37.117 | 36.5157 | 37.2167 | 34.3423 | 33.6778 | 36.0159 | 36.0654 | 37.1689 | 37.1597 | 37.5047 | 37.6882 | 23.9611 | 18.8651 | 93.1763 | 33.6896 | 34.9308 | 36.1824 | 35.0497 | 34.475 | 34.6791 | 35.7511 | 34.9509 | 34.9141 | 37.6941 | 36.6986 | 34.6756 | 34.9181 | 36.7087 | 37.301 | 37.9785 | 36.7186 | 35.0134 | 34.5629 | 35.9348 | 36.3419 | 34.4559 | 34.5564 | 34.4385 | 34.4981 | 34.4433 | 33.9395 | 33.5894 | 34.3248 | 34.4472 | 35.1264 | 36.304 | 35.2172 | 35.3875 | 35.1613 | 95.2563 | 95.7142 | 94.5542
2022-09-07 23:40 | 1:50 | 18.2014 | 18.3917 | 20.1983 | 35.4871 | 33.7627 | 35.6679 | 35.8946 | 36.2171 | 37.0086 | 37.1106 | 36.508 | 37.2109 | 34.3331 | 33.6917 | 36.0142 | 36.0842 | 37.1717 | 37.1685 | 37.5313 | 37.6796 | 23.9443 | 18.8892 | 93.1416 | 33.6581 | 34.9169 | 36.1831 | 35.0306 | 34.4727 | 34.6793 | 35.7438 | 34.9454 | 34.9324 | 37.7043 | 36.7048 | 34.6902 | 34.925 | 36.7244 | 37.2952 | 37.9725 | 36.7365 | 35.0345 | 34.5301 | 35.9541 | 36.3596 | 34.4627 | 34.5572 | 34.423 | 34.5178 | 34.4488 | 33.9505 | 33.5787 | 34.3122 | 34.4433 | 35.1325 | 36.3149 | 35.2004 | 35.3978 | 35.1439 | 95.0817 | 95.5216 | 94.4188
2022-09-07 23:40 | 1:50 | 18.1964 | 18.3723 | 20.1894 | 35.465 | 33.7624 | 35.6624 | 35.9263 | 36.2046 | 36.9964 | 37.1095 | 36.5267 | 37.2162 | 34.323 | 33.6961 | 36.0061 | 36.0764 | 37.1863 | 37.1744 | 37.5245 | 37.6937 | 23.945 | 18.8375 | 92.9708 | 33.5416 | 34.9114 | 36.1948 | 35.0292 | 34.4753 | 34.6739 | 35.7325 | 34.9456 | 34.9291 | 37.7238 | 36.7255 | 34.6829 | 34.8986 | 36.6986 | 37.2963 | 37.9864 | 36.7215 | 35.0148 | 34.5251 | 35.9446 | 36.3487 | 34.4425 | 34.5596 | 34.4348 | 34.5135 | 34.4307 | 33.9141 | 33.571 | 34.3364 | 34.4488 | 35.1406 | 36.3004 | 35.2076 | 35.4244 | 35.1382 | 94.8367 | 95.2685 | 94.1964
2022-09-07 23:40 | 1:50 | 18.1356 | 18.3167 | 20.1916 | 35.4091 | 33.7509 | 35.6542 | 35.8959 | 36.2072 | 37.0006 | 37.1112 | 36.5365 | 37.2151 | 34.3287 | 33.6728 | 36.0072 | 36.0649 | 37.1831 | 37.1431 | 37.5244 | 37.6863 | 23.9434 | 18.7913 | 92.8566 | 33.5382 | 34.9128 | 36.1767 | 35.0204 | 34.455 | 34.6867 | 35.7609 | 34.9406 | 34.9192 | 37.6962 | 36.7206 | 34.6693 | 34.9098 | 36.7048 | 37.2965 | 37.998 | 36.7087 | 35.0226 | 34.5294 | 35.9243 | 36.3467 | 34.4356 | 34.5483 | 34.426 | 34.5081 | 34.4567 | 33.9179 | 33.5744 | 34.3149 | 34.4307 | 35.1336 | 36.2958 | 35.2065 | 35.3849 | 35.1387 | 94.5849 | 95.0111 | 94.0264
2022-09-07 23:41 | 1:50 | 18.1417 | 18.2943 | 20.1416 | 35.3879 | 33.7572 | 35.6282 | 35.8937 | 36.1971 | 37.0039 | 37.1251 | 36.5418 | 37.2207 | 34.3189 | 33.6766 | 36.0184 | 36.0666 | 37.1683 | 37.1708 | 37.5182 | 37.679 | 23.9111 | 18.7936 | 92.7877 | 33.7526 | 34.918 | 36.1933 | 35.0134 | 34.4645 | 34.6756 | 35.7495 | 34.9519 | 34.9225 | 37.7179 | 36.7148 | 34.682 | 34.9336 | 36.7255 | 37.3078 | 37.987 | 36.7244 | 35.0202 | 34.5115 | 35.9533 | 36.3235 | 34.4482 | 34.5636 | 34.422 | 34.5134 | 34.4334 | 33.9202 | 33.563 | 34.315 | 34.4567 | 35.1469 | 36.2998 | 35.2086 | 35.4083 | 35.1415 | 94.3384 | 94.7889 | 93.9156
2022-09-07 23:41 | 1:51 | 18.124 | 18.2444 | 20.1417 | 35.5386 | 33.7505 | 35.6409 | 35.8999 | 36.1949 | 37.0013 | 37.1362 | 36.5531 | 37.2285 | 34.329 | 33.6575 | 36.0268 | 36.0693 | 37.173 | 37.1584 | 37.5218 | 37.6767 | 23.9173 | 18.7862 | 92.6682 | 33.7099 | 34.9129 | 36.169 | 35.0345 | 34.4864 | 34.6902 | 35.7471 | 34.9427 | 34.926 | 37.692 | 36.7212 | 34.6649 | 34.9266 | 36.7206 | 37.3132 | 37.9714 | 36.6986 | 35.0167 | 34.5248 | 35.9313 | 36.35 | 34.4376 | 34.568 | 34.4314 | 34.5081 | 34.4463 | 33.9591 | 33.5644 | 34.3039 | 34.4334 | 35.1459 | 36.2804 | 35.2045 | 35.3906 | 35.1297 | 94.2212 | 94.6393 | 93.8161
2022-09-07 23:41 | 1:51 | 18.1242 | 18.2555 | 20.1521 | 35.4842 | 33.7551 | 35.6419 | 35.9013 | 36.1985 | 37.0186 | 37.1339 | 36.5314 | 37.2191 | 34.3239 | 33.6513 | 36.0157 | 36.0717 | 37.17 | 37.1763 | 37.5359 | 37.6887 | 23.9066 | 18.7538 | 92.5549 | 33.6048 | 34.9088 | 36.1643 | 35.0148 | 34.4569 | 34.6829 | 35.7377 | 34.9652 | 34.9297 | 37.7011 | 36.71 | 34.68 | 34.9328 | 36.7148 | 37.2964 | 38.0005 | 36.7048 | 35.0134 | 34.4948 | 35.9447 | 36.3558 | 34.4169 | 34.5542 | 34.4409 | 34.4929 | 34.4521 | 33.9314 | 33.5569 | 34.314 | 34.4463 | 35.1453 | 36.2989 | 35.2063 | 35.4001 | 35.1422 | 94.128 | 94.5246 | 93.7557
2022-09-07 23:41 | 1:51 | 18.0354 | 18.2 | 20.076 | 35.4276 | 33.7362 | 35.6417 | 35.9096 | 36.2052 | 37.0039 | 37.1112 | 36.5411 | 37.2367 | 34.3075 | 33.6467 | 36.009 | 36.0849 | 37.178 | 37.1662 | 37.5307 | 37.6925 | 23.8677 | 18.7242 | 92.4736 | 33.4991 | 34.9121 | 36.1924 | 35.0226 | 34.4773 | 34.6693 | 35.759 | 34.946 | 34.9576 | 37.6906 | 36.6996 | 34.6795 | 34.925 | 36.7212 | 37.3115 | 37.9886 | 36.7255 | 35.0227 | 34.5089 | 35.9325 | 36.3674 | 34.4209 | 34.5784 | 34.4174 | 34.5023 | 34.4561 | 33.9301 | 33.5721 | 34.3081 | 34.4521 | 35.1277 | 36.2956 | 35.2133 | 35.4003 | 35.1572 | 94.1 | 94.4615 | 93.7602
2022-09-07 23:41 | 1:51 | 18.0533 | 18.2516 | 20.1072 | 35.4681 | 33.7497 | 35.6443 | 35.9132 | 36.1943 | 37.0118 | 37.1394 | 36.5531 | 37.245 | 34.2976 | 33.6522 | 36.0072 | 36.0763 | 37.1739 | 37.1729 | 37.5105 | 37.7019 | 23.8605 | 18.6954 | 92.3409 | 33.6444 | 34.9069 | 36.1619 | 35.0202 | 34.4418 | 34.682 | 35.7377 | 34.9637 | 34.9222 | 37.6849 | 36.7106 | 34.6734 | 34.909 | 36.71 | 37.289 | 37.9811 | 36.7206 | 34.9945 | 34.5215 | 35.9116 | 36.3424 | 34.4119 | 34.5839 | 34.4221 | 34.5121 | 34.4321 | 33.9154 | 33.5801 | 34.3165 | 34.4561 | 35.1514 | 36.2978 | 35.2185 | 35.4048 | 35.1341 | 93.979 | 94.3535 | 93.6486
2022-09-07 23:41 | 1:51 | 18.0734 | 18.2007 | 20.089 | 35.4669 | 33.7345 | 35.6372 | 35.9111 | 36.2076 | 36.9921 | 37.1335 | 36.5614 | 37.226 | 34.3304 | 33.6586 | 36.0102 | 36.0759 | 37.163 | 37.1774 | 37.5304 | 37.6818 | 23.8372 | 18.7063 | 92.151 | 33.6665 | 34.8825 | 36.1646 | 35.0167 | 34.4541 | 34.6649 | 35.7438 | 34.9473 | 34.938 | 37.7041 | 36.7082 | 34.6555 | 34.946 | 36.6996 | 37.314 | 37.9749 | 36.7148 | 34.9906 | 34.4786 | 35.924 | 36.3605 | 34.4111 | 34.5676 | 34.4384 | 34.4782 | 34.439 | 33.927 | 33.5619 | 34.3069 | 34.4321 | 35.1346 | 36.2729 | 35.2157 | 35.4029 | 35.1412 | 93.953 | 94.287 | 93.6095
2022-09-07 23:42 | 1:51 | 18.0388 | 18.159 | 20.1044 | 35.4877 | 33.7398 | 35.6414 | 35.9188 | 36.2059 | 37.0049 | 37.1398 | 36.5535 | 37.2317 | 34.3033 | 33.6433 | 36.0056 | 36.0799 | 37.1495 | 37.1756 | 37.5194 | 37.677 | 23.8502 | 18.6983 | 92.0457 | 33.5976 | 34.9001 | 36.1577 | 35.0134 | 34.45 | 34.68 | 35.7447 | 34.9605 | 34.932 | 37.6993 | 36.7008 | 34.659 | 34.9182 | 36.7106 | 37.2782 | 37.9769 | 36.7212 | 34.9956 | 34.4804 | 35.9381 | 36.3549 | 34.3957 | 34.5672 | 34.4187 | 34.4974 | 34.4377 | 33.9091 | 33.6068 | 34.2883 | 34.439 | 35.1608 | 36.2843 | 35.2294 | 35.3987 | 35.1341 | 93.9419 | 94.219 | 93.6103
2022-09-07 23:42 | 1:52 | 17.9856 | 18.1602 | 20.0397 | 35.4098 | 33.7114 | 35.6234 | 35.9139 | 36.1967 | 37.0144 | 37.1338 | 36.5381 | 37.2549 | 34.3232 | 33.6334 | 36.0127 | 36.077 | 37.1616 | 37.1585 | 37.5323 | 37.6824 | 23.8357 | 18.6393 | 92.0557 | 33.7056 | 34.9011 | 36.1759 | 35.0227 | 34.4671 | 34.6795 | 35.755 | 34.9499 | 34.9443 | 37.7064 | 36.7011 | 34.6655 | 34.9195 | 36.7082 | 37.2958 | 37.9765 | 36.71 | 34.9924 | 34.4749 | 35.9286 | 36.348 | 34.4048 | 34.5646 | 34.4511 | 34.4804 | 34.4175 | 33.9179 | 33.581 | 34.3128 | 34.4377 | 35.1506 | 36.2805 | 35.2176 | 35.4108 | 35.1392 | 93.8825 | 94.151 | 93.5868
2022-09-07 23:42 | 1:52 | 18.0215 | 18.1574 | 20.0408 | 35.4738 | 33.7469 | 35.6423 | 35.9053 | 36.2082 | 37.0161 | 37.1546 | 36.5573 | 37.253 | 34.3096 | 33.6237 | 36.0121 | 36.0835 | 37.1562 | 37.1754 | 37.5174 | 37.6957 | 23.8515 | 18.6662 | 92.0924 | 33.6124 | 34.872 | 36.1699 | 34.9945 | 34.4508 | 34.6734 | 35.7534 | 34.9492 | 34.928 | 37.6951 | 36.6812 | 34.6699 | 34.9228 | 36.7008 | 37.2978 | 37.9775 | 36.6996 | 34.9799 | 34.4842 | 35.9099 | 36.3488 | 34.4061 | 34.5722 | 34.4283 | 34.4891 | 34.4455 | 33.9106 | 33.5767 | 34.2979 | 34.4175 | 35.1495 | 36.2888 | 35.2284 | 35.4061 | 35.1165 | 93.8097 | 94.0633 | 93.4558
2022-09-07 23:42 | 1:52 | 18.0219 | 18.1755 | 20.0416 | 35.4651 | 33.7238 | 35.6058 | 35.9201 | 36.1998 | 37.0079 | 37.1453 | 36.5498 | 37.2684 | 34.3117 | 33.6083 | 35.9913 | 36.0561 | 37.1453 | 37.1807 | 37.5385 | 37.6974 | 23.8375 | 18.6556 | 92.0739 | 33.6248 | 34.8857 | 36.1634 | 34.9906 | 34.4739 | 34.6555 | 35.7604 | 34.9457 | 34.9263 | 37.7043 | 36.6734 | 34.6462 | 34.9175 | 36.7011 | 37.2761 | 37.9877 | 36.7106 | 34.9641 | 34.4776 | 35.9204 | 36.3453 | 34.3688 | 34.5739 | 34.4471 | 34.4555 | 34.4333 | 33.905 | 33.5516 | 34.3059 | 34.4455 | 35.1652 | 36.2809 | 35.2246 | 35.4214 | 35.115 | 93.7461 | 93.9858 | 93.4631
2022-09-07 23:42 | 1:52 | 18.0322 | 18.192 | 20.0636 | 35.408 | 33.715 | 35.6164 | 35.8988 | 36.1896 | 37.0162 | 37.1376 | 36.5421 | 37.2557 | 34.296 | 33.6061 | 35.9811 | 36.0719 | 37.1516 | 37.1669 | 37.5187 | 37.6696 | 23.8162 | 18.6775 | 92.2272 | 33.7311 | 34.8906 | 36.1491 | 34.9956 | 34.4609 | 34.659 | 35.7384 | 34.9379 | 34.9267 | 37.6893 | 36.6707 | 34.673 | 34.9138 | 36.6812 | 37.2995 | 37.9803 | 36.7082 | 34.992 | 34.4727 | 35.9134 | 36.3234 | 34.3734 | 34.5524 | 34.4458 | 34.4629 | 34.4184 | 33.9151 | 33.5662 | 34.3018 | 34.4333 | 35.1371 | 36.2742 | 35.2107 | 35.4006 | 35.1388 | 93.6376 | 93.9096 | 93.4447
2022-09-07 23:42 | 1:52 | 18.0012 | 18.133 | 20.0367 | 35.3602 | 33.72 | 35.5964 | 35.8984 | 36.1973 | 37.0027 | 37.1486 | 36.5576 | 37.2617 | 34.3086 | 33.5891 | 35.9957 | 36.0462 | 37.1347 | 37.15 | 37.5299 | 37.6872 | 23.7899 | 18.6559 | 92.3618 | 33.7279 | 34.8723 | 36.1694 | 34.9924 | 34.4377 | 34.6655 | 35.7451 | 34.94 | 34.9348 | 37.6947 | 36.6934 | 34.6572 | 34.9175 | 36.6734 | 37.2894 | 37.9613 | 36.7008 | 34.9767 | 34.4728 | 35.9027 | 36.325 | 34.3755 | 34.5728 | 34.4488 | 34.4656 | 34.4355 | 33.8936 | 33.5492 | 34.2972 | 34.4184 | 35.1501 | 36.2699 | 35.2094 | 35.4162 | 35.1245 | 93.6086 | 93.869 | 93.4195
2022-09-07 23:43 | 1:52 | 17.9057 | 18.0707 | 19.9563 | 35.4811 | 33.6997 | 35.5928 | 35.9074 | 36.2072 | 37.006 | 37.1381 | 36.549 | 37.2482 | 34.2818 | 33.5826 | 36.0067 | 36.0573 | 37.1517 | 37.1622 | 37.5174 | 37.6842 | 23.775 | 18.5876 | 92.3616 | 33.6263 | 34.8956 | 36.1505 | 34.9799 | 34.46 | 34.6699 | 35.7699 | 34.9501 | 34.9286 | 37.6679 | 36.672 | 34.6547 | 34.8972 | 36.6707 | 37.2915 | 37.9602 | 36.7011 | 34.9734 | 34.4523 | 35.9044 | 36.3366 | 34.3697 | 34.58 | 34.4568 | 34.4677 | 34.4332 | 33.8956 | 33.5318 | 34.2915 | 34.4355 | 35.1442 | 36.2683 | 35.2051 | 35.4183 | 35.1187 | 93.4873 | 93.7791 | 93.2973
2022-09-07 23:43 | 1:53 | 17.9065 | 18.0222 | 19.9405 | 35.431 | 33.6999 | 35.587 | 35.9007 | 36.2186 | 36.9937 | 37.1658 | 36.5369 | 37.2605 | 34.265 | 33.6092 | 35.9939 | 36.0687 | 37.131 | 37.1542 | 37.5173 | 37.6708 | 23.7315 | 18.5796 | 92.4224 | 33.463 | 34.9008 | 36.1456 | 34.9641 | 34.462 | 34.6462 | 35.7655 | 34.9599 | 34.9049 | 37.6931 | 36.6919 | 34.6607 | 34.8935 | 36.6934 | 37.2828 | 37.9876 | 36.6812 | 34.9698 | 34.466 | 35.8856 | 36.3229 | 34.3492 | 34.5568 | 34.4473 | 34.4402 | 34.4265 | 33.9102 | 33.5521 | 34.2971 | 34.4332 | 35.1488 | 36.2539 | 35.2218 | 35.4143 | 35.1067 | 93.4857 | 93.7126 | 93.3553
2022-09-07 23:43 | 1:53 | 17.927 | 18.047 | 19.9349 | 35.3823 | 33.701 | 35.5931 | 35.902 | 36.1833 | 37.001 | 37.1578 | 36.545 | 37.2437 | 34.271 | 33.576 | 35.9871 | 36.077 | 37.1244 | 37.1642 | 37.5041 | 37.6729 | 23.6825 | 18.6392 | 92.4689 | 33.6189 | 34.8738 | 36.1494 | 34.992 | 34.4558 | 34.673 | 35.7391 | 34.9661 | 34.911 | 37.6892 | 36.6726 | 34.6585 | 34.9034 | 36.672 | 37.2876 | 37.9602 | 36.6734 | 34.9598 | 34.4425 | 35.896 | 36.3382 | 34.3605 | 34.5423 | 34.4623 | 34.4581 | 34.4158 | 33.8931 | 33.5462 | 34.2843 | 34.4265 | 35.1417 | 36.2634 | 35.2347 | 35.4127 | 35.129 | 93.4024 | 93.6383 | 93.3024
2022-09-07 23:43 | 1:53 | 17.9461 | 18.0969 | 19.9468 | 35.3935 | 33.7007 | 35.5829 | 35.8873 | 36.1932 | 37.0005 | 37.1685 | 36.5557 | 37.2547 | 34.2741 | 33.5771 | 35.9792 | 36.0515 | 37.1076 | 37.178 | 37.5325 | 37.6698 | 23.6852 | 18.5819 | 92.4469 | 33.6417 | 34.879 | 36.12 | 34.9767 | 34.437 | 34.6572 | 35.7518 | 34.9526 | 34.9113 | 37.6902 | 36.6667 | 34.6358 | 34.9008 | 36.6919 | 37.2915 | 37.9751 | 36.6707 | 34.9645 | 34.4402 | 35.8773 | 36.3138 | 34.3524 | 34.5566 | 34.4505 | 34.4591 | 34.4145 | 33.9093 | 33.5491 | 34.2858 | 34.4158 | 35.1727 | 36.2813 | 35.2505 | 35.4238 | 35.1011 | 93.2956 | 93.5791 | 93.1475
2022-09-07 23:43 | 1:53 | 17.8841 | 18.0409 | 19.9428 | 35.5176 | 33.6954 | 35.5832 | 35.8909 | 36.1949 | 37.0022 | 37.169 | 36.5592 | 37.2437 | 34.2615 | 33.5732 | 35.9754 | 36.0645 | 37.1145 | 37.1503 | 37.5094 | 37.6683 | 23.6503 | 18.5705 | 92.5553 | 33.5273 | 34.8694 | 36.1183 | 34.9734 | 34.4532 | 34.6547 | 35.7462 | 34.9508 | 34.9294 | 37.6766 | 36.6681 | 34.6465 | 34.8935 | 36.6726 | 37.2895 | 37.9629 | 36.6934 | 34.9358 | 34.4287 | 35.8878 | 36.304 | 34.3248 | 34.5833 | 34.4601 | 34.4413 | 34.4145 | 33.9081 | 33.5361 | 34.2901 | 34.4145 | 35.1527 | 36.2653 | 35.2288 | 35.4327 | 35.1085 | 93.2029 | 93.4237 | 93.1156
2022-09-07 23:43 | 1:53 | 17.8833 | 18.0424 | 19.897 | 35.4001 | 33.6947 | 35.5884 | 35.8888 | 36.1839 | 36.9883 | 37.1577 | 36.5565 | 37.2621 | 34.2488 | 33.568 | 35.9743 | 36.0598 | 37.1145 | 37.1634 | 37.5015 | 37.6667 | 23.6369 | 18.5561 | 92.6383 | 33.571 | 34.8556 | 36.1337 | 34.9698 | 34.4435 | 34.6607 | 35.7572 | 34.9368 | 34.9197 | 37.6754 | 36.6769 | 34.6552 | 34.9075 | 36.6667 | 37.2747 | 37.9637 | 36.672 | 34.9474 | 34.439 | 35.8819 | 36.3018 | 34.3367 | 34.5597 | 34.4486 | 34.4588 | 34.4227 | 33.8983 | 33.52 | 34.2802 | 34.4145 | 35.1551 | 36.2689 | 35.2298 | 35.396 | 35.0934 | 93.0775 | 93.3192 | 93.0276
2022-09-07 23:44 | 1:53 | 17.9407 | 18.1004 | 19.9305 | 35.3981 | 33.6946 | 35.5677 | 35.8818 | 36.1969 | 36.9938 | 37.1568 | 36.5486 | 37.2597 | 34.2563 | 33.5589 | 35.9862 | 36.0578 | 37.121 | 37.1587 | 37.5129 | 37.6853 | 23.6075 | 18.5831 | 92.767 | 33.7312 | 34.8625 | 36.1416 | 34.9598 | 34.4499 | 34.6585 | 35.7653 | 34.9347 | 34.9014 | 37.673 | 36.6759 | 34.6415 | 34.9098 | 36.6681 | 37.3036 | 37.9648 | 36.6919 | 34.9514 | 34.4221 | 35.8902 | 36.2968 | 34.3309 | 34.5408 | 34.4761 | 34.431 | 34.4188 | 33.8888 | 33.5256 | 34.2865 | 34.4227 | 35.1443 | 36.2612 | 35.2176 | 35.4157 | 35.1042 | 92.9891 | 93.1928 | 92.9156
2022-09-07 23:44 | 1:54 | 17.9409 | 18.0729 | 19.952 | 35.4017 | 33.6923 | 35.5674 | 35.8833 | 36.1782 | 37.0026 | 37.1414 | 36.5662 | 37.2413 | 34.2504 | 33.5412 | 35.9977 | 36.0419 | 37.1232 | 37.1683 | 37.5064 | 37.6753 | 23.6243 | 18.5961 | 92.7669 | 33.5157 | 34.859 | 36.1205 | 34.9645 | 34.4439 | 34.6358 | 35.7481 | 34.9216 | 34.9054 | 37.6811 | 36.6672 | 34.6497 | 34.8975 | 36.6769 | 37.2688 | 37.9641 | 36.6726 | 34.9592 | 34.4395 | 35.8682 | 36.298 | 34.3175 | 34.5539 | 34.4657 | 34.4291 | 34.3866 | 33.8781 | 33.5399 | 34.2693 | 34.4188 | 35.1535 | 36.2643 | 35.2186 | 35.4114 | 35.1052 | 92.8511 | 93.1052 | 92.8051
2022-09-07 23:44 | 1:54 | 17.9191 | 18.0659 | 19.9503 | 35.3891 | 33.692 | 35.5704 | 35.8805 | 36.1798 | 37.0045 | 37.1752 | 36.5478 | 37.2843 | 34.2377 | 33.5356 | 35.9774 | 36.0552 | 37.1134 | 37.1624 | 37.5126 | 37.6637 | 23.6126 | 18.6016 | 92.916 | 33.5599 | 34.8629 | 36.1234 | 34.9358 | 34.4271 | 34.6465 | 35.7583 | 34.9403 | 34.9185 | 37.6799 | 36.6617 | 34.6473 | 34.8937 | 36.6759 | 37.2867 | 37.9638 | 36.6667 | 34.9306 | 34.4199 | 35.8659 | 36.2951 | 34.308 | 34.5292 | 34.469 | 34.4222 | 34.4416 | 33.8799 | 33.5222 | 34.2698 | 34.3866 | 35.1384 | 36.2432 | 35.2426 | 35.416 | 35.1009 | 92.7434 | 92.9807 | 92.6954
2022-09-07 23:44 | 1:54 | 17.8984 | 18.0658 | 19.9084 | 35.4417 | 33.6693 | 35.5775 | 35.8842 | 36.1633 | 36.9916 | 37.1733 | 36.5644 | 37.2579 | 34.2276 | 33.5334 | 35.9771 | 36.0565 | 37.0894 | 37.154 | 37.5204 | 37.6727 | 23.5801 | 18.5829 | 92.9931 | 33.4513 | 34.8759 | 36.0973 | 34.9474 | 34.4391 | 34.6552 | 35.7529 | 34.9244 | 34.9084 | 37.675 | 36.6458 | 34.6101 | 34.894 | 36.6672 | 37.2871 | 37.9614 | 36.6681 | 34.9403 | 34.401 | 35.8482 | 36.2888 | 34.3147 | 34.5408 | 34.4839 | 34.4083 | 34.4127 | 33.8909 | 33.526 | 34.2895 | 34.4416 | 35.1479 | 36.2543 | 35.2294 | 35.4374 | 35.0822 | 92.6337 | 92.8667 | 92.6198
2022-09-07 23:44 | 1:54 | 17.9181 | 18.0609 | 19.9131 | 35.4053 | 33.6675 | 35.5642 | 35.8889 | 36.174 | 36.9914 | 37.1801 | 36.5529 | 37.2624 | 34.2382 | 33.524 | 35.9731 | 36.0419 | 37.0943 | 37.1426 | 37.4974 | 37.6927 | 23.5489 | 18.5624 | 93.1162 | 33.5483 | 34.8527 | 36.0949 | 34.9514 | 34.4236 | 34.6415 | 35.7536 | 34.941 | 34.911 | 37.6706 | 36.647 | 34.6468 | 34.8842 | 36.6617 | 37.2892 | 37.9809 | 36.6769 | 34.9306 | 34.4055 | 35.8534 | 36.2994 | 34.3018 | 34.5173 | 34.4885 | 34.4293 | 34.4259 | 33.8886 | 33.5172 | 34.2709 | 34.4127 | 35.153 | 36.2398 | 35.2477 | 35.425 | 35.0876 | 92.5383 | 92.7232 | 92.5442
2022-09-07 23:44 | 1:54 | 17.9348 | 18.0448 | 19.954 | 35.295 | 33.6913 | 35.5568 | 35.8865 | 36.1768 | 36.9962 | 37.1907 | 36.5656 | 37.2683 | 34.2524 | 33.53 | 35.9766 | 36.0503 | 37.0964 | 37.1445 | 37.5067 | 37.6726 | 23.5133 | 18.5979 | 93.2432 | 33.6341 | 34.8461 | 36.0987 | 34.9592 | 34.4208 | 34.6497 | 35.7713 | 34.9148 | 34.9041 | 37.6764 | 36.6596 | 34.6467 | 34.8954 | 36.6458 | 37.2683 | 37.9579 | 36.6759 | 34.9407 | 34.3904 | 35.8344 | 36.2618 | 34.3008 | 34.5357 | 34.4627 | 34.4121 | 34.4147 | 33.8606 | 33.5165 | 34.2572 | 34.4259 | 35.1321 | 36.2497 | 35.2254 | 35.4234 | 35.0953 | 92.3488 | 92.5613 | 92.4145
2022-09-07 23:45 | 1:55 | 17.9056 | 18.0525 | 19.9793 | 35.4327 | 33.6717 | 35.5591 | 35.8909 | 36.1746 | 36.9806 | 37.1728 | 36.5693 | 37.2645 | 34.2278 | 33.4998 | 35.9766 | 36.0298 | 37.1059 | 37.1469 | 37.5112 | 37.6874 | 23.5038 | 18.5743 | 93.3512 | 33.5816 | 34.8501 | 36.1054 | 34.9306 | 34.4299 | 34.6473 | 35.7768 | 34.9245 | 34.9052 | 37.6818 | 36.653 | 34.6369 | 34.9036 | 36.647 | 37.2766 | 37.968 | 36.6672 | 34.9415 | 34.3877 | 35.8495 | 36.2732 | 34.2831 | 34.5425 | 34.4792 | 34.3993 | 34.406 | 33.8721 | 33.5139 | 34.2761 | 34.4147 | 35.162 | 36.261 | 35.2523 | 35.4292 | 35.1022 | 92.2306 | 92.4099 | 92.325
2022-09-07 23:45 | 1:55 | 17.8694 | 18.0668 | 19.9285 | 35.3952 | 33.6795 | 35.5475 | 35.895 | 36.1815 | 37.0076 | 37.1752 | 36.5642 | 37.2682 | 34.2204 | 33.5104 | 35.9803 | 36.0466 | 37.0798 | 37.1253 | 37.5064 | 37.6783 | 23.4749 | 18.5761 | 93.2251 | 33.6712 | 34.8498 | 36.0879 | 34.9403 | 34.4359 | 34.6101 | 35.7671 | 34.9394 | 34.9081 | 37.6786 | 36.6465 | 34.6539 | 34.8983 | 36.6596 | 37.2711 | 37.9539 | 36.6617 | 34.9103 | 34.3853 | 35.8472 | 36.2621 | 34.2862 | 34.5249 | 34.484 | 34.383 | 34.4066 | 33.8617 | 33.5239 | 34.2769 | 34.406 | 35.1544 | 36.2402 | 35.2426 | 35.4219 | 35.0828 | 92.09 | 92.2629 | 92.1651
2022-09-07 23:45 | 1:55 | 17.9571 | 18.0637 | 19.9128 | 35.3715 | 33.6658 | 35.5312 | 35.8892 | 36.1876 | 37 | 37.1835 | 36.5671 | 37.2644 | 34.2288 | 33.4997 | 35.9682 | 36.0307 | 37.0869 | 37.1437 | 37.5256 | 37.6845 | 23.4682 | 18.593 | 93.4213 | 33.5775 | 34.8577 | 36.0941 | 34.9306 | 34.4427 | 34.6468 | 35.7568 | 34.9367 | 34.9034 | 37.6614 | 36.654 | 34.6442 | 34.8857 | 36.653 | 37.2636 | 37.9629 | 36.6458 | 34.9288 | 34.373 | 35.8347 | 36.276 | 34.2656 | 34.5307 | 34.4718 | 34.4175 | 34.4136 | 33.8634 | 33.5264 | 34.2764 | 34.4066 | 35.1633 | 36.2629 | 35.2421 | 35.4228 | 35.0626 | 91.9889 | 92.1864 | 92.104
2022-09-07 23:45 | 1:55 | 17.8972 | 18.0622 | 19.9136 | 35.4072 | 33.6701 | 35.5353 | 35.8829 | 36.179 | 36.9969 | 37.1896 | 36.5595 | 37.2689 | 34.2157 | 33.4945 | 35.9763 | 36.0246 | 37.1007 | 37.1499 | 37.5065 | 37.6632 | 23.4484 | 18.572 | 93.4864 | 33.5663 | 34.8459 | 36.1087 | 34.9407 | 34.4139 | 34.6467 | 35.7817 | 34.9297 | 34.9141 | 37.6811 | 36.6543 | 34.6232 | 34.8927 | 36.6465 | 37.2638 | 37.9717 | 36.647 | 34.9065 | 34.3911 | 35.8473 | 36.252 | 34.2569 | 34.5005 | 34.4673 | 34.3929 | 34.3965 | 33.8535 | 33.4935 | 34.2716 | 34.4136 | 35.1516 | 36.2287 | 35.2557 | 35.4217 | 35.0646 | 91.9703 | 92.1629 | 92.0837
2022-09-07 23:45 | 1:55 | 17.893 | 18.0627 | 19.9356 | 35.3574 | 33.6465 | 35.5184 | 35.8901 | 36.186 | 36.9876 | 37.1972 | 36.5586 | 37.2678 | 34.2299 | 33.4857 | 35.9608 | 36.0201 | 37.0844 | 37.1523 | 37.5193 | 37.6755 | 23.4358 | 18.5728 | 93.5412 | 33.5349 | 34.8438 | 36.0809 | 34.9415 | 34.4126 | 34.6369 | 35.7683 | 34.913 | 34.9102 | 37.687 | 36.6514 | 34.6234 | 34.8913 | 36.654 | 37.2623 | 37.9439 | 36.6596 | 34.9123 | 34.3643 | 35.8364 | 36.2777 | 34.2614 | 34.5194 | 34.5022 | 34.3894 | 34.4198 | 33.8602 | 33.5174 | 34.2669 | 34.3965 | 35.1427 | 36.2558 | 35.2476 | 35.434 | 35.0727 | 92.0098 | 92.2057 | 92.1964
2022-09-07 23:45 | 1:55 | 17.913 | 18.0777 | 19.9499 | 35.2945 | 33.65 | 35.5207 | 35.8965 | 36.1839 | 36.9937 | 37.192 | 36.5777 | 37.2945 | 34.2092 | 33.4674 | 35.9364 | 36.0357 | 37.0731 | 37.1492 | 37.5087 | 37.6859 | 23.4221 | 18.5406 | 93.6772 | 33.64 | 34.8544 | 36.0781 | 34.9103 | 34.4144 | 34.6539 | 35.7564 | 34.9327 | 34.8984 | 37.6745 | 36.6419 | 34.6276 | 34.8856 | 36.6543 | 37.2834 | 37.9571 | 36.653 | 34.9093 | 34.3649 | 35.8101 | 36.2421 | 34.2758 | 34.5104 | 34.4804 | 34.3781 | 34.4169 | 33.8591 | 33.5116 | 34.2587 | 34.4198 | 35.163 | 36.2253 | 35.2566 | 35.4257 | 35.0469 | 92.0874 | 92.318 | 92.3001
2022-09-07 23:46 | 1:55 | 17.8931 | 18.0315 | 19.8986 | 35.3822 | 33.6585 | 35.5285 | 35.8802 | 36.1775 | 36.9891 | 37.2048 | 36.5726 | 37.2738 | 34.214 | 33.4738 | 35.96 | 36.025 | 37.0778 | 37.1321 | 37.5069 | 37.6786 | 23.4068 | 18.5519 | 93.6759 | 33.5737 | 34.8343 | 36.0572 | 34.9288 | 34.4133 | 34.6442 | 35.7815 | 34.9087 | 34.9045 | 37.6721 | 36.6215 | 34.6327 | 34.882 | 36.6514 | 37.2623 | 37.9623 | 36.6465 | 34.9031 | 34.3745 | 35.825 | 36.2552 | 34.2594 | 34.4991 | 34.4997 | 34.3892 | 34.4241 | 33.8713 | 33.4983 | 34.2774 | 34.4169 | 35.1645 | 36.2476 | 35.243 | 35.4577 | 35.0574 | 92.1672 | 92.3961 | 92.3591
2022-09-07 23:46 | 1:56 | 17.883 | 18.0438 | 19.8918 | 35.3185 | 33.6472 | 35.5223 | 35.8917 | 36.177 | 36.9824 | 37.1999 | 36.5581 | 37.2749 | 34.1909 | 33.4736 | 35.956 | 36.038 | 37.0606 | 37.1365 | 37.5016 | 37.6646 | 23.4057 | 18.5354 | 93.8129 | 33.4982 | 34.8237 | 36.0797 | 34.9065 | 34.4191 | 34.6232 | 35.7624 | 34.9203 | 34.9126 | 37.6674 | 36.6441 | 34.6417 | 34.8863 | 36.6419 | 37.2611 | 37.9373 | 36.654 | 34.8977 | 34.3496 | 35.8104 | 36.257 | 34.2598 | 34.4986 | 34.4834 | 34.3685 | 34.4261 | 33.8583 | 33.5067 | 34.273 | 34.4241 | 35.1696 | 36.2498 | 35.2335 | 35.4291 | 35.0408 | 92.2496 | 92.4852 | 92.413
2022-09-07 23:46 | 1:56 | 17.8186 | 18.0178 | 19.893 | 35.4185 | 33.6391 | 35.5259 | 35.9031 | 36.1664 | 36.9727 | 37.2053 | 36.5505 | 37.2753 | 34.2023 | 33.4531 | 35.9525 | 36.0245 | 37.0672 | 37.136 | 37.5223 | 37.6705 | 23.3681 | 18.5049 | 93.9805 | 33.6529 | 34.8248 | 36.0715 | 34.9123 | 34.3996 | 34.6234 | 35.7659 | 34.9248 | 34.8858 | 37.6574 | 36.6412 | 34.6103 | 34.887 | 36.6215 | 37.2689 | 37.9693 | 36.6543 | 34.9006 | 34.3436 | 35.8148 | 36.2536 | 34.2367 | 34.5005 | 34.5132 | 34.3801 | 34.409 | 33.8567 | 33.4946 | 34.2751 | 34.4261 | 35.1517 | 36.2319 | 35.2572 | 35.4313 | 35.05 | 92.4007 | 92.5243 | 92.5866
2022-09-07 23:46 | 1:56 | 17.9036 | 18.0413 | 19.8828 | 35.4438 | 33.6505 | 35.5254 | 35.8881 | 36.183 | 36.9709 | 37.2089 | 36.57 | 37.2889 | 34.1823 | 33.4609 | 35.955 | 36.0388 | 37.0413 | 37.1364 | 37.5245 | 37.669 | 23.3575 | 18.5478 | 94.0124 | 33.5112 | 34.8124 | 36.0927 | 34.9093 | 34.4122 | 34.6276 | 35.7674 | 34.9254 | 34.8965 | 37.664 | 36.6327 | 34.6127 | 34.8892 | 36.6441 | 37.2534 | 37.9507 | 36.6514 | 34.9126 | 34.3589 | 35.7846 | 36.2383 | 34.2469 | 34.4877 | 34.4918 | 34.3915 | 34.4133 | 33.8539 | 33.4903 | 34.2484 | 34.409 | 35.166 | 36.2408 | 35.2487 | 35.433 | 35.0377 | 92.4369 | 92.5491 | 92.6306
2022-09-07 23:46 | 1:56 | 17.9287 | 18.1011 | 19.929 | 35.3908 | 33.6206 | 35.5057 | 35.9039 | 36.1769 | 36.9757 | 37.2077 | 36.552 | 37.2813 | 34.1983 | 33.4466 | 35.9323 | 36.0337 | 37.0452 | 37.129 | 37.5039 | 37.6605 | 23.3711 | 18.5617 | 94.0996 | 33.5324 | 34.8137 | 36.0717 | 34.9031 | 34.4002 | 34.6327 | 35.76 | 34.9309 | 34.9061 | 37.6775 | 36.6389 | 34.6053 | 34.8874 | 36.6412 | 37.2544 | 37.9449 | 36.6419 | 34.9125 | 34.322 | 35.8075 | 36.2223 | 34.2207 | 34.4942 | 34.5001 | 34.3709 | 34.4082 | 33.8481 | 33.484 | 34.2449 | 34.4133 | 35.1747 | 36.2237 | 35.2644 | 35.4353 | 35.0394 | 92.4751 | 92.5757 | 92.6436
2022-09-07 23:46 | 1:56 | 17.9152 | 18.1077 | 19.8904 | 35.4631 | 33.6295 | 35.5149 | 35.8974 | 36.1783 | 36.9928 | 37.1953 | 36.5676 | 37.2827 | 34.1849 | 33.4667 | 35.9227 | 36.031 | 37.0559 | 37.1243 | 37.4844 | 37.6599 | 23.3787 | 18.5557 | 94.1105 | 33.4967 | 34.8048 | 36.0632 | 34.8977 | 34.4038 | 34.6417 | 35.7594 | 34.9334 | 34.9061 | 37.6691 | 36.6279 | 34.6261 | 34.8786 | 36.6327 | 37.2359 | 37.9376 | 36.6215 | 34.906 | 34.3541 | 35.8041 | 36.2028 | 34.2243 | 34.4987 | 34.4813 | 34.3548 | 34.4096 | 33.8451 | 33.4792 | 34.256 | 34.4082 | 35.1492 | 36.2071 | 35.2445 | 35.4355 | 35.035 | 92.5585 | 92.6653 | 92.7206
2022-09-07 23:47 | 1:57 | 17.9041 | 18.0427 | 19.8778 | 35.3586 | 33.6222 | 35.5066 | 35.8957 | 36.1539 | 36.9713 | 37.193 | 36.5552 | 37.2807 | 34.1713 | 33.4613 | 35.9059 | 36.0094 | 37.0569 | 37.1309 | 37.5039 | 37.6417 | 23.3638 | 18.5454 | 94.002 | 33.5155 | 34.8062 | 36.0616 | 34.9006 | 34.4164 | 34.6103 | 35.7491 | 34.9111 | 34.8982 | 37.6474 | 36.6395 | 34.6322 | 34.8783 | 36.6389 | 37.2469 | 37.9326 | 36.6441 | 34.8963 | 34.3298 | 35.7923 | 36.2228 | 34.2171 | 34.4771 | 34.5003 | 34.3594 | 34.4053 | 33.8698 | 33.4794 | 34.2435 | 34.4096 | 35.1551 | 36.2146 | 35.2554 | 35.4226 | 35.0269 | 92.6488 | 92.7339 | 92.7956
2022-09-07 23:47 | 1:57 | 17.8485 | 18.0182 | 19.8518 | 35.3109 | 33.6122 | 35.4947 | 35.8801 | 36.1703 | 36.9784 | 37.1929 | 36.5625 | 37.2857 | 34.1613 | 33.388 | 35.9206 | 36.0228 | 37.0591 | 37.131 | 37.5007 | 37.6636 | 23.3497 | 18.459 | 94.1569 | 33.4957 | 34.8096 | 36.0594 | 34.9126 | 34.412 | 34.6127 | 35.7554 | 34.9166 | 34.8915 | 37.6447 | 36.611 | 34.6101 | 34.8764 | 36.6279 | 37.2533 | 37.923 | 36.6412 | 34.8925 | 34.3119 | 35.7851 | 36.2038 | 34.2223 | 34.4866 | 34.5073 | 34.3454 | 34.4288 | 33.8362 | 33.4902 | 34.2476 | 34.4053 | 35.1477 | 36.2341 | 35.2627 | 35.4273 | 34.9912 | 92.7684 | 92.819 | 92.8349
2022-09-07 23:47 | 1:57 | 17.7699 | 17.9111 | 19.8219 | 35.3059 | 33.6107 | 35.4948 | 35.8758 | 36.1628 | 36.9701 | 37.2006 | 36.559 | 37.2801 | 34.1638 | 33.4079 | 35.897 | 36.0156 | 37.0445 | 37.1262 | 37.4897 | 37.6505 | 23.3554 | 18.394 | 94.0621 | 33.5247 | 34.8045 | 36.0508 | 34.9125 | 34.4084 | 34.6053 | 35.7511 | 34.9023 | 34.8917 | 37.6617 | 36.6323 | 34.6246 | 34.8652 | 36.6395 | 37.2419 | 37.9312 | 36.6327 | 34.8903 | 34.3262 | 35.7823 | 36.1941 | 34.214 | 34.4769 | 34.4845 | 34.3624 | 34.4007 | 33.833 | 33.4795 | 34.2383 | 34.4288 | 35.1586 | 36.2195 | 35.2464 | 35.4254 | 35.0126 | 92.754 | 92.9119 | 92.7969
2022-09-07 23:47 | 1:57 | 17.7747 | 17.9611 | 19.7982 | 35.3278 | 33.6112 | 35.4875 | 35.8783 | 36.1554 | 36.9666 | 37.1795 | 36.5867 | 37.2809 | 34.177 | 34.4908 | 35.9069 | 36.0228 | 37.0339 | 37.1063 | 37.4901 | 37.6387 | 23.3362 | 18.3938 | 93.9 | 33.3436 | 34.7859 | 36.0362 | 34.906 | 34.3982 | 34.6261 | 35.7439 | 34.9146 | 34.8749 | 37.655 | 36.6465 | 34.608 | 34.8652 | 36.611 | 37.2481 | 37.9378 | 36.6389 | 34.8873 | 34.3078 | 35.7598 | 36.1846 | 34.2004 | 34.4737 | 34.524 | 34.3303 | 34.4162 | 33.8309 | 33.4772 | 34.2298 | 34.4007 | 35.1328 | 36.2083 | 35.25 | 35.4389 | 34.9932 | 92.9127 | 93.0447 | 92.932
2022-09-07 23:47 | 1:57 | 17.8261 | 18.0017 | 19.8087 | 35.3024 | 33.607 | 35.5101 | 35.8977 | 36.1692 | 36.9633 | 37.1836 | 36.5706 | 37.2898 | 34.1567 | 34.4978 | 35.9037 | 36.019 | 37.023 | 37.103 | 37.4795 | 37.6352 | 23.3614 | 18.4044 | 93.815 | 33.499 | 34.8125 | 36.0596 | 34.8963 | 34.4116 | 34.6322 | 35.7402 | 34.9136 | 34.8835 | 37.6506 | 36.6214 | 34.6036 | 34.8723 | 36.6323 | 37.2421 | 37.9406 | 36.6279 | 34.8863 | 34.2943 | 35.7453 | 36.1958 | 34.1928 | 34.4859 | 34.5103 | 34.3357 | 34.4172 | 33.8359 | 33.4573 | 34.2302 | 34.4162 | 35.1374 | 36.223 | 35.2546 | 35.4134 | 34.9994 | 93.0716 | 93.1432 | 93.1025
2022-09-07 23:47 | 1:57 | 17.8959 | 18.0211 | 19.8467 | 35.2712 | 33.5964 | 35.4636 | 35.8976 | 36.1591 | 36.9712 | 37.1985 | 36.5631 | 37.2948 | 34.154 | 34.4957 | 35.8971 | 35.9941 | 37.0174 | 37.1235 | 37.4868 | 37.6332 | 23.3886 | 18.4878 | 93.7447 | 33.4597 | 34.7931 | 36.0578 | 34.8925 | 34.3942 | 34.6101 | 35.7515 | 34.9143 | 34.8796 | 37.6539 | 36.6161 | 34.5942 | 34.8703 | 36.6465 | 37.2345 | 37.919 | 36.6395 | 34.878 | 34.3023 | 35.7483 | 36.1737 | 34.187 | 34.4734 | 34.5049 | 34.3207 | 34.4061 | 33.8281 | 33.4779 | 34.2264 | 34.4172 | 35.142 | 36.2202 | 35.2375 | 35.4252 | 34.9704 | 93.2174 | 93.2832 | 93.1287
2022-09-07 23:48 | 1:57 | 17.8377 | 18.0131 | 19.8447 | 35.3278 | 33.5872 | 35.4895 | 35.888 | 36.1652 | 36.9873 | 37.1934 | 36.5655 | 37.2872 | 34.1501 | 34.4833 | 35.8812 | 36.0147 | 37.0026 | 37.1136 | 37.4929 | 37.6279 | 23.3857 | 18.4318 | 93.7328 | 33.4231 | 34.784 | 36.045 | 34.8903 | 34.4127 | 34.6246 | 35.759 | 34.9018 | 34.8638 | 37.6604 | 36.6272 | 34.5996 | 34.8653 | 36.6214 | 37.2393 | 37.913 | 36.611 | 34.8732 | 34.2891 | 35.7469 | 36.1729 | 34.179 | 34.4576 | 34.4975 | 34.3027 | 34.4011 | 33.848 | 33.4585 | 34.2231 | 34.4061 | 35.1379 | 36.2261 | 35.2586 | 35.4463 | 34.9756 | 93.3696 | 93.4372 | 93.2315
2022-09-07 23:48 | 1:58 | 17.8459 | 17.9843 | 19.8338 | 35.3409 | 33.5781 | 35.4757 | 35.8979 | 36.16 | 36.9679 | 37.2022 | 36.5836 | 37.2865 | 34.1601 | 34.4959 | 35.8868 | 36.0013 | 37.0402 | 37.1105 | 37.4946 | 37.6245 | 23.4164 | 18.443 | 93.6837 | 33.3589 | 34.7805 | 36.0374 | 34.8873 | 34.3996 | 34.608 | 35.7385 | 34.9075 | 34.8921 | 37.6551 | 36.6302 | 34.588 | 34.8686 | 36.6161 | 37.223 | 37.9101 | 36.6323 | 34.8667 | 34.2902 | 35.7338 | 36.1659 | 34.1852 | 34.4557 | 34.4876 | 34.2944 | 34.4159 | 33.8175 | 33.457 | 34.1962 | 34.4011 | 35.1508 | 36.2132 | 35.2471 | 35.4282 | 34.9718 | 93.554 | 93.5915 | 93.3279
2022-09-07 23:48 | 1:58 | 17.8038 | 18.0318 | 19.8541 | 35.2964 | 33.5613 | 35.4627 | 35.8904 | 36.1518 | 36.9597 | 37.1862 | 36.5682 | 37.2806 | 34.1413 | 34.4665 | 35.8869 | 36.0192 | 37.0165 | 37.1074 | 37.4853 | 37.6232 | 23.4076 | 18.4153 | 93.6915 | 33.4641 | 34.7858 | 36.0476 | 34.8863 | 34.4012 | 34.6036 | 35.7318 | 34.9208 | 34.9034 | 37.6454 | 36.6356 | 34.6011 | 34.8909 | 36.6272 | 37.2142 | 37.9151 | 36.6465 | 34.877 | 34.2831 | 35.7238 | 36.1693 | 34.1765 | 34.4537 | 34.5055 | 34.3338 | 34.418 | 33.8416 | 33.4597 | 34.2122 | 34.4159 | 35.1345 | 36.2195 | 35.2636 | 35.4504 | 34.9863 | 93.6717 | 93.7259 | 93.4366
2022-09-07 23:48 | 1:58 | 17.7976 | 17.9533 | 19.8041 | 35.2278 | 33.5799 | 35.4571 | 35.8796 | 36.1546 | 36.9446 | 37.1917 | 36.5789 | 37.2965 | 34.1305 | 34.4603 | 35.8978 | 36.018 | 37.017 | 37.1098 | 37.4747 | 37.6197 | 23.3937 | 18.3956 | 93.5043 | 33.4771 | 34.7812 | 36.049 | 34.878 | 34.3851 | 34.5942 | 35.7373 | 34.9305 | 34.8779 | 37.6508 | 36.6221 | 34.6042 | 34.8766 | 36.6302 | 37.2228 | 37.9123 | 36.6214 | 34.868 | 34.2817 | 35.7421 | 36.1511 | 34.1671 | 34.428 | 34.5152 | 34.2839 | 34.4385 | 33.8343 | 33.447 | 34.1916 | 34.418 | 35.1228 | 36.2375 | 35.2368 | 35.4285 | 34.9629 | 93.8166 | 93.926 | 93.5956
2022-09-07 23:48 | 1:58 | 17.7284 | 17.943 | 19.7888 | 35.3757 | 33.5826 | 35.481 | 35.8869 | 36.1502 | 36.9599 | 37.1956 | 36.5832 | 37.2812 | 34.1392 | 34.4801 | 35.8945 | 36.01 | 37.027 | 37.1085 | 37.4892 | 37.6115 | 23.3887 | 18.3372 | 93.4796 | 33.428 | 34.7595 | 36.0339 | 34.8732 | 34.3865 | 34.5996 | 35.7381 | 34.9225 | 34.8906 | 37.6613 | 36.6317 | 34.5899 | 34.8717 | 36.6356 | 37.2202 | 37.8925 | 36.6161 | 34.8948 | 34.2624 | 35.7236 | 36.1405 | 34.1739 | 34.4265 | 34.511 | 34.2974 | 34.423 | 33.8374 | 33.4558 | 34.2204 | 34.4385 | 35.1294 | 36.2058 | 35.2624 | 35.4128 | 34.9311 | 93.9953 | 94.1089 | 93.5853
2022-09-07 23:48 | 1:58 | 17.7819 | 17.9244 | 19.7945 | 35.3909 | 33.5635 | 35.4689 | 35.8859 | 36.1503 | 36.94 | 37.1928 | 36.5886 | 37.2991 | 34.1217 | 34.4601 | 35.8683 | 36.0181 | 37.0093 | 37.1153 | 37.477 | 37.6276 | 23.3717 | 18.3965 | 93.3682 | 33.4783 | 34.7512 | 36.0309 | 34.8667 | 34.3794 | 34.588 | 35.7365 | 34.9476 | 34.8853 | 37.6469 | 36.6321 | 34.6011 | 34.8704 | 36.6221 | 37.2113 | 37.9137 | 36.6272 | 34.8796 | 34.2532 | 35.7298 | 36.1432 | 34.1769 | 34.4303 | 34.4948 | 34.2953 | 34.4348 | 33.8294 | 33.45 | 34.2254 | 34.423 | 35.1248 | 36.205 | 35.2608 | 35.4206 | 34.9528 | 94.2272 | 94.1958 | 93.747
2022-09-07 23:49 | 1:59 | 17.8177 | 17.9869 | 19.7859 | 35.277 | 33.5677 | 35.4721 | 35.8899 | 36.1613 | 36.9612 | 37.1879 | 36.5917 | 37.3025 | 34.1327 | 34.469 | 35.8686 | 36.0279 | 37.0047 | 37.1143 | 37.4605 | 37.612 | 23.368 | 18.4091 | 93.3698 | 33.4809 | 34.7605 | 36.0294 | 34.877 | 34.379 | 34.6011 | 35.7423 | 34.9357 | 34.8813 | 37.6431 | 36.6333 | 34.5881 | 34.8608 | 36.6317 | 37.2234 | 37.9037 | 36.6302 | 34.8648 | 34.2575 | 35.7252 | 36.1264 | 34.174 | 34.433 | 34.5159 | 34.3021 | 34.426 | 33.8399 | 33.4442 | 34.2281 | 34.4348 | 35.1409 | 36.1964 | 35.2521 | 35.438 | 34.9603 | 94.3733 | 94.4168 | 93.9113
2022-09-07 23:49 | 1:59 | 17.8243 | 17.9711 | 19.8075 | 35.3129 | 33.5745 | 35.475 | 35.8915 | 36.1702 | 36.9731 | 37.2021 | 36.5966 | 37.302 | 34.1261 | 34.4537 | 35.8652 | 36.018 | 37.0159 | 37.1024 | 37.4732 | 37.6214 | 23.3567 | 18.3781 | 93.3293 | 33.3939 | 34.7627 | 36.0379 | 34.868 | 34.386 | 34.6042 | 35.7462 | 34.9338 | 34.8893 | 37.659 | 36.6299 | 34.5781 | 34.8766 | 36.6321 | 37.2281 | 37.9004 | 36.6356 | 34.8634 | 34.2582 | 35.7223 | 36.1429 | 34.1578 | 34.4242 | 34.5105 | 34.2907 | 34.422 | 33.8408 | 33.4704 | 34.2082 | 34.426 | 35.1326 | 36.2223 | 35.2657 | 35.4197 | 34.9303 | 94.5508 | 94.5736 | 93.8972
2022-09-07 23:49 | 1:59 | 17.7438 | 17.9192 | 19.7839 | 35.3177 | 33.5371 | 35.4624 | 35.8975 | 36.1561 | 36.9441 | 37.1806 | 36.5854 | 37.3167 | 34.125 | 34.4765 | 35.8606 | 35.9968 | 36.9909 | 37.0987 | 37.489 | 37.6136 | 23.371 | 18.3495 | 93.264 | 33.375 | 34.7534 | 36.0273 | 34.8948 | 34.3888 | 34.5899 | 35.7325 | 34.9417 | 34.9002 | 37.6433 | 36.6452 | 34.5863 | 34.8816 | 36.6333 | 37.2335 | 37.8997 | 36.6221 | 34.8693 | 34.2618 | 35.7225 | 36.1369 | 34.1513 | 34.4164 | 34.5205 | 34.287 | 34.4314 | 33.8178 | 33.4678 | 34.204 | 34.422 | 35.1448 | 36.202 | 35.2653 | 35.4321 | 34.9515 | 94.6262 | 94.7131 | 93.9073
2022-09-07 23:49 | 1:59 | 17.7425 | 17.8742 | 19.7265 | 35.3944 | 33.5491 | 35.4686 | 35.914 | 36.1709 | 36.9474 | 37.1927 | 36.5979 | 37.3042 | 34.1238 | 34.4607 | 35.8428 | 36.013 | 36.992 | 37.1267 | 37.4631 | 37.6113 | 23.3497 | 18.2869 | 93.2005 | 33.4648 | 34.759 | 36.0311 | 34.8796 | 34.3926 | 34.6011 | 35.7348 | 34.9478 | 34.8921 | 37.6423 | 36.6283 | 34.5846 | 34.8916 | 36.6299 | 37.2329 | 37.8955 | 36.6317 | 34.87 | 34.2471 | 35.7045 | 36.1344 | 34.1385 | 34.407 | 34.524 | 34.2695 | 34.4409 | 33.8024 | 33.4327 | 34.2123 | 34.4314 | 35.1249 | 36.2197 | 35.2646 | 35.4354 | 34.9447 | 94.7638 | 94.8317 | 93.9787
2022-09-07 23:49 | 1:59 | 17.7583 | 17.9186 | 19.7619 | 35.3558 | 33.537 | 35.4939 | 35.8977 | 36.1692 | 36.9573 | 37.1969 | 36.5985 | 37.2888 | 34.1123 | 34.4725 | 35.8626 | 36.0186 | 37.0211 | 37.1082 | 37.4704 | 37.6223 | 23.3471 | 18.3383 | 93.2151 | 33.6265 | 34.7628 | 36.041 | 34.8648 | 34.3864 | 34.5881 | 35.7405 | 34.9405 | 34.8781 | 37.6683 | 36.6471 | 34.588 | 34.884 | 36.6452 | 37.2187 | 37.8997 | 36.6321 | 34.8547 | 34.2218 | 35.7285 | 36.128 | 34.1589 | 34.4045 | 34.5166 | 34.2915 | 34.4174 | 33.8142 | 33.449 | 34.215 | 34.4409 | 35.1255 | 36.2151 | 35.2827 | 35.4453 | 34.954 | 94.8842 | 94.9291 | 94.1048
2022-09-07 23:49 | 1:59 | 17.7584 | 17.9405 | 19.794 | 35.3166 | 33.5529 | 35.4378 | 35.9058 | 36.169 | 36.9597 | 37.2152 | 36.5978 | 37.3077 | 34.1104 | 34.462 | 35.8486 | 36.0115 | 36.9917 | 37.1094 | 37.4676 | 37.6303 | 23.3501 | 18.3378 | 93.1451 | 33.6236 | 34.767 | 36.0336 | 34.8634 | 34.3932 | 34.5781 | 35.7324 | 34.9235 | 34.8847 | 37.6518 | 36.6379 | 34.5727 | 34.8884 | 36.6283 | 37.2347 | 37.9049 | 36.6333 | 34.8549 | 34.2445 | 35.6823 | 36.1531 | 34.1505 | 34.4054 | 34.5186 | 34.2699 | 34.4221 | 33.8241 | 33.4505 | 34.1842 | 34.4174 | 35.1473 | 36.2122 | 35.2733 | 35.4262 | 34.9355 | 95.0065 | 94.98 | 94.2719
2022-09-07 23:50 | 1:59 | 17.8136 | 17.9274 | 19.7601 | 35.3262 | 33.5516 | 35.4664 | 35.8945 | 36.1794 | 36.9485 | 37.2135 | 36.6136 | 37.3145 | 34.1117 | 34.4569 | 35.8718 | 36.0136 | 36.9931 | 37.1066 | 37.46 | 37.6171 | 23.3581 | 18.3401 | 93.0981 | 33.4248 | 34.7401 | 36.0431 | 34.8693 | 34.3723 | 34.5863 | 35.7331 | 34.9389 | 34.9023 | 37.6494 | 36.6262 | 34.5845 | 34.8764 | 36.6471 | 37.2286 | 37.894 | 36.6299 | 34.8661 | 34.2223 | 35.7094 | 36.1276 | 34.1286 | 34.399 | 34.5311 | 34.2762 | 34.4384 | 33.817 | 33.4552 | 34.2144 | 34.4221 | 35.1449 | 36.2082 | 35.2792 | 35.4295 | 34.9346 | 94.9826 | 95.098 | 94.2391
2022-09-07 23:50 | 2:00 | 17.7638 | 17.9035 | 19.7901 | 35.3312 | 33.5399 | 35.4692 | 35.8971 | 36.1645 | 36.9632 | 37.2071 | 36.5898 | 37.2971 | 34.1088 | 34.4577 | 35.8637 | 36.0198 | 36.987 | 37.1068 | 37.4674 | 37.6169 | 23.3574 | 18.3456 | 92.9743 | 33.5062 | 34.7534 | 36.0233 | 34.87 | 34.3986 | 34.5846 | 35.7333 | 34.927 | 34.9084 | 37.6504 | 36.6236 | 34.5878 | 34.8858 | 36.6379 | 37.2478 | 37.9105 | 36.6452 | 34.8582 | 34.2385 | 35.7092 | 36.139 | 34.1343 | 34.4106 | 34.529 | 34.2647 | 34.4187 | 33.8055 | 33.4443 | 34.1899 | 34.4384 | 35.1533 | 36.2069 | 35.2779 | 35.445 | 34.9294 | 95.0548 | 95.2154 | 94.3559
2022-09-07 23:50 | 2:00 | 17.7193 | 17.8884 | 19.7728 | 35.2323 | 33.5363 | 35.4544 | 35.9003 | 36.1802 | 36.955 | 37.2081 | 36.6011 | 37.3349 | 34.1065 | 34.4593 | 35.8563 | 36.001 | 36.988 | 37.1223 | 37.463 | 37.6045 | 23.3341 | 18.2895 | 92.8928 | 33.5645 | 34.746 | 36.0287 | 34.8547 | 34.3987 | 34.588 | 35.7402 | 34.9462 | 34.8826 | 37.6531 | 36.62 | 34.5886 | 34.8847 | 36.6262 | 37.2121 | 37.8939 | 36.6283 | 34.8552 | 34.2306 | 35.7036 | 36.1244 | 34.1294 | 34.3932 | 34.515 | 34.2762 | 34.4511 | 33.8066 | 33.4544 | 34.1978 | 34.4187 | 35.1512 | 36.2074 | 35.2862 | 35.4527 | 34.9301 | 95.0288 | 95.163 | 94.2938
2022-09-07 23:50 | 2:00 | 17.6764 | 17.8463 | 19.7584 | 35.3228 | 33.522 | 35.4604 | 35.9045 | 36.164 | 36.9484 | 37.2225 | 36.6045 | 37.3193 | 34.1061 | 34.4451 | 35.854 | 35.9991 | 37.0082 | 37.119 | 37.4931 | 37.617 | 23.3271 | 18.2567 | 92.8161 | 33.545 | 34.7421 | 36.0236 | 34.8549 | 34.389 | 34.5727 | 35.7459 | 34.9292 | 34.8873 | 37.6573 | 36.6104 | 34.5828 | 34.8729 | 36.6236 | 37.23 | 37.8966 | 36.6471 | 34.8582 | 34.2046 | 35.6978 | 36.1141 | 34.1435 | 34.4041 | 34.5234 | 34.2747 | 34.4283 | 33.7903 | 33.4355 | 34.1989 | 34.4511 | 35.1321 | 36.2022 | 35.2517 | 35.4487 | 34.9273 | 94.8405 | 95.0136 | 94.1362
2022-09-07 23:50 | 2:00 | 17.6336 | 17.8204 | 19.724 | 35.3631 | 33.5356 | 35.4644 | 35.8893 | 36.1623 | 36.977 | 37.2121 | 36.6199 | 37.3331 | 34.1003 | 34.4578 | 35.8427 | 36.0211 | 37.0047 | 37.1106 | 37.4676 | 37.6236 | 23.3031 | 18.207 | 92.8334 | 33.1747 | 34.7512 | 36.0247 | 34.8661 | 34.3704 | 34.5845 | 35.739 | 34.9512 | 34.8952 | 37.653 | 36.6275 | 34.5627 | 34.8864 | 36.62 | 37.225 | 37.8861 | 36.6379 | 34.8636 | 34.2209 | 35.6845 | 36.1141 | 34.1336 | 34.4192 | 34.5235 | 34.2627 | 34.4471 | 33.8141 | 33.4485 | 34.2097 | 34.4283 | 35.1407 | 36.2061 | 35.2615 | 35.455 | 34.9124 | 94.6048 | 94.7756 | 93.9559
2022-09-07 23:50 | 2:00 | 17.627 | 17.7967 | 19.7205 | 35.3238 | 33.5444 | 35.4313 | 35.9316 | 36.1604 | 36.9808 | 37.227 | 36.6334 | 37.3289 | 34.092 | 34.4566 | 35.8393 | 36.0138 | 37.0063 | 37.1231 | 37.4758 | 37.6112 | 23.2932 | 18.1754 | 92.7185 | 33.4311 | 34.7386 | 36.0209 | 34.8582 | 34.3867 | 34.5878 | 35.7409 | 34.9512 | 34.8942 | 37.6621 | 36.6319 | 34.5758 | 34.8883 | 36.6104 | 37.2293 | 37.8899 | 36.6262 | 34.8535 | 34.1999 | 35.7003 | 36.124 | 34.1216 | 34.4095 | 34.5212 | 34.2706 | 34.4458 | 33.7918 | 33.441 | 34.2 | 34.4471 | 35.1503 | 36.2041 | 35.2853 | 35.4518 | 34.9231 | 94.3555 | 94.5294 | 93.7533
2022-09-07 23:51 | 2:00 | 17.621 | 17.7767 | 19.6709 | 35.3755 | 33.517 | 35.4573 | 35.908 | 36.1655 | 36.9888 | 37.2201 | 36.6218 | 37.3349 | 34.0915 | 34.4468 | 35.8385 | 36.0206 | 37.0101 | 37.1104 | 37.468 | 37.6134 | 23.2854 | 18.1527 | 92.6132 | 33.3617 | 34.7454 | 36.0127 | 34.8552 | 34.3614 | 34.5886 | 35.7384 | 34.9483 | 34.899 | 37.6469 | 36.5992 | 34.5879 | 34.8931 | 36.6275 | 37.2299 | 37.9049 | 36.6236 | 34.8517 | 34.2159 | 35.6748 | 36.1286 | 34.1087 | 34.4173 | 34.5264 | 34.2557 | 34.4488 | 33.8008 | 33.4251 | 34.1864 | 34.4458 | 35.1579 | 36.2081 | 35.2898 | 35.4543 | 34.9239 | 94.221 | 94.4169 | 93.7528
2022-09-07 23:51 | 2:01 | 17.566 | 17.731 | 19.6772 | 35.3672 | 33.517 | 35.4341 | 35.9189 | 36.1643 | 36.9724 | 37.2388 | 36.6377 | 37.3291 | 34.0925 | 34.4566 | 35.8437 | 36.0228 | 37.0069 | 37.1181 | 37.4601 | 37.6237 | 23.3117 | 18.1644 | 92.4738 | 33.3999 | 34.7492 | 36.0018 | 34.8582 | 34.3762 | 34.5828 | 35.7394 | 34.9522 | 34.9134 | 37.6537 | 36.6276 | 34.5731 | 34.8882 | 36.6319 | 37.2295 | 37.9121 | 36.62 | 34.8296 | 34.1951 | 35.689 | 36.1143 | 34.1122 | 34.408 | 34.532 | 34.2576 | 34.4568 | 33.7885 | 33.4484 | 34.1937 | 34.4488 | 35.1495 | 36.2105 | 35.2624 | 35.4325 | 34.931 | 94.0563 | 94.2855 | 93.6776
2022-09-07 23:51 | 2:01 | 17.5848 | 17.7245 | 19.6546 | 35.1861 | 33.5243 | 35.4283 | 35.91 | 36.1577 | 36.9772 | 37.2328 | 36.6207 | 37.3572 | 34.1027 | 34.4503 | 35.854 | 36.0285 | 36.9884 | 37.131 | 37.4643 | 37.6037 | 23.2948 | 18.1311 | 92.3988 | 33.417 | 34.7287 | 36.0163 | 34.8636 | 34.3834 | 34.5627 | 35.7311 | 34.9586 | 34.8975 | 37.6615 | 36.6067 | 34.5607 | 34.8912 | 36.5992 | 37.218 | 37.8886 | 36.6104 | 34.837 | 34.2076 | 35.6913 | 36.1165 | 34.097 | 34.411 | 34.5422 | 34.2479 | 34.4473 | 33.8027 | 33.4485 | 34.2041 | 34.4568 | 35.1595 | 36.2082 | 35.29 | 35.4436 | 34.9216 | 93.9418 | 94.1398 | 93.6079
2022-09-07 23:51 | 2:01 | 17.5496 | 17.7166 | 19.6547 | 35.1943 | 33.5221 | 35.4452 | 35.8969 | 36.1588 | 36.9704 | 37.2339 | 36.6348 | 37.3318 | 34.0841 | 34.4472 | 35.8366 | 36.0111 | 37.0064 | 37.1138 | 37.4724 | 37.617 | 23.266 | 18.1492 | 92.3066 | 33.4809 | 34.7319 | 36.016 | 34.8535 | 34.3608 | 34.5758 | 35.7548 | 34.9548 | 34.9023 | 37.6598 | 36.6135 | 34.57 | 34.9149 | 36.6276 | 37.2324 | 37.8869 | 36.6275 | 34.8393 | 34.1991 | 35.6752 | 36.1148 | 34.0896 | 34.3913 | 34.5447 | 34.259 | 34.4623 | 33.7908 | 33.446 | 34.1742 | 34.4473 | 35.1618 | 36.2019 | 35.2837 | 35.464 | 34.9092 | 93.8548 | 94.021 | 93.5826
2022-09-07 23:51 | 2:01 | 17.5285 | 17.6884 | 19.6608 | 35.2928 | 33.5194 | 35.4325 | 35.9058 | 36.1634 | 36.9523 | 37.2488 | 36.6378 | 37.3437 | 34.0833 | 34.4433 | 35.8413 | 36.0347 | 36.9809 | 37.1007 | 37.4727 | 37.5958 | 23.2491 | 18.0787 | 92.2214 | 33.4845 | 34.7413 | 36.024 | 34.8517 | 34.3731 | 34.5879 | 35.7442 | 34.9557 | 34.8965 | 37.6522 | 36.6042 | 34.5662 | 34.8937 | 36.6067 | 37.2331 | 37.8924 | 36.6319 | 34.8427 | 34.1862 | 35.686 | 36.1244 | 34.0896 | 34.3945 | 34.5512 | 34.2512 | 34.4505 | 33.7892 | 34.4908 | 34.1849 | 34.4623 | 35.1666 | 36.2104 | 35.2875 | 35.4365 | 34.9207 | 93.7719 | 93.9228 | 93.5336
2022-09-07 23:51 | 2:01 | 17.5123 | 17.6827 | 19.6431 | 35.4516 | 33.5129 | 35.4355 | 35.9018 | 36.1661 | 36.9684 | 37.2389 | 36.6362 | 37.34 | 34.0841 | 34.4488 | 35.8361 | 36.02 | 36.9684 | 37.1289 | 37.4673 | 37.6168 | 23.2371 | 18.0845 | 92.0613 | 33.4175 | 34.721 | 36.0081 | 34.8296 | 34.3903 | 34.5731 | 35.7443 | 34.9466 | 34.8949 | 37.6523 | 36.6023 | 34.5698 | 34.9055 | 36.6135 | 37.2227 | 37.9035 | 36.5992 | 34.8327 | 34.1935 | 35.6676 | 36.1225 | 34.0794 | 34.3949 | 34.5315 | 34.2535 | 34.4601 | 33.8026 | 34.4978 | 34.1999 | 34.4505 | 35.163 | 36.1965 | 35.26 | 35.456 | 34.9103 | 93.7646 | 93.8893 | 93.5448
2022-09-07 23:52 | 2:02 | 17.5139 | 17.6825 | 19.6287 | 35.2768 | 33.5104 | 35.4342 | 35.9133 | 36.1804 | 36.971 | 37.2506 | 36.6485 | 37.3633 | 34.0832 | 34.4307 | 35.8235 | 36.0173 | 36.9805 | 37.0976 | 37.4746 | 37.6268 | 23.2357 | 18.085 | 92.1037 | 33.356 | 34.7254 | 36.0112 | 34.837 | 34.3553 | 34.5607 | 35.7429 | 34.9546 | 34.9163 | 37.6803 | 36.6058 | 34.5621 | 34.8902 | 36.6042 | 37.2401 | 37.8957 | 36.6276 | 34.8321 | 34.1953 | 35.6598 | 36.1196 | 34.068 | 34.401 | 34.5338 | 34.248 | 34.4486 | 33.7895 | 34.4957 | 34.1889 | 34.4601 | 35.1718 | 36.1786 | 35.2953 | 35.4514 | 34.9285 | 93.7128 | 93.7729 | 93.4905
2022-09-07 23:52 | 2:02 | 17.5132 | 17.6842 | 19.6207 | 35.2488 | 33.5054 | 35.4428 | 35.9096 | 36.1683 | 36.9739 | 37.2465 | 36.6395 | 37.3506 | 34.0715 | 34.4567 | 35.8159 | 36.0164 | 37.0029 | 37.1191 | 37.4759 | 37.6256 | 23.2641 | 18.0937 | 92.1608 | 33.4799 | 34.7272 | 36.0033 | 34.8393 | 34.3814 | 34.57 | 35.7409 | 34.9667 | 34.9073 | 37.6512 | 36.5942 | 34.5758 | 34.8965 | 36.6023 | 37.2118 | 37.8746 | 36.6067 | 34.8272 | 34.1777 | 35.6872 | 36.116 | 34.0638 | 34.3877 | 34.5333 | 34.2193 | 34.4761 | 33.7834 | 34.4833 | 34.2207 | 34.4486 | 35.1623 | 36.1951 | 35.2837 | 35.4419 | 34.9051 | 93.7107 | 93.7352 | 93.4987
2022-09-07 23:52 | 2:02 | 17.5049 | 17.6964 | 19.6275 | 35.3181 | 33.5135 | 35.4139 | 35.8882 | 36.1696 | 36.9592 | 37.2591 | 36.6473 | 37.3543 | 34.0729 | 34.4334 | 35.8241 | 36.0203 | 36.9745 | 37.1191 | 37.4656 | 37.6269 | 23.2144 | 18.1101 | 92.1445 | 33.4851 | 34.7114 | 36.0036 | 34.8427 | 34.3635 | 34.5662 | 35.7303 | 34.9497 | 34.9109 | 37.6807 | 36.6045 | 34.5707 | 34.9054 | 36.6058 | 37.2006 | 37.8812 | 36.6135 | 34.8078 | 34.1763 | 35.6798 | 36.1279 | 34.0596 | 34.3966 | 34.538 | 34.2606 | 34.4657 | 33.7824 | 34.4959 | 34.1857 | 34.4761 | 35.1725 | 36.212 | 35.2954 | 35.4594 | 34.9236 | 93.5602 | 93.6777 | 93.3538
2022-09-07 23:52 | 2:02 | 17.5518 | 17.6718 | 19.6335 | 35.2665 | 33.5173 | 35.4241 | 35.9136 | 36.1657 | 36.9656 | 37.2377 | 36.6404 | 37.349 | 34.0759 | 34.4463 | 35.8233 | 36.0256 | 36.9833 | 37.1202 | 37.4897 | 37.6263 | 23.1937 | 18.1172 | 92.1721 | 33.2412 | 34.7258 | 35.996 | 34.8327 | 34.3776 | 34.5698 | 35.7341 | 34.9453 | 34.897 | 37.6659 | 36.5845 | 34.5922 | 34.8835 | 36.5942 | 37.2225 | 37.8847 | 36.6042 | 34.7982 | 34.183 | 35.6686 | 36.0976 | 34.0463 | 34.3931 | 34.5456 | 34.2325 | 34.469 | 33.8047 | 34.4665 | 34.1937 | 34.4657 | 35.1641 | 36.1838 | 35.292 | 35.4563 | 34.9044 | 93.4958 | 93.6141 | 93.3809
2022-09-07 23:52 | 2:02 | 17.5212 | 17.6725 | 19.6248 | 35.3261 | 33.4882 | 35.4335 | 35.9043 | 36.1625 | 36.9573 | 37.2554 | 36.6347 | 37.3495 | 34.0634 | 34.4521 | 35.8246 | 36.0239 | 36.9584 | 37.1242 | 37.4671 | 37.6159 | 23.197 | 18.0786 | 92.2998 | 33.3003 | 34.7146 | 35.9932 | 34.8321 | 34.3648 | 34.5621 | 35.7464 | 34.9428 | 34.9117 | 37.6535 | 36.5842 | 34.5486 | 34.8769 | 36.6045 | 37.2203 | 37.8907 | 36.6023 | 34.81 | 34.172 | 35.6612 | 36.0941 | 34.0099 | 34.42 | 34.5389 | 34.2419 | 34.4839 | 33.7821 | 34.4603 | 34.1874 | 34.469 | 35.1629 | 36.1868 | 35.3052 | 35.4557 | 34.9092 | 93.4168 | 93.5535 | 93.3136
2022-09-07 23:52 | 2:02 | 17.4361 | 17.6182 | 19.6332 | 35.2882 | 33.5009 | 35.411 | 35.9175 | 36.1843 | 36.9509 | 37.2483 | 36.6446 | 37.3646 | 34.0545 | 34.4561 | 35.811 | 36.0153 | 36.9765 | 37.0989 | 37.4995 | 37.6052 | 23.1537 | 18.0421 | 92.4527 | 33.4675 | 34.7015 | 35.997 | 34.8272 | 34.3522 | 34.5758 | 35.738 | 34.9311 | 34.8995 | 37.6454 | 36.5705 | 34.5513 | 34.8753 | 36.5845 | 37.2236 | 37.8987 | 36.6058 | 34.8025 | 34.1658 | 35.6625 | 36.1003 | 34.0451 | 34.3828 | 34.558 | 34.2371 | 34.4885 | 33.7857 | 34.4801 | 34.198 | 34.4839 | 35.1905 | 36.1694 | 35.2926 | 35.4649 | 34.9187 | 93.2395 | 93.4536 | 93.164
2022-09-07 23:53 | 2:02 | 17.4332 | 17.6216 | 19.5984 | 35.3422 | 33.4855 | 35.3948 | 35.8967 | 36.1658 | 36.9656 | 37.2355 | 36.6337 | 37.3685 | 34.0679 | 34.4321 | 35.8181 | 35.9965 | 36.9761 | 37.1 | 37.4676 | 37.6303 | 23.14 | 18.0336 | 92.3799 | 33.5336 | 34.7209 | 35.9749 | 34.8078 | 34.355 | 34.5707 | 35.7454 | 34.9427 | 34.8963 | 37.6445 | 36.5832 | 34.5712 | 34.8867 | 36.5842 | 37.2069 | 37.8705 | 36.5942 | 34.7976 | 34.1591 | 35.6572 | 36.0776 | 34.0149 | 34.3939 | 34.5571 | 34.2053 | 34.4627 | 33.7565 | 34.4601 | 34.1898 | 34.4885 | 35.1709 | 36.165 | 35.3088 | 35.4573 | 34.9123 | 93.1359 | 93.3331 | 93.1635
2022-09-07 23:53 | 2:03 | 17.4826 | 17.6117 | 19.5788 | 35.2362 | 33.4911 | 35.4085 | 35.8994 | 36.1527 | 36.9714 | 37.2698 | 36.6274 | 37.3474 | 34.0475 | 34.439 | 35.7985 | 36.0003 | 36.957 | 37.0974 | 37.473 | 37.6124 | 23.1069 | 18.0772 | 92.318 | 33.4491 | 34.7007 | 35.981 | 34.7982 | 34.3439 | 34.5922 | 35.7244 | 34.9301 | 34.8869 | 37.6279 | 36.5696 | 34.5493 | 34.8918 | 36.5705 | 37.2114 | 37.8682 | 36.6045 | 34.8057 | 34.1445 | 35.6604 | 36.0878 | 34.0107 | 34.4055 | 34.5525 | 34.2226 | 34.4792 | 33.7691 | 34.469 | 34.1765 | 34.4627 | 35.1564 | 36.1707 | 35.3014 | 35.4333 | 34.8985 | 93.1205 | 93.2826 | 93.1554
2022-09-07 23:53 | 2:03 | 17.4817 | 17.639 | 19.6212 | 35.2269 | 33.4821 | 35.3932 | 35.8889 | 36.1555 | 36.97 | 37.2625 | 36.6329 | 37.3448 | 34.05 | 34.4377 | 35.8166 | 36.0017 | 36.9515 | 37.1147 | 37.4755 | 37.6043 | 23.083 | 18.0868 | 92.4266 | 33.5131 | 34.7082 | 35.9659 | 34.81 | 34.3583 | 34.5486 | 35.7343 | 34.9314 | 34.884 | 37.6328 | 36.5672 | 34.5478 | 34.8833 | 36.5832 | 37.2115 | 37.8724 | 36.5845 | 34.8091 | 34.1422 | 35.6422 | 36.0784 | 34.0214 | 34.3849 | 34.5464 | 34.2211 | 34.484 | 33.7861 | 34.4537 | 34.1685 | 34.4792 | 35.1536 | 36.1741 | 35.2942 | 35.4483 | 34.899 | 93.0772 | 93.1749 | 93.1151
2022-09-07 23:53 | 2:03 | 17.4848 | 17.6487 | 19.606 | 35.2956 | 33.4812 | 35.3963 | 35.9103 | 36.1397 | 36.9581 | 37.2514 | 36.6409 | 37.3445 | 34.0516 | 34.4175 | 35.8139 | 35.9985 | 36.9475 | 37.1006 | 37.4722 | 37.6026 | 23.0661 | 18.0807 | 92.6002 | 33.3549 | 34.7053 | 35.9753 | 34.8025 | 34.3447 | 34.5513 | 35.743 | 34.9328 | 34.8882 | 37.6503 | 36.5739 | 34.5361 | 34.873 | 36.5696 | 37.2289 | 37.8886 | 36.5842 | 34.7977 | 34.1482 | 35.6406 | 36.0964 | 33.9829 | 34.4143 | 34.5564 | 34.2354 | 34.4718 | 33.7572 | 34.4765 | 34.1933 | 34.484 | 35.17 | 36.1737 | 35.2874 | 35.4528 | 34.8845 | 93.025 | 93.1036 | 93.0716
2022-09-07 23:53 | 2:03 | 17.4957 | 17.6521 | 19.6155 | 35.2454 | 33.4629 | 35.3702 | 35.8888 | 36.1497 | 36.9671 | 37.2601 | 36.6361 | 37.3454 | 34.0342 | 34.4455 | 35.8023 | 36.0037 | 36.9565 | 37.0863 | 37.4723 | 37.6117 | 23.0649 | 18.0974 | 92.5582 | 33.3775 | 34.6976 | 35.9774 | 34.7976 | 34.3515 | 34.5712 | 35.7345 | 34.9258 | 34.8741 | 37.6372 | 36.5843 | 34.5448 | 34.8746 | 36.5672 | 37.2151 | 37.8776 | 36.5705 | 34.8 | 34.1382 | 35.6282 | 36.0629 | 34.0058 | 34.3972 | 34.5572 | 34.208 | 34.4673 | 33.7502 | 34.4607 | 34.1681 | 34.4718 | 35.1478 | 36.1564 | 35.3082 | 35.4409 | 34.902 | 92.954 | 92.978 | 92.9969
2022-09-07 23:53 | 2:03 | 17.4484 | 17.601 | 19.5946 | 35.3458 | 33.4735 | 35.3849 | 35.8792 | 36.1514 | 36.9591 | 37.2723 | 36.6503 | 37.351 | 34.0401 | 34.4333 | 35.7991 | 36.0092 | 36.9521 | 37.1043 | 37.4669 | 37.5947 | 23.032 | 18.0258 | 92.6181 | 33.3434 | 34.6816 | 35.9606 | 34.8057 | 34.3384 | 34.5493 | 35.7426 | 34.9199 | 34.8892 | 37.631 | 36.576 | 34.5419 | 34.851 | 36.5739 | 37.2079 | 37.88 | 36.5832 | 34.7911 | 34.1324 | 35.6306 | 36.0739 | 33.9975 | 34.3841 | 34.5596 | 34.2086 | 34.5022 | 33.7555 | 34.4725 | 34.1703 | 34.4673 | 35.1588 | 36.186 | 35.2963 | 35.4605 | 34.8957 | 92.7894 | 92.8814 | 92.8669
2022-09-07 23:54 | 2:04 | 17.4629 | 17.6249 | 19.5797 | 35.2702 | 33.4793 | 35.3761 | 35.8848 | 36.1469 | 36.9662 | 37.2517 | 36.6574 | 37.3533 | 34.025 | 34.4184 | 35.8002 | 35.9861 | 36.9357 | 37.1051 | 37.4484 | 37.6121 | 23.0051 | 18.0633 | 92.6765 | 33.3941 | 34.6806 | 35.9614 | 34.8091 | 34.3593 | 34.5478 | 35.7396 | 34.9096 | 34.876 | 37.6438 | 36.5944 | 34.5421 | 34.8768 | 36.5843 | 37.194 | 37.8798 | 36.5696 | 34.788 | 34.1157 | 35.6238 | 36.0642 | 33.9956 | 34.3941 | 34.5483 | 34.1997 | 34.4804 | 33.7699 | 34.462 | 34.1793 | 34.5022 | 35.1879 | 36.1673 | 35.3021 | 35.4478 | 34.8838 | 92.647 | 92.8252 | 92.848
2022-09-07 23:54 | 2:04 | 17.4667 | 17.6213 | 19.618 | 35.3514 | 33.4516 | 35.3684 | 35.8964 | 36.1524 | 36.9537 | 37.2532 | 36.6452 | 37.3465 | 34.0303 | 34.4355 | 35.8085 | 35.9901 | 36.9265 | 37.0967 | 37.4791 | 37.5909 | 22.9965 | 18.0849 | 92.7617 | 33.3398 | 34.672 | 35.963 | 34.7977 | 34.3484 | 34.5361 | 35.7347 | 34.9397 | 34.8883 | 37.631 | 36.5722 | 34.5346 | 34.8556 | 36.576 | 37.2064 | 37.8644 | 36.5672 | 34.798 | 34.1242 | 35.6192 | 36.0515 | 33.9862 | 34.4037 | 34.5636 | 34.2044 | 34.4997 | 33.7424 | 34.4569 | 34.164 | 34.4804 | 35.1719 | 36.1526 | 35.2768 | 35.4566 | 34.872 | 92.553 | 92.6878 | 92.8077
2022-09-07 23:54 | 2:04 | 17.4852 | 17.627 | 19.6177 | 35.2212 | 33.4674 | 35.355 | 35.9033 | 36.1476 | 36.9601 | 37.268 | 36.6351 | 37.3409 | 34.0277 | 34.4332 | 35.8054 | 36.0019 | 36.9483 | 37.1172 | 37.463 | 37.6099 | 22.9861 | 18.0511 | 92.7546 | 33.4008 | 34.6877 | 35.9699 | 34.8 | 34.3289 | 34.5448 | 35.7382 | 34.9253 | 34.8771 | 37.6269 | 36.5708 | 34.5497 | 34.872 | 36.5944 | 37.2052 | 37.8837 | 36.5739 | 34.7762 | 34.072 | 35.6185 | 36.0427 | 33.9855 | 34.3853 | 34.568 | 34.2009 | 34.4834 | 33.7488 | 34.4577 | 34.1638 | 34.4997 | 35.1704 | 36.1574 | 35.2821 | 35.459 | 34.8729 | 92.4367 | 92.5714 | 92.7188
2022-09-07 23:54 | 2:04 | 17.4317 | 17.5781 | 19.6129 | 35.2191 | 33.4584 | 35.3455 | 35.9109 | 36.1396 | 36.9577 | 37.2595 | 36.6366 | 37.3569 | 34.0137 | 34.4265 | 35.7895 | 35.9895 | 36.9348 | 37.0941 | 37.4463 | 37.6072 | 22.9471 | 18.0523 | 92.7278 | 33.4586 | 34.6805 | 35.9465 | 34.7911 | 34.3255 | 34.5419 | 35.7442 | 34.9319 | 34.8725 | 37.6459 | 36.569 | 34.5471 | 34.8687 | 36.5722 | 37.204 | 37.8772 | 36.5843 | 34.8019 | 34.0926 | 35.6052 | 36.0492 | 33.9695 | 34.3991 | 34.5542 | 34.1803 | 34.5132 | 33.7669 | 34.4593 | 34.1813 | 34.4834 | 35.1613 | 36.1654 | 35.2909 | 35.4513 | 34.8715 | 92.3444 | 92.4017 | 92.6338
2022-09-07 23:54 | 2:04 | 17.4429 | 17.6317 | 19.6439 | 35.2886 | 33.4477 | 35.3725 | 35.9013 | 36.1525 | 36.9575 | 37.2736 | 36.6202 | 37.3458 | 34.0175 | 34.4158 | 35.7819 | 35.9807 | 36.9346 | 37.0986 | 37.4607 | 37.6151 | 22.9388 | 18.052 | 92.84 | 33.2788 | 34.6717 | 35.9354 | 34.788 | 34.3404 | 34.5421 | 35.7608 | 34.9245 | 34.8745 | 37.6342 | 36.5522 | 34.5346 | 34.863 | 36.5708 | 37.1936 | 37.8853 | 36.576 | 34.7775 | 34.0901 | 35.5897 | 36.0452 | 33.9903 | 34.3877 | 34.5784 | 34.1896 | 34.4918 | 33.7278 | 34.4451 | 34.1678 | 34.5132 | 35.1704 | 36.1384 | 35.3138 | 35.4743 | 34.8792 | 92.2541 | 92.3358 | 92.5655
2022-09-07 23:54 | 2:04 | 17.4617 | 17.6329 | 19.6207 | 35.2889 | 33.4478 | 35.3535 | 35.9046 | 36.1374 | 36.9485 | 37.2655 | 36.6349 | 37.3683 | 34.0121 | 34.4145 | 35.8023 | 35.9721 | 36.9199 | 37.0974 | 37.4623 | 37.6059 | 22.9114 | 18.0624 | 92.9626 | 33.4461 | 34.6899 | 35.9316 | 34.798 | 34.3309 | 34.5346 | 35.7548 | 34.9267 | 34.8607 | 37.6393 | 36.5707 | 34.5342 | 34.8439 | 36.569 | 37.2037 | 37.8803 | 36.5944 | 34.7772 | 34.0841 | 35.5949 | 36.0487 | 33.9548 | 34.3896 | 34.5839 | 34.1645 | 34.5001 | 33.7408 | 34.4578 | 34.1698 | 34.4918 | 35.1899 | 36.1476 | 35.3034 | 35.4661 | 34.8802 | 92.1495 | 92.2468 | 92.5193
2022-09-07 23:55 | 2:04 | 17.4978 | 17.6431 | 19.6367 | 35.2239 | 33.4443 | 35.3465 | 35.88 | 36.1438 | 36.9551 | 37.2887 | 36.6319 | 37.3602 | 34.0002 | 34.4145 | 35.7927 | 35.9913 | 36.9463 | 37.0899 | 37.4596 | 37.5974 | 22.9216 | 18.0749 | 93.1817 | 33.1879 | 34.6759 | 35.9419 | 34.7762 | 34.3402 | 34.5497 | 35.7406 | 34.9073 | 34.8746 | 37.6408 | 36.5684 | 34.5507 | 34.8669 | 36.5522 | 37.2139 | 37.8749 | 36.5722 | 34.758 | 34.0751 | 35.6085 | 36.0443 | 33.9601 | 34.3913 | 34.5676 | 34.1727 | 34.4813 | 33.7578 | 34.4566 | 34.1617 | 34.5001 | 35.1985 | 36.1467 | 35.2791 | 35.4593 | 34.8644 | 91.9586 | 92.052 | 92.3743
2022-09-07 23:55 | 2:05 | 17.4761 | 17.6647 | 19.6278 | 35.2073 | 33.4387 | 35.3546 | 35.8904 | 36.1344 | 36.9676 | 37.282 | 36.6232 | 37.3583 | 34.0082 | 34.4227 | 35.7957 | 35.9835 | 36.9388 | 37.0857 | 37.4613 | 37.6104 | 22.9042 | 18.058 | 93.2763 | 33.2216 | 34.6548 | 35.932 | 34.8019 | 34.3386 | 34.5471 | 35.7459 | 34.9211 | 34.8728 | 37.6483 | 36.5609 | 34.5246 | 34.8677 | 36.5707 | 37.1798 | 37.8935 | 36.5708 | 34.77 | 34.0793 | 35.6131 | 36.0279 | 33.9804 | 34.3937 | 34.5672 | 34.1785 | 34.5003 | 33.7401 | 34.4468 | 34.1491 | 34.4813 | 35.1643 | 36.1589 | 35.2933 | 35.4719 | 34.8647 | 91.8264 | 91.9032 | 92.372
2022-09-07 23:55 | 2:05 | 17.4576 | 17.6219 | 19.6305 | 35.2556 | 33.4344 | 35.3394 | 35.9064 | 36.1461 | 36.9685 | 37.2824 | 36.655 | 37.3623 | 34.0202 | 34.4188 | 35.7746 | 35.9864 | 36.9028 | 37.09 | 37.4766 | 37.5922 | 22.8682 | 18.0305 | 93.2134 | 33.1874 | 34.6766 | 35.9184 | 34.7775 | 34.3421 | 34.5346 | 35.7495 | 34.9138 | 34.8622 | 37.6439 | 36.5513 | 34.5388 | 34.858 | 36.5684 | 37.1972 | 37.8903 | 36.569 | 34.7413 | 34.0814 | 35.5813 | 36.0333 | 33.9442 | 34.382 | 34.5646 | 34.192 | 34.5073 | 33.7399 | 34.4566 | 34.1725 | 34.5003 | 35.1906 | 36.1516 | 35.3121 | 35.4746 | 34.8567 | 91.6764 | 91.8413 | 92.264
2022-09-07 23:55 | 2:05 | 17.4456 | 17.6042 | 19.6232 | 35.3092 | 33.4565 | 35.3325 | 35.9031 | 36.1335 | 36.9557 | 37.2857 | 36.6283 | 37.3672 | 33.9913 | 34.3866 | 35.7806 | 35.9886 | 36.9108 | 37.105 | 37.4585 | 37.618 | 22.8755 | 18.0334 | 93.4475 | 33.3561 | 34.6606 | 35.928 | 34.7772 | 34.3205 | 34.5342 | 35.7479 | 34.9195 | 34.874 | 37.6334 | 36.5556 | 34.5318 | 34.8664 | 36.5609 | 37.2081 | 37.8855 | 36.5522 | 34.7735 | 34.0733 | 35.6037 | 36.0199 | 33.9339 | 34.3771 | 34.5722 | 34.1652 | 34.4845 | 33.7357 | 34.4503 | 34.161 | 34.5073 | 35.1661 | 36.1347 | 35.3016 | 35.4583 | 34.8441 | 91.6895 | 91.8111 | 92.2502
2022-09-07 23:55 | 2:05 | 17.4775 | 17.6523 | 19.646 | 35.2747 | 33.4256 | 35.3472 | 35.8959 | 36.1509 | 36.9501 | 37.2682 | 36.6395 | 37.3653 | 33.9799 | 34.4416 | 35.781 | 35.9789 | 36.9097 | 37.0938 | 37.4706 | 37.6049 | 22.8676 | 18.0439 | 93.504 | 33.3823 | 34.6645 | 35.929 | 34.758 | 34.3288 | 34.5507 | 35.7461 | 34.9113 | 34.8735 | 37.6203 | 36.572 | 34.5293 | 34.8522 | 36.5513 | 37.1881 | 37.8685 | 36.5707 | 34.768 | 34.0836 | 35.5709 | 36.0279 | 33.9453 | 34.411 | 34.5739 | 34.1727 | 34.524 | 33.7253 | 34.4472 | 34.1733 | 34.4845 | 35.1636 | 36.1596 | 35.3265 | 35.4673 | 34.8356 | 91.8084 | 91.8277 | 92.2616
2022-09-07 23:55 | 2:05 | 17.4807 | 17.6599 | 19.6599 | 35.2873 | 33.431 | 35.3274 | 35.9027 | 36.137 | 36.9477 | 37.2655 | 36.6335 | 37.3694 | 33.9962 | 34.4127 | 35.7781 | 35.9785 | 36.9029 | 37.0818 | 37.4588 | 37.6086 | 22.8422 | 18.0603 | 93.7317 | 33.2565 | 34.6769 | 35.9193 | 34.77 | 34.3313 | 34.5246 | 35.7418 | 34.937 | 34.8684 | 37.6388 | 36.5669 | 34.5174 | 34.8591 | 36.5556 | 37.1899 | 37.8786 | 36.5684 | 34.7507 | 34.0505 | 35.5759 | 36.0029 | 33.9339 | 34.3903 | 34.5524 | 34.1597 | 34.5103 | 33.7247 | 34.4433 | 34.1639 | 34.524 | 35.1817 | 36.1431 | 35.3103 | 35.4596 | 34.8512 | 91.9133 | 91.9077 | 92.3234
2022-09-07 23:56 | 2:06 | 17.4743 | 17.6301 | 19.6455 | 35.3041 | 33.4179 | 35.3271 | 35.8953 | 36.1397 | 36.9513 | 37.2873 | 36.639 | 37.3618 | 33.9921 | 34.4259 | 35.775 | 35.9751 | 36.8992 | 37.0744 | 37.4425 | 37.6191 | 22.8543 | 18.0351 | 93.8329 | 33.3571 | 34.6412 | 35.9204 | 34.7413 | 34.3329 | 34.5388 | 35.745 | 34.9252 | 34.8776 | 37.6145 | 36.5613 | 34.5123 | 34.8575 | 36.572 | 37.2079 | 37.8768 | 36.5609 | 34.7505 | 34.0545 | 35.5798 | 36.015 | 33.9344 | 34.3847 | 34.5728 | 34.1615 | 34.5049 | 33.7233 | 34.4488 | 34.1601 | 34.5103 | 35.1899 | 36.1324 | 35.3184 | 35.474 | 34.8404 | 91.9591 | 92.0872 | 92.4312
2022-09-07 23:56 | 2:06 | 17.4973 | 17.6439 | 19.6292 | 35.3442 | 33.4291 | 35.3211 | 35.8929 | 36.1621 | 36.9591 | 37.2784 | 36.6309 | 37.3623 | 33.9892 | 34.4147 | 35.7717 | 35.9818 | 36.8907 | 37.0886 | 37.4651 | 37.5842 | 22.8144 | 18.0788 | 93.8341 | 33.2549 | 34.6377 | 35.8937 | 34.7735 | 34.3409 | 34.5318 | 35.7394 | 34.9204 | 34.8777 | 37.6165 | 36.5589 | 34.5292 | 34.8456 | 36.5669 | 37.1853 | 37.8671 | 36.5513 | 34.7528 | 34.0453 | 35.5758 | 36.0067 | 33.946 | 34.3867 | 34.58 | 34.1658 | 34.4975 | 33.7142 | 34.4307 | 34.1506 | 34.5049 | 35.1581 | 36.1261 | 35.3015 | 35.4801 | 34.8433 | 92.1305 | 92.2282 | 92.5216
2022-09-07 23:56 | 2:06 | 17.4595 | 17.6296 | 19.658 | 35.1685 | 33.4256 | 35.328 | 35.8869 | 36.1296 | 36.9496 | 37.2752 | 36.6478 | 37.374 | 33.9856 | 34.406 | 35.7574 | 35.9756 | 36.9123 | 37.0769 | 37.4551 | 37.6022 | 22.8073 | 18.0418 | 93.7542 | 33.4149 | 34.6561 | 35.9186 | 34.768 | 34.3325 | 34.5293 | 35.7385 | 34.9228 | 34.8585 | 37.6308 | 36.566 | 34.5292 | 34.8625 | 36.5613 | 37.1986 | 37.8432 | 36.5556 | 34.7449 | 34.0453 | 35.566 | 36.013 | 33.903 | 34.3794 | 34.5568 | 34.1618 | 34.4876 | 33.705 | 34.4567 | 34.1576 | 34.4975 | 35.1951 | 36.1455 | 35.3038 | 35.4629 | 34.8173 | 92.144 | 92.3642 | 92.5312
2022-09-07 23:56 | 2:06 | 17.4551 | 17.605 | 19.6372 | 35.2578 | 34.4908 | 35.3166 | 35.8934 | 36.1403 | 36.9509 | 37.293 | 36.6493 | 37.3609 | 33.9587 | 34.4066 | 35.7583 | 35.9606 | 36.8983 | 37.0869 | 37.4606 | 37.5913 | 22.7826 | 18.0307 | 94.1697 | 33.2672 | 34.6311 | 35.8897 | 34.7507 | 34.3235 | 34.5174 | 35.7262 | 34.8961 | 34.8706 | 37.6082 | 36.5376 | 34.4945 | 34.8541 | 36.5589 | 37.1826 | 37.8556 | 36.572 | 34.7578 | 34.0522 | 35.5698 | 35.9779 | 33.8994 | 34.3867 | 34.5423 | 34.1488 | 34.5055 | 33.7179 | 34.4334 | 34.1445 | 34.4876 | 35.1709 | 36.1198 | 35.2958 | 35.4634 | 34.8137 | 92.3369 | 92.426 | 92.6102
2022-09-07 23:56 | 2:06 | 17.4499 | 17.6263 | 19.6139 | 35.1873 | 34.4978 | 35.312 | 35.8896 | 36.1449 | 36.9534 | 37.2994 | 36.6537 | 37.372 | 33.9674 | 34.4136 | 35.749 | 35.9643 | 36.9069 | 37.0844 | 37.4517 | 37.5843 | 22.7823 | 18.059 | 94.0287 | 33.2816 | 34.632 | 35.9124 | 34.7505 | 34.318 | 34.5123 | 35.7337 | 34.9175 | 34.8745 | 37.6266 | 36.5258 | 34.5136 | 34.8416 | 36.566 | 37.1689 | 37.8544 | 36.5669 | 34.7428 | 34.034 | 35.5517 | 35.9799 | 33.9006 | 34.3824 | 34.5566 | 34.1257 | 34.5152 | 33.732 | 34.4463 | 34.1289 | 34.5055 | 35.1616 | 36.1278 | 35.3073 | 35.4645 | 34.8242 | 92.5092 | 92.5262 | 92.6645
2022-09-07 23:56 | 2:06 | 17.4349 | 17.6281 | 19.6653 | 35.2264 | 34.4957 | 35.2938 | 35.8954 | 36.124 | 36.9388 | 37.2568 | 36.6343 | 37.3627 | 33.9787 | 34.3965 | 35.758 | 35.9811 | 36.8991 | 37.0665 | 37.4306 | 37.5757 | 22.7647 | 18.0378 | 94.1122 | 33.3932 | 34.6373 | 35.8964 | 34.7528 | 34.328 | 34.5292 | 35.7301 | 34.924 | 34.8675 | 37.6013 | 36.538 | 34.508 | 34.8354 | 36.5376 | 37.1666 | 37.8558 | 36.5613 | 34.7479 | 34.0512 | 35.5276 | 35.974 | 33.8887 | 34.369 | 34.5833 | 34.1415 | 34.511 | 33.6966 | 34.4521 | 34.1343 | 34.5152 | 35.1608 | 36.1308 | 35.2973 | 35.4628 | 34.8202 | 92.6119 | 92.6925 | 92.7878
2022-09-07 23:57 | 2:06 | 17.4604 | 17.6156 | 19.6405 | 35.2247 | 34.4833 | 35.2998 | 35.8776 | 36.1317 | 36.9553 | 37.2685 | 36.64 | 37.3687 | 33.9516 | 34.4198 | 35.7437 | 35.9669 | 36.8869 | 37.0879 | 37.4484 | 37.5833 | 22.7523 | 18.0147 | 94.2353 | 33.381 | 34.6079 | 35.8831 | 34.7449 | 34.2988 | 34.5292 | 35.7254 | 34.9067 | 34.853 | 37.6039 | 36.5079 | 34.5157 | 34.8447 | 36.5258 | 37.1842 | 37.8404 | 36.5589 | 34.7281 | 34.0238 | 35.5333 | 35.9689 | 33.8645 | 34.3826 | 34.5597 | 34.1228 | 34.4948 | 33.7265 | 34.4561 | 34.1406 | 34.511 | 35.1473 | 36.1222 | 35.2967 | 35.4603 | 34.8105 | 92.7192 | 92.8264 | 92.8505
2022-09-07 23:57 | 2:07 | 17.3752 | 17.5745 | 19.6433 | 35.1888 | 34.4959 | 35.3014 | 35.9002 | 36.1133 | 36.9387 | 37.2647 | 36.6434 | 37.3721 | 33.95 | 34.4169 | 35.7214 | 35.9733 | 36.8772 | 37.0706 | 37.4333 | 37.5709 | 22.7645 | 17.9573 | 94.0862 | 33.2239 | 34.6258 | 35.8789 | 34.7578 | 34.292 | 34.4945 | 35.7268 | 34.9077 | 34.8431 | 37.5921 | 36.5349 | 34.4924 | 34.8223 | 36.538 | 37.1633 | 37.8452 | 36.566 | 34.7329 | 34.0143 | 35.5154 | 35.9499 | 33.8966 | 34.3901 | 34.5408 | 34.1177 | 34.5159 | 33.693 | 34.4321 | 34.1343 | 34.4948 | 35.151 | 36.1276 | 35.2978 | 35.4603 | 34.7957 | 92.8782 | 92.9361 | 93.0045
2022-09-07 23:57 | 2:07 | 17.3654 | 17.5497 | 19.6059 | 35.2211 | 34.4665 | 35.3106 | 35.8948 | 36.1197 | 36.9358 | 37.274 | 36.6367 | 37.3624 | 33.9533 | 34.4241 | 35.7313 | 35.954 | 36.8957 | 37.061 | 37.4155 | 37.5715 | 22.7483 | 17.8964 | 93.8438 | 33.1853 | 34.6222 | 35.8869 | 34.7428 | 34.3005 | 34.5136 | 35.7173 | 34.9199 | 34.8475 | 37.6132 | 36.5438 | 34.5014 | 34.8306 | 36.5079 | 37.1542 | 37.8453 | 36.5376 | 34.7223 | 34.0189 | 35.5224 | 35.959 | 33.8763 | 34.3802 | 34.5539 | 34.1093 | 34.5105 | 33.6979 | 34.439 | 34.1212 | 34.5159 | 35.1592 | 36.122 | 35.3278 | 35.4561 | 34.7993 | 92.9841 | 93.019 | 92.9819
2022-09-07 23:57 | 2:07 | 17.3348 | 17.4976 | 19.5752 | 35.2328 | 34.4603 | 35.2897 | 35.887 | 36.113 | 36.9369 | 37.2766 | 36.6339 | 37.3477 | 33.9421 | 34.4261 | 35.728 | 35.9704 | 36.865 | 37.0622 | 37.4312 | 37.5635 | 22.7403 | 17.8441 | 93.7843 | 33.3117 | 34.6042 | 35.8982 | 34.7479 | 34.3044 | 34.508 | 35.7206 | 34.8989 | 34.8391 | 37.6036 | 36.5332 | 34.498 | 34.8451 | 36.5349 | 37.1671 | 37.8306 | 36.5258 | 34.7194 | 34.0044 | 35.5014 | 35.9603 | 33.8757 | 34.3905 | 34.5292 | 34.1082 | 34.5205 | 33.7187 | 34.4377 | 34.1072 | 34.5105 | 35.1589 | 36.1268 | 35.3102 | 35.4398 | 34.7819 | 93.2262 | 93.1622 | 93.1287
2022-09-07 23:57 | 2:07 | 17.3655 | 17.5613 | 19.6022 | 35.2524 | 34.4801 | 35.3137 | 35.8987 | 36.1223 | 36.9273 | 37.261 | 36.6333 | 37.3602 | 33.9348 | 34.409 | 35.7263 | 35.9616 | 36.8708 | 37.0558 | 37.4244 | 37.5532 | 22.7483 | 17.8579 | 93.5871 | 33.1588 | 34.5947 | 35.8822 | 34.7281 | 34.3249 | 34.5157 | 35.7122 | 34.9282 | 34.8547 | 37.6035 | 36.5257 | 34.4835 | 34.8602 | 36.5438 | 37.168 | 37.8257 | 36.538 | 34.741 | 34.0027 | 35.509 | 35.9446 | 33.8737 | 34.3869 | 34.5408 | 34.0887 | 34.524 | 33.6894 | 34.4175 | 34.1188 | 34.5205 | 35.163 | 36.1287 | 35.2953 | 35.4361 | 34.7642 | 93.335 | 93.3383 | 93.2616
2022-09-07 23:57 | 2:07 | 17.369 | 17.5307 | 19.5984 | 35.2233 | 34.4601 | 35.2954 | 35.8957 | 36.1177 | 36.9395 | 37.2717 | 36.6538 | 37.3644 | 33.9255 | 34.4133 | 35.7135 | 35.9575 | 36.887 | 37.0481 | 37.4151 | 37.5488 | 22.7921 | 17.8926 | 93.5807 | 33.3253 | 34.6013 | 35.8785 | 34.7329 | 34.3053 | 34.4924 | 35.6953 | 34.9134 | 34.8511 | 37.614 | 36.5271 | 34.4915 | 34.8531 | 36.5332 | 37.1658 | 37.8189 | 36.5079 | 34.7203 | 33.9718 | 35.5 | 35.947 | 33.8639 | 34.3754 | 34.5173 | 34.121 | 34.5166 | 33.7102 | 34.4455 | 34.1119 | 34.524 | 35.1362 | 36.1222 | 35.3082 | 35.463 | 34.7724 | 93.5156 | 93.4972 | 93.2943
2022-09-07 23:58 | 2:08 | 17.3551 | 17.5254 | 19.5908 | 35.3763 | 34.469 | 35.285 | 35.907 | 36.1291 | 36.9352 | 37.2531 | 36.6541 | 37.3687 | 33.9158 | 34.4082 | 35.726 | 35.9591 | 36.869 | 37.049 | 37.4267 | 37.5438 | 22.7998 | 17.8681 | 93.5293 | 33.3066 | 34.5861 | 35.862 | 34.7223 | 34.301 | 34.5014 | 35.7206 | 34.9215 | 34.8538 | 37.6045 | 36.5684 | 34.4907 | 34.846 | 36.5257 | 37.1682 | 37.8366 | 36.5349 | 34.6969 | 33.9804 | 35.5014 | 35.9363 | 33.8661 | 34.3833 | 34.5357 | 34.0885 | 34.5186 | 33.684 | 34.4333 | 34.1037 | 34.5166 | 35.1635 | 36.1218 | 35.311 | 35.4429 | 34.7595 | 93.566 | 93.6882 | 93.2688
2022-09-07 23:58 | 2:08 | 17.3848 | 17.537 | 19.5908 | 35.2359 | 34.4537 | 35.2751 | 35.9031 | 36.1276 | 36.9358 | 37.2655 | 36.6394 | 37.3713 | 33.922 | 34.4096 | 35.7129 | 35.9915 | 36.873 | 37.0534 | 37.3968 | 37.5339 | 22.8203 | 17.8763 | 93.3034 | 33.3122 | 34.5786 | 35.8691 | 34.7194 | 34.3056 | 34.498 | 35.6834 | 34.9088 | 34.8316 | 37.6079 | 36.5277 | 34.5068 | 34.8534 | 36.5271 | 37.1445 | 37.8283 | 36.5438 | 34.7209 | 33.9698 | 35.4783 | 35.9292 | 33.8573 | 34.3724 | 34.5425 | 34.0642 | 34.5311 | 33.6756 | 34.4184 | 34.1103 | 34.5186 | 35.1558 | 36.1105 | 35.3157 | 35.4535 | 34.7516 | 93.8244 | 93.8697 | 93.4455
2022-09-07 23:58 | 2:08 | 17.3721 | 17.525 | 19.6088 | 35.1689 | 34.4765 | 35.2844 | 35.8911 | 36.1078 | 36.9328 | 37.2551 | 36.6407 | 37.3667 | 33.9242 | 34.4053 | 35.7108 | 35.9504 | 36.8904 | 37.0519 | 37.4147 | 37.5438 | 22.8224 | 17.8997 | 93.4798 | 33.322 | 34.5845 | 35.8857 | 34.741 | 34.2988 | 34.4835 | 35.7007 | 34.9122 | 34.8508 | 37.6038 | 36.5605 | 34.4909 | 34.8493 | 36.5684 | 37.1599 | 37.8227 | 36.5332 | 34.7224 | 33.9584 | 35.4689 | 35.9267 | 33.8733 | 34.3781 | 34.5249 | 34.0614 | 34.529 | 33.6872 | 34.4355 | 34.1116 | 34.5311 | 35.1357 | 36.0996 | 35.3127 | 35.4446 | 34.7424 | 94.0639 | 94.0934 | 93.6382
2022-09-07 23:58 | 2:08 | 17.3704 | 17.5516 | 19.6068 | 35.1308 | 34.4607 | 35.2703 | 35.8762 | 36.1266 | 36.9116 | 37.2597 | 36.6426 | 37.3695 | 33.9358 | 34.4288 | 35.7068 | 35.951 | 36.8633 | 37.0309 | 37.4358 | 37.5323 | 22.8429 | 17.8827 | 93.5286 | 33.2799 | 34.5621 | 35.8818 | 34.7203 | 34.3104 | 34.4915 | 35.7225 | 34.9012 | 34.849 | 37.6049 | 36.5341 | 34.5003 | 34.8421 | 36.5277 | 37.1549 | 37.8271 | 36.5257 | 34.7116 | 33.9574 | 35.4934 | 35.9284 | 33.8375 | 34.3773 | 34.5307 | 34.0685 | 34.515 | 33.6757 | 34.4332 | 34.1048 | 34.529 | 35.1506 | 36.1072 | 35.3238 | 35.4543 | 34.7509 | 94.222 | 94.2467 | 93.7256
2022-09-07 23:58 | 2:08 | 17.4145 | 17.5726 | 19.5924 | 35.2369 | 34.4725 | 35.2824 | 35.8858 | 36.1028 | 36.9364 | 37.2688 | 36.657 | 37.3642 | 33.8863 | 34.4007 | 35.7052 | 35.9669 | 36.8732 | 37.0487 | 37.4191 | 37.5502 | 22.8543 | 17.8787 | 93.5455 | 33.3171 | 34.5697 | 35.862 | 34.6969 | 34.2837 | 34.4907 | 35.7217 | 34.9096 | 34.8434 | 37.6027 | 36.5407 | 34.483 | 34.8492 | 36.5605 | 37.1613 | 37.8361 | 36.5271 | 34.7226 | 33.9582 | 35.4867 | 35.9024 | 33.8481 | 34.3834 | 34.5005 | 34.0802 | 34.5234 | 33.6887 | 34.4265 | 34.1069 | 34.515 | 35.1433 | 36.1159 | 35.3135 | 35.4603 | 34.7536 | 94.3429 | 94.4347 | 93.7853
2022-09-07 23:58 | 2:08 | 17.3667 | 17.5151 | 19.584 | 35.1845 | 34.462 | 35.2725 | 35.9098 | 36.1079 | 36.9272 | 37.2791 | 36.6512 | 37.3895 | 33.8989 | 34.4162 | 35.6795 | 35.9655 | 36.8788 | 37.0671 | 37.4198 | 37.5487 | 22.8473 | 17.9147 | 93.4948 | 33.4066 | 34.5783 | 35.9017 | 34.7209 | 34.2916 | 34.5068 | 35.7015 | 34.9086 | 34.8439 | 37.5988 | 36.5469 | 34.4701 | 34.8373 | 36.5341 | 37.1499 | 37.8393 | 36.5684 | 34.7175 | 33.9528 | 35.4703 | 35.9196 | 33.8462 | 34.3858 | 34.5194 | 34.0613 | 34.5235 | 33.6888 | 34.4158 | 34.0966 | 34.5234 | 35.1407 | 36.1101 | 35.3103 | 35.4611 | 34.7297 | 94.4337 | 94.6139 | 93.9518
2022-09-07 23:59 | 2:08 | 17.3394 | 17.5477 | 19.5955 | 35.1136 | 34.4569 | 35.273 | 35.8782 | 36.1146 | 36.9159 | 37.2717 | 36.6515 | 37.3927 | 33.9005 | 34.4172 | 35.6967 | 35.9635 | 36.8626 | 37.0641 | 37.4106 | 37.5727 | 22.8426 | 17.8776 | 93.1691 | 33.1808 | 34.5776 | 35.8839 | 34.7224 | 34.2973 | 34.4909 | 35.7032 | 34.9082 | 34.8536 | 37.6057 | 36.5515 | 34.4833 | 34.8597 | 36.5407 | 37.1515 | 37.8278 | 36.5277 | 34.7081 | 33.942 | 35.466 | 35.8939 | 33.8369 | 34.3911 | 34.5104 | 34.0667 | 34.5212 | 33.6838 | 34.4145 | 34.1069 | 34.5235 | 35.1392 | 36.1043 | 35.3186 | 35.4636 | 34.7149 | 94.5466 | 94.6918 | 94.0516
2022-09-07 23:59 | 2:09 | 17.4246 | 17.5503 | 19.5786 | 35.2618 | 34.4577 | 35.2856 | 35.9012 | 36.1195 | 36.9328 | 37.265 | 36.6638 | 37.3826 | 33.9036 | 34.4061 | 35.6895 | 35.965 | 36.8729 | 37.057 | 37.4055 | 37.5505 | 22.8345 | 17.8781 | 93.3607 | 33.2957 | 34.5692 | 35.8681 | 34.7116 | 34.2995 | 34.5003 | 35.7047 | 34.9205 | 34.8458 | 37.5984 | 36.5416 | 34.4948 | 34.8571 | 36.5469 | 37.1722 | 37.814 | 36.5605 | 34.7142 | 33.9501 | 35.4754 | 35.8963 | 33.8382 | 34.3682 | 34.4991 | 34.0592 | 34.5264 | 33.6779 | 34.4145 | 34.0941 | 34.5212 | 35.1462 | 36.1146 | 35.318 | 35.4547 | 34.7375 | 94.6899 | 94.8569 | 94.0365
2022-09-07 23:59 | 2:09 | 17.4049 | 17.5507 | 19.6068 | 35.2362 | 34.4593 | 35.2618 | 35.8809 | 36.1326 | 36.9271 | 37.2746 | 36.6575 | 37.3813 | 33.9014 | 34.4011 | 35.6876 | 35.9674 | 36.8519 | 37.0444 | 37.4284 | 37.5381 | 22.849 | 17.8975 | 93.3004 | 33.2563 | 34.5721 | 35.8797 | 34.7226 | 34.2826 | 34.483 | 35.7105 | 34.931 | 34.8411 | 37.6061 | 36.5648 | 34.4928 | 34.8648 | 36.5515 | 37.16 | 37.8312 | 36.5341 | 34.7274 | 33.9393 | 35.4676 | 35.8936 | 33.8332 | 34.3718 | 34.4986 | 34.0517 | 34.532 | 33.7033 | 34.4227 | 34.1091 | 34.5264 | 35.1442 | 36.1038 | 35.3223 | 35.4431 | 34.7321 | 94.6853 | 94.8814 | 93.9298
2022-09-07 23:59 | 2:09 | 17.3397 | 17.5175 | 19.5817 | 35.2794 | 34.4451 | 35.2462 | 35.8809 | 36.1252 | 36.9472 | 37.2745 | 36.6728 | 37.3882 | 33.8953 | 34.4159 | 35.6727 | 35.964 | 36.8543 | 37.0577 | 37.4178 | 37.5401 | 22.8071 | 17.8332 | 93.2936 | 33.2885 | 34.5667 | 35.8668 | 34.7175 | 34.2965 | 34.4701 | 35.6994 | 34.9264 | 34.841 | 37.6074 | 36.5259 | 34.4819 | 34.8479 | 36.5416 | 37.1486 | 37.8212 | 36.5407 | 34.7245 | 33.942 | 35.4689 | 35.8994 | 33.8315 | 34.3734 | 34.5005 | 34.048 | 34.5422 | 33.6898 | 34.4188 | 34.1225 | 34.532 | 35.1451 | 36.1051 | 35.3252 | 35.45 | 34.7268 | 94.8962 | 95.0434 | 94.1795
2022-09-07 23:59 | 2:09 | 17.342 | 17.4941 | 19.5791 | 35.1068 | 34.4578 | 35.2608 | 35.8825 | 36.12 | 36.9524 | 37.2746 | 36.6801 | 37.3876 | 33.904 | 34.418 | 35.6688 | 35.9653 | 36.8599 | 37.0473 | 37.4023 | 37.5393 | 22.8229 | 17.819 | 93.0984 | 33.3805 | 34.5584 | 35.8753 | 34.7081 | 34.2933 | 34.4833 | 35.7255 | 34.9411 | 34.8574 | 37.6094 | 36.5362 | 34.4744 | 34.844 | 36.5648 | 37.1399 | 37.8023 | 36.5469 | 34.7129 | 33.9375 | 35.4804 | 35.8778 | 33.8209 | 34.3861 | 34.4877 | 34.0665 | 34.5447 | 33.6886 | 34.3866 | 34.1016 | 34.5422 | 35.1497 | 36.1084 | 35.3248 | 35.441 | 34.7421 | 94.964 | 95.0856 | 94.1883
2022-09-07 23:59 | 2:09 | 17.3177 | 17.4581 | 19.5687 | 35.1977 | 34.4566 | 35.2504 | 35.893 | 36.1041 | 36.9218 | 37.2869 | 36.68 | 37.3934 | 33.895 | 34.4385 | 35.6809 | 35.9584 | 36.8584 | 37.0396 | 37.4107 | 37.5452 | 22.8089 | 17.8143 | 93.1258 | 33.4037 | 34.5481 | 35.872 | 34.7142 | 34.2817 | 34.4948 | 35.7112 | 34.9237 | 34.8451 | 37.5967 | 36.544 | 34.4807 | 34.8575 | 36.5259 | 37.1548 | 37.8248 | 36.5515 | 34.7122 | 33.9304 | 35.4725 | 35.8993 | 33.8178 | 34.3814 | 34.4942 | 34.0555 | 34.5512 | 33.6865 | 34.4416 | 34.1032 | 34.5447 | 35.1536 | 36.1334 | 35.3235 | 35.4655 | 34.7266 | 94.9853 | 95.1438 | 94.2599
2022-09-08 | 2:10 | 17.2857 | 17.4688 | 19.5645 | 35.2117 | 34.4468 | 35.2569 | 35.9061 | 36.1123 | 36.9452 | 37.2768 | 36.6821 | 37.3991 | 33.9031 | 34.423 | 35.6769 | 35.9652 | 36.8655 | 37.0421 | 37.4075 | 37.5623 | 22.7965 | 17.7828 | 93.0186 | 33.0889 | 34.5619 | 35.8736 | 34.7274 | 34.2758 | 34.4928 | 35.6919 | 34.919 | 34.8536 | 37.6054 | 36.5357 | 34.4796 | 34.8575 | 36.5362 | 37.1535 | 37.8239 | 36.5416 | 34.7038 | 33.9146 | 35.4507 | 35.8852 | 33.8163 | 34.3775 | 34.4987 | 34.0326 | 34.5315 | 33.6834 | 34.4127 | 34.0984 | 34.5512 | 35.1572 | 36.1058 | 35.326 | 35.438 | 34.7119 | 94.9792 | 95.1667 | 94.263
2022-09-08 | 2:10 | 17.3023 | 17.4699 | 19.5798 | 35.1941 | 34.4566 | 35.282 | 35.9057 | 36.1187 | 36.9462 | 37.2785 | 36.6745 | 37.4032 | 33.8896 | 34.4348 | 35.678 | 35.9743 | 36.8491 | 37.0444 | 37.4181 | 37.5457 | 22.7925 | 17.7649 | 93.0102 | 33.0952 | 34.5675 | 35.8745 | 34.7245 | 34.2732 | 34.4819 | 35.717 | 34.9357 | 34.8516 | 37.6224 | 36.5401 | 34.4935 | 34.8573 | 36.544 | 37.16 | 37.8307 | 36.5648 | 34.697 | 33.9228 | 35.4416 | 35.8971 | 33.8035 | 34.392 | 34.4771 | 34.0458 | 34.5338 | 33.6754 | 34.4259 | 34.0921 | 34.5315 | 35.1552 | 36.1 | 35.3148 | 35.4482 | 34.7242 | 94.8806 | 94.9749 | 94.1957
2022-09-08 | 2:10 | 17.3 | 17.4489 | 19.5749 | 35.2319 | 34.4503 | 35.2446 | 35.9094 | 36.1305 | 36.9433 | 37.2719 | 36.6663 | 37.4004 | 33.9013 | 34.426 | 35.674 | 35.9666 | 36.8568 | 37.0462 | 37.4093 | 37.5381 | 22.8049 | 17.7735 | 92.956 | 33.2366 | 34.5486 | 35.8733 | 34.7129 | 34.269 | 34.4744 | 35.689 | 34.9092 | 34.8541 | 37.6241 | 36.5272 | 34.4785 | 34.8621 | 36.5357 | 37.1613 | 37.8307 | 36.5259 | 34.7042 | 33.916 | 35.4439 | 35.886 | 33.795 | 34.3765 | 34.4866 | 34.0549 | 34.5333 | 33.6818 | 34.4147 | 34.1133 | 34.5338 | 35.1542 | 36.1084 | 35.3332 | 35.4513 | 34.7201 | 94.6874 | 94.8022 | 94.119
2022-09-08 | 2:10 | 17.2825 | 17.4396 | 19.5655 | 35.2636 | 34.4472 | 35.2535 | 35.9135 | 36.1141 | 36.9419 | 37.2762 | 36.6732 | 37.4074 | 33.8822 | 34.422 | 35.6668 | 35.954 | 36.8584 | 37.061 | 37.4185 | 37.5521 | 22.804 | 17.7725 | 92.8259 | 33.3521 | 34.5295 | 35.8563 | 34.7122 | 34.2809 | 34.4807 | 35.7088 | 34.9271 | 34.8459 | 37.6196 | 36.5491 | 34.4737 | 34.863 | 36.5401 | 37.1494 | 37.8147 | 36.5362 | 34.6906 | 33.9006 | 35.4487 | 35.8889 | 33.7802 | 34.3869 | 34.4769 | 34.048 | 34.538 | 33.6684 | 34.406 | 34.1052 | 34.5333 | 35.1525 | 36.1074 | 35.3235 | 35.4763 | 34.7268 | 94.3952 | 94.5732 | 93.9114
2022-09-08 | 2:10 | 17.2733 | 17.4359 | 19.5796 | 35.2088 | 34.4433 | 35.2671 | 35.9046 | 36.1175 | 36.9477 | 37.3012 | 36.6831 | 37.4005 | 33.898 | 34.4314 | 35.6612 | 35.9591 | 36.8566 | 37.0452 | 37.4093 | 37.5469 | 22.7698 | 17.7351 | 92.6581 | 33.2216 | 34.5737 | 35.8575 | 34.7038 | 34.2853 | 34.4796 | 35.6949 | 34.9396 | 34.8745 | 37.5994 | 36.5161 | 34.4744 | 34.8673 | 36.5272 | 37.1628 | 37.8128 | 36.544 | 34.6777 | 33.903 | 35.4551 | 35.8905 | 33.8012 | 34.3803 | 34.4737 | 34.0598 | 34.5456 | 33.6476 | 34.4066 | 34.1034 | 34.538 | 35.1715 | 36.0997 | 35.3352 | 35.4606 | 34.7267 | 94.117 | 94.3016 | 93.7629
2022-09-08 | 2:10 | 17.2301 | 17.413 | 19.5563 | 35.1336 | 34.4488 | 35.2573 | 35.9065 | 36.1154 | 36.9222 | 37.3016 | 36.7061 | 37.4127 | 33.8902 | 34.4409 | 35.6606 | 35.9592 | 36.8635 | 37.0578 | 37.4374 | 37.5484 | 22.7666 | 17.7449 | 92.5638 | 33.2837 | 34.5454 | 35.8646 | 34.697 | 34.2982 | 34.4935 | 35.6982 | 34.9303 | 34.8517 | 37.6112 | 36.5335 | 34.4519 | 34.8657 | 36.5491 | 37.1433 | 37.8173 | 36.5357 | 34.6846 | 33.9199 | 35.4421 | 35.8947 | 33.7738 | 34.3792 | 34.4859 | 34.0371 | 34.5389 | 33.6631 | 34.4136 | 34.0939 | 34.5456 | 35.1694 | 36.088 | 35.3428 | 35.4719 | 34.7024 | 93.9686 | 94.1228 | 93.641
2022-09-08 00:01 | 2:10 | 17.182 | 17.3492 | 19.5435 | 35.2172 | 34.4307 | 35.2464 | 35.9096 | 36.1193 | 36.951 | 37.3054 | 36.6957 | 37.4171 | 33.8923 | 34.4174 | 35.6701 | 35.9534 | 36.8519 | 37.0548 | 37.4134 | 37.5271 | 22.7565 | 17.6849 | 92.6076 | 33.2098 | 34.535 | 35.8546 | 34.7042 | 34.3042 | 34.4785 | 35.7225 | 34.9381 | 34.8559 | 37.6115 | 36.5261 | 34.4768 | 34.87 | 36.5161 | 37.1482 | 37.8182 | 36.5401 | 34.6988 | 33.9204 | 35.4547 | 35.8775 | 33.7952 | 34.3854 | 34.4734 | 34.0316 | 34.558 | 33.6749 | 34.3965 | 34.0876 | 34.5389 | 35.1841 | 36.1085 | 35.3386 | 35.46 | 34.7081 | 93.8587 | 93.9716 | 93.567
2022-09-08 00:01 | 2:11 | 17.1584 | 17.318 | 19.4841 | 35.1925 | 34.4567 | 35.2423 | 35.8785 | 36.1003 | 36.934 | 37.2901 | 36.6854 | 37.431 | 33.8701 | 34.4221 | 35.6706 | 35.9598 | 36.8367 | 37.0373 | 37.4089 | 37.5467 | 22.7099 | 17.6349 | 92.456 | 33.4469 | 34.5357 | 35.8576 | 34.6906 | 34.2645 | 34.4737 | 35.7014 | 34.9264 | 34.8612 | 37.602 | 36.515 | 34.464 | 34.8778 | 36.5335 | 37.1686 | 37.8228 | 36.5272 | 34.6974 | 33.9032 | 35.4351 | 35.8806 | 33.7796 | 34.3719 | 34.4576 | 34.0297 | 34.5571 | 33.6552 | 34.4198 | 34.0838 | 34.558 | 35.165 | 36.1025 | 35.3287 | 35.4772 | 34.6989 | 93.7308 | 93.9442 | 93.5173
2022-09-08 00:01 | 2:11 | 17.1059 | 17.2848 | 19.462 | 35.228 | 34.4334 | 35.245 | 35.8991 | 36.1141 | 36.9393 | 37.3031 | 36.6774 | 37.4043 | 33.8756 | 34.4384 | 35.6601 | 35.9707 | 36.8648 | 37.0497 | 37.4139 | 37.5448 | 22.7164 | 17.576 | 92.3752 | 33.1867 | 34.5341 | 35.8504 | 34.6777 | 34.2659 | 34.4744 | 35.6977 | 34.9203 | 34.8599 | 37.6183 | 36.5099 | 34.4799 | 34.8522 | 36.5261 | 37.1564 | 37.8178 | 36.5491 | 34.7039 | 33.8931 | 35.4228 | 35.9046 | 33.7545 | 34.3863 | 34.4557 | 34.0235 | 34.5525 | 33.6585 | 34.4169 | 34.093 | 34.5571 | 35.1659 | 36.087 | 35.3304 | 35.4498 | 34.699 | 93.6391 | 93.8745 | 93.4944
2022-09-08 00:01 | 2:11 | 17.1229 | 17.2645 | 19.479 | 35.1826 | 34.4463 | 35.2435 | 35.9013 | 36.1263 | 36.9472 | 37.3029 | 36.703 | 37.4239 | 33.8786 | 34.4187 | 35.6587 | 35.9514 | 36.8415 | 37.0435 | 37.4104 | 37.5482 | 22.7208 | 17.6275 | 92.2682 | 33.274 | 34.556 | 35.8701 | 34.6846 | 34.2778 | 34.4519 | 35.7181 | 34.9473 | 34.8594 | 37.6074 | 36.5315 | 34.4545 | 34.862 | 36.515 | 37.1502 | 37.8142 | 36.5161 | 34.6946 | 33.898 | 35.4401 | 35.8803 | 33.767 | 34.3726 | 34.4537 | 34.0405 | 34.5464 | 33.6519 | 34.4241 | 34.0806 | 34.5525 | 35.1576 | 36.0817 | 35.3467 | 35.4869 | 34.7091 | 93.6424 | 93.767 | 93.4377
2022-09-08 00:01 | 2:11 | 17.1723 | 17.2921 | 19.4703 | 35.1967 | 34.4521 | 35.2332 | 35.9026 | 36.1273 | 36.931 | 37.3018 | 36.687 | 37.448 | 33.86 | 34.4511 | 35.6733 | 35.9677 | 36.8434 | 37.0487 | 37.4253 | 37.5347 | 22.7128 | 17.6126 | 92.1153 | 33.2037 | 34.5366 | 35.8515 | 34.6988 | 34.2734 | 34.4768 | 35.689 | 34.9297 | 34.8661 | 37.6147 | 36.5229 | 34.4757 | 34.8529 | 36.5099 | 37.1799 | 37.8104 | 36.5335 | 34.6814 | 33.9034 | 35.4385 | 35.8864 | 33.7555 | 34.3944 | 34.428 | 34.0325 | 34.5564 | 33.657 | 34.4261 | 34.1031 | 34.5464 | 35.1687 | 36.0982 | 35.3355 | 35.4712 | 34.7213 | 93.5437 | 93.6658 | 93.4418
2022-09-08 00:01 | 2:11 | 17.157 | 17.2794 | 19.4699 | 35.1746 | 34.4561 | 35.2416 | 35.9177 | 36.137 | 36.9449 | 37.2959 | 36.6953 | 37.4157 | 33.8628 | 34.4283 | 35.6532 | 35.9649 | 36.8478 | 37.0408 | 37.4311 | 37.5557 | 22.7024 | 17.592 | 92.014 | 33.1692 | 34.5245 | 35.8375 | 34.6974 | 34.2727 | 34.464 | 35.6964 | 34.9388 | 34.8681 | 37.6168 | 36.5309 | 34.4623 | 34.8544 | 36.5315 | 37.1419 | 37.8159 | 36.5261 | 34.6768 | 33.8856 | 35.4427 | 35.8899 | 33.7452 | 34.385 | 34.4265 | 34.0319 | 34.5572 | 33.6634 | 34.409 | 34.0765 | 34.5564 | 35.1725 | 36.0917 | 35.3319 | 35.4801 | 34.7152 | 93.5741 | 93.6557 | 93.4551
2022-09-08 00:02 | 2:11 | 17.1122 | 17.2632 | 19.4348 | 35.1219 | 34.4321 | 35.2433 | 35.9123 | 36.1093 | 36.9329 | 37.3154 | 36.7047 | 37.4178 | 33.8695 | 34.4471 | 35.6624 | 35.9723 | 36.848 | 37.0411 | 37.426 | 37.5621 | 22.7024 | 17.5875 | 91.9318 | 33.3916 | 34.5152 | 35.8364 | 34.7039 | 34.2847 | 34.4799 | 35.7084 | 34.9259 | 34.8643 | 37.6287 | 36.5039 | 34.4342 | 34.8514 | 36.5229 | 37.1409 | 37.8132 | 36.515 | 34.6599 | 33.8833 | 35.4264 | 35.8658 | 33.7325 | 34.3849 | 34.4303 | 34.0404 | 34.5596 | 33.6561 | 34.4133 | 34.0872 | 34.5572 | 35.1756 | 36.0721 | 35.3222 | 35.4904 | 34.7099 | 93.5101 | 93.5681 | 93.3563
2022-09-08 00:02 | 2:12 | 17.0997 | 17.23 | 19.4207 | 35.1109 | 34.439 | 35.2177 | 35.9079 | 36.1303 | 36.9245 | 37.3131 | 36.7185 | 37.4403 | 33.8765 | 34.4458 | 35.6573 | 35.962 | 36.8526 | 37.0495 | 37.4108 | 37.5488 | 22.7151 | 17.5801 | 92.0731 | 33.3966 | 34.5097 | 35.8382 | 34.6946 | 34.2662 | 34.4545 | 35.702 | 34.946 | 34.8535 | 37.6155 | 36.4961 | 34.4611 | 34.8536 | 36.5309 | 37.1568 | 37.8028 | 36.5099 | 34.6559 | 33.8957 | 35.434 | 35.8701 | 33.7469 | 34.4131 | 34.433 | 34.0104 | 34.5483 | 33.6627 | 34.4082 | 34.0745 | 34.5596 | 35.1725 | 36.0816 | 35.3432 | 35.4741 | 34.6972 | 93.4395 | 93.443 | 93.2872
2022-09-08 00:02 | 2:12 | 17.1074 | 17.2388 | 19.4294 | 35.1159 | 34.4377 | 35.2272 | 35.903 | 36.1005 | 36.9424 | 37.3159 | 36.6878 | 37.4304 | 33.8611 | 34.4488 | 35.6574 | 35.9689 | 36.8367 | 37.0664 | 37.4154 | 37.5434 | 22.6803 | 17.592 | 92.1895 | 33.3235 | 34.507 | 35.8302 | 34.6814 | 34.2601 | 34.4757 | 35.7016 | 34.9373 | 34.8419 | 37.6098 | 36.5078 | 34.4502 | 34.8533 | 36.5039 | 37.1394 | 37.8235 | 36.5315 | 34.6542 | 33.8708 | 35.4268 | 35.8645 | 33.7164 | 34.394 | 34.4242 | 34.0062 | 34.5636 | 33.6358 | 34.4096 | 34.0904 | 34.5483 | 35.1728 | 36.08 | 35.3435 | 35.4492 | 34.6999 | 93.3511 | 93.3666 | 93.2613
2022-09-08 00:02 | 2:12 | 17.1212 | 17.2535 | 19.4222 | 35.1238 | 34.4175 | 35.2179 | 35.9096 | 36.1133 | 36.9415 | 37.2981 | 36.6922 | 37.4245 | 33.8394 | 34.4568 | 35.6606 | 35.9518 | 36.8235 | 37.052 | 37.3917 | 37.5525 | 22.685 | 17.587 | 92.2678 | 33.293 | 34.5016 | 35.85 | 34.6768 | 34.2653 | 34.4623 | 35.7103 | 34.9411 | 34.8259 | 37.6031 | 36.49 | 34.4371 | 34.8778 | 36.4961 | 37.1502 | 37.8119 | 36.5229 | 34.6553 | 33.8729 | 35.43 | 35.8704 | 33.7264 | 34.3927 | 34.4164 | 33.9958 | 34.568 | 33.639 | 34.4053 | 34.0744 | 34.5636 | 35.1848 | 36.0827 | 35.3509 | 35.4813 | 34.7047 | 93.3726 | 93.275 | 93.2429
2022-09-08 00:02 | 2:12 | 17.1251 | 17.2288 | 19.4042 | 35.1823 | 34.4455 | 35.2161 | 35.8994 | 36.1309 | 36.9481 | 37.3256 | 36.6835 | 37.4254 | 33.8457 | 34.4473 | 35.6257 | 35.9535 | 36.8589 | 37.0462 | 37.4031 | 37.5313 | 22.6557 | 17.5959 | 92.4241 | 33.3793 | 34.5164 | 35.8161 | 34.6599 | 34.2434 | 34.4342 | 35.6854 | 34.9329 | 34.8594 | 37.6075 | 36.5068 | 34.4436 | 34.8532 | 36.5078 | 37.1398 | 37.8116 | 36.5309 | 34.6286 | 33.8823 | 35.4059 | 35.8578 | 33.7405 | 34.4089 | 34.407 | 33.9894 | 34.5542 | 33.623 | 34.4288 | 34.0948 | 34.568 | 35.1797 | 36.0638 | 35.3353 | 35.4648 | 34.709 | 93.3054 | 93.346 | 93.2626
2022-09-08 00:02 | 2:12 | 17.1186 | 17.2731 | 19.4256 | 35.1685 | 34.4333 | 35.2026 | 35.9008 | 36.1144 | 36.9204 | 37.3049 | 36.6997 | 37.4359 | 33.867 | 34.4623 | 35.6328 | 35.9517 | 36.8371 | 37.0582 | 37.4122 | 37.5522 | 22.6475 | 17.6049 | 92.4631 | 33.3554 | 34.5147 | 35.8227 | 34.6559 | 34.243 | 34.4611 | 35.7159 | 34.9255 | 34.8601 | 37.6035 | 36.4962 | 34.4484 | 34.8244 | 36.49 | 37.1537 | 37.806 | 36.5039 | 34.644 | 33.8709 | 35.4087 | 35.8415 | 33.733 | 34.4066 | 34.4045 | 34.002 | 34.5784 | 33.6514 | 34.4007 | 34.0777 | 34.5542 | 35.1808 | 36.0881 | 35.3524 | 35.4655 | 34.6981 | 93.1881 | 93.23 | 93.145
2022-09-08 00:03 | 2:12 | 17.1264 | 17.2666 | 19.4428 | 35.0909 | 34.4184 | 35.1953 | 35.891 | 36.1019 | 36.935 | 37.3045 | 36.6938 | 37.413 | 33.841 | 34.4505 | 35.6317 | 35.9496 | 36.8271 | 37.0267 | 37.4 | 37.5561 | 22.6185 | 17.6145 | 92.5553 | 33.3423 | 34.4928 | 35.8199 | 34.6542 | 34.24 | 34.4502 | 35.6962 | 34.9073 | 34.8524 | 37.5761 | 36.4941 | 34.4374 | 34.8591 | 36.5068 | 37.137 | 37.8059 | 36.4961 | 34.6576 | 33.8577 | 35.4008 | 35.851 | 33.7098 | 34.4207 | 34.4054 | 33.9776 | 34.5839 | 33.6142 | 34.4162 | 34.0607 | 34.5784 | 35.1807 | 36.0587 | 35.3534 | 35.4806 | 34.6838 | 93.1504 | 93.0421 | 93.0866
2022-09-08 00:03 | 2:13 | 17.0935 | 17.2569 | 19.4662 | 35.1891 | 34.4355 | 35.2129 | 35.8972 | 36.1193 | 36.9332 | 37.3311 | 36.7003 | 37.4465 | 33.8311 | 34.4601 | 35.6179 | 35.9557 | 36.8294 | 37.0314 | 37.4 | 37.5492 | 22.5908 | 17.6186 | 92.6477 | 33.212 | 34.498 | 35.8197 | 34.6553 | 34.2481 | 34.4371 | 35.69 | 34.927 | 34.8403 | 37.5959 | 36.4703 | 34.4555 | 34.8415 | 36.4962 | 37.1318 | 37.8079 | 36.5078 | 34.659 | 33.8441 | 35.4038 | 35.8495 | 33.6954 | 34.409 | 34.399 | 33.9694 | 34.5676 | 33.634 | 34.4172 | 34.0713 | 34.5839 | 35.1806 | 36.0652 | 35.3511 | 35.4743 | 34.6682 | 93.0304 | 92.9672 | 93.0197
2022-09-08 00:03 | 2:13 | 17.0736 | 17.2124 | 19.423 | 35.1081 | 34.4332 | 35.2099 | 35.8973 | 36.0954 | 36.945 | 37.3248 | 36.6906 | 37.4295 | 33.8344 | 34.4486 | 35.628 | 35.9408 | 36.815 | 37.0356 | 37.3731 | 37.5452 | 22.5693 | 17.6185 | 92.6805 | 33.2549 | 34.4764 | 35.8093 | 34.6286 | 34.2448 | 34.4436 | 35.6892 | 34.9194 | 34.8292 | 37.6041 | 36.4922 | 34.4309 | 34.8401 | 36.4941 | 37.1237 | 37.7912 | 36.49 | 34.6232 | 33.8364 | 35.3908 | 35.8415 | 33.7001 | 34.411 | 34.4106 | 33.9664 | 34.5672 | 33.6037 | 34.4061 | 34.0555 | 34.5676 | 35.162 | 36.0476 | 35.3454 | 35.4587 | 34.6832 | 92.9383 | 92.9132 | 93.0398
2022-09-08 00:03 | 2:13 | 17.0847 | 17.2021 | 19.4339 | 35.228 | 34.4265 | 35.2009 | 35.9037 | 36.0932 | 36.9068 | 37.3153 | 36.6912 | 37.4229 | 33.8145 | 34.4761 | 35.6235 | 35.9443 | 36.8168 | 37.0312 | 37.3919 | 37.5343 | 22.5606 | 17.5963 | 92.7362 | 33.3268 | 34.464 | 35.7993 | 34.644 | 34.2464 | 34.4484 | 35.6995 | 34.9282 | 34.827 | 37.5993 | 36.5087 | 34.44 | 34.8314 | 36.4703 | 37.1088 | 37.7949 | 36.5068 | 34.6418 | 33.8402 | 35.3815 | 35.8323 | 33.6938 | 34.4179 | 34.3932 | 33.9715 | 34.5646 | 33.6205 | 34.4011 | 34.0706 | 34.5672 | 35.179 | 36.0564 | 35.3168 | 35.4545 | 34.6877 | 92.7694 | 92.7579 | 92.94
2022-09-08 00:03 | 2:13 | 17.055 | 17.191 | 19.427 | 35.0924 | 34.4158 | 35.1923 | 35.895 | 36.0989 | 36.9328 | 37.3079 | 36.7037 | 37.4136 | 33.8207 | 34.4657 | 35.6188 | 35.9397 | 36.8168 | 37.0344 | 37.3869 | 37.5346 | 22.5087 | 17.5634 | 92.8378 | 33.1658 | 34.4831 | 35.807 | 34.6576 | 34.2233 | 34.4374 | 35.6851 | 34.9179 | 34.8359 | 37.6048 | 36.48 | 34.4433 | 34.8455 | 36.4922 | 37.1258 | 37.8042 | 36.4962 | 34.6332 | 33.8432 | 35.3769 | 35.8177 | 33.6979 | 34.3964 | 34.4041 | 33.969 | 34.5722 | 33.6367 | 34.4159 | 34.0564 | 34.5646 | 35.1853 | 36.0423 | 35.3435 | 35.4655 | 34.6825 | 92.6345 | 92.7077 | 92.8874
2022-09-08 00:03 | 2:13 | 17.0457 | 17.1622 | 19.4045 | 35.1295 | 34.4145 | 35.1887 | 35.9072 | 36.0964 | 36.9306 | 37.289 | 36.696 | 37.4164 | 33.8041 | 34.469 | 35.6213 | 35.9259 | 36.8098 | 37.0316 | 37.4091 | 37.5536 | 22.4856 | 17.5749 | 92.9235 | 33.268 | 34.4739 | 35.7988 | 34.659 | 34.2347 | 34.4555 | 35.6771 | 34.9098 | 34.837 | 37.5771 | 36.4745 | 34.4273 | 34.8309 | 36.5087 | 37.1333 | 37.7998 | 36.4941 | 34.6324 | 33.8222 | 35.3805 | 35.8406 | 33.6775 | 34.4229 | 34.4192 | 33.9729 | 34.5739 | 33.6208 | 34.418 | 34.0604 | 34.5722 | 35.1683 | 36.0421 | 35.3515 | 35.4639 | 34.6758 | 92.5948 | 92.5688 | 92.7507
2022-09-08 00:04 | 2:13 | 17.1106 | 17.2379 | 19.3977 | 35.1649 | 34.4145 | 35.1842 | 35.8965 | 36.1012 | 36.9395 | 37.3218 | 36.6857 | 37.4209 | 33.803 | 34.4839 | 35.613 | 35.9495 | 36.8071 | 37.0241 | 37.3846 | 37.5404 | 22.4457 | 17.6022 | 93.0243 | 33.2126 | 34.4698 | 35.7873 | 34.6232 | 34.2322 | 34.4309 | 35.683 | 34.9439 | 34.8348 | 37.5756 | 36.4966 | 34.4391 | 34.8364 | 36.48 | 37.1323 | 37.8049 | 36.4703 | 34.6234 | 33.8254 | 35.3803 | 35.8067 | 33.6572 | 34.4296 | 34.4095 | 33.9661 | 34.5524 | 33.6153 | 34.4385 | 34.0494 | 34.5739 | 35.1845 | 36.049 | 35.3301 | 35.4677 | 34.678 | 92.4354 | 92.3773 | 92.6668
2022-09-08 00:04 | 2:14 | 17.1206 | 17.2877 | 19.4151 | 35.2027 | 34.4227 | 35.1716 | 35.8969 | 36.099 | 36.9144 | 37.3276 | 36.6994 | 37.428 | 33.795 | 34.4885 | 35.6118 | 35.9159 | 36.8081 | 37.0295 | 37.3856 | 37.5225 | 22.449 | 17.6161 | 93.0812 | 33.3011 | 34.4902 | 35.7882 | 34.6418 | 34.2377 | 34.44 | 35.6794 | 34.9189 | 34.8368 | 37.6069 | 36.4887 | 34.4386 | 34.8383 | 36.4745 | 37.1277 | 37.8008 | 36.4922 | 34.6204 | 33.805 | 35.379 | 35.8228 | 33.6616 | 34.4419 | 34.4173 | 33.9671 | 34.5728 | 33.6258 | 34.423 | 34.0534 | 34.5524 | 35.1686 | 36.0393 | 35.3292 | 35.4625 | 34.6489 | 92.2935 | 92.2937 | 92.5486
2022-09-08 00:04 | 2:14 | 17.1189 | 17.2292 | 19.4292 | 35.1452 | 34.4188 | 35.1675 | 35.8916 | 36.1021 | 36.9388 | 37.3349 | 36.6899 | 37.4374 | 33.8 | 34.4627 | 35.6037 | 35.9192 | 36.8096 | 37.0342 | 37.3805 | 37.5355 | 22.4171 | 17.6029 | 93.1418 | 33.313 | 34.4759 | 35.7851 | 34.6332 | 34.208 | 34.4433 | 35.6744 | 34.9213 | 34.8169 | 37.5736 | 36.4941 | 34.4282 | 34.8318 | 36.4966 | 37.1289 | 37.8029 | 36.5087 | 34.6066 | 33.813 | 35.3652 | 35.7911 | 33.6557 | 34.44 | 34.408 | 33.973 | 34.58 | 33.6272 | 34.4348 | 34.0662 | 34.5728 | 35.1689 | 36.0444 | 35.3626 | 35.4478 | 34.6509 | 92.132 | 92.1751 | 92.4923
2022-09-08 00:04 | 2:14 | 17.0534 | 17.1972 | 19.4125 | 35.1516 | 34.3866 | 35.1818 | 35.8935 | 36.0873 | 36.9257 | 37.3274 | 36.6906 | 37.4211 | 33.7831 | 34.4792 | 35.6206 | 35.9343 | 36.8138 | 37.0219 | 37.395 | 37.541 | 22.4069 | 17.5677 | 93.2362 | 33.2517 | 34.4587 | 35.7778 | 34.6324 | 34.2204 | 34.4273 | 35.6904 | 34.9177 | 34.8145 | 37.5991 | 36.4823 | 34.4145 | 34.829 | 36.4887 | 37.1048 | 37.7867 | 36.48 | 34.6123 | 33.7952 | 35.3448 | 35.8093 | 33.6581 | 34.4337 | 34.411 | 33.9632 | 34.5568 | 33.6036 | 34.426 | 34.0635 | 34.58 | 35.172 | 36.0401 | 35.36 | 35.4601 | 34.6402 | 91.9779 | 92.0091 | 92.3532
2022-09-08 00:04 | 2:14 | 17.0483 | 17.2243 | 19.3865 | 35.1698 | 34.4416 | 35.1753 | 35.8903 | 36.0914 | 36.9344 | 37.322 | 36.6848 | 37.4203 | 33.8024 | 34.484 | 35.5979 | 35.9305 | 36.8007 | 37.0271 | 37.3839 | 37.5284 | 22.3809 | 17.559 | 93.3231 | 33.0671 | 34.4505 | 35.7918 | 34.6234 | 34.2246 | 34.4391 | 35.6829 | 34.9243 | 34.8447 | 37.5895 | 36.469 | 34.4415 | 34.8408 | 36.4941 | 37.1129 | 37.7944 | 36.4745 | 34.6098 | 33.8097 | 35.3512 | 35.7985 | 33.6495 | 34.4416 | 34.3913 | 33.9607 | 34.5423 | 33.6083 | 34.422 | 34.0588 | 34.5568 | 35.1604 | 36.0514 | 35.3448 | 35.4554 | 34.6456 | 91.8731 | 91.8802 | 92.2829
2022-09-08 00:04 | 2:14 | 17.0697 | 17.215 | 19.3788 | 35.1741 | 34.4127 | 35.1537 | 35.8827 | 36.089 | 36.9412 | 37.3282 | 36.6906 | 37.4396 | 33.782 | 34.4718 | 35.6095 | 35.9326 | 36.8067 | 37.0219 | 37.4038 | 37.5416 | 22.3905 | 17.5819 | 93.367 | 33.2935 | 34.4651 | 35.7856 | 34.6204 | 34.2283 | 34.4386 | 35.6888 | 34.9053 | 34.8282 | 37.5776 | 36.472 | 34.4058 | 34.8244 | 36.4823 | 37.1223 | 37.7934 | 36.4966 | 34.6157 | 33.8053 | 35.3524 | 35.7808 | 33.6266 | 34.456 | 34.3945 | 33.9511 | 34.5566 | 33.6042 | 34.4314 | 34.0664 | 34.5423 | 35.1836 | 36.0196 | 35.3505 | 35.4496 | 34.6757 | 91.7136 | 91.736 | 92.2234
2022-09-08 00:05 | 2:15 | 17.1141 | 17.2495 | 19.4096 | 35.1408 | 34.4259 | 35.1731 | 35.8793 | 36.0992 | 36.9327 | 37.3362 | 36.6925 | 37.4344 | 33.7895 | 34.4673 | 35.6019 | 35.9242 | 36.8043 | 37.0202 | 37.3913 | 37.5402 | 22.3922 | 17.6305 | 93.4691 | 33.2752 | 34.472 | 35.7745 | 34.6066 | 34.2147 | 34.4282 | 35.7086 | 34.8981 | 34.8269 | 37.585 | 36.4774 | 34.4293 | 34.826 | 36.469 | 37.1131 | 37.8123 | 36.4887 | 34.6113 | 33.798 | 35.3391 | 35.7863 | 33.647 | 34.4223 | 34.3949 | 33.9623 | 34.5833 | 33.5831 | 34.4409 | 34.0617 | 34.5566 | 35.1678 | 36.029 | 35.334 | 35.4717 | 34.6524 | 91.6496 | 91.6319 | 92.1239
2022-09-08 00:05 | 2:15 | 17.075 | 17.2334 | 19.3987 | 35.1191 | 34.4147 | 35.1673 | 35.9095 | 36.0971 | 36.9346 | 37.3228 | 36.6984 | 37.4307 | 33.7784 | 34.5022 | 35.603 | 35.9365 | 36.8029 | 37.0028 | 37.4004 | 37.5297 | 22.375 | 17.5775 | 93.5049 | 33.2239 | 34.4498 | 35.7668 | 34.6123 | 34.2322 | 34.4145 | 35.6961 | 34.9128 | 34.8115 | 37.5877 | 36.4753 | 34.4212 | 34.8105 | 36.472 | 37.114 | 37.7992 | 36.4941 | 34.5988 | 33.7767 | 35.359 | 35.7795 | 33.6485 | 34.4529 | 34.401 | 33.9345 | 34.5597 | 33.5846 | 34.4174 | 34.0511 | 34.5833 | 35.1724 | 36.0425 | 35.3518 | 35.4607 | 34.6359 | 91.4922 | 91.569 | 92.0986
2022-09-08 00:05 | 2:15 | 17.086 | 17.2565 | 19.4143 | 35.1495 | 34.406 | 35.1528 | 35.8785 | 36.0957 | 36.9451 | 37.3358 | 36.6909 | 37.4421 | 33.7785 | 34.4804 | 35.6018 | 35.9372 | 36.7975 | 37.0173 | 37.3797 | 37.5377 | 22.3613 | 17.605 | 93.5892 | 33.1957 | 34.451 | 35.7627 | 34.6098 | 34.2216 | 34.4415 | 35.6788 | 34.8918 | 34.8296 | 37.578 | 36.4625 | 34.4177 | 34.8371 | 36.4774 | 37.1155 | 37.7961 | 36.4823 | 34.6017 | 33.7725 | 35.3254 | 35.7729 | 33.633 | 34.4382 | 34.3877 | 33.9486 | 34.5408 | 33.6028 | 34.4221 | 34.0418 | 34.5597 | 35.1792 | 36.0266 | 35.3631 | 35.4541 | 34.6446 | 91.5316 | 91.5909 | 92.2076
2022-09-08 00:05 | 2:15 | 17.1054 | 17.276 | 19.3873 | 35.1662 | 34.4066 | 35.1595 | 35.8979 | 36.0962 | 36.9414 | 37.3403 | 36.6898 | 37.4267 | 33.7857 | 34.4997 | 35.5864 | 35.9288 | 36.7965 | 37.0202 | 37.3759 | 37.5237 | 22.3879 | 17.6049 | 93.7545 | 33.2501 | 34.4647 | 35.7836 | 34.6157 | 34.221 | 34.4058 | 35.6811 | 34.928 | 34.8261 | 37.5739 | 36.4762 | 34.4093 | 34.8329 | 36.4753 | 37.1134 | 37.8017 | 36.469 | 34.615 | 33.7503 | 35.3359 | 35.7898 | 33.6278 | 34.4355 | 34.3966 | 33.9328 | 34.5539 | 33.5806 | 34.4384 | 34.0494 | 34.5408 | 35.1678 | 36.0402 | 35.3493 | 35.4633 | 34.6533 | 91.6841 | 91.7111 | 92.2733
2022-09-08 00:05 | 2:15 | 17.1284 | 17.2907 | 19.4045 | 35.1087 | 34.4136 | 35.1598 | 35.8782 | 36.0777 | 36.9396 | 37.3323 | 36.6978 | 37.4365 | 33.7541 | 34.4834 | 35.5878 | 35.9218 | 36.79 | 37.0045 | 37.389 | 37.532 | 22.3347 | 17.6361 | 93.7823 | 33.3971 | 34.4378 | 35.7542 | 34.6113 | 34.2123 | 34.4293 | 35.7012 | 34.9027 | 34.8088 | 37.5848 | 36.475 | 34.4 | 34.835 | 36.4625 | 37.1197 | 37.8066 | 36.472 | 34.6044 | 33.7713 | 35.325 | 35.7559 | 33.6072 | 34.4299 | 34.3931 | 33.9413 | 34.5292 | 33.5765 | 34.4187 | 34.0377 | 34.5539 | 35.1654 | 36.0306 | 35.344 | 35.4643 | 34.6192 | 91.8578 | 91.8152 | 92.325
2022-09-08 00:05 | 2:15 | 17.1669 | 17.317 | 19.438 | 35.1616 | 34.3965 | 35.1568 | 35.8957 | 36.0864 | 36.9144 | 37.3333 | 36.6889 | 37.4329 | 33.7831 | 34.5132 | 35.5887 | 35.912 | 36.8046 | 37.0038 | 37.3886 | 37.5249 | 22.3446 | 17.6551 | 93.9384 | 33.0603 | 34.4396 | 35.7532 | 34.5988 | 34.2092 | 34.4212 | 35.6836 | 34.9161 | 34.8213 | 37.583 | 36.474 | 34.4252 | 34.8119 | 36.4762 | 37.1247 | 37.8036 | 36.4774 | 34.5863 | 33.7679 | 35.3323 | 35.7398 | 33.6023 | 34.443 | 34.42 | 33.93 | 34.5408 | 33.5804 | 34.4511 | 34.0497 | 34.5292 | 35.1824 | 36.0251 | 35.3406 | 35.4814 | 34.6173 | 91.9148 | 91.9574 | 92.4222
2022-09-08 00:06 | 2:15 | 17.1197 | 17.2795 | 19.4146 | 35.1263 | 34.4198 | 35.1465 | 35.897 | 36.088 | 36.9451 | 37.3467 | 36.674 | 37.424 | 33.7693 | 34.4918 | 35.5746 | 35.9104 | 36.7895 | 37.0038 | 37.3898 | 37.5374 | 22.2986 | 17.6392 | 94.073 | 33.1554 | 34.4386 | 35.7597 | 34.6017 | 34.2128 | 34.4177 | 35.6846 | 34.9 | 34.8135 | 37.5756 | 36.4457 | 34.4001 | 34.829 | 36.475 | 37.1154 | 37.798 | 36.4753 | 34.5926 | 33.7586 | 35.3228 | 35.7679 | 33.6262 | 34.4311 | 34.3828 | 33.9153 | 34.5173 | 33.5701 | 34.4283 | 34.0535 | 34.5408 | 35.1572 | 36.0396 | 35.3422 | 35.4681 | 34.6404 | 91.9993 | 92.1002 | 92.4561
2022-09-08 00:06 | 2:16 | 17.1454 | 17.3038 | 19.4099 | 35.0983 | 34.4169 | 35.1402 | 35.8798 | 36.0979 | 36.9318 | 37.3421 | 36.6851 | 37.4325 | 33.7552 | 34.5001 | 35.5904 | 35.9204 | 36.7904 | 37.0051 | 37.357 | 37.5017 | 22.3006 | 17.6271 | 94.1577 | 33.1357 | 34.4425 | 35.7604 | 34.615 | 34.2152 | 34.4093 | 35.6897 | 34.8967 | 34.8044 | 37.5776 | 36.4746 | 34.4089 | 34.8234 | 36.474 | 37.102 | 37.7836 | 36.4625 | 34.5903 | 33.7398 | 35.3112 | 35.7446 | 33.6223 | 34.4389 | 34.3939 | 33.9237 | 34.5357 | 33.5886 | 34.4471 | 34.0325 | 34.5173 | 35.1695 | 36.0317 | 35.3677 | 35.4596 | 34.6349 | 92.2837 | 92.2616 | 92.5928
2022-09-08 00:06 | 2:16 | 17.1636 | 17.2968 | 19.4171 | 35.08 | 34.4241 | 35.1215 | 35.8941 | 36.0816 | 36.9387 | 37.3272 | 36.701 | 37.4284 | 33.7449 | 34.4813 | 35.5695 | 35.9178 | 36.7761 | 36.9983 | 37.3929 | 37.5164 | 22.2762 | 17.6232 | 94.2931 | 33.1165 | 34.4282 | 35.7469 | 34.6044 | 34.2171 | 34.4 | 35.685 | 34.8822 | 34.8076 | 37.5742 | 36.4603 | 34.3854 | 34.8215 | 36.4457 | 37.0971 | 37.7713 | 36.4762 | 34.5977 | 33.7375 | 35.301 | 35.7499 | 33.5987 | 34.4469 | 34.4055 | 33.9104 | 34.5425 | 33.5865 | 34.4458 | 34.0415 | 34.5357 | 35.1745 | 36.0104 | 35.3342 | 35.4651 | 34.6183 | 92.5 | 92.4496 | 92.7381
2022-09-08 00:06 | 2:16 | 17.153 | 17.3168 | 19.4218 | 35.1518 | 34.4261 | 35.146 | 35.8835 | 36.099 | 36.9412 | 37.34 | 36.6842 | 37.4504 | 33.7545 | 34.5003 | 35.5647 | 35.903 | 36.7667 | 37.0105 | 37.3908 | 37.5081 | 22.2723 | 17.6717 | 94.3414 | 33.2009 | 34.4287 | 35.7507 | 34.5863 | 34.2077 | 34.4252 | 35.684 | 34.8942 | 34.8177 | 37.5776 | 36.4656 | 34.4031 | 34.8228 | 36.4746 | 37.0943 | 37.7798 | 36.475 | 34.5727 | 33.7421 | 35.3097 | 35.7278 | 33.59 | 34.4404 | 34.3849 | 33.9051 | 34.5249 | 33.5683 | 34.4488 | 34.023 | 34.5425 | 35.1515 | 36.0196 | 35.3559 | 35.4739 | 34.5903 | 92.6212 | 92.5884 | 92.7946
2022-09-08 00:06 | 2:16 | 17.1646 | 17.3339 | 19.4211 | 35.1918 | 34.409 | 35.1288 | 35.8908 | 36.0866 | 36.925 | 37.3397 | 36.6822 | 37.4427 | 33.7684 | 34.5073 | 35.5709 | 35.9258 | 36.7715 | 36.9943 | 37.3679 | 37.5072 | 22.2626 | 17.6176 | 94.4019 | 33.369 | 34.4196 | 35.7412 | 34.5926 | 34.192 | 34.4001 | 35.6858 | 34.9002 | 34.8031 | 37.5706 | 36.4529 | 34.39 | 34.8125 | 36.4603 | 37.0954 | 37.7889 | 36.474 | 34.563 | 33.7415 | 35.2862 | 35.7245 | 33.6152 | 34.4671 | 34.4143 | 33.8902 | 34.5307 | 33.5789 | 34.4568 | 34.0268 | 34.5249 | 35.1701 | 36.0218 | 35.3478 | 35.469 | 34.5928 | 92.6867 | 92.8013 | 92.8957
2022-09-08 00:06 | 2:16 | 17.0873 | 17.2841 | 19.4027 | 35.1786 | 34.4133 | 35.1432 | 35.8927 | 36.056 | 36.9292 | 37.3197 | 36.6767 | 37.4198 | 33.7404 | 34.4845 | 35.5555 | 35.8983 | 36.7816 | 36.9906 | 37.381 | 37.5027 | 22.2553 | 17.5669 | 94.4253 | 33.2444 | 34.4109 | 35.7393 | 34.5903 | 34.1786 | 34.4089 | 35.6681 | 34.9179 | 34.8022 | 37.5631 | 36.4743 | 34.3905 | 34.8119 | 36.4656 | 37.1 | 37.7592 | 36.4457 | 34.5779 | 33.7422 | 35.282 | 35.7239 | 33.568 | 34.4465 | 34.3972 | 33.8694 | 34.5005 | 33.5499 | 34.4473 | 34.0454 | 34.5307 | 35.1486 | 36.0098 | 35.3612 | 35.4758 | 34.6037 | 92.8411 | 92.9368 | 93.0179
2022-09-08 00:07 | 2:17 | 17.0508 | 17.2105 | 19.3591 | 35.121 | 34.4082 | 35.1216 | 35.8989 | 36.0783 | 36.9154 | 37.3167 | 36.6906 | 37.4373 | 33.73 | 34.524 | 35.5659 | 35.9233 | 36.7485 | 36.9959 | 37.361 | 37.5051 | 22.2315 | 17.4781 | 94.3914 | 33.142 | 34.3854 | 35.7314 | 34.5977 | 34.1946 | 34.3854 | 35.6796 | 34.8883 | 34.8077 | 37.5598 | 36.4305 | 34.3926 | 34.82 | 36.4529 | 37.0908 | 37.7782 | 36.4746 | 34.5847 | 33.7273 | 35.294 | 35.7408 | 33.5788 | 34.465 | 34.3841 | 33.8745 | 34.5194 | 33.5494 | 34.4623 | 34.021 | 34.5005 | 35.1543 | 36.0128 | 35.349 | 35.4525 | 34.5812 | 93.0575 | 93.1798 | 93.108
2022-09-08 00:07 | 2:17 | 17.0479 | 17.2228 | 19.3183 | 35.1541 | 34.4096 | 35.1087 | 35.8916 | 36.0896 | 36.9014 | 37.3347 | 36.6903 | 37.4141 | 33.7297 | 34.5103 | 35.5331 | 35.9156 | 36.7575 | 36.9813 | 37.3392 | 37.4978 | 22.2249 | 17.4604 | 94.1946 | 33.0833 | 34.3886 | 35.7457 | 34.5727 | 34.1923 | 34.4031 | 35.6632 | 34.8921 | 34.8069 | 37.5774 | 36.448 | 34.3765 | 34.8124 | 36.4743 | 37.074 | 37.7821 | 36.4603 | 34.5679 | 33.7165 | 35.2826 | 35.6975 | 33.5577 | 34.471 | 34.3941 | 33.8866 | 34.5104 | 33.5609 | 34.4505 | 34.0224 | 34.5194 | 35.1513 | 36.0223 | 35.3606 | 35.4616 | 34.5729 | 93.3024 | 93.2557 | 93.1397
2022-09-08 00:07 | 2:17 | 17.029 | 17.182 | 19.3338 | 35.1097 | 34.4053 | 35.1061 | 35.8885 | 36.0812 | 36.909 | 37.2936 | 36.6771 | 37.4364 | 33.733 | 34.5049 | 35.5389 | 35.8964 | 36.7495 | 36.978 | 37.3548 | 37.483 | 22.2426 | 17.4838 | 94.0139 | 33.1968 | 34.3886 | 35.7084 | 34.563 | 34.1999 | 34.39 | 35.6604 | 34.8733 | 34.7917 | 37.5524 | 36.4699 | 34.3821 | 34.7966 | 36.4305 | 37.0877 | 37.7538 | 36.4656 | 34.5624 | 33.7146 | 35.275 | 35.7121 | 33.5733 | 34.4436 | 34.4037 | 33.8879 | 34.4991 | 33.586 | 34.4601 | 34.0116 | 34.5104 | 35.1341 | 36.02 | 35.3538 | 35.4511 | 34.5542 | 93.5208 | 93.4438 | 93.3431
2022-09-08 00:07 | 2:17 | 17.0029 | 17.1704 | 19.3165 | 35.1263 | 34.4288 | 35.1183 | 35.9052 | 36.0832 | 36.9233 | 37.3165 | 36.6788 | 37.4271 | 33.7118 | 34.4975 | 35.5311 | 35.9032 | 36.7578 | 36.9887 | 37.356 | 37.5022 | 22.2555 | 17.3866 | 93.8991 | 33.1619 | 34.4076 | 35.7411 | 34.5779 | 34.1826 | 34.3905 | 35.6486 | 34.8774 | 34.7979 | 37.5572 | 36.4628 | 34.3876 | 34.8111 | 36.448 | 37.0897 | 37.7584 | 36.4529 | 34.5701 | 33.6841 | 35.2582 | 35.6915 | 33.5518 | 34.4717 | 34.3853 | 33.8627 | 34.4986 | 33.5509 | 34.4486 | 34.0288 | 34.4991 | 35.1488 | 36.0266 | 35.364 | 35.4278 | 34.5571 | 93.6987 | 93.5893 | 93.3931
2022-09-08 00:07 | 2:17 | 16.9723 | 17.1534 | 19.3141 | 35.1229 | 34.4007 | 35.0968 | 35.8934 | 36.0806 | 36.9003 | 37.3248 | 36.692 | 37.438 | 33.7123 | 34.4876 | 35.5356 | 35.9064 | 36.7474 | 36.9631 | 37.3465 | 37.4857 | 22.2873 | 17.3863 | 93.8452 | 33.1949 | 34.3847 | 35.7218 | 34.5847 | 34.1814 | 34.3926 | 35.6749 | 34.8848 | 34.7842 | 37.5503 | 36.4522 | 34.3635 | 34.8183 | 36.4699 | 37.0827 | 37.7697 | 36.4743 | 34.5572 | 33.6799 | 35.279 | 35.6813 | 33.5817 | 34.4547 | 34.3991 | 33.8732 | 34.5005 | 33.5628 | 34.4761 | 34.0139 | 34.4986 | 35.1221 | 35.994 | 35.3469 | 35.4746 | 34.5366 | 93.8677 | 93.8091 | 93.5616
2022-09-08 00:07 | 2:17 | 17.0902 | 17.2062 | 19.31 | 35.176 | 34.4162 | 35.0977 | 35.8947 | 36.0716 | 36.9089 | 37.3295 | 36.6753 | 37.4296 | 33.714 | 34.5055 | 35.5416 | 35.908 | 36.7463 | 36.9736 | 37.345 | 37.4917 | 22.3166 | 17.4892 | 93.8422 | 33.2753 | 34.3604 | 35.724 | 34.5679 | 34.1697 | 34.3765 | 35.654 | 34.8863 | 34.8108 | 37.5427 | 36.4473 | 34.3812 | 34.8192 | 36.4628 | 37.0722 | 37.767 | 36.4305 | 34.5539 | 33.6826 | 35.2454 | 35.6605 | 33.5514 | 34.459 | 34.3877 | 33.8536 | 34.4877 | 33.5421 | 34.4657 | 34.0084 | 34.5005 | 35.123 | 36.015 | 35.3513 | 35.4534 | 34.5337 | 93.9415 | 93.972 | 93.6596
2022-09-08 00:08 | 2:18 | 17.0943 | 17.284 | 19.3525 | 35.156 | 34.4172 | 35.0907 | 35.8854 | 36.0669 | 36.9339 | 37.3033 | 36.6992 | 37.4508 | 33.7025 | 34.5152 | 35.522 | 35.8935 | 36.7488 | 36.9652 | 37.3656 | 37.4854 | 22.3424 | 17.5452 | 93.8229 | 33.1827 | 34.3654 | 35.7315 | 34.5624 | 34.1876 | 34.3821 | 35.6445 | 34.8818 | 34.7927 | 37.5478 | 36.4581 | 34.3892 | 34.805 | 36.4522 | 37.0769 | 37.7591 | 36.448 | 34.5632 | 33.7082 | 35.2493 | 35.6681 | 33.5455 | 34.4436 | 34.3896 | 33.8702 | 34.4942 | 33.5529 | 34.469 | 34.0048 | 34.4877 | 35.1378 | 36.0176 | 35.3503 | 35.4416 | 34.5376 | 94.0665 | 94.1766 | 93.7485
2022-09-08 00:08 | 2:18 | 17.1159 | 17.2935 | 19.3781 | 35.1385 | 34.4061 | 35.1074 | 35.8967 | 36.0681 | 36.9209 | 37.3255 | 36.6824 | 37.4325 | 33.7076 | 34.511 | 35.5116 | 35.8835 | 36.7433 | 36.9537 | 37.3356 | 37.4719 | 22.3671 | 17.5436 | 93.8094 | 33.1142 | 34.3681 | 35.7239 | 34.5701 | 34.1802 | 34.3876 | 35.6519 | 34.893 | 34.8079 | 37.5706 | 36.4662 | 34.3817 | 34.8091 | 36.4473 | 37.0754 | 37.7576 | 36.4699 | 34.5612 | 33.6777 | 35.2507 | 35.6705 | 33.5432 | 34.4778 | 34.3913 | 33.8552 | 34.4987 | 33.5536 | 34.4839 | 33.9885 | 34.4942 | 35.1341 | 36.0066 | 35.3471 | 35.4565 | 34.5288 | 94.1938 | 94.3721 | 93.8433
2022-09-08 00:08 | 2:18 | 17.0622 | 17.2604 | 19.3547 | 35.1203 | 34.4011 | 35.1022 | 35.8984 | 36.0835 | 36.9152 | 37.3117 | 36.6953 | 37.4423 | 33.7059 | 34.4948 | 35.5202 | 35.8929 | 36.7438 | 36.9683 | 37.3453 | 37.4832 | 22.3829 | 17.4847 | 93.7442 | 33.1876 | 34.3375 | 35.7324 | 34.5572 | 34.172 | 34.3635 | 35.6534 | 34.9002 | 34.8116 | 37.545 | 36.4572 | 34.3877 | 34.797 | 36.4581 | 37.0802 | 37.7468 | 36.4628 | 34.548 | 33.6724 | 35.2396 | 35.6539 | 33.5187 | 34.48 | 34.3937 | 33.8399 | 34.4771 | 33.5385 | 34.4885 | 33.9972 | 34.4987 | 35.1441 | 35.9961 | 35.36 | 35.4519 | 34.5259 | 94.4198 | 94.528 | 93.9343
2022-09-08 00:08 | 2:18 | 17.0241 | 17.2075 | 19.3289 | 35.1717 | 34.4159 | 35.0982 | 35.8835 | 36.0725 | 36.918 | 37.3153 | 36.7089 | 37.4319 | 33.6956 | 34.5159 | 35.5147 | 35.8965 | 36.72 | 36.9751 | 37.3407 | 37.4806 | 22.3856 | 17.4772 | 93.7441 | 33.2571 | 34.3722 | 35.7289 | 34.5539 | 34.1849 | 34.3812 | 35.6541 | 34.8867 | 34.8021 | 37.5575 | 36.4551 | 34.3711 | 34.8141 | 36.4662 | 37.0691 | 37.7499 | 36.4522 | 34.5606 | 33.6755 | 35.2274 | 35.6537 | 33.5583 | 34.4678 | 34.382 | 33.8582 | 34.4866 | 33.5461 | 34.4627 | 33.995 | 34.4771 | 35.1335 | 35.9975 | 35.3658 | 35.4413 | 34.5344 | 94.5808 | 94.6239 | 94.0711
2022-09-08 00:08 | 2:18 | 17.0499 | 17.1865 | 19.3099 | 35.1747 | 34.418 | 35.1029 | 35.8824 | 36.0608 | 36.924 | 37.3122 | 36.7023 | 37.4345 | 33.7053 | 34.5105 | 35.5126 | 35.8953 | 36.7492 | 36.9564 | 37.3307 | 37.4742 | 22.3645 | 17.4607 | 93.699 | 33.2419 | 34.3503 | 35.7159 | 34.5632 | 34.1691 | 34.3892 | 35.6478 | 34.8864 | 34.7944 | 37.5504 | 36.4416 | 34.3711 | 34.8055 | 36.4572 | 37.0799 | 37.7193 | 36.4473 | 34.5525 | 33.6649 | 35.2378 | 35.645 | 33.535 | 34.486 | 34.3771 | 33.8558 | 34.4769 | 33.5575 | 34.4792 | 33.9973 | 34.4866 | 35.1325 | 36.0108 | 35.3659 | 35.4481 | 34.5278 | 94.6009 | 94.7479 | 94.0332
2022-09-08 00:08 | 2:18 | 17.0447 | 17.1896 | 19.3634 | 35.1156 | 34.4385 | 35.0831 | 35.8904 | 36.0577 | 36.9145 | 37.303 | 36.6949 | 37.4396 | 33.6833 | 34.5205 | 35.4989 | 35.8859 | 36.7344 | 36.9427 | 37.3228 | 37.4915 | 22.3652 | 17.4551 | 93.627 | 33.255 | 34.3488 | 35.7139 | 34.5612 | 34.1606 | 34.3817 | 35.6432 | 34.9116 | 34.7899 | 37.5392 | 36.4518 | 34.375 | 34.8288 | 36.4551 | 37.0667 | 37.7382 | 36.4581 | 34.5641 | 33.6572 | 35.2177 | 35.6392 | 33.5245 | 34.4632 | 34.411 | 33.8361 | 34.4737 | 33.5421 | 34.484 | 34.0063 | 34.4769 | 35.1095 | 35.9999 | 35.3823 | 35.4528 | 34.5095 | 94.7514 | 94.8469 | 94.016
2022-09-08 00:09 | 2:18 | 17.0272 | 17.1929 | 19.3134 | 35.07 | 34.423 | 35.1071 | 35.9061 | 36.0481 | 36.8872 | 37.3176 | 36.7063 | 37.4261 | 33.6666 | 34.524 | 35.5063 | 35.889 | 36.7482 | 36.9706 | 37.333 | 37.4605 | 22.3567 | 17.4288 | 93.5631 | 33.1598 | 34.3497 | 35.7231 | 34.548 | 34.1673 | 34.3877 | 35.6609 | 34.9006 | 34.8104 | 37.5523 | 36.4534 | 34.3626 | 34.8089 | 36.4416 | 37.0627 | 37.7561 | 36.4662 | 34.5719 | 33.6578 | 35.2293 | 35.642 | 33.5323 | 34.4693 | 34.3903 | 33.8449 | 34.4859 | 33.539 | 34.4718 | 33.9935 | 34.4737 | 35.141 | 35.9898 | 35.3488 | 35.4444 | 34.5122 | 94.858 | 94.9028 | 94.1958
2022-09-08 00:09 | 2:19 | 16.9658 | 17.1332 | 19.3079 | 35.0797 | 34.4348 | 35.0969 | 35.8896 | 36.0699 | 36.9014 | 37.3258 | 36.7002 | 37.4514 | 33.668 | 34.5166 | 35.4898 | 35.8944 | 36.7222 | 36.9628 | 37.3382 | 37.4731 | 22.3397 | 17.3967 | 93.5702 | 33.1965 | 34.3482 | 35.708 | 34.5606 | 34.1541 | 34.3711 | 35.6341 | 34.8877 | 34.7985 | 37.5597 | 36.4506 | 34.3777 | 34.8043 | 36.4518 | 37.0686 | 37.7521 | 36.4572 | 34.5503 | 33.6491 | 35.2278 | 35.6513 | 33.5441 | 34.499 | 34.3847 | 33.8564 | 34.4734 | 33.5207 | 34.4673 | 34.0126 | 34.4859 | 35.1545 | 36.0141 | 35.347 | 35.458 | 34.4994 | 94.8219 | 95.0689 | 94.2691
2022-09-08 00:09 | 2:19 | 16.9592 | 17.1134 | 19.3134 | 35.1735 | 34.426 | 35.1036 | 35.9049 | 36.0723 | 36.9159 | 37.3246 | 36.698 | 37.4668 | 33.6786 | 34.5186 | 35.4909 | 35.8922 | 36.7245 | 36.9669 | 37.3308 | 37.4665 | 22.3241 | 17.3757 | 93.5754 | 33.1331 | 34.3298 | 35.7079 | 34.5525 | 34.166 | 34.3711 | 35.6396 | 34.905 | 34.8063 | 37.5546 | 36.4417 | 34.3626 | 34.8032 | 36.4534 | 37.0711 | 37.7529 | 36.4551 | 34.5441 | 33.6494 | 35.2307 | 35.6419 | 33.5195 | 34.49 | 34.3867 | 33.8321 | 34.4576 | 33.5296 | 34.5022 | 33.9833 | 34.4734 | 35.1277 | 36.0055 | 35.3413 | 35.4404 | 34.4962 | 94.8135 | 95.1323 | 94.3263
2022-09-08 00:09 | 2:19 | 16.9907 | 17.1455 | 19.2982 | 35.0808 | 34.422 | 35.0862 | 35.9002 | 36.0649 | 36.902 | 37.3176 | 36.715 | 37.4407 | 33.6824 | 34.5311 | 35.4802 | 35.9092 | 36.724 | 36.9597 | 37.3357 | 37.4546 | 22.317 | 17.4046 | 93.4506 | 33.1654 | 34.3215 | 35.7338 | 34.5641 | 34.1541 | 34.375 | 35.6487 | 34.9079 | 34.7977 | 37.5551 | 36.4346 | 34.3654 | 34.8347 | 36.4506 | 37.0618 | 37.7524 | 36.4416 | 34.5636 | 33.6689 | 35.194 | 35.6426 | 33.5273 | 34.4802 | 34.3794 | 33.8137 | 34.4557 | 33.5498 | 34.4804 | 33.9984 | 34.4576 | 35.1215 | 36 | 35.3549 | 35.4395 | 34.5116 | 94.8882 | 95.1222 | 94.3255
2022-09-08 00:09 | 2:19 | 17.017 | 17.1449 | 19.2663 | 35.0885 | 34.4314 | 35.0816 | 35.9151 | 36.0821 | 36.8944 | 37.3417 | 36.7134 | 37.4595 | 33.6679 | 34.529 | 35.4903 | 35.8989 | 36.7584 | 36.9771 | 37.3337 | 37.4677 | 22.3307 | 17.4396 | 93.356 | 33.0547 | 34.3628 | 35.7097 | 34.5719 | 34.182 | 34.3626 | 35.6352 | 34.915 | 34.8033 | 37.5521 | 36.4448 | 34.3683 | 34.8137 | 36.4417 | 37.081 | 37.733 | 36.4518 | 34.5573 | 33.6505 | 35.2243 | 35.6456 | 33.5367 | 34.4823 | 34.3867 | 33.8239 | 34.4537 | 33.5426 | 34.4997 | 34.0007 | 34.4557 | 35.1537 | 36.0087 | 35.3813 | 35.4458 | 34.4991 | 94.7575 | 94.954 | 94.1087
2022-09-08 00:09 | 2:19 | 16.9997 | 17.183 | 19.3212 | 35.171 | 34.4409 | 35.0778 | 35.9117 | 36.0624 | 36.912 | 37.3367 | 36.7164 | 37.4486 | 33.6886 | 34.515 | 35.498 | 35.8874 | 36.7459 | 36.9445 | 37.3423 | 37.4751 | 22.3246 | 17.389 | 93.3201 | 33.1627 | 34.3396 | 35.7123 | 34.5503 | 34.1631 | 34.3777 | 35.639 | 34.9131 | 34.8102 | 37.5587 | 36.4445 | 34.354 | 34.8253 | 36.4346 | 37.0758 | 37.7307 | 36.4534 | 34.5535 | 33.6425 | 35.2009 | 35.6405 | 33.5202 | 34.4894 | 34.3824 | 33.8207 | 34.428 | 33.5428 | 34.4834 | 33.9984 | 34.4537 | 35.1515 | 36.0008 | 35.3649 | 35.4517 | 34.5194 | 94.5667 | 94.7082 | 93.9532
2022-09-08 00:10 | 2:20 | 16.988 | 17.1513 | 19.2901 | 35.0545 | 34.4174 | 35.0889 | 35.9088 | 36.0671 | 36.9156 | 37.3602 | 36.7165 | 37.4416 | 33.6745 | 34.5234 | 35.4852 | 35.891 | 36.7636 | 36.9579 | 37.3279 | 37.4864 | 22.3441 | 17.3998 | 93.3063 | 33.0212 | 34.3365 | 35.6944 | 34.5441 | 34.1436 | 34.3626 | 35.6297 | 34.9062 | 34.7863 | 37.5543 | 36.4321 | 34.3426 | 34.8338 | 36.4448 | 37.0662 | 37.7298 | 36.4506 | 34.55 | 33.6338 | 35.1968 | 35.6342 | 33.5131 | 34.4669 | 34.369 | 33.815 | 34.4265 | 33.5532 | 34.5132 | 33.9983 | 34.428 | 35.1453 | 35.9983 | 35.3659 | 35.4797 | 34.5045 | 94.3122 | 94.4691 | 93.7904
2022-09-08 00:10 | 2:20 | 16.9746 | 17.12 | 19.2853 | 35.1521 | 34.4221 | 35.0843 | 35.899 | 36.0659 | 36.9025 | 37.3325 | 36.7218 | 37.4554 | 33.6538 | 34.5235 | 35.4893 | 35.8778 | 36.7273 | 36.9734 | 37.3302 | 37.4727 | 22.3353 | 17.3888 | 93.1742 | 33.2359 | 34.3307 | 35.6905 | 34.5636 | 34.1484 | 34.3654 | 35.6597 | 34.9023 | 34.8069 | 37.5561 | 36.4609 | 34.3554 | 34.8285 | 36.4445 | 37.0714 | 37.738 | 36.4417 | 34.5564 | 33.6411 | 35.1982 | 35.6484 | 33.5103 | 34.4876 | 34.3826 | 33.8162 | 34.4303 | 33.5185 | 34.4918 | 33.9921 | 34.4265 | 35.164 | 35.999 | 35.3698 | 35.4422 | 34.5175 | 94.0324 | 94.1181 | 93.653
2022-09-08 00:10 | 2:20 | 16.955 | 17.1254 | 19.2806 | 35.1083 | 34.4384 | 35.0727 | 35.9168 | 36.0775 | 36.9274 | 37.3308 | 36.7269 | 37.4545 | 33.673 | 34.5212 | 35.4773 | 35.8918 | 36.7506 | 36.9858 | 37.3468 | 37.4591 | 22.3108 | 17.304 | 93.1663 | 33.1412 | 34.3097 | 35.7078 | 34.5573 | 34.1676 | 34.3683 | 35.6513 | 34.91 | 34.808 | 37.5664 | 36.4682 | 34.3533 | 34.813 | 36.4321 | 37.0705 | 37.7398 | 36.4346 | 34.5368 | 33.6217 | 35.2028 | 35.635 | 33.4943 | 34.4797 | 34.3901 | 33.8059 | 34.433 | 33.539 | 34.5001 | 33.9995 | 34.4303 | 35.1391 | 36.0104 | 35.3481 | 35.4576 | 34.4915 | 93.8833 | 93.9254 | 93.5693
2022-09-08 00:10 | 2:20 | 16.9036 | 17.0797 | 19.2622 | 35.206 | 34.4187 | 35.0879 | 35.9086 | 36.0732 | 36.9151 | 37.3317 | 36.7332 | 37.4646 | 33.652 | 34.5264 | 35.4902 | 35.8983 | 36.7413 | 36.9694 | 37.3308 | 37.4605 | 22.2878 | 17.3337 | 93.0634 | 33.1073 | 34.3106 | 35.6958 | 34.5535 | 34.1596 | 34.354 | 35.6294 | 34.9173 | 34.812 | 37.5557 | 36.4315 | 34.3431 | 34.821 | 36.4609 | 37.0697 | 37.7519 | 36.4448 | 34.5454 | 33.6324 | 35.2076 | 35.6243 | 33.4988 | 34.4893 | 34.3802 | 33.8221 | 34.4242 | 33.5244 | 34.4813 | 33.9847 | 34.433 | 35.1511 | 35.9973 | 35.3651 | 35.4652 | 34.5059 | 93.7566 | 93.8229 | 93.4857
2022-09-08 00:10 | 2:20 | 16.9196 | 17.0747 | 19.2657 | 35.1427 | 34.4511 | 35.0887 | 35.9077 | 36.0827 | 36.906 | 37.3432 | 36.7276 | 37.4722 | 33.6649 | 34.532 | 35.4816 | 35.9065 | 36.7214 | 36.9703 | 37.3404 | 37.4719 | 22.2846 | 17.3067 | 92.9204 | 33.2148 | 34.3235 | 35.7177 | 34.55 | 34.1572 | 34.3426 | 35.6308 | 34.8983 | 34.798 | 37.5588 | 36.4514 | 34.3517 | 34.8378 | 36.4682 | 37.0593 | 37.7297 | 36.4445 | 34.545 | 33.6267 | 35.1983 | 35.6306 | 33.4943 | 34.4851 | 34.3905 | 33.8195 | 34.4164 | 33.5293 | 34.5003 | 33.9883 | 34.4242 | 35.1796 | 35.9952 | 35.3928 | 35.4422 | 34.5025 | 93.6033 | 93.7382 | 93.3643
2022-09-08 00:10 | 2:20 | 16.9023 | 17.0343 | 19.2786 | 35.0734 | 34.4283 | 35.0685 | 35.898 | 36.087 | 36.9137 | 37.3309 | 36.7209 | 37.4725 | 33.6557 | 34.5422 | 35.4676 | 35.8863 | 36.7376 | 36.9778 | 37.3304 | 37.4688 | 22.3016 | 17.2915 | 92.846 | 33.2072 | 34.3035 | 35.7046 | 34.5564 | 34.1595 | 34.3554 | 35.6343 | 34.9407 | 34.806 | 37.5544 | 36.4416 | 34.369 | 34.8232 | 36.4315 | 37.0616 | 37.7522 | 36.4321 | 34.534 | 33.6185 | 35.187 | 35.6233 | 33.5007 | 34.4894 | 34.3869 | 33.8136 | 34.407 | 33.515 | 34.5073 | 33.9993 | 34.4164 | 35.1515 | 35.9798 | 35.3752 | 35.4519 | 34.4991 | 93.4576 | 93.6165 | 93.2571
2022-09-08 00:11 | 2:20 | 16.869 | 17.0361 | 19.232 | 35.0686 | 34.4471 | 35.0676 | 35.9019 | 36.0535 | 36.915 | 37.3477 | 36.7292 | 37.4837 | 33.681 | 34.5447 | 35.4615 | 35.9134 | 36.7309 | 36.9892 | 37.3227 | 37.4745 | 22.2958 | 17.259 | 92.7553 | 33.2636 | 34.3143 | 35.7027 | 34.5368 | 34.1659 | 34.3533 | 35.6457 | 34.9077 | 34.8071 | 37.5742 | 36.428 | 34.333 | 34.8069 | 36.4514 | 37.0652 | 37.7555 | 36.4609 | 34.5346 | 33.6091 | 35.191 | 35.6281 | 33.4844 | 34.4819 | 34.3754 | 33.808 | 34.4045 | 33.5232 | 34.4845 | 33.9912 | 34.407 | 35.1463 | 35.9756 | 35.3866 | 35.4695 | 34.4991 | 93.4154 | 93.5575 | 93.2602
2022-09-08 00:11 | 2:21 | 16.8082 | 16.9623 | 19.2498 | 35.0678 | 34.4458 | 35.0795 | 35.9158 | 36.0848 | 36.9166 | 37.3293 | 36.737 | 37.4817 | 33.6488 | 34.5512 | 35.4664 | 35.8946 | 36.7304 | 36.9748 | 37.3232 | 37.475 | 22.2834 | 17.2108 | 92.6571 | 33.1666 | 34.2978 | 35.6756 | 34.5454 | 34.1603 | 34.3431 | 35.638 | 34.9256 | 34.7992 | 37.5645 | 36.4215 | 34.3274 | 34.8291 | 36.4416 | 37.0578 | 37.7433 | 36.4682 | 34.5444 | 33.612 | 35.1913 | 35.6225 | 33.4693 | 34.5033 | 34.3833 | 33.7973 | 34.4054 | 33.5108 | 34.524 | 33.9659 | 34.4045 | 35.1656 | 35.9676 | 35.3798 | 35.4738 | 34.5002 | 93.3559 | 93.4737 | 93.2133
2022-09-08 00:11 | 2:21 | 16.7667 | 16.9238 | 19.2068 | 35.1208 | 34.4488 | 35.0451 | 35.9064 | 36.0568 | 36.9241 | 37.3446 | 36.7118 | 37.4721 | 33.656 | 34.5315 | 35.4719 | 35.9001 | 36.7499 | 36.9732 | 37.3254 | 37.4782 | 22.2598 | 17.1852 | 92.5802 | 33.1324 | 34.3127 | 35.7021 | 34.545 | 34.1575 | 34.3517 | 35.6179 | 34.9158 | 34.8115 | 37.5564 | 36.4429 | 34.332 | 34.8448 | 36.428 | 37.0603 | 37.7488 | 36.4315 | 34.5161 | 33.5978 | 35.1843 | 35.6201 | 33.4638 | 34.5032 | 34.3724 | 33.7969 | 34.399 | 33.5326 | 34.5103 | 33.9773 | 34.4054 | 35.1716 | 35.983 | 35.3885 | 35.4604 | 34.4753 | 93.3102 | 93.4294 | 93.2863
2022-09-08 00:11 | 2:21 | 16.7722 | 16.9306 | 19.1598 | 35.0596 | 34.4568 | 35.0512 | 35.907 | 36.0633 | 36.9374 | 37.3475 | 36.7213 | 37.4703 | 33.6518 | 34.5338 | 35.4639 | 35.8866 | 36.7308 | 36.9663 | 37.3417 | 37.4668 | 22.2602 | 17.1953 | 92.3418 | 33.183 | 34.2963 | 35.6965 | 34.534 | 34.1504 | 34.369 | 35.6271 | 34.8965 | 34.819 | 37.5623 | 36.4393 | 34.3288 | 34.8341 | 36.4215 | 37.074 | 37.7414 | 36.4514 | 34.5311 | 33.6222 | 35.1865 | 35.6132 | 33.4469 | 34.5095 | 34.3781 | 33.7974 | 34.4106 | 33.5038 | 34.5049 | 33.99 | 34.399 | 35.1645 | 35.9856 | 35.3627 | 35.4744 | 34.4999 | 93.2947 | 93.4132 | 93.2483
2022-09-08 00:11 | 2:21 | 16.7832 | 16.9194 | 19.1846 | 35.1655 | 34.4473 | 35.0704 | 35.916 | 36.0721 | 36.9207 | 37.3484 | 36.714 | 37.4934 | 33.6353 | 34.5333 | 35.4802 | 35.8872 | 36.7455 | 36.966 | 37.3479 | 37.4707 | 22.252 | 17.1727 | 92.1537 | 33.1962 | 34.3024 | 35.6908 | 34.5346 | 34.142 | 34.333 | 35.634 | 34.9018 | 34.7902 | 37.5504 | 36.4568 | 34.3422 | 34.8195 | 36.4429 | 37.0611 | 37.7443 | 36.4416 | 34.5449 | 33.594 | 35.1907 | 35.6215 | 33.4484 | 34.4768 | 34.3773 | 33.789 | 34.3932 | 33.4986 | 34.4975 | 33.9841 | 34.4106 | 35.152 | 35.9863 | 35.3811 | 35.4539 | 34.4723 | 93.2423 | 93.425 | 93.1696
2022-09-08 00:11 | 2:21 | 16.7647 | 16.8965 | 19.1477 | 35.0505 | 34.4623 | 35.0563 | 35.9134 | 36.0734 | 36.917 | 37.3439 | 36.7267 | 37.4833 | 33.6267 | 34.538 | 35.4627 | 35.8893 | 36.7497 | 36.9603 | 37.3402 | 37.4668 | 22.2782 | 17.1715 | 92.0448 | 33.3174 | 34.3068 | 35.6915 | 34.5444 | 34.1448 | 34.3274 | 35.6351 | 34.9214 | 34.8111 | 37.5672 | 36.4231 | 34.3245 | 34.8316 | 36.4393 | 37.0728 | 37.7401 | 36.428 | 34.5186 | 33.5802 | 35.1884 | 35.6166 | 33.4487 | 34.5128 | 34.3834 | 33.8054 | 34.4041 | 33.5101 | 34.4876 | 33.9946 | 34.3932 | 35.1793 | 35.9724 | 35.3848 | 35.4549 | 34.4951 | 93.1782 | 93.3605 | 93.1472
2022-09-08 00:12 | 2:22 | 16.7834 | 16.8918 | 19.1533 | 35.072 | 34.4505 | 35.0608 | 35.9226 | 36.0516 | 36.9241 | 37.3607 | 36.734 | 37.4679 | 33.6408 | 34.5456 | 35.4446 | 35.9165 | 36.7359 | 36.9581 | 37.3498 | 37.4775 | 22.2524 | 17.1955 | 92.1753 | 33.1938 | 34.2967 | 35.6919 | 34.5161 | 34.1422 | 34.332 | 35.6232 | 34.9094 | 34.805 | 37.5643 | 36.4136 | 34.3247 | 34.8178 | 36.4568 | 37.068 | 37.7314 | 36.4215 | 34.5244 | 33.5973 | 35.1966 | 35.6225 | 33.4534 | 34.4866 | 34.3858 | 33.7802 | 34.4192 | 33.5088 | 34.5055 | 34.0042 | 34.4041 | 35.1778 | 35.9618 | 35.4012 | 35.4638 | 34.4821 | 93.134 | 93.3285 | 93.0552
2022-09-08 00:12 | 2:22 | 16.813 | 16.9349 | 19.1757 | 35.0751 | 34.4601 | 35.0556 | 35.9188 | 36.0779 | 36.9338 | 37.3608 | 36.7519 | 37.499 | 33.6247 | 34.5389 | 35.4583 | 35.8983 | 36.7338 | 36.9583 | 37.3398 | 37.4844 | 22.247 | 17.2614 | 92.3531 | 33.051 | 34.2906 | 35.6805 | 34.5311 | 34.1243 | 34.3288 | 35.6327 | 34.9175 | 34.8135 | 37.5551 | 36.4232 | 34.3296 | 34.8064 | 36.4231 | 37.0629 | 37.7366 | 36.4429 | 34.5018 | 33.5854 | 35.1651 | 35.6058 | 33.4328 | 34.4986 | 34.3911 | 33.7951 | 34.4095 | 33.4876 | 34.5152 | 33.9738 | 34.4192 | 35.1641 | 35.9749 | 35.3856 | 35.4721 | 34.4801 | 93.1083 | 93.2347 | 93.0724
2022-09-08 00:12 | 2:22 | 16.8761 | 17.0058 | 19.2182 | 35.0337 | 34.4486 | 35.0536 | 35.9013 | 36.072 | 36.934 | 37.3593 | 36.7274 | 37.4778 | 33.6293 | 34.558 | 35.4393 | 35.8837 | 36.7245 | 36.9749 | 37.3312 | 37.465 | 22.2475 | 17.2817 | 92.3676 | 33.0524 | 34.2862 | 35.6771 | 34.5449 | 34.1394 | 34.3422 | 35.6374 | 34.9199 | 34.8071 | 37.572 | 36.4179 | 34.3351 | 34.824 | 36.4136 | 37.0606 | 37.7339 | 36.4393 | 34.534 | 33.5941 | 35.1681 | 35.6159 | 33.4452 | 34.5178 | 34.3682 | 33.7983 | 34.4173 | 33.4902 | 34.511 | 33.9915 | 34.4095 | 35.172 | 35.9752 | 35.391 | 35.4545 | 34.5073 | 93.0358 | 93.1364 | 92.9173
2022-09-08 00:12 | 2:22 | 16.8573 | 16.973 | 19.1972 | 35.0941 | 34.4761 | 35.0379 | 35.9203 | 36.0722 | 36.9145 | 37.3492 | 36.7351 | 37.4889 | 33.6204 | 34.5571 | 35.4478 | 35.8845 | 36.7295 | 36.9661 | 37.322 | 37.4855 | 22.238 | 17.2725 | 92.47 | 33.0151 | 34.2866 | 35.6853 | 34.5186 | 34.1513 | 34.3245 | 35.6208 | 34.901 | 34.7947 | 37.5502 | 36.4151 | 34.3241 | 34.8224 | 36.4232 | 37.0507 | 37.7356 | 36.4568 | 34.487 | 33.5872 | 35.1692 | 35.6312 | 33.4322 | 34.5075 | 34.3718 | 33.7811 | 34.408 | 33.4811 | 34.4948 | 33.9775 | 34.4173 | 35.16 | 35.9798 | 35.3978 | 35.4708 | 34.4857 | 92.8844 | 93.0511 | 92.8544
2022-09-08 00:12 | 2:22 | 16.8165 | 16.9478 | 19.1653 | 35.0511 | 34.4657 | 35.0264 | 35.8969 | 36.0544 | 36.9115 | 37.3587 | 36.7302 | 37.4803 | 33.6173 | 34.5525 | 35.4488 | 35.8947 | 36.7366 | 36.9515 | 37.3218 | 37.4571 | 22.1818 | 17.2404 | 92.5213 | 33.1903 | 34.2753 | 35.6685 | 34.5244 | 34.1498 | 34.3247 | 35.6366 | 34.9054 | 34.7879 | 37.5492 | 36.4003 | 34.3213 | 34.8153 | 36.4179 | 37.0552 | 37.7515 | 36.4231 | 34.4955 | 33.5896 | 35.1668 | 35.6135 | 33.417 | 34.5197 | 34.3734 | 33.7896 | 34.411 | 33.4746 | 34.5159 | 33.9816 | 34.408 | 35.1656 | 35.9692 | 35.3862 | 35.4657 | 34.502 | 92.8153 | 92.9932 | 92.8473
2022-09-08 00:12 | 2:22 | 16.7547 | 16.8903 | 19.1947 | 35.1463 | 34.469 | 35.0463 | 35.9072 | 36.0672 | 36.9171 | 37.3553 | 36.7285 | 37.477 | 33.6319 | 34.5464 | 35.4329 | 35.8683 | 36.7282 | 36.9455 | 37.3258 | 37.4652 | 22.1509 | 17.1777 | 92.5773 | 33.1694 | 34.2584 | 35.669 | 34.5018 | 34.1444 | 34.3296 | 35.6339 | 34.899 | 34.7906 | 37.5394 | 36.4002 | 34.3217 | 34.8043 | 36.4151 | 37.0539 | 37.7315 | 36.4136 | 34.505 | 33.565 | 35.1583 | 35.5827 | 33.3937 | 34.5078 | 34.3861 | 33.7696 | 34.3913 | 33.4733 | 34.5105 | 33.9947 | 34.411 | 35.1795 | 35.9677 | 35.3912 | 35.4725 | 34.4899 | 92.7524 | 92.9086 | 92.7776
2022-09-08 00:13 | 2:22 | 16.8008 | 16.9136 | 19.1572 | 35.1173 | 34.4839 | 35.0366 | 35.8971 | 36.0741 | 36.9102 | 37.3441 | 36.7317 | 37.4751 | 33.627 | 34.5564 | 35.4522 | 35.8764 | 36.7178 | 36.9505 | 37.3225 | 37.4601 | 22.1134 | 17.2463 | 92.6299 | 33.1287 | 34.2493 | 35.6688 | 34.534 | 34.1284 | 34.3351 | 35.649 | 34.9047 | 34.7945 | 37.5461 | 36.4019 | 34.3193 | 34.8015 | 36.4003 | 37.0534 | 37.7205 | 36.4232 | 34.4999 | 33.579 | 35.176 | 35.5868 | 33.398 | 34.5153 | 34.3814 | 33.7693 | 34.3945 | 33.4782 | 34.5205 | 33.9696 | 34.3913 | 35.181 | 35.9775 | 35.3967 | 35.4623 | 34.4806 | 92.6532 | 92.8124 | 92.6787
2022-09-08 00:13 | 2:23 | 16.8116 | 16.9556 | 19.1468 | 35.065 | 34.4885 | 35.0312 | 35.9083 | 36.0707 | 36.9036 | 37.3545 | 36.7307 | 37.4936 | 33.6229 | 34.5572 | 35.4224 | 35.8779 | 36.7214 | 36.9519 | 37.312 | 37.4802 | 22.0831 | 17.2149 | 92.6437 | 33.2063 | 34.2682 | 35.6521 | 34.487 | 34.1257 | 34.3241 | 35.6171 | 34.8787 | 34.7665 | 37.5539 | 36.4156 | 34.3179 | 34.8084 | 36.4002 | 37.049 | 37.7247 | 36.4179 | 34.4937 | 33.5619 | 35.1421 | 35.5864 | 33.403 | 34.5134 | 34.3775 | 33.7792 | 34.3949 | 33.4751 | 34.524 | 33.9736 | 34.3945 | 35.1645 | 35.9678 | 35.3892 | 35.4727 | 34.4737 | 92.5264 | 92.7216 | 92.5732
2022-09-08 00:13 | 2:23 | 16.7411 | 16.9099 | 19.1302 | 35.0581 | 34.4627 | 35.0356 | 35.9064 | 36.0565 | 36.9102 | 37.362 | 36.7269 | 37.483 | 33.6006 | 34.5596 | 35.432 | 35.888 | 36.7174 | 36.9568 | 37.3068 | 37.4455 | 22.039 | 17.1809 | 92.7082 | 33.1631 | 34.2602 | 35.6557 | 34.4955 | 34.1329 | 34.3213 | 35.6321 | 34.903 | 34.7709 | 37.5532 | 36.3779 | 34.3168 | 34.8228 | 36.4019 | 37.0429 | 37.7373 | 36.4151 | 34.4912 | 33.5392 | 35.1271 | 35.5768 | 33.409 | 34.5185 | 34.392 | 33.7578 | 34.401 | 33.4704 | 34.5166 | 33.9659 | 34.3949 | 35.1704 | 35.9535 | 35.3911 | 35.4467 | 34.4717 | 92.5188 | 92.6047 | 92.6409
2022-09-08 00:13 | 2:23 | 16.7113 | 16.8465 | 19.1455 | 35.0173 | 34.4792 | 35.0456 | 35.8997 | 36.0561 | 36.9211 | 37.3738 | 36.7372 | 37.4835 | 33.6019 | 34.5483 | 35.431 | 35.8553 | 36.7117 | 36.9508 | 37.3229 | 37.4726 | 21.9736 | 17.1761 | 92.7683 | 32.9757 | 34.2605 | 35.6482 | 34.505 | 34.1111 | 34.3217 | 35.6364 | 34.8876 | 34.7737 | 37.5365 | 36.4019 | 34.3176 | 34.8156 | 36.4156 | 37.0443 | 37.7418 | 36.4003 | 34.4712 | 33.5358 | 35.1523 | 35.5777 | 33.3954 | 34.5114 | 34.3765 | 33.7607 | 34.3877 | 33.4686 | 34.5186 | 33.9775 | 34.401 | 35.1776 | 35.955 | 35.3882 | 35.4623 | 34.4607 | 92.4269 | 92.5136 | 92.5882
2022-09-08 00:13 | 2:23 | 16.6978 | 16.8372 | 19.1098 | 35.1055 | 34.484 | 34.9969 | 35.9155 | 36.0387 | 36.9388 | 37.3699 | 36.7384 | 37.4817 | 33.5946 | 34.5636 | 35.4325 | 35.8612 | 36.7127 | 36.9558 | 37.3309 | 37.4618 | 21.9609 | 17.1727 | 92.9151 | 33.2203 | 34.2649 | 35.6475 | 34.4999 | 34.1229 | 34.3193 | 35.6287 | 34.8933 | 34.7714 | 37.531 | 36.396 | 34.3133 | 34.7957 | 36.3779 | 37.0397 | 37.7495 | 36.4002 | 34.4802 | 33.5443 | 35.1289 | 35.5702 | 33.3914 | 34.5304 | 34.3869 | 33.7518 | 34.3966 | 33.4431 | 34.5311 | 33.969 | 34.3877 | 35.1738 | 35.9261 | 35.3705 | 35.4385 | 34.4543 | 92.2903 | 92.4324 | 92.5409
2022-09-08 00:13 | 2:23 | 16.751 | 16.8955 | 19.0977 | 35.1239 | 34.4718 | 34.9986 | 35.8924 | 36.0608 | 36.915 | 37.3748 | 36.7178 | 37.4733 | 33.6097 | 34.568 | 35.4303 | 35.8604 | 36.7071 | 36.956 | 37.2898 | 37.4776 | 21.9524 | 17.2001 | 93.0073 | 33.0827 | 34.2445 | 35.6437 | 34.4937 | 34.0984 | 34.3179 | 35.6216 | 34.8877 | 34.7741 | 37.527 | 36.3769 | 34.2894 | 34.8102 | 36.4019 | 37.0331 | 37.7517 | 36.4019 | 34.4777 | 33.5336 | 35.1336 | 35.5583 | 33.3694 | 34.5156 | 34.3803 | 33.7484 | 34.3931 | 34.4908 | 34.529 | 33.9614 | 34.3966 | 35.1731 | 35.9277 | 35.3879 | 35.4588 | 34.4549 | 92.1811 | 92.344 | 92.331
2022-09-08 00:14 | 2:24 | 16.7048 | 16.9123 | 19.0941 | 35.0462 | 34.4673 | 34.9986 | 35.8947 | 36.0476 | 36.9373 | 37.3568 | 36.7266 | 37.4724 | 33.5867 | 34.5542 | 35.4448 | 35.8632 | 36.7013 | 36.9464 | 37.3166 | 37.4738 | 21.9112 | 17.1759 | 93.0597 | 33.1192 | 34.2399 | 35.6361 | 34.4912 | 34.0891 | 34.3168 | 35.6285 | 34.9057 | 34.7623 | 37.5401 | 36.3905 | 34.3118 | 34.8092 | 36.396 | 37.0395 | 37.7215 | 36.4156 | 34.4614 | 33.5346 | 35.1327 | 35.5626 | 33.379 | 34.5354 | 34.3792 | 33.7414 | 34.42 | 34.4978 | 34.515 | 33.9637 | 34.3931 | 35.1691 | 35.9411 | 35.398 | 35.4677 | 34.4612 | 92.0617 | 92.2082 | 92.2705
2022-09-08 00:14 | 2:24 | 16.7295 | 16.9014 | 19.0852 | 35.1431 | 34.5022 | 34.983 | 35.9132 | 36.0295 | 36.9114 | 37.3679 | 36.7111 | 37.4722 | 33.5809 | 34.5784 | 35.4274 | 35.861 | 36.719 | 36.9418 | 37.3179 | 37.4827 | 21.8797 | 17.162 | 93.1946 | 33.0671 | 34.2416 | 35.6391 | 34.4712 | 34.1298 | 34.3176 | 35.6275 | 34.9023 | 34.7761 | 37.546 | 36.3863 | 34.3055 | 34.79 | 36.3769 | 37.035 | 37.7244 | 36.3779 | 34.4522 | 33.5149 | 35.11 | 35.5604 | 33.387 | 34.528 | 34.3854 | 33.74 | 34.3828 | 34.4957 | 34.5234 | 33.9659 | 34.42 | 35.1721 | 35.9499 | 35.3813 | 35.4831 | 34.4528 | 92.0199 | 92.1569 | 92.2441
2022-09-08 00:14 | 2:24 | 16.7426 | 16.9172 | 19.1171 | 35.1352 | 34.4804 | 35.0097 | 35.9144 | 36.0397 | 36.9308 | 37.38 | 36.723 | 37.4809 | 33.5909 | 34.5839 | 35.4222 | 35.8538 | 36.6999 | 36.9414 | 37.298 | 37.4811 | 21.8963 | 17.161 | 93.2932 | 33.0928 | 34.2156 | 35.6301 | 34.4802 | 34.0987 | 34.3133 | 35.6179 | 34.8785 | 34.7751 | 37.5212 | 36.3891 | 34.3019 | 34.7985 | 36.3905 | 37.0382 | 37.7539 | 36.4019 | 34.4537 | 33.5335 | 35.1181 | 35.5401 | 33.3685 | 34.5302 | 34.3719 | 33.7347 | 34.3939 | 34.4833 | 34.5235 | 33.9563 | 34.3828 | 35.1597 | 35.9433 | 35.3871 | 35.4783 | 34.4708 | 92.0377 | 92.1314 | 92.312
2022-09-08 00:14 | 2:24 | 16.7533 | 16.9121 | 19.0838 | 34.9703 | 34.4997 | 34.9957 | 35.8926 | 36.0422 | 36.9122 | 37.3743 | 36.7275 | 37.4915 | 33.5711 | 34.5676 | 35.4239 | 35.8591 | 36.7147 | 36.961 | 37.3315 | 37.4596 | 21.9041 | 17.2077 | 93.3656 | 33.1971 | 34.2342 | 35.6235 | 34.4777 | 34.1019 | 34.2894 | 35.6239 | 34.8876 | 34.7904 | 37.5226 | 36.3862 | 34.2993 | 34.7968 | 36.3863 | 37.0338 | 37.7332 | 36.396 | 34.4743 | 33.5161 | 35.1141 | 35.5473 | 33.3418 | 34.5091 | 34.3863 | 33.737 | 34.4055 | 34.4959 | 34.5212 | 33.9545 | 34.3939 | 35.163 | 35.9373 | 35.3891 | 35.4614 | 34.4589 | 92.0802 | 92.2248 | 92.3485
2022-09-08 00:14 | 2:24 | 16.7922 | 16.9313 | 19.1014 | 35.102 | 34.4834 | 34.9928 | 35.9174 | 36.0301 | 36.9167 | 37.3638 | 36.724 | 37.4862 | 33.5857 | 34.5672 | 35.4177 | 35.8518 | 36.6935 | 36.9618 | 37.3063 | 37.4785 | 21.8937 | 17.2112 | 93.4407 | 33.1897 | 34.2354 | 35.6439 | 34.4614 | 34.0941 | 34.3118 | 35.642 | 34.8769 | 34.789 | 37.5451 | 36.387 | 34.3226 | 34.7971 | 36.3891 | 37.0347 | 37.7193 | 36.3769 | 34.4492 | 33.5157 | 35.0998 | 35.5501 | 33.3537 | 34.5243 | 34.3726 | 33.7407 | 34.3849 | 34.4665 | 34.5264 | 33.9595 | 34.4055 | 35.1374 | 35.9432 | 35.3963 | 35.4883 | 34.4481 | 92.2993 | 92.3985 | 92.5797
2022-09-08 00:14 | 2:24 | 16.7427 | 16.8971 | 19.1392 | 35.0159 | 34.5132 | 35.008 | 35.9077 | 36.0545 | 36.9273 | 37.3727 | 36.7173 | 37.4853 | 33.576 | 34.5646 | 35.4256 | 35.8444 | 36.675 | 36.9382 | 37.3017 | 37.4791 | 21.8768 | 17.2038 | 93.5035 | 33.1598 | 34.2281 | 35.6214 | 34.4522 | 34.0988 | 34.3055 | 35.6172 | 34.8939 | 34.771 | 37.5219 | 36.3628 | 34.3109 | 34.7986 | 36.3862 | 37.0194 | 37.7182 | 36.3905 | 34.4567 | 33.5162 | 35.1063 | 35.5459 | 33.3592 | 34.5286 | 34.3944 | 33.7338 | 34.4143 | 34.4603 | 34.532 | 33.9742 | 34.3849 | 35.1475 | 35.9316 | 35.4034 | 35.471 | 34.4491 | 92.4547 | 92.601 | 92.7408
2022-09-08 00:15 | 2:24 | 16.8025 | 16.9158 | 19.0972 | 35.0848 | 34.4918 | 35.001 | 35.8839 | 36.0449 | 36.9324 | 37.3759 | 36.7327 | 37.4774 | 33.5677 | 34.5722 | 35.4165 | 35.8363 | 36.6933 | 36.9365 | 37.3052 | 37.4778 | 21.8591 | 17.1959 | 93.5814 | 33.0479 | 34.2157 | 35.605 | 34.4537 | 34.0983 | 34.3019 | 35.6365 | 34.8951 | 34.7584 | 37.5306 | 36.3945 | 34.2988 | 34.8117 | 36.387 | 37.0333 | 37.7122 | 36.3863 | 34.4545 | 33.4925 | 35.1019 | 35.533 | 33.3247 | 34.52 | 34.385 | 33.7249 | 34.3972 | 34.4801 | 34.5422 | 33.9619 | 34.4143 | 35.1668 | 35.9365 | 35.3902 | 35.461 | 34.4373 | 92.6937 | 92.7828 | 92.8719
2022-09-08 00:15 | 2:25 | 16.8106 | 16.9386 | 19.1216 | 35.018 | 34.5001 | 34.9768 | 35.8849 | 36.0381 | 36.9368 | 37.3613 | 36.7229 | 37.4702 | 33.5759 | 34.5739 | 35.4183 | 35.8331 | 36.7021 | 36.9472 | 37.2925 | 37.4531 | 21.849 | 17.2423 | 93.6857 | 33.0871 | 34.2191 | 35.6268 | 34.4743 | 34.1066 | 34.2993 | 35.628 | 34.8799 | 34.7619 | 37.5315 | 36.3781 | 34.2967 | 34.7956 | 36.3628 | 37.0341 | 37.7287 | 36.3891 | 34.4516 | 33.5013 | 35.0987 | 35.542 | 33.3446 | 34.5276 | 34.3849 | 33.7388 | 34.3841 | 34.4601 | 34.5447 | 33.9487 | 34.3972 | 35.1638 | 35.9153 | 35.4016 | 35.4813 | 34.4239 | 92.85 | 92.9928 | 92.9334
2022-09-08 00:15 | 2:25 | 16.7679 | 16.9239 | 19.0887 | 35.109 | 34.4813 | 34.9866 | 35.9003 | 36.0269 | 36.9225 | 37.3766 | 36.712 | 37.4783 | 33.5846 | 34.5524 | 35.4032 | 35.8533 | 36.6864 | 36.9298 | 37.3141 | 37.4468 | 21.8515 | 17.2103 | 93.8128 | 33.071 | 34.2229 | 35.6156 | 34.4492 | 34.0845 | 34.3226 | 35.6199 | 34.8602 | 34.7503 | 37.5175 | 36.3954 | 34.277 | 34.8036 | 36.3945 | 37.02 | 37.7254 | 36.3862 | 34.4628 | 33.491 | 35.0765 | 35.5173 | 33.3314 | 34.5259 | 34.4131 | 33.7075 | 34.3941 | 34.469 | 34.5512 | 33.9675 | 34.3841 | 35.1773 | 35.9141 | 35.3979 | 35.4813 | 34.4263 | 92.986 | 93.1846 | 92.9647
2022-09-08 00:15 | 2:25 | 16.7506 | 16.9304 | 19.1096 | 35.0348 | 34.5003 | 34.9888 | 35.9036 | 36.0514 | 36.924 | 37.3735 | 36.7196 | 37.4954 | 33.5458 | 34.5728 | 35.4097 | 35.8369 | 36.6888 | 36.9244 | 37.325 | 37.469 | 21.834 | 17.2197 | 93.8826 | 33.1359 | 34.201 | 35.6098 | 34.4567 | 34.0829 | 34.3109 | 35.6253 | 34.8828 | 34.7659 | 37.5225 | 36.3799 | 34.2819 | 34.7857 | 36.3781 | 37.0084 | 37.7261 | 36.387 | 34.4591 | 33.4898 | 35.068 | 35.517 | 33.323 | 34.5264 | 34.394 | 33.7244 | 34.4037 | 34.4537 | 34.5315 | 33.9277 | 34.3941 | 35.1814 | 35.9213 | 35.4035 | 35.4722 | 34.4399 | 93.1493 | 93.3716 | 93.0859
2022-09-08 00:15 | 2:25 | 16.7236 | 16.8898 | 19.0919 | 35.0623 | 34.5073 | 34.9877 | 35.8967 | 36.027 | 36.94 | 37.3937 | 36.7182 | 37.4848 | 33.5708 | 34.58 | 35.4101 | 35.8547 | 36.6765 | 36.9314 | 37.2981 | 37.4869 | 21.8151 | 17.1099 | 94.0044 | 33.0884 | 34.2214 | 35.6093 | 34.4545 | 34.0624 | 34.2988 | 35.6268 | 34.8796 | 34.7447 | 37.5432 | 36.3747 | 34.2798 | 34.7965 | 36.3954 | 37.0442 | 37.7343 | 36.3628 | 34.452 | 33.4601 | 35.0781 | 35.5104 | 33.3321 | 34.5164 | 34.3927 | 33.7398 | 34.3853 | 34.4765 | 34.5338 | 33.9569 | 34.4037 | 35.1787 | 35.9201 | 35.3934 | 35.4789 | 34.4093 | 93.2707 | 93.5577 | 93.1535
2022-09-08 00:15 | 2:25 | 16.718 | 16.8908 | 19.0827 | 34.9949 | 34.4845 | 34.9606 | 35.9003 | 36.0476 | 36.9193 | 37.3646 | 36.7359 | 37.4712 | 33.5395 | 34.5568 | 35.4036 | 35.8486 | 36.6987 | 36.9389 | 37.3028 | 37.4606 | 21.7798 | 17.1541 | 94.094 | 33.0545 | 34.1925 | 35.5983 | 34.4516 | 34.0678 | 34.2967 | 35.6103 | 34.8784 | 34.7621 | 37.5383 | 36.3799 | 34.277 | 34.806 | 36.3799 | 37.01 | 37.7309 | 36.3945 | 34.4264 | 33.4984 | 35.0728 | 35.5133 | 33.3228 | 34.5196 | 34.4089 | 33.709 | 34.3991 | 34.4607 | 34.5333 | 33.9486 | 34.3853 | 35.1584 | 35.9128 | 35.3917 | 35.4589 | 34.4106 | 93.4786 | 93.7718 | 93.3584
2022-09-08 00:16 | 2:26 | 16.6784 | 16.8693 | 19.0939 | 34.9917 | 34.524 | 34.9903 | 35.9 | 36.0322 | 36.9082 | 37.3703 | 36.7168 | 37.485 | 33.529 | 34.5423 | 35.3948 | 35.8399 | 36.6832 | 36.9198 | 37.2876 | 37.462 | 21.7646 | 17.0778 | 94.2356 | 33.0324 | 34.1838 | 35.6049 | 34.4628 | 34.0797 | 34.277 | 35.6337 | 34.8756 | 34.7551 | 37.5374 | 36.3817 | 34.2909 | 34.8028 | 36.3747 | 37.0332 | 37.7143 | 36.3781 | 34.4474 | 33.486 | 35.0647 | 35.5132 | 33.3101 | 34.5234 | 34.4066 | 33.7214 | 34.3877 | 34.4725 | 34.538 | 33.9687 | 34.3991 | 35.1657 | 35.909 | 35.3933 | 35.4747 | 34.4282 | 93.664 | 94.0031 | 93.4822
2022-09-08 00:16 | 2:26 | 16.7437 | 16.9122 | 19.1083 | 34.984 | 34.5103 | 34.9653 | 35.8828 | 36.0321 | 36.9249 | 37.377 | 36.72 | 37.4706 | 33.5387 | 34.5566 | 35.3987 | 35.8214 | 36.6809 | 36.904 | 37.3006 | 37.4731 | 21.7571 | 17.1219 | 94.2643 | 33.0589 | 34.19 | 35.5947 | 34.4591 | 34.079 | 34.2819 | 35.6058 | 34.8742 | 34.7566 | 37.5322 | 36.3604 | 34.2881 | 34.7948 | 36.3799 | 37.0142 | 37.7167 | 36.3954 | 34.4215 | 33.4758 | 35.0606 | 35.5048 | 33.3069 | 34.5318 | 34.4207 | 33.7204 | 34.3896 | 34.462 | 34.5456 | 33.9367 | 34.3877 | 35.1589 | 35.9144 | 35.3962 | 35.4492 | 34.4047 | 93.8352 | 94.2082 | 93.6544
2022-09-08 00:16 | 2:26 | 16.7746 | 16.9238 | 19.1512 | 35.0706 | 34.5049 | 34.9492 | 35.8997 | 36.0476 | 36.9141 | 37.3671 | 36.7247 | 37.4918 | 33.5506 | 34.5833 | 35.4009 | 35.8478 | 36.6799 | 36.9237 | 37.2983 | 37.4566 | 21.7605 | 17.1344 | 94.3993 | 33.0594 | 34.1775 | 35.5959 | 34.452 | 34.0754 | 34.2798 | 35.6026 | 34.8753 | 34.7636 | 37.5186 | 36.3699 | 34.2574 | 34.7747 | 36.3817 | 37.0093 | 37.7172 | 36.3799 | 34.4209 | 33.453 | 35.0444 | 35.4973 | 33.3074 | 34.523 | 34.409 | 33.7025 | 34.3913 | 34.4569 | 34.5389 | 33.9565 | 34.3896 | 35.1626 | 35.9201 | 35.3944 | 35.4654 | 34.3974 | 94.0786 | 94.4429 | 93.8409
2022-09-08 00:16 | 2:26 | 16.792 | 16.9175 | 19.1279 | 35.0065 | 34.4975 | 34.9511 | 35.9045 | 36.0448 | 36.9269 | 37.3669 | 36.7146 | 37.4746 | 33.5463 | 34.5597 | 35.382 | 35.8319 | 36.6707 | 36.9094 | 37.2842 | 37.4489 | 21.7856 | 17.1925 | 94.4834 | 33.0725 | 34.1731 | 35.5961 | 34.4264 | 34.093 | 34.277 | 35.6225 | 34.8623 | 34.7447 | 37.5168 | 36.3688 | 34.2706 | 34.8003 | 36.3604 | 37.0104 | 37.706 | 36.3747 | 34.4301 | 33.4723 | 35.054 | 35.4782 | 33.2971 | 34.5256 | 34.411 | 33.6923 | 34.3937 | 34.4577 | 34.558 | 33.9468 | 34.3913 | 35.1606 | 35.9131 | 35.3914 | 35.4535 | 34.3921 | 94.2006 | 94.6295 | 93.8496
2022-09-08 00:16 | 2:26 | 16.7698 | 16.9108 | 19.116 | 35.0101 | 34.4876 | 34.956 | 35.9136 | 36.0168 | 36.9441 | 37.3833 | 36.7141 | 37.4922 | 33.5238 | 34.5408 | 35.3672 | 35.8265 | 36.6755 | 36.9254 | 37.2772 | 37.4549 | 21.7634 | 17.1174 | 94.4422 | 33.0522 | 34.1781 | 35.5965 | 34.4474 | 34.0851 | 34.2909 | 35.5991 | 34.8654 | 34.7576 | 37.5087 | 36.3687 | 34.2448 | 34.7849 | 36.3699 | 37.0089 | 37.7047 | 36.3799 | 34.4267 | 33.4573 | 35.053 | 35.4654 | 33.3068 | 34.5383 | 34.4179 | 33.6726 | 34.382 | 34.4593 | 34.5571 | 33.9401 | 34.3937 | 35.1702 | 35.9129 | 35.3922 | 35.4556 | 34.3914 | 94.39 | 94.8396 | 94.0568
2022-09-08 00:16 | 2:26 | 16.7411 | 16.9031 | 19.101 | 35.0333 | 34.5055 | 34.9568 | 35.9023 | 36.0039 | 36.9258 | 37.3563 | 36.7246 | 37.4947 | 33.5312 | 34.5539 | 35.3791 | 35.8303 | 36.6535 | 36.927 | 37.2621 | 37.4455 | 21.777 | 17.1011 | 94.307 | 33.0774 | 34.1644 | 35.5862 | 34.4215 | 34.0662 | 34.2881 | 35.6104 | 34.8678 | 34.7335 | 37.5167 | 36.3595 | 34.2715 | 34.771 | 36.3688 | 37.0122 | 37.7104 | 36.3817 | 34.4253 | 33.4456 | 35.0384 | 35.4517 | 33.2905 | 34.5317 | 34.3964 | 33.6724 | 34.3771 | 34.4451 | 34.5525 | 33.9394 | 34.382 | 35.1687 | 35.9135 | 35.4087 | 35.4663 | 34.3769 | 94.6024 | 95.0834 | 94.1744
2022-09-08 00:17 | 2:26 | 16.7306 | 16.8997 | 19.0473 | 35.0907 | 34.5152 | 34.9493 | 35.8856 | 36.0458 | 36.9049 | 37.356 | 36.7001 | 37.4696 | 33.5131 | 34.5292 | 35.3833 | 35.8258 | 36.6614 | 36.9093 | 37.2816 | 37.447 | 21.7718 | 17.0484 | 94.2299 | 33.1192 | 34.1695 | 35.5887 | 34.4209 | 34.0565 | 34.2574 | 35.5958 | 34.8626 | 34.745 | 37.5128 | 36.381 | 34.2528 | 34.7821 | 36.3687 | 36.9867 | 37.6939 | 36.3604 | 34.4353 | 33.427 | 35.0358 | 35.4781 | 33.2921 | 34.5299 | 34.4229 | 33.6482 | 34.411 | 34.4578 | 34.5464 | 33.9333 | 34.3771 | 35.1459 | 35.8871 | 35.3893 | 35.4532 | 34.3461 | 94.8309 | 95.2497 | 94.3758
2022-09-08 00:17 | 2:27 | 16.6979 | 16.8769 | 19.0609 | 35.0015 | 34.511 | 34.9298 | 35.9027 | 36.0338 | 36.9049 | 37.3693 | 36.7081 | 37.4894 | 33.5136 | 34.5408 | 35.3608 | 35.8186 | 36.6547 | 36.9096 | 37.2655 | 37.4321 | 21.774 | 17.0558 | 94.0846 | 32.9583 | 34.1566 | 35.5867 | 34.4301 | 34.0623 | 34.2706 | 35.5868 | 34.8552 | 34.7484 | 37.5136 | 36.3662 | 34.2532 | 34.7771 | 36.3595 | 37.0044 | 37.7007 | 36.3699 | 34.4209 | 33.4253 | 35.0262 | 35.4541 | 33.282 | 34.5159 | 34.4296 | 33.6687 | 34.3903 | 34.4566 | 34.5564 | 33.9238 | 34.411 | 35.1444 | 35.9041 | 35.3743 | 35.4533 | 34.3624 | 94.9789 | 95.3726 | 94.4821
2022-09-08 00:17 | 2:27 | 16.7048 | 16.8555 | 19.0456 | 35.1015 | 34.4948 | 34.9235 | 35.8777 | 36.0278 | 36.9236 | 37.3593 | 36.7058 | 37.4773 | 33.5012 | 34.5173 | 35.3377 | 35.8176 | 36.6539 | 36.9025 | 37.2738 | 37.4339 | 21.8016 | 17.05 | 93.9585 | 32.9605 | 34.1508 | 35.5626 | 34.4267 | 34.0477 | 34.2448 | 35.6017 | 34.8759 | 34.756 | 37.5009 | 36.357 | 34.2594 | 34.8073 | 36.381 | 36.9984 | 37.6962 | 36.3688 | 34.4091 | 33.4369 | 35.0099 | 35.4514 | 33.2768 | 34.5281 | 34.4419 | 33.6598 | 34.3847 | 34.4468 | 34.5572 | 33.9238 | 34.3903 | 35.1368 | 35.8862 | 35.3916 | 35.4435 | 34.3805 | 95.1759 | 95.5464 | 94.5387
2022-09-08 00:17 | 2:27 | 16.7395 | 16.8995 | 19.0389 | 34.9966 | 34.5159 | 34.9284 | 35.89 | 36.0282 | 36.9082 | 37.3511 | 36.729 | 37.4846 | 33.4918 | 34.5357 | 35.3497 | 35.8221 | 36.6645 | 36.8975 | 37.2508 | 37.4235 | 21.8196 | 17.027 | 93.9087 | 33.137 | 34.1564 | 35.572 | 34.4253 | 34.048 | 34.2715 | 35.5894 | 34.8652 | 34.7195 | 37.5015 | 36.3618 | 34.2427 | 34.7847 | 36.3662 | 36.9878 | 37.6916 | 36.3687 | 34.4206 | 33.4134 | 34.9937 | 35.4184 | 33.2701 | 34.5265 | 34.44 | 33.6343 | 34.3867 | 34.4566 | 34.5596 | 33.9145 | 34.3847 | 35.1341 | 35.9054 | 35.3801 | 35.4713 | 34.355 | 95.1956 | 95.6531 | 94.5715
2022-09-08 00:17 | 2:27 | 16.7509 | 16.9079 | 19.0483 | 34.9452 | 34.5105 | 34.927 | 35.905 | 36.0116 | 36.9078 | 37.3579 | 36.7073 | 37.4826 | 33.4866 | 34.5425 | 35.3529 | 35.8279 | 36.6528 | 36.8938 | 37.255 | 37.4221 | 21.8516 | 17.0666 | 93.947 | 32.9621 | 34.1506 | 35.5753 | 34.4353 | 34.0574 | 34.2528 | 35.6028 | 34.8574 | 34.7331 | 37.4893 | 36.3532 | 34.2451 | 34.7774 | 36.357 | 36.9929 | 37.6847 | 36.3595 | 34.4107 | 33.4257 | 35.0143 | 35.4312 | 33.2595 | 34.5041 | 34.4337 | 33.6497 | 34.3794 | 34.4503 | 34.5483 | 33.9098 | 34.3867 | 35.1251 | 35.8976 | 35.4153 | 35.4425 | 34.3602 | 95.3323 | 95.7022 | 94.6141
2022-09-08 00:17 | 2:27 | 15.9212 | 16.6744 | 18.9736 | 34.9724 | 34.5205 | 34.9474 | 35.8852 | 36.0113 | 36.8857 | 37.3585 | 36.72 | 37.4633 | 33.4947 | 34.5249 | 35.3331 | 35.8179 | 36.6674 | 36.9034 | 37.2579 | 37.4224 | 21.8457 | 17.2096 | 93.9472 | 32.9867 | 34.1171 | 35.5735 | 34.4209 | 34.0395 | 34.2532 | 35.5812 | 34.8742 | 34.7361 | 37.4971 | 36.3606 | 34.2386 | 34.7902 | 36.3618 | 36.9857 | 37.6724 | 36.381 | 34.4225 | 33.4157 | 35.0032 | 35.4253 | 33.2651 | 34.5163 | 34.4416 | 33.6347 | 34.3867 | 34.4472 | 34.5636 | 33.9102 | 34.3794 | 35.123 | 35.903 | 35.3825 | 35.4361 | 34.3282 | 95.3976 | 95.7848 | 94.6974
2022-09-08 00:18 | 2:28 | 15.0644 | 16.1846 | 18.6294 | 34.9757 | 34.524 | 34.9105 | 35.89 | 36.009 | 36.9048 | 37.3515 | 36.7137 | 37.4763 | 33.5051 | 34.5307 | 35.3374 | 35.8131 | 36.6374 | 36.8874 | 37.2419 | 37.4116 | 22.1555 | 18.0503 | 93.8323 | 33.01 | 34.1324 | 35.5631 | 34.4091 | 34.0473 | 34.2594 | 35.5848 | 34.8635 | 34.7326 | 37.4892 | 36.3613 | 34.2353 | 34.7694 | 36.3532 | 36.9901 | 37.6975 | 36.3662 | 34.4031 | 33.4002 | 35.0059 | 35.4074 | 33.2693 | 34.5282 | 34.456 | 33.6336 | 34.3824 | 34.4433 | 34.568 | 33.9156 | 34.3867 | 35.1213 | 35.8725 | 35.3999 | 35.4384 | 34.3434 | 95.4128 | 95.7444 | 94.7051
2022-09-08 00:18 | 2:28 | 14.8171 | 15.9565 | 18.4032 | 34.9214 | 34.5166 | 34.935 | 35.8829 | 36.0081 | 36.8975 | 37.3369 | 36.7235 | 37.4857 | 33.4789 | 34.5005 | 35.3296 | 35.8156 | 36.6516 | 36.8906 | 37.2482 | 37.4084 | 22.7851 | 19.0761 | 93.8157 | 33.197 | 34.1221 | 35.5669 | 34.4206 | 34.049 | 34.2427 | 35.5918 | 34.8657 | 34.7552 | 37.5149 | 36.3713 | 34.2333 | 34.7769 | 36.3606 | 36.9859 | 37.6829 | 36.357 | 34.4052 | 33.4146 | 34.988 | 35.4274 | 33.2503 | 34.5365 | 34.4223 | 33.6527 | 34.369 | 34.4488 | 34.5542 | 33.915 | 34.3824 | 35.1478 | 35.9012 | 35.3953 | 35.4534 | 34.3438 | 95.2702 | 95.6145 | 94.4962
2022-09-08 00:18 | 2:28 | 14.5402 | 15.7546 | 18.2073 | 34.9557 | 34.5186 | 34.9148 | 35.8899 | 35.998 | 36.9137 | 37.3469 | 36.7336 | 37.4694 | 33.4841 | 34.5194 | 35.3231 | 35.8154 | 36.6535 | 36.8927 | 37.2434 | 37.4337 | 23.6136 | 20.29 | 93.8376 | 33.393 | 34.1312 | 35.5766 | 34.4107 | 34.0459 | 34.2451 | 35.5853 | 34.8672 | 34.7164 | 37.4955 | 36.3653 | 34.2295 | 34.7771 | 36.3613 | 36.9769 | 37.6691 | 36.3618 | 34.425 | 33.3975 | 34.9851 | 35.4002 | 33.2515 | 34.5052 | 34.4529 | 33.6465 | 34.3826 | 34.4307 | 34.5784 | 33.9103 | 34.369 | 35.1343 | 35.9179 | 35.3855 | 35.4499 | 34.3223 | 95.0379 | 95.4014 | 94.3183
2022-09-08 00:18 | 2:28 | 14.2464 | 15.5386 | 18.0937 | 34.8833 | 34.5311 | 34.9179 | 35.8792 | 36.0074 | 36.9114 | 37.3626 | 36.7277 | 37.4819 | 33.4698 | 34.5104 | 35.33 | 35.8295 | 36.6329 | 36.8762 | 37.2453 | 37.4022 | 24.4239 | 21.4973 | 93.7934 | 33.3829 | 34.1295 | 35.5688 | 34.4225 | 34.0471 | 34.2386 | 35.5696 | 34.8627 | 34.7357 | 37.5044 | 36.3468 | 34.2483 | 34.7733 | 36.3713 | 36.9891 | 37.685 | 36.3532 | 34.3989 | 33.392 | 35.0088 | 35.395 | 33.2511 | 34.5077 | 34.4382 | 33.647 | 34.3901 | 34.4567 | 34.5839 | 33.9265 | 34.3826 | 35.1248 | 35.8954 | 35.3966 | 35.4368 | 34.3353 | 94.782 | 95.1235 | 94.2378
2022-09-08 00:18 | 2:28 | 14.0496 | 15.3992 | 17.9695 | 34.88 | 34.529 | 34.9162 | 35.8882 | 35.9914 | 36.9002 | 37.3387 | 36.7346 | 37.4597 | 33.4721 | 34.4991 | 35.3199 | 35.8174 | 36.6517 | 36.8692 | 37.2587 | 37.4197 | 25.2581 | 22.6588 | 93.7698 | 33.4855 | 34.1405 | 35.5506 | 34.4031 | 34.0547 | 34.2353 | 35.6094 | 34.8735 | 34.7278 | 37.5052 | 36.3521 | 34.2494 | 34.7799 | 36.3653 | 36.9875 | 37.6782 | 36.3606 | 34.4237 | 33.3933 | 34.9955 | 35.4 | 33.2536 | 34.5046 | 34.4355 | 33.6419 | 34.3802 | 34.4334 | 34.5676 | 33.9243 | 34.3901 | 35.1311 | 35.8837 | 35.3974 | 35.4518 | 34.3286 | 94.5462 | 94.8757 | 94.0243
2022-09-08 00:18 | 2:28 | 13.8549 | 15.2032 | 17.8493 | 34.8134 | 34.515 | 34.916 | 35.8644 | 35.9912 | 36.9006 | 37.3397 | 36.7283 | 37.4968 | 33.4796 | 34.4986 | 35.3281 | 35.8108 | 36.6471 | 36.9078 | 37.2494 | 37.4156 | 26.013 | 23.7463 | 93.6809 | 33.5386 | 34.1328 | 35.5772 | 34.4052 | 34.0327 | 34.2333 | 35.5956 | 34.8602 | 34.7232 | 37.5023 | 36.3683 | 34.2567 | 34.7742 | 36.3468 | 36.9759 | 37.6819 | 36.3613 | 34.4167 | 33.3963 | 34.9925 | 35.3987 | 33.2774 | 34.5253 | 34.4299 | 33.6161 | 34.3905 | 34.4463 | 34.5672 | 33.9088 | 34.3802 | 35.1392 | 35.891 | 35.3935 | 35.4253 | 34.3341 | 94.3359 | 94.6945 | 93.8956
2022-09-08 00:19 | 2:28 | 13.6472 | 15.0134 | 17.7014 | 34.7842 | 34.5234 | 34.9096 | 35.8721 | 36.0002 | 36.9145 | 37.349 | 36.7409 | 37.4993 | 33.4635 | 34.5005 | 35.3367 | 35.812 | 36.6495 | 36.8603 | 37.2422 | 37.4023 | 26.6949 | 24.6998 | 93.6148 | 33.5694 | 34.1075 | 35.5647 | 34.425 | 34.0528 | 34.2295 | 35.5919 | 34.8539 | 34.7259 | 37.4925 | 36.3536 | 34.231 | 34.7781 | 36.3521 | 36.9883 | 37.6711 | 36.3713 | 34.4256 | 33.3956 | 34.9851 | 35.4047 | 33.2722 | 34.4931 | 34.443 | 33.6387 | 34.3869 | 34.4521 | 34.5646 | 33.9018 | 34.3905 | 35.1413 | 35.884 | 35.4013 | 35.4554 | 34.3224 | 94.2023 | 94.5338 | 93.7782
2022-09-08 00:19 | 2:29 | 13.4588 | 14.8398 | 17.5996 | 34.7619 | 34.5235 | 34.8853 | 35.8682 | 36.0046 | 36.8939 | 37.3569 | 36.7333 | 37.507 | 33.4624 | 34.4877 | 35.3336 | 35.8151 | 36.6458 | 36.8783 | 37.2546 | 37.4203 | 27.2893 | 25.537 | 93.6311 | 33.6554 | 34.113 | 35.571 | 34.3989 | 34.0438 | 34.2483 | 35.5842 | 34.8674 | 34.7429 | 37.5115 | 36.3539 | 34.2633 | 34.7815 | 36.3683 | 36.9735 | 37.6786 | 36.3653 | 34.4044 | 33.3996 | 34.9808 | 35.3996 | 33.2751 | 34.502 | 34.4311 | 33.6252 | 34.3754 | 34.4561 | 34.5722 | 33.9032 | 34.3869 | 35.1542 | 35.9006 | 35.4054 | 35.4551 | 34.326 | 94.1544 | 94.4222 | 93.7885
2022-09-08 00:19 | 2:29 | 13.2781 | 14.6773 | 17.4708 | 34.7712 | 34.5212 | 34.8995 | 35.8648 | 35.9854 | 36.9052 | 37.3502 | 36.7264 | 37.4682 | 33.4667 | 34.4942 | 35.3242 | 35.8297 | 36.6514 | 36.8916 | 37.2557 | 37.4158 | 27.8407 | 26.3001 | 93.68 | 33.7664 | 34.12 | 35.5737 | 34.4237 | 34.0571 | 34.2494 | 35.5926 | 34.8746 | 34.7412 | 37.4871 | 36.3593 | 34.2519 | 34.76 | 36.3536 | 36.9898 | 37.6716 | 36.3468 | 34.4111 | 33.3923 | 34.9746 | 35.4083 | 33.2777 | 34.4957 | 34.4389 | 33.6183 | 34.3833 | 34.4321 | 34.5739 | 33.9069 | 34.3754 | 35.118 | 35.9082 | 35.4143 | 35.4423 | 34.3341 | 94.0141 | 94.3204 | 93.7342
2022-09-08 00:19 | 2:29 | 13.1649 | 14.5288 | 17.3534 | 34.8418 | 34.5264 | 34.9081 | 35.8785 | 36.016 | 36.8855 | 37.3452 | 36.7347 | 37.5009 | 33.4754 | 34.4987 | 35.322 | 35.8353 | 36.6372 | 36.8823 | 37.2409 | 37.3987 | 28.287 | 26.9164 | 93.5855 | 33.868 | 34.1216 | 35.5813 | 34.4167 | 34.0612 | 34.2567 | 35.5635 | 34.8802 | 34.7519 | 37.5008 | 36.3705 | 34.2369 | 34.7884 | 36.3539 | 36.9741 | 37.6657 | 36.3521 | 34.3838 | 33.3867 | 34.988 | 35.4034 | 33.2672 | 34.4831 | 34.4469 | 33.6123 | 34.3724 | 34.439 | 34.5524 | 33.9102 | 34.3833 | 35.1596 | 35.896 | 35.4164 | 35.4436 | 34.3402 | 93.9526 | 94.1419 | 93.7632
2022-09-08 00:19 | 2:29 | 12.9797 | 14.4061 | 17.1875 | 34.7065 | 34.532 | 34.9096 | 35.8677 | 36.0047 | 36.903 | 37.3565 | 36.7384 | 37.4947 | 33.4594 | 34.4771 | 35.3112 | 35.8215 | 36.6506 | 36.8719 | 37.2453 | 37.4081 | 28.6736 | 27.4714 | 93.3389 | 33.9546 | 34.1266 | 35.5934 | 34.4256 | 34.0647 | 34.231 | 35.5733 | 34.8737 | 34.7182 | 37.4998 | 36.38 | 34.2523 | 34.7854 | 36.3593 | 36.9909 | 37.6736 | 36.3683 | 34.3996 | 33.392 | 35.0173 | 35.4017 | 33.29 | 34.4669 | 34.4404 | 33.6266 | 34.3781 | 34.4377 | 34.5728 | 33.8938 | 34.3724 | 35.1529 | 35.9039 | 35.4111 | 35.4564 | 34.3268 | 93.7801 | 93.9983 | 93.5544
2022-09-08 00:19 | 2:29 | 12.8526 | 14.2434 | 17.0843 | 34.7989 | 34.5422 | 34.8878 | 35.8695 | 35.998 | 36.8945 | 37.3413 | 36.712 | 37.4962 | 33.4555 | 34.4866 | 35.325 | 35.8223 | 36.6393 | 36.8663 | 37.2535 | 37.4056 | 29.0095 | 27.9427 | 93.3013 | 33.961 | 34.1332 | 35.5726 | 34.4044 | 34.049 | 34.2633 | 35.5794 | 34.8794 | 34.7473 | 37.4911 | 36.352 | 34.2394 | 34.7921 | 36.3705 | 36.9981 | 37.689 | 36.3536 | 34.4096 | 33.3772 | 34.9961 | 35.4153 | 33.2809 | 34.4927 | 34.4671 | 33.6298 | 34.3773 | 34.4175 | 34.58 | 33.8937 | 34.3781 | 35.1518 | 35.9152 | 35.4057 | 35.4543 | 34.3319 | 93.7001 | 93.9474 | 93.4996
2022-09-08 00:20 | 2:29 | 12.6865 | 14.1005 | 16.9429 | 34.6635 | 34.5447 | 34.9108 | 35.8599 | 36.0032 | 36.9213 | 37.3648 | 36.7308 | 37.5066 | 33.456 | 34.4769 | 35.3022 | 35.8186 | 36.649 | 36.8629 | 37.2372 | 37.4099 | 29.2841 | 28.3432 | 93.2199 | 34.0647 | 34.13 | 35.5679 | 34.4111 | 34.0484 | 34.2519 | 35.576 | 34.8933 | 34.7494 | 37.5145 | 36.3661 | 34.2431 | 34.7884 | 36.38 | 36.9882 | 37.667 | 36.3539 | 34.4174 | 33.4064 | 35.0023 | 35.4151 | 33.2711 | 34.4716 | 34.4465 | 33.6197 | 34.3834 | 34.4455 | 34.5568 | 33.9137 | 34.3773 | 35.1508 | 35.9027 | 35.4118 | 35.4539 | 34.3173 | 93.633 | 93.8835 | 93.4931
2022-09-08 00:20 | 2:30 | 12.5764 | 13.9448 | 16.9039 | 34.6354 | 34.5512 | 34.8963 | 35.8593 | 35.9924 | 36.9048 | 37.342 | 36.7523 | 37.5094 | 33.465 | 34.4737 | 35.3032 | 35.8242 | 36.6336 | 36.8701 | 37.2536 | 37.4064 | 29.5236 | 28.6669 | 93.21 | 34.1526 | 34.1113 | 35.5598 | 34.3838 | 34.0658 | 34.2369 | 35.5791 | 34.8809 | 34.7376 | 37.4897 | 36.371 | 34.2453 | 34.7871 | 36.352 | 36.9903 | 37.6691 | 36.3593 | 34.4022 | 33.3909 | 35.0156 | 35.4247 | 33.2879 | 34.4777 | 34.465 | 33.6314 | 34.3858 | 34.4333 | 34.5423 | 33.9008 | 34.3834 | 35.1668 | 35.9129 | 35.403 | 35.4584 | 34.3255 | 93.5961 | 93.8632 | 93.4232
2022-09-08 00:20 | 2:30 | 12.473 | 13.8291 | 16.7637 | 34.5681 | 34.5315 | 34.8835 | 35.8675 | 36.0129 | 36.9034 | 37.3734 | 36.7396 | 37.4927 | 33.4492 | 34.4859 | 35.2974 | 35.7964 | 36.6543 | 36.8734 | 37.2496 | 37.4296 | 29.77 | 28.9847 | 93.3039 | 34.0924 | 34.1137 | 35.5924 | 34.3996 | 34.0453 | 34.2523 | 35.5823 | 34.8725 | 34.7351 | 37.4913 | 36.3492 | 34.2442 | 34.7815 | 36.3661 | 36.9871 | 37.6674 | 36.3705 | 34.41 | 33.3961 | 35.0135 | 35.4004 | 33.2912 | 34.472 | 34.471 | 33.6121 | 34.3911 | 34.4184 | 34.5566 | 33.913 | 34.3858 | 35.1582 | 35.8995 | 35.4066 | 35.4567 | 34.3175 | 93.5676 | 93.8191 | 93.4175
2022-09-08 00:20 | 2:30 | 12.2954 | 13.6508 | 16.6628 | 34.5868 | 34.5338 | 34.8849 | 35.8493 | 35.9791 | 36.9025 | 37.3383 | 36.7449 | 37.5063 | 33.4417 | 34.4734 | 35.3135 | 35.8257 | 36.6469 | 36.8709 | 37.2612 | 37.4022 | 29.9408 | 29.2418 | 93.1753 | 34.1499 | 34.1345 | 35.5827 | 34.4096 | 34.0533 | 34.2394 | 35.582 | 34.8617 | 34.762 | 37.5093 | 36.339 | 34.2497 | 34.8044 | 36.371 | 37.0008 | 37.6744 | 36.38 | 34.416 | 33.4207 | 35.0103 | 35.4261 | 33.3025 | 34.4674 | 34.4436 | 33.6286 | 34.3682 | 34.4355 | 34.5833 | 33.9029 | 34.3911 | 35.1603 | 35.9002 | 35.4157 | 35.4608 | 34.335 | 93.5143 | 93.764 | 93.3982
2022-09-08 00:20 | 2:30 | 12.2117 | 13.5552 | 16.5106 | 34.5935 | 34.5333 | 34.8875 | 35.865 | 35.9696 | 36.8979 | 37.3687 | 36.7453 | 37.5184 | 33.4406 | 34.4576 | 35.3015 | 35.8139 | 36.6485 | 36.8797 | 37.2594 | 37.4186 | 30.0929 | 29.4357 | 93.1157 | 34.1351 | 34.1283 | 35.5814 | 34.4174 | 34.0615 | 34.2431 | 35.5721 | 34.8822 | 34.7404 | 37.4933 | 36.3699 | 34.2458 | 34.8006 | 36.3492 | 36.9836 | 37.6696 | 36.352 | 34.4033 | 33.3897 | 35.0201 | 35.3966 | 33.2972 | 34.462 | 34.4717 | 33.6073 | 34.3718 | 34.4332 | 34.5597 | 33.9214 | 34.3682 | 35.1446 | 35.9072 | 35.4054 | 35.4513 | 34.3333 | 93.4599 | 93.6703 | 93.2676
2022-09-08 00:20 | 2:30 | 12.0447 | 13.378 | 16.4647 | 34.5298 | 34.538 | 34.8683 | 35.8583 | 35.9831 | 36.9002 | 37.3555 | 36.745 | 37.5197 | 33.4301 | 34.4557 | 35.2959 | 35.8215 | 36.6505 | 36.8746 | 37.2627 | 37.414 | 30.2086 | 29.6267 | 92.8595 | 34.2068 | 34.1382 | 35.5857 | 34.4022 | 34.0678 | 34.2453 | 35.564 | 34.8791 | 34.74 | 37.4872 | 36.3334 | 34.2408 | 34.7867 | 36.339 | 36.9998 | 37.6689 | 36.3661 | 34.4163 | 33.3968 | 35.0278 | 35.4161 | 33.3102 | 34.4595 | 34.4547 | 33.6294 | 34.3734 | 34.4265 | 34.5408 | 33.9078 | 34.3718 | 35.1643 | 35.9006 | 35.4049 | 35.4694 | 34.3368 | 93.4134 | 93.5494 | 93.3391
2022-09-08 00:21 | 2:31 | 11.9538 | 13.2978 | 16.3153 | 34.5662 | 34.5456 | 34.8648 | 35.8573 | 36.0022 | 36.8983 | 37.3758 | 36.7391 | 37.5178 | 34.4908 | 34.4537 | 35.2932 | 35.8104 | 36.632 | 36.8744 | 37.2382 | 37.4371 | 30.3497 | 29.8291 | 92.7942 | 34.3475 | 34.118 | 35.5697 | 34.41 | 34.0526 | 34.2442 | 35.5759 | 34.8872 | 34.7506 | 37.5097 | 36.3537 | 34.2429 | 34.7863 | 36.3699 | 36.9837 | 37.6907 | 36.371 | 34.3983 | 33.412 | 35.0226 | 35.4125 | 33.3258 | 34.4501 | 34.459 | 33.6244 | 34.3861 | 34.4158 | 34.5539 | 33.9129 | 34.3734 | 35.1774 | 35.9064 | 35.4218 | 35.4656 | 34.3312 | 93.3339 | 93.4638 | 93.2656
2022-09-08 00:21 | 2:31 | 11.8491 | 13.2043 | 16.22 | 34.4862 | 34.5389 | 34.862 | 35.8426 | 35.9899 | 36.9139 | 37.365 | 36.7536 | 37.514 | 34.4978 | 34.428 | 35.2937 | 35.8223 | 36.6397 | 36.8662 | 37.2458 | 37.4124 | 30.4238 | 29.9408 | 92.6192 | 34.349 | 34.1191 | 35.5596 | 34.416 | 34.0593 | 34.2497 | 35.5836 | 34.8802 | 34.7505 | 37.5044 | 36.3462 | 34.2338 | 34.7771 | 36.3334 | 36.9958 | 37.6746 | 36.3492 | 34.4215 | 33.4118 | 35.0408 | 35.4381 | 33.299 | 34.4713 | 34.4436 | 33.649 | 34.3814 | 34.4145 | 34.5292 | 33.9021 | 34.3861 | 35.1661 | 35.907 | 35.4215 | 35.4676 | 34.3294 | 93.1523 | 93.3711 | 93.1196
2022-09-08 00:21 | 2:31 | 11.71 | 13.0378 | 16.1986 | 34.4453 | 34.558 | 34.8848 | 35.824 | 35.9997 | 36.9121 | 37.374 | 36.7428 | 37.5338 | 34.4957 | 34.4265 | 35.2967 | 35.8167 | 36.6294 | 36.8664 | 37.2535 | 37.4273 | 30.5215 | 30.0842 | 92.4835 | 34.4218 | 34.1114 | 35.5711 | 34.4033 | 34.0616 | 34.2458 | 35.5663 | 34.8689 | 34.7588 | 37.5046 | 36.3532 | 34.2413 | 34.8028 | 36.3537 | 36.9818 | 37.6684 | 36.339 | 34.402 | 33.4173 | 35.0376 | 35.4184 | 33.3159 | 34.4616 | 34.4778 | 33.6371 | 34.3775 | 34.4145 | 34.5408 | 33.9176 | 34.3814 | 35.1698 | 35.9094 | 35.4423 | 35.4727 | 34.3301 | 93.0648 | 93.2817 | 93.1394
2022-09-08 00:21 | 2:31 | 11.578 | 12.9035 | 16.1029 | 34.4047 | 34.5571 | 34.8633 | 35.823 | 35.9573 | 36.904 | 37.3571 | 36.7461 | 37.5234 | 34.4833 | 34.4303 | 35.2864 | 35.8248 | 36.6527 | 36.8732 | 37.2404 | 37.4109 | 30.5964 | 30.1747 | 92.3391 | 34.4099 | 34.127 | 35.5714 | 34.4163 | 34.057 | 34.2408 | 35.5737 | 34.8735 | 34.7527 | 37.4977 | 36.3609 | 34.237 | 34.7864 | 36.3462 | 37.0006 | 37.6687 | 36.3699 | 34.3904 | 33.4086 | 35.0468 | 35.426 | 33.3243 | 34.4672 | 34.48 | 33.6273 | 34.392 | 34.4227 | 34.5173 | 33.9167 | 34.3775 | 35.1659 | 35.9048 | 35.4371 | 35.4866 | 34.3345 | 93.0862 | 93.2142 | 93.1175
2022-09-08 00:21 | 2:31 | 11.4204 | 12.7445 | 15.9623 | 34.352 | 34.5525 | 34.8765 | 35.8408 | 35.9947 | 36.9121 | 37.3576 | 36.7585 | 37.5391 | 34.4959 | 34.433 | 35.2914 | 35.8217 | 36.6404 | 36.8597 | 37.257 | 37.4221 | 30.6532 | 30.2923 | 92.2868 | 34.425 | 34.1075 | 35.6021 | 34.3983 | 34.0629 | 34.2429 | 35.5773 | 34.8898 | 34.7375 | 37.4966 | 36.3541 | 34.2363 | 34.7931 | 36.3532 | 37.0044 | 37.6737 | 36.3334 | 34.3822 | 33.4374 | 35.0425 | 35.4207 | 33.3135 | 34.4415 | 34.4678 | 33.6322 | 34.3765 | 34.4188 | 34.5357 | 33.9284 | 34.392 | 35.1691 | 35.892 | 35.428 | 35.4689 | 34.3213 | 92.894 | 93.0796 | 92.9821
2022-09-08 00:21 | 2:31 | 11.2559 | 12.5909 | 15.8884 | 34.4491 | 34.5464 | 34.868 | 35.8444 | 35.9897 | 36.9116 | 37.3861 | 36.7375 | 37.5359 | 34.4665 | 34.4242 | 35.2839 | 35.8227 | 36.6412 | 36.8724 | 37.2694 | 37.4077 | 30.7129 | 30.3922 | 92.4055 | 34.3905 | 34.1158 | 35.5746 | 34.4215 | 34.0489 | 34.2338 | 35.5681 | 34.8676 | 34.744 | 37.518 | 36.3481 | 34.2434 | 34.7992 | 36.3609 | 36.9987 | 37.6826 | 36.3537 | 34.3783 | 33.4263 | 35.0499 | 35.4396 | 33.3503 | 34.4315 | 34.486 | 33.6206 | 34.3869 | 34.3866 | 34.5425 | 33.9095 | 34.3765 | 35.1775 | 35.8877 | 35.4219 | 35.4667 | 34.323 | 92.7725 | 92.9671 | 92.8695
2022-09-08 00:22 | 2:31 | 10.2197 | 11.2067 | 15.5335 | 34.3969 | 34.5564 | 34.852 | 35.8263 | 35.997 | 36.9164 | 37.3663 | 36.754 | 37.5205 | 34.4603 | 34.4164 | 35.2896 | 35.8218 | 36.6322 | 36.8477 | 37.2604 | 37.4217 | 30.7655 | 30.4523 | 92.371 | 34.4688 | 34.1157 | 35.5696 | 34.402 | 34.0391 | 34.2413 | 35.5558 | 34.9005 | 34.7531 | 37.5089 | 36.3611 | 34.2353 | 34.7823 | 36.3541 | 36.9608 | 37.6765 | 36.3462 | 34.3652 | 33.3912 | 35.0517 | 35.4337 | 33.329 | 34.4031 | 34.4632 | 33.63 | 34.3803 | 34.4416 | 34.5249 | 33.9174 | 34.3869 | 35.1731 | 35.8871 | 35.4154 | 35.4758 | 34.3019 | 92.7498 | 92.8667 | 92.8144
2022-09-08 00:22 | 2:32 | 11.4342 | 10.3577 | 15.4448 | 34.2769 | 34.5572 | 34.8506 | 35.8347 | 35.9906 | 36.9034 | 37.36 | 36.7671 | 37.5483 | 34.4801 | 34.407 | 35.2833 | 35.8088 | 36.6356 | 36.8612 | 37.2465 | 37.4151 | 30.7431 | 30.51 | 92.5408 | 34.4595 | 34.0988 | 35.581 | 34.3904 | 34.0533 | 34.237 | 35.5617 | 34.879 | 34.7357 | 37.4834 | 36.3194 | 34.2191 | 34.7729 | 36.3481 | 36.9934 | 37.6673 | 36.3532 | 34.3809 | 33.4068 | 35.069 | 35.4198 | 33.3341 | 34.4401 | 34.4693 | 33.6323 | 34.3792 | 34.4127 | 34.5307 | 33.9459 | 34.3803 | 35.186 | 35.9209 | 35.4238 | 35.4611 | 34.3265 | 92.6193 | 92.7461 | 92.7124
2022-09-08 00:22 | 2:32 | 13.5161 | 11.1363 | 16.308 | 34.3042 | 34.5596 | 34.8454 | 35.8172 | 35.9729 | 36.9114 | 37.3811 | 36.7587 | 37.5255 | 34.4601 | 34.4045 | 35.2748 | 35.8143 | 36.6329 | 36.8563 | 37.2516 | 37.4029 | 30.8028 | 30.5857 | 92.5363 | 34.5206 | 34.103 | 35.5622 | 34.3822 | 34.0594 | 34.2363 | 35.5833 | 34.8893 | 34.7551 | 37.4985 | 36.3393 | 34.2244 | 34.7783 | 36.3611 | 37.0025 | 37.6878 | 36.3609 | 34.3581 | 33.4252 | 35.0484 | 35.4435 | 33.3571 | 34.4203 | 34.499 | 33.6206 | 34.3854 | 34.4259 | 34.5005 | 33.9201 | 34.3792 | 35.196 | 35.8981 | 35.4549 | 35.4546 | 34.3377 | 92.5261 | 92.6181 | 92.6954
2022-09-08 00:22 | 2:32 | 15.1226 | 12.3069 | 17.4547 | 34.3406 | 34.5483 | 34.8439 | 35.8002 | 35.946 | 36.8956 | 37.3542 | 36.7623 | 37.5199 | 34.469 | 34.4054 | 35.2867 | 35.8204 | 36.6218 | 36.8399 | 37.2362 | 37.4043 | 30.863 | 30.6419 | 92.6206 | 34.5315 | 34.115 | 35.5661 | 34.3783 | 34.0372 | 34.2434 | 35.5661 | 34.8721 | 34.7369 | 37.5056 | 36.3187 | 34.2227 | 34.7841 | 36.3194 | 36.9791 | 37.6731 | 36.3541 | 34.3657 | 33.4166 | 35.0601 | 35.4311 | 33.3249 | 34.4203 | 34.49 | 33.6302 | 34.3719 | 34.4147 | 34.5194 | 33.9294 | 34.3854 | 35.1759 | 35.9041 | 35.4083 | 35.4915 | 34.341 | 92.3538 | 92.5231 | 92.6046
2022-09-08 00:22 | 2:32 | 16.4147 | 13.668 | 18.6178 | 34.4349 | 34.5636 | 34.8516 | 35.785 | 35.9585 | 36.8813 | 37.3366 | 36.7439 | 37.5163 | 34.4537 | 34.399 | 35.2729 | 35.8114 | 36.6285 | 36.8359 | 37.2452 | 37.4097 | 30.9012 | 30.6873 | 92.7042 | 34.5201 | 34.0952 | 35.5742 | 34.3652 | 34.0452 | 34.2353 | 35.5754 | 34.871 | 34.7222 | 37.4847 | 36.3418 | 34.2192 | 34.7758 | 36.3393 | 36.9796 | 37.6665 | 36.3481 | 34.3695 | 33.4149 | 35.078 | 35.4316 | 33.3475 | 34.4028 | 34.4802 | 33.6172 | 34.3863 | 34.406 | 34.5104 | 33.9197 | 34.3719 | 35.1935 | 35.8875 | 35.4325 | 35.4697 | 34.3531 | 92.2913 | 92.4006 | 92.4481
2022-09-08 00:22 | 2:32 | 17.5117 | 15.066 | 19.6932 | 34.5903 | 34.568 | 34.8468 | 35.7858 | 35.9615 | 36.9079 | 37.3601 | 36.7524 | 37.5291 | 34.4765 | 34.4106 | 35.2452 | 35.8001 | 36.6081 | 36.8345 | 37.2474 | 37.3889 | 30.9436 | 30.7363 | 92.7104 | 34.5794 | 34.1014 | 35.5494 | 34.3809 | 34.0348 | 34.2191 | 35.5646 | 34.8563 | 34.7384 | 37.5001 | 36.3398 | 34.2096 | 34.7694 | 36.3187 | 36.9892 | 37.6566 | 36.3611 | 34.3469 | 33.427 | 35.0691 | 35.4385 | 33.3471 | 34.41 | 34.4823 | 33.6189 | 34.3726 | 34.4066 | 34.4991 | 33.9222 | 34.3863 | 35.1983 | 35.8689 | 35.4372 | 35.4855 | 34.3274 | 92.1915 | 92.3134 | 92.3962
2022-09-08 00:23 | 2:33 | 18.5133 | 16.5363 | 20.7377 | 34.6802 | 34.5542 | 34.8321 | 35.7874 | 35.9584 | 36.8935 | 37.351 | 36.7297 | 37.5022 | 34.4607 | 34.3932 | 35.2633 | 35.8069 | 36.6045 | 36.8384 | 37.2456 | 37.4007 | 30.9582 | 30.7997 | 92.7649 | 34.616 | 34.0822 | 35.5465 | 34.3581 | 34.0419 | 34.2244 | 35.547 | 34.869 | 34.7303 | 37.4924 | 36.3211 | 34.2236 | 34.7785 | 36.3418 | 36.9772 | 37.6594 | 36.3194 | 34.3475 | 33.4377 | 35.0785 | 35.4235 | 33.3596 | 34.4062 | 34.4894 | 33.6033 | 34.3944 | 34.4136 | 34.4986 | 33.9308 | 34.3726 | 35.1803 | 35.8888 | 35.4279 | 35.4813 | 34.3317 | 92.1885 | 92.3653 | 92.4408
2022-09-08 00:23 | 2:33 | 19.3834 | 17.9111 | 21.7064 | 34.7548 | 34.5784 | 34.8357 | 35.777 | 35.9642 | 36.911 | 37.3585 | 36.7323 | 37.5238 | 34.4725 | 34.4041 | 35.2607 | 35.7789 | 36.6108 | 36.8319 | 37.231 | 37.4213 | 31.0043 | 30.8352 | 92.8293 | 34.6179 | 34.0663 | 35.5323 | 34.3657 | 34.0411 | 34.2227 | 35.5642 | 34.8709 | 34.7313 | 37.4772 | 36.3304 | 34.219 | 34.761 | 36.3398 | 36.9701 | 37.6639 | 36.3393 | 34.3614 | 33.4119 | 35.0841 | 35.4418 | 33.3506 | 34.4086 | 34.4669 | 33.6153 | 34.385 | 34.3965 | 34.5005 | 33.9129 | 34.3944 | 35.175 | 35.8779 | 35.4374 | 35.49 | 34.3269 | 92.2197 | 92.4175 | 92.4724
2022-09-08 00:23 | 2:33 | 20.2045 | 19.2577 | 22.4777 | 34.8029 | 34.5839 | 34.8193 | 35.7979 | 35.9447 | 36.8906 | 37.359 | 36.7437 | 37.5043 | 34.462 | 34.4192 | 35.2595 | 35.7971 | 36.6005 | 36.8316 | 37.2349 | 37.4143 | 31.046 | 30.8679 | 92.8237 | 34.6072 | 34.1004 | 35.5382 | 34.3695 | 34.0384 | 34.2192 | 35.5537 | 34.8662 | 34.7326 | 37.487 | 36.3451 | 34.2191 | 34.7737 | 36.3211 | 36.9628 | 37.6769 | 36.3187 | 34.3609 | 33.4121 | 35.0706 | 35.4464 | 33.3591 | 34.3894 | 34.4876 | 33.6249 | 34.3849 | 34.4198 | 34.4877 | 33.9268 | 34.385 | 35.1964 | 35.8838 | 35.4459 | 35.4742 | 34.3143 | 92.3276 | 92.5058 | 92.491
2022-09-08 00:23 | 2:33 | 20.9979 | 20.4866 | 23.2471 | 34.8289 | 34.5676 | 34.8401 | 35.7791 | 35.9614 | 36.9127 | 37.3639 | 36.7273 | 37.5173 | 34.4569 | 34.4095 | 35.2474 | 35.8025 | 36.6184 | 36.8286 | 37.255 | 37.4276 | 31.0912 | 30.9064 | 92.883 | 34.6499 | 34.0833 | 35.5397 | 34.3469 | 34.0352 | 34.2096 | 35.5691 | 34.8498 | 34.7101 | 37.4822 | 36.328 | 34.2241 | 34.7776 | 36.3304 | 36.9733 | 37.6744 | 36.3418 | 34.3542 | 33.4409 | 35.0877 | 35.4219 | 33.3594 | 34.3925 | 34.4797 | 33.6242 | 34.4131 | 34.4169 | 34.4942 | 33.9425 | 34.3849 | 35.1917 | 35.8865 | 35.4283 | 35.4815 | 34.3163 | 92.3834 | 92.6051 | 92.558
2022-09-08 00:23 | 2:33 | 21.7128 | 21.6376 | 23.9892 | 34.9485 | 34.5672 | 34.8231 | 35.7622 | 35.9443 | 36.897 | 37.382 | 36.7324 | 37.5177 | 34.4577 | 34.4173 | 35.2724 | 35.7769 | 36.6283 | 36.8238 | 37.2426 | 37.4102 | 31.0998 | 30.9498 | 92.9656 | 34.6239 | 34.0806 | 35.5426 | 34.3475 | 34.0227 | 34.2236 | 35.5728 | 34.8656 | 34.7196 | 37.4755 | 36.3295 | 34.2243 | 34.752 | 36.3451 | 36.9672 | 37.6808 | 36.3398 | 34.3628 | 33.425 | 35.0801 | 35.4416 | 33.384 | 34.3826 | 34.4893 | 33.6189 | 34.394 | 34.4241 | 34.4987 | 33.9322 | 34.4131 | 35.1904 | 35.8741 | 35.4347 | 35.4898 | 34.3183 | 92.4733 | 92.705 | 92.6103
2022-09-08 00:23 | 2:33 | 23.469 | 22.2893 | 24.4651 | 34.9877 | 34.5646 | 34.851 | 35.7736 | 35.9402 | 36.8984 | 37.4022 | 36.7459 | 37.5212 | 34.4593 | 34.408 | 35.2602 | 35.8116 | 36.6046 | 36.831 | 37.2656 | 37.41 | 31.0487 | 25.3159 | 93.0456 | 34.6044 | 34.093 | 35.5394 | 34.3614 | 34.0294 | 34.219 | 35.5488 | 34.8524 | 34.735 | 37.4888 | 36.3211 | 34.2164 | 34.7638 | 36.328 | 36.9759 | 37.6662 | 36.3211 | 34.3566 | 33.4279 | 35.1009 | 35.4366 | 33.3699 | 34.3957 | 34.4851 | 33.6276 | 34.3927 | 34.4261 | 34.4771 | 33.9235 | 34.394 | 35.1813 | 35.8714 | 35.4315 | 35.4918 | 34.3306 | 92.5585 | 92.8193 | 92.6548
2022-09-08 00:24 | 2:33 | 27.7109 | 27.6005 | 25.0927 | 35.176 | 34.5722 | 34.8427 | 35.7669 | 35.9419 | 36.9108 | 37.3755 | 36.7356 | 37.5026 | 34.4451 | 34.411 | 35.2514 | 35.7865 | 36.6038 | 36.84 | 37.2574 | 37.407 | 31.1201 | 27.9424 | 93.1449 | 34.6671 | 34.0839 | 35.5489 | 34.3609 | 34.0396 | 34.2191 | 35.5705 | 34.8712 | 34.7092 | 37.4862 | 36.3172 | 34.2163 | 34.7626 | 36.3295 | 36.9565 | 37.6759 | 36.3304 | 34.3509 | 33.4212 | 35.0994 | 35.444 | 33.3804 | 34.4073 | 34.4894 | 33.6315 | 34.4089 | 34.409 | 34.4866 | 33.9369 | 34.3927 | 35.1691 | 35.8736 | 35.4348 | 35.4896 | 34.32 | 92.6668 | 92.9168 | 92.7738
2022-09-08 00:24 | 2:34 | 30.2811 | 29.1301 | 26.1506 | 35.2161 | 34.5739 | 34.8539 | 35.7946 | 35.9612 | 36.9019 | 37.3954 | 36.7276 | 37.5272 | 34.4578 | 34.3913 | 35.2582 | 35.8065 | 36.588 | 36.835 | 37.2752 | 37.4137 | 31.6201 | 29.4346 | 93.2193 | 34.6781 | 34.0821 | 35.5454 | 34.3542 | 34.0156 | 34.2241 | 35.5755 | 34.8663 | 34.7268 | 37.4796 | 36.3188 | 34.2182 | 34.7638 | 36.3211 | 36.9676 | 37.6756 | 36.3451 | 34.3471 | 33.4334 | 35.0838 | 35.4394 | 33.3768 | 34.3946 | 34.4819 | 33.628 | 34.4066 | 34.4133 | 34.4769 | 33.9212 | 34.4089 | 35.1818 | 35.8777 | 35.449 | 35.4981 | 34.3195 | 92.7535 | 93.0109 | 92.8736
2022-09-08 00:24 | 2:34 | 31.2808 | 29.5763 | 27.1254 | 35.3661 | 34.5524 | 34.8299 | 35.7912 | 35.9457 | 36.8895 | 37.3948 | 36.7482 | 37.5182 | 34.4566 | 34.3945 | 35.2529 | 35.7891 | 36.5909 | 36.8435 | 37.2684 | 37.4233 | 32.2606 | 29.9669 | 93.2815 | 34.7516 | 34.068 | 35.5339 | 34.3628 | 34.0271 | 34.2243 | 35.567 | 34.8543 | 34.7114 | 37.4837 | 36.3218 | 34.2093 | 34.7718 | 36.3172 | 36.9592 | 37.6713 | 36.328 | 34.3478 | 33.4399 | 35.0894 | 35.4209 | 33.3899 | 34.3862 | 34.5033 | 33.6168 | 34.4207 | 34.4082 | 34.4737 | 33.9476 | 34.4066 | 35.1864 | 35.881 | 35.4322 | 35.5041 | 34.3143 | 92.8257 | 93.1237 | 92.9205
2022-09-08 00:24 | 2:34 | 31.7147 | 29.751 | 27.6868 | 35.4731 | 34.5728 | 34.8445 | 35.7989 | 35.9609 | 36.8897 | 37.4032 | 36.729 | 37.5122 | 34.4468 | 34.3949 | 35.2634 | 35.8077 | 36.6224 | 36.8342 | 37.2831 | 37.4113 | 32.7617 | 30.2806 | 93.3476 | 34.7238 | 34.0711 | 35.5371 | 34.3566 | 34.0332 | 34.2164 | 35.5662 | 34.8425 | 34.7037 | 37.4933 | 36.3322 | 34.2117 | 34.7819 | 36.3188 | 36.9695 | 37.682 | 36.3295 | 34.3438 | 33.4347 | 35.0885 | 35.4485 | 33.3983 | 34.3777 | 34.5032 | 33.6242 | 34.409 | 34.4096 | 34.4859 | 33.9157 | 34.4207 | 35.19 | 35.862 | 35.4316 | 35.4897 | 34.2997 | 92.9613 | 93.2879 | 92.9886
2022-09-08 00:24 | 2:34 | 31.9961 | 29.9487 | 28.2229 | 35.4751 | 34.58 | 34.8514 | 35.8132 | 35.9678 | 36.9089 | 37.4144 | 36.7522 | 37.5382 | 34.4566 | 34.401 | 35.269 | 35.8107 | 36.5841 | 36.8369 | 37.276 | 37.3959 | 33.1494 | 30.5049 | 93.378 | 34.7839 | 34.0687 | 35.5385 | 34.3509 | 34.0245 | 34.2163 | 35.567 | 34.8575 | 34.7361 | 37.4841 | 36.332 | 34.2375 | 34.7749 | 36.3218 | 36.9755 | 37.6883 | 36.3211 | 34.3388 | 33.4407 | 35.0974 | 35.4421 | 33.3957 | 34.3956 | 34.5095 | 33.6367 | 34.411 | 34.4053 | 34.4734 | 33.9491 | 34.409 | 35.1863 | 35.8616 | 35.428 | 35.493 | 34.3094 | 93.0374 | 93.3842 | 93.0301
2022-09-08 00:24 | 2:34 | 32.2164 | 30.11 | 28.6011 | 35.5812 | 34.5568 | 34.8592 | 35.8178 | 35.9624 | 36.9148 | 37.4151 | 36.75 | 37.5284 | 34.4503 | 34.3877 | 35.2766 | 35.8125 | 36.5861 | 36.8456 | 37.2772 | 37.4156 | 33.6533 | 30.6747 | 93.3628 | 34.7278 | 34.0763 | 35.5214 | 34.3471 | 34.0348 | 34.2182 | 35.5811 | 34.8467 | 34.7097 | 37.4838 | 36.3292 | 34.2145 | 34.7864 | 36.3322 | 36.9587 | 37.6868 | 36.3172 | 34.34 | 33.4344 | 35.0971 | 35.4331 | 33.4049 | 34.3873 | 34.4768 | 33.6265 | 34.4179 | 34.4288 | 34.4576 | 33.9323 | 34.411 | 35.2001 | 35.8607 | 35.4576 | 35.4969 | 34.3299 | 93.1575 | 93.4909 | 93.1283
2022-09-08 00:25 | 2:35 | 32.3146 | 30.2612 | 28.8702 | 35.616 | 34.5423 | 34.8535 | 35.8146 | 35.954 | 36.9181 | 37.4183 | 36.7407 | 37.5186 | 34.4472 | 34.3966 | 35.2701 | 35.8121 | 36.5848 | 36.8457 | 37.3011 | 37.4247 | 33.9528 | 30.7921 | 93.4308 | 34.7285 | 34.052 | 35.5389 | 34.3478 | 34.031 | 34.2093 | 35.5692 | 34.8622 | 34.7252 | 37.4748 | 36.3467 | 34.2149 | 34.777 | 36.332 | 36.9622 | 37.6851 | 36.3188 | 34.3473 | 33.436 | 35.1063 | 35.438 | 33.4249 | 34.3965 | 34.5128 | 33.6321 | 34.3964 | 34.4007 | 34.4557 | 33.9327 | 34.4179 | 35.1846 | 35.8546 | 35.4256 | 35.4851 | 34.3025 | 93.3163 | 93.6084 | 93.1822
2022-09-08 00:25 | 2:35 | 32.3997 | 30.4186 | 29.2032 | 35.7555 | 34.5566 | 34.8568 | 35.8258 | 35.9541 | 36.9104 | 37.4251 | 36.7293 | 37.5343 | 34.4433 | 34.3931 | 35.2542 | 35.8005 | 36.592 | 36.8586 | 37.2958 | 37.4173 | 34.0374 | 30.9031 | 93.5068 | 34.8352 | 34.0624 | 35.5367 | 34.3438 | 34.0401 | 34.2117 | 35.5724 | 34.8531 | 34.7296 | 37.4833 | 36.3279 | 34.225 | 34.7661 | 36.3292 | 36.9534 | 37.6847 | 36.3218 | 34.3508 | 33.4427 | 35.1248 | 35.4583 | 33.4186 | 34.3668 | 34.4866 | 33.6276 | 34.4229 | 34.4162 | 34.4537 | 33.9484 | 34.3964 | 35.196 | 35.8637 | 35.4603 | 35.4865 | 34.3193 | 93.4348 | 93.7606 | 93.3411
2022-09-08 00:25 | 2:35 | 32.4817 | 30.5789 | 29.4756 | 35.7951 | 34.5833 | 34.8502 | 35.8289 | 35.9847 | 36.9194 | 37.4333 | 36.7434 | 37.5379 | 34.4488 | 34.42 | 35.2619 | 35.7811 | 36.5853 | 36.8558 | 37.3037 | 37.418 | 34.0129 | 30.9766 | 93.6076 | 34.8406 | 34.0562 | 35.5431 | 34.3388 | 34.0324 | 34.2375 | 35.5762 | 34.8536 | 34.7162 | 37.4812 | 36.3369 | 34.2169 | 34.7782 | 36.3467 | 36.9721 | 37.6897 | 36.3322 | 34.3578 | 33.4371 | 35.1155 | 35.4589 | 33.4327 | 34.3864 | 34.4986 | 33.6424 | 34.4296 | 34.4172 | 34.428 | 33.9545 | 34.4229 | 35.1962 | 35.8768 | 35.433 | 35.4889 | 34.3045 | 93.5838 | 93.9232 | 93.4323
2022-09-08 00:25 | 2:35 | 32.6037 | 30.6846 | 29.6856 | 35.7726 | 34.5597 | 34.8461 | 35.8377 | 35.9741 | 36.9131 | 37.4411 | 36.7582 | 37.5117 | 34.4307 | 34.3828 | 35.2481 | 35.7945 | 36.5922 | 36.8525 | 37.304 | 37.42 | 33.9167 | 31.0448 | 93.6477 | 34.9588 | 34.0637 | 35.5191 | 34.34 | 34.0281 | 34.2145 | 35.5703 | 34.8531 | 34.7217 | 37.4869 | 36.3409 | 34.2249 | 34.7655 | 36.3279 | 36.9689 | 37.6899 | 36.332 | 34.3539 | 33.4493 | 35.1236 | 35.4423 | 33.4257 | 34.3865 | 34.5178 | 33.6415 | 34.4419 | 34.4061 | 34.4265 | 33.9297 | 34.4296 | 35.2052 | 35.8634 | 35.4473 | 35.4954 | 34.3065 | 93.7554 | 94.1264 | 93.5518
2022-09-08 00:25 | 2:35 | 32.8005 | 30.786 | 29.946 | 35.8056 | 34.5408 | 34.8523 | 35.8597 | 35.9807 | 36.8977 | 37.4316 | 36.7549 | 37.5465 | 34.4567 | 34.3939 | 35.2527 | 35.8043 | 36.5957 | 36.8458 | 37.3134 | 37.4267 | 33.8359 | 31.1344 | 93.6727 | 34.9473 | 34.0627 | 35.5235 | 34.3473 | 34.0382 | 34.2149 | 35.5772 | 34.8587 | 34.7189 | 37.4788 | 36.343 | 34.2057 | 34.7834 | 36.3369 | 36.9682 | 37.6966 | 36.3292 | 34.3394 | 33.4599 | 35.1273 | 35.4656 | 33.43 | 34.3892 | 34.5075 | 33.6243 | 34.44 | 34.4011 | 34.4303 | 33.9463 | 34.4419 | 35.1905 | 35.8721 | 35.4492 | 35.4883 | 34.3047 | 93.9012 | 94.3173 | 93.599
2022-09-08 00:25 | 2:35 | 32.9464 | 30.8873 | 30.1609 | 35.8318 | 34.5539 | 34.8551 | 35.8512 | 35.9785 | 36.9164 | 37.4469 | 36.7546 | 37.5316 | 34.4334 | 34.4055 | 35.2537 | 35.814 | 36.5745 | 36.8664 | 37.3116 | 37.4136 | 33.7958 | 31.1962 | 93.8298 | 34.9472 | 34.065 | 35.5356 | 34.3508 | 34.0408 | 34.225 | 35.5842 | 34.8707 | 34.7299 | 37.4699 | 36.3442 | 34.2004 | 34.7798 | 36.3409 | 36.9587 | 37.7002 | 36.3467 | 34.3401 | 33.4542 | 35.1014 | 35.452 | 33.4484 | 34.3744 | 34.5197 | 33.6506 | 34.4337 | 34.4159 | 34.433 | 33.9383 | 34.44 | 35.2125 | 35.8733 | 35.4589 | 35.4956 | 34.2905 | 94.1432 | 94.5221 | 93.7812
2022-09-08 00:26 | 2:35 | 33.017 | 30.9575 | 30.3219 | 35.8915 | 34.5292 | 34.8592 | 35.8347 | 35.9702 | 36.9245 | 37.4318 | 36.7366 | 37.5266 | 34.4463 | 34.3849 | 35.2829 | 35.7996 | 36.58 | 36.8628 | 37.3085 | 37.4082 | 33.7465 | 31.229 | 93.8661 | 34.9915 | 34.0769 | 35.5253 | 34.3578 | 34.0242 | 34.2169 | 35.5812 | 34.8436 | 34.7122 | 37.4853 | 36.3408 | 34.2219 | 34.751 | 36.343 | 36.9537 | 37.6873 | 36.3279 | 34.347 | 33.4513 | 35.1169 | 35.475 | 33.4408 | 34.3846 | 34.5078 | 33.6374 | 34.4416 | 34.418 | 34.4242 | 33.9322 | 34.4337 | 35.1989 | 35.8592 | 35.4499 | 35.4876 | 34.3021 | 94.2589 | 94.6997 | 93.9104
2022-09-08 00:26 | 2:36 | 33.0953 | 31.0344 | 30.4462 | 35.9381 | 34.5408 | 34.8646 | 35.8317 | 35.9872 | 36.9073 | 37.4307 | 36.7563 | 37.5236 | 34.4521 | 34.4143 | 35.2629 | 35.82 | 36.5851 | 36.8592 | 37.3199 | 37.4347 | 33.6691 | 31.2772 | 93.8358 | 34.9477 | 34.0486 | 35.525 | 34.3539 | 34.0146 | 34.2249 | 35.577 | 34.8659 | 34.7352 | 37.4759 | 36.3244 | 34.1953 | 34.783 | 36.3442 | 36.9481 | 37.7076 | 36.3369 | 34.3548 | 33.4633 | 35.1327 | 35.4505 | 33.4468 | 34.3785 | 34.5153 | 33.6405 | 34.456 | 34.4385 | 34.4164 | 33.9493 | 34.4416 | 35.1907 | 35.8638 | 35.4334 | 35.508 | 34.2934 | 94.4286 | 94.8846 | 94.032
2022-09-08 00:26 | 2:36 | 33.1027 | 31.0777 | 30.5796 | 35.9785 | 34.5173 | 34.8447 | 35.8339 | 35.9767 | 36.901 | 37.4525 | 36.7391 | 37.5415 | 34.4561 | 34.3972 | 35.2519 | 35.8032 | 36.5759 | 36.8485 | 37.3096 | 37.4217 | 33.5746 | 31.3184 | 93.9918 | 34.9458 | 34.0662 | 35.523 | 34.3394 | 34.0182 | 34.2057 | 35.5733 | 34.8516 | 34.7041 | 37.4788 | 36.3448 | 34.2009 | 34.7759 | 36.3408 | 36.9549 | 37.6913 | 36.3409 | 34.3098 | 33.4543 | 35.1318 | 35.4651 | 33.4573 | 34.3644 | 34.5134 | 33.6524 | 34.4223 | 34.423 | 34.407 | 33.9305 | 34.456 | 35.2052 | 35.8519 | 35.4428 | 35.4894 | 34.3006 | 94.6034 | 95.0656 | 94.1296
2022-09-08 00:26 | 2:36 | 33.1492 | 31.1564 | 30.7293 | 35.9899 | 34.5357 | 34.8469 | 35.8338 | 35.9672 | 36.9067 | 37.4523 | 36.7397 | 37.539 | 34.4321 | 34.3841 | 35.255 | 35.8008 | 36.5747 | 36.862 | 37.3219 | 37.4145 | 33.4792 | 31.3562 | 93.9911 | 34.9936 | 34.0523 | 35.5252 | 34.3401 | 34.0314 | 34.2004 | 35.574 | 34.8466 | 34.7249 | 37.4901 | 36.3404 | 34.2041 | 34.7732 | 36.3244 | 36.9604 | 37.702 | 36.343 | 34.3347 | 33.4656 | 35.1413 | 35.4733 | 33.4798 | 34.3547 | 34.5185 | 33.6326 | 34.4529 | 34.4348 | 34.4045 | 33.9507 | 34.4223 | 35.1961 | 35.8632 | 35.4494 | 35.5103 | 34.3007 | 94.7642 | 95.2276 | 94.2785
2022-09-08 00:26 | 2:36 | 33.1649 | 31.196 | 30.8276 | 36.0672 | 34.5425 | 34.8391 | 35.8337 | 35.9685 | 36.9071 | 37.4491 | 36.7473 | 37.5396 | 34.439 | 34.3941 | 35.2413 | 35.8129 | 36.5738 | 36.8527 | 37.3258 | 37.4308 | 33.4101 | 31.3921 | 93.9628 | 35.0129 | 34.0527 | 35.5283 | 34.347 | 34.0252 | 34.2219 | 35.5691 | 34.8406 | 34.7227 | 37.4806 | 36.3274 | 34.204 | 34.7983 | 36.3448 | 36.9453 | 37.6782 | 36.3442 | 34.3384 | 33.4794 | 35.1279 | 35.4699 | 33.4783 | 34.3855 | 34.5114 | 33.642 | 34.4382 | 34.426 | 34.4054 | 33.9552 | 34.4529 | 35.207 | 35.853 | 35.4684 | 35.4984 | 34.2948 | 94.9669 | 95.4062 | 94.2968
2022-09-08 00:26 | 2:36 | 33.2889 | 31.2451 | 30.9446 | 36.1039 | 34.5249 | 34.8455 | 35.8196 | 35.955 | 36.9036 | 37.4523 | 36.7317 | 37.5263 | 34.4377 | 34.4037 | 35.2524 | 35.7997 | 36.5756 | 36.8618 | 37.3125 | 37.4061 | 33.3994 | 31.4133 | 94.0878 | 34.954 | 34.0464 | 35.5288 | 34.3548 | 34.0117 | 34.1953 | 35.5713 | 34.8479 | 34.7186 | 37.4696 | 36.3329 | 34.1934 | 34.7899 | 36.3404 | 36.9551 | 37.6867 | 36.3408 | 34.3359 | 33.4856 | 35.1463 | 35.4643 | 33.4636 | 34.3825 | 34.5304 | 33.6579 | 34.4355 | 34.422 | 34.399 | 33.9469 | 34.4382 | 35.2019 | 35.8595 | 35.4325 | 35.4894 | 34.2902 | 95.0317 | 95.5288 | 94.4236
2022-09-08 00:27 | 2:37 | 33.4196 | 31.2908 | 31.1005 | 36.0239 | 34.5307 | 34.8481 | 35.8302 | 35.9618 | 36.9011 | 37.4517 | 36.7394 | 37.5186 | 34.4175 | 34.3853 | 35.2484 | 35.8036 | 36.5704 | 36.8488 | 37.3151 | 37.387 | 33.3639 | 31.409 | 93.9948 | 35.0823 | 34.0525 | 35.5242 | 34.3098 | 34.0159 | 34.2009 | 35.5573 | 34.839 | 34.7137 | 37.4845 | 36.3484 | 34.1987 | 34.7642 | 36.3274 | 36.9356 | 37.6906 | 36.3244 | 34.3236 | 33.4688 | 35.1416 | 35.4545 | 33.4686 | 34.3695 | 34.5156 | 33.6409 | 34.4299 | 34.4314 | 34.4106 | 33.9528 | 34.4355 | 35.2086 | 35.8413 | 35.4415 | 35.5001 | 34.2858 | 95.1639 | 95.6418 | 94.5395
2022-09-08 00:27 | 2:37 | 33.4864 | 31.335 | 31.2033 | 36.2075 | 34.5005 | 34.841 | 35.822 | 35.9574 | 36.8941 | 37.4431 | 36.7315 | 37.5241 | 34.4455 | 34.3991 | 35.2428 | 35.8136 | 36.5609 | 36.8384 | 37.3156 | 37.4062 | 33.4091 | 31.4366 | 93.8796 | 35.0746 | 34.0395 | 35.5291 | 34.3347 | 34.0216 | 34.2041 | 35.5767 | 34.8461 | 34.6917 | 37.4728 | 36.3324 | 34.1919 | 34.7734 | 36.3329 | 36.9412 | 37.6901 | 36.3448 | 34.3314 | 33.48 | 35.1228 | 35.4452 | 33.4865 | 34.3678 | 34.5354 | 33.6457 | 34.443 | 34.4409 | 34.3932 | 33.9544 | 34.4299 | 35.2092 | 35.8564 | 35.4555 | 35.4823 | 34.2951 | 95.159 | 95.7023 | 94.5684
2022-09-08 00:27 | 2:37 | 33.476 | 31.3733 | 31.2974 | 36.1667 | 34.5194 | 34.8453 | 35.8273 | 35.9645 | 36.9036 | 37.4524 | 36.7508 | 37.5315 | 34.4333 | 34.3877 | 35.239 | 35.8097 | 36.551 | 36.8492 | 37.3021 | 37.3957 | 33.3566 | 31.4366 | 93.7103 | 35.0169 | 34.0293 | 35.5153 | 34.3384 | 34.03 | 34.204 | 35.5635 | 34.8642 | 34.7001 | 37.4709 | 36.3616 | 34.1921 | 34.7721 | 36.3484 | 36.9393 | 37.6889 | 36.3404 | 34.3199 | 33.4719 | 35.1299 | 35.4622 | 33.4845 | 34.3802 | 34.528 | 33.6469 | 34.4311 | 34.4174 | 34.4041 | 33.9469 | 34.443 | 35.2047 | 35.845 | 35.4561 | 35.5108 | 34.2805 | 95.2524 | 95.8093 | 94.575
2022-09-08 00:27 | 2:37 | 33.6887 | 31.4307 | 31.4107 | 36.3508 | 34.5104 | 34.8226 | 35.8317 | 35.959 | 36.8907 | 37.4613 | 36.7352 | 37.5495 | 34.4184 | 34.3896 | 35.2389 | 35.7907 | 36.555 | 36.8517 | 37.3118 | 37.3806 | 33.4489 | 31.4536 | 93.5344 | 35.038 | 34.0477 | 35.5106 | 34.3359 | 34.0272 | 34.1934 | 35.5527 | 34.8403 | 34.7087 | 37.4704 | 36.3286 | 34.1969 | 34.7712 | 36.3324 | 36.9427 | 37.6833 | 36.3274 | 34.3405 | 33.4812 | 35.1319 | 35.4695 | 33.5087 | 34.3605 | 34.5302 | 33.6585 | 34.4389 | 34.4221 | 34.4192 | 33.9445 | 34.4311 | 35.1812 | 35.8419 | 35.447 | 35.4871 | 34.2808 | 95.312 | 95.9162 | 94.7191
2022-09-08 00:27 | 2:37 | 33.6631 | 31.446 | 31.5379 | 36.3694 | 34.4991 | 34.8373 | 35.8385 | 35.9522 | 36.8905 | 37.4347 | 36.7438 | 37.5536 | 34.4355 | 34.3913 | 35.2459 | 35.7991 | 36.5805 | 36.8484 | 37.3174 | 37.3836 | 33.5279 | 31.4572 | 93.4331 | 35.008 | 34.0783 | 35.5228 | 34.3236 | 34.0153 | 34.1987 | 35.5565 | 34.8391 | 34.6987 | 37.4701 | 36.3532 | 34.2013 | 34.7716 | 36.3616 | 36.9503 | 37.6853 | 36.3329 | 34.3436 | 33.4826 | 35.1432 | 35.4654 | 33.5122 | 34.3851 | 34.5091 | 33.6487 | 34.4469 | 34.4384 | 34.4095 | 33.9502 | 34.4389 | 35.1855 | 35.8504 | 35.4639 | 35.4953 | 34.258 | 95.3197 | 95.7623 | 94.6289
2022-09-08 00:27 | 2:37 | 33.833 | 31.4675 | 31.5865 | 36.2401 | 34.4986 | 34.8391 | 35.825 | 35.9487 | 36.8843 | 37.4331 | 36.7438 | 37.5537 | 34.4332 | 34.3937 | 35.2311 | 35.8057 | 36.5577 | 36.8668 | 37.3342 | 37.3883 | 33.466 | 31.4755 | 93.4274 | 35.0455 | 34.0548 | 35.5176 | 34.3314 | 34.0017 | 34.1919 | 35.5533 | 34.8482 | 34.7041 | 37.4777 | 36.3539 | 34.1885 | 34.7854 | 36.3286 | 36.9445 | 37.6763 | 36.3484 | 34.3158 | 33.4896 | 35.155 | 35.4649 | 33.5134 | 34.373 | 34.5243 | 33.6522 | 34.4404 | 34.4187 | 34.4173 | 33.9552 | 34.4469 | 35.1914 | 35.8541 | 35.462 | 35.4951 | 34.2601 | 95.0244 | 95.4726 | 94.4095
2022-09-08 00:28 | 2:38 | 33.9733 | 31.5075 | 31.6937 | 36.3699 | 34.5005 | 34.8507 | 35.8194 | 35.9654 | 36.8951 | 37.43 | 36.7365 | 37.5355 | 34.4265 | 34.382 | 35.2324 | 35.8021 | 36.5579 | 36.8563 | 37.3261 | 37.3954 | 33.6579 | 31.4691 | 93.366 | 35.0643 | 34.0436 | 35.5242 | 34.3199 | 34.0196 | 34.1921 | 35.5443 | 34.8461 | 34.7045 | 37.4555 | 36.3624 | 34.1964 | 34.7678 | 36.3532 | 36.9323 | 37.6884 | 36.3324 | 34.33 | 33.482 | 35.1356 | 35.4727 | 33.5262 | 34.387 | 34.5286 | 33.6514 | 34.4671 | 34.4511 | 34.408 | 33.9458 | 34.4404 | 35.2005 | 35.8565 | 35.4687 | 35.4896 | 34.2814 | 94.8216 | 95.2538 | 94.2318
2022-09-08 00:28 | 2:38 | 33.8046 | 31.4928 | 31.7644 | 36.3327 | 34.4877 | 34.8378 | 35.8081 | 35.9485 | 36.8799 | 37.4302 | 36.7392 | 37.5476 | 34.4158 | 34.3771 | 35.2158 | 35.7972 | 36.5469 | 36.8489 | 37.3097 | 37.3711 | 32.4372 | 31.426 | 93.3474 | 35.0913 | 34.0362 | 35.5381 | 34.3405 | 34.0251 | 34.1969 | 35.5516 | 34.8588 | 34.7051 | 37.4891 | 36.3619 | 34.2007 | 34.7716 | 36.3539 | 36.9388 | 37.6708 | 36.3616 | 34.3446 | 33.4674 | 35.1623 | 35.4776 | 33.5357 | 34.3648 | 34.52 | 33.6476 | 34.4465 | 34.4283 | 34.411 | 33.9365 | 34.4671 | 35.2135 | 35.8417 | 35.4491 | 35.4979 | 34.2499 | 94.581 | 94.9667 | 94.1147
2022-09-08 00:28 | 2:38 | 30.7862 | 31.0985 | 31.649 | 36.3828 | 34.4942 | 34.8362 | 35.8314 | 35.9741 | 36.8928 | 37.427 | 36.7395 | 37.5384 | 34.4145 | 34.411 | 35.2292 | 35.8002 | 36.5588 | 36.8306 | 37.3166 | 37.376 | 30.3956 | 31.1213 | 93.2592 | 35.0653 | 34.0367 | 35.5315 | 34.3436 | 34.0162 | 34.2013 | 35.5618 | 34.8331 | 34.7055 | 37.4571 | 36.3608 | 34.2082 | 34.7903 | 36.3624 | 36.9486 | 37.6795 | 36.3286 | 34.3373 | 33.4753 | 35.1595 | 35.4404 | 33.5157 | 34.3713 | 34.5276 | 33.6533 | 34.465 | 34.4471 | 34.3913 | 33.9676 | 34.4465 | 35.2126 | 35.8486 | 35.4536 | 35.5158 | 34.2625 | 94.4595 | 94.7485 | 93.9374
2022-09-08 00:28 | 2:38 | 31.2989 | 23.7373 | 31.3047 | 36.272 | 34.4987 | 34.8428 | 35.8296 | 35.9447 | 36.8671 | 37.4336 | 36.7568 | 37.5478 | 34.4145 | 34.3903 | 35.2261 | 35.8082 | 36.5454 | 36.859 | 37.3285 | 37.4023 | 28.4569 | 30.4189 | 93.274 | 35.0848 | 34.0404 | 35.5176 | 34.3158 | 34.0168 | 34.1885 | 35.5467 | 34.8604 | 34.6958 | 37.4675 | 36.3543 | 34.1932 | 34.7731 | 36.3619 | 36.9305 | 37.6917 | 36.3532 | 34.3366 | 33.4721 | 35.1573 | 35.4807 | 33.5266 | 34.3747 | 34.5259 | 33.6634 | 34.471 | 34.4458 | 34.3945 | 33.9747 | 34.465 | 35.2141 | 35.8537 | 35.4525 | 35.5121 | 34.2514 | 94.3132 | 94.6399 | 93.8871
2022-09-08 00:28 | 2:38 | 31.4953 | 20.5919 | 31.4521 | 36.3169 | 34.4771 | 34.8195 | 35.8013 | 35.936 | 36.8751 | 37.438 | 36.7436 | 37.5358 | 34.4227 | 34.3847 | 35.2283 | 35.8 | 36.5544 | 36.8534 | 37.3351 | 37.3814 | 29.3159 | 30.763 | 93.2297 | 35.0565 | 34.0436 | 35.5278 | 34.33 | 34.0207 | 34.1964 | 35.5533 | 34.8502 | 34.7054 | 37.4699 | 36.3706 | 34.1912 | 34.7988 | 36.3608 | 36.9478 | 37.6784 | 36.3539 | 34.327 | 33.4878 | 35.1664 | 35.456 | 33.5594 | 34.3605 | 34.5264 | 33.6786 | 34.4436 | 34.4488 | 34.3949 | 33.9307 | 34.471 | 35.2156 | 35.8353 | 35.4544 | 35.5091 | 34.2518 | 94.2213 | 94.5426 | 93.8219
2022-09-08 00:28 | 2:38 | 31.4504 | 24.0043 | 31.5549 | 36.3328 | 34.4866 | 34.8187 | 35.8031 | 35.9498 | 36.8517 | 37.4342 | 36.7593 | 37.5387 | 34.4188 | 34.3867 | 35.2233 | 35.7985 | 36.5647 | 36.8743 | 37.329 | 37.3997 | 29.9915 | 30.8886 | 93.2038 | 35.0889 | 34.0347 | 35.5292 | 34.3446 | 34.0171 | 34.2007 | 35.5558 | 34.8502 | 34.6875 | 37.4706 | 36.3719 | 34.1889 | 34.8056 | 36.3543 | 36.9351 | 37.6998 | 36.3624 | 34.3469 | 33.4942 | 35.1668 | 35.4512 | 33.544 | 34.3467 | 34.5164 | 33.6775 | 34.4717 | 34.4568 | 34.401 | 33.9813 | 34.4436 | 35.1841 | 35.8486 | 35.4528 | 35.5194 | 34.2591 | 94.1401 | 94.463 | 93.8131
2022-09-08 00:29 | 2:38 | 31.4433 | 26.6749 | 31.6394 | 36.2837 | 34.4769 | 34.8375 | 35.8094 | 35.9572 | 36.8829 | 37.4273 | 36.7544 | 37.5336 | 34.3866 | 34.3794 | 35.2162 | 35.8067 | 36.5552 | 36.8641 | 37.3289 | 37.4038 | 30.5009 | 31.0074 | 93.1349 | 35.1263 | 34.0463 | 35.5294 | 34.3373 | 34.0199 | 34.2082 | 35.5511 | 34.8516 | 34.7014 | 37.4801 | 36.353 | 34.1891 | 34.778 | 36.3706 | 36.9338 | 37.6779 | 36.3619 | 34.3337 | 33.5055 | 35.1692 | 35.4729 | 33.5462 | 34.3521 | 34.5196 | 33.6625 | 34.4547 | 34.4473 | 34.3877 | 33.943 | 34.4717 | 35.2113 | 35.8624 | 35.4616 | 35.5062 | 34.2558 | 94.089 | 94.4045 | 93.7792
2022-09-08 00:29 | 2:39 | 31.4739 | 28.4161 | 31.6985 | 36.3362 | 34.4737 | 34.8264 | 35.7947 | 35.9359 | 36.873 | 37.4299 | 36.7484 | 37.5393 | 34.4416 | 34.3867 | 35.2241 | 35.7973 | 36.5589 | 36.8468 | 37.3465 | 37.3756 | 30.8671 | 31.0656 | 93.1127 | 35.0976 | 34.0265 | 35.5447 | 34.3366 | 34.0111 | 34.1932 | 35.5514 | 34.8571 | 34.7029 | 37.472 | 36.3685 | 34.2009 | 34.7796 | 36.3719 | 36.9324 | 37.7 | 36.3608 | 34.3548 | 33.5022 | 35.1965 | 35.4843 | 33.5686 | 34.365 | 34.5234 | 33.685 | 34.459 | 34.4623 | 34.3966 | 33.9596 | 34.4547 | 35.2067 | 35.8546 | 35.4518 | 35.532 | 34.2633 | 94.0504 | 94.3097 | 93.7335
2022-09-08 00:29 | 2:39 | 31.537 | 29.4938 | 31.7382 | 36.2638 | 34.4859 | 34.8073 | 35.821 | 35.9416 | 36.9041 | 37.4207 | 36.7574 | 37.5442 | 34.4127 | 34.3824 | 35.2205 | 35.7985 | 36.5493 | 36.8545 | 37.3295 | 37.3931 | 31.0947 | 31.1159 | 93.0542 | 35.1209 | 34.0298 | 35.5246 | 34.327 | 33.9996 | 34.1912 | 35.5634 | 34.852 | 34.7008 | 37.4849 | 36.3609 | 34.1947 | 34.7738 | 36.353 | 36.9293 | 37.687 | 36.3543 | 34.3295 | 33.5219 | 35.1679 | 35.5054 | 33.5932 | 34.376 | 34.5318 | 33.6634 | 34.4436 | 34.4505 | 34.3931 | 33.9888 | 34.459 | 35.2109 | 35.8429 | 35.4796 | 35.5054 | 34.2966 | 93.963 | 94.2354 | 93.7318
2022-09-08 00:29 | 2:39 | 31.6 | 30.1517 | 31.8001 | 36.3366 | 34.4734 | 34.8397 | 35.8082 | 35.9537 | 36.8847 | 37.4445 | 36.7614 | 37.5431 | 34.4259 | 34.369 | 35.2241 | 35.7978 | 36.5503 | 36.8562 | 37.3394 | 37.4145 | 31.2711 | 31.1624 | 93.0231 | 35.1658 | 34.0494 | 35.5298 | 34.3469 | 34.0262 | 34.1889 | 35.5399 | 34.8438 | 34.7006 | 37.4825 | 36.3809 | 34.1939 | 34.7804 | 36.3685 | 36.9284 | 37.6911 | 36.3706 | 34.3552 | 33.5088 | 35.1731 | 35.4931 | 33.5855 | 34.3753 | 34.523 | 33.6683 | 34.4778 | 34.4601 | 34.42 | 33.9689 | 34.4436 | 35.2022 | 35.8518 | 35.464 | 35.5218 | 34.2653 | 93.8714 | 94.1776 | 93.6464
2022-09-08 00:29 | 2:39 | 31.6402 | 30.6005 | 31.8331 | 36.3514 | 34.4576 | 34.8342 | 35.8198 | 35.9538 | 36.8908 | 37.4435 | 36.7626 | 37.5536 | 34.4147 | 34.3826 | 35.2274 | 35.8087 | 36.5431 | 36.855 | 37.3338 | 37.3903 | 31.3776 | 31.2035 | 92.9448 | 35.055 | 34.041 | 35.5457 | 34.3337 | 34.017 | 34.1891 | 35.5515 | 34.8439 | 34.7138 | 37.4845 | 36.3774 | 34.2166 | 34.7754 | 36.3609 | 36.9206 | 37.7044 | 36.3719 | 34.3368 | 33.5075 | 35.1745 | 35.506 | 33.5931 | 34.3558 | 34.5256 | 33.6654 | 34.48 | 34.4486 | 34.3828 | 33.9843 | 34.4778 | 35.2022 | 35.8562 | 35.4715 | 35.5175 | 34.2737 | 93.8283 | 94.1154 | 93.6327
2022-09-08 00:29 | 2:39 | 31.6533 | 30.8627 | 31.8546 | 36.4894 | 34.4557 | 34.8258 | 35.822 | 35.9603 | 36.895 | 37.435 | 36.762 | 37.5506 | 34.406 | 34.3901 | 35.2334 | 35.8015 | 36.5535 | 36.8435 | 37.344 | 37.3971 | 31.4954 | 31.2377 | 92.8651 | 34.9865 | 34.0433 | 35.521 | 34.3548 | 34.0305 | 34.2009 | 35.5592 | 34.8732 | 34.6985 | 37.482 | 36.3824 | 34.2082 | 34.7905 | 36.3809 | 36.9372 | 37.7 | 36.353 | 34.3288 | 33.5177 | 35.1754 | 35.5206 | 33.6109 | 34.3558 | 34.5383 | 33.6782 | 34.4678 | 34.4761 | 34.3939 | 33.9832 | 34.48 | 35.2555 | 35.841 | 35.4743 | 35.526 | 34.2665 | 93.8294 | 94.0619 | 93.653
2022-09-08 00:30 | 2:40 | 31.6973 | 31.0367 | 31.9026 | 36.4946 | 34.4537 | 34.8273 | 35.8262 | 35.9576 | 36.8826 | 37.4567 | 36.7477 | 37.5547 | 34.4066 | 34.3802 | 35.2294 | 35.781 | 36.5717 | 36.8543 | 37.3425 | 37.418 | 31.5401 | 31.2614 | 92.7498 | 35.0504 | 34.0504 | 35.5436 | 34.3295 | 34.0144 | 34.1947 | 35.549 | 34.8521 | 34.7198 | 37.4648 | 36.361 | 34.1917 | 34.809 | 36.3774 | 36.9418 | 37.718 | 36.3685 | 34.3479 | 33.5469 | 35.2091 | 35.511 | 33.5932 | 34.3663 | 34.5317 | 33.6896 | 34.486 | 34.4657 | 34.4055 | 33.9869 | 34.4678 | 35.2192 | 35.8342 | 35.4732 | 35.5192 | 34.2693 | 93.7758 | 93.9153 | 93.6599
2022-09-08 00:30 | 2:40 | 31.634 | 26.821 | 31.5996 | 36.3035 | 34.428 | 34.8373 | 35.8311 | 35.929 | 36.8948 | 37.461 | 36.7783 | 37.5662 | 34.4136 | 34.3905 | 35.2478 | 35.8088 | 36.5656 | 36.8611 | 37.3381 | 37.4141 | 31.7376 | 31.303 | 92.6127 | 35.1248 | 34.0595 | 35.5283 | 34.3552 | 34.0346 | 34.1939 | 35.5484 | 34.8604 | 34.7048 | 37.4734 | 36.3699 | 34.2024 | 34.7887 | 36.3824 | 36.9182 | 37.6912 | 36.3609 | 34.3237 | 33.5306 | 35.1976 | 35.5098 | 33.6152 | 34.3631 | 34.5299 | 33.6925 | 34.4632 | 34.469 | 34.3849 | 34.0028 | 34.486 | 35.2289 | 35.8388 | 35.4934 | 35.523 | 34.2683 | 93.6758 | 93.7758 | 93.6116
2022-09-08 00:30 | 2:40 | 30.8793 | 23.0472 | 29.1204 | 36.3075 | 34.4265 | 34.8266 | 35.8299 | 35.9619 | 36.8787 | 37.4538 | 36.7602 | 37.5569 | 34.3965 | 34.3869 | 35.2137 | 35.7965 | 36.5637 | 36.8556 | 37.3297 | 37.4129 | 31.7776 | 31.3303 | 92.4109 | 35.1099 | 34.0388 | 35.557 | 34.3368 | 34.0172 | 34.2166 | 35.5581 | 34.8624 | 34.6974 | 37.4941 | 36.3803 | 34.2049 | 34.7893 | 36.361 | 36.9614 | 37.7115 | 36.3809 | 34.3337 | 33.5354 | 35.2114 | 35.5165 | 33.6088 | 34.3711 | 34.5159 | 33.6898 | 34.4693 | 34.4839 | 34.4143 | 34.0024 | 34.4632 | 35.2152 | 35.85 | 35.4681 | 35.5376 | 34.2717 | 93.5759 | 93.636 | 93.5521
2022-09-08 00:30 | 2:40 | 29.426 | 21.8385 | 27.5148 | 36.0398 | 34.4303 | 34.8378 | 35.8115 | 35.9361 | 36.8956 | 37.4656 | 36.7498 | 37.5741 | 34.4198 | 34.3754 | 35.2305 | 35.8093 | 36.566 | 36.8649 | 37.3427 | 37.4081 | 31.7575 | 31.3449 | 92.4245 | 35.1783 | 34.059 | 35.5583 | 34.3288 | 34.0284 | 34.2082 | 35.5658 | 34.8589 | 34.7039 | 37.4967 | 36.3984 | 34.1888 | 34.7694 | 36.3699 | 36.9464 | 37.7103 | 36.3774 | 34.351 | 33.5537 | 35.2095 | 35.5239 | 33.607 | 34.3757 | 34.5281 | 33.7052 | 34.499 | 34.4885 | 34.3972 | 33.9924 | 34.4693 | 35.2323 | 35.8482 | 35.4681 | 35.5389 | 34.3012 | 93.4502 | 93.5519 | 93.4789
2022-09-08 00:30 | 2:40 | 28.196 | 22.2261 | 26.8259 | 36.052 | 34.433 | 34.8353 | 35.8065 | 35.9449 | 36.8945 | 37.4622 | 36.7627 | 37.5482 | 34.4169 | 34.3833 | 35.2376 | 35.8063 | 36.5575 | 36.8538 | 37.3512 | 37.4084 | 31.7565 | 31.3603 | 92.4337 | 35.1971 | 34.0657 | 35.5581 | 34.3479 | 34.0159 | 34.1917 | 35.5566 | 34.8362 | 34.7162 | 37.4954 | 36.3862 | 34.1988 | 34.7791 | 36.3803 | 36.9226 | 37.7268 | 36.3824 | 34.3423 | 33.5529 | 35.2097 | 35.5525 | 33.612 | 34.361 | 34.5265 | 33.6921 | 34.49 | 34.4627 | 34.3841 | 34.0026 | 34.499 | 35.2186 | 35.8376 | 35.4742 | 35.5357 | 34.2865 | 93.333 | 93.4015 | 93.3782
2022-09-08 00:30 | 2:40 | 27.2152 | 22.4556 | 26.3855 | 35.9201 | 34.4242 | 34.8143 | 35.8068 | 35.94 | 36.8817 | 37.4517 | 36.7538 | 37.557 | 34.4241 | 34.3724 | 35.2456 | 35.8009 | 36.5466 | 36.8572 | 37.3231 | 37.4152 | 31.7881 | 31.3852 | 92.2501 | 35.146 | 34.0427 | 35.5411 | 34.3237 | 34.0226 | 34.2024 | 35.5599 | 34.8453 | 34.711 | 37.4896 | 36.3963 | 34.2025 | 34.8125 | 36.3984 | 36.9525 | 37.7266 | 36.361 | 34.3486 | 33.5664 | 35.212 | 35.5396 | 33.637 | 34.3565 | 34.5041 | 33.6955 | 34.4802 | 34.4792 | 34.3941 | 34.0054 | 34.49 | 35.2584 | 35.8432 | 35.4912 | 35.5291 | 34.293 | 93.2241 | 93.3115 | 93.2878
2022-09-08 00:31 | 2:40 | 25.316 | 22.3351 | 25.299 | 35.8752 | 34.4164 | 34.8195 | 35.7912 | 35.9353 | 36.8963 | 37.4637 | 36.7578 | 37.5673 | 34.4261 | 34.3781 | 35.2432 | 35.7801 | 36.5607 | 36.8539 | 37.3442 | 37.4195 | 31.7843 | 31.3941 | 92.1826 | 35.1431 | 34.0434 | 35.5344 | 34.3337 | 34.0387 | 34.2049 | 35.5362 | 34.8576 | 34.7237 | 37.496 | 36.4056 | 34.1826 | 34.7875 | 36.3862 | 36.9425 | 37.7147 | 36.3699 | 34.3355 | 33.5531 | 35.2323 | 35.5628 | 33.6197 | 34.3704 | 34.5163 | 33.6985 | 34.4823 | 34.484 | 34.4037 | 34.0016 | 34.4802 | 35.2358 | 35.8575 | 35.4758 | 35.5352 | 34.2793 | 93.1017 | 93.235 | 93.2683
2022-09-08 00:31 | 2:41 | 18.4814 | 21.9705 | 23.0723 | 35.765 | 34.407 | 34.8043 | 35.7929 | 35.9467 | 36.8832 | 37.4576 | 36.7659 | 37.5663 | 34.409 | 34.3773 | 35.2376 | 35.7802 | 36.5539 | 36.8466 | 37.3149 | 37.3891 | 31.7902 | 31.3991 | 92.0407 | 35.1967 | 34.0479 | 35.5414 | 34.351 | 34.038 | 34.1888 | 35.5593 | 34.8558 | 34.725 | 37.4949 | 36.3836 | 34.2028 | 34.7632 | 36.3963 | 36.9377 | 37.7171 | 36.3803 | 34.3468 | 33.5585 | 35.2304 | 35.5419 | 33.6589 | 34.3687 | 34.5282 | 33.7073 | 34.4894 | 34.4718 | 34.3853 | 34.0222 | 34.4823 | 35.2249 | 35.8419 | 35.487 | 35.5426 | 34.3113 | 92.943 | 93.0914 | 93.1213
2022-09-08 00:31 | 2:41 | 17.5656 | 21.6217 | 22.2234 | 35.6508 | 34.4045 | 34.7986 | 35.7791 | 35.9434 | 36.9083 | 37.4868 | 36.762 | 37.5716 | 34.4133 | 34.3834 | 35.2231 | 35.778 | 36.5643 | 36.8398 | 37.305 | 37.4171 | 31.8138 | 31.4212 | 92.1007 | 35.2103 | 34.0493 | 35.5333 | 34.3423 | 34.0191 | 34.1988 | 35.5561 | 34.8598 | 34.7105 | 37.5005 | 36.4117 | 34.2087 | 34.7827 | 36.4056 | 36.9561 | 37.6997 | 36.3984 | 34.3526 | 33.5524 | 35.2526 | 35.5412 | 33.6351 | 34.3704 | 34.5365 | 33.7228 | 34.4669 | 34.4673 | 34.3991 | 34.0079 | 34.4894 | 35.2509 | 35.8421 | 35.4837 | 35.5285 | 34.2891 | 92.8673 | 93.0316 | 93.0884
2022-09-08 00:31 | 2:41 | 17.1122 | 21.1076 | 21.6536 | 35.6453 | 34.4054 | 34.8048 | 35.7493 | 35.9414 | 36.9036 | 37.4742 | 36.7514 | 37.5679 | 34.4082 | 34.3858 | 35.2427 | 35.8012 | 36.551 | 36.8336 | 37.2996 | 37.4182 | 31.8314 | 31.4328 | 91.9561 | 35.1643 | 34.0464 | 35.5529 | 34.3486 | 34.03 | 34.2025 | 35.5579 | 34.8539 | 34.7198 | 37.4914 | 36.3952 | 34.1887 | 34.7699 | 36.3836 | 36.9507 | 37.7173 | 36.3862 | 34.3322 | 33.5697 | 35.2264 | 35.5567 | 33.6531 | 34.3681 | 34.5052 | 33.6965 | 34.4876 | 34.5022 | 34.3877 | 33.9918 | 34.4669 | 35.2647 | 35.8608 | 35.4759 | 35.5417 | 34.3007 | 92.7573 | 92.9418 | 93.0506
2022-09-08 00:31 | 2:41 | 16.7193 | 20.5184 | 21.2012 | 35.5576 | 34.399 | 34.7895 | 35.7366 | 35.9325 | 36.8957 | 37.4496 | 36.7738 | 37.569 | 34.4096 | 34.3911 | 35.2179 | 35.7965 | 36.5597 | 36.8398 | 37.3064 | 37.386 | 31.8712 | 31.4477 | 91.8905 | 35.2518 | 34.0508 | 35.5597 | 34.3355 | 34.0315 | 34.1826 | 35.5688 | 34.8642 | 34.7071 | 37.5095 | 36.3856 | 34.2026 | 34.7753 | 36.4117 | 36.9576 | 37.712 | 36.3963 | 34.3272 | 33.5963 | 35.2355 | 35.5865 | 33.6684 | 34.3673 | 34.5077 | 33.7268 | 34.4797 | 34.4804 | 34.3896 | 34.0167 | 34.4876 | 35.2563 | 35.8293 | 35.4972 | 35.559 | 34.2916 | 92.6755 | 92.7521 | 92.9619
2022-09-08 00:31 | 2:41 | 16.7428 | 20.3272 | 20.8751 | 35.4073 | 34.4106 | 34.7972 | 35.7473 | 35.9249 | 36.8992 | 37.467 | 36.7546 | 37.578 | 34.4053 | 34.3682 | 35.2221 | 35.7761 | 36.5536 | 36.8285 | 37.3003 | 37.4021 | 31.8904 | 31.44 | 91.9533 | 35.228 | 34.0516 | 35.5539 | 34.3468 | 34.0167 | 34.2028 | 35.5612 | 34.8443 | 34.7105 | 37.5041 | 36.3864 | 34.2169 | 34.7618 | 36.3952 | 36.9475 | 37.7188 | 36.4056 | 34.3322 | 33.5731 | 35.2479 | 35.575 | 33.662 | 34.3464 | 34.5046 | 33.7296 | 34.4893 | 34.4997 | 34.3913 | 34.0175 | 34.4797 | 35.2578 | 35.8483 | 35.4952 | 35.5619 | 34.3081 | 92.5298 | 92.6278 | 92.7913
2022-09-08 00:32 | 2:42 | 17.3333 | 20.7755 | 21.0808 | 35.4104 | 34.3932 | 34.795 | 35.714 | 35.9123 | 36.9126 | 37.4594 | 36.7531 | 37.5804 | 34.4288 | 34.3718 | 35.2376 | 35.7946 | 36.5566 | 36.8195 | 37.3018 | 37.3927 | 31.9305 | 31.437 | 91.9624 | 35.1138 | 34.0605 | 35.5647 | 34.3526 | 34.0123 | 34.2087 | 35.5496 | 34.8484 | 34.7206 | 37.5022 | 36.4148 | 34.1884 | 34.7712 | 36.3856 | 36.9436 | 37.7263 | 36.3836 | 34.3458 | 33.5946 | 35.2627 | 35.5832 | 33.6766 | 34.3669 | 34.5253 | 33.7146 | 34.4851 | 34.4834 | 34.3937 | 34.0168 | 34.4893 | 35.262 | 35.8454 | 35.4831 | 35.5427 | 34.3203 | 92.4701 | 92.5324 | 92.7932
2022-09-08 00:32 | 2:42 | 17.5475 | 21.0419 | 21.2854 | 35.3802 | 34.4041 | 34.7858 | 35.7071 | 35.9165 | 36.9004 | 37.4754 | 36.7612 | 37.5615 | 34.4007 | 34.3734 | 35.2259 | 35.7836 | 36.5485 | 36.8189 | 37.287 | 37.4087 | 31.9519 | 31.4609 | 91.9756 | 35.2514 | 34.0571 | 35.5409 | 34.3322 | 34.0067 | 34.1887 | 35.5614 | 34.8608 | 34.7212 | 37.4991 | 36.4084 | 34.1886 | 34.773 | 36.3864 | 36.9515 | 37.7077 | 36.4117 | 34.3438 | 33.5854 | 35.2625 | 35.5747 | 33.6485 | 34.3738 | 34.4931 | 33.739 | 34.4894 | 34.5132 | 34.382 | 34.0336 | 34.4851 | 35.2687 | 35.8317 | 35.4957 | 35.5508 | 34.2936 | 92.3202 | 92.4328 | 92.7016
2022-09-08 00:32 | 2:42 | 17.4798 | 21.0562 | 21.3364 | 35.3613 | 34.4192 | 34.7692 | 35.7156 | 35.9126 | 36.9172 | 37.4697 | 36.7481 | 37.5952 | 34.4162 | 34.3861 | 35.2428 | 35.7785 | 36.5536 | 36.801 | 37.2652 | 37.4016 | 31.9577 | 31.4623 | 92.0248 | 35.1671 | 34.0639 | 35.5436 | 34.3272 | 34.0179 | 34.2026 | 35.5588 | 34.8472 | 34.7156 | 37.511 | 36.3997 | 34.1949 | 34.767 | 36.4148 | 36.9398 | 37.7231 | 36.3952 | 34.3325 | 33.5918 | 35.2608 | 35.5827 | 33.6641 | 34.3554 | 34.502 | 33.7374 | 34.4819 | 34.4918 | 34.3771 | 34.0311 | 34.4894 | 35.2609 | 35.8292 | 35.5009 | 35.5251 | 34.3174 | 92.1753 | 92.248 | 92.5897
2022-09-08 00:32 | 2:42 | 17.0039 | 20.7342 | 21.1028 | 35.2454 | 34.4095 | 34.7497 | 35.6919 | 35.9083 | 36.895 | 37.473 | 36.7518 | 37.571 | 34.4172 | 34.3814 | 35.2163 | 35.7482 | 36.5497 | 36.8077 | 37.282 | 37.3993 | 31.9667 | 31.4705 | 92.1741 | 35.1489 | 34.0369 | 35.5365 | 34.3322 | 34.009 | 34.2169 | 35.5439 | 34.8386 | 34.7075 | 37.4973 | 36.393 | 34.1891 | 34.7679 | 36.4084 | 36.9348 | 37.729 | 36.3856 | 34.3408 | 33.5798 | 35.2615 | 35.5696 | 33.6735 | 34.3501 | 34.4957 | 33.7234 | 34.5033 | 34.5001 | 34.411 | 34.0185 | 34.4819 | 35.2633 | 35.8222 | 35.4884 | 35.5562 | 34.306 | 92.0391 | 92.0688 | 92.4765
2022-09-08 00:32 | 2:42 | 16.4432 | 20.1469 | 20.6765 | 35.1011 | 34.4173 | 34.75 | 35.6859 | 35.8851 | 36.8974 | 37.4613 | 36.7471 | 37.5781 | 34.4061 | 34.3775 | 35.236 | 35.7537 | 36.5433 | 36.8021 | 37.2881 | 37.4078 | 31.9803 | 31.4594 | 92.2333 | 35.2355 | 34.0485 | 35.5479 | 34.3458 | 34.0004 | 34.1884 | 35.5599 | 34.8351 | 34.7015 | 37.4919 | 36.4088 | 34.1925 | 34.7456 | 36.3997 | 36.9492 | 37.7405 | 36.3864 | 34.3346 | 33.5825 | 35.2723 | 35.5983 | 33.6626 | 34.3571 | 34.4831 | 33.7249 | 34.5032 | 34.4813 | 34.3903 | 34.0393 | 34.5033 | 35.2776 | 35.8299 | 35.4881 | 35.5551 | 34.3129 | 91.9715 | 91.9604 | 92.4204
2022-09-08 00:32 | 2:42 | 15.7588 | 19.6051 | 20.15 | 35.1188 | 34.408 | 34.7436 | 35.6445 | 35.8939 | 36.9063 | 37.4571 | 36.7351 | 37.5688 | 34.4011 | 34.392 | 35.2225 | 35.7469 | 36.5502 | 36.8021 | 37.2673 | 37.3925 | 31.9769 | 31.4831 | 92.3237 | 35.2216 | 34.0274 | 35.5464 | 34.3438 | 33.991 | 34.1886 | 35.5575 | 34.8491 | 34.7103 | 37.501 | 36.3878 | 34.1921 | 34.7562 | 36.393 | 36.9415 | 37.7269 | 36.4148 | 34.3105 | 33.6056 | 35.2611 | 35.584 | 33.6581 | 34.3721 | 34.4669 | 33.7076 | 34.5095 | 34.5003 | 34.3847 | 34.0356 | 34.5032 | 35.2641 | 35.819 | 35.5112 | 35.5351 | 34.2848 | 91.8462 | 91.8528 | 92.3585
2022-09-08 00:33 | 2:42 | 15.1907 | 19.0916 | 19.6994 | 35.0844 | 34.411 | 34.735 | 35.6679 | 35.8933 | 36.9066 | 37.4721 | 36.7612 | 37.5629 | 34.4159 | 34.3765 | 35.2257 | 35.7755 | 36.53 | 36.8152 | 37.2571 | 37.3865 | 31.9843 | 31.4652 | 92.4788 | 35.1964 | 34.0472 | 35.5512 | 34.3325 | 34.018 | 34.1949 | 35.5464 | 34.8457 | 34.7108 | 37.5035 | 36.3822 | 34.1604 | 34.7625 | 36.4088 | 36.9234 | 37.7322 | 36.4084 | 34.3307 | 33.5933 | 35.2565 | 35.583 | 33.6859 | 34.3577 | 34.4927 | 33.7545 | 34.4768 | 34.5073 | 34.3867 | 34.0164 | 34.5095 | 35.267 | 35.8359 | 35.5138 | 35.5527 | 34.3226 | 91.7896 | 91.8573 | 92.3514
2022-09-08 00:33 | 2:43 | 14.7434 | 18.6499 | 19.27 | 34.8972 | 34.3913 | 34.7391 | 35.649 | 35.8812 | 36.8883 | 37.4499 | 36.7238 | 37.5545 | 34.418 | 34.3869 | 35.2252 | 35.7411 | 36.5468 | 36.7964 | 37.2587 | 37.4028 | 31.9852 | 31.4742 | 92.4069 | 35.2146 | 34.0308 | 35.5466 | 34.3408 | 34.0085 | 34.1891 | 35.5542 | 34.8443 | 34.7086 | 37.4872 | 36.3931 | 34.2013 | 34.7311 | 36.3878 | 36.9374 | 37.7203 | 36.3997 | 34.3261 | 33.5973 | 35.278 | 35.5824 | 33.6871 | 34.3799 | 34.4716 | 33.7364 | 34.5128 | 34.4845 | 34.3794 | 34.0172 | 34.4768 | 35.2596 | 35.8338 | 35.4859 | 35.5764 | 34.3033 | 91.8635 | 91.9423 | 92.4251
2022-09-08 00:33 | 2:43 | 14.2215 | 18.1703 | 18.8378 | 34.923 | 34.3945 | 34.7361 | 35.6135 | 35.875 | 36.8852 | 37.4813 | 36.7075 | 37.5628 | 34.4385 | 34.3803 | 35.1948 | 35.7677 | 36.5342 | 36.7821 | 37.2495 | 37.4122 | 32.0073 | 31.4983 | 92.4628 | 35.176 | 34.0408 | 35.5396 | 34.3346 | 34.0001 | 34.1925 | 35.5413 | 34.8264 | 34.7112 | 37.4941 | 36.3787 | 34.1865 | 34.755 | 36.3822 | 36.9315 | 37.7297 | 36.393 | 34.3255 | 33.6111 | 35.2623 | 35.5768 | 33.6827 | 34.3784 | 34.4777 | 33.7513 | 34.4866 | 34.524 | 34.3867 | 34.0433 | 34.5128 | 35.2704 | 35.8173 | 35.486 | 35.5587 | 34.3097 | 91.8498 | 91.9691 | 92.4806
2022-09-08 00:33 | 2:43 | 13.8796 | 17.756 | 18.4804 | 34.9107 | 34.3949 | 34.7267 | 35.6082 | 35.8715 | 36.886 | 37.4468 | 36.727 | 37.5566 | 34.423 | 34.3792 | 35.2048 | 35.7343 | 36.5338 | 36.7912 | 37.2433 | 37.3877 | 32.0154 | 31.488 | 92.5293 | 35.2674 | 34.0493 | 35.5466 | 34.3105 | 34.0092 | 34.1921 | 35.5485 | 34.8441 | 34.7069 | 37.4885 | 36.3988 | 34.1786 | 34.737 | 36.3931 | 36.9308 | 37.7356 | 36.4088 | 34.3383 | 33.6082 | 35.2569 | 35.5911 | 33.6919 | 34.3816 | 34.472 | 33.7475 | 34.4986 | 34.5103 | 34.3824 | 34.0322 | 34.4866 | 35.2713 | 35.822 | 35.5014 | 35.5547 | 34.3098 | 92.0073 | 92.0683 | 92.5878
2022-09-08 00:33 | 2:43 | 13.6389 | 17.4514 | 18.1581 | 34.8112 | 34.401 | 34.7143 | 35.5921 | 35.8741 | 36.8685 | 37.454 | 36.7135 | 37.5542 | 34.4348 | 34.3854 | 35.2111 | 35.7298 | 36.524 | 36.7762 | 37.2495 | 37.3937 | 32.016 | 31.4954 | 92.6611 | 35.1217 | 34.0576 | 35.5223 | 34.3307 | 33.9863 | 34.1604 | 35.5451 | 34.8229 | 34.6976 | 37.4879 | 36.4134 | 34.1826 | 34.7333 | 36.3787 | 36.9224 | 37.7349 | 36.3878 | 34.3059 | 33.6039 | 35.2694 | 35.5864 | 33.6906 | 34.3632 | 34.4674 | 33.7307 | 34.5178 | 34.5049 | 34.369 | 34.06 | 34.4986 | 35.2817 | 35.8216 | 35.5 | 35.5548 | 34.3003 | 92.1317 | 92.2266 | 92.6272
2022-09-08 00:33 | 2:43 | 13.3092 | 17.0878 | 17.8193 | 34.6937 | 34.3877 | 34.7139 | 35.5854 | 35.8507 | 36.8859 | 37.443 | 36.7308 | 37.5564 | 34.426 | 34.3719 | 35.216 | 35.7253 | 36.5221 | 36.7784 | 37.2468 | 37.4088 | 32.0164 | 31.4869 | 92.6171 | 35.1953 | 34.0461 | 35.5421 | 34.3261 | 33.9755 | 34.2013 | 35.5664 | 34.8356 | 34.703 | 37.4904 | 36.3968 | 34.1788 | 34.7444 | 36.3988 | 36.9298 | 37.7313 | 36.3822 | 34.3306 | 33.5843 | 35.2813 | 35.5799 | 33.6923 | 34.3705 | 34.462 | 33.7501 | 34.5075 | 34.4975 | 34.3826 | 34.0393 | 34.5178 | 35.2739 | 35.8235 | 35.4937 | 35.5444 | 34.3011 | 92.2062 | 92.3058 | 92.6523
2022-09-08 00:34 | 2:44 | 12.9612 | 16.7325 | 17.5185 | 34.703 | 34.3966 | 34.7107 | 35.5671 | 35.8722 | 36.9014 | 37.4676 | 36.7163 | 37.5637 | 34.422 | 34.3863 | 35.2146 | 35.7387 | 36.526 | 36.7712 | 37.2336 | 37.39 | 32.0321 | 31.4863 | 92.7368 | 35.163 | 34.0333 | 35.5524 | 34.3255 | 33.974 | 34.1865 | 35.5536 | 34.8397 | 34.708 | 37.4824 | 36.3972 | 34.1948 | 34.7177 | 36.4134 | 36.9289 | 37.7292 | 36.3931 | 34.3435 | 33.61 | 35.279 | 35.5881 | 33.7073 | 34.3728 | 34.4595 | 33.7645 | 34.5197 | 34.4876 | 34.3901 | 34.0331 | 34.5075 | 35.2681 | 35.8178 | 35.5035 | 35.5418 | 34.3264 | 92.3712 | 92.3582 | 92.7227
2022-09-08 00:34 | 2:44 | 12.6604 | 16.3897 | 17.1985 | 34.519 | 34.3931 | 34.7071 | 35.5611 | 35.8521 | 36.8768 | 37.4592 | 36.7306 | 37.5418 | 34.4314 | 34.3726 | 35.2181 | 35.7207 | 36.5143 | 36.7541 | 37.225 | 37.413 | 32.0329 | 31.5074 | 92.8731 | 35.1903 | 34.0408 | 35.5282 | 34.3383 | 33.9797 | 34.1786 | 35.5448 | 34.7999 | 34.6916 | 37.4925 | 36.4057 | 34.1983 | 34.7391 | 36.3968 | 36.9164 | 37.7426 | 36.3787 | 34.3359 | 33.6358 | 35.2897 | 35.5968 | 33.7037 | 34.3638 | 34.4501 | 33.7549 | 34.5078 | 34.5055 | 34.3802 | 34.0589 | 34.5197 | 35.2686 | 35.8447 | 35.5136 | 35.5583 | 34.3101 | 92.4586 | 92.5235 | 92.7912
2022-09-08 00:34 | 2:44 | 12.3415 | 16.0757 | 16.9224 | 34.4858 | 34.42 | 34.7024 | 35.5327 | 35.8436 | 36.8925 | 37.4665 | 36.7146 | 37.5644 | 34.4409 | 34.3944 | 35.2044 | 35.7458 | 36.5118 | 36.7748 | 37.2082 | 37.399 | 32.0575 | 31.506 | 92.9604 | 35.1495 | 34.0437 | 35.5418 | 34.3059 | 33.9751 | 34.1826 | 35.5359 | 34.837 | 34.7128 | 37.4926 | 36.3933 | 34.1859 | 34.7135 | 36.3972 | 36.925 | 37.7533 | 36.3988 | 34.3336 | 33.6006 | 35.2805 | 35.5906 | 33.7232 | 34.3801 | 34.4713 | 33.7569 | 34.5153 | 34.5152 | 34.3905 | 34.0565 | 34.5078 | 35.2925 | 35.8385 | 35.5131 | 35.5703 | 34.3071 | 92.6456 | 92.6577 | 92.9088
2022-09-08 00:34 | 2:44 | 14.6959 | 16.354 | 17.4263 | 34.668 | 34.3828 | 34.6818 | 35.532 | 35.8351 | 36.8975 | 37.4561 | 36.7123 | 37.5527 | 34.4174 | 34.385 | 35.2003 | 35.7183 | 36.5138 | 36.7641 | 37.2176 | 37.4057 | 32.0699 | 31.5126 | 93.0046 | 35.1374 | 34.0547 | 35.5478 | 34.3306 | 33.9791 | 34.1788 | 35.5431 | 34.8147 | 34.6931 | 37.5059 | 36.4032 | 34.2034 | 34.7338 | 36.4057 | 36.9232 | 37.7369 | 36.4134 | 34.3245 | 33.629 | 35.2909 | 35.6095 | 33.7265 | 34.3706 | 34.4616 | 33.7696 | 34.5134 | 34.511 | 34.3869 | 34.0378 | 34.5153 | 35.2788 | 35.8262 | 35.5031 | 35.5647 | 34.3005 | 92.7665 | 92.772 | 93.0321
2022-09-08 00:34 | 2:44 | 14.9761 | 16.4925 | 17.73 | 34.4821 | 34.3939 | 34.6786 | 35.5303 | 35.812 | 36.889 | 37.4359 | 36.7292 | 37.545 | 34.4221 | 34.3849 | 35.2078 | 35.7023 | 36.5029 | 36.7745 | 37.2151 | 37.3951 | 32.0869 | 31.5136 | 93.1241 | 35.2255 | 34.0442 | 35.5362 | 34.3435 | 33.9893 | 34.1948 | 35.5483 | 34.8226 | 34.6955 | 37.476 | 36.3934 | 34.1632 | 34.7134 | 36.3933 | 36.93 | 37.728 | 36.3968 | 34.3279 | 33.6038 | 35.2861 | 35.613 | 33.7318 | 34.366 | 34.4672 | 33.7577 | 34.5185 | 34.4948 | 34.3754 | 34.0517 | 34.5134 | 35.2889 | 35.8308 | 35.501 | 35.5574 | 34.2958 | 92.8455 | 92.9582 | 93.0872
2022-09-08 00:34 | 2:44 | 14.439 | 16.202 | 17.5345 | 34.5531 | 34.4055 | 34.6865 | 35.5165 | 35.8043 | 36.8799 | 37.4413 | 36.7224 | 37.5448 | 34.4384 | 34.4131 | 35.1948 | 35.7225 | 36.5042 | 36.7682 | 37.2128 | 37.3599 | 32.0691 | 31.5207 | 93.0273 | 35.1748 | 34.0452 | 35.5455 | 34.3359 | 33.9892 | 34.1983 | 35.5438 | 34.8137 | 34.6801 | 37.4959 | 36.3964 | 34.1643 | 34.7269 | 36.4032 | 36.9288 | 37.7304 | 36.3972 | 34.346 | 33.6245 | 35.3012 | 35.5986 | 33.7379 | 34.3873 | 34.4415 | 33.7564 | 34.5114 | 34.5159 | 34.3833 | 34.0684 | 34.5185 | 35.2841 | 35.8283 | 35.5121 | 35.5843 | 34.2969 | 93.0142 | 93.0934 | 93.1286
2022-09-08 00:35 | 2:44 | 14.2749 | 15.9989 | 17.3672 | 34.4776 | 34.3849 | 34.6658 | 35.5359 | 35.8285 | 36.8788 | 37.4563 | 36.7223 | 37.5641 | 34.4187 | 34.394 | 35.2157 | 35.7216 | 36.52 | 36.7511 | 37.2164 | 37.3917 | 32.0747 | 31.5096 | 93.0384 | 35.166 | 34.0633 | 35.5486 | 34.3336 | 33.9832 | 34.1859 | 35.5285 | 34.8116 | 34.6999 | 37.4928 | 36.4267 | 34.1724 | 34.7316 | 36.3934 | 36.916 | 37.7437 | 36.4057 | 34.3394 | 33.642 | 35.2892 | 35.6118 | 33.7309 | 34.3551 | 34.4315 | 33.773 | 34.5304 | 34.5105 | 34.3724 | 34.0642 | 34.5114 | 35.2872 | 35.8416 | 35.5275 | 35.5688 | 34.2933 | 93.1566 | 93.1991 | 93.2062
2022-09-08 00:35 | 2:45 | 14.1176 | 15.8675 | 17.2335 | 34.453 | 34.4143 | 34.6708 | 35.5181 | 35.8247 | 36.8888 | 37.4451 | 36.7211 | 37.5592 | 34.4511 | 34.3927 | 35.2143 | 35.7117 | 36.5151 | 36.7471 | 37.2152 | 37.4024 | 32.0912 | 31.4959 | 93.0882 | 35.1839 | 34.0407 | 35.5378 | 34.3245 | 33.9945 | 34.2034 | 35.5403 | 34.8114 | 34.6967 | 37.5027 | 36.4113 | 34.1832 | 34.6983 | 36.3964 | 36.915 | 37.7458 | 36.3933 | 34.334 | 33.6328 | 35.2888 | 35.6064 | 33.7327 | 34.3778 | 34.4031 | 33.7631 | 34.5156 | 34.5205 | 34.3781 | 34.046 | 34.5304 | 35.2826 | 35.8265 | 35.5067 | 35.5753 | 34.3082 | 93.3074 | 93.3333 | 93.2669
2022-09-08 00:35 | 2:45 | 14.0576 | 15.742 | 17.1457 | 34.252 | 34.3972 | 34.6616 | 35.5144 | 35.8183 | 36.8739 | 37.4574 | 36.7264 | 37.5586 | 34.4283 | 34.4089 | 35.2106 | 35.7031 | 36.4978 | 36.7376 | 37.2114 | 37.4035 | 32.0884 | 31.5105 | 93.1993 | 35.2298 | 34.0581 | 35.5201 | 34.3279 | 33.993 | 34.1632 | 35.5313 | 34.8259 | 34.7019 | 37.4918 | 36.4171 | 34.1842 | 34.7193 | 36.4267 | 36.9232 | 37.727 | 36.4032 | 34.3283 | 33.6278 | 35.3102 | 35.6085 | 33.7281 | 34.3713 | 34.4401 | 33.7554 | 34.5354 | 34.524 | 34.3773 | 34.0595 | 34.5156 | 35.2842 | 35.8274 | 35.497 | 35.5868 | 34.2992 | 93.3809 | 93.5237 | 93.3227
2022-09-08 00:35 | 2:45 | 13.8898 | 15.6317 | 17.0033 | 34.2437 | 34.3841 | 34.6787 | 35.5121 | 35.8144 | 36.9005 | 37.4535 | 36.7161 | 37.5637 | 34.4471 | 34.4066 | 35.2017 | 35.6923 | 36.4935 | 36.7445 | 37.2009 | 37.3772 | 32.0869 | 31.519 | 93.621 | 35.2471 | 34.0556 | 35.5536 | 34.346 | 33.9801 | 34.1643 | 35.5488 | 34.8146 | 34.6931 | 37.5125 | 36.4148 | 34.1841 | 34.7158 | 36.4113 | 36.9187 | 37.751 | 36.3934 | 34.3329 | 33.6409 | 35.2907 | 35.6093 | 33.7588 | 34.3633 | 34.4203 | 33.7841 | 34.528 | 34.5166 | 34.3834 | 34.0516 | 34.5354 | 35.2926 | 35.8234 | 35.5094 | 35.5652 | 34.3127 | 93.562 | 93.6388 | 93.4685
2022-09-08 00:35 | 2:45 | 13.7973 | 15.5336 | 16.892 | 34.2946 | 34.3941 | 34.6703 | 35.526 | 35.8061 | 36.8851 | 37.4586 | 36.7166 | 37.5423 | 34.4458 | 34.4207 | 35.1909 | 35.7181 | 36.5099 | 36.7289 | 37.1877 | 37.3669 | 32.0895 | 31.5211 | 93.6342 | 35.1709 | 34.026 | 35.5536 | 34.3394 | 33.9812 | 34.1724 | 35.5321 | 34.821 | 34.7017 | 37.4823 | 36.4201 | 34.1859 | 34.719 | 36.4171 | 36.9147 | 37.7373 | 36.3964 | 34.3239 | 33.63 | 35.3017 | 35.6197 | 33.7604 | 34.3766 | 34.4203 | 33.752 | 34.5302 | 34.5186 | 34.3858 | 34.0502 | 34.528 | 35.2932 | 35.8179 | 35.4993 | 35.5714 | 34.3122 | 93.727 | 93.7827 | 93.6022
2022-09-08 00:35 | 2:45 | 13.6793 | 15.41 | 16.7379 | 34.2166 | 34.4037 | 34.6549 | 35.5039 | 35.8131 | 36.8827 | 37.425 | 36.704 | 37.5459 | 34.4488 | 34.409 | 35.199 | 35.7076 | 36.4845 | 36.7386 | 37.1771 | 37.376 | 32.0894 | 31.5203 | 93.8213 | 35.1563 | 34.0311 | 35.5299 | 34.334 | 33.9763 | 34.1832 | 35.5333 | 34.8094 | 34.6948 | 37.4797 | 36.4214 | 34.1742 | 34.7299 | 36.4148 | 36.9226 | 37.7171 | 36.4267 | 34.3286 | 33.6363 | 35.2998 | 35.6111 | 33.7568 | 34.3783 | 34.4028 | 33.7743 | 34.5091 | 34.5311 | 34.3911 | 34.0741 | 34.5302 | 35.2956 | 35.8253 | 35.5361 | 35.5668 | 34.3016 | 93.9859 | 93.9914 | 93.715
2022-09-08 00:36 | 2:46 | 13.5811 | 15.3024 | 16.6169 | 34.3174 | 34.3853 | 34.6697 | 35.4959 | 35.8154 | 36.8723 | 37.4344 | 36.6964 | 37.5612 | 34.4568 | 34.411 | 35.1851 | 35.7232 | 36.4772 | 36.7345 | 37.19 | 37.3797 | 32.1091 | 31.545 | 93.8907 | 35.156 | 34.0353 | 35.5325 | 34.3283 | 33.9733 | 34.1842 | 35.5388 | 34.8139 | 34.7045 | 37.4925 | 36.4242 | 34.1786 | 34.7017 | 36.4201 | 36.9109 | 37.7356 | 36.4113 | 34.3322 | 33.631 | 35.3203 | 35.6071 | 33.7651 | 34.3802 | 34.41 | 33.7896 | 34.5243 | 34.529 | 34.3682 | 34.0687 | 34.5091 | 35.2905 | 35.8266 | 35.5279 | 35.5657 | 34.2944 | 94.1413 | 94.1583 | 93.8255
2022-09-08 00:36 | 2:46 | 13.513 | 15.1687 | 16.5021 | 34.2573 | 34.3991 | 34.6292 | 35.5069 | 35.7878 | 36.8743 | 37.4312 | 36.7263 | 37.5588 | 34.4473 | 34.4179 | 35.1881 | 35.7094 | 36.4759 | 36.7269 | 37.1922 | 37.3591 | 32.1024 | 31.5291 | 93.9648 | 35.1421 | 34.0285 | 35.5291 | 34.3329 | 33.9798 | 34.1841 | 35.5147 | 34.8136 | 34.6966 | 37.4813 | 36.4177 | 34.1837 | 34.6991 | 36.4214 | 36.9147 | 37.7371 | 36.4171 | 34.3172 | 33.6277 | 35.3117 | 35.6088 | 33.7657 | 34.3824 | 34.4062 | 33.7887 | 34.5286 | 34.515 | 34.3718 | 34.0618 | 34.5243 | 35.2925 | 35.8275 | 35.5111 | 35.5647 | 34.2814 | 94.2585 | 94.3601 | 93.9006
2022-09-08 00:36 | 2:46 | 13.4039 | 15.1058 | 16.4101 | 34.2316 | 34.3877 | 34.6409 | 35.5084 | 35.7905 | 36.8825 | 37.419 | 36.7062 | 37.5575 | 34.4623 | 34.3964 | 35.1861 | 35.7139 | 36.4717 | 36.722 | 37.1938 | 37.3656 | 32.1009 | 31.5172 | 93.9421 | 35.1511 | 34.0312 | 35.5515 | 34.3239 | 33.977 | 34.1859 | 35.5361 | 34.8048 | 34.684 | 37.5081 | 36.4192 | 34.175 | 34.7024 | 36.4242 | 36.9027 | 37.7241 | 36.4148 | 34.3177 | 33.6465 | 35.3243 | 35.6069 | 33.7561 | 34.3835 | 34.4086 | 33.7809 | 34.52 | 34.5234 | 34.3734 | 34.072 | 34.5286 | 35.3005 | 35.8319 | 35.5267 | 35.5729 | 34.2813 | 94.4263 | 94.4835 | 93.9657
2022-09-08 00:36 | 2:46 | 13.2885 | 14.9633 | 16.2875 | 34.1354 | 34.3896 | 34.6442 | 35.4879 | 35.7903 | 36.8597 | 37.4487 | 36.7078 | 37.5526 | 34.4505 | 34.4229 | 35.1748 | 35.7037 | 36.492 | 36.7337 | 37.1685 | 37.3498 | 32.1074 | 31.5355 | 93.9326 | 35.139 | 34.0294 | 35.5441 | 34.3286 | 33.98 | 34.1742 | 35.5296 | 34.8036 | 34.6701 | 37.475 | 36.4213 | 34.1798 | 34.7099 | 36.4177 | 36.9053 | 37.6999 | 36.4201 | 34.3041 | 33.6592 | 35.3013 | 35.6081 | 33.7711 | 34.3919 | 34.3894 | 33.7739 | 34.5276 | 34.5235 | 34.3861 | 34.0796 | 34.52 | 35.266 | 35.8319 | 35.5108 | 35.5771 | 34.2737 | 94.6332 | 94.6031 | 94.1173
2022-09-08 00:36 | 2:46 | 13.1024 | 14.7841 | 16.1885 | 34.0964 | 34.3913 | 34.6379 | 35.5052 | 35.7979 | 36.8716 | 37.4092 | 36.7375 | 37.5322 | 34.4601 | 34.4296 | 35.1541 | 35.6949 | 36.4819 | 36.731 | 37.1735 | 37.3447 | 32.1079 | 31.5217 | 93.9268 | 35.1923 | 34.0387 | 35.5404 | 34.3322 | 33.9676 | 34.1786 | 35.5206 | 34.7919 | 34.688 | 37.4835 | 36.4453 | 34.1801 | 34.7019 | 36.4192 | 36.8974 | 37.7114 | 36.4214 | 34.3174 | 33.6562 | 35.3234 | 35.6048 | 33.7826 | 34.3925 | 34.3925 | 33.7844 | 34.5259 | 34.5212 | 34.3814 | 34.0763 | 34.5276 | 35.2954 | 35.8198 | 35.5317 | 35.5781 | 34.2656 | 94.7768 | 94.7667 | 94.1899
2022-09-08 00:36 | 2:46 | 13.0461 | 14.6889 | 16.0213 | 33.9956 | 34.3937 | 34.6263 | 35.497 | 35.786 | 36.8683 | 37.4247 | 36.7138 | 37.5321 | 34.4486 | 34.4419 | 35.1574 | 35.6877 | 36.4608 | 36.6959 | 37.163 | 37.3464 | 32.1214 | 31.5395 | 93.7506 | 35.0748 | 34.0301 | 35.5449 | 34.3172 | 33.9595 | 34.1837 | 35.5253 | 34.8207 | 34.6735 | 37.4672 | 36.4306 | 34.1712 | 34.6957 | 36.4213 | 36.902 | 37.7025 | 36.4242 | 34.3188 | 33.6561 | 35.3048 | 35.613 | 33.7847 | 34.3942 | 34.3826 | 33.7679 | 34.5264 | 34.5264 | 34.3775 | 34.0873 | 34.5259 | 35.2581 | 35.8141 | 35.5121 | 35.5652 | 34.2739 | 94.8358 | 94.9108 | 94.2092
2022-09-08 00:37 | 2:46 | 12.9498 | 14.6416 | 15.9241 | 33.9754 | 34.382 | 34.6289 | 35.4606 | 35.7447 | 36.8666 | 37.4219 | 36.7112 | 37.5641 | 34.4761 | 34.44 | 35.1602 | 35.6888 | 36.4411 | 36.7103 | 37.1513 | 37.3304 | 32.1399 | 31.5252 | 93.6628 | 35.1596 | 34.0299 | 35.5414 | 34.3177 | 33.9732 | 34.175 | 35.5163 | 34.8022 | 34.6853 | 37.4687 | 36.4027 | 34.1939 | 34.715 | 36.4453 | 36.9016 | 37.7131 | 36.4177 | 34.3349 | 33.657 | 35.316 | 35.6032 | 33.7975 | 34.3892 | 34.3957 | 33.7514 | 34.5164 | 34.532 | 34.392 | 34.0707 | 34.5264 | 35.2803 | 35.8238 | 35.5222 | 35.5798 | 34.2637 | 94.935 | 95.0242 | 94.3399
2022-09-08 00:37 | 2:47 | 12.8923 | 14.5055 | 15.842 | 33.9994 | 34.3771 | 34.6145 | 35.4676 | 35.773 | 36.865 | 37.4103 | 36.7078 | 37.5525 | 34.4657 | 34.4337 | 35.1652 | 35.6945 | 36.4662 | 36.6835 | 37.1383 | 37.3257 | 32.1215 | 31.523 | 93.5642 | 35.1183 | 34.0273 | 35.5541 | 34.3041 | 33.9871 | 34.1798 | 35.5179 | 34.7972 | 34.6755 | 37.4757 | 36.4196 | 34.1723 | 34.7087 | 36.4306 | 36.9056 | 37.715 | 36.4192 | 34.3155 | 33.6505 | 35.3137 | 35.6111 | 33.8052 | 34.3941 | 34.4073 | 33.7938 | 34.5196 | 34.5422 | 34.3765 | 34.0878 | 34.5164 | 35.3092 | 35.8376 | 35.524 | 35.5491 | 34.2844 | 95.0186 | 95.1131 | 94.3397
2022-09-08 00:37 | 2:47 | 12.0889 | 12.7064 | 15.1939 | 33.9949 | 34.411 | 34.623 | 35.4668 | 35.783 | 36.8645 | 37.4285 | 36.72 | 37.5568 | 34.469 | 34.4416 | 35.158 | 35.7001 | 36.4429 | 36.6958 | 37.1422 | 37.3461 | 32.0852 | 31.5423 | 93.2339 | 35.1184 | 34.0181 | 35.5489 | 34.3174 | 33.9721 | 34.1801 | 35.5129 | 34.8 | 34.6788 | 37.4845 | 36.4233 | 34.1789 | 34.7027 | 36.4027 | 36.8864 | 37.7199 | 36.4213 | 34.3366 | 33.6601 | 35.3076 | 35.6159 | 33.808 | 34.4079 | 34.3946 | 33.7917 | 34.5234 | 34.5447 | 34.3869 | 34.0819 | 34.5196 | 35.2757 | 35.8207 | 35.5341 | 35.5812 | 34.2764 | 95.0763 | 95.2177 | 94.455
2022-09-08 00:37 | 2:47 | 14.5755 | 13.0657 | 16.4058 | 33.8581 | 34.3903 | 34.6314 | 35.4474 | 35.7614 | 36.8619 | 37.3929 | 36.7019 | 37.5475 | 34.4839 | 34.456 | 35.1456 | 35.6869 | 36.4288 | 36.6783 | 37.1336 | 37.3199 | 32.0635 | 31.5352 | 93.2982 | 35.0827 | 34.0282 | 35.5529 | 34.3188 | 33.9712 | 34.1712 | 35.5104 | 34.7887 | 34.682 | 37.4853 | 36.439 | 34.1713 | 34.6826 | 36.4196 | 36.8937 | 37.7296 | 36.4453 | 34.3373 | 33.6682 | 35.3083 | 35.6244 | 33.798 | 34.413 | 34.3862 | 33.7883 | 34.5318 | 34.5512 | 34.3803 | 34.0737 | 34.5234 | 35.2783 | 35.8228 | 35.5091 | 35.584 | 34.2647 | 95.1098 | 95.2266 | 94.4438
2022-09-08 00:37 | 2:47 | 16.3317 | 14.6291 | 18.5815 | 33.903 | 34.3847 | 34.6112 | 35.4486 | 35.7683 | 36.8691 | 37.4201 | 36.7005 | 37.5478 | 34.4885 | 34.4223 | 35.1623 | 35.6933 | 36.4386 | 36.6937 | 37.124 | 37.3451 | 32.0803 | 31.5414 | 93.315 | 35.1908 | 34.0111 | 35.5483 | 34.3349 | 33.9838 | 34.1939 | 35.5176 | 34.8019 | 34.6771 | 37.4713 | 36.419 | 34.1566 | 34.6904 | 36.4233 | 36.8929 | 37.7211 | 36.4306 | 34.3199 | 33.6505 | 35.3417 | 35.5959 | 33.8275 | 34.4139 | 34.3777 | 33.7842 | 34.523 | 34.5315 | 34.3792 | 34.0895 | 34.5318 | 35.2992 | 35.8224 | 35.541 | 35.5673 | 34.26 | 94.9302 | 95.0915 | 94.3104
2022-09-08 00:37 | 2:47 | 17.9547 | 16.5063 | 20.7117 | 34.14 | 34.3867 | 34.6271 | 35.4445 | 35.7763 | 36.854 | 37.4152 | 36.7067 | 37.5555 | 34.4627 | 34.4529 | 35.1475 | 35.6627 | 36.443 | 36.6916 | 37.1149 | 37.34 | 32.0811 | 31.5277 | 93.1706 | 35.2194 | 34.0183 | 35.5563 | 34.3155 | 33.9674 | 34.1723 | 35.5201 | 34.8016 | 34.6827 | 37.4754 | 36.4415 | 34.1707 | 34.6783 | 36.439 | 36.8997 | 37.7025 | 36.4027 | 34.3311 | 33.6647 | 35.3198 | 35.5827 | 33.8309 | 34.4005 | 34.3956 | 33.7916 | 34.5256 | 34.5338 | 34.3854 | 34.0744 | 34.523 | 35.2863 | 35.8389 | 35.5236 | 35.5802 | 34.2497 | 94.7187 | 94.916 | 94.1469
2022-09-08 00:38 | 2:47 | 19.2784 | 18.3906 | 22.5481 | 34.2223 | 34.3794 | 34.602 | 35.4698 | 35.7702 | 36.8658 | 37.4129 | 36.7084 | 37.5424 | 34.4792 | 34.4382 | 35.1399 | 35.6916 | 36.4512 | 36.6904 | 37.1386 | 37.3317 | 32.1056 | 31.5463 | 93.134 | 35.173 | 34.0306 | 35.5512 | 34.3366 | 33.9758 | 34.1789 | 35.5089 | 34.8194 | 34.6793 | 37.4802 | 36.4406 | 34.1673 | 34.6854 | 36.419 | 36.8891 | 37.7097 | 36.4196 | 34.3279 | 33.6636 | 35.3474 | 35.6049 | 33.8203 | 34.4228 | 34.3873 | 33.7792 | 34.5383 | 34.5333 | 34.3719 | 34.0726 | 34.5256 | 35.2737 | 35.8173 | 35.5274 | 35.5731 | 34.2636 | 94.4856 | 94.6996 | 94.0147
2022-09-08 00:38 | 2:48 | 20.5135 | 20.203 | 23.9857 | 34.4193 | 34.3867 | 34.601 | 35.4379 | 35.7717 | 36.8596 | 37.3999 | 36.7135 | 37.5477 | 34.484 | 34.4355 | 35.147 | 35.6945 | 36.4416 | 36.6841 | 37.1275 | 37.335 | 32.1164 | 31.5578 | 93.1569 | 35.2193 | 34.0223 | 35.5475 | 34.3373 | 33.9492 | 34.1713 | 35.5114 | 34.8118 | 34.6711 | 37.4701 | 36.4334 | 34.1826 | 34.6934 | 36.4415 | 36.8882 | 37.703 | 36.4233 | 34.3299 | 33.6747 | 35.3187 | 35.6384 | 33.855 | 34.428 | 34.3965 | 33.7783 | 34.5317 | 34.538 | 34.3863 | 34.084 | 34.5383 | 35.2711 | 35.8443 | 35.536 | 35.5684 | 34.2651 | 94.2493 | 94.4819 | 93.8628
2022-09-08 00:38 | 2:48 | 21.6028 | 21.8385 | 25.0631 | 34.4574 | 34.3824 | 34.6293 | 35.4605 | 35.7855 | 36.8587 | 37.4171 | 36.7372 | 37.5527 | 34.4718 | 34.4299 | 35.1497 | 35.7022 | 36.4249 | 36.6716 | 37.1356 | 37.3163 | 32.127 | 31.5437 | 93.2055 | 35.2036 | 34.0294 | 35.578 | 34.3199 | 33.9728 | 34.1566 | 35.5145 | 34.821 | 34.6861 | 37.4757 | 36.4438 | 34.1759 | 34.6888 | 36.4406 | 36.9217 | 37.7149 | 36.439 | 34.3538 | 33.6702 | 35.3421 | 35.6296 | 33.8434 | 34.4127 | 34.3668 | 33.7916 | 34.5299 | 34.5456 | 34.3726 | 34.0689 | 34.5317 | 35.2706 | 35.8339 | 35.5278 | 35.5771 | 34.241 | 94.0789 | 94.306 | 93.8007
2022-09-08 00:38 | 2:48 | 22.5291 | 23.2509 | 26.3011 | 34.5294 | 34.369 | 34.6456 | 35.4601 | 35.7856 | 36.8568 | 37.4023 | 36.7331 | 37.5663 | 34.4673 | 34.443 | 35.1667 | 35.7002 | 36.4228 | 36.7044 | 37.1592 | 37.3421 | 32.1828 | 31.5746 | 92.989 | 35.1973 | 34.0247 | 35.5762 | 34.3311 | 33.9604 | 34.1707 | 35.4869 | 34.8023 | 34.6858 | 37.4722 | 36.4481 | 34.1937 | 34.7107 | 36.4334 | 36.9052 | 37.6994 | 36.419 | 34.3261 | 33.6825 | 35.3354 | 35.608 | 33.8603 | 34.4023 | 34.3864 | 33.7949 | 34.5159 | 34.5389 | 34.3944 | 34.0942 | 34.5299 | 35.308 | 35.8266 | 35.5335 | 35.5874 | 34.2668 | 93.9594 | 94.1535 | 93.7086
2022-09-08 00:38 | 2:48 | 23.4269 | 24.4672 | 27.1472 | 34.6855 | 34.3826 | 34.6131 | 35.4932 | 35.789 | 36.8478 | 37.41 | 36.7332 | 37.5719 | 34.5022 | 34.4311 | 35.1484 | 35.6952 | 36.4118 | 36.6788 | 37.1536 | 37.3451 | 32.1888 | 31.5503 | 93.09 | 35.2121 | 34.0154 | 35.5563 | 34.3279 | 33.97 | 34.1673 | 35.5079 | 34.8091 | 34.6735 | 37.4779 | 36.4287 | 34.1957 | 34.7256 | 36.4438 | 36.9028 | 37.7147 | 36.4415 | 34.3333 | 33.6669 | 35.348 | 35.6299 | 33.8265 | 34.421 | 34.3865 | 33.806 | 34.5281 | 34.558 | 34.385 | 34.1041 | 34.5159 | 35.2994 | 35.8204 | 35.5238 | 35.5649 | 34.2695 | 93.8548 | 94.047 | 93.6475
2022-09-08 00:38 | 2:48 | 24.1397 | 25.5068 | 27.4783 | 34.8274 | 34.3901 | 34.6367 | 35.4861 | 35.7807 | 36.8601 | 37.4208 | 36.7398 | 37.5735 | 34.4804 | 34.4389 | 35.1474 | 35.715 | 36.4263 | 36.6906 | 37.1546 | 37.3467 | 32.2148 | 31.572 | 92.9039 | 35.1914 | 34.0149 | 35.5774 | 34.3299 | 33.9686 | 34.1826 | 35.5112 | 34.8127 | 34.6865 | 37.4775 | 36.4448 | 34.1712 | 34.7156 | 36.4481 | 36.8985 | 37.6954 | 36.4406 | 34.3281 | 33.6755 | 35.3566 | 35.644 | 33.8668 | 34.4118 | 34.3892 | 33.7972 | 34.5265 | 34.5571 | 34.3849 | 34.0721 | 34.5281 | 35.2806 | 35.8318 | 35.5325 | 35.568 | 34.2685 | 93.7574 | 93.8984 | 93.5899
2022-09-08 00:39 | 2:49 | 24.8715 | 26.3753 | 27.9617 | 34.9031 | 34.3802 | 34.6327 | 35.4849 | 35.7836 | 36.8448 | 37.4075 | 36.7209 | 37.5657 | 34.4997 | 34.4469 | 35.1448 | 35.7311 | 36.4223 | 36.6853 | 37.1659 | 37.3328 | 32.3616 | 31.5728 | 92.9836 | 35.2557 | 34.028 | 35.5768 | 34.3538 | 33.9855 | 34.1759 | 35.5245 | 34.8071 | 34.6873 | 37.4857 | 36.4389 | 34.1926 | 34.7229 | 36.4287 | 36.9102 | 37.6958 | 36.4334 | 34.3568 | 33.689 | 35.3366 | 35.6357 | 33.8733 | 34.4243 | 34.3744 | 33.8088 | 34.5041 | 34.5525 | 34.4131 | 34.1023 | 34.5265 | 35.3014 | 35.8363 | 35.5333 | 35.6008 | 34.2717 | 93.6642 | 93.8424 | 93.4648
2022-09-08 00:39 | 2:49 | 26.3344 | 20.4129 | 25.9549 | 34.832 | 34.3905 | 34.6543 | 35.5052 | 35.7888 | 36.8719 | 37.404 | 36.7368 | 37.5656 | 34.4834 | 34.4404 | 35.1632 | 35.7219 | 36.4201 | 36.6854 | 37.1827 | 37.3423 | 32.5272 | 31.5977 | 92.9028 | 35.2091 | 34.0344 | 35.5695 | 34.3261 | 33.9828 | 34.1937 | 35.5155 | 34.8153 | 34.6886 | 37.472 | 36.4653 | 34.1749 | 34.7194 | 36.4448 | 36.8862 | 37.7028 | 36.4438 | 34.35 | 33.7047 | 35.3426 | 35.6422 | 33.8627 | 34.4173 | 34.3846 | 33.8005 | 34.5163 | 34.5464 | 34.394 | 34.1013 | 34.5041 | 35.3109 | 35.8297 | 35.5278 | 35.5862 | 34.2804 | 93.5814 | 93.727 | 93.4312
2022-09-08 00:39 | 2:49 | 27.4477 | 26.638 | 26.9393 | 34.8477 | 34.3869 | 34.6547 | 35.5049 | 35.7976 | 36.8522 | 37.4193 | 36.7466 | 37.5561 | 34.5132 | 34.4671 | 35.1446 | 35.7044 | 36.4218 | 36.6931 | 37.1741 | 37.3455 | 32.6071 | 31.5753 | 92.8358 | 35.2054 | 34.0281 | 35.5716 | 34.3333 | 33.9979 | 34.1957 | 35.4846 | 34.8228 | 34.691 | 37.482 | 36.4515 | 34.1866 | 34.7266 | 36.4389 | 36.9194 | 37.7092 | 36.4481 | 34.3425 | 33.6933 | 35.3432 | 35.6423 | 33.8878 | 34.4247 | 34.3785 | 33.7988 | 34.5282 | 34.5564 | 34.3927 | 34.0959 | 34.5163 | 35.2845 | 35.8269 | 35.5388 | 35.5951 | 34.2612 | 93.5394 | 93.6796 | 93.3977
2022-09-08 00:39 | 2:49 | 30.228 | 29.9742 | 28.7305 | 34.8948 | 34.3754 | 34.6567 | 35.517 | 35.807 | 36.865 | 37.4298 | 36.7308 | 37.5822 | 34.4918 | 34.4465 | 35.1501 | 35.7237 | 36.4142 | 36.7042 | 37.1694 | 37.3381 | 32.7418 | 31.7873 | 92.7244 | 35.3121 | 34.0255 | 35.592 | 34.3281 | 33.9951 | 34.1712 | 35.5038 | 34.8276 | 34.6809 | 37.498 | 36.4699 | 34.1786 | 34.7214 | 36.4653 | 36.9109 | 37.7135 | 36.4287 | 34.338 | 33.6963 | 35.3467 | 35.6692 | 33.8921 | 34.4217 | 34.3644 | 33.8296 | 34.5365 | 34.5572 | 34.4089 | 34.1025 | 34.5282 | 35.3088 | 35.8395 | 35.5662 | 35.578 | 34.2784 | 93.4721 | 93.6132 | 93.3587
2022-09-08 00:39 | 2:49 | 31.6122 | 30.4911 | 29.7528 | 35.1729 | 34.3833 | 34.6376 | 35.5393 | 35.7916 | 36.8796 | 37.4074 | 36.7521 | 37.5804 | 34.5001 | 34.465 | 35.1502 | 35.7352 | 36.4018 | 36.6886 | 37.1651 | 37.343 | 32.9891 | 31.7996 | 92.722 | 35.2391 | 34.0341 | 35.5935 | 34.3568 | 33.979 | 34.1926 | 35.5073 | 34.8229 | 34.7073 | 37.4771 | 36.4443 | 34.1919 | 34.7373 | 36.4515 | 36.8909 | 37.7346 | 36.4448 | 34.3295 | 33.7017 | 35.3529 | 35.6654 | 33.8998 | 34.426 | 34.3547 | 33.8163 | 34.5052 | 34.5596 | 34.4066 | 34.1093 | 34.5365 | 35.3026 | 35.8311 | 35.5532 | 35.6118 | 34.2795 | 93.3922 | 93.5076 | 93.211
2022-09-08 00:39 | 2:49 | 32.4549 | 30.7029 | 30.2888 | 35.1436 | 34.3724 | 34.6676 | 35.5286 | 35.8042 | 36.8585 | 37.4331 | 36.742 | 37.5617 | 34.4813 | 34.471 | 35.1597 | 35.7396 | 36.399 | 36.7032 | 37.1721 | 37.3433 | 33.4076 | 31.7127 | 92.5331 | 35.2863 | 34.0305 | 35.5746 | 34.35 | 33.9784 | 34.1749 | 35.4998 | 34.823 | 34.69 | 37.4942 | 36.4516 | 34.1813 | 34.7282 | 36.4699 | 36.9135 | 37.7076 | 36.4389 | 34.351 | 33.7009 | 35.3598 | 35.6769 | 33.9004 | 34.4297 | 34.3855 | 33.8163 | 34.5077 | 34.5483 | 34.4207 | 34.1066 | 34.5052 | 35.3157 | 35.835 | 35.5596 | 35.5932 | 34.2925 | 93.2972 | 93.4492 | 93.1841
2022-09-08 00:40 | 2:49 | 32.9552 | 30.7709 | 30.6368 | 35.2124 | 34.3781 | 34.6491 | 35.5532 | 35.8019 | 36.8555 | 37.4263 | 36.752 | 37.6032 | 34.5003 | 34.4436 | 35.1628 | 35.7486 | 36.3909 | 36.6991 | 37.2035 | 37.3443 | 33.716 | 31.6994 | 92.5345 | 35.3325 | 34.0412 | 35.5716 | 34.3425 | 33.9948 | 34.1866 | 35.4997 | 34.8382 | 34.6948 | 37.5128 | 36.4674 | 34.1838 | 34.7321 | 36.4443 | 36.9099 | 37.7049 | 36.4653 | 34.3485 | 33.6929 | 35.3802 | 35.6567 | 33.9103 | 34.441 | 34.3825 | 33.8185 | 34.5046 | 34.5636 | 34.409 | 34.1014 | 34.5077 | 35.3137 | 35.8413 | 35.535 | 35.609 | 34.2735 | 93.2263 | 93.4293 | 93.1572
2022-09-08 00:40 | 2:50 | 33.3058 | 30.862 | 30.8775 | 35.247 | 34.3773 | 34.6659 | 35.5636 | 35.8192 | 36.871 | 37.4298 | 36.7485 | 37.5873 | 34.5073 | 34.4717 | 35.166 | 35.7454 | 36.4248 | 36.7003 | 37.2014 | 37.3579 | 33.9028 | 31.6754 | 92.4775 | 35.3478 | 34.0296 | 35.6049 | 34.338 | 33.9937 | 34.1786 | 35.503 | 34.8147 | 34.6836 | 37.4967 | 36.451 | 34.1838 | 34.7422 | 36.4516 | 36.9136 | 37.7233 | 36.4515 | 34.3507 | 33.7162 | 35.3833 | 35.6913 | 33.8974 | 34.4365 | 34.3695 | 33.8462 | 34.5253 | 34.568 | 34.411 | 34.1224 | 34.5046 | 35.3349 | 35.8346 | 35.5371 | 35.6128 | 34.2906 | 93.1871 | 93.3369 | 93.1501
2022-09-08 00:40 | 2:50 | 33.6051 | 30.9661 | 31.0711 | 35.2995 | 34.3834 | 34.6602 | 35.5492 | 35.8218 | 36.8545 | 37.4417 | 36.751 | 37.5984 | 34.4845 | 34.4547 | 35.1439 | 35.7543 | 36.4112 | 36.6971 | 37.1987 | 37.3533 | 34.0282 | 31.6634 | 92.4059 | 35.3705 | 34.0422 | 35.5824 | 34.3295 | 33.9847 | 34.1919 | 35.5115 | 34.8321 | 34.6878 | 37.4964 | 36.472 | 34.1878 | 34.7411 | 36.4674 | 36.9144 | 37.7152 | 36.4699 | 34.3609 | 33.7266 | 35.387 | 35.7044 | 33.9221 | 34.4279 | 34.3678 | 33.8242 | 34.4931 | 34.5542 | 34.4179 | 34.1248 | 34.5253 | 35.3218 | 35.8418 | 35.5494 | 35.6221 | 34.3022 | 93.0379 | 93.2463 | 92.9925
2022-09-08 00:40 | 2:50 | 33.6466 | 31.0378 | 31.2106 | 35.3837 | 34.3858 | 34.6575 | 35.5684 | 35.8192 | 36.8679 | 37.445 | 36.7657 | 37.5875 | 34.524 | 34.459 | 35.1558 | 35.7506 | 36.4122 | 36.7028 | 37.1957 | 37.3708 | 34.0232 | 31.6797 | 92.3172 | 35.3817 | 34.046 | 35.6083 | 34.351 | 33.9858 | 34.1813 | 35.5105 | 34.8365 | 34.7118 | 37.488 | 36.4536 | 34.1871 | 34.7472 | 36.451 | 36.9261 | 37.7253 | 36.4443 | 34.3482 | 33.7103 | 35.3777 | 35.6945 | 33.9144 | 34.437 | 34.3802 | 33.8386 | 34.502 | 34.5784 | 34.3964 | 34.1288 | 34.4931 | 35.3276 | 35.8395 | 35.5566 | 35.6258 | 34.2902 | 92.9601 | 93.1705 | 92.9453
2022-09-08 00:40 | 2:50 | 33.6329 | 31.0983 | 31.2217 | 35.5598 | 34.3911 | 34.6823 | 35.559 | 35.8228 | 36.8664 | 37.4594 | 36.7543 | 37.5869 | 34.5103 | 34.4436 | 35.1816 | 35.7483 | 36.3992 | 36.7017 | 37.2195 | 37.3754 | 34.0725 | 31.6725 | 92.0988 | 35.427 | 34.0403 | 35.5968 | 34.3485 | 33.9903 | 34.1838 | 35.496 | 34.8346 | 34.7038 | 37.5066 | 36.4548 | 34.1757 | 34.7231 | 36.472 | 36.9112 | 37.7276 | 36.4516 | 34.3813 | 33.7173 | 35.3918 | 35.6928 | 33.9121 | 34.4252 | 34.3605 | 33.8461 | 34.4957 | 34.5839 | 34.4229 | 34.1161 | 34.502 | 35.3066 | 35.8378 | 35.562 | 35.6087 | 34.3078 | 92.8846 | 93.0563 | 92.9566
2022-09-08 00:40 | 2:50 | 33.6232 | 31.1051 | 31.2797 | 35.6005 | 34.3682 | 34.675 | 35.5808 | 35.8189 | 36.8675 | 37.4469 | 36.7607 | 37.5942 | 34.5049 | 34.4778 | 35.1679 | 35.7737 | 36.4011 | 36.7167 | 37.2282 | 37.3729 | 34.106 | 31.6639 | 91.9704 | 35.4185 | 34.0352 | 35.5901 | 34.3507 | 33.9698 | 34.1838 | 35.5155 | 34.834 | 34.7083 | 37.4994 | 36.4556 | 34.1942 | 34.7474 | 36.4536 | 36.9198 | 37.7191 | 36.4674 | 34.3652 | 33.7359 | 35.4025 | 35.7068 | 33.9286 | 34.4519 | 34.3851 | 33.829 | 34.4831 | 34.5676 | 34.4296 | 34.119 | 34.4957 | 35.335 | 35.8405 | 35.5673 | 35.6313 | 34.322 | 92.8197 | 92.9781 | 92.9253
2022-09-08 00:41 | 2:51 | 33.3793 | 31.1424 | 31.3392 | 35.5454 | 34.3718 | 34.6705 | 35.5873 | 35.8325 | 36.8784 | 37.4514 | 36.7719 | 37.597 | 34.4975 | 34.48 | 35.1651 | 35.75 | 36.4115 | 36.6968 | 37.2174 | 37.353 | 34.1591 | 31.6866 | 91.9079 | 35.4746 | 34.0517 | 35.6038 | 34.3609 | 33.9745 | 34.1878 | 35.5134 | 34.8422 | 34.7119 | 37.5222 | 36.4649 | 34.1971 | 34.7425 | 36.4548 | 36.9198 | 37.7336 | 36.451 | 34.3573 | 33.7378 | 35.4042 | 35.714 | 33.9314 | 34.4396 | 34.373 | 33.8504 | 34.4669 | 34.5672 | 34.4419 | 34.1373 | 34.4831 | 35.3377 | 35.8402 | 35.5751 | 35.6266 | 34.3273 | 92.7053 | 92.8711 | 92.789
2022-09-08 00:41 | 2:51 | 33.691 | 31.194 | 31.3721 | 35.6052 | 34.3734 | 34.6619 | 35.5936 | 35.8476 | 36.8786 | 37.4685 | 36.7668 | 37.6087 | 34.4876 | 34.4678 | 35.1873 | 35.765 | 36.4067 | 36.7303 | 37.2235 | 37.3664 | 34.2276 | 31.6825 | 91.795 | 35.4599 | 34.0642 | 35.6081 | 34.3482 | 33.9795 | 34.1871 | 35.5129 | 34.8325 | 34.6957 | 37.5024 | 36.4586 | 34.206 | 34.7531 | 36.4556 | 36.914 | 37.727 | 36.472 | 34.3558 | 33.7478 | 35.4228 | 35.7184 | 33.9287 | 34.4511 | 34.387 | 33.8548 | 34.4927 | 34.5646 | 34.44 | 34.1446 | 34.4669 | 35.3434 | 35.8274 | 35.5678 | 35.6161 | 34.3182 | 92.5344 | 92.7473 | 92.722
2022-09-08 00:41 | 2:51 | 33.9549 | 31.2185 | 31.4286 | 35.6285 | 34.3861 | 34.6764 | 35.5976 | 35.8595 | 36.8684 | 37.4544 | 36.7747 | 37.5912 | 34.5055 | 34.486 | 35.1823 | 35.7677 | 36.3912 | 36.7131 | 37.2327 | 37.3703 | 34.3112 | 31.687 | 91.7317 | 35.4461 | 34.0609 | 35.6024 | 34.3813 | 34.0074 | 34.1757 | 35.5162 | 34.8438 | 34.7049 | 37.5042 | 36.4612 | 34.2071 | 34.7486 | 36.4649 | 36.9199 | 37.7289 | 36.4536 | 34.3404 | 33.7347 | 35.4038 | 35.7377 | 33.9595 | 34.4442 | 34.3648 | 33.8479 | 34.4716 | 34.5722 | 34.4337 | 34.1493 | 34.4927 | 35.3635 | 35.8266 | 35.5873 | 35.6338 | 34.3181 | 92.4535 | 92.6594 | 92.6285
2022-09-08 00:41 | 2:51 | 34.149 | 31.2639 | 31.5404 | 35.7137 | 34.3814 | 34.6809 | 35.6072 | 35.844 | 36.8849 | 37.4604 | 36.7612 | 37.6148 | 34.5152 | 34.4632 | 35.1814 | 35.7768 | 36.4015 | 36.7176 | 37.2464 | 37.3777 | 34.4141 | 31.6919 | 91.7607 | 35.4708 | 34.0622 | 35.6137 | 34.3652 | 33.9924 | 34.1942 | 35.5322 | 34.8454 | 34.7009 | 37.509 | 36.4454 | 34.1897 | 34.7637 | 36.4586 | 36.9192 | 37.7397 | 36.4548 | 34.3498 | 33.7515 | 35.4323 | 35.7455 | 33.9665 | 34.4433 | 34.3713 | 33.8772 | 34.4777 | 34.5739 | 34.4416 | 34.1421 | 34.4716 | 35.346 | 35.8462 | 35.5639 | 35.6535 | 34.3319 | 92.2743 | 92.5196 | 92.5248
2022-09-08 00:41 | 2:51 | 34.2445 | 31.3219 | 31.6258 | 35.7235 | 34.3775 | 34.67 | 35.6023 | 35.8487 | 36.8852 | 37.4679 | 36.7739 | 37.6142 | 34.511 | 34.4693 | 35.1804 | 35.7833 | 36.4 | 36.7064 | 37.247 | 37.38 | 34.4614 | 31.6864 | 91.796 | 35.5161 | 34.0678 | 35.6091 | 34.3573 | 33.9803 | 34.1971 | 35.5049 | 34.8405 | 34.7056 | 37.5246 | 36.4572 | 34.1961 | 34.7554 | 36.4612 | 36.9254 | 37.7357 | 36.4556 | 34.3404 | 33.7591 | 35.4408 | 35.7441 | 33.9553 | 34.4596 | 34.3747 | 33.8799 | 34.472 | 34.5524 | 34.456 | 34.1483 | 34.4777 | 35.3515 | 35.841 | 35.5741 | 35.64 | 34.3358 | 92.1798 | 92.4146 | 92.5495
2022-09-08 00:41 | 2:51 | 34.3098 | 31.3528 | 31.6722 | 35.8796 | 34.392 | 34.6639 | 35.6018 | 35.834 | 36.8805 | 37.4812 | 36.7795 | 37.6067 | 34.4948 | 34.499 | 35.1754 | 35.7743 | 36.4054 | 36.7438 | 37.232 | 37.394 | 34.4903 | 31.6732 | 91.7514 | 35.5062 | 34.037 | 35.6071 | 34.3558 | 33.9929 | 34.206 | 35.4998 | 34.8249 | 34.7106 | 37.5054 | 36.4485 | 34.1954 | 34.7473 | 36.4454 | 36.9358 | 37.7227 | 36.4649 | 34.3394 | 33.7516 | 35.43 | 35.7489 | 33.9509 | 34.4457 | 34.3605 | 33.8813 | 34.4674 | 34.5728 | 34.4223 | 34.1434 | 34.472 | 35.3728 | 35.8431 | 35.5583 | 35.6446 | 34.323 | 92.103 | 92.2902 | 92.4518
2022-09-08 00:42 | 2:51 | 34.3748 | 31.3892 | 31.7201 | 35.7711 | 34.3765 | 34.6601 | 35.5875 | 35.8431 | 36.8948 | 37.4614 | 36.7672 | 37.6125 | 34.5159 | 34.49 | 35.187 | 35.7778 | 36.3987 | 36.7158 | 37.2742 | 37.3777 | 34.5702 | 31.6824 | 91.8623 | 35.5612 | 34.0526 | 35.5966 | 34.3404 | 33.9923 | 34.2071 | 35.5005 | 34.8177 | 34.6985 | 37.5041 | 36.4501 | 34.2024 | 34.7732 | 36.4572 | 36.9273 | 37.7274 | 36.4586 | 34.3327 | 33.7572 | 35.4462 | 35.7501 | 33.9546 | 34.4453 | 34.3467 | 33.8751 | 34.462 | 34.58 | 34.4529 | 34.1478 | 34.4674 | 35.3767 | 35.8293 | 35.5772 | 35.6488 | 34.3524 | 91.9459 | 92.2145 | 92.2682
2022-09-08 00:42 | 2:52 | 34.5809 | 31.4383 | 31.8372 | 35.8163 | 34.3869 | 34.6813 | 35.5759 | 35.8601 | 36.8839 | 37.4915 | 36.767 | 37.6092 | 34.5105 | 34.4802 | 35.1862 | 35.7633 | 36.3923 | 36.7336 | 37.2553 | 37.3944 | 34.7032 | 31.6742 | 91.8932 | 35.5654 | 34.0687 | 35.592 | 34.3498 | 33.9883 | 34.1897 | 35.5106 | 34.8265 | 34.703 | 37.5074 | 36.4335 | 34.2013 | 34.7552 | 36.4485 | 36.9257 | 37.7501 | 36.4612 | 34.3404 | 33.7648 | 35.4499 | 35.7598 | 33.9766 | 34.4519 | 34.3521 | 33.8858 | 34.4595 | 34.5568 | 34.4382 | 34.1348 | 34.462 | 35.3672 | 35.8379 | 35.562 | 35.6447 | 34.3418 | 91.8198 | 92.0885 | 92.2312
2022-09-08 00:42 | 2:52 | 34.8097 | 31.4633 | 31.9175 | 35.8055 | 34.3803 | 34.6719 | 35.5864 | 35.856 | 36.8795 | 37.4881 | 36.7849 | 37.6075 | 34.5205 | 34.4823 | 35.1943 | 35.7762 | 36.3885 | 36.7411 | 37.2773 | 37.3939 | 34.7966 | 31.6938 | 92.0435 | 35.6486 | 34.0661 | 35.5913 | 34.3404 | 33.9884 | 34.1961 | 35.5308 | 34.8315 | 34.6851 | 37.5112 | 36.431 | 34.1905 | 34.7695 | 36.4501 | 36.9206 | 37.7469 | 36.4454 | 34.3365 | 33.7686 | 35.4475 | 35.7519 | 33.9733 | 34.4597 | 34.365 | 33.8957 | 34.4501 | 34.5423 | 34.4355 | 34.15 | 34.4595 | 35.392 | 35.8402 | 35.5648 | 35.6368 | 34.349 | 91.7431 | 91.9254 | 92.1705
2022-09-08 00:42 | 2:52 | 34.8869 | 31.4943 | 32.0218 | 35.9833 | 34.3792 | 34.6872 | 35.5917 | 35.8429 | 36.8789 | 37.4985 | 36.7782 | 37.5982 | 34.524 | 34.4894 | 35.1896 | 35.7754 | 36.3833 | 36.7293 | 37.2627 | 37.3906 | 34.8921 | 31.7172 | 92.033 | 35.6208 | 34.0726 | 35.6046 | 34.3394 | 33.9934 | 34.1954 | 35.5152 | 34.8413 | 34.7012 | 37.4921 | 36.4593 | 34.2057 | 34.7525 | 36.4335 | 36.9136 | 37.7511 | 36.4572 | 34.3436 | 33.7842 | 35.4468 | 35.7738 | 33.9894 | 34.4354 | 34.376 | 33.8855 | 34.4713 | 34.5566 | 34.4299 | 34.1541 | 34.4501 | 35.3678 | 35.8312 | 35.5665 | 35.6547 | 34.3503 | 91.6267 | 91.7764 | 92.0934
2022-09-08 00:42 | 2:52 | 34.9167 | 31.5157 | 32.0834 | 35.9601 | 34.3854 | 34.6607 | 35.5812 | 35.8532 | 36.8634 | 37.4973 | 36.764 | 37.597 | 34.5166 | 34.4669 | 35.184 | 35.7587 | 36.3817 | 36.7208 | 37.2764 | 37.3841 | 35.0312 | 31.6828 | 92.1911 | 35.6005 | 34.0662 | 35.6074 | 34.3327 | 33.9857 | 34.2024 | 35.5199 | 34.8094 | 34.6985 | 37.5121 | 36.4399 | 34.1902 | 34.7628 | 36.431 | 36.9058 | 37.7515 | 36.4485 | 34.3439 | 33.7739 | 35.4666 | 35.7643 | 33.9977 | 34.465 | 34.3753 | 33.8809 | 34.4616 | 34.5833 | 34.443 | 34.1562 | 34.4713 | 35.3827 | 35.8341 | 35.5763 | 35.6662 | 34.3614 | 91.5063 | 91.6554 | 92.0269
2022-09-08 00:42 | 2:52 | 35.0164 | 31.5405 | 32.1479 | 35.9757 | 34.3719 | 34.653 | 35.5753 | 35.8448 | 36.8603 | 37.4983 | 36.7498 | 37.5979 | 34.5186 | 34.4876 | 35.1875 | 35.7874 | 36.3856 | 36.7166 | 37.2741 | 37.3865 | 35.1299 | 31.6977 | 92.2012 | 35.6661 | 34.0631 | 35.6001 | 34.3404 | 33.9862 | 34.2013 | 35.5325 | 34.8087 | 34.6853 | 37.493 | 36.4664 | 34.1913 | 34.7553 | 36.4593 | 36.9325 | 37.7453 | 36.4501 | 34.3484 | 33.782 | 35.4768 | 35.776 | 33.9898 | 34.4532 | 34.3558 | 33.8877 | 34.4672 | 34.5597 | 34.4311 | 34.1775 | 34.4616 | 35.3833 | 35.8391 | 35.5922 | 35.649 | 34.3346 | 91.4494 | 91.5709 | 92.0087
2022-09-08 00:43 | 2:53 | 35.1593 | 31.5583 | 32.1957 | 36.0381 | 34.3863 | 34.6621 | 35.599 | 35.8469 | 36.8765 | 37.5165 | 36.7579 | 37.5996 | 34.5311 | 34.4797 | 35.1915 | 35.7445 | 36.3722 | 36.7253 | 37.2837 | 37.3965 | 35.2127 | 31.7085 | 92.2696 | 35.7061 | 34.0716 | 35.6091 | 34.3365 | 34.0099 | 34.1905 | 35.5122 | 34.815 | 34.707 | 37.4996 | 36.4319 | 34.2041 | 34.7501 | 36.4399 | 36.9225 | 37.7599 | 36.4335 | 34.3339 | 33.7869 | 35.4659 | 35.7715 | 33.9975 | 34.4507 | 34.3558 | 33.9024 | 34.4415 | 34.5408 | 34.4389 | 34.1717 | 34.4672 | 35.4066 | 35.8355 | 35.5858 | 35.6669 | 34.3674 | 91.4785 | 91.603 | 92.0373
2022-09-08 00:43 | 2:53 | 35.1148 | 31.5905 | 32.2381 | 35.9756 | 34.3726 | 34.6637 | 35.5881 | 35.8383 | 36.8706 | 37.5038 | 36.7603 | 37.6185 | 34.529 | 34.4893 | 35.1968 | 35.7761 | 36.3911 | 36.7273 | 37.2714 | 37.3885 | 35.0102 | 31.6424 | 92.3548 | 35.746 | 34.0735 | 35.5949 | 34.3436 | 33.9974 | 34.2057 | 35.523 | 34.8192 | 34.705 | 37.5029 | 36.4597 | 34.2092 | 34.7545 | 36.4664 | 36.9106 | 37.7492 | 36.431 | 34.3315 | 33.7661 | 35.4749 | 35.7771 | 34.0103 | 34.458 | 34.3663 | 33.8942 | 34.4315 | 34.5539 | 34.4469 | 34.1487 | 34.4415 | 35.4013 | 35.8045 | 35.5856 | 35.6509 | 34.3663 | 91.6185 | 91.689 | 92.1513
2022-09-08 00:43 | 2:53 | 31.0639 | 30.8572 | 32.0055 | 36.0601 | 34.3944 | 34.6661 | 35.5899 | 35.834 | 36.8832 | 37.517 | 36.755 | 37.6104 | 34.515 | 34.4851 | 35.2028 | 35.7611 | 36.3728 | 36.7359 | 37.2875 | 37.4056 | 30.8637 | 31.6127 | 92.3549 | 35.7246 | 34.0735 | 35.6189 | 34.3439 | 33.9812 | 34.1902 | 35.5246 | 34.8065 | 34.7058 | 37.495 | 36.4573 | 34.1982 | 34.7453 | 36.4319 | 36.9321 | 37.7673 | 36.4593 | 34.3387 | 33.7744 | 35.4634 | 35.7761 | 34.011 | 34.4474 | 34.3631 | 33.9027 | 34.4031 | 34.5292 | 34.4404 | 34.1932 | 34.4315 | 35.3712 | 35.8325 | 35.5942 | 35.6586 | 34.3586 | 91.6639 | 91.8524 | 92.1815
2022-09-08 00:43 | 2:53 | 31.4249 | 27.455 | 31.6839 | 36.0737 | 34.385 | 34.648 | 35.5789 | 35.8404 | 36.8716 | 37.4988 | 36.7636 | 37.5936 | 34.5234 | 34.4894 | 35.189 | 35.7786 | 36.3601 | 36.7234 | 37.2787 | 37.3971 | 29.5604 | 28.9205 | 92.4251 | 35.608 | 34.0714 | 35.592 | 34.3484 | 33.9912 | 34.1913 | 35.5348 | 34.7972 | 34.7015 | 37.4923 | 36.4398 | 34.1829 | 34.7297 | 36.4597 | 36.9144 | 37.7398 | 36.4399 | 34.3438 | 33.778 | 35.4798 | 35.7771 | 34.0423 | 34.4783 | 34.3711 | 33.9026 | 34.4401 | 34.5408 | 34.4671 | 34.1822 | 34.4031 | 35.3962 | 35.8294 | 35.5796 | 35.6621 | 34.3496 | 91.7644 | 91.9546 | 92.2825
2022-09-08 00:43 | 2:53 | 31.6938 | 25.9085 | 31.8391 | 36.137 | 34.3849 | 34.6441 | 35.5703 | 35.8346 | 36.8775 | 37.5055 | 36.7624 | 37.6027 | 34.5235 | 34.4819 | 35.2024 | 35.7573 | 36.335 | 36.727 | 37.2801 | 37.3957 | 29.2452 | 27.2622 | 92.4679 | 35.4224 | 34.076 | 35.6055 | 34.3339 | 33.9942 | 34.2041 | 35.5142 | 34.789 | 34.694 | 37.5038 | 36.4458 | 34.207 | 34.7404 | 36.4573 | 36.9252 | 37.7605 | 36.4664 | 34.3401 | 33.7887 | 35.4624 | 35.8014 | 34.0092 | 34.469 | 34.3757 | 33.9145 | 34.4203 | 34.5173 | 34.4465 | 34.184 | 34.4401 | 35.3853 | 35.8352 | 35.5776 | 35.6817 | 34.3592 | 91.8907 | 92.0616 | 92.3464
2022-09-08 00:43 | 2:53 | 31.7685 | 26.4627 | 31.8761 | 36.2337 | 34.4131 | 34.6554 | 35.561 | 35.8405 | 36.8783 | 37.5091 | 36.7514 | 37.6233 | 34.5212 | 34.5033 | 35.1917 | 35.7701 | 36.358 | 36.7382 | 37.2684 | 37.4011 | 29.4717 | 25.5618 | 92.4148 | 35.3389 | 34.0774 | 35.593 | 34.3315 | 33.9917 | 34.2092 | 35.5351 | 34.8007 | 34.685 | 37.5069 | 36.4548 | 34.2074 | 34.7448 | 36.4398 | 36.9227 | 37.7736 | 36.4319 | 34.345 | 33.7799 | 35.4826 | 35.7844 | 34.0125 | 34.4585 | 34.361 | 33.9111 | 34.4203 | 34.5357 | 34.465 | 34.1877 | 34.4203 | 35.4139 | 35.8239 | 35.5863 | 35.6844 | 34.3644 | 92.0813 | 92.2869 | 92.4731
2022-09-08 00:44 | 2:53 | 31.7619 | 27.0334 | 31.9502 | 36.2859 | 34.394 | 34.6418 | 35.601 | 35.8199 | 36.8812 | 37.5001 | 36.7327 | 37.6314 | 34.5264 | 34.5032 | 35.1857 | 35.761 | 36.3492 | 36.7261 | 37.2734 | 37.3985 | 29.4911 | 24.822 | 92.5409 | 35.3443 | 34.078 | 35.6033 | 34.3387 | 33.9693 | 34.1982 | 35.5292 | 34.7872 | 34.6739 | 37.5224 | 36.4611 | 34.1958 | 34.7369 | 36.4458 | 36.9188 | 37.7786 | 36.4597 | 34.3417 | 33.7972 | 35.4721 | 35.8025 | 34.0326 | 34.4428 | 34.3565 | 33.9171 | 34.4028 | 34.5425 | 34.471 | 34.1799 | 34.4203 | 35.3906 | 35.8273 | 35.593 | 35.6771 | 34.3662 | 92.2645 | 92.4336 | 92.586
2022-09-08 00:44 | 2:54 | 31.8194 | 27.6435 | 31.9937 | 36.3213 | 34.3927 | 34.6495 | 35.5833 | 35.857 | 36.8635 | 37.5167 | 36.7432 | 37.6006 | 34.532 | 34.5095 | 35.1852 | 35.7702 | 36.3582 | 36.7321 | 37.2744 | 37.4014 | 29.2089 | 24.2987 | 92.7376 | 35.2165 | 34.0916 | 35.5957 | 34.3438 | 34.0014 | 34.1829 | 35.5394 | 34.8097 | 34.6779 | 37.4985 | 36.4461 | 34.2084 | 34.7535 | 36.4548 | 36.9275 | 37.7679 | 36.4573 | 34.3393 | 33.7916 | 35.4679 | 35.8144 | 34.0279 | 34.4408 | 34.3704 | 33.9269 | 34.41 | 34.5249 | 34.4436 | 34.1864 | 34.4028 | 35.412 | 35.8241 | 35.5667 | 35.6697 | 34.3429 | 92.3671 | 92.6051 | 92.6605
2022-09-08 00:44 | 2:54 | 31.8596 | 28.467 | 32.0172 | 36.3086 | 34.4089 | 34.6519 | 35.5816 | 35.8266 | 36.8671 | 37.524 | 36.7393 | 37.6273 | 34.5422 | 34.4768 | 35.2055 | 35.7688 | 36.3417 | 36.728 | 37.2691 | 37.4005 | 28.7626 | 23.8194 | 92.8957 | 35.2352 | 34.0763 | 35.5945 | 34.3401 | 33.9758 | 34.207 | 35.5176 | 34.8061 | 34.6899 | 37.4919 | 36.4483 | 34.1983 | 34.7418 | 36.4611 | 36.9284 | 37.788 | 36.4398 | 34.3141 | 33.7974 | 35.5083 | 35.8108 | 34.0125 | 34.4549 | 34.3687 | 33.9285 | 34.4062 | 34.5307 | 34.4717 | 34.1837 | 34.41 | 35.3891 | 35.8249 | 35.5795 | 35.681 | 34.3689 | 92.5341 | 92.7974 | 92.757
2022-09-08 00:44 | 2:54 | 31.9108 | 29.4482 | 32.047 | 36.2352 | 34.4066 | 34.6435 | 35.5827 | 35.8349 | 36.8834 | 37.5391 | 36.7465 | 37.6041 | 34.5447 | 34.5128 | 35.1981 | 35.7466 | 36.3541 | 36.742 | 37.2829 | 37.3938 | 28.3103 | 23.4981 | 92.9202 | 35.113 | 34.0801 | 35.6065 | 34.345 | 34.0012 | 34.2074 | 35.5349 | 34.7995 | 34.6713 | 37.5047 | 36.4551 | 34.1994 | 34.7564 | 36.4461 | 36.9067 | 37.7562 | 36.4458 | 34.3243 | 33.7937 | 35.4905 | 35.7928 | 34.0414 | 34.4617 | 34.3704 | 33.9129 | 34.4086 | 34.5005 | 34.4547 | 34.1775 | 34.4062 | 35.403 | 35.8458 | 35.6001 | 35.6644 | 34.3539 | 92.6717 | 92.9849 | 92.8497
2022-09-08 00:44 | 2:54 | 31.9791 | 30.0974 | 32.0703 | 36.2964 | 34.4207 | 34.6482 | 35.5909 | 35.8456 | 36.8701 | 37.5215 | 36.7416 | 37.6131 | 34.5512 | 34.4866 | 35.1968 | 35.7801 | 36.355 | 36.7398 | 37.2828 | 37.4178 | 27.8809 | 23.2499 | 92.8665 | 35.0885 | 34.0788 | 35.5978 | 34.3417 | 33.9778 | 34.1958 | 35.5448 | 34.8212 | 34.6826 | 37.4974 | 36.4528 | 34.1827 | 34.7314 | 36.4483 | 36.9198 | 37.7709 | 36.4548 | 34.3347 | 33.8 | 35.4715 | 35.7836 | 34.0325 | 34.4611 | 34.3681 | 33.927 | 34.3894 | 34.5194 | 34.459 | 34.1906 | 34.4086 | 35.4106 | 35.825 | 35.5707 | 35.6821 | 34.3451 | 92.8701 | 93.0752 | 92.9672
2022-09-08 00:44 | 2:54 | 32.0685 | 30.5214 | 32.1007 | 36.427 | 34.409 | 34.6398 | 35.5953 | 35.8464 | 36.8745 | 37.5265 | 36.7558 | 37.615 | 34.5315 | 34.4986 | 35.1909 | 35.7787 | 36.3613 | 36.7232 | 37.2743 | 37.4061 | 27.5661 | 23.0174 | 93.2301 | 35.1148 | 34.075 | 35.6146 | 34.3393 | 33.994 | 34.2084 | 35.5434 | 34.8023 | 34.6807 | 37.4936 | 36.4776 | 34.2005 | 34.733 | 36.4551 | 36.9286 | 37.7604 | 36.4611 | 34.3371 | 33.7969 | 35.4552 | 35.7836 | 34.0075 | 34.4674 | 34.3673 | 33.9215 | 34.3925 | 34.5104 | 34.4436 | 34.1981 | 34.3894 | 35.4119 | 35.797 | 35.6076 | 35.6853 | 34.3491 | 93.0881 | 93.236 | 93.0764
2022-09-08 00:45 | 2:55 | 32.1389 | 30.815 | 32.1325 | 36.3924 | 34.411 | 34.6509 | 35.6016 | 35.8608 | 36.8749 | 37.5316 | 36.7584 | 37.6095 | 34.5338 | 34.5178 | 35.2008 | 35.773 | 36.3496 | 36.7247 | 37.2704 | 37.4083 | 27.3342 | 22.7994 | 92.9823 | 34.9402 | 34.0528 | 35.6051 | 34.3141 | 33.9713 | 34.1983 | 35.5338 | 34.7926 | 34.6732 | 37.5149 | 36.482 | 34.1868 | 34.7328 | 36.4528 | 36.9309 | 37.7643 | 36.4461 | 34.3254 | 33.7912 | 35.4785 | 35.8057 | 34.006 | 34.4669 | 34.3464 | 33.9464 | 34.3826 | 34.4991 | 34.4778 | 34.1947 | 34.3925 | 35.4068 | 35.8081 | 35.5892 | 35.6757 | 34.3449 | 93.2389 | 93.3271 | 93.0889
2022-09-08 00:45 | 2:55 | 32.1793 | 30.9974 | 32.1555 | 36.4312 | 34.4179 | 34.6417 | 35.5889 | 35.8517 | 36.8935 | 37.5096 | 36.7351 | 37.6123 | 34.5333 | 34.5075 | 35.1906 | 35.7732 | 36.342 | 36.7115 | 37.2807 | 37.3878 | 26.9542 | 22.647 | 93.1628 | 34.9594 | 34.0613 | 35.5787 | 34.3243 | 33.9913 | 34.1994 | 35.5235 | 34.8023 | 34.6587 | 37.5026 | 36.4558 | 34.193 | 34.7584 | 36.4776 | 36.9011 | 37.7929 | 36.4483 | 34.3348 | 33.8052 | 35.4736 | 35.8 | 33.9989 | 34.4645 | 34.3669 | 33.9571 | 34.3957 | 34.4986 | 34.48 | 34.2031 | 34.3826 | 35.4114 | 35.8124 | 35.5836 | 35.673 | 34.3275 | 93.3433 | 93.4741 | 93.1513
2022-09-08 00:45 | 2:55 | 32.2497 | 31.129 | 32.174 | 36.457 | 34.3964 | 34.6267 | 35.591 | 35.8332 | 36.8727 | 37.5169 | 36.7442 | 37.594 | 34.538 | 34.5197 | 35.1882 | 35.7537 | 36.3519 | 36.7162 | 37.2723 | 37.3799 | 26.5547 | 22.4549 | 93.5568 | 34.9163 | 34.0604 | 35.5819 | 34.3347 | 33.9899 | 34.1827 | 35.5167 | 34.8086 | 34.6789 | 37.501 | 36.4748 | 34.1867 | 34.7424 | 36.482 | 36.9125 | 37.7794 | 36.4551 | 34.3417 | 33.8064 | 35.4701 | 35.8111 | 33.9968 | 34.4557 | 34.3738 | 33.9487 | 34.4073 | 34.5005 | 34.4678 | 34.1741 | 34.3957 | 35.392 | 35.8234 | 35.6039 | 35.6756 | 34.3329 | 93.6 | 93.6313 | 93.3456
2022-09-08 00:45 | 2:55 | 32.2798 | 31.2217 | 32.1964 | 36.5323 | 34.4229 | 34.6301 | 35.61 | 35.8554 | 36.8712 | 37.5174 | 36.7371 | 37.5965 | 34.5456 | 34.5078 | 35.1866 | 35.7642 | 36.3208 | 36.7271 | 37.2676 | 37.3906 | 26.123 | 22.2365 | 93.713 | 34.8902 | 34.0691 | 35.5844 | 34.3371 | 33.9989 | 34.2005 | 35.5418 | 34.7912 | 34.6723 | 37.5156 | 36.4683 | 34.1986 | 34.7451 | 36.4558 | 36.9218 | 37.7761 | 36.4528 | 34.3312 | 33.7964 | 35.4809 | 35.7976 | 34.017 | 34.453 | 34.3554 | 33.9453 | 34.3946 | 34.4877 | 34.486 | 34.2106 | 34.4073 | 35.3957 | 35.7916 | 35.6007 | 35.654 | 34.3469 | 93.8263 | 93.8318 | 93.4349
2022-09-08 00:45 | 2:55 | 32.3228 | 31.3035 | 32.2134 | 36.5053 | 34.4296 | 34.6402 | 35.6055 | 35.8329 | 36.8664 | 37.5268 | 36.7308 | 37.6111 | 34.5389 | 34.5153 | 35.1862 | 35.7722 | 36.3336 | 36.707 | 37.2742 | 37.3922 | 25.6588 | 22.0096 | 93.6191 | 34.8204 | 34.0795 | 35.5892 | 34.3254 | 33.9833 | 34.1868 | 35.5249 | 34.8142 | 34.6672 | 37.5079 | 36.4579 | 34.2018 | 34.7122 | 36.4748 | 36.9181 | 37.7766 | 36.4776 | 34.3271 | 33.794 | 35.4507 | 35.7884 | 33.9918 | 34.4808 | 34.3501 | 33.9214 | 34.3862 | 34.4942 | 34.4632 | 34.2085 | 34.3946 | 35.4075 | 35.8189 | 35.6009 | 35.6662 | 34.3373 | 93.9207 | 94.0124 | 93.5392
2022-09-08 00:45 | 2:55 | 32.3754 | 31.3572 | 32.2437 | 36.5274 | 34.4419 | 34.6232 | 35.5994 | 35.8449 | 36.8716 | 37.5264 | 36.7435 | 37.6081 | 34.558 | 34.5134 | 35.1846 | 35.7696 | 36.3267 | 36.7177 | 37.2616 | 37.3722 | 25.2386 | 21.8051 | 93.8016 | 34.7736 | 34.0449 | 35.6001 | 34.3348 | 33.9649 | 34.193 | 35.5248 | 34.7972 | 34.6703 | 37.5211 | 36.4582 | 34.1819 | 34.7285 | 36.4683 | 36.9125 | 37.7761 | 36.482 | 34.3392 | 33.7918 | 35.4435 | 35.7999 | 33.9822 | 34.4654 | 34.3571 | 33.9326 | 34.3777 | 34.4987 | 34.4693 | 34.1955 | 34.3862 | 35.4031 | 35.8159 | 35.6097 | 35.6498 | 34.312 | 94.0974 | 94.1358 | 93.5544
2022-09-08 00:46 | 2:56 | 32.3973 | 31.4089 | 32.2679 | 36.5639 | 34.44 | 34.6382 | 35.6247 | 35.8423 | 36.8575 | 37.5195 | 36.7473 | 37.6099 | 34.5571 | 34.5185 | 35.2017 | 35.7771 | 36.3217 | 36.7359 | 37.2766 | 37.4018 | 24.767 | 21.536 | 93.7486 | 34.8788 | 34.0643 | 35.6008 | 34.3417 | 33.9731 | 34.1867 | 35.5365 | 34.7906 | 34.6723 | 37.4957 | 36.4807 | 34.1751 | 34.7443 | 36.4579 | 36.9142 | 37.7772 | 36.4558 | 34.3249 | 33.7984 | 35.4557 | 35.783 | 33.9861 | 34.4572 | 34.3721 | 33.9483 | 34.3956 | 34.4771 | 34.499 | 34.1991 | 34.3777 | 35.3967 | 35.8057 | 35.6145 | 35.6728 | 34.3294 | 94.2322 | 94.3393 | 93.7389
2022-09-08 00:46 | 2:56 | 32.1091 | 28.4742 | 31.9338 | 36.7097 | 34.4337 | 34.6507 | 35.6091 | 35.8306 | 36.8776 | 37.5015 | 36.7456 | 37.6176 | 34.5525 | 34.5114 | 35.18 | 35.7711 | 36.3509 | 36.72 | 37.259 | 37.382 | 25.1084 | 23.0057 | 93.6848 | 34.6502 | 34.0644 | 35.585 | 34.3312 | 33.9728 | 34.1986 | 35.5067 | 34.7844 | 34.6547 | 37.4824 | 36.4847 | 34.1753 | 34.7267 | 36.4582 | 36.8936 | 37.7986 | 36.4748 | 34.3239 | 33.7871 | 35.4354 | 35.7831 | 33.9784 | 34.4861 | 34.3577 | 33.9681 | 34.3873 | 34.4866 | 34.49 | 34.1892 | 34.3956 | 35.3955 | 35.8108 | 35.5924 | 35.6731 | 34.3115 | 94.3066 | 94.4662 | 93.8046
2022-09-08 00:46 | 2:56 | 31.6559 | 26.0113 | 30.6827 | 36.5117 | 34.4416 | 34.6359 | 35.6377 | 35.8355 | 36.8604 | 37.5222 | 36.735 | 37.6031 | 34.5464 | 34.5304 | 35.1837 | 35.7884 | 36.3353 | 36.7071 | 37.2702 | 37.3708 | 25.2703 | 23.1685 | 93.6916 | 34.6966 | 34.0438 | 35.5939 | 34.3271 | 33.9613 | 34.2018 | 35.5215 | 34.786 | 34.6729 | 37.5106 | 36.4685 | 34.1887 | 34.7266 | 36.4807 | 36.8998 | 37.7622 | 36.4683 | 34.3203 | 33.7818 | 35.456 | 35.7687 | 33.9798 | 34.4672 | 34.3799 | 33.9508 | 34.3965 | 34.4769 | 34.4802 | 34.2086 | 34.3873 | 35.3938 | 35.8094 | 35.6035 | 35.6793 | 34.2874 | 94.5352 | 94.5404 | 93.9289
2022-09-08 00:46 | 2:56 | 31.2027 | 25.8551 | 30.0562 | 36.4654 | 34.456 | 34.6181 | 35.6352 | 35.8412 | 36.8433 | 37.5137 | 36.7444 | 37.5954 | 34.5564 | 34.5156 | 35.1835 | 35.7708 | 36.3184 | 36.6955 | 37.25 | 37.3868 | 25.5777 | 23.1982 | 93.6952 | 34.7687 | 34.0576 | 35.5847 | 34.3392 | 33.9634 | 34.1819 | 35.5214 | 34.7795 | 34.6568 | 37.5008 | 36.4577 | 34.1808 | 34.7245 | 36.4847 | 36.878 | 37.7787 | 36.4579 | 34.3365 | 33.7824 | 35.4189 | 35.7884 | 33.9714 | 34.4714 | 34.3784 | 33.9469 | 34.3668 | 34.4737 | 34.4823 | 34.1771 | 34.3965 | 35.4111 | 35.8155 | 35.5911 | 35.6706 | 34.3156 | 94.6102 | 94.702 | 93.922
2022-09-08 00:46 | 2:56 | 30.9392 | 25.9743 | 29.831 | 36.3692 | 34.4223 | 34.6296 | 35.6265 | 35.8432 | 36.8689 | 37.4917 | 36.7488 | 37.5914 | 34.5572 | 34.5354 | 35.1724 | 35.7624 | 36.3328 | 36.6929 | 37.2495 | 37.37 | 25.8291 | 23.1873 | 93.5625 | 34.6541 | 34.0444 | 35.5968 | 34.3249 | 33.9731 | 34.1751 | 35.5192 | 34.7856 | 34.6681 | 37.4942 | 36.4808 | 34.1656 | 34.7242 | 36.4685 | 36.9067 | 37.78 | 36.4582 | 34.3392 | 33.7775 | 35.4167 | 35.7673 | 33.947 | 34.4702 | 34.3816 | 33.9443 | 34.3864 | 34.4859 | 34.4894 | 34.2054 | 34.3668 | 35.3952 | 35.8103 | 35.6025 | 35.6779 | 34.3045 | 94.7595 | 94.7998 | 94.0256
2022-09-08 00:46 | 2:56 | 30.6617 | 26.0091 | 29.5765 | 36.4374 | 34.4529 | 34.6369 | 35.6288 | 35.8424 | 36.8703 | 37.503 | 36.7238 | 37.6023 | 34.5596 | 34.528 | 35.1696 | 35.7692 | 36.3293 | 36.7111 | 37.246 | 37.3638 | 25.9894 | 23.241 | 93.4999 | 34.6655 | 34.0516 | 35.5858 | 34.3239 | 33.956 | 34.1753 | 35.5146 | 34.8052 | 34.6491 | 37.4913 | 36.4879 | 34.1862 | 34.7422 | 36.4577 | 36.9168 | 37.7653 | 36.4807 | 34.3172 | 33.766 | 35.4168 | 35.7473 | 33.9599 | 34.468 | 34.3632 | 33.9181 | 34.3865 | 34.4734 | 34.4669 | 34.2031 | 34.3864 | 35.4019 | 35.8094 | 35.5962 | 35.6714 | 34.2955 | 94.878 | 94.8896 | 94.1337
2022-09-08 00:47 | 2:56 | 30.1262 | 26.0308 | 29.3219 | 36.4159 | 34.4382 | 34.6244 | 35.6241 | 35.8491 | 36.8497 | 37.4673 | 36.7323 | 37.5993 | 34.5483 | 34.5302 | 35.1858 | 35.7888 | 36.3199 | 36.6977 | 37.2289 | 37.381 | 26.0644 | 23.175 | 93.2085 | 34.7037 | 34.0465 | 35.6028 | 34.3203 | 33.9602 | 34.1887 | 35.526 | 34.7893 | 34.6659 | 37.4853 | 36.5022 | 34.194 | 34.7278 | 36.4808 | 36.9102 | 37.7659 | 36.4847 | 34.3296 | 33.7739 | 35.4252 | 35.7505 | 33.957 | 34.4695 | 34.3705 | 33.9396 | 34.3892 | 34.4576 | 34.4876 | 34.1912 | 34.3865 | 35.3912 | 35.7949 | 35.5958 | 35.6573 | 34.3004 | 94.9036 | 94.9499 | 94.1569
2022-09-08 00:47 | 2:57 | 29.6196 | 26.0504 | 29.1814 | 36.2953 | 34.4355 | 34.6166 | 35.6453 | 35.855 | 36.858 | 37.495 | 36.7271 | 37.5872 | 34.5636 | 34.5091 | 35.1771 | 35.7767 | 36.3174 | 36.6994 | 37.2488 | 37.3665 | 26.0982 | 23.1488 | 93.0883 | 34.7178 | 34.0442 | 35.6148 | 34.3365 | 33.9799 | 34.1808 | 35.4975 | 34.7796 | 34.6669 | 37.4908 | 36.4909 | 34.178 | 34.7277 | 36.4879 | 36.9053 | 37.7844 | 36.4685 | 34.319 | 33.7626 | 35.428 | 35.744 | 33.9469 | 34.4764 | 34.3728 | 33.933 | 34.3744 | 34.4557 | 34.4797 | 34.1828 | 34.3892 | 35.3784 | 35.7839 | 35.5981 | 35.6617 | 34.301 | 94.9715 | 95.0417 | 94.1366
2022-09-08 00:47 | 2:57 | 29.2598 | 26.0919 | 29.0129 | 36.2526 | 34.4299 | 34.6081 | 35.6406 | 35.8341 | 36.8733 | 37.4923 | 36.7417 | 37.5993 | 34.568 | 34.5243 | 35.1529 | 35.7668 | 36.3107 | 36.6943 | 37.2403 | 37.3437 | 26.0919 | 23.1547 | 93.0536 | 34.6107 | 34.0184 | 35.5983 | 34.3392 | 33.9613 | 34.1656 | 35.5006 | 34.7943 | 34.6503 | 37.4872 | 36.4748 | 34.1993 | 34.7367 | 36.5022 | 36.9002 | 37.7584 | 36.4577 | 34.3513 | 33.7615 | 35.4093 | 35.7594 | 33.9448 | 34.4903 | 34.3638 | 33.9201 | 34.3846 | 34.4537 | 34.4893 | 34.1867 | 34.3744 | 35.3787 | 35.8211 | 35.5955 | 35.6722 | 34.2943 | 94.9315 | 95.0562 | 94.1967
2022-09-08 00:47 | 2:57 | 28.8928 | 26.0296 | 28.7428 | 36.3212 | 34.443 | 34.6117 | 35.6524 | 35.8453 | 36.8542 | 37.5126 | 36.7452 | 37.6177 | 34.5542 | 34.5286 | 35.1708 | 35.7654 | 36.3059 | 36.6964 | 37.2489 | 37.3414 | 26.0419 | 23.0517 | 92.8885 | 34.6609 | 34.0153 | 35.5856 | 34.3172 | 33.9571 | 34.1862 | 35.5016 | 34.7813 | 34.6464 | 37.5049 | 36.5146 | 34.1836 | 34.7329 | 36.4909 | 36.8908 | 37.7603 | 36.4808 | 34.3418 | 33.7839 | 35.3989 | 35.7673 | 33.9602 | 34.4759 | 34.3801 | 33.9393 | 34.3785 | 34.428 | 34.4851 | 34.195 | 34.3846 | 35.404 | 35.8135 | 35.598 | 35.6776 | 34.2674 | 94.7681 | 94.9518 | 94.0601
2022-09-08 00:47 | 2:57 | 28.403 | 25.9288 | 28.3875 | 36.3483 | 34.4311 | 34.6267 | 35.632 | 35.8393 | 36.8566 | 37.4916 | 36.7387 | 37.6149 | 34.5784 | 34.52 | 35.1776 | 35.7806 | 36.3066 | 36.6889 | 37.2283 | 37.363 | 26.0029 | 23.0459 | 93.0684 | 34.6187 | 34.0533 | 35.6131 | 34.3296 | 33.962 | 34.194 | 35.5005 | 34.8 | 34.6887 | 37.4722 | 36.4957 | 34.1814 | 34.7204 | 36.4748 | 36.8976 | 37.773 | 36.4879 | 34.334 | 33.7756 | 35.3869 | 35.7236 | 33.9461 | 34.466 | 34.3706 | 33.921 | 34.3644 | 34.4265 | 34.4894 | 34.2075 | 34.3785 | 35.3893 | 35.8073 | 35.6178 | 35.6821 | 34.2871 | 94.5714 | 94.7816 | 93.9542
2022-09-08 00:47 | 2:57 | 27.4628 | 25.8551 | 27.8809 | 36.3387 | 34.4389 | 34.6105 | 35.6606 | 35.843 | 36.8615 | 37.4913 | 36.7516 | 37.6242 | 34.5839 | 34.5276 | 35.166 | 35.7784 | 36.3195 | 36.6893 | 37.2362 | 37.3535 | 25.8932 | 22.8808 | 92.9969 | 34.553 | 34.0309 | 35.5988 | 34.319 | 33.9704 | 34.178 | 35.499 | 34.8018 | 34.6656 | 37.4912 | 36.4962 | 34.1748 | 34.7344 | 36.5146 | 36.8993 | 37.7593 | 36.5022 | 34.3303 | 33.7494 | 35.3762 | 35.7341 | 33.9547 | 34.4876 | 34.366 | 33.9336 | 34.3547 | 34.4303 | 34.4819 | 34.1763 | 34.3644 | 35.3835 | 35.808 | 35.5965 | 35.6726 | 34.275 | 94.2939 | 94.4875 | 93.7289
2022-09-08 00:48 | 2:58 | 24.6171 | 25.7066 | 27.2303 | 36.3439 | 34.4469 | 34.6199 | 35.6577 | 35.8368 | 36.8605 | 37.4975 | 36.7295 | 37.6014 | 34.5676 | 34.5259 | 35.1576 | 35.776 | 36.3315 | 36.6989 | 37.2429 | 37.3396 | 25.7548 | 22.7451 | 92.9677 | 34.5387 | 34.0264 | 35.6039 | 34.3513 | 33.963 | 34.1993 | 35.5184 | 34.7913 | 34.677 | 37.5069 | 36.5133 | 34.185 | 34.7374 | 36.4957 | 36.8944 | 37.7603 | 36.4909 | 34.3335 | 33.766 | 35.4009 | 35.7429 | 33.9376 | 34.484 | 34.3873 | 33.8878 | 34.3855 | 34.433 | 34.5033 | 34.1895 | 34.3547 | 35.3875 | 35.8161 | 35.6048 | 35.6601 | 34.2753 | 94.0709 | 94.2643 | 93.5783
2022-09-08 00:48 | 2:58 | 23.978 | 25.4374 | 26.809 | 36.2538 | 34.4404 | 34.6199 | 35.6501 | 35.8383 | 36.8746 | 37.4911 | 36.7559 | 37.6073 | 34.5672 | 34.5264 | 35.1625 | 35.7856 | 36.3389 | 36.6954 | 37.2429 | 37.3433 | 25.5857 | 22.6349 | 93.028 | 34.6391 | 34.0564 | 35.6199 | 34.3418 | 33.9662 | 34.1836 | 35.4803 | 34.7974 | 34.6651 | 37.4909 | 36.5025 | 34.1739 | 34.7092 | 36.4962 | 36.8847 | 37.7661 | 36.4748 | 34.3402 | 33.7638 | 35.3843 | 35.7497 | 33.9571 | 34.4972 | 34.3551 | 33.9171 | 34.3825 | 34.4242 | 34.5032 | 34.1972 | 34.3855 | 35.3823 | 35.822 | 35.6153 | 35.6721 | 34.2849 | 93.9115 | 94.0781 | 93.5034
2022-09-08 00:48 | 2:58 | 23.7621 | 25.2234 | 26.5596 | 36.1769 | 34.4671 | 34.6206 | 35.6426 | 35.8237 | 36.8488 | 37.4792 | 36.7481 | 37.6105 | 34.5646 | 34.5164 | 35.1582 | 35.7872 | 36.3259 | 36.6873 | 37.2261 | 37.3441 | 25.3381 | 22.5416 | 93.0016 | 34.561 | 34.0289 | 35.6158 | 34.334 | 33.9464 | 34.1814 | 35.49 | 34.7927 | 34.663 | 37.4914 | 36.5089 | 34.1799 | 34.7344 | 36.5133 | 36.8941 | 37.7626 | 36.5146 | 34.341 | 33.7716 | 35.4029 | 35.7284 | 33.9465 | 34.4734 | 34.3778 | 33.9089 | 34.3695 | 34.4164 | 34.5095 | 34.213 | 34.3825 | 35.3975 | 35.8197 | 35.6309 | 35.6627 | 34.2847 | 93.7955 | 93.9476 | 93.4647
2022-09-08 00:48 | 2:58 | 23.4905 | 24.9811 | 26.3336 | 36.2009 | 34.4465 | 34.6212 | 35.6367 | 35.8187 | 36.8736 | 37.4789 | 36.7524 | 37.6044 | 34.5722 | 34.5196 | 35.1522 | 35.7846 | 36.331 | 36.6728 | 37.219 | 37.3373 | 25.1151 | 22.319 | 92.9735 | 34.385 | 34.0116 | 35.6161 | 34.3303 | 33.9643 | 34.1748 | 35.4836 | 34.7978 | 34.679 | 37.4786 | 36.5074 | 34.1786 | 34.7195 | 36.5025 | 36.9029 | 37.7787 | 36.4957 | 34.3312 | 33.7482 | 35.3918 | 35.7286 | 33.9456 | 34.4966 | 34.3713 | 33.9188 | 34.3678 | 34.407 | 34.4768 | 34.1809 | 34.3695 | 35.4071 | 35.8094 | 35.6122 | 35.6829 | 34.2788 | 93.7287 | 93.8646 | 93.5033
2022-09-08 00:48 | 2:58 | 23.2785 | 24.6875 | 26.0866 | 36.1704 | 34.465 | 34.6232 | 35.6303 | 35.8447 | 36.8587 | 37.4832 | 36.7647 | 37.6157 | 34.5739 | 34.5234 | 35.1398 | 35.7911 | 36.3207 | 36.6919 | 37.215 | 37.339 | 24.8911 | 22.2159 | 92.8369 | 34.4635 | 34.0306 | 35.6078 | 34.3335 | 33.9493 | 34.185 | 35.4867 | 34.8167 | 34.6765 | 37.4909 | 36.5142 | 34.191 | 34.7184 | 36.5089 | 36.9 | 37.7547 | 36.4962 | 34.3351 | 33.7484 | 35.3816 | 35.7367 | 33.945 | 34.4726 | 34.3633 | 33.9246 | 34.3802 | 34.4045 | 34.5128 | 34.1922 | 34.3678 | 35.4226 | 35.8178 | 35.6227 | 35.6849 | 34.2862 | 93.5956 | 93.8232 | 93.4464
2022-09-08 00:48 | 2:58 | 23.14 | 24.4594 | 25.8561 | 36.1289 | 34.471 | 34.5985 | 35.6371 | 35.8339 | 36.8442 | 37.4862 | 36.7676 | 37.6182 | 34.5524 | 34.5318 | 35.1574 | 35.7791 | 36.303 | 36.676 | 37.2158 | 37.3457 | 24.6684 | 22.0591 | 92.7237 | 34.4044 | 34.0262 | 35.6309 | 34.3402 | 33.9673 | 34.1739 | 35.4935 | 34.7776 | 34.6793 | 37.4848 | 36.5163 | 34.1908 | 34.7312 | 36.5074 | 36.9071 | 37.7704 | 36.5133 | 34.3375 | 33.7552 | 35.3719 | 35.7275 | 33.9505 | 34.4718 | 34.3766 | 33.9223 | 34.3605 | 34.4054 | 34.4866 | 34.1969 | 34.3802 | 35.3981 | 35.8197 | 35.6283 | 35.6859 | 34.2679 | 93.5518 | 93.7848 | 93.4057
2022-09-08 00:49 | 2:58 | 22.8771 | 24.2257 | 25.6835 | 36.134 | 34.4436 | 34.6255 | 35.6308 | 35.8247 | 36.8559 | 37.4722 | 36.7629 | 37.6307 | 34.5728 | 34.523 | 35.1556 | 35.7749 | 36.321 | 36.6805 | 37.2057 | 37.3249 | 24.4521 | 21.9581 | 92.8793 | 34.4979 | 34.0225 | 35.6082 | 34.341 | 33.9558 | 34.1799 | 35.4865 | 34.8024 | 34.672 | 37.507 | 36.5135 | 34.1865 | 34.7353 | 36.5142 | 36.8901 | 37.7695 | 36.5025 | 34.3581 | 33.7272 | 35.3541 | 35.7439 | 33.9259 | 34.4814 | 34.3783 | 33.9155 | 34.3851 | 34.399 | 34.4986 | 34.2144 | 34.3605 | 35.4016 | 35.8019 | 35.6211 | 35.7005 | 34.3045 | 93.5272 | 93.7544 | 93.3661
2022-09-08 00:49 | 2:59 | 22.7624 | 24.0385 | 25.5445 | 36.1967 | 34.4717 | 34.5986 | 35.6402 | 35.8388 | 36.8636 | 37.4826 | 36.7544 | 37.6315 | 34.58 | 34.5256 | 35.1568 | 35.7807 | 36.3259 | 36.6657 | 37.1993 | 37.3431 | 24.285 | 21.7848 | 92.8658 | 34.4693 | 34.0313 | 35.6106 | 34.3312 | 33.9658 | 34.1786 | 35.4826 | 34.7824 | 34.6893 | 37.495 | 36.5135 | 34.1823 | 34.7407 | 36.5163 | 36.9075 | 37.764 | 36.5089 | 34.3309 | 33.7429 | 35.3616 | 35.7318 | 33.9104 | 34.4913 | 34.3802 | 33.9083 | 34.373 | 34.4106 | 34.5178 | 34.1959 | 34.3851 | 35.4023 | 35.8221 | 35.6373 | 35.694 | 34.2785 | 93.5089 | 93.6785 | 93.3159
2022-09-08 00:49 | 2:59 | 22.543 | 23.8661 | 25.3609 | 36.0221 | 34.4547 | 34.5936 | 35.6053 | 35.8082 | 36.8647 | 37.4896 | 36.7761 | 37.6315 | 34.5568 | 34.5383 | 35.1489 | 35.7796 | 36.3298 | 36.6805 | 37.1903 | 37.3241 | 24.0985 | 21.6445 | 92.8628 | 34.3918 | 34.0284 | 35.6307 | 34.3351 | 33.9586 | 34.191 | 35.4722 | 34.7755 | 34.686 | 37.4995 | 36.5233 | 34.1752 | 34.7435 | 36.5135 | 36.9058 | 37.7678 | 36.5074 | 34.3479 | 33.7485 | 35.3595 | 35.7281 | 33.9445 | 34.4938 | 34.3824 | 33.9259 | 34.387 | 34.3932 | 34.5075 | 34.2073 | 34.373 | 35.3963 | 35.8152 | 35.631 | 35.6877 | 34.2884 | 93.4073 | 93.6025 | 93.2064
2022-09-08 00:49 | 2:59 | 22.4298 | 23.6538 | 25.2039 | 35.9287 | 34.459 | 34.6025 | 35.6015 | 35.8211 | 36.8635 | 37.5038 | 36.7532 | 37.6251 | 34.5423 | 34.5317 | 35.1358 | 35.7862 | 36.32 | 36.6626 | 37.1861 | 37.3292 | 23.9361 | 21.5589 | 92.831 | 34.3929 | 34.0211 | 35.6157 | 34.3375 | 33.9547 | 34.1908 | 35.4689 | 34.7908 | 34.6805 | 37.5155 | 36.5247 | 34.1726 | 34.7238 | 36.5135 | 36.9028 | 37.7707 | 36.5142 | 34.3436 | 33.7497 | 35.363 | 35.7318 | 33.9048 | 34.4729 | 34.3835 | 33.9008 | 34.3648 | 34.4041 | 34.5197 | 34.1966 | 34.387 | 35.4013 | 35.8046 | 35.6213 | 35.6662 | 34.2805 | 93.366 | 93.4751 | 93.1919
2022-09-08 00:49 | 2:59 | 22.2416 | 23.4738 | 25.0323 | 36.056 | 34.4436 | 34.6088 | 35.5919 | 35.8193 | 36.8689 | 37.4892 | 36.7575 | 37.6218 | 34.5566 | 34.5299 | 35.1425 | 35.7807 | 36.3277 | 36.6618 | 37.185 | 37.3381 | 23.7847 | 21.3233 | 92.7615 | 34.2582 | 34.0468 | 35.6174 | 34.3581 | 33.9463 | 34.1865 | 35.4858 | 34.8075 | 34.6703 | 37.5096 | 36.5203 | 34.1714 | 34.7408 | 36.5233 | 36.9019 | 37.7886 | 36.5163 | 34.3447 | 33.7341 | 35.3634 | 35.7249 | 33.9015 | 34.4853 | 34.3919 | 33.9146 | 34.3713 | 34.4192 | 34.5078 | 34.2042 | 34.3648 | 35.3973 | 35.8328 | 35.629 | 35.7004 | 34.2847 | 93.2907 | 93.4183 | 93.2577
2022-09-08 00:49 | 2:59 | 22.04 | 23.2318 | 24.8469 | 35.9828 | 34.4778 | 34.5916 | 35.5949 | 35.8274 | 36.8793 | 37.4908 | 36.7648 | 37.634 | 34.5833 | 34.5159 | 35.1495 | 35.7946 | 36.3359 | 36.6692 | 37.1851 | 37.3346 | 23.6367 | 21.1512 | 92.7342 | 34.3022 | 34.0302 | 35.6223 | 34.3309 | 33.94 | 34.1823 | 35.485 | 34.7787 | 34.6927 | 37.5143 | 36.5189 | 34.1763 | 34.7348 | 36.5247 | 36.9018 | 37.7598 | 36.5135 | 34.3447 | 33.7306 | 35.3625 | 35.7381 | 33.9168 | 34.5006 | 34.3925 | 33.9122 | 34.3747 | 34.4095 | 34.5153 | 34.1929 | 34.3713 | 35.4242 | 35.799 | 35.6206 | 35.6902 | 34.2772 | 93.1825 | 93.4111 | 93.1804
2022-09-08 00:50 | 3:00 | 21.8549 | 23.0375 | 24.6627 | 35.9505 | 34.48 | 34.5915 | 35.6018 | 35.825 | 36.8749 | 37.4903 | 36.7786 | 37.6428 | 34.5597 | 34.5281 | 35.1496 | 35.7921 | 36.3209 | 36.6794 | 37.1819 | 37.3329 | 23.4996 | 21.0908 | 92.7191 | 34.2116 | 34.0368 | 35.6153 | 34.3479 | 33.945 | 34.1752 | 35.4918 | 34.8025 | 34.6874 | 37.5227 | 36.5127 | 34.1697 | 34.7583 | 36.5203 | 36.9037 | 37.7858 | 36.5135 | 34.3512 | 33.7318 | 35.3556 | 35.7384 | 33.8985 | 34.4899 | 34.3942 | 33.9151 | 34.3605 | 34.4173 | 34.5134 | 34.1922 | 34.3747 | 35.3912 | 35.807 | 35.6324 | 35.6882 | 34.2865 | 93.1963 | 93.3122 | 93.1713
2022-09-08 00:50 | 3:00 | 21.9029 | 22.9254 | 24.5442 | 35.9114 | 34.4678 | 34.6051 | 35.6019 | 35.8355 | 36.8621 | 37.4918 | 36.7685 | 37.6275 | 34.5408 | 34.5265 | 35.1245 | 35.8053 | 36.3192 | 36.6675 | 37.1718 | 37.3471 | 23.3954 | 20.9083 | 92.6461 | 34.2219 | 34.0304 | 35.6125 | 34.3436 | 33.9476 | 34.1726 | 35.4733 | 34.8035 | 34.6883 | 37.5071 | 36.5173 | 34.1714 | 34.7359 | 36.5189 | 36.8993 | 37.7712 | 36.5233 | 34.3338 | 33.7266 | 35.365 | 35.7506 | 33.9064 | 34.4851 | 34.3892 | 33.9201 | 34.3467 | 34.408 | 34.5185 | 34.2103 | 34.3605 | 35.4222 | 35.808 | 35.6292 | 35.6858 | 34.2974 | 93.1362 | 93.1803 | 93.0487
2022-09-08 00:50 | 3:00 | 21.6731 | 22.7204 | 24.3919 | 35.9099 | 34.486 | 34.6103 | 35.5858 | 35.8208 | 36.8561 | 37.4778 | 36.76 | 37.6356 | 34.5539 | 34.5041 | 35.1641 | 35.7993 | 36.3201 | 36.6663 | 37.1966 | 37.3348 | 23.2746 | 20.7746 | 92.5506 | 34.1663 | 34.0287 | 35.6125 | 34.3447 | 33.9543 | 34.1714 | 35.4835 | 34.7978 | 34.6895 | 37.5123 | 36.5277 | 34.1734 | 34.7475 | 36.5127 | 36.9105 | 37.7811 | 36.5247 | 34.3597 | 33.7162 | 35.3581 | 35.7331 | 33.889 | 34.4887 | 34.3941 | 33.9233 | 34.3521 | 34.411 | 34.5114 | 34.2082 | 34.3467 | 35.4417 | 35.8058 | 35.6334 | 35.7111 | 34.2986 | 93.0261 | 93.0941 | 93.0337
2022-09-08 00:50 | 3:00 | 21.5846 | 22.569 | 24.241 | 35.9041 | 34.4632 | 34.6007 | 35.5896 | 35.8135 | 36.8718 | 37.4892 | 36.7709 | 37.6376 | 34.5292 | 34.5163 | 35.1514 | 35.7982 | 36.3396 | 36.6774 | 37.1653 | 37.3343 | 23.1793 | 20.6584 | 92.5361 | 34.15 | 34.0308 | 35.6381 | 34.3447 | 33.9498 | 34.1763 | 35.4616 | 34.8008 | 34.6777 | 37.5249 | 36.5195 | 34.1823 | 34.7435 | 36.5173 | 36.9132 | 37.7622 | 36.5203 | 34.3509 | 33.7115 | 35.3331 | 35.7345 | 33.8767 | 34.4995 | 34.4079 | 33.9217 | 34.365 | 34.3913 | 34.5304 | 34.1806 | 34.3521 | 35.4082 | 35.8143 | 35.6213 | 35.7054 | 34.3029 | 92.9646 | 92.9652 | 92.9461
2022-09-08 00:50 | 3:00 | 21.4047 | 22.3976 | 24.0852 | 35.8787 | 34.4693 | 34.5831 | 35.5875 | 35.8159 | 36.8668 | 37.4835 | 36.7631 | 37.6506 | 34.5408 | 34.5282 | 35.1568 | 35.808 | 36.3335 | 36.6607 | 37.1615 | 37.3387 | 23.0989 | 20.5013 | 92.4259 | 34.046 | 34.0312 | 35.6276 | 34.3512 | 33.9416 | 34.1697 | 35.4881 | 34.801 | 34.6705 | 37.5192 | 36.5272 | 34.1871 | 34.7319 | 36.5277 | 36.8873 | 37.7737 | 36.5189 | 34.3485 | 33.7185 | 35.3436 | 35.7299 | 33.8724 | 34.4841 | 34.413 | 33.9192 | 34.376 | 34.3945 | 34.5156 | 34.184 | 34.365 | 35.4219 | 35.8305 | 35.6248 | 35.7041 | 34.2872 | 92.7909 | 92.8432 | 92.9116
2022-09-08 00:50 | 3:00 | 21.2334 | 22.1999 | 23.9244 | 35.7705 | 34.499 | 34.5794 | 35.5815 | 35.8099 | 36.8781 | 37.4814 | 36.7761 | 37.6403 | 34.5173 | 34.5365 | 35.1671 | 35.8003 | 36.3384 | 36.6637 | 37.1602 | 37.3336 | 23.0039 | 20.3715 | 92.3923 | 34.1485 | 34.0228 | 35.6218 | 34.3338 | 33.9505 | 34.1714 | 35.4836 | 34.8155 | 34.6795 | 37.5171 | 36.5254 | 34.1769 | 34.7332 | 36.5195 | 36.8903 | 37.7871 | 36.5127 | 34.3426 | 33.7235 | 35.3336 | 35.724 | 33.8732 | 34.4864 | 34.4139 | 33.9227 | 34.3753 | 34.3949 | 34.5354 | 34.2133 | 34.376 | 35.4249 | 35.7962 | 35.6586 | 35.7023 | 34.2855 | 92.6701 | 92.767 | 92.8105
2022-09-08 00:51 | 3:00 | 21.0994 | 22.0731 | 23.7949 | 35.7647 | 34.49 | 34.5858 | 35.5611 | 35.8143 | 36.8639 | 37.4812 | 36.7592 | 37.6217 | 34.5357 | 34.5052 | 35.1576 | 35.7878 | 36.3507 | 36.6504 | 37.1514 | 37.3389 | 22.9571 | 20.246 | 92.1861 | 34.2066 | 34.0092 | 35.6077 | 34.3597 | 33.9484 | 34.1734 | 35.4897 | 34.8034 | 34.6887 | 37.5116 | 36.5198 | 34.1778 | 34.748 | 36.5272 | 36.9126 | 37.7734 | 36.5173 | 34.3338 | 33.7065 | 35.3147 | 35.726 | 33.8708 | 34.4901 | 34.4005 | 33.912 | 34.3558 | 34.401 | 34.528 | 34.1953 | 34.3753 | 35.447 | 35.7968 | 35.6446 | 35.7061 | 34.3004 | 92.6077 | 92.6395 | 92.7744
2022-09-08 00:51 | 3:01 | 21.0839 | 21.9864 | 23.7047 | 35.7325 | 34.4802 | 34.5742 | 35.5768 | 35.8105 | 36.8765 | 37.4814 | 36.7881 | 37.6552 | 34.5425 | 34.5077 | 35.1551 | 35.8152 | 36.3199 | 36.6505 | 37.1844 | 37.3373 | 22.9465 | 20.2452 | 92.0853 | 34.0688 | 34.0124 | 35.6316 | 34.3509 | 33.9507 | 34.1823 | 35.4668 | 34.8171 | 34.6803 | 37.5437 | 36.541 | 34.1777 | 34.7338 | 36.5254 | 36.9235 | 37.7615 | 36.5277 | 34.358 | 33.7035 | 35.3032 | 35.7234 | 33.8648 | 34.4906 | 34.4228 | 33.9342 | 34.3558 | 34.3877 | 34.5302 | 34.1794 | 34.3558 | 35.438 | 35.8078 | 35.6669 | 35.7161 | 34.2925 | 92.4822 | 92.5217 | 92.678
2022-09-08 00:51 | 3:01 | 20.8481 | 21.7092 | 23.5359 | 35.6992 | 34.4823 | 34.5834 | 35.5461 | 35.8285 | 36.8697 | 37.5033 | 36.7463 | 37.6536 | 34.5249 | 34.5046 | 35.1583 | 35.8074 | 36.3198 | 36.6367 | 37.1641 | 37.3376 | 22.8945 | 20.1244 | 92.1197 | 34.1316 | 34.029 | 35.6327 | 34.3485 | 33.9505 | 34.1871 | 35.476 | 34.8037 | 34.6875 | 37.5273 | 36.5446 | 34.1842 | 34.7184 | 36.5198 | 36.9197 | 37.7835 | 36.5195 | 34.3423 | 33.7154 | 35.3162 | 35.7074 | 33.8487 | 34.4638 | 34.428 | 33.9244 | 34.3663 | 34.3966 | 34.5091 | 34.2022 | 34.3558 | 35.4359 | 35.8132 | 35.6409 | 35.7121 | 34.2952 | 92.4266 | 92.5083 | 92.6112
2022-09-08 00:51 | 3:01 | 20.8102 | 21.6541 | 23.4257 | 35.6845 | 34.4894 | 34.6036 | 35.5605 | 35.8228 | 36.8799 | 37.4978 | 36.7831 | 37.6484 | 34.5307 | 34.5253 | 35.1607 | 35.803 | 36.3266 | 36.6717 | 37.1648 | 37.3415 | 22.8134 | 19.9999 | 92.1389 | 34.0669 | 34.0284 | 35.6193 | 34.3426 | 33.9156 | 34.1769 | 35.4815 | 34.8034 | 34.6683 | 37.514 | 36.5197 | 34.1577 | 34.7485 | 36.541 | 36.9031 | 37.7543 | 36.5272 | 34.3633 | 33.7112 | 35.3365 | 35.7247 | 33.8498 | 34.4935 | 34.4127 | 33.9104 | 34.3631 | 34.3931 | 34.5243 | 34.2016 | 34.3663 | 35.4377 | 35.8072 | 35.6427 | 35.6887 | 34.3065 | 92.2811 | 92.3919 | 92.5509
2022-09-08 00:51 | 3:01 | 20.6681 | 21.4028 | 23.2581 | 35.6965 | 34.4669 | 34.5869 | 35.564 | 35.8224 | 36.8929 | 37.481 | 36.7726 | 37.664 | 34.5005 | 34.4931 | 35.1474 | 35.7977 | 36.3272 | 36.6644 | 37.1544 | 37.3438 | 22.7518 | 19.8709 | 92.3665 | 33.9726 | 34.0207 | 35.6222 | 34.3338 | 33.9444 | 34.1778 | 35.4761 | 34.8209 | 34.6782 | 37.5279 | 36.5059 | 34.1799 | 34.7575 | 36.5446 | 36.9142 | 37.7653 | 36.5254 | 34.3318 | 33.6817 | 35.3454 | 35.7374 | 33.8094 | 34.4833 | 34.4023 | 33.9174 | 34.3711 | 34.42 | 34.5286 | 34.1965 | 34.3631 | 35.4341 | 35.8077 | 35.6547 | 35.7238 | 34.3033 | 92.1347 | 92.2134 | 92.4394
2022-09-08 00:51 | 3:01 | 20.4752 | 21.3087 | 23.1385 | 35.6018 | 34.4876 | 34.5698 | 35.5449 | 35.8155 | 36.87 | 37.4931 | 36.7677 | 37.6628 | 34.5194 | 34.502 | 35.1352 | 35.8113 | 36.3154 | 36.653 | 37.1516 | 37.334 | 22.6895 | 19.7584 | 92.3598 | 33.8913 | 34.0209 | 35.6084 | 34.358 | 33.9352 | 34.1777 | 35.465 | 34.7975 | 34.6822 | 37.5289 | 36.5189 | 34.1644 | 34.7425 | 36.5197 | 36.9362 | 37.7846 | 36.5198 | 34.3322 | 33.6998 | 35.3215 | 35.7098 | 33.837 | 34.4706 | 34.421 | 33.896 | 34.3757 | 34.3828 | 34.52 | 34.199 | 34.3711 | 35.4361 | 35.7937 | 35.6395 | 35.7011 | 34.3041 | 92.096 | 92.102 | 92.3999
2022-09-08 00:52 | 3:02 | 20.3725 | 21.246 | 23.0299 | 35.6489 | 34.4797 | 34.5916 | 35.5433 | 35.8229 | 36.8736 | 37.4797 | 36.7738 | 37.6487 | 34.5104 | 34.4957 | 35.1496 | 35.8063 | 36.3239 | 36.6497 | 37.1637 | 37.3535 | 22.6302 | 19.7015 | 92.3435 | 33.9633 | 34.0281 | 35.6007 | 34.3423 | 33.9372 | 34.1842 | 35.476 | 34.7925 | 34.6778 | 37.5161 | 36.5158 | 34.1668 | 34.726 | 36.5059 | 36.9299 | 37.773 | 36.541 | 34.3188 | 33.6882 | 35.3064 | 35.7124 | 33.7968 | 34.4778 | 34.4118 | 33.9099 | 34.361 | 34.3939 | 34.5276 | 34.1703 | 34.3757 | 35.4491 | 35.8041 | 35.6495 | 35.7235 | 34.3019 | 91.8821 | 91.9444 | 92.2508
2022-09-08 00:52 | 3:02 | 20.2837 | 21.0361 | 22.9154 | 35.5669 | 34.4893 | 34.5815 | 35.5547 | 35.8068 | 36.8784 | 37.4791 | 36.7739 | 37.6294 | 34.4991 | 34.4831 | 35.1761 | 35.8102 | 36.3197 | 36.6522 | 37.1416 | 37.3088 | 22.5966 | 19.6432 | 92.3668 | 33.9753 | 34.0221 | 35.6322 | 34.3633 | 33.9313 | 34.1577 | 35.4879 | 34.7835 | 34.666 | 37.52 | 36.5068 | 34.1669 | 34.7176 | 36.5189 | 36.9079 | 37.7519 | 36.5446 | 34.319 | 33.6808 | 35.2968 | 35.6932 | 33.8009 | 34.453 | 34.4243 | 33.901 | 34.3565 | 34.4055 | 34.5259 | 34.2033 | 34.361 | 35.4515 | 35.8006 | 35.6525 | 35.7037 | 34.2922 | 91.7341 | 91.8055 | 92.191
2022-09-08 00:52 | 3:02 | 20.1474 | 20.9288 | 22.8144 | 35.4961 | 34.4851 | 34.5785 | 35.5535 | 35.8111 | 36.8629 | 37.4954 | 36.7397 | 37.645 | 34.4986 | 34.4669 | 35.1523 | 35.8014 | 36.3237 | 36.6463 | 37.1529 | 37.3385 | 22.5406 | 19.5107 | 92.4393 | 34.0503 | 34.004 | 35.611 | 34.3318 | 33.9252 | 34.1799 | 35.481 | 34.7735 | 34.6897 | 37.5128 | 36.5033 | 34.1645 | 34.7179 | 36.5158 | 36.9184 | 37.7796 | 36.5197 | 34.3346 | 33.6902 | 35.3062 | 35.7103 | 33.8005 | 34.4804 | 34.4173 | 33.9055 | 34.3704 | 34.3849 | 34.5264 | 34.2112 | 34.3565 | 35.4306 | 35.8141 | 35.6679 | 35.7081 | 34.296 | 91.6856 | 91.6675 | 92.1196
2022-09-08 00:52 | 3:02 | 20.0774 | 20.8195 | 22.692 | 35.4791 | 34.4894 | 34.5778 | 35.531 | 35.8094 | 36.8713 | 37.4896 | 36.7781 | 37.6559 | 34.5005 | 34.4927 | 35.1577 | 35.8091 | 36.3013 | 36.6576 | 37.1491 | 37.3421 | 22.4829 | 19.4837 | 92.5542 | 33.8874 | 34.0263 | 35.6142 | 34.3322 | 33.9358 | 34.1644 | 35.4596 | 34.7824 | 34.6798 | 37.5168 | 36.4913 | 34.1639 | 34.7228 | 36.5068 | 36.902 | 37.7629 | 36.5059 | 34.3261 | 33.6638 | 35.299 | 35.7003 | 33.8029 | 34.4565 | 34.4247 | 33.9003 | 34.3687 | 34.4143 | 34.5164 | 34.1862 | 34.3704 | 35.4351 | 35.8118 | 35.6634 | 35.7206 | 34.3124 | 91.6136 | 91.5546 | 92.0222
2022-09-08 00:52 | 3:02 | 19.8617 | 20.6286 | 22.5583 | 35.5203 | 34.4819 | 34.5733 | 35.5378 | 35.7998 | 36.8845 | 37.4967 | 36.7628 | 37.6618 | 34.4877 | 34.4716 | 35.1372 | 35.7831 | 36.3162 | 36.636 | 37.1381 | 37.312 | 22.4154 | 19.309 | 92.6378 | 33.9175 | 34.0096 | 35.6056 | 34.3188 | 33.8942 | 34.1668 | 35.4657 | 34.7715 | 34.6914 | 37.5266 | 36.4884 | 34.1508 | 34.7355 | 36.5033 | 36.9047 | 37.7793 | 36.5189 | 34.3113 | 33.6828 | 35.2969 | 35.6883 | 33.7845 | 34.4695 | 34.4217 | 33.8996 | 34.3704 | 34.3972 | 34.5196 | 34.1817 | 34.3687 | 35.4414 | 35.8034 | 35.6474 | 35.7266 | 34.3047 | 91.6253 | 91.6111 | 92.0906
2022-09-08 00:52 | 3:02 | 19.7635 | 20.5108 | 22.4396 | 35.4767 | 34.5033 | 34.5708 | 35.5367 | 35.8108 | 36.8728 | 37.479 | 36.7604 | 37.6378 | 34.4942 | 34.4777 | 35.1476 | 35.7966 | 36.2793 | 36.636 | 37.1366 | 37.3316 | 22.4151 | 19.2399 | 92.7205 | 33.8888 | 34.0073 | 35.6266 | 34.319 | 33.9136 | 34.1669 | 35.4629 | 34.7879 | 34.6588 | 37.5154 | 36.5274 | 34.1568 | 34.7279 | 36.4913 | 36.9029 | 37.7643 | 36.5158 | 34.3414 | 33.6527 | 35.2771 | 35.6805 | 33.7665 | 34.4558 | 34.426 | 33.8756 | 34.3681 | 34.3841 | 34.5234 | 34.1782 | 34.3704 | 35.4477 | 35.8055 | 35.6436 | 35.7302 | 34.2964 | 91.7463 | 91.637 | 92.1594
2022-09-08 00:53 | 3:02 | 19.7126 | 20.4621 | 22.3381 | 35.5056 | 34.5032 | 34.5506 | 35.5311 | 35.807 | 36.8761 | 37.4658 | 36.768 | 37.6519 | 34.4987 | 34.472 | 35.1432 | 35.7964 | 36.3122 | 36.6355 | 37.1078 | 37.3196 | 22.5087 | 19.1465 | 92.8136 | 33.9124 | 34.0077 | 35.6204 | 34.3346 | 33.9161 | 34.1645 | 35.4765 | 34.797 | 34.6701 | 37.5293 | 36.5258 | 34.1603 | 34.7172 | 36.4884 | 36.8966 | 37.7512 | 36.5068 | 34.3247 | 33.677 | 35.2716 | 35.7016 | 33.7697 | 34.4459 | 34.4297 | 33.8718 | 34.3673 | 34.3941 | 34.5318 | 34.1816 | 34.3681 | 35.4422 | 35.8015 | 35.653 | 35.7216 | 34.3036 | 91.8346 | 91.7645 | 92.2373
2022-09-08 00:53 | 3:03 | 19.6036 | 20.3562 | 22.2357 | 35.4562 | 34.5095 | 34.5634 | 35.5321 | 35.7991 | 36.8541 | 37.4864 | 36.7659 | 37.6566 | 34.4771 | 34.4674 | 35.1598 | 35.8032 | 36.3027 | 36.6213 | 37.1326 | 37.3228 | 22.3295 | 19.0816 | 92.8094 | 33.8743 | 33.9989 | 35.5987 | 34.3261 | 33.9234 | 34.1639 | 35.4725 | 34.7844 | 34.6549 | 37.5085 | 36.5046 | 34.1563 | 34.7194 | 36.5274 | 36.8964 | 37.7701 | 36.5033 | 34.331 | 33.6564 | 35.2579 | 35.674 | 33.7442 | 34.4397 | 34.441 | 33.8895 | 34.3464 | 34.4037 | 34.523 | 34.1916 | 34.3673 | 35.4567 | 35.8072 | 35.6783 | 35.7056 | 34.2934 | 91.9522 | 91.9194 | 92.3143
2022-09-08 00:53 | 3:03 | 19.5034 | 20.24 | 22.1406 | 35.464 | 34.4768 | 34.5648 | 35.5089 | 35.7976 | 36.8823 | 37.4737 | 36.7656 | 37.6417 | 34.4866 | 34.462 | 35.149 | 35.801 | 36.2966 | 36.6136 | 37.1237 | 37.3212 | 22.259 | 18.9796 | 92.9289 | 33.9501 | 33.9851 | 35.5935 | 34.3113 | 33.9145 | 34.1508 | 35.4523 | 34.7856 | 34.6839 | 37.5164 | 36.4945 | 34.1608 | 34.7064 | 36.5258 | 36.9032 | 37.7822 | 36.4913 | 34.3035 | 33.6546 | 35.2537 | 35.6812 | 33.7735 | 34.4423 | 34.4365 | 33.8812 | 34.3669 | 34.3853 | 34.5256 | 34.1902 | 34.3464 | 35.4513 | 35.7967 | 35.6484 | 35.7096 | 34.2804 | 92.1619 | 92.1276 | 92.463
2022-09-08 00:53 | 3:03 | 19.4328 | 20.1082 | 22.0286 | 35.4485 | 34.5128 | 34.5388 | 35.4989 | 35.8015 | 36.8784 | 37.4837 | 36.774 | 37.651 | 34.4769 | 34.4595 | 35.1364 | 35.8007 | 36.3076 | 36.6258 | 37.1268 | 37.3255 | 22.1925 | 18.9286 | 93.0328 | 33.7113 | 33.9962 | 35.6058 | 34.3414 | 33.9225 | 34.1568 | 35.475 | 34.7819 | 34.6737 | 37.5155 | 36.5014 | 34.1658 | 34.7241 | 36.5046 | 36.9048 | 37.7569 | 36.4884 | 34.3122 | 33.621 | 35.2542 | 35.6609 | 33.7538 | 34.443 | 34.4279 | 33.8616 | 34.3738 | 34.3991 | 34.5383 | 34.1773 | 34.3669 | 35.4432 | 35.7885 | 35.6737 | 35.7161 | 34.2984 | 92.2818 | 92.3662 | 92.6219
2022-09-08 00:53 | 3:03 | 19.4707 | 20.0665 | 21.9535 | 35.341 | 34.4866 | 34.5557 | 35.4966 | 35.7904 | 36.8585 | 37.4875 | 36.747 | 37.6353 | 34.4737 | 34.4501 | 35.1425 | 35.8011 | 36.2942 | 36.6018 | 37.134 | 37.3181 | 22.1629 | 18.8483 | 93.1328 | 33.8056 | 33.9951 | 35.597 | 34.3247 | 33.9077 | 34.1603 | 35.482 | 34.7702 | 34.6734 | 37.5078 | 36.4898 | 34.1664 | 34.7116 | 36.4945 | 36.8962 | 37.7527 | 36.5274 | 34.3219 | 33.6356 | 35.2677 | 35.6807 | 33.7451 | 34.4518 | 34.437 | 33.8732 | 34.3554 | 34.3877 | 34.5317 | 34.1903 | 34.3738 | 35.4563 | 35.8003 | 35.6704 | 35.7245 | 34.2932 | 92.4649 | 92.5506 | 92.7184
2022-09-08 00:53 | 3:03 | 19.4584 | 19.9682 | 21.9012 | 35.2636 | 34.4986 | 34.5427 | 35.5097 | 35.7918 | 36.8969 | 37.4746 | 36.7898 | 37.6293 | 34.4859 | 34.4713 | 35.1311 | 35.8006 | 36.3003 | 36.6261 | 37.1213 | 37.3247 | 22.1473 | 18.8354 | 93.2833 | 33.8825 | 33.9783 | 35.5976 | 34.331 | 33.8853 | 34.1563 | 35.4648 | 34.7943 | 34.6658 | 37.5091 | 36.4912 | 34.1685 | 34.7179 | 36.5014 | 36.8843 | 37.767 | 36.5258 | 34.3177 | 33.6191 | 35.2548 | 35.6639 | 33.7317 | 34.437 | 34.4252 | 33.8562 | 34.3501 | 34.3896 | 34.5299 | 34.1745 | 34.3554 | 35.4583 | 35.7948 | 35.6957 | 35.7299 | 34.2868 | 92.6714 | 92.6991 | 92.7873
2022-09-08 00:54 | 3:04 | 19.2785 | 19.8564 | 21.7852 | 35.3501 | 34.5178 | 34.5489 | 35.501 | 35.7945 | 36.8701 | 37.499 | 36.7675 | 37.656 | 34.4734 | 34.4616 | 35.1397 | 35.7881 | 36.2973 | 36.6305 | 37.1129 | 37.3274 | 22.1266 | 18.7885 | 93.3472 | 33.7461 | 33.9995 | 35.5961 | 34.3035 | 33.9157 | 34.1608 | 35.4726 | 34.7734 | 34.6761 | 37.5023 | 36.5074 | 34.1847 | 34.7079 | 36.4898 | 36.9041 | 37.7748 | 36.5046 | 34.3095 | 33.6189 | 35.2375 | 35.6526 | 33.7276 | 34.4467 | 34.4519 | 33.8514 | 34.3571 | 34.3913 | 34.5159 | 34.185 | 34.3501 | 35.4512 | 35.8089 | 35.6684 | 35.7383 | 34.2933 | 92.8361 | 92.9046 | 92.8481
2022-09-08 00:54 | 3:04 | 19.1972 | 19.8322 | 21.75 | 35.2459 | 34.5075 | 34.5382 | 35.4949 | 35.7953 | 36.8673 | 37.491 | 36.7545 | 37.633 | 34.4576 | 34.4672 | 35.1458 | 35.7942 | 36.2891 | 36.6003 | 37.1239 | 37.3088 | 22.0714 | 18.7463 | 93.4087 | 33.9078 | 33.9911 | 35.5825 | 34.3122 | 33.9042 | 34.1658 | 35.4912 | 34.7826 | 34.6547 | 37.5008 | 36.5023 | 34.1782 | 34.7246 | 36.4912 | 36.899 | 37.7562 | 36.4945 | 34.3147 | 33.6187 | 35.2497 | 35.654 | 33.7237 | 34.429 | 34.4396 | 33.8658 | 34.3721 | 34.3937 | 34.5281 | 34.171 | 34.3571 | 35.438 | 35.799 | 35.6727 | 35.7127 | 34.2642 | 93.0419 | 93.1493 | 93.0352
2022-09-08 00:54 | 3:04 | 19.0363 | 19.6647 | 21.6628 | 35.2766 | 34.5197 | 34.5391 | 35.4854 | 35.7937 | 36.8759 | 37.4776 | 36.7737 | 37.6555 | 34.4557 | 34.4415 | 35.1264 | 35.798 | 36.2782 | 36.6192 | 37.1001 | 37.3174 | 22.0568 | 18.6502 | 93.4766 | 33.7938 | 33.9706 | 35.5972 | 34.3219 | 33.8919 | 34.1664 | 35.4751 | 34.7716 | 34.6774 | 37.5179 | 36.4825 | 34.1734 | 34.7259 | 36.5074 | 36.8928 | 37.7668 | 36.5014 | 34.3164 | 33.6045 | 35.2103 | 35.656 | 33.7155 | 34.4404 | 34.4511 | 33.8659 | 34.3577 | 34.382 | 34.5265 | 34.1679 | 34.3721 | 35.4493 | 35.7794 | 35.6684 | 35.7096 | 34.2714 | 93.2024 | 93.402 | 93.0253
2022-09-08 00:54 | 3:04 | 18.9728 | 19.6641 | 21.6027 | 35.2023 | 34.5078 | 34.5555 | 35.4923 | 35.7943 | 36.8831 | 37.4821 | 36.7516 | 37.6369 | 34.4537 | 34.4315 | 35.1317 | 35.7938 | 36.2984 | 36.5968 | 37.0926 | 37.3113 | 22.0084 | 18.6522 | 93.6248 | 33.6965 | 33.9779 | 35.5827 | 34.3177 | 33.9096 | 34.1685 | 35.4727 | 34.7547 | 34.6602 | 37.4937 | 36.4894 | 34.14 | 34.7007 | 36.5023 | 36.8849 | 37.7522 | 36.4898 | 34.3033 | 33.596 | 35.2113 | 35.6245 | 33.7228 | 34.4295 | 34.4442 | 33.8563 | 34.3799 | 34.3771 | 34.5041 | 34.1897 | 34.3577 | 35.433 | 35.7989 | 35.6587 | 35.7163 | 34.2742 | 93.4584 | 93.6741 | 93.2103
2022-09-08 00:54 | 3:04 | 18.9746 | 19.6164 | 21.5886 | 35.3195 | 34.5153 | 34.5422 | 35.474 | 35.7841 | 36.8788 | 37.4786 | 36.7639 | 37.6347 | 34.428 | 34.4031 | 35.1329 | 35.7889 | 36.2816 | 36.6167 | 37.1014 | 37.3257 | 21.9993 | 18.5915 | 93.7934 | 33.7105 | 33.98 | 35.5895 | 34.3095 | 33.8769 | 34.1847 | 35.4453 | 34.7538 | 34.6537 | 37.5076 | 36.4899 | 34.155 | 34.7119 | 36.4825 | 36.9065 | 37.7531 | 36.4912 | 34.2978 | 33.5953 | 35.2148 | 35.6435 | 33.7139 | 34.4351 | 34.4433 | 33.8347 | 34.3784 | 34.411 | 34.5163 | 34.1714 | 34.3799 | 35.4615 | 35.8012 | 35.6838 | 35.7445 | 34.2629 | 93.6873 | 93.9177 | 93.3278
2022-09-08 00:54 | 3:04 | 18.9324 | 19.5042 | 21.5324 | 35.1913 | 34.5134 | 34.5416 | 35.4724 | 35.7744 | 36.8521 | 37.4975 | 36.758 | 37.6422 | 34.4265 | 34.4401 | 35.1262 | 35.7685 | 36.2919 | 36.6058 | 37.0938 | 37.295 | 21.9726 | 18.5855 | 93.863 | 33.8197 | 33.9638 | 35.6073 | 34.3147 | 33.8778 | 34.1782 | 35.4601 | 34.7503 | 34.6686 | 37.504 | 36.5032 | 34.1606 | 34.7103 | 36.4894 | 36.8965 | 37.7675 | 36.5074 | 34.3249 | 33.6108 | 35.2041 | 35.6302 | 33.6951 | 34.4223 | 34.4596 | 33.8429 | 34.3816 | 34.3903 | 34.5282 | 34.179 | 34.3784 | 35.4441 | 35.7874 | 35.6692 | 35.7195 | 34.278 | 93.9124 | 94.1689 | 93.4702
2022-09-08 00:55 | 3:04 | 18.8303 | 19.491 | 21.4361 | 35.299 | 34.5185 | 34.5324 | 35.4832 | 35.7806 | 36.8767 | 37.4861 | 36.7573 | 37.639 | 34.4303 | 34.4203 | 35.1279 | 35.8011 | 36.2822 | 36.5915 | 37.0888 | 37.3307 | 21.9533 | 18.5197 | 94.0919 | 33.7498 | 33.9887 | 35.5843 | 34.3164 | 33.8891 | 34.1734 | 35.4554 | 34.7673 | 34.6593 | 37.4978 | 36.4937 | 34.1608 | 34.6931 | 36.4899 | 36.8947 | 37.7573 | 36.5023 | 34.3095 | 33.5876 | 35.2155 | 35.626 | 33.703 | 34.4075 | 34.4457 | 33.8176 | 34.3632 | 34.3847 | 34.5365 | 34.1623 | 34.3816 | 35.45 | 35.8088 | 35.6827 | 35.7247 | 34.2833 | 94.0685 | 94.3426 | 93.6205
2022-09-08 00:55 | 3:05 | 18.8506 | 19.4281 | 21.3362 | 35.2191 | 34.5114 | 34.5244 | 35.4644 | 35.7867 | 36.8717 | 37.4846 | 36.7397 | 37.6332 | 34.433 | 34.4203 | 35.1298 | 35.8102 | 36.2899 | 36.589 | 37.0994 | 37.3006 | 21.9163 | 18.4826 | 94.0845 | 33.6892 | 33.9635 | 35.5965 | 34.3033 | 33.8668 | 34.14 | 35.4671 | 34.7726 | 34.66 | 37.5079 | 36.4958 | 34.1558 | 34.718 | 36.5032 | 36.8996 | 37.751 | 36.4825 | 34.296 | 33.5767 | 35.2025 | 35.6202 | 33.6872 | 34.4201 | 34.4453 | 33.828 | 34.3705 | 34.3867 | 34.5052 | 34.175 | 34.3632 | 35.4493 | 35.7823 | 35.6956 | 35.7273 | 34.2806 | 94.3184 | 94.5926 | 93.7969
2022-09-08 00:55 | 3:05 | 18.7848 | 19.3234 | 21.2814 | 35.1549 | 34.5304 | 34.5271 | 35.4784 | 35.795 | 36.87 | 37.4823 | 36.7589 | 37.6146 | 34.4242 | 34.4028 | 35.1286 | 35.7898 | 36.2738 | 36.5882 | 37.0956 | 37.3002 | 21.9064 | 18.4291 | 94.1061 | 33.6124 | 33.9697 | 35.5887 | 34.2978 | 33.8969 | 34.155 | 35.4593 | 34.7688 | 34.649 | 37.4993 | 36.4871 | 34.1512 | 34.6921 | 36.4937 | 36.8984 | 37.7577 | 36.4894 | 34.2917 | 33.5621 | 35.1882 | 35.6121 | 33.6722 | 34.4168 | 34.4519 | 33.8199 | 34.3728 | 34.3794 | 34.5077 | 34.1716 | 34.3705 | 35.4317 | 35.7979 | 35.6783 | 35.7149 | 34.2584 | 94.4618 | 94.7859 | 93.9181
2022-09-08 00:55 | 3:05 | 18.7354 | 19.2898 | 21.2381 | 35.1537 | 34.5156 | 34.5481 | 35.45 | 35.7763 | 36.8635 | 37.4843 | 36.748 | 37.629 | 34.4164 | 34.41 | 35.133 | 35.8014 | 36.2739 | 36.5846 | 37.0687 | 37.306 | 21.8919 | 18.4264 | 94.2086 | 33.6204 | 33.981 | 35.5984 | 34.3249 | 33.882 | 34.1606 | 35.4417 | 34.7667 | 34.6483 | 37.4975 | 36.4944 | 34.136 | 34.6963 | 36.4958 | 36.8883 | 37.7555 | 36.4899 | 34.2935 | 33.5665 | 35.1928 | 35.6123 | 33.6957 | 34.4184 | 34.4597 | 33.8353 | 34.3638 | 34.3867 | 34.5046 | 34.1702 | 34.3728 | 35.4327 | 35.8047 | 35.6841 | 35.7153 | 34.2576 | 94.6734 | 95.0121 | 94.0885
2022-09-08 00:55 | 3:05 | 18.67 | 19.2248 | 21.1763 | 35.1509 | 34.5354 | 34.5229 | 35.4519 | 35.7884 | 36.8693 | 37.477 | 36.7611 | 37.6354 | 34.407 | 34.4062 | 35.1067 | 35.7876 | 36.2798 | 36.582 | 37.0783 | 37.3099 | 21.8868 | 18.3821 | 94.3747 | 33.5894 | 33.9566 | 35.5875 | 34.3095 | 33.8619 | 34.1608 | 35.4373 | 34.7553 | 34.6459 | 37.4983 | 36.4859 | 34.161 | 34.6996 | 36.4871 | 36.8824 | 37.7485 | 36.5032 | 34.285 | 33.5651 | 35.178 | 35.6123 | 33.6507 | 34.4179 | 34.4354 | 33.8181 | 34.3801 | 34.3824 | 34.5253 | 34.1516 | 34.3638 | 35.4524 | 35.7865 | 35.6972 | 35.7236 | 34.2411 | 94.7808 | 95.2025 | 94.1887
2022-09-08 00:55 | 3:05 | 18.6339 | 19.1798 | 21.1619 | 35.1388 | 34.528 | 34.5215 | 35.4521 | 35.7697 | 36.867 | 37.4703 | 36.7532 | 37.6369 | 34.4045 | 34.4086 | 35.1254 | 35.7945 | 36.2461 | 36.5832 | 37.0826 | 37.3131 | 21.9174 | 18.3623 | 94.3071 | 33.7608 | 33.9603 | 35.5873 | 34.296 | 33.8776 | 34.1558 | 35.451 | 34.7686 | 34.6572 | 37.4966 | 36.4968 | 34.1416 | 34.7 | 36.4944 | 36.8792 | 37.7447 | 36.4937 | 34.3043 | 33.563 | 35.1702 | 35.5895 | 33.6719 | 34.3846 | 34.465 | 33.8155 | 34.3706 | 34.369 | 34.4931 | 34.1482 | 34.3801 | 35.4525 | 35.7818 | 35.685 | 35.7243 | 34.2537 | 94.9052 | 95.3533 | 94.2154
2022-09-08 00:56 | 3:05 | 18.5818 | 19.1201 | 21.1084 | 35.029 | 34.5302 | 34.5164 | 35.453 | 35.7805 | 36.8516 | 37.4726 | 36.7486 | 37.6407 | 34.4054 | 34.3894 | 35.1123 | 35.7701 | 36.2625 | 36.5612 | 37.0552 | 37.2879 | 22.1016 | 18.3307 | 94.1898 | 33.5978 | 33.9571 | 35.5795 | 34.2917 | 33.8595 | 34.1512 | 35.4383 | 34.7603 | 34.6707 | 37.5083 | 36.4671 | 34.1271 | 34.7063 | 36.4859 | 36.8843 | 37.7487 | 36.4958 | 34.2912 | 33.5374 | 35.161 | 35.599 | 33.6439 | 34.3978 | 34.4532 | 33.8029 | 34.366 | 34.3826 | 34.502 | 34.1581 | 34.3706 | 35.4337 | 35.7895 | 35.6688 | 35.7235 | 34.2333 | 95.1165 | 95.5205 | 94.3726
2022-09-08 00:56 | 3:06 | 18.5733 | 19.0917 | 21.0668 | 35.0224 | 34.5091 | 34.5193 | 35.4544 | 35.7772 | 36.8651 | 37.4663 | 36.7525 | 37.6472 | 34.399 | 34.3925 | 35.1073 | 35.7699 | 36.2663 | 36.5681 | 37.0621 | 37.2889 | 22.0161 | 18.2407 | 94.0445 | 33.5712 | 33.9491 | 35.5792 | 34.2935 | 33.8666 | 34.136 | 35.4395 | 34.7552 | 34.6328 | 37.4861 | 36.4926 | 34.1298 | 34.6893 | 36.4968 | 36.8698 | 37.7364 | 36.4871 | 34.2957 | 33.5447 | 35.1677 | 35.5844 | 33.6446 | 34.3915 | 34.4507 | 33.8042 | 34.3873 | 34.3901 | 34.4957 | 34.1518 | 34.366 | 35.4385 | 35.803 | 35.6799 | 35.7234 | 34.2325 | 95.2245 | 95.5944 | 94.3663
2022-09-08 00:56 | 3:06 | 18.4545 | 18.982 | 21.0041 | 35.0306 | 34.5243 | 34.519 | 35.4455 | 35.7773 | 36.8603 | 37.454 | 36.7526 | 37.6514 | 34.4106 | 34.3826 | 35.1011 | 35.781 | 36.265 | 36.562 | 37.0578 | 37.2876 | 21.9677 | 18.213 | 93.8833 | 33.5867 | 33.939 | 35.5883 | 34.285 | 33.8623 | 34.161 | 35.4347 | 34.7673 | 34.6411 | 37.4723 | 36.4931 | 34.1237 | 34.6922 | 36.4671 | 36.8731 | 37.7408 | 36.4944 | 34.2757 | 33.5509 | 35.14 | 35.5687 | 33.6429 | 34.4027 | 34.458 | 33.7848 | 34.3551 | 34.3802 | 34.4831 | 34.1675 | 34.3873 | 35.4164 | 35.8006 | 35.6763 | 35.7179 | 34.2253 | 95.3944 | 95.6703 | 94.5804
2022-09-08 00:56 | 3:06 | 18.3827 | 18.975 | 20.9212 | 34.9992 | 34.5286 | 34.5262 | 35.4473 | 35.7726 | 36.8389 | 37.4641 | 36.75 | 37.6452 | 34.3932 | 34.3957 | 35.1004 | 35.7873 | 36.2512 | 36.5629 | 37.0522 | 37.2604 | 21.9462 | 18.1575 | 93.7788 | 33.5455 | 33.9411 | 35.5698 | 34.3043 | 33.8569 | 34.1416 | 35.4305 | 34.7552 | 34.6466 | 37.4872 | 36.4866 | 34.1343 | 34.7016 | 36.4926 | 36.8877 | 37.7245 | 36.4859 | 34.3009 | 33.5323 | 35.1322 | 35.5665 | 33.6176 | 34.404 | 34.4474 | 33.7822 | 34.3778 | 34.3905 | 34.4669 | 34.1461 | 34.3551 | 35.4252 | 35.7934 | 35.6759 | 35.7067 | 34.2266 | 95.4387 | 95.7271 | 94.667
2022-09-08 00:56 | 3:06 | 18.4185 | 18.9242 | 20.8633 | 34.9782 | 34.52 | 34.5198 | 35.4334 | 35.7498 | 36.855 | 37.4528 | 36.7713 | 37.6439 | 34.4041 | 34.4073 | 35.1049 | 35.7713 | 36.2659 | 36.5525 | 37.0555 | 37.2596 | 21.937 | 18.1881 | 93.7722 | 33.4435 | 33.9473 | 35.5749 | 34.2912 | 33.8578 | 34.1271 | 35.418 | 34.7774 | 34.6588 | 37.4894 | 36.4917 | 34.1389 | 34.6987 | 36.4931 | 36.8807 | 37.7154 | 36.4968 | 34.2816 | 33.5172 | 35.1529 | 35.564 | 33.6334 | 34.394 | 34.4783 | 33.7757 | 34.3713 | 34.3869 | 34.4927 | 34.1472 | 34.3778 | 35.4164 | 35.7951 | 35.7004 | 35.7239 | 34.2171 | 95.3131 | 95.6879 | 94.5444
2022-09-08 00:56 | 3:06 | 18.4433 | 18.8975 | 20.7981 | 35.1227 | 34.5276 | 34.5389 | 35.4257 | 35.7495 | 36.8525 | 37.4678 | 36.7581 | 37.6438 | 34.4192 | 34.3946 | 35.0918 | 35.7806 | 36.242 | 36.561 | 37.0457 | 37.2741 | 21.9616 | 18.1624 | 93.6939 | 33.3852 | 33.939 | 35.5763 | 34.2957 | 33.8689 | 34.1298 | 35.4378 | 34.7653 | 34.6561 | 37.5003 | 36.468 | 34.1229 | 34.703 | 36.4866 | 36.8925 | 37.7284 | 36.4671 | 34.2884 | 33.5232 | 35.1276 | 35.5385 | 33.6387 | 34.3853 | 34.469 | 33.7677 | 34.3633 | 34.3754 | 34.4716 | 34.1348 | 34.3713 | 35.4299 | 35.7774 | 35.688 | 35.7128 | 34.2117 | 95.152 | 95.5542 | 94.3924
2022-09-08 00:57 | 3:07 | 18.417 | 18.9389 | 20.8241 | 34.9609 | 34.5259 | 34.5089 | 35.4185 | 35.7439 | 36.8458 | 37.4475 | 36.7539 | 37.6248 | 34.4095 | 34.3862 | 35.0721 | 35.7788 | 36.2547 | 36.5545 | 37.0489 | 37.2706 | 21.9805 | 18.1455 | 93.6336 | 33.5365 | 33.9384 | 35.5712 | 34.2757 | 33.8679 | 34.1237 | 35.4233 | 34.7565 | 34.6417 | 37.5033 | 36.4861 | 34.1251 | 34.7139 | 36.4917 | 36.8773 | 37.7274 | 36.4926 | 34.2802 | 33.5093 | 35.1204 | 35.5609 | 33.607 | 34.4028 | 34.4585 | 33.7655 | 34.3766 | 34.3833 | 34.4777 | 34.1316 | 34.3633 | 35.4161 | 35.7775 | 35.6832 | 35.7087 | 34.1928 | 94.8559 | 95.2485 | 94.1109
2022-09-08 00:57 | 3:07 | 18.3304 | 18.8319 | 20.7651 | 35.0429 | 34.5264 | 34.5118 | 35.432 | 35.7696 | 36.8613 | 37.4652 | 36.7703 | 37.6458 | 34.4173 | 34.3777 | 35.1017 | 35.7792 | 36.2462 | 36.5312 | 37.0382 | 37.2541 | 21.9765 | 18.1685 | 93.6448 | 33.5654 | 33.9257 | 35.5607 | 34.3009 | 33.857 | 34.1343 | 35.4227 | 34.7463 | 34.6517 | 37.4879 | 36.4892 | 34.1354 | 34.7005 | 36.468 | 36.8943 | 37.698 | 36.4931 | 34.29 | 33.5021 | 35.1083 | 35.5466 | 33.6139 | 34.3963 | 34.4428 | 33.7793 | 34.3783 | 34.3724 | 34.472 | 34.153 | 34.3766 | 35.4289 | 35.7932 | 35.6904 | 35.7243 | 34.2042 | 94.6105 | 94.9981 | 94.092
2022-09-08 00:57 | 3:07 | 18.2581 | 18.8133 | 20.7319 | 35.0207 | 34.5164 | 34.5142 | 35.4235 | 35.7603 | 36.8501 | 37.4678 | 36.7634 | 37.6261 | 34.408 | 34.3956 | 35.0704 | 35.7717 | 36.2516 | 36.5427 | 37.0356 | 37.2766 | 22.0102 | 18.1252 | 93.6542 | 33.4708 | 33.9454 | 35.5592 | 34.2816 | 33.8676 | 34.1389 | 35.4116 | 34.7691 | 34.6502 | 37.5065 | 36.4878 | 34.1245 | 34.6936 | 36.4861 | 36.8731 | 37.7073 | 36.4866 | 34.2844 | 33.4933 | 35.1131 | 35.5447 | 33.6102 | 34.3786 | 34.4408 | 33.7618 | 34.3802 | 34.3781 | 34.4674 | 34.121 | 34.3783 | 35.442 | 35.7896 | 35.688 | 35.7352 | 34.1949 | 94.4348 | 94.7653 | 93.9735
2022-09-08 00:57 | 3:07 | 18.2527 | 18.7419 | 20.6688 | 35.0291 | 34.5196 | 34.5238 | 35.4202 | 35.7585 | 36.8355 | 37.4596 | 36.7814 | 37.628 | 34.411 | 34.3873 | 35.0986 | 35.7936 | 36.2447 | 36.5387 | 37.0192 | 37.2552 | 22.0288 | 18.0916 | 93.619 | 33.5878 | 33.9371 | 35.5935 | 34.2884 | 33.8417 | 34.1229 | 35.4344 | 34.779 | 34.6399 | 37.5077 | 36.4913 | 34.1317 | 34.7013 | 36.4892 | 36.8741 | 37.7069 | 36.4917 | 34.281 | 33.4953 | 35.1089 | 35.534 | 33.577 | 34.3816 | 34.4549 | 33.7687 | 34.3824 | 34.3773 | 34.462 | 34.1354 | 34.3802 | 35.4015 | 35.7982 | 35.6777 | 35.7121 | 34.1979 | 94.2303 | 94.5938 | 93.7974
2022-09-08 00:57 | 3:07 | 18.3169 | 18.7458 | 20.6093 | 34.9961 | 34.5234 | 34.5067 | 35.4341 | 35.7539 | 36.8471 | 37.4372 | 36.7703 | 37.6565 | 34.3913 | 34.3965 | 35.0888 | 35.7791 | 36.2387 | 36.5532 | 37.041 | 37.269 | 22.0183 | 18.0427 | 93.5776 | 33.4272 | 33.9221 | 35.5739 | 34.2802 | 33.862 | 34.1251 | 35.4217 | 34.7697 | 34.6474 | 37.4929 | 36.4857 | 34.1174 | 34.6979 | 36.4878 | 36.885 | 37.7197 | 36.468 | 34.2923 | 33.476 | 35.0817 | 35.5109 | 33.5969 | 34.3742 | 34.4617 | 33.7565 | 34.3835 | 34.3834 | 34.4595 | 34.1319 | 34.3824 | 35.4249 | 35.773 | 35.6806 | 35.7166 | 34.184 | 94.1241 | 94.4657 | 93.811
2022-09-08 00:57 | 3:07 | 18.2355 | 18.7048 | 20.6046 | 34.9192 | 34.5318 | 34.519 | 35.4158 | 35.7609 | 36.8545 | 37.4327 | 36.7616 | 37.6524 | 34.3945 | 34.3668 | 35.089 | 35.7878 | 36.2274 | 36.5358 | 37.026 | 37.2536 | 22.0098 | 18.0596 | 93.5832 | 33.4421 | 33.9068 | 35.5935 | 34.29 | 33.8646 | 34.1354 | 35.4172 | 34.7699 | 34.6621 | 37.487 | 36.4926 | 34.1139 | 34.6973 | 36.4913 | 36.8832 | 37.7089 | 36.4861 | 34.2774 | 33.4733 | 35.0787 | 35.5249 | 33.5866 | 34.369 | 34.4611 | 33.756 | 34.3919 | 34.3858 | 34.4501 | 34.1202 | 34.3835 | 35.4016 | 35.7847 | 35.694 | 35.7229 | 34.175 | 94.0175 | 94.4001 | 93.7511
2022-09-08 00:58 | 3:07 | 18.1218 | 18.6096 | 20.5462 | 34.8644 | 34.523 | 34.5051 | 35.4031 | 35.758 | 36.8508 | 37.428 | 36.757 | 37.6358 | 34.3949 | 34.3864 | 35.0842 | 35.7784 | 36.2391 | 36.5344 | 37.0175 | 37.245 | 22.0074 | 17.9965 | 93.6251 | 33.4228 | 33.9317 | 35.5664 | 34.2844 | 33.8636 | 34.1245 | 35.4126 | 34.7731 | 34.6375 | 37.4982 | 36.4776 | 34.1356 | 34.7111 | 36.4857 | 36.8846 | 37.7003 | 36.4892 | 34.2856 | 33.4846 | 35.0765 | 35.5226 | 33.5936 | 34.3625 | 34.4674 | 33.7523 | 34.3925 | 34.3911 | 34.4713 | 34.1324 | 34.3919 | 35.4295 | 35.7799 | 35.6819 | 35.72 | 34.1673 | 93.969 | 94.3159 | 93.6775
2022-09-08 00:58 | 3:08 | 18.1597 | 18.549 | 20.4585 | 34.76 | 34.5256 | 34.5211 | 35.4186 | 35.7612 | 36.8415 | 37.4343 | 36.781 | 37.6579 | 34.401 | 34.3865 | 35.0702 | 35.7883 | 36.2214 | 36.5334 | 37.0098 | 37.255 | 21.9936 | 17.9828 | 93.6685 | 33.4218 | 33.9138 | 35.569 | 34.281 | 33.8476 | 34.1317 | 35.4101 | 34.764 | 34.648 | 37.5007 | 36.4948 | 34.1256 | 34.7134 | 36.4926 | 36.8749 | 37.7058 | 36.4878 | 34.2834 | 33.4736 | 35.0649 | 35.507 | 33.5981 | 34.3686 | 34.4669 | 33.7665 | 34.3942 | 34.3682 | 34.4616 | 34.146 | 34.3925 | 35.4234 | 35.7732 | 35.7027 | 35.7278 | 34.1857 | 93.8804 | 94.244 | 93.676
2022-09-08 00:58 | 3:08 | 18.1842 | 18.5853 | 20.4676 | 34.8254 | 34.5383 | 34.5012 | 35.4253 | 35.7379 | 36.8204 | 37.4444 | 36.7648 | 37.6471 | 34.3877 | 34.3892 | 35.088 | 35.7811 | 36.2307 | 36.55 | 37.016 | 37.2541 | 21.9726 | 17.9296 | 93.545 | 33.3712 | 33.9154 | 35.5579 | 34.2923 | 33.8497 | 34.1174 | 35.422 | 34.7814 | 34.6537 | 37.4828 | 36.4631 | 34.1334 | 34.7112 | 36.4776 | 36.8851 | 37.7089 | 36.4913 | 34.2771 | 33.4729 | 35.0903 | 35.5053 | 33.5618 | 34.3632 | 34.4645 | 33.7448 | 34.3892 | 34.3718 | 34.4672 | 34.1387 | 34.3942 | 35.4081 | 35.7818 | 35.6941 | 35.722 | 34.1651 | 93.8376 | 94.1607 | 93.618
2022-09-08 00:58 | 3:08 | 18.2123 | 18.5991 | 20.4654 | 34.8551 | 34.5317 | 34.5165 | 35.4005 | 35.7466 | 36.8445 | 37.4629 | 36.7574 | 37.654 | 34.3966 | 34.3744 | 35.0781 | 35.7692 | 36.2388 | 36.5545 | 37.0035 | 37.243 | 21.9691 | 17.8995 | 93.462 | 33.5341 | 33.9144 | 35.5612 | 34.2774 | 33.8631 | 34.1139 | 35.3935 | 34.7632 | 34.6412 | 37.4881 | 36.5089 | 34.1287 | 34.725 | 36.4948 | 36.8751 | 37.7018 | 36.4857 | 34.2832 | 33.4584 | 35.0796 | 35.5199 | 33.5746 | 34.3732 | 34.4557 | 33.746 | 34.3941 | 34.3734 | 34.4415 | 34.1116 | 34.3892 | 35.4258 | 35.7871 | 35.7076 | 35.7107 | 34.1908 | 93.7641 | 94.0856 | 93.5255
2022-09-08 00:58 | 3:08 | 18.0511 | 18.4981 | 20.4216 | 34.8832 | 34.5299 | 34.5281 | 35.4107 | 35.753 | 36.8395 | 37.4509 | 36.7734 | 37.6414 | 34.3931 | 34.3846 | 35.0635 | 35.7856 | 36.2395 | 36.5337 | 37.0218 | 37.2499 | 21.9563 | 17.9284 | 93.3086 | 33.3813 | 33.9182 | 35.5807 | 34.2856 | 33.8547 | 34.1356 | 35.4211 | 34.7737 | 34.6593 | 37.4931 | 36.5025 | 34.1342 | 34.6951 | 36.4631 | 36.8601 | 37.6962 | 36.4926 | 34.2865 | 33.4663 | 35.0871 | 35.5107 | 33.5722 | 34.3588 | 34.453 | 33.7366 | 34.4079 | 34.3861 | 34.4315 | 34.1301 | 34.3941 | 35.4428 | 35.779 | 35.7152 | 35.727 | 34.1812 | 93.7469 | 94.0365 | 93.5086
2022-09-08 00:58 | 3:08 | 18.067 | 18.4834 | 20.4401 | 34.8577 | 34.5159 | 34.497 | 35.4003 | 35.7548 | 36.8711 | 37.4544 | 36.7747 | 37.6445 | 34.42 | 34.3785 | 35.074 | 35.7853 | 36.2452 | 36.5203 | 37.0244 | 37.2424 | 21.9333 | 17.8533 | 93.2226 | 33.4257 | 33.9122 | 35.5603 | 34.2834 | 33.852 | 34.1256 | 35.4127 | 34.8066 | 34.6516 | 37.4855 | 36.4893 | 34.1165 | 34.7245 | 36.5089 | 36.8874 | 37.6893 | 36.4776 | 34.2671 | 33.4714 | 35.0732 | 35.5146 | 33.549 | 34.3777 | 34.4808 | 33.736 | 34.413 | 34.3814 | 34.4031 | 34.1163 | 34.4079 | 35.4261 | 35.8052 | 35.6925 | 35.7276 | 34.1809 | 93.7306 | 93.9806 | 93.5877
2022-09-08 00:59 | 3:09 | 17.9439 | 18.335 | 20.3443 | 34.7079 | 34.5281 | 34.5104 | 35.3967 | 35.7508 | 36.8677 | 37.4476 | 36.7853 | 37.6565 | 34.3828 | 34.3644 | 35.0767 | 35.7971 | 36.2272 | 36.5337 | 37.0075 | 37.243 | 21.9154 | 17.8359 | 93.1632 | 33.349 | 33.9069 | 35.5735 | 34.2771 | 33.8402 | 34.1334 | 35.4087 | 34.7777 | 34.6434 | 37.4969 | 36.492 | 34.1269 | 34.7371 | 36.5025 | 36.8906 | 37.712 | 36.4948 | 34.2524 | 33.474 | 35.0449 | 35.5152 | 33.55 | 34.3644 | 34.4654 | 33.7428 | 34.4139 | 34.3775 | 34.4401 | 34.1137 | 34.413 | 35.4273 | 35.7846 | 35.6931 | 35.7298 | 34.1811 | 93.6878 | 93.9152 | 93.5176
2022-09-08 00:59 | 3:09 | 17.9518 | 18.3601 | 20.31 | 34.8714 | 34.5265 | 34.5161 | 35.4034 | 35.762 | 36.8539 | 37.4398 | 36.7882 | 37.6546 | 34.3939 | 34.3547 | 35.0746 | 35.7921 | 36.2152 | 36.5468 | 37.0075 | 37.2548 | 21.9013 | 17.79 | 93.1606 | 33.3682 | 33.8937 | 35.5716 | 34.2832 | 33.8327 | 34.1287 | 35.4161 | 34.7729 | 34.6586 | 37.4928 | 36.4912 | 34.114 | 34.7208 | 36.4893 | 36.8756 | 37.6832 | 36.4631 | 34.2663 | 33.4389 | 35.0329 | 35.5114 | 33.5342 | 34.3685 | 34.4572 | 33.7177 | 34.4005 | 34.392 | 34.4203 | 34.1096 | 34.4139 | 35.4306 | 35.7814 | 35.7229 | 35.7165 | 34.1643 | 93.6855 | 93.8602 | 93.4869
2022-09-08 00:59 | 3:09 | 17.9427 | 18.332 | 20.3043 | 34.7321 | 34.5041 | 34.5158 | 35.4024 | 35.7598 | 36.8375 | 37.4443 | 36.7713 | 37.6672 | 34.4055 | 34.3855 | 35.0806 | 35.7977 | 36.2339 | 36.5287 | 36.9934 | 37.2648 | 21.8884 | 17.794 | 93.1945 | 33.2659 | 33.9084 | 35.554 | 34.2865 | 33.8512 | 34.1342 | 35.4271 | 34.78 | 34.6461 | 37.4927 | 36.483 | 34.1343 | 34.702 | 36.492 | 36.8824 | 37.6878 | 36.5089 | 34.2718 | 33.4452 | 35.0292 | 35.4999 | 33.532 | 34.3754 | 34.4861 | 33.6911 | 34.4228 | 34.3765 | 34.4203 | 34.1097 | 34.4005 | 35.423 | 35.7973 | 35.7119 | 35.7314 | 34.1691 | 93.5288 | 93.767 | 93.3689
2022-09-08 00:59 | 3:09 | 17.9276 | 18.3381 | 20.2624 | 34.7991 | 34.5163 | 34.5082 | 35.3807 | 35.7666 | 36.8421 | 37.4386 | 36.7973 | 37.6513 | 34.3849 | 34.3825 | 35.0704 | 35.7885 | 36.2301 | 36.5191 | 37.0044 | 37.2375 | 21.8971 | 17.7462 | 93.1819 | 33.3427 | 33.9001 | 35.5648 | 34.2671 | 33.8391 | 34.1165 | 35.4129 | 34.7606 | 34.6645 | 37.4923 | 36.499 | 34.1073 | 34.718 | 36.4912 | 36.8832 | 37.6944 | 36.5025 | 34.2763 | 33.4344 | 35.048 | 35.4742 | 33.5509 | 34.3604 | 34.4672 | 33.7277 | 34.428 | 34.3869 | 34.4028 | 34.1073 | 34.4228 | 35.4247 | 35.7898 | 35.7159 | 35.7268 | 34.1681 | 93.4489 | 93.6906 | 93.329
2022-09-08 00:59 | 3:09 | 17.8829 | 18.3391 | 20.2204 | 34.7635 | 34.5282 | 34.5116 | 35.4063 | 35.7651 | 36.8545 | 37.4586 | 36.7736 | 37.6612 | 34.4143 | 34.3695 | 35.072 | 35.7949 | 36.2221 | 36.521 | 36.9954 | 37.2552 | 21.854 | 17.7152 | 93.0192 | 33.2789 | 33.9022 | 35.5466 | 34.2524 | 33.8303 | 34.1269 | 35.4117 | 34.7818 | 34.6638 | 37.5 | 36.5074 | 34.123 | 34.7013 | 36.483 | 36.8816 | 37.6976 | 36.4893 | 34.275 | 33.4156 | 35.0639 | 35.5082 | 33.5182 | 34.3679 | 34.4714 | 33.7213 | 34.4127 | 34.3803 | 34.41 | 34.1178 | 34.428 | 35.45 | 35.769 | 35.7033 | 35.7432 | 34.1734 | 93.3524 | 93.575 | 93.1916
2022-09-08 00:59 | 3:09 | 17.8804 | 18.2518 | 20.1743 | 34.7117 | 34.5365 | 34.5188 | 35.3868 | 35.7538 | 36.8339 | 37.4423 | 36.7863 | 37.6608 | 34.3972 | 34.3678 | 35.0772 | 35.797 | 36.2417 | 36.5221 | 36.9942 | 37.2396 | 21.8622 | 17.7543 | 92.9132 | 33.4551 | 33.9009 | 35.5686 | 34.2663 | 33.8605 | 34.114 | 35.4048 | 34.7912 | 34.6611 | 37.499 | 36.4892 | 34.1098 | 34.7157 | 36.499 | 36.8845 | 37.6889 | 36.492 | 34.2641 | 33.4354 | 35.0497 | 35.5048 | 33.5127 | 34.3635 | 34.4702 | 33.7002 | 34.4023 | 34.3792 | 34.4062 | 34.1081 | 34.4127 | 35.4433 | 35.7882 | 35.7234 | 35.7303 | 34.1682 | 93.2691 | 93.4985 | 93.156
2022-09-08 01:00 | 3:09 | 17.8289 | 18.2234 | 20.154 | 34.7165 | 34.5052 | 34.5005 | 35.4049 | 35.7461 | 36.8417 | 37.4484 | 36.7966 | 37.6698 | 34.3841 | 34.3802 | 35.0608 | 35.7999 | 36.2071 | 36.535 | 37.0006 | 37.2525 | 21.8611 | 17.7301 | 92.7654 | 33.4839 | 33.9039 | 35.5741 | 34.2718 | 33.8244 | 34.1343 | 35.407 | 34.7602 | 34.6359 | 37.5048 | 36.4876 | 34.1058 | 34.7125 | 36.5074 | 36.8913 | 37.6985 | 36.4912 | 34.2591 | 33.4212 | 35.0493 | 35.5104 | 33.5289 | 34.3662 | 34.468 | 33.7188 | 34.421 | 34.3854 | 34.4086 | 34.1158 | 34.4023 | 35.4374 | 35.781 | 35.7336 | 35.7275 | 34.1694 | 93.2399 | 93.4381 | 93.1435
2022-09-08 01:00 | 3:10 | 17.8039 | 18.2142 | 20.1319 | 34.6616 | 34.5077 | 34.5119 | 35.3877 | 35.7649 | 36.835 | 37.4637 | 36.7987 | 37.6612 | 34.3941 | 34.3605 | 35.0513 | 35.7965 | 36.2288 | 36.5296 | 36.9999 | 37.2477 | 21.8397 | 17.67 | 92.6981 | 33.2483 | 33.9106 | 35.5652 | 34.2763 | 33.8352 | 34.1073 | 35.3846 | 34.7542 | 34.655 | 37.4871 | 36.4892 | 34.1253 | 34.7129 | 36.4892 | 36.8847 | 37.6965 | 36.483 | 34.2811 | 33.4363 | 35.0315 | 35.4969 | 33.5204 | 34.3678 | 34.4695 | 33.7132 | 34.4118 | 34.3719 | 34.3894 | 34.0988 | 34.421 | 35.432 | 35.7876 | 35.7294 | 35.7235 | 34.1617 | 93.1569 | 93.3501 | 93.0986
2022-09-08 01:00 | 3:10 | 17.7839 | 18.1975 | 20.1137 | 34.7169 | 34.5046 | 34.5032 | 35.3858 | 35.7462 | 36.839 | 37.437 | 36.79 | 37.6763 | 34.4037 | 34.3851 | 35.0779 | 35.7897 | 36.2136 | 36.5268 | 36.9904 | 37.2301 | 21.8203 | 17.6244 | 92.6169 | 33.3891 | 33.8946 | 35.5709 | 34.275 | 33.8458 | 34.123 | 35.3821 | 34.787 | 34.6625 | 37.4862 | 36.4868 | 34.1251 | 34.7234 | 36.4876 | 36.8886 | 37.6875 | 36.499 | 34.2467 | 33.4179 | 35.0417 | 35.4966 | 33.4988 | 34.3684 | 34.4764 | 33.7139 | 34.4243 | 34.3863 | 34.3925 | 34.1215 | 34.4118 | 35.4435 | 35.7808 | 35.7377 | 35.7452 | 34.1936 | 93.0345 | 93.243 | 92.9704
2022-09-08 01:00 | 3:10 | 17.7149 | 18.1363 | 20.0645 | 34.6356 | 34.5253 | 34.5035 | 35.3961 | 35.7533 | 36.8563 | 37.4126 | 36.7873 | 37.6691 | 34.3853 | 34.373 | 35.0606 | 35.7882 | 36.2197 | 36.521 | 36.9994 | 37.2416 | 21.7922 | 17.6048 | 92.487 | 33.3483 | 33.8884 | 35.5739 | 34.2641 | 33.8347 | 34.1098 | 35.4061 | 34.7844 | 34.665 | 37.5012 | 36.4933 | 34.1144 | 34.7276 | 36.4892 | 36.8914 | 37.6775 | 36.5074 | 34.2609 | 33.4041 | 35.0449 | 35.5067 | 33.4825 | 34.3735 | 34.4903 | 33.6934 | 34.4173 | 34.3726 | 34.3826 | 34.1053 | 34.4243 | 35.45 | 35.7792 | 35.7178 | 35.7346 | 34.1587 | 92.9613 | 93.1388 | 92.9272
2022-09-08 01:00 | 3:10 | 17.7381 | 18.146 | 20.0453 | 34.7591 | 34.4931 | 34.5203 | 35.3747 | 35.7616 | 36.859 | 37.4499 | 36.7978 | 37.6768 | 34.3991 | 34.387 | 35.0591 | 35.8057 | 36.2284 | 36.5206 | 37.012 | 37.2475 | 21.757 | 17.5981 | 92.3376 | 33.4619 | 33.8898 | 35.5663 | 34.2591 | 33.8351 | 34.1058 | 35.3917 | 34.7817 | 34.6796 | 37.5014 | 36.4978 | 34.1216 | 34.7187 | 36.4868 | 36.885 | 37.6792 | 36.4892 | 34.251 | 33.4164 | 35.0324 | 35.4724 | 33.5056 | 34.3545 | 34.4759 | 33.6896 | 34.4247 | 34.3944 | 34.3957 | 34.1117 | 34.4173 | 35.4349 | 35.783 | 35.7301 | 35.739 | 34.1865 | 92.818 | 92.9825 | 92.8362
2022-09-08 01:00 | 3:10 | 17.7085 | 18.1153 | 20.0868 | 34.618 | 34.502 | 34.5204 | 35.3736 | 35.7379 | 36.8366 | 37.4306 | 36.7989 | 37.701 | 34.3877 | 34.3648 | 35.063 | 35.8025 | 36.2227 | 36.5056 | 36.9922 | 37.2387 | 21.7561 | 17.551 | 92.4019 | 33.2114 | 33.8883 | 35.5671 | 34.2811 | 33.8265 | 34.1253 | 35.3809 | 34.7849 | 34.6662 | 37.5005 | 36.4806 | 34.1049 | 34.717 | 36.4933 | 36.8819 | 37.6952 | 36.4876 | 34.2542 | 33.4106 | 35.0184 | 35.4886 | 33.4928 | 34.3578 | 34.466 | 33.6897 | 34.4217 | 34.385 | 34.4073 | 34.1214 | 34.4247 | 35.4598 | 35.7733 | 35.7204 | 35.7421 | 34.1823 | 92.7646 | 92.9204 | 92.81
2022-09-08 01:01 | 3:11 | 17.6662 | 18.0974 | 20.0407 | 34.6931 | 34.4957 | 34.5053 | 35.3728 | 35.7552 | 36.851 | 37.434 | 36.8019 | 37.6725 | 34.3896 | 34.3713 | 35.0674 | 35.7954 | 36.2063 | 36.5275 | 36.9834 | 37.245 | 21.7187 | 17.5422 | 92.405 | 33.3638 | 33.8907 | 35.5716 | 34.2467 | 33.8289 | 34.1251 | 35.3944 | 34.7798 | 34.6676 | 37.4958 | 36.4685 | 34.1036 | 34.7041 | 36.4978 | 36.8909 | 37.6781 | 36.4892 | 34.2392 | 33.3994 | 35.0249 | 35.4752 | 33.4695 | 34.3728 | 34.4876 | 33.7114 | 34.426 | 34.3849 | 34.3946 | 34.112 | 34.4217 | 35.4752 | 35.7792 | 35.7222 | 35.7492 | 34.1842 | 92.5999 | 92.7609 | 92.6811
2022-09-08 01:01 | 3:11 | 17.6844 | 18.1197 | 20.0353 | 34.6781 | 34.4831 | 34.5102 | 35.3705 | 35.772 | 36.851 | 37.4446 | 36.7908 | 37.6825 | 34.3913 | 34.3747 | 35.0649 | 35.7958 | 36.2218 | 36.516 | 37.0016 | 37.25 | 21.7134 | 17.561 | 92.4655 | 33.3611 | 33.8848 | 35.5742 | 34.2609 | 33.837 | 34.1144 | 35.3844 | 34.7822 | 34.6558 | 37.5011 | 36.4894 | 34.1251 | 34.7241 | 36.4806 | 36.896 | 37.68 | 36.4868 | 34.2469 | 33.3982 | 35.0166 | 35.473 | 33.4727 | 34.3603 | 34.484 | 33.6921 | 34.4297 | 34.4131 | 34.3862 | 34.1286 | 34.426 | 35.4542 | 35.7773 | 35.7259 | 35.7421 | 34.1805 | 92.4595 | 92.594 | 92.5762
2022-09-08 01:01 | 3:11 | 17.6768 | 18.057 | 20.0341 | 34.6273 | 34.4669 | 34.4975 | 35.3832 | 35.7413 | 36.8489 | 37.4304 | 36.8024 | 37.6723 | 34.3937 | 34.3605 | 35.0393 | 35.8132 | 36.2225 | 36.5265 | 36.9944 | 37.2358 | 21.7133 | 17.5466 | 92.4403 | 33.1513 | 33.8716 | 35.5788 | 34.251 | 33.8303 | 34.1216 | 35.4004 | 34.786 | 34.672 | 37.5026 | 36.4751 | 34.1059 | 34.7128 | 36.4685 | 36.8843 | 37.6782 | 36.4933 | 34.2494 | 33.3678 | 35.0126 | 35.4788 | 33.4606 | 34.3712 | 34.4972 | 33.6888 | 34.441 | 34.394 | 34.3777 | 34.1062 | 34.4297 | 35.428 | 35.7773 | 35.7387 | 35.7363 | 34.1646 | 92.3657 | 92.5354 | 92.514
2022-09-08 01:01 | 3:11 | 17.6022 | 17.9969 | 19.9617 | 34.624 | 34.4927 | 34.5025 | 35.3629 | 35.748 | 36.8354 | 37.4489 | 36.8046 | 37.6827 | 34.382 | 34.3467 | 35.0721 | 35.7944 | 36.1963 | 36.516 | 36.9986 | 37.2371 | 21.678 | 17.4527 | 92.5676 | 33.3188 | 33.899 | 35.5343 | 34.2542 | 33.8321 | 34.1049 | 35.3845 | 34.7818 | 34.643 | 37.5059 | 36.4693 | 34.1086 | 34.7213 | 36.4894 | 36.8692 | 37.6958 | 36.4978 | 34.2049 | 33.3746 | 35.02 | 35.4655 | 33.4631 | 34.3591 | 34.4734 | 33.6604 | 34.4365 | 34.3927 | 34.3956 | 34.1194 | 34.441 | 35.4618 | 35.7885 | 35.7377 | 35.744 | 34.1875 | 92.2133 | 92.3984 | 92.2928
2022-09-08 01:01 | 3:11 | 17.5055 | 17.9405 | 19.8637 | 34.6644 | 34.4716 | 34.5076 | 35.379 | 35.7363 | 36.85 | 37.4372 | 36.7972 | 37.6778 | 34.3771 | 34.3521 | 35.0493 | 35.7755 | 36.2102 | 36.5182 | 36.9898 | 37.2535 | 21.6413 | 17.4693 | 92.5622 | 33.1289 | 33.8759 | 35.5444 | 34.2392 | 33.8364 | 34.1036 | 35.3961 | 34.7784 | 34.6628 | 37.4785 | 36.4597 | 34.0984 | 34.7143 | 36.4751 | 36.8877 | 37.6732 | 36.4806 | 34.2249 | 33.3939 | 35.016 | 35.4692 | 33.4833 | 34.3628 | 34.4966 | 33.6729 | 34.4279 | 34.4089 | 34.3873 | 34.1129 | 34.4365 | 35.4801 | 35.7818 | 35.7426 | 35.7691 | 34.1719 | 92.1229 | 92.2829 | 92.3917
2022-09-08 01:01 | 3:11 | 17.5877 | 17.9113 | 19.8266 | 34.5737 | 34.4777 | 34.4726 | 35.3546 | 35.7665 | 36.8271 | 37.4416 | 36.7886 | 37.6773 | 34.411 | 34.365 | 35.0578 | 35.7823 | 36.1983 | 36.5058 | 36.9823 | 37.2242 | 21.6182 | 17.5329 | 92.6124 | 33.2504 | 33.8719 | 35.5519 | 34.2469 | 33.8228 | 34.1251 | 35.3993 | 34.7824 | 34.6743 | 37.5042 | 36.4794 | 34.092 | 34.7013 | 36.4693 | 36.8989 | 37.678 | 36.4685 | 34.2173 | 33.3667 | 35.0111 | 35.4653 | 33.4306 | 34.3625 | 34.4726 | 33.6636 | 34.437 | 34.4066 | 34.3965 | 34.1023 | 34.4279 | 35.4713 | 35.7756 | 35.7288 | 35.7512 | 34.1545 | 92.2491 | 92.3622 | 92.5025
2022-09-08 01:02 | 3:11 | 17.5444 | 17.9358 | 19.817 | 34.6297 | 34.472 | 34.4928 | 35.3688 | 35.7416 | 36.8236 | 37.4609 | 36.7825 | 37.6958 | 34.3903 | 34.376 | 35.0654 | 35.802 | 36.1803 | 36.5066 | 36.9826 | 37.2276 | 21.5939 | 17.4702 | 92.6209 | 33.3856 | 33.8673 | 35.5491 | 34.2494 | 33.836 | 34.1059 | 35.3848 | 34.775 | 34.6626 | 37.5046 | 36.4581 | 34.0956 | 34.715 | 36.4597 | 36.8818 | 37.6917 | 36.4894 | 34.2307 | 33.3631 | 34.9837 | 35.465 | 33.435 | 34.3835 | 34.4718 | 33.6898 | 34.4252 | 34.4207 | 34.3668 | 34.116 | 34.437 | 35.4537 | 35.7876 | 35.7276 | 35.7535 | 34.1733 | 92.3362 | 92.4033 | 92.6011
2022-09-08 01:02 | 3:12 | 17.4579 | 17.8459 | 19.8298 | 34.5814 | 34.4674 | 34.4701 | 35.3605 | 35.7393 | 36.8387 | 37.4584 | 36.7819 | 37.6945 | 34.3847 | 34.3753 | 35.0262 | 35.7801 | 36.1948 | 36.5194 | 36.9713 | 37.2288 | 21.5108 | 17.4045 | 92.6657 | 33.3091 | 33.8802 | 35.5314 | 34.2049 | 33.813 | 34.1086 | 35.3865 | 34.7683 | 34.6628 | 37.4861 | 36.467 | 34.1022 | 34.7106 | 36.4794 | 36.8917 | 37.6827 | 36.4751 | 34.2159 | 33.3794 | 35.0059 | 35.4507 | 33.4246 | 34.3499 | 34.4814 | 33.6737 | 34.4519 | 34.409 | 34.3864 | 34.0912 | 34.4252 | 35.4838 | 35.7702 | 35.7314 | 35.7498 | 34.1664 | 92.3926 | 92.494 | 92.5055
2022-09-08 01:02 | 3:12 | 17.4573 | 17.8852 | 19.8313 | 34.6212 | 34.462 | 34.4756 | 35.3584 | 35.7531 | 36.8427 | 37.4354 | 36.7944 | 37.6783 | 34.3867 | 34.3558 | 35.0372 | 35.7731 | 36.1833 | 36.5169 | 36.9741 | 37.2148 | 21.5128 | 17.3945 | 92.7772 | 33.0111 | 33.8665 | 35.5318 | 34.2249 | 33.8113 | 34.0984 | 35.3828 | 34.7831 | 34.6481 | 37.4863 | 36.4877 | 34.0941 | 34.7063 | 36.4581 | 36.8928 | 37.6683 | 36.4693 | 34.2141 | 33.3518 | 34.989 | 35.4593 | 33.3958 | 34.3518 | 34.4913 | 33.6702 | 34.4396 | 34.411 | 34.3865 | 34.0997 | 34.4519 | 35.4702 | 35.7755 | 35.7301 | 35.7502 | 34.1654 | 92.4824 | 92.5667 | 92.6229
2022-09-08 01:02 | 3:12 | 17.4622 | 17.8411 | 19.8405 | 34.4344 | 34.4595 | 34.4898 | 35.3632 | 35.7503 | 36.847 | 37.4522 | 36.7852 | 37.6874 | 34.3794 | 34.3558 | 35.0569 | 35.7877 | 36.169 | 36.5008 | 36.9836 | 37.2483 | 21.4612 | 17.3687 | 92.8489 | 33.066 | 33.8794 | 35.5268 | 34.2173 | 33.836 | 34.092 | 35.3938 | 34.778 | 34.6567 | 37.4776 | 36.4596 | 34.0895 | 34.692 | 36.467 | 36.8624 | 37.6721 | 36.4597 | 34.2022 | 33.3479 | 34.9882 | 35.4498 | 33.397 | 34.3533 | 34.4938 | 33.6546 | 34.4511 | 34.4179 | 34.3892 | 34.1068 | 34.4396 | 35.4675 | 35.7548 | 35.7149 | 35.7285 | 34.1724 | 92.5524 | 92.6617 | 92.7703
2022-09-08 01:02 | 3:12 | 17.4602 | 17.7975 | 19.8136 | 34.6186 | 34.4501 | 34.4908 | 35.3449 | 35.7283 | 36.8443 | 37.4448 | 36.7909 | 37.6878 | 34.3867 | 34.3663 | 35.0471 | 35.7712 | 36.1698 | 36.4859 | 36.9887 | 37.2412 | 21.4542 | 17.3506 | 92.8421 | 33.2856 | 33.8486 | 35.5272 | 34.2307 | 33.8007 | 34.0956 | 35.3989 | 34.7575 | 34.642 | 37.493 | 36.4354 | 34.0998 | 34.7087 | 36.4877 | 36.877 | 37.6651 | 36.4794 | 34.2067 | 33.3399 | 34.9899 | 35.4169 | 33.4072 | 34.3676 | 34.4729 | 33.6316 | 34.4442 | 34.3964 | 34.3744 | 34.0913 | 34.4511 | 35.4657 | 35.7479 | 35.7232 | 35.7549 | 34.1749 | 92.7157 | 92.8029 | 92.8948
2022-09-08 01:02 | 3:12 | 17.3945 | 17.7725 | 19.7742 | 34.5151 | 34.4713 | 34.4969 | 35.3495 | 35.7338 | 36.8296 | 37.4488 | 36.7755 | 37.6738 | 34.3824 | 34.3631 | 35.0259 | 35.7724 | 36.1531 | 36.5065 | 36.9609 | 37.2423 | 21.436 | 17.3165 | 92.9514 | 33.0842 | 33.8644 | 35.5145 | 34.2159 | 33.8033 | 34.1022 | 35.3924 | 34.7665 | 34.6372 | 37.4915 | 36.4408 | 34.0885 | 34.7082 | 36.4596 | 36.867 | 37.6726 | 36.4581 | 34.2089 | 33.3497 | 34.9771 | 35.4416 | 33.3881 | 34.3614 | 34.4853 | 33.6385 | 34.4433 | 34.4229 | 34.3846 | 34.0796 | 34.4442 | 35.4498 | 35.7596 | 35.7103 | 35.7414 | 34.1848 | 92.7891 | 92.9037 | 92.9094
2022-09-08 01:03 | 3:13 | 17.3936 | 17.7551 | 19.76 | 34.5406 | 34.4616 | 34.4728 | 35.3352 | 35.7378 | 36.8366 | 37.4662 | 36.7803 | 37.663 | 34.369 | 34.3711 | 35.0471 | 35.7561 | 36.1788 | 36.5031 | 36.9457 | 37.2244 | 21.3961 | 17.3056 | 92.9868 | 33.1942 | 33.8484 | 35.5158 | 34.2141 | 33.8089 | 34.0941 | 35.39 | 34.7691 | 34.6436 | 37.4733 | 36.4261 | 34.0919 | 34.678 | 36.4354 | 36.8709 | 37.6792 | 36.467 | 34.1987 | 33.3384 | 34.9816 | 35.4183 | 33.39 | 34.3413 | 34.5006 | 33.6302 | 34.4596 | 34.4296 | 34.3785 | 34.0943 | 34.4433 | 35.4592 | 35.758 | 35.746 | 35.7434 | 34.1482 | 92.8654 | 93.0271 | 92.91
2022-09-08 01:03 | 3:13 | 17.3866 | 17.8138 | 19.7815 | 34.5592 | 34.4672 | 34.4782 | 35.3298 | 35.7226 | 36.822 | 37.4317 | 36.7972 | 37.6723 | 34.3826 | 34.3757 | 35.0318 | 35.779 | 36.165 | 36.5003 | 36.9721 | 37.2199 | 21.4017 | 17.2987 | 93.0503 | 33.2058 | 33.8511 | 35.5272 | 34.2022 | 33.8267 | 34.0895 | 35.4032 | 34.7767 | 34.6531 | 37.4875 | 36.4224 | 34.0891 | 34.7044 | 36.4408 | 36.8492 | 37.671 | 36.4877 | 34.2025 | 33.3234 | 34.9694 | 35.4104 | 33.3613 | 34.3613 | 34.4899 | 33.654 | 34.4457 | 34.4419 | 34.3644 | 34.077 | 34.4596 | 35.4547 | 35.7395 | 35.7227 | 35.7613 | 34.1477 | 92.9768 | 93.1523 | 92.9113
2022-09-08 01:03 | 3:13 | 17.399 | 17.7815 | 19.7764 | 34.4132 | 34.4415 | 34.4806 | 35.351 | 35.7307 | 36.8316 | 37.4411 | 36.7857 | 37.6849 | 34.3901 | 34.361 | 35.0267 | 35.7613 | 36.1597 | 36.493 | 36.9453 | 37.2308 | 21.3943 | 17.3437 | 93.0734 | 33.124 | 33.8583 | 35.5112 | 34.2067 | 33.7954 | 34.0998 | 35.3976 | 34.7654 | 34.6169 | 37.4753 | 36.438 | 34.09 | 34.6941 | 36.4261 | 36.8783 | 37.6738 | 36.4596 | 34.1955 | 33.3339 | 34.9494 | 35.4102 | 33.3554 | 34.3661 | 34.4851 | 33.653 | 34.4453 | 34.44 | 34.3547 | 34.0674 | 34.4457 | 35.4634 | 35.7626 | 35.7508 | 35.7424 | 34.1657 | 93.0429 | 93.3108 | 92.9959
2022-09-08 01:03 | 3:13 | 17.495 | 17.8678 | 19.8012 | 34.5561 | 34.4315 | 34.477 | 35.3411 | 35.7323 | 36.8226 | 37.427 | 36.7818 | 37.6778 | 34.3802 | 34.3565 | 35.0233 | 35.7543 | 36.1677 | 36.4809 | 36.9643 | 37.2359 | 21.4041 | 17.343 | 93.2295 | 33.2034 | 33.8552 | 35.4991 | 34.2089 | 33.7777 | 34.0885 | 35.3782 | 34.7737 | 34.6379 | 37.4967 | 36.4503 | 34.0789 | 34.6906 | 36.4224 | 36.8751 | 37.6728 | 36.4354 | 34.181 | 33.3158 | 34.9552 | 35.4266 | 33.3691 | 34.3659 | 34.4887 | 33.6233 | 34.4519 | 34.4337 | 34.3855 | 34.0831 | 34.4453 | 35.4678 | 35.755 | 35.7396 | 35.7529 | 34.1494 | 93.1837 | 93.4087 | 93.1569
2022-09-08 01:03 | 3:13 | 17.4795 | 17.7832 | 19.7565 | 34.4754 | 34.4031 | 34.4503 | 35.3324 | 35.7306 | 36.8254 | 37.4601 | 36.7707 | 37.6661 | 34.3905 | 34.3704 | 35.0345 | 35.7619 | 36.1683 | 36.4762 | 36.9387 | 37.228 | 21.3759 | 17.3044 | 93.3521 | 33.0826 | 33.839 | 35.5036 | 34.1987 | 33.804 | 34.0919 | 35.3806 | 34.7503 | 34.642 | 37.4913 | 36.4205 | 34.0759 | 34.7039 | 36.438 | 36.8792 | 37.6637 | 36.4408 | 34.1841 | 33.3097 | 34.9485 | 35.4054 | 33.357 | 34.361 | 34.4995 | 33.6248 | 34.4597 | 34.4416 | 34.3825 | 34.0897 | 34.4519 | 35.4467 | 35.7565 | 35.7289 | 35.7375 | 34.1641 | 93.2767 | 93.5169 | 93.1637
2022-09-08 01:03 | 3:13 | 17.3196 | 17.6983 | 19.6886 | 34.4434 | 34.4401 | 34.4645 | 35.3254 | 35.7285 | 36.8137 | 37.4418 | 36.7773 | 37.6698 | 34.3869 | 34.3687 | 35.0185 | 35.7716 | 36.1353 | 36.4763 | 36.9555 | 37.2324 | 21.3441 | 17.31 | 93.4188 | 33.196 | 33.8618 | 35.4985 | 34.2025 | 33.7959 | 34.0891 | 35.4026 | 34.7348 | 34.6384 | 37.4756 | 36.4402 | 34.0912 | 34.6919 | 36.4503 | 36.8762 | 37.672 | 36.4261 | 34.1923 | 33.3207 | 34.9425 | 35.4106 | 33.3516 | 34.3587 | 34.4841 | 33.611 | 34.4354 | 34.456 | 34.3695 | 34.0879 | 34.4597 | 35.4597 | 35.7718 | 35.7365 | 35.7462 | 34.1458 | 93.3904 | 93.6356 | 93.2664
2022-09-08 01:04 | 3:14 | 17.4624 | 17.7003 | 19.6923 | 34.4327 | 34.4203 | 34.4708 | 35.3113 | 35.7255 | 36.8101 | 37.4631 | 36.7859 | 37.6866 | 34.3754 | 34.3704 | 35.0207 | 35.7628 | 36.1408 | 36.4774 | 36.9472 | 37.246 | 21.3214 | 17.2633 | 93.6096 | 33.1289 | 33.8245 | 35.5032 | 34.1955 | 33.7979 | 34.09 | 35.3909 | 34.7516 | 34.6188 | 37.4809 | 36.4165 | 34.0709 | 34.6861 | 36.4205 | 36.8624 | 37.6723 | 36.4224 | 34.1837 | 33.2983 | 34.955 | 35.3904 | 33.3361 | 34.3718 | 34.4864 | 33.6194 | 34.465 | 34.4223 | 34.3678 | 34.0764 | 34.4354 | 35.4702 | 35.7347 | 35.7422 | 35.7616 | 34.1464 | 93.4773 | 93.7575 | 93.3654
2022-09-08 01:04 | 3:14 | 17.4569 | 17.6851 | 19.69 | 34.4231 | 34.4203 | 34.4442 | 35.3205 | 35.7184 | 36.8271 | 37.4377 | 36.7723 | 37.6732 | 34.3833 | 34.3681 | 35.0173 | 35.7672 | 36.1556 | 36.468 | 36.9365 | 37.2319 | 21.2938 | 17.262 | 93.6705 | 33.1246 | 33.8323 | 35.5035 | 34.181 | 33.7825 | 34.0789 | 35.3944 | 34.753 | 34.6344 | 37.465 | 36.4389 | 34.0716 | 34.6878 | 36.4402 | 36.8616 | 37.6641 | 36.438 | 34.1879 | 33.2868 | 34.9315 | 35.4034 | 33.353 | 34.3258 | 34.4901 | 33.6007 | 34.4532 | 34.4529 | 34.3802 | 34.0921 | 34.465 | 35.4583 | 35.7354 | 35.7532 | 35.758 | 34.1325 | 93.6177 | 93.947 | 93.4517
2022-09-08 01:04 | 3:14 | 17.5139 | 17.7154 | 19.685 | 34.3571 | 34.4028 | 34.4596 | 35.3346 | 35.7382 | 36.8409 | 37.4369 | 36.7878 | 37.6627 | 34.3724 | 34.3673 | 35.0313 | 35.7775 | 36.1416 | 36.4795 | 36.9425 | 37.2244 | 21.2949 | 17.2885 | 93.7892 | 33.0931 | 33.8358 | 35.5196 | 34.1841 | 33.7889 | 34.0759 | 35.386 | 34.7571 | 34.623 | 37.4548 | 36.425 | 34.0639 | 34.702 | 36.4165 | 36.8771 | 37.6765 | 36.4503 | 34.1661 | 33.2941 | 34.9193 | 35.384 | 33.3346 | 34.368 | 34.4906 | 33.6177 | 34.4507 | 34.4382 | 34.3605 | 34.0765 | 34.4532 | 35.4794 | 35.7501 | 35.7543 | 35.7446 | 34.1191 | 93.842 | 94.1582 | 93.6563
2022-09-08 01:04 | 3:14 | 17.3971 | 17.7132 | 19.7124 | 34.3272 | 34.41 | 34.4464 | 35.301 | 35.7217 | 36.8224 | 37.4519 | 36.7683 | 37.6658 | 34.3781 | 34.3464 | 35.0174 | 35.7446 | 36.1367 | 36.4682 | 36.9376 | 37.2284 | 21.2678 | 17.2366 | 93.8887 | 33.1285 | 33.8188 | 35.4997 | 34.1923 | 33.802 | 34.0912 | 35.3725 | 34.7334 | 34.6203 | 37.4687 | 36.415 | 34.0738 | 34.6887 | 36.4389 | 36.8498 | 37.6624 | 36.4205 | 34.157 | 33.2674 | 34.9247 | 35.4018 | 33.3258 | 34.3634 | 34.4638 | 33.614 | 34.458 | 34.4355 | 34.3851 | 34.0552 | 34.4507 | 35.4693 | 35.7346 | 35.7358 | 35.7416 | 34.1252 | 94.0388 | 94.3503 | 93.7926
2022-09-08 01:04 | 3:14 | 17.3307 | 17.6855 | 19.6984 | 34.3351 | 34.4062 | 34.4563 | 35.3091 | 35.7208 | 36.828 | 37.4363 | 36.7712 | 37.6646 | 34.3773 | 34.3669 | 35.0283 | 35.7673 | 36.1343 | 36.4698 | 36.9409 | 37.2284 | 21.2517 | 17.2287 | 94.054 | 33.0441 | 33.8431 | 35.482 | 34.1837 | 33.7989 | 34.0709 | 35.3834 | 34.7527 | 34.6224 | 37.4699 | 36.4267 | 34.0862 | 34.6834 | 36.425 | 36.8772 | 37.6701 | 36.4402 | 34.1534 | 33.2759 | 34.915 | 35.3743 | 33.3242 | 34.3498 | 34.4935 | 33.6007 | 34.4474 | 34.4299 | 34.373 | 34.0738 | 34.458 | 35.456 | 35.7486 | 35.7614 | 35.7239 | 34.1498 | 94.2069 | 94.5211 | 93.855
2022-09-08 01:04 | 3:14 | 17.2793 | 17.6207 | 19.6492 | 34.3838 | 34.4086 | 34.4496 | 35.3054 | 35.7166 | 36.829 | 37.4273 | 36.7784 | 37.6689 | 34.3834 | 34.3738 | 35.0139 | 35.7473 | 36.1316 | 36.4889 | 36.9446 | 37.2327 | 21.2473 | 17.1988 | 94.1727 | 33.1215 | 33.8428 | 35.4934 | 34.1879 | 33.7812 | 34.0716 | 35.372 | 34.7461 | 34.6205 | 37.4646 | 36.4289 | 34.0808 | 34.6793 | 36.415 | 36.8681 | 37.6608 | 36.4165 | 34.1765 | 33.2704 | 34.907 | 35.3792 | 33.3069 | 34.3538 | 34.4833 | 33.6102 | 34.4783 | 34.443 | 34.387 | 34.048 | 34.4474 | 35.4796 | 35.7403 | 35.7451 | 35.7373 | 34.1134 | 94.3156 | 94.7267 | 93.9815
2022-09-08 01:05 | 3:14 | 17.2581 | 17.6232 | 19.6254 | 34.4115 | 34.3894 | 34.433 | 35.2938 | 35.7228 | 36.8273 | 37.4527 | 36.7703 | 37.6631 | 34.3858 | 34.3554 | 35.0282 | 35.7462 | 36.1253 | 36.4639 | 36.9223 | 37.2146 | 21.2353 | 17.181 | 94.185 | 33.1416 | 33.8167 | 35.4752 | 34.1661 | 33.7878 | 34.0639 | 35.38 | 34.7503 | 34.6193 | 37.462 | 36.4193 | 34.0676 | 34.6784 | 36.4267 | 36.8599 | 37.6581 | 36.4389 | 34.1656 | 33.2728 | 34.9031 | 35.3571 | 33.2978 | 34.3479 | 34.4706 | 33.5784 | 34.469 | 34.4311 | 34.3648 | 34.0677 | 34.4783 | 35.4631 | 35.7394 | 35.7535 | 35.7472 | 34.1336 | 94.5012 | 94.917 | 94.1318
2022-09-08 01:05 | 3:15 | 17.2727 | 17.6393 | 19.6272 | 34.3952 | 34.3925 | 34.4639 | 35.3077 | 35.7009 | 36.8222 | 37.4312 | 36.7717 | 37.686 | 34.3911 | 34.3501 | 34.9972 | 35.7478 | 36.1201 | 36.4688 | 36.926 | 37.2152 | 21.2191 | 17.183 | 94.2906 | 33.0512 | 33.8237 | 35.4753 | 34.157 | 33.7835 | 34.0738 | 35.3888 | 34.7516 | 34.6217 | 37.4566 | 36.4189 | 34.0578 | 34.6683 | 36.4289 | 36.8614 | 37.6539 | 36.425 | 34.1608 | 33.2644 | 34.8996 | 35.3635 | 33.3092 | 34.3627 | 34.4778 | 33.5784 | 34.4585 | 34.4389 | 34.3713 | 34.0695 | 34.469 | 35.4469 | 35.7405 | 35.7655 | 35.7449 | 34.1035 | 94.716 | 95.1022 | 94.2366
2022-09-08 01:05 | 3:15 | 17.2551 | 17.6288 | 19.6119 | 34.3449 | 34.3826 | 34.4407 | 35.2933 | 35.7144 | 36.8002 | 37.4265 | 36.7842 | 37.6782 | 34.3682 | 34.3571 | 35.0036 | 35.7627 | 36.1147 | 36.4548 | 36.9184 | 37.2073 | 21.216 | 17.1775 | 94.3893 | 33.0507 | 33.8101 | 35.4803 | 34.1534 | 33.7698 | 34.0862 | 35.3762 | 34.757 | 34.61 | 37.4505 | 36.4262 | 34.0836 | 34.6829 | 36.4193 | 36.8478 | 37.6416 | 36.415 | 34.1494 | 33.2342 | 34.8915 | 35.3474 | 33.2877 | 34.3617 | 34.453 | 33.5869 | 34.4428 | 34.4469 | 34.3747 | 34.0606 | 34.4585 | 35.4703 | 35.7471 | 35.7273 | 35.7391 | 34.122 | 94.8721 | 95.2519 | 94.359
2022-09-08 01:05 | 3:15 | 17.2408 | 17.6343 | 19.6045 | 34.3516 | 34.3957 | 34.4304 | 35.289 | 35.6949 | 36.8205 | 37.4245 | 36.77 | 37.6624 | 34.3718 | 34.3721 | 34.9985 | 35.733 | 36.1166 | 36.4523 | 36.931 | 37.1971 | 21.2041 | 17.1537 | 94.507 | 33.25 | 33.804 | 35.4832 | 34.1765 | 33.7844 | 34.0808 | 35.3773 | 34.7231 | 34.6137 | 37.4674 | 36.433 | 34.0537 | 34.6709 | 36.4189 | 36.8778 | 37.6434 | 36.4267 | 34.1629 | 33.2371 | 34.8805 | 35.341 | 33.2734 | 34.3503 | 34.4804 | 33.5689 | 34.4408 | 34.4404 | 34.3605 | 34.06 | 34.4428 | 35.4559 | 35.7369 | 35.736 | 35.7432 | 34.1028 | 94.9409 | 95.4036 | 94.3056
2022-09-08 01:05 | 3:15 | 17.207 | 17.5959 | 19.5935 | 34.374 | 34.4073 | 34.4476 | 35.3057 | 35.7118 | 36.796 | 37.4248 | 36.7674 | 37.6835 | 34.3734 | 34.3577 | 35.0208 | 35.7456 | 36.1055 | 36.4607 | 36.9489 | 37.2023 | 21.2258 | 17.1184 | 94.5085 | 32.9088 | 33.8025 | 35.4649 | 34.1656 | 33.7715 | 34.0676 | 35.3838 | 34.741 | 34.6074 | 37.4441 | 36.4278 | 34.0586 | 34.6676 | 36.4262 | 36.8486 | 37.652 | 36.4289 | 34.1623 | 33.2303 | 34.8859 | 35.3404 | 33.293 | 34.3367 | 34.4565 | 33.5684 | 34.4549 | 34.4671 | 34.3467 | 34.0407 | 34.4408 | 35.4547 | 35.7252 | 35.7446 | 35.7236 | 34.0859 | 95.0721 | 95.5314 | 94.4774
2022-09-08 01:05 | 3:15 | 17.216 | 17.5748 | 19.6077 | 34.3796 | 34.3946 | 34.4473 | 35.3052 | 35.719 | 36.8173 | 37.4236 | 36.7699 | 37.6771 | 34.3861 | 34.3799 | 34.9813 | 35.7366 | 36.1096 | 36.453 | 36.9295 | 37.1917 | 21.1995 | 17.1167 | 94.3945 | 33.0442 | 33.7877 | 35.4772 | 34.1608 | 33.7684 | 34.0578 | 35.3843 | 34.7409 | 34.6195 | 37.4446 | 36.4156 | 34.0395 | 34.6647 | 36.433 | 36.8607 | 37.6508 | 36.4193 | 34.1552 | 33.2368 | 34.8873 | 35.3364 | 33.2813 | 34.3436 | 34.4695 | 33.5662 | 34.4617 | 34.4465 | 34.3521 | 34.0616 | 34.4549 | 35.4457 | 35.716 | 35.7445 | 35.7656 | 34.0911 | 95.2721 | 95.6295 | 94.6386
2022-09-08 01:06 | 3:16 | 17.1895 | 17.5804 | 19.5724 | 34.4557 | 34.3862 | 34.4308 | 35.2833 | 35.6968 | 36.8066 | 37.4112 | 36.7828 | 37.6588 | 34.3814 | 34.3784 | 34.9964 | 35.7414 | 36.0967 | 36.4457 | 36.926 | 37.19 | 21.2026 | 17.1013 | 94.2056 | 32.9063 | 33.7919 | 35.464 | 34.1494 | 33.7753 | 34.0836 | 35.3674 | 34.7382 | 34.6262 | 37.4424 | 36.422 | 34.0372 | 34.6724 | 36.4278 | 36.857 | 37.6295 | 36.4189 | 34.1418 | 33.2217 | 34.8606 | 35.3219 | 33.2807 | 34.3611 | 34.4558 | 33.5777 | 34.4611 | 34.465 | 34.365 | 34.0507 | 34.4617 | 35.4552 | 35.7348 | 35.7418 | 35.7478 | 34.0675 | 95.3781 | 95.783 | 94.8489
2022-09-08 01:06 | 3:16 | 17.2254 | 17.6105 | 19.5492 | 34.5202 | 34.3777 | 34.4287 | 35.2866 | 35.707 | 36.8077 | 37.4183 | 36.7625 | 37.6731 | 34.3775 | 34.3816 | 34.9873 | 35.7469 | 36.09 | 36.4392 | 36.9107 | 37.1996 | 21.2403 | 17.1493 | 94.0962 | 33.0438 | 33.7791 | 35.4699 | 34.1629 | 33.7597 | 34.0537 | 35.3873 | 34.7404 | 34.6079 | 37.4577 | 36.4151 | 34.0507 | 34.675 | 36.4156 | 36.8605 | 37.619 | 36.4262 | 34.1472 | 33.2216 | 34.8665 | 35.3137 | 33.2777 | 34.364 | 34.4459 | 33.566 | 34.4674 | 34.471 | 34.376 | 34.041 | 34.4611 | 35.4486 | 35.7327 | 35.747 | 35.7338 | 34.0774 | 95.4473 | 95.8285 | 94.7403
2022-09-08 01:06 | 3:16 | 17.2608 | 17.635 | 19.605 | 34.2918 | 34.3956 | 34.4416 | 35.2708 | 35.7118 | 36.811 | 37.4019 | 36.7644 | 37.6653 | 34.392 | 34.3632 | 34.9672 | 35.7329 | 36.0841 | 36.4229 | 36.9139 | 37.1857 | 21.241 | 17.0908 | 93.9348 | 32.9985 | 33.7859 | 35.4737 | 34.1623 | 33.7688 | 34.0586 | 35.3745 | 34.73 | 34.6112 | 37.4511 | 36.4086 | 34.061 | 34.6728 | 36.422 | 36.851 | 37.604 | 36.433 | 34.1506 | 33.2198 | 34.8423 | 35.3063 | 33.2501 | 34.3409 | 34.4397 | 33.5414 | 34.4669 | 34.4436 | 34.3753 | 34.0401 | 34.4674 | 35.4206 | 35.7301 | 35.7627 | 35.7428 | 34.0582 | 95.4323 | 95.8313 | 94.7238
2022-09-08 01:06 | 3:16 | 17.2353 | 17.602 | 19.5603 | 34.4116 | 34.3873 | 34.4246 | 35.2737 | 35.6986 | 36.7976 | 37.4074 | 36.7827 | 37.6776 | 34.3765 | 34.3705 | 34.9906 | 35.7209 | 36.0734 | 36.4175 | 36.8903 | 37.1725 | 21.2625 | 17.0917 | 93.8373 | 33.014 | 33.7874 | 35.4682 | 34.1552 | 33.7492 | 34.0395 | 35.3437 | 34.746 | 34.6015 | 37.447 | 36.4001 | 34.0477 | 34.6624 | 36.4151 | 36.853 | 37.6208 | 36.4278 | 34.1392 | 33.2066 | 34.8447 | 35.303 | 33.2478 | 34.3465 | 34.4423 | 33.5424 | 34.4645 | 34.4717 | 34.3558 | 34.0188 | 34.4669 | 35.4299 | 35.7241 | 35.7305 | 35.7294 | 34.0608 | 95.2413 | 95.6809 | 94.6935
2022-09-08 01:06 | 3:16 | 17.1751 | 17.5559 | 19.557 | 34.2735 | 34.3965 | 34.4252 | 35.2817 | 35.6993 | 36.789 | 37.4071 | 36.7805 | 37.6691 | 34.3869 | 34.3728 | 34.9691 | 35.7271 | 36.0886 | 36.4155 | 36.8942 | 37.1751 | 21.2761 | 17.0293 | 93.8293 | 33.0204 | 33.7846 | 35.459 | 34.1418 | 33.7483 | 34.0372 | 35.3707 | 34.7475 | 34.5895 | 37.4475 | 36.413 | 34.06 | 34.6827 | 36.4086 | 36.8464 | 37.6236 | 36.4156 | 34.1426 | 33.221 | 34.8439 | 35.3032 | 33.2547 | 34.3507 | 34.443 | 33.5153 | 34.4557 | 34.4547 | 34.3558 | 34.0361 | 34.4645 | 35.4303 | 35.7316 | 35.7623 | 35.7468 | 34.0448 | 94.9777 | 95.4059 | 94.3698
2022-09-08 01:06 | 3:16 | 17.1984 | 17.5497 | 19.5405 | 34.376 | 34.3668 | 34.425 | 35.2752 | 35.7101 | 36.8048 | 37.4063 | 36.7824 | 37.6623 | 34.3803 | 34.3638 | 34.9829 | 35.7429 | 36.0774 | 36.4231 | 36.8983 | 37.1583 | 21.3003 | 17.0497 | 93.8246 | 33.1779 | 33.7668 | 35.461 | 34.1472 | 33.7625 | 34.0507 | 35.3291 | 34.7284 | 34.5997 | 37.4303 | 36.4312 | 34.0433 | 34.6831 | 36.4001 | 36.8394 | 37.6324 | 36.422 | 34.1367 | 33.2007 | 34.8417 | 35.2943 | 33.2427 | 34.3516 | 34.4518 | 33.5188 | 34.453 | 34.459 | 34.3663 | 34.0407 | 34.4557 | 35.4438 | 35.716 | 35.7464 | 35.7273 | 34.0382 | 94.6689 | 95.135 | 94.1758
2022-09-08 01:07 | 3:16 | 17.2763 | 17.5843 | 19.5308 | 34.2442 | 34.3864 | 34.4098 | 35.2658 | 35.6912 | 36.7803 | 37.4137 | 36.7716 | 37.6646 | 34.3792 | 34.3801 | 34.9614 | 35.7257 | 36.0571 | 36.4254 | 36.8939 | 37.1581 | 21.2993 | 17.1296 | 93.7369 | 33.1394 | 33.7709 | 35.4618 | 34.1506 | 33.7567 | 34.061 | 35.3398 | 34.7446 | 34.6095 | 37.4299 | 36.4313 | 34.044 | 34.6752 | 36.413 | 36.8372 | 37.6196 | 36.4151 | 34.1369 | 33.1848 | 34.851 | 35.2895 | 33.2222 | 34.335 | 34.437 | 33.5366 | 34.4808 | 34.4436 | 34.3631 | 34.0255 | 34.453 | 35.4349 | 35.7304 | 35.7308 | 35.7253 | 34.0464 | 94.5083 | 94.8954 | 94.1773
2022-09-08 01:07 | 3:17 | 17.2157 | 17.5588 | 19.5171 | 34.2788 | 34.3865 | 34.4148 | 35.2494 | 35.684 | 36.7808 | 37.4111 | 36.7926 | 37.6626 | 34.3854 | 34.3706 | 34.9364 | 35.7372 | 36.0756 | 36.4253 | 36.8912 | 37.1558 | 21.3257 | 17.1091 | 93.7166 | 33.0428 | 33.7403 | 35.4649 | 34.1392 | 33.7319 | 34.0477 | 35.3474 | 34.7504 | 34.5957 | 37.436 | 36.4208 | 34.0191 | 34.6611 | 36.4312 | 36.8339 | 37.6106 | 36.4086 | 34.1323 | 33.1823 | 34.8207 | 35.2608 | 33.2374 | 34.3701 | 34.4467 | 33.5382 | 34.4654 | 34.4778 | 34.3711 | 34.0324 | 34.4808 | 35.4378 | 35.7239 | 35.7527 | 35.7196 | 34.035 | 94.4292 | 94.7413 | 94.0795
2022-09-08 01:07 | 3:17 | 17.1152 | 17.4575 | 19.5146 | 34.2164 | 34.3892 | 34.4379 | 35.2791 | 35.6985 | 36.786 | 37.398 | 36.7756 | 37.6577 | 34.3719 | 34.366 | 34.956 | 35.7354 | 36.0789 | 36.4164 | 36.8748 | 37.1593 | 21.3185 | 17.04 | 93.7221 | 33.0447 | 33.7673 | 35.4652 | 34.1426 | 33.746 | 34.06 | 35.341 | 34.7492 | 34.6098 | 37.4294 | 36.422 | 34.0472 | 34.6915 | 36.4313 | 36.8463 | 37.6191 | 36.4001 | 34.1374 | 33.19 | 34.8359 | 35.272 | 33.2396 | 34.3582 | 34.429 | 33.5302 | 34.4572 | 34.48 | 34.3757 | 34.0116 | 34.4654 | 35.4217 | 35.7219 | 35.7556 | 35.7447 | 34.0362 | 94.3542 | 94.6166 | 93.9397
2022-09-08 01:07 | 3:17 | 17.1019 | 17.4073 | 19.4529 | 34.287 | 34.3744 | 34.4224 | 35.2557 | 35.6926 | 36.7685 | 37.4036 | 36.7881 | 37.6766 | 34.3863 | 34.3873 | 34.9679 | 35.7308 | 36.0566 | 36.4394 | 36.8624 | 37.144 | 21.2607 | 16.9925 | 93.7934 | 33.0956 | 33.7642 | 35.4607 | 34.1367 | 33.755 | 34.0433 | 35.3423 | 34.7475 | 34.5959 | 37.444 | 36.4016 | 34.0287 | 34.6668 | 36.4208 | 36.8433 | 37.6221 | 36.413 | 34.121 | 33.1836 | 34.8217 | 35.2638 | 33.2349 | 34.3366 | 34.4404 | 33.505 | 34.4861 | 34.4678 | 34.361 | 34.0162 | 34.4572 | 35.4284 | 35.7236 | 35.7642 | 35.7307 | 34.0416 | 94.1698 | 94.5141 | 93.8441
2022-09-08 01:07 | 3:17 | 17.0995 | 17.4192 | 19.4481 | 34.2775 | 34.3846 | 34.4141 | 35.2638 | 35.6975 | 36.7882 | 37.3967 | 36.7854 | 37.6673 | 34.3726 | 34.3551 | 34.9409 | 35.7195 | 36.0549 | 36.4278 | 36.8767 | 37.1498 | 21.2667 | 17.0523 | 93.6684 | 33.1703 | 33.7511 | 35.4483 | 34.1369 | 33.7386 | 34.044 | 35.3527 | 34.7287 | 34.5824 | 37.4454 | 36.411 | 34.0299 | 34.6609 | 36.422 | 36.8347 | 37.62 | 36.4312 | 34.1507 | 33.1741 | 34.822 | 35.2485 | 33.2146 | 34.3695 | 34.4295 | 33.5012 | 34.4672 | 34.486 | 34.3565 | 34.032 | 34.4861 | 35.4387 | 35.7222 | 35.7669 | 35.725 | 34.009 | 94.1649 | 94.4471 | 93.8175
2022-09-08 01:07 | 3:17 | 17.1545 | 17.4775 | 19.4786 | 34.2009 | 34.3785 | 34.4059 | 35.2344 | 35.7058 | 36.7664 | 37.3999 | 36.7853 | 37.6851 | 34.3944 | 34.3778 | 34.9378 | 35.7208 | 36.053 | 36.4086 | 36.8722 | 37.1458 | 21.2709 | 17.0686 | 93.5897 | 33.0739 | 33.7512 | 35.4544 | 34.1323 | 33.7328 | 34.0191 | 35.3443 | 34.7498 | 34.6039 | 37.436 | 36.4093 | 34.0405 | 34.6837 | 36.4016 | 36.835 | 37.6107 | 36.4313 | 34.1162 | 33.171 | 34.8077 | 35.2632 | 33.2142 | 34.3447 | 34.4351 | 33.5042 | 34.4714 | 34.4632 | 34.3704 | 34.014 | 34.4672 | 35.4335 | 35.7161 | 35.7697 | 35.7359 | 34.0374 | 94.0478 | 94.3681 | 93.7224
2022-09-08 01:08 | 3:18 | 17.1416 | 17.5015 | 19.4645 | 34.2565 | 34.3644 | 34.4184 | 35.2554 | 35.6949 | 36.7835 | 37.4096 | 36.7659 | 37.6763 | 34.385 | 34.3713 | 34.9433 | 35.726 | 36.0511 | 36.423 | 36.8869 | 37.1492 | 21.2845 | 17.02 | 93.5823 | 32.9965 | 33.7482 | 35.4506 | 34.1374 | 33.7515 | 34.0472 | 35.3426 | 34.7415 | 34.5973 | 37.4463 | 36.3883 | 34.0434 | 34.6787 | 36.411 | 36.8345 | 37.6011 | 36.4208 | 34.1167 | 33.1538 | 34.7891 | 35.2424 | 33.2101 | 34.3517 | 34.4223 | 33.5087 | 34.4702 | 34.4693 | 34.3687 | 34.0309 | 34.4714 | 35.4542 | 35.7281 | 35.7542 | 35.7367 | 34.0137 | 93.9807 | 94.2856 | 93.7557
2022-09-08 01:08 | 3:18 | 17.1192 | 17.4382 | 19.4343 | 34.2383 | 34.3547 | 34.4096 | 35.2501 | 35.6918 | 36.776 | 37.404 | 36.7909 | 37.6784 | 34.3849 | 34.3633 | 34.9348 | 35.7367 | 36.0503 | 36.4209 | 36.8883 | 37.1576 | 21.2722 | 17.057 | 93.6384 | 32.8839 | 33.7528 | 35.4679 | 34.121 | 33.7387 | 34.0287 | 35.3411 | 34.7484 | 34.5911 | 37.4451 | 36.4286 | 34.0266 | 34.6635 | 36.4093 | 36.8383 | 37.6013 | 36.422 | 34.1237 | 33.1654 | 34.8 | 35.2582 | 33.2039 | 34.3428 | 34.4075 | 33.4928 | 34.468 | 34.499 | 34.3704 | 34.0173 | 34.4702 | 35.4388 | 35.7107 | 35.7673 | 35.7414 | 34.017 | 93.9887 | 94.2065 | 93.8716
2022-09-08 01:08 | 3:18 | 17.0916 | 17.3918 | 19.4302 | 34.1877 | 34.3855 | 34.4407 | 35.248 | 35.6851 | 36.7796 | 37.4034 | 36.7855 | 37.6946 | 34.4131 | 34.3766 | 34.9354 | 35.7177 | 36.0471 | 36.3974 | 36.8841 | 37.157 | 21.2684 | 16.986 | 93.6957 | 33.0077 | 33.7543 | 35.4569 | 34.1507 | 33.7529 | 34.0299 | 35.3333 | 34.7499 | 34.5974 | 37.4428 | 36.4235 | 34.042 | 34.6797 | 36.3883 | 36.8222 | 37.6044 | 36.4016 | 34.121 | 33.1748 | 34.794 | 35.2584 | 33.2083 | 34.3549 | 34.4201 | 33.483 | 34.4695 | 34.49 | 34.3681 | 34.0085 | 34.468 | 35.4345 | 35.7268 | 35.7518 | 35.7215 | 34.0211 | 93.9075 | 94.1193 | 93.7775
2022-09-08 01:08 | 3:18 | 17.0455 | 17.4376 | 19.4298 | 34.172 | 34.3825 | 34.4081 | 35.2445 | 35.6769 | 36.7738 | 37.3985 | 36.7939 | 37.6688 | 34.394 | 34.3783 | 34.927 | 35.7317 | 36.0445 | 36.4158 | 36.8859 | 37.1401 | 21.2412 | 16.9948 | 93.5358 | 33.0954 | 33.7477 | 35.4528 | 34.1162 | 33.7326 | 34.0405 | 35.3555 | 34.7464 | 34.6029 | 37.4425 | 36.4091 | 34.0355 | 34.6777 | 36.4286 | 36.8435 | 37.6044 | 36.411 | 34.1221 | 33.1449 | 34.8044 | 35.2447 | 33.1991 | 34.3454 | 34.4168 | 33.4942 | 34.4764 | 34.4802 | 34.3673 | 34.0122 | 34.4695 | 35.43 | 35.7232 | 35.7822 | 35.741 | 34.0114 | 93.8089 | 94.0673 | 93.7089
2022-09-08 01:08 | 3:18 | 17.1216 | 17.4248 | 19.4293 | 34.1914 | 34.3695 | 34.4079 | 35.2501 | 35.687 | 36.7772 | 37.4182 | 36.7983 | 37.682 | 34.3927 | 34.3802 | 34.9138 | 35.7396 | 36.0411 | 36.4078 | 36.8579 | 37.1471 | 21.2537 | 17.0038 | 93.4159 | 33.007 | 33.7467 | 35.4387 | 34.1167 | 33.746 | 34.0434 | 35.3323 | 34.7581 | 34.5801 | 37.4345 | 36.4089 | 34.0419 | 34.6856 | 36.4235 | 36.8354 | 37.6017 | 36.4093 | 34.1133 | 33.1557 | 34.7816 | 35.2575 | 33.1918 | 34.3573 | 34.4184 | 33.5015 | 34.4903 | 34.4823 | 34.3464 | 34.0159 | 34.4764 | 35.4236 | 35.7207 | 35.7749 | 35.7366 | 34.016 | 93.8348 | 94.0135 | 93.7171
2022-09-08 01:08 | 3:18 | 17.0771 | 17.4187 | 19.4087 | 34.1731 | 34.3678 | 34.4191 | 35.2618 | 35.6872 | 36.7832 | 37.4124 | 36.7874 | 37.6829 | 34.4089 | 34.3824 | 34.9273 | 35.7372 | 36.0436 | 36.437 | 36.8634 | 37.153 | 21.2446 | 16.9571 | 93.4023 | 33.1026 | 33.7356 | 35.4534 | 34.1237 | 33.7347 | 34.0266 | 35.3424 | 34.738 | 34.5904 | 37.4412 | 36.4075 | 34.0295 | 34.6823 | 36.4091 | 36.8522 | 37.6076 | 36.3883 | 34.1268 | 33.1433 | 34.7689 | 35.2504 | 33.1834 | 34.3704 | 34.4179 | 33.4875 | 34.4759 | 34.4894 | 34.3669 | 34.0085 | 34.4903 | 35.4317 | 35.7238 | 35.7601 | 35.7287 | 34.0428 | 93.7442 | 93.9512 | 93.5687
2022-09-08 01:09 | 3:18 | 17.0951 | 17.3825 | 19.378 | 34.2562 | 34.3802 | 34.4055 | 35.2493 | 35.6738 | 36.7826 | 37.4004 | 36.8145 | 37.6898 | 34.4066 | 34.3835 | 34.9327 | 35.7286 | 36.042 | 36.4038 | 36.8727 | 37.1499 | 21.2453 | 16.9841 | 93.2776 | 33.0294 | 33.7568 | 35.4583 | 34.121 | 33.7344 | 34.042 | 35.3462 | 34.7374 | 34.6033 | 37.4452 | 36.4196 | 34.0268 | 34.6598 | 36.4089 | 36.8423 | 37.6076 | 36.4286 | 34.1341 | 33.1209 | 34.7768 | 35.2439 | 33.1671 | 34.3557 | 34.3846 | 33.5014 | 34.466 | 34.4669 | 34.3738 | 34.0036 | 34.4759 | 35.4375 | 35.7158 | 35.7848 | 35.7445 | 34.0054 | 93.7565 | 93.9186 | 93.6737
2022-09-08 01:09 | 3:19 | 16.9876 | 17.3344 | 19.3842 | 34.2487 | 34.3605 | 34.3982 | 35.2508 | 35.6895 | 36.766 | 37.398 | 36.7911 | 37.6837 | 34.4207 | 34.3919 | 34.9201 | 35.7214 | 36.0266 | 36.4084 | 36.8678 | 37.1331 | 21.2191 | 16.9655 | 93.1552 | 32.9307 | 33.7253 | 35.4396 | 34.1221 | 33.7393 | 34.0355 | 35.345 | 34.7575 | 34.609 | 37.4257 | 36.3918 | 34.0316 | 34.6689 | 36.4075 | 36.8445 | 37.6285 | 36.4235 | 34.1163 | 33.1299 | 34.7657 | 35.243 | 33.1617 | 34.349 | 34.3978 | 33.482 | 34.4876 | 34.4876 | 34.3554 | 33.9867 | 34.466 | 35.4323 | 35.7319 | 35.7543 | 35.7421 | 34.0097 | 93.6571 | 93.841 | 93.5712
2022-09-08 01:09 | 3:19 | 17.0693 | 17.3895 | 19.4077 | 34.227 | 34.3851 | 34.4158 | 35.2432 | 35.6887 | 36.7769 | 37.4217 | 36.8062 | 37.7044 | 34.409 | 34.3925 | 34.9193 | 35.7265 | 36.025 | 36.4108 | 36.8439 | 37.1593 | 21.2437 | 16.9873 | 93.1099 | 33.0147 | 33.732 | 35.4702 | 34.1133 | 33.7332 | 34.0419 | 35.3305 | 34.7543 | 34.5792 | 37.4404 | 36.396 | 34.0263 | 34.683 | 36.4196 | 36.8364 | 37.5949 | 36.4091 | 34.1114 | 33.1288 | 34.7722 | 35.2145 | 33.1626 | 34.3421 | 34.3915 | 33.4781 | 34.484 | 34.4797 | 34.3501 | 33.9928 | 34.4876 | 35.4304 | 35.7085 | 35.7579 | 35.7295 | 34.0247 | 93.5506 | 93.7612 | 93.4582
2022-09-08 01:09 | 3:19 | 17.0098 | 17.3351 | 19.3608 | 34.1708 | 34.373 | 34.4077 | 35.2357 | 35.6886 | 36.7605 | 37.4081 | 36.8107 | 37.6743 | 34.411 | 34.3942 | 34.9035 | 35.7192 | 36.0491 | 36.4067 | 36.8616 | 37.143 | 21.2183 | 16.9587 | 92.9811 | 33.0108 | 33.7262 | 35.4436 | 34.1268 | 33.7209 | 34.0295 | 35.3364 | 34.7512 | 34.5917 | 37.4369 | 36.4041 | 34.0333 | 34.687 | 36.3918 | 36.8505 | 37.6073 | 36.4089 | 34.1195 | 33.1157 | 34.7661 | 35.2369 | 33.1576 | 34.34 | 34.4027 | 33.4695 | 34.4972 | 34.4893 | 34.3571 | 34.0039 | 34.484 | 35.4399 | 35.7079 | 35.7727 | 35.7262 | 34.0089 | 93.4848 | 93.6586 | 93.3932
2022-09-08 01:09 | 3:19 | 16.9831 | 17.3058 | 19.3381 | 34.1972 | 34.387 | 34.4036 | 35.2481 | 35.6783 | 36.7687 | 37.3921 | 36.7995 | 37.7101 | 34.4179 | 34.3892 | 34.941 | 35.7242 | 36.0251 | 36.3967 | 36.8648 | 37.1632 | 21.1926 | 16.8936 | 92.9327 | 32.9407 | 33.7318 | 35.4487 | 34.1341 | 33.737 | 34.0268 | 35.3376 | 34.7565 | 34.5895 | 37.4527 | 36.4085 | 34.0312 | 34.6718 | 36.396 | 36.8434 | 37.5971 | 36.4075 | 34.1022 | 33.1368 | 34.7569 | 35.2358 | 33.1576 | 34.3432 | 34.404 | 33.4758 | 34.4734 | 34.4851 | 34.3721 | 34.0171 | 34.4972 | 35.4396 | 35.7125 | 35.7721 | 35.7366 | 34.0021 | 93.347 | 93.5555 | 93.3131
2022-09-08 01:09 | 3:19 | 17.0544 | 17.3504 | 19.3454 | 34.2325 | 34.3648 | 34.4029 | 35.233 | 35.679 | 36.7649 | 37.3894 | 36.7993 | 37.6987 | 34.3964 | 34.3941 | 34.9365 | 35.7469 | 36.0411 | 36.4195 | 36.8664 | 37.1578 | 21.1852 | 16.923 | 92.8361 | 33.0017 | 33.7387 | 35.4338 | 34.1163 | 33.7456 | 34.0316 | 35.3385 | 34.7516 | 34.6081 | 37.4444 | 36.3941 | 34.0206 | 34.6662 | 36.4041 | 36.8509 | 37.5911 | 36.4196 | 34.1032 | 33.1109 | 34.782 | 35.2386 | 33.1419 | 34.3653 | 34.394 | 33.4681 | 34.4966 | 34.4894 | 34.3577 | 34.0081 | 34.4734 | 35.4532 | 35.7145 | 35.767 | 35.7475 | 34.0116 | 93.269 | 93.4489 | 93.2482
2022-09-08 01:10 | 3:20 | 17.0075 | 17.3004 | 19.3673 | 34.1463 | 34.3713 | 34.4152 | 35.245 | 35.6724 | 36.7495 | 37.3937 | 36.7908 | 37.701 | 34.4229 | 34.4079 | 34.922 | 35.7195 | 36.0332 | 36.3995 | 36.8756 | 37.1405 | 21.1504 | 16.8823 | 92.7131 | 32.8939 | 33.7321 | 35.4525 | 34.1114 | 33.7418 | 34.0263 | 35.3436 | 34.7546 | 34.6024 | 37.4498 | 36.3843 | 34.0291 | 34.6661 | 36.4085 | 36.8384 | 37.5895 | 36.3918 | 34.106 | 33.1272 | 34.7758 | 35.2208 | 33.1408 | 34.3685 | 34.3853 | 33.4592 | 34.4726 | 34.4819 | 34.3799 | 33.9974 | 34.4966 | 35.4523 | 35.7073 | 35.7764 | 35.7648 | 34.0097 | 93.1774 | 93.3655 | 93.1562
2022-09-08 01:10 | 3:20 | 16.975 | 17.2827 | 19.3494 | 34.2521 | 34.3747 | 34.4106 | 35.2289 | 35.7049 | 36.7735 | 37.4134 | 36.7921 | 37.7062 | 34.4296 | 34.413 | 34.92 | 35.7278 | 36.0404 | 36.4007 | 36.8667 | 37.1419 | 21.1493 | 16.8934 | 92.5748 | 32.9324 | 33.7285 | 35.4285 | 34.1195 | 33.7197 | 34.0333 | 35.3377 | 34.7567 | 34.5902 | 37.4281 | 36.4083 | 34.0144 | 34.7009 | 36.3941 | 36.849 | 37.6095 | 36.396 | 34.0995 | 33.1202 | 34.7664 | 35.2237 | 33.1425 | 34.3612 | 34.4028 | 33.4689 | 34.4718 | 34.5033 | 34.3784 | 34.0047 | 34.4726 | 35.4574 | 35.7051 | 35.7616 | 35.7421 | 34.0068 | 93.1171 | 93.2792 | 93.219
2022-09-08 01:10 | 3:20 | 16.9164 | 17.2393 | 19.2908 | 34.1553 | 34.3605 | 34.3903 | 35.2438 | 35.6905 | 36.7763 | 37.4052 | 36.8048 | 37.6939 | 34.4419 | 34.4139 | 34.9261 | 35.7327 | 36.0143 | 36.3969 | 36.8679 | 37.1646 | 21.169 | 16.8438 | 92.5094 | 33.0103 | 33.7182 | 35.4277 | 34.1022 | 33.7469 | 34.0312 | 35.3385 | 34.7564 | 34.5907 | 37.4257 | 36.4032 | 34.0306 | 34.6785 | 36.3843 | 36.826 | 37.6052 | 36.4041 | 34.101 | 33.115 | 34.766 | 35.2058 | 33.1288 | 34.3607 | 34.3963 | 33.4727 | 34.4814 | 34.5032 | 34.3816 | 33.9998 | 34.4718 | 35.4579 | 35.7113 | 35.7816 | 35.74 | 33.9961 | 93.0005 | 93.1441 | 93.0907
2022-09-08 01:10 | 3:20 | 16.9106 | 17.232 | 19.3072 | 34.0732 | 34.3467 | 34.4046 | 35.2329 | 35.6871 | 36.7834 | 37.4209 | 36.8107 | 37.6951 | 34.44 | 34.4005 | 34.9041 | 35.7381 | 36.0299 | 36.3914 | 36.8787 | 37.1399 | 21.1414 | 16.8508 | 92.3624 | 32.8045 | 33.7177 | 35.4295 | 34.1032 | 33.7292 | 34.0206 | 35.3391 | 34.7587 | 34.6025 | 37.4612 | 36.4041 | 34.0328 | 34.6777 | 36.4083 | 36.8424 | 37.5958 | 36.4085 | 34.0984 | 33.1345 | 34.7652 | 35.2232 | 33.1085 | 34.3558 | 34.3786 | 33.4737 | 34.4913 | 34.5095 | 34.3632 | 34.0072 | 34.4814 | 35.4652 | 35.6954 | 35.7852 | 35.7365 | 34.0016 | 92.8571 | 93.0354 | 92.9565
2022-09-08 01:10 | 3:20 | 16.9024 | 17.2364 | 19.3237 | 34.231 | 34.3521 | 34.392 | 35.2186 | 35.6781 | 36.7697 | 37.3973 | 36.8136 | 37.6998 | 34.4337 | 34.4228 | 34.9222 | 35.7351 | 36.0149 | 36.4041 | 36.8612 | 37.1176 | 21.1482 | 16.8419 | 92.313 | 32.8938 | 33.7115 | 35.442 | 34.106 | 33.7343 | 34.0291 | 35.3303 | 34.7665 | 34.5833 | 37.4436 | 36.3899 | 34.0121 | 34.6966 | 36.4032 | 36.8728 | 37.6023 | 36.3941 | 34.0879 | 33.1113 | 34.7533 | 35.2198 | 33.1326 | 34.3766 | 34.3816 | 33.4419 | 34.4938 | 34.4768 | 34.3705 | 34.0038 | 34.4913 | 35.471 | 35.7118 | 35.7794 | 35.7409 | 34.006 | 92.7541 | 92.9201 | 92.877
2022-09-08 01:10 | 3:20 | 16.8743 | 17.1896 | 19.2627 | 34.0632 | 34.365 | 34.3958 | 35.2183 | 35.6886 | 36.7874 | 37.4149 | 36.7843 | 37.7097 | 34.4416 | 34.428 | 34.9241 | 35.7376 | 36.0248 | 36.4039 | 36.8646 | 37.1325 | 21.1426 | 16.8137 | 92.2606 | 33.0076 | 33.7137 | 35.4408 | 34.0995 | 33.726 | 34.0144 | 35.3418 | 34.7608 | 34.5869 | 37.4342 | 36.3851 | 34.0152 | 34.6843 | 36.4041 | 36.8393 | 37.594 | 36.3843 | 34.0764 | 33.1129 | 34.7652 | 35.2315 | 33.1093 | 34.3529 | 34.3742 | 33.4479 | 34.4729 | 34.5128 | 34.3728 | 33.9847 | 34.4938 | 35.4366 | 35.6852 | 35.7883 | 35.73 | 33.9915 | 92.6494 | 92.7742 | 92.796
2022-09-08 01:11 | 3:20 | 16.8562 | 17.171 | 19.2326 | 34.1063 | 34.376 | 34.3885 | 35.2168 | 35.6756 | 36.7523 | 37.3941 | 36.7971 | 37.6905 | 34.456 | 34.4127 | 34.9244 | 35.7222 | 36.0162 | 36.4161 | 36.8637 | 37.1394 | 21.1055 | 16.7655 | 92.2061 | 32.9479 | 33.7296 | 35.4432 | 34.101 | 33.7344 | 34.0306 | 35.3483 | 34.7429 | 34.6071 | 37.4545 | 36.3763 | 34.0123 | 34.675 | 36.3899 | 36.8638 | 37.5943 | 36.4083 | 34.0806 | 33.1 | 34.7796 | 35.2232 | 33.1232 | 34.3656 | 34.369 | 33.4613 | 34.4853 | 34.4866 | 34.3638 | 33.9976 | 34.4729 | 35.4739 | 35.7034 | 35.7828 | 35.7412 | 33.9945 | 92.4916 | 92.6051 | 92.6711
2022-09-08 01:11 | 3:21 | 16.8462 | 17.1497 | 19.2198 | 34.0953 | 34.3753 | 34.3915 | 35.2308 | 35.6757 | 36.7798 | 37.4013 | 36.8015 | 37.6991 | 34.4223 | 34.4023 | 34.91 | 35.723 | 36.0194 | 36.4011 | 36.8683 | 37.1579 | 21.0921 | 16.8598 | 92.145 | 32.8658 | 33.7034 | 35.4208 | 34.0984 | 33.7236 | 34.0328 | 35.336 | 34.7404 | 34.591 | 37.4457 | 36.3694 | 34.0007 | 34.6912 | 36.3851 | 36.8382 | 37.6018 | 36.4032 | 34.0685 | 33.0864 | 34.7821 | 35.2241 | 33.1043 | 34.3706 | 34.3625 | 33.4304 | 34.5006 | 34.4986 | 34.3801 | 33.9831 | 34.4853 | 35.4594 | 35.6914 | 35.7713 | 35.753 | 33.9947 | 92.396 | 92.4852 | 92.6144
2022-09-08 01:11 | 3:21 | 16.8915 | 17.2206 | 19.2558 | 34.1166 | 34.3558 | 34.3875 | 35.2302 | 35.6865 | 36.773 | 37.4024 | 36.8062 | 37.7055 | 34.4529 | 34.421 | 34.8996 | 35.7412 | 36.0292 | 36.4167 | 36.8498 | 37.1488 | 21.0932 | 16.8221 | 92.3108 | 32.9057 | 33.7038 | 35.4293 | 34.0879 | 33.7159 | 34.0121 | 35.3481 | 34.7565 | 34.5956 | 37.4593 | 36.3751 | 34.0029 | 34.6598 | 36.3763 | 36.8636 | 37.5903 | 36.4041 | 34.0714 | 33.09 | 34.7647 | 35.2208 | 33.0986 | 34.3792 | 34.3686 | 33.432 | 34.4899 | 34.5178 | 34.3706 | 33.9781 | 34.5006 | 35.4513 | 35.6992 | 35.7888 | 35.7435 | 34.0154 | 92.3257 | 92.3737 | 92.5516
2022-09-08 01:11 | 3:21 | 16.8731 | 17.1207 | 19.2471 | 34.0817 | 34.3558 | 34.409 | 35.2095 | 35.673 | 36.7698 | 37.4063 | 36.81 | 37.7058 | 34.4382 | 34.4118 | 34.895 | 35.7122 | 35.999 | 36.4021 | 36.8584 | 37.139 | 21.0714 | 16.7353 | 92.3172 | 32.9157 | 33.7112 | 35.4101 | 34.0764 | 33.7253 | 34.0152 | 35.3492 | 34.7421 | 34.5874 | 37.4391 | 36.3906 | 33.9979 | 34.6609 | 36.3694 | 36.8461 | 37.5982 | 36.3899 | 34.0551 | 33.0753 | 34.7402 | 35.2167 | 33.1144 | 34.3865 | 34.3632 | 33.4444 | 34.4851 | 34.5075 | 34.366 | 33.9876 | 34.4899 | 35.4765 | 35.6885 | 35.7795 | 35.7579 | 34.0056 | 92.2163 | 92.3123 | 92.3559
2022-09-08 01:11 | 3:21 | 16.8875 | 17.1667 | 19.2157 | 34.0367 | 34.3663 | 34.3756 | 35.2097 | 35.6983 | 36.7592 | 37.3984 | 36.8056 | 37.6931 | 34.4355 | 34.4243 | 34.9134 | 35.7156 | 35.9913 | 36.3888 | 36.8533 | 37.1516 | 21.0395 | 16.7971 | 92.3164 | 32.9236 | 33.6722 | 35.4125 | 34.0806 | 33.7091 | 34.0123 | 35.3255 | 34.7441 | 34.5989 | 37.4136 | 36.3536 | 34.0027 | 34.6761 | 36.3751 | 36.8507 | 37.5971 | 36.3851 | 34.051 | 33.0719 | 34.7463 | 35.2026 | 33.0814 | 34.3806 | 34.3732 | 33.429 | 34.4887 | 34.5197 | 34.3873 | 34.007 | 34.4851 | 35.4582 | 35.6768 | 35.7833 | 35.7448 | 34.007 | 92.1296 | 92.2568 | 92.4733
2022-09-08 01:11 | 3:21 | 16.875 | 17.1746 | 19.219 | 34.1745 | 34.3631 | 34.3766 | 35.2186 | 35.6776 | 36.7688 | 37.3929 | 36.809 | 37.7136 | 34.4299 | 34.4173 | 34.8864 | 35.7212 | 36.0054 | 36.4029 | 36.8552 | 37.1507 | 21.0363 | 16.7969 | 92.2568 | 32.9408 | 33.7006 | 35.4186 | 34.0685 | 33.7116 | 34.0007 | 35.3182 | 34.7539 | 34.5816 | 37.444 | 36.3719 | 33.9885 | 34.6448 | 36.3906 | 36.8328 | 37.5779 | 36.3763 | 34.0481 | 33.0669 | 34.7282 | 35.2116 | 33.0843 | 34.3863 | 34.3588 | 33.428 | 34.4995 | 34.5078 | 34.3551 | 33.9963 | 34.4887 | 35.4701 | 35.6791 | 35.7783 | 35.7471 | 33.9894 | 92.2418 | 92.3111 | 92.429
2022-09-08 01:12 | 3:22 | 16.9605 | 17.1848 | 19.1912 | 34.0867 | 34.3711 | 34.364 | 35.2079 | 35.6773 | 36.7546 | 37.4133 | 36.793 | 37.7092 | 34.443 | 34.4247 | 34.9041 | 35.7091 | 35.9975 | 36.3944 | 36.8502 | 37.1422 | 21.0288 | 16.8046 | 92.4078 | 33.0248 | 33.6974 | 35.3894 | 34.0714 | 33.7048 | 34.0029 | 35.3094 | 34.7414 | 34.5806 | 37.4408 | 36.3644 | 33.9858 | 34.66 | 36.3536 | 36.8293 | 37.5916 | 36.3694 | 34.0563 | 33.0646 | 34.732 | 35.1928 | 33.0733 | 34.392 | 34.3777 | 33.4145 | 34.4841 | 34.5153 | 34.3778 | 33.9919 | 34.4995 | 35.463 | 35.6941 | 35.7745 | 35.7751 | 33.9841 | 92.2788 | 92.4303 | 92.4914
2022-09-08 01:12 | 3:22 | 16.9429 | 17.2147 | 19.2013 | 34.1713 | 34.3757 | 34.3738 | 35.1998 | 35.6688 | 36.7534 | 37.4007 | 36.8018 | 37.7122 | 34.4311 | 34.4217 | 34.8964 | 35.6976 | 35.9886 | 36.3918 | 36.8405 | 37.1276 | 21.0277 | 16.8098 | 92.4524 | 33.0003 | 33.6892 | 35.4141 | 34.0551 | 33.6952 | 33.9979 | 35.3282 | 34.7469 | 34.5744 | 37.4266 | 36.3551 | 33.9895 | 34.6578 | 36.3719 | 36.8281 | 37.598 | 36.3751 | 34.0394 | 33.0558 | 34.7335 | 35.2109 | 33.0625 | 34.3833 | 34.3644 | 33.4258 | 34.4864 | 34.5134 | 34.3713 | 33.9907 | 34.4841 | 35.4716 | 35.7048 | 35.7746 | 35.7447 | 33.9779 | 92.4027 | 92.521 | 92.6727
2022-09-08 01:12 | 3:22 | 16.8293 | 17.1679 | 19.2274 | 34.0966 | 34.361 | 34.3852 | 35.1981 | 35.6572 | 36.7278 | 37.3963 | 36.7869 | 37.7042 | 34.4389 | 34.426 | 34.8858 | 35.6968 | 35.9752 | 36.3809 | 36.8441 | 37.1307 | 21.0236 | 16.7598 | 92.3936 | 32.9677 | 33.7006 | 35.3942 | 34.051 | 33.6997 | 34.0027 | 35.339 | 34.7255 | 34.5784 | 37.4305 | 36.3635 | 33.9842 | 34.6457 | 36.3644 | 36.8357 | 37.5821 | 36.3906 | 34.0402 | 33.0584 | 34.7129 | 35.1711 | 33.0384 | 34.3823 | 34.3685 | 33.3912 | 34.4901 | 34.5185 | 34.3633 | 33.9765 | 34.4864 | 35.4577 | 35.6846 | 35.781 | 35.7441 | 33.9829 | 92.4963 | 92.6192 | 92.7539
2022-09-08 01:12 | 3:22 | 16.7597 | 17.0533 | 19.1656 | 34.136 | 34.3565 | 34.3549 | 35.1912 | 35.6499 | 36.7373 | 37.4083 | 36.791 | 37.7167 | 34.4469 | 34.4297 | 34.8884 | 35.6933 | 35.9716 | 36.3793 | 36.8437 | 37.1162 | 21.0093 | 16.7378 | 92.5763 | 32.9419 | 33.6758 | 35.3931 | 34.0481 | 33.7077 | 33.9885 | 35.3104 | 34.7167 | 34.5627 | 37.4383 | 36.353 | 33.995 | 34.623 | 36.3551 | 36.8308 | 37.5803 | 36.3536 | 34.0261 | 33.0379 | 34.7151 | 35.1814 | 33.0373 | 34.4017 | 34.3754 | 33.4026 | 34.4906 | 34.5114 | 34.3766 | 33.9735 | 34.4901 | 35.4503 | 35.6761 | 35.7928 | 35.735 | 33.9778 | 92.5967 | 92.7862 | 92.8803
2022-09-08 01:12 | 3:22 | 16.8191 | 17.0511 | 19.169 | 34.127 | 34.3704 | 34.3444 | 35.1867 | 35.6592 | 36.746 | 37.3993 | 36.7966 | 37.697 | 34.4404 | 34.441 | 34.8976 | 35.7035 | 35.9735 | 36.379 | 36.8278 | 37.1283 | 20.954 | 16.7158 | 92.5937 | 32.8986 | 33.6802 | 35.3813 | 34.0563 | 33.6907 | 33.9858 | 35.3215 | 34.7206 | 34.5695 | 37.4315 | 36.3481 | 33.9703 | 34.6396 | 36.3635 | 36.8303 | 37.5873 | 36.3719 | 34.0443 | 33.026 | 34.7134 | 35.1771 | 33.0321 | 34.3862 | 34.3604 | 33.3913 | 34.4638 | 34.5304 | 34.3783 | 33.9825 | 34.4906 | 35.4585 | 35.6702 | 35.7913 | 35.7461 | 33.9831 | 92.6764 | 92.8505 | 92.8537
2022-09-08 01:12 | 3:22 | 16.7724 | 17.1016 | 19.1087 | 33.9793 | 34.3687 | 34.3483 | 35.1718 | 35.6695 | 36.7428 | 37.3827 | 36.7904 | 37.712 | 34.4671 | 34.4365 | 34.8895 | 35.6954 | 35.9566 | 36.354 | 36.8374 | 37.117 | 20.9349 | 16.7574 | 92.7071 | 33.0274 | 33.6841 | 35.3775 | 34.0394 | 33.6824 | 33.9895 | 35.322 | 34.7278 | 34.569 | 37.4165 | 36.3463 | 33.9775 | 34.6554 | 36.353 | 36.8473 | 37.5739 | 36.3644 | 34.0195 | 33.0422 | 34.7061 | 35.1596 | 33.0382 | 34.3773 | 34.3679 | 33.4019 | 34.4935 | 34.5156 | 34.3802 | 33.9808 | 34.4638 | 35.452 | 35.6895 | 35.7764 | 35.7473 | 33.9885 | 92.784 | 93.001 | 92.9226
2022-09-08 01:13 | 3:22 | 16.7622 | 17.0808 | 19.1223 | 34.0249 | 34.3704 | 34.3531 | 35.16 | 35.6362 | 36.7464 | 37.3962 | 36.7919 | 37.6982 | 34.4465 | 34.4279 | 34.8884 | 35.6905 | 35.963 | 36.3823 | 36.8196 | 37.1326 | 20.9311 | 16.7549 | 92.7937 | 32.8369 | 33.6931 | 35.3752 | 34.0402 | 33.6806 | 33.9842 | 35.3418 | 34.7153 | 34.5664 | 37.4289 | 36.3546 | 33.9651 | 34.6483 | 36.3481 | 36.8217 | 37.5762 | 36.3551 | 34.0253 | 33.0169 | 34.7026 | 35.1647 | 33.0203 | 34.4033 | 34.3635 | 33.4029 | 34.4833 | 34.5354 | 34.3824 | 33.9693 | 34.4935 | 35.4581 | 35.6763 | 35.8017 | 35.7575 | 33.9676 | 92.9611 | 93.1367 | 93.08
2022-09-08 01:13 | 3:23 | 16.7309 | 17.0344 | 19.0885 | 33.995 | 34.3681 | 34.3611 | 35.1905 | 35.6355 | 36.7632 | 37.3877 | 36.7973 | 37.6992 | 34.465 | 34.437 | 34.883 | 35.7037 | 35.9549 | 36.3498 | 36.8443 | 37.1207 | 20.9188 | 16.6967 | 92.8512 | 32.8892 | 33.6657 | 35.3917 | 34.0261 | 33.6922 | 33.995 | 35.3146 | 34.7184 | 34.5517 | 37.4313 | 36.3657 | 33.987 | 34.6504 | 36.3463 | 36.8321 | 37.5731 | 36.3635 | 34.0281 | 33.0336 | 34.6912 | 35.1616 | 33.0106 | 34.4073 | 34.3662 | 33.3977 | 34.4706 | 34.528 | 34.3835 | 33.9842 | 34.4833 | 35.4592 | 35.6777 | 35.7747 | 35.7414 | 33.9465 | 93.0735 | 93.2482 | 93.2027
2022-09-08 01:13 | 3:23 | 16.809 | 17.0809 | 19.1001 | 34.0067 | 34.3673 | 34.3263 | 35.1759 | 35.6469 | 36.7468 | 37.3932 | 36.7822 | 37.696 | 34.471 | 34.4252 | 34.8802 | 35.6861 | 35.9528 | 36.3594 | 36.822 | 37.1202 | 20.9286 | 16.7234 | 92.8086 | 32.7354 | 33.6525 | 35.3934 | 34.0443 | 33.6783 | 33.9703 | 35.3347 | 34.7187 | 34.5644 | 37.4096 | 36.3627 | 33.9806 | 34.6352 | 36.3546 | 36.8352 | 37.5779 | 36.353 | 34.0115 | 33.0296 | 34.7115 | 35.1566 | 33.0048 | 34.4149 | 34.3678 | 33.3794 | 34.4778 | 34.5302 | 34.3919 | 33.9573 | 34.4706 | 35.4639 | 35.6801 | 35.7875 | 35.7438 | 33.9555 | 93.183 | 93.291 | 93.296
2022-09-08 01:13 | 3:23 | 16.7806 | 17.0783 | 19.1322 | 33.9624 | 34.3464 | 34.3451 | 35.1739 | 35.6553 | 36.7525 | 37.38 | 36.7803 | 37.7073 | 34.4436 | 34.4519 | 34.8633 | 35.6888 | 35.9471 | 36.3513 | 36.8397 | 37.1228 | 20.9275 | 16.7114 | 92.9271 | 32.894 | 33.6653 | 35.3878 | 34.0195 | 33.6826 | 33.9775 | 35.3169 | 34.7054 | 34.5615 | 37.3948 | 36.3572 | 33.9715 | 34.6282 | 36.3657 | 36.8245 | 37.568 | 36.3481 | 34.023 | 33.0098 | 34.6922 | 35.1442 | 33.0008 | 34.408 | 34.3684 | 33.3948 | 34.453 | 34.5091 | 34.3925 | 33.9583 | 34.4778 | 35.4545 | 35.6588 | 35.7876 | 35.7589 | 33.958 | 93.2252 | 93.3046 | 93.32
2022-09-08 01:13 | 3:23 | 16.7257 | 16.9999 | 19.095 | 34.125 | 34.3669 | 34.335 | 35.1662 | 35.6289 | 36.7394 | 37.3822 | 36.7723 | 37.7144 | 34.4717 | 34.4396 | 34.8716 | 35.6747 | 35.9363 | 36.3712 | 36.8359 | 37.1174 | 20.91 | 16.7068 | 92.9348 | 32.7729 | 33.6719 | 35.3717 | 34.0253 | 33.681 | 33.9651 | 35.3197 | 34.7088 | 34.5594 | 37.4027 | 36.3328 | 33.9861 | 34.6434 | 36.3627 | 36.8237 | 37.5843 | 36.3463 | 34.0312 | 33.0203 | 34.6794 | 35.1425 | 33.0037 | 34.4058 | 34.3735 | 33.3674 | 34.4804 | 34.5243 | 34.3942 | 33.9523 | 34.453 | 35.4527 | 35.6497 | 35.7966 | 35.749 | 33.9812 | 93.2698 | 93.3341 | 93.3097
2022-09-08 01:13 | 3:23 | 16.6732 | 17.0084 | 19.0665 | 34.0383 | 34.3738 | 34.3322 | 35.1563 | 35.6601 | 36.748 | 37.3669 | 36.781 | 37.6829 | 34.4547 | 34.4511 | 34.8745 | 35.6779 | 35.9306 | 36.3492 | 36.814 | 37.1331 | 20.903 | 16.706 | 92.9933 | 32.7763 | 33.6594 | 35.3611 | 34.0281 | 33.6683 | 33.987 | 35.3314 | 34.7214 | 34.5489 | 37.4198 | 36.3404 | 33.9819 | 34.6327 | 36.3572 | 36.8075 | 37.5745 | 36.3546 | 34.0159 | 33.0083 | 34.6794 | 35.1384 | 32.9881 | 34.4159 | 34.3545 | 33.376 | 34.4565 | 34.5286 | 34.3892 | 33.949 | 34.4804 | 35.4439 | 35.6669 | 35.7896 | 35.7323 | 33.9397 | 93.3159 | 93.3102 | 93.3237
2022-09-08 01:14 | 3:23 | 16.75 | 17.0311 | 19.1032 | 34.0056 | 34.3554 | 34.3313 | 35.1577 | 35.6285 | 36.7443 | 37.3759 | 36.7938 | 37.6971 | 34.459 | 34.4442 | 34.8456 | 35.673 | 35.9473 | 36.3411 | 36.8278 | 37.1236 | 20.9089 | 16.7115 | 93.2533 | 32.7933 | 33.6836 | 35.368 | 34.0115 | 33.6633 | 33.9806 | 35.322 | 34.7223 | 34.5615 | 37.3946 | 36.3622 | 33.9781 | 34.6473 | 36.3328 | 36.8184 | 37.5742 | 36.3657 | 34.0265 | 33.0116 | 34.6775 | 35.1367 | 32.9925 | 34.4064 | 34.3578 | 33.3754 | 34.4695 | 34.52 | 34.3941 | 33.9481 | 34.4565 | 35.4636 | 35.6638 | 35.7756 | 35.7491 | 33.9403 | 93.4166 | 93.4141 | 93.4039
2022-09-08 01:14 | 3:24 | 16.77 | 17.0713 | 19.0691 | 34.0848 | 34.3501 | 34.3217 | 35.1665 | 35.6445 | 36.7404 | 37.386 | 36.7712 | 37.6947 | 34.4436 | 34.4433 | 34.8634 | 35.6736 | 35.9225 | 36.3474 | 36.8201 | 37.1202 | 20.9084 | 16.7354 | 93.3735 | 32.843 | 33.6613 | 35.3613 | 34.023 | 33.672 | 33.9715 | 35.3322 | 34.7191 | 34.5585 | 37.4053 | 36.3473 | 33.9703 | 34.6384 | 36.3404 | 36.8245 | 37.5868 | 36.3627 | 34.0008 | 32.9832 | 34.6778 | 35.1367 | 32.9864 | 34.4028 | 34.3728 | 33.359 | 34.4558 | 34.5276 | 34.4079 | 33.9434 | 34.4695 | 35.4426 | 35.6561 | 35.8001 | 35.7439 | 33.9391 | 93.5903 | 93.5369 | 93.5298
2022-09-08 01:14 | 3:24 | 16.7264 | 17.0196 | 19.0509 | 34.0075 | 34.3571 | 34.3332 | 35.1622 | 35.6437 | 36.7227 | 37.3866 | 36.7833 | 37.6993 | 34.4778 | 34.4596 | 34.8656 | 35.6732 | 35.9228 | 36.3416 | 36.8332 | 37.1164 | 20.9036 | 16.6929 | 93.4091 | 32.7932 | 33.6539 | 35.3724 | 34.0312 | 33.6814 | 33.9861 | 35.3289 | 34.7196 | 34.5508 | 37.4071 | 36.3236 | 33.969 | 34.6326 | 36.3622 | 36.8201 | 37.5759 | 36.3572 | 34.0224 | 32.9884 | 34.6631 | 35.1303 | 32.9725 | 34.4004 | 34.3603 | 33.3745 | 34.4459 | 34.5259 | 34.413 | 33.9684 | 34.4558 | 35.441 | 35.636 | 35.7858 | 35.7462 | 33.9596 | 93.7119 | 93.6541 | 93.6131
2022-09-08 01:14 | 3:24 | 16.8016 | 17.0983 | 19.09 | 34.0114 | 34.3721 | 34.3254 | 35.1445 | 35.6602 | 36.7465 | 37.3828 | 36.7792 | 37.69 | 34.48 | 34.4457 | 34.8642 | 35.6638 | 35.9201 | 36.3388 | 36.8193 | 37.1184 | 20.8978 | 16.6961 | 93.4668 | 32.7954 | 33.6549 | 35.3499 | 34.0159 | 33.6912 | 33.9819 | 35.3211 | 34.7267 | 34.5443 | 37.4148 | 36.3245 | 33.964 | 34.6217 | 36.3473 | 36.8211 | 37.599 | 36.3328 | 34.002 | 32.9893 | 34.6542 | 35.1388 | 32.9502 | 34.3999 | 34.3712 | 33.3403 | 34.4397 | 34.5264 | 34.4139 | 33.927 | 34.4459 | 35.4518 | 35.6507 | 35.8017 | 35.7375 | 33.9493 | 93.8211 | 93.894 | 93.5832
2022-09-08 01:14 | 3:24 | 16.7663 | 17.0914 | 19.0896 | 34.0609 | 34.3577 | 34.3128 | 35.1431 | 35.6519 | 36.7439 | 37.3827 | 36.79 | 37.6858 | 34.4678 | 34.4453 | 34.8674 | 35.6545 | 35.8986 | 36.3457 | 36.811 | 37.116 | 20.8869 | 16.7168 | 93.6687 | 32.9809 | 33.6514 | 35.3463 | 34.0265 | 33.6622 | 33.9781 | 35.3113 | 34.7056 | 34.5445 | 37.4027 | 36.3475 | 33.9655 | 34.6299 | 36.3236 | 36.8232 | 37.5783 | 36.3404 | 33.9914 | 32.9846 | 34.6568 | 35.1227 | 32.9648 | 34.4069 | 34.3591 | 33.3775 | 34.4423 | 34.5164 | 34.4005 | 33.9521 | 34.4397 | 35.4563 | 35.6584 | 35.7715 | 35.7585 | 33.932 | 93.9568 | 94.0023 | 93.7317
2022-09-08 01:14 | 3:24 | 16.7712 | 17.0514 | 19.0613 | 33.9673 | 34.3799 | 34.3243 | 35.1543 | 35.6345 | 36.7181 | 37.3991 | 36.7693 | 37.6902 | 34.486 | 34.4519 | 34.8644 | 35.6602 | 35.9088 | 36.3407 | 36.8224 | 37.1308 | 20.8516 | 16.7121 | 93.788 | 32.8982 | 33.6609 | 35.3621 | 34.0008 | 33.6653 | 33.9703 | 35.312 | 34.7123 | 34.542 | 37.3985 | 36.328 | 33.9522 | 34.6185 | 36.3245 | 36.8152 | 37.5609 | 36.3622 | 34.0204 | 32.9796 | 34.6456 | 35.1205 | 32.9587 | 34.4079 | 34.3628 | 33.3661 | 34.443 | 34.5196 | 34.4228 | 33.9642 | 34.4423 | 35.4683 | 35.6492 | 35.8068 | 35.733 | 33.9134 | 94.0998 | 94.2188 | 93.842
2022-09-08 01:15 | 3:25 | 16.6936 | 17.0358 | 19.0479 | 33.9751 | 34.3784 | 34.2969 | 35.1419 | 35.6431 | 36.7141 | 37.3912 | 36.7991 | 37.6921 | 34.4632 | 34.4597 | 34.8645 | 35.6568 | 35.9129 | 36.3308 | 36.8142 | 37.1186 | 20.8576 | 16.6894 | 93.7939 | 32.7023 | 33.6463 | 35.3336 | 34.0224 | 33.6519 | 33.969 | 35.325 | 34.7033 | 34.5531 | 37.4098 | 36.3255 | 33.9516 | 34.6119 | 36.3475 | 36.8312 | 37.5575 | 36.3473 | 33.994 | 32.9603 | 34.6642 | 35.1151 | 32.9514 | 34.414 | 34.3625 | 33.3536 | 34.4518 | 34.5234 | 34.428 | 33.9384 | 34.443 | 35.4669 | 35.6422 | 35.7956 | 35.7428 | 33.922 | 94.1209 | 94.3459 | 93.7682
2022-09-08 01:15 | 3:25 | 16.7795 | 17.0738 | 19.0736 | 34.0082 | 34.3816 | 34.2876 | 35.1454 | 35.6362 | 36.7268 | 37.3989 | 36.7805 | 37.702 | 34.4693 | 34.4354 | 34.8544 | 35.6499 | 35.9041 | 36.3482 | 36.8297 | 37.1014 | 20.8447 | 16.7337 | 93.9144 | 32.6783 | 33.6307 | 35.3394 | 34.002 | 33.6688 | 33.964 | 35.2987 | 34.6943 | 34.5295 | 37.4094 | 36.3256 | 33.9579 | 34.6345 | 36.328 | 36.7974 | 37.5652 | 36.3236 | 33.9863 | 32.9583 | 34.6452 | 35.1052 | 32.9459 | 34.4321 | 34.3835 | 33.3403 | 34.437 | 34.5318 | 34.4127 | 33.936 | 34.4518 | 35.4387 | 35.6388 | 35.7928 | 35.7338 | 33.9425 | 94.3029 | 94.4712 | 93.8782
2022-09-08 01:15 | 3:25 | 16.7346 | 17.0572 | 19.0705 | 33.9634 | 34.3632 | 34.3006 | 35.1474 | 35.6142 | 36.7336 | 37.3854 | 36.7694 | 37.6953 | 34.499 | 34.465 | 34.8474 | 35.6542 | 35.895 | 36.3475 | 36.8148 | 37.1135 | 20.8256 | 16.7208 | 94.0005 | 32.8215 | 33.6361 | 35.3515 | 33.9914 | 33.6616 | 33.9655 | 35.3189 | 34.702 | 34.5376 | 37.4018 | 36.3593 | 33.9513 | 34.5944 | 36.3255 | 36.8102 | 37.5628 | 36.3245 | 33.9661 | 32.9588 | 34.6461 | 35.0986 | 32.9223 | 34.4082 | 34.3499 | 33.3421 | 34.4467 | 34.523 | 34.4023 | 33.9481 | 34.437 | 35.4784 | 35.6282 | 35.788 | 35.7512 | 33.9175 | 94.4914 | 94.6198 | 94.0281
2022-09-08 01:15 | 3:25 | 16.7347 | 17.0356 | 19.0854 | 33.9613 | 34.3705 | 34.3062 | 35.1428 | 35.6352 | 36.7256 | 37.3767 | 36.7748 | 37.7089 | 34.49 | 34.4532 | 34.8469 | 35.6718 | 35.8795 | 36.3229 | 36.8244 | 37.088 | 20.8231 | 16.691 | 94.0411 | 32.8376 | 33.6416 | 35.3223 | 34.0204 | 33.6614 | 33.9522 | 35.3335 | 34.7019 | 34.5323 | 37.3964 | 36.3494 | 33.953 | 34.616 | 36.3256 | 36.8243 | 37.5523 | 36.3475 | 33.9823 | 32.964 | 34.6374 | 35.099 | 32.9524 | 34.4182 | 34.3518 | 33.3441 | 34.429 | 34.5256 | 34.421 | 33.9385 | 34.4467 | 35.4441 | 35.6393 | 35.8014 | 35.7339 | 33.924 | 94.7185 | 94.7403 | 94.2428
2022-09-08 01:15 | 3:25 | 16.7413 | 17.0181 | 19.0232 | 33.9685 | 34.3728 | 34.3081 | 35.1439 | 35.6269 | 36.7248 | 37.3787 | 36.774 | 37.6992 | 34.4802 | 34.4507 | 34.8444 | 35.6453 | 35.8899 | 36.3254 | 36.8011 | 37.0971 | 20.81 | 16.72 | 93.8504 | 32.9038 | 33.618 | 35.3049 | 33.994 | 33.6558 | 33.9516 | 35.3064 | 34.7013 | 34.54 | 37.3914 | 36.3116 | 33.9333 | 34.6132 | 36.3593 | 36.8052 | 37.549 | 36.328 | 33.9716 | 32.9609 | 34.622 | 35.0831 | 32.9221 | 34.4147 | 34.3533 | 33.3194 | 34.4404 | 34.5383 | 34.4118 | 33.9276 | 34.429 | 35.4489 | 35.6333 | 35.7917 | 35.7389 | 33.899 | 94.8555 | 94.8342 | 94.2382
2022-09-08 01:15 | 3:25 | 16.7324 | 17.0245 | 19.0214 | 33.8733 | 34.3638 | 34.2871 | 35.1404 | 35.6214 | 36.7147 | 37.3702 | 36.7885 | 37.7079 | 34.4823 | 34.458 | 34.8285 | 35.6352 | 35.8846 | 36.3461 | 36.7857 | 37.0937 | 20.8209 | 16.6718 | 94.2284 | 32.7538 | 33.6205 | 35.3112 | 33.9863 | 33.6534 | 33.9579 | 35.3059 | 34.7016 | 34.5205 | 37.3912 | 36.3379 | 33.9477 | 34.611 | 36.3494 | 36.7964 | 37.5581 | 36.3255 | 33.9679 | 32.9438 | 34.6148 | 35.0663 | 32.9368 | 34.4103 | 34.3676 | 33.3363 | 34.4295 | 34.5317 | 34.4243 | 33.9245 | 34.4404 | 35.4412 | 35.6343 | 35.7909 | 35.7338 | 33.8959 | 94.9033 | 94.9404 | 94.2751
2022-09-08 01:16 | 3:25 | 16.7152 | 17.0023 | 19.0008 | 33.9712 | 34.3801 | 34.2894 | 35.1392 | 35.6207 | 36.7055 | 37.3541 | 36.7928 | 37.6938 | 34.4894 | 34.4474 | 34.8279 | 35.6493 | 35.8831 | 36.3158 | 36.7885 | 37.0793 | 20.8159 | 16.6059 | 94.124 | 32.9051 | 33.6195 | 35.3398 | 33.9661 | 33.6406 | 33.9513 | 35.2812 | 34.6791 | 34.5207 | 37.3757 | 36.3285 | 33.924 | 34.6208 | 36.3116 | 36.7938 | 37.5379 | 36.3256 | 33.9742 | 32.9474 | 34.612 | 35.0551 | 32.9207 | 34.4113 | 34.3614 | 33.3103 | 34.4351 | 34.5299 | 34.4173 | 33.9156 | 34.4295 | 35.4462 | 35.6417 | 35.7812 | 35.7309 | 33.8885 | 95.0226 | 95.0179 | 94.3743
2022-09-08 01:16 | 3:26 | 16.7297 | 16.9812 | 18.9989 | 33.9567 | 34.3706 | 34.2777 | 35.1324 | 35.6062 | 36.6982 | 37.3573 | 36.7805 | 37.6796 | 34.4669 | 34.4783 | 34.8102 | 35.641 | 35.871 | 36.3267 | 36.8164 | 37.0706 | 20.8187 | 16.6379 | 94.0369 | 32.9245 | 33.6082 | 35.3236 | 33.9823 | 33.6518 | 33.953 | 35.2858 | 34.686 | 34.5014 | 37.3895 | 36.3276 | 33.9352 | 34.6019 | 36.3379 | 36.7766 | 37.5339 | 36.3593 | 33.979 | 32.9354 | 34.6125 | 35.0547 | 32.8981 | 34.4163 | 34.3413 | 33.3356 | 34.4223 | 34.5159 | 34.4247 | 33.9254 | 34.4351 | 35.4505 | 35.6273 | 35.7766 | 35.7333 | 33.8735 | 95.1086 | 95.0891 | 94.3879
2022-09-08 01:16 | 3:26 | 16.7067 | 17.0211 | 19.0187 | 33.9381 | 34.366 | 34.2863 | 35.1038 | 35.6238 | 36.7003 | 37.3558 | 36.7631 | 37.6754 | 34.4876 | 34.469 | 34.8094 | 35.644 | 35.8669 | 36.3162 | 36.7952 | 37.0808 | 20.8197 | 16.6035 | 93.8772 | 32.6163 | 33.613 | 35.3048 | 33.9716 | 33.646 | 33.9333 | 35.2856 | 34.6967 | 34.5174 | 37.3899 | 36.3245 | 33.9496 | 34.6144 | 36.3285 | 36.8003 | 37.5453 | 36.3494 | 33.9723 | 32.9483 | 34.5956 | 35.054 | 32.8898 | 34.4302 | 34.3613 | 33.3083 | 34.4075 | 34.5281 | 34.4217 | 33.9178 | 34.4223 | 35.4279 | 35.6268 | 35.7813 | 35.7422 | 33.8819 | 95.1221 | 95.1158 | 94.5025
2022-09-08 01:16 | 3:26 | 16.6588 | 17.0043 | 19.0203 | 33.9328 | 34.3873 | 34.269 | 35.118 | 35.5916 | 36.6859 | 37.3498 | 36.7727 | 37.6932 | 34.4797 | 34.4585 | 34.8192 | 35.6419 | 35.8745 | 36.3059 | 36.7884 | 37.0721 | 20.8368 | 16.6412 | 93.7481 | 32.7562 | 33.612 | 35.3183 | 33.9679 | 33.618 | 33.9477 | 35.3022 | 34.6964 | 34.5088 | 37.3897 | 36.3248 | 33.9206 | 34.5953 | 36.3276 | 36.7827 | 37.5198 | 36.3116 | 33.9466 | 32.924 | 34.59 | 35.0481 | 32.8954 | 34.4363 | 34.3661 | 33.2862 | 34.4201 | 34.5265 | 34.426 | 33.9176 | 34.4075 | 35.437 | 35.6217 | 35.7724 | 35.7398 | 33.8483 | 94.9569 | 95.0501 | 94.3041
2022-09-08 01:16 | 3:26 | 16.7314 | 17.0304 | 19.028 | 33.9213 | 34.3551 | 34.2658 | 35.0992 | 35.59 | 36.6999 | 37.3733 | 36.7707 | 37.664 | 34.4893 | 34.4428 | 34.8066 | 35.6202 | 35.8609 | 36.2945 | 36.7743 | 37.059 | 20.8659 | 16.6593 | 93.6434 | 32.6955 | 33.5908 | 35.3119 | 33.9742 | 33.636 | 33.924 | 35.2733 | 34.7004 | 34.5073 | 37.3758 | 36.3083 | 33.9341 | 34.595 | 36.3245 | 36.7896 | 37.546 | 36.3379 | 33.9667 | 32.9156 | 34.5889 | 35.0333 | 32.874 | 34.4237 | 34.3659 | 33.2923 | 34.4168 | 34.5041 | 34.4297 | 33.9172 | 34.4201 | 35.4246 | 35.6288 | 35.7786 | 35.7069 | 33.854 | 94.6693 | 94.8481 | 94.1495
2022-09-08 01:16 | 3:26 | 16.6967 | 17.042 | 19.0234 | 33.914 | 34.3778 | 34.2688 | 35.1086 | 35.6036 | 36.6804 | 37.3308 | 36.7799 | 37.6842 | 34.4851 | 34.4408 | 34.8088 | 35.6345 | 35.858 | 36.3015 | 36.776 | 37.0605 | 20.8831 | 16.6162 | 93.5857 | 32.852 | 33.5874 | 35.3003 | 33.979 | 33.6346 | 33.9352 | 35.2837 | 34.6882 | 34.5063 | 37.3788 | 36.3432 | 33.9297 | 34.5907 | 36.3248 | 36.7851 | 37.526 | 36.3285 | 33.9577 | 32.9084 | 34.5766 | 35.0356 | 32.8867 | 34.4293 | 34.361 | 33.2828 | 34.4184 | 34.5163 | 34.441 | 33.9147 | 34.4168 | 35.4283 | 35.6063 | 35.7848 | 35.7319 | 33.8672 | 94.3947 | 94.5975 | 94.007
2022-09-08 01:17 | 3:27 | 16.7336 | 17.069 | 19.0403 | 33.8846 | 34.3713 | 34.2677 | 35.1105 | 35.5946 | 36.679 | 37.3539 | 36.7775 | 37.687 | 34.4894 | 34.4549 | 34.8023 | 35.6318 | 35.8559 | 36.3112 | 36.7645 | 37.0553 | 20.9138 | 16.6331 | 93.5195 | 32.8276 | 33.5928 | 35.304 | 33.9723 | 33.6314 | 33.9496 | 35.2856 | 34.6814 | 34.4942 | 37.3757 | 36.3131 | 33.9511 | 34.6072 | 36.3083 | 36.7885 | 37.5307 | 36.3276 | 33.9597 | 32.9054 | 34.5646 | 35.0373 | 32.8834 | 34.4425 | 34.3587 | 33.3056 | 34.4179 | 34.5282 | 34.4365 | 33.9151 | 34.4184 | 35.4325 | 35.6171 | 35.8035 | 35.7217 | 33.8515 | 94.1911 | 94.3865 | 93.8569
2022-09-08 01:17 | 3:27 | 16.674 | 16.9934 | 19.0101 | 33.8859 | 34.3633 | 34.2652 | 35.104 | 35.6158 | 36.6947 | 37.3457 | 36.789 | 37.6846 | 34.4819 | 34.4617 | 34.8015 | 35.6237 | 35.8531 | 36.2957 | 36.7594 | 37.0611 | 20.9417 | 16.5977 | 93.4873 | 32.8935 | 33.5848 | 35.3064 | 33.9466 | 33.5944 | 33.9206 | 35.2826 | 34.6801 | 34.5055 | 37.3603 | 36.334 | 33.9255 | 34.5988 | 36.3432 | 36.7762 | 37.544 | 36.3245 | 33.9575 | 32.8868 | 34.5636 | 35.0212 | 32.8664 | 34.4411 | 34.3718 | 33.2899 | 34.3846 | 34.5365 | 34.4279 | 33.9127 | 34.4179 | 35.4275 | 35.6159 | 35.7889 | 35.7268 | 33.8489 | 94.0472 | 94.2119 | 93.7423
2022-09-08 01:17 | 3:27 | 16.666 | 16.969 | 19.011 | 33.8801 | 34.3766 | 34.2713 | 35.1141 | 35.586 | 36.6875 | 37.3401 | 36.7801 | 37.7017 | 34.5033 | 34.4611 | 34.8034 | 35.631 | 35.8466 | 36.3013 | 36.7643 | 37.0525 | 20.9462 | 16.6439 | 93.1262 | 32.6796 | 33.5919 | 35.2944 | 33.9667 | 33.6238 | 33.9341 | 35.2959 | 34.6815 | 34.5037 | 37.3681 | 36.3107 | 33.9202 | 34.6108 | 36.3131 | 36.7551 | 37.524 | 36.3248 | 33.9512 | 32.9033 | 34.5584 | 35.0124 | 32.8826 | 34.424 | 34.3258 | 33.2927 | 34.3978 | 34.5052 | 34.437 | 33.9084 | 34.3846 | 35.4171 | 35.6272 | 35.7987 | 35.7248 | 33.833 | 93.8809 | 94.0261 | 93.644
2022-09-08 01:17 | 3:27 | 16.7441 | 17.0504 | 19.0289 | 33.881 | 34.3783 | 34.2702 | 35.0926 | 35.6004 | 36.7039 | 37.3522 | 36.7799 | 37.6939 | 34.5032 | 34.4674 | 34.7886 | 35.6217 | 35.851 | 36.2934 | 36.7745 | 37.0298 | 20.9278 | 16.6574 | 93.17 | 32.5498 | 33.5802 | 35.2977 | 33.9577 | 33.626 | 33.9297 | 35.2939 | 34.6874 | 34.5085 | 37.3648 | 36.3629 | 33.9141 | 34.6107 | 36.334 | 36.7673 | 37.5373 | 36.3083 | 33.9595 | 32.8904 | 34.5554 | 35.0156 | 32.86 | 34.44 | 34.368 | 33.2699 | 34.3915 | 34.5077 | 34.4252 | 33.8996 | 34.3978 | 35.422 | 35.6033 | 35.7878 | 35.7268 | 33.8443 | 93.8423 | 93.9473 | 93.6223
2022-09-08 01:17 | 3:27 | 16.705 | 16.9666 | 18.9811 | 33.8733 | 34.3802 | 34.2736 | 35.0989 | 35.5949 | 36.691 | 37.3338 | 36.7678 | 37.6928 | 34.5095 | 34.4669 | 34.7817 | 35.6428 | 35.8345 | 36.2893 | 36.7661 | 37.0407 | 20.943 | 16.6015 | 93.0752 | 32.8165 | 33.5767 | 35.2903 | 33.9597 | 33.6333 | 33.9511 | 35.2711 | 34.6816 | 34.5073 | 37.3723 | 36.3253 | 33.9103 | 34.5852 | 36.3107 | 36.7737 | 37.5145 | 36.3432 | 33.9404 | 32.8845 | 34.5652 | 35.0259 | 32.8728 | 34.4454 | 34.3634 | 33.2658 | 34.4027 | 34.5046 | 34.4519 | 33.8866 | 34.3915 | 35.4351 | 35.6037 | 35.8003 | 35.7047 | 33.8444 | 93.7189 | 93.9139 | 93.5349
2022-09-08 01:17 | 3:27 | 16.6673 | 16.9623 | 18.9921 | 33.9172 | 34.3824 | 34.2548 | 35.1003 | 35.5922 | 36.6757 | 37.3319 | 36.7789 | 37.6853 | 34.4768 | 34.4645 | 34.7669 | 35.6185 | 35.8357 | 36.3043 | 36.7667 | 37.0575 | 20.9896 | 16.6015 | 93.1004 | 32.7486 | 33.5727 | 35.3155 | 33.9575 | 33.621 | 33.9255 | 35.2796 | 34.6885 | 34.5213 | 37.3716 | 36.323 | 33.9304 | 34.6078 | 36.3629 | 36.7794 | 37.5266 | 36.3131 | 33.9397 | 32.8993 | 34.5528 | 34.9924 | 32.8792 | 34.4384 | 34.3498 | 33.2727 | 34.404 | 34.5253 | 34.4396 | 33.8974 | 34.4027 | 35.4187 | 35.6182 | 35.7946 | 35.7294 | 33.8235 | 93.6622 | 93.8331 | 93.529
2022-09-08 01:18 | 3:27 | 16.6814 | 16.9663 | 18.9795 | 33.9517 | 34.3835 | 34.2571 | 35.1089 | 35.5943 | 36.6884 | 37.3373 | 36.7723 | 37.6934 | 34.5128 | 34.4557 | 34.8075 | 35.6348 | 35.8392 | 36.2912 | 36.7623 | 37.0647 | 21.0469 | 16.6131 | 93.0917 | 32.9374 | 33.5857 | 35.3055 | 33.9512 | 33.6135 | 33.9202 | 35.2689 | 34.6913 | 34.4927 | 37.3719 | 36.3294 | 33.9136 | 34.6104 | 36.3253 | 36.7661 | 37.5167 | 36.334 | 33.9539 | 32.9061 | 34.5483 | 35.0078 | 32.8448 | 34.4509 | 34.3538 | 33.2637 | 34.394 | 34.4931 | 34.4511 | 33.8969 | 34.404 | 35.4026 | 35.6091 | 35.7839 | 35.7261 | 33.824 | 93.6103 | 93.715 | 93.5023
2022-09-08 01:18 | 3:28 | 16.7023 | 16.9971 | 18.9968 | 33.9466 | 34.3919 | 34.2514 | 35.0912 | 35.5976 | 36.6564 | 37.348 | 36.7833 | 37.6914 | 34.4866 | 34.453 | 34.785 | 35.6232 | 35.8044 | 36.2747 | 36.7646 | 37.0408 | 21.0414 | 16.6168 | 93.1786 | 32.7654 | 33.5791 | 35.2967 | 33.9595 | 33.6018 | 33.9141 | 35.2866 | 34.6954 | 34.5162 | 37.367 | 36.3225 | 33.9147 | 34.6044 | 36.323 | 36.7971 | 37.5174 | 36.3107 | 33.9676 | 32.8657 | 34.5705 | 34.9866 | 32.8713 | 34.4368 | 34.3479 | 33.2874 | 34.3853 | 34.502 | 34.4442 | 33.9051 | 34.394 | 35.4168 | 35.6232 | 35.7983 | 35.7387 | 33.8452 | 93.4766 | 93.6253 | 93.407
2022-09-08 01:18 | 3:28 | 16.7453 | 17.0296 | 19.0406 | 33.8452 | 34.3925 | 34.2334 | 35.0914 | 35.5962 | 36.6689 | 37.3346 | 36.8013 | 37.6995 | 34.4986 | 34.4808 | 34.7887 | 35.6189 | 35.8214 | 36.293 | 36.7512 | 37.0451 | 21.0164 | 16.626 | 93.0536 | 32.7631 | 33.5773 | 35.31 | 33.9404 | 33.607 | 33.9103 | 35.286 | 34.6981 | 34.5222 | 37.368 | 36.3303 | 33.9123 | 34.6022 | 36.3294 | 36.7757 | 37.5153 | 36.3629 | 33.949 | 32.8704 | 34.5656 | 35.0009 | 32.8518 | 34.4566 | 34.3627 | 33.2787 | 34.4028 | 34.4957 | 34.4433 | 33.9024 | 34.3853 | 35.4295 | 35.6136 | 35.8072 | 35.7418 | 33.8355 | 93.426 | 93.548 | 93.4129
2022-09-08 01:18 | 3:28 | 15.5723 | 16.6487 | 18.7674 | 33.8802 | 34.3942 | 34.2761 | 35.1079 | 35.5938 | 36.6658 | 37.3418 | 36.7789 | 37.7078 | 34.5178 | 34.4654 | 34.7651 | 35.6226 | 35.8293 | 36.293 | 36.7781 | 37.0483 | 21.0291 | 16.9249 | 93.0706 | 32.744 | 33.572 | 35.309 | 33.9397 | 33.6261 | 33.9304 | 35.2649 | 34.6968 | 34.5045 | 37.3637 | 36.3014 | 33.9132 | 34.6083 | 36.3225 | 36.7811 | 37.5139 | 36.3253 | 33.9198 | 32.8638 | 34.5416 | 34.9999 | 32.8546 | 34.4528 | 34.3617 | 33.2387 | 34.3963 | 34.4831 | 34.4596 | 33.8914 | 34.4028 | 35.4198 | 35.63 | 35.7903 | 35.721 | 33.8192 | 93.3568 | 93.4825 | 93.4051
2022-09-08 01:18 | 3:28 | 15.0853 | 16.2455 | 18.3591 | 33.8338 | 34.3892 | 34.2551 | 35.0814 | 35.5789 | 36.6707 | 37.3368 | 36.7866 | 37.6838 | 34.5075 | 34.4572 | 34.7749 | 35.6244 | 35.8095 | 36.2908 | 36.7696 | 37.0413 | 21.4169 | 17.7451 | 93.106 | 32.8765 | 33.5646 | 35.2935 | 33.9539 | 33.6222 | 33.9136 | 35.26 | 34.6974 | 34.519 | 37.3678 | 36.3242 | 33.9176 | 34.5989 | 36.3303 | 36.7664 | 37.532 | 36.323 | 33.937 | 32.8725 | 34.5416 | 34.9716 | 32.8387 | 34.4496 | 34.3503 | 33.2563 | 34.3786 | 34.4669 | 34.4457 | 33.8859 | 34.3963 | 35.3915 | 35.6161 | 35.7855 | 35.7185 | 33.8189 | 93.323 | 93.4887 | 93.3447
2022-09-08 01:18 | 3:28 | 14.8558 | 16.0569 | 18.134 | 33.8032 | 34.3941 | 34.2507 | 35.0707 | 35.5933 | 36.6634 | 37.3187 | 36.7964 | 37.6921 | 34.5197 | 34.4861 | 34.7719 | 35.621 | 35.828 | 36.3011 | 36.7435 | 37.0358 | 22.0707 | 18.8475 | 92.7752 | 33.0048 | 33.5694 | 35.2986 | 33.9676 | 33.6011 | 33.9147 | 35.2664 | 34.6867 | 34.5226 | 37.3821 | 36.3253 | 33.9069 | 34.5961 | 36.3014 | 36.7733 | 37.5113 | 36.3294 | 33.9389 | 32.8432 | 34.5622 | 34.9911 | 32.833 | 34.4403 | 34.3367 | 33.2466 | 34.3816 | 34.4927 | 34.4453 | 33.9025 | 34.3786 | 35.437 | 35.6029 | 35.7884 | 35.7412 | 33.811 | 93.2861 | 93.459 | 93.2895
2022-09-08 01:19 | 3:29 | 14.5048 | 15.7989 | 17.8984 | 33.8666 | 34.4079 | 34.2487 | 35.0805 | 35.5916 | 36.6802 | 37.3319 | 36.7922 | 37.7072 | 34.5078 | 34.4672 | 34.7712 | 35.6276 | 35.8089 | 36.2946 | 36.7686 | 37.0431 | 22.8463 | 20.0424 | 92.7804 | 33.0745 | 33.5819 | 35.3057 | 33.949 | 33.6219 | 33.9123 | 35.2692 | 34.6885 | 34.4918 | 37.3578 | 36.3242 | 33.9056 | 34.5961 | 36.3242 | 36.7786 | 37.523 | 36.3225 | 33.928 | 32.8887 | 34.5433 | 34.9989 | 32.8466 | 34.4414 | 34.3436 | 33.2428 | 34.3742 | 34.4716 | 34.4519 | 33.8946 | 34.3816 | 35.4108 | 35.5957 | 35.772 | 35.7226 | 33.8106 | 93.2401 | 93.4063 | 93.2616
2022-09-08 01:19 | 3:29 | 14.3363 | 15.6684 | 17.7009 | 33.8479 | 34.413 | 34.2474 | 35.0808 | 35.5774 | 36.6589 | 37.3315 | 36.776 | 37.7116 | 34.5153 | 34.4714 | 34.7785 | 35.6302 | 35.8129 | 36.2876 | 36.7739 | 37.0409 | 23.6546 | 21.2521 | 92.8349 | 33.1532 | 33.5553 | 35.2905 | 33.9198 | 33.6242 | 33.9132 | 35.2753 | 34.6917 | 34.5162 | 37.3574 | 36.3183 | 33.9013 | 34.5975 | 36.3253 | 36.7633 | 37.5108 | 36.3303 | 33.953 | 32.8569 | 34.5448 | 35.0072 | 32.8459 | 34.4326 | 34.3611 | 33.2403 | 34.369 | 34.4777 | 34.4597 | 33.8831 | 34.3742 | 35.4301 | 35.605 | 35.8014 | 35.7324 | 33.8277 | 93.0679 | 93.3789 | 93.2062
2022-09-08 01:19 | 3:29 | 14.1319 | 15.5006 | 17.5757 | 33.7201 | 34.4139 | 34.2516 | 35.0811 | 35.5767 | 36.6621 | 37.322 | 36.7769 | 37.6979 | 34.5134 | 34.4702 | 34.7556 | 35.6215 | 35.8083 | 36.2808 | 36.7639 | 37.022 | 24.4381 | 22.4393 | 92.6487 | 33.2162 | 33.569 | 35.2741 | 33.937 | 33.624 | 33.9176 | 35.2785 | 34.6877 | 34.4965 | 37.3564 | 36.3075 | 33.896 | 34.5805 | 36.3242 | 36.7874 | 37.5148 | 36.3014 | 33.9271 | 32.8561 | 34.5404 | 34.9797 | 32.8335 | 34.458 | 34.364 | 33.2398 | 34.3625 | 34.472 | 34.4354 | 33.9012 | 34.369 | 35.4344 | 35.6094 | 35.8117 | 35.7153 | 33.8387 | 93.0546 | 93.1248 | 93.1725
2022-09-08 01:19 | 3:29 | 13.9195 | 15.3451 | 17.3933 | 33.7182 | 34.4005 | 34.2383 | 35.0527 | 35.6004 | 36.6694 | 37.3373 | 36.7861 | 37.6995 | 34.5185 | 34.468 | 34.7582 | 35.6319 | 35.8045 | 36.2761 | 36.76 | 37.03 | 25.2154 | 23.5276 | 92.7155 | 33.2797 | 33.575 | 35.2957 | 33.9389 | 33.614 | 33.9069 | 35.2653 | 34.7007 | 34.4885 | 37.3788 | 36.3094 | 33.9107 | 34.6021 | 36.3183 | 36.7822 | 37.5116 | 36.3242 | 33.9229 | 32.8583 | 34.5612 | 34.9809 | 32.8539 | 34.4617 | 34.3409 | 33.258 | 34.3686 | 34.4674 | 34.465 | 33.8713 | 34.3625 | 35.4337 | 35.5934 | 35.8161 | 35.7346 | 33.8165 | 92.9902 | 93.0467 | 93.092
2022-09-08 01:19 | 3:29 | 13.7382 | 15.1342 | 17.2371 | 33.7347 | 34.4228 | 34.2405 | 35.0784 | 35.6009 | 36.6859 | 37.32 | 36.7976 | 37.7026 | 34.5114 | 34.4695 | 34.7646 | 35.6255 | 35.7924 | 36.2895 | 36.7627 | 37.0263 | 25.9104 | 24.4666 | 92.6281 | 33.3136 | 33.5802 | 35.2916 | 33.928 | 33.6109 | 33.9056 | 35.2707 | 34.6766 | 34.5039 | 37.3793 | 36.316 | 33.915 | 34.6018 | 36.3075 | 36.781 | 37.5064 | 36.3253 | 33.9195 | 32.8502 | 34.5477 | 34.9969 | 32.8383 | 34.4287 | 34.3465 | 33.2361 | 34.3632 | 34.462 | 34.4532 | 33.8709 | 34.3686 | 35.4305 | 35.6084 | 35.8112 | 35.7434 | 33.8217 | 92.9003 | 93.0303 | 93.0471
2022-09-08 01:19 | 3:29 | 13.5871 | 14.9845 | 17.0691 | 33.744 | 34.428 | 34.2455 | 35.0602 | 35.5844 | 36.686 | 37.3259 | 36.7894 | 37.7002 | 34.5304 | 34.4764 | 34.7735 | 35.6052 | 35.7977 | 36.2899 | 36.7521 | 37.0328 | 26.5402 | 25.3252 | 92.5052 | 33.3712 | 33.5771 | 35.2972 | 33.953 | 33.621 | 33.9013 | 35.275 | 34.6964 | 34.5047 | 37.3721 | 36.3104 | 33.9114 | 34.5851 | 36.3094 | 36.784 | 37.5067 | 36.3242 | 33.9079 | 32.8385 | 34.5704 | 35.0064 | 32.8466 | 34.4475 | 34.3507 | 33.2469 | 34.3732 | 34.4595 | 34.4507 | 33.8754 | 34.3632 | 35.4533 | 35.6116 | 35.802 | 35.7381 | 33.8254 | 92.8073 | 92.9629 | 93.0134
2022-09-08 01:20 | 3:29 | 13.4772 | 14.8528 | 16.9681 | 33.6838 | 34.4127 | 34.2168 | 35.0664 | 35.5732 | 36.6873 | 37.3541 | 36.8055 | 37.7209 | 34.5156 | 34.4903 | 34.755 | 35.6078 | 35.8023 | 36.2851 | 36.7622 | 37.047 | 27.1228 | 26.0354 | 92.4933 | 33.3609 | 33.5877 | 35.2996 | 33.9271 | 33.6216 | 33.896 | 35.2785 | 34.7032 | 34.4896 | 37.3536 | 36.3052 | 33.8957 | 34.6046 | 36.316 | 36.7857 | 37.5136 | 36.3183 | 33.92 | 32.8596 | 34.5546 | 35.0176 | 32.8436 | 34.4374 | 34.3516 | 33.2427 | 34.3588 | 34.4501 | 34.458 | 33.889 | 34.3732 | 35.4563 | 35.5938 | 35.8039 | 35.7467 | 33.8256 | 92.6962 | 92.8248 | 92.9808
2022-09-08 01:20 | 3:30 | 13.3543 | 14.7245 | 16.906 | 33.6515 | 34.4023 | 34.2266 | 35.06 | 35.5627 | 36.6756 | 37.3232 | 36.7998 | 37.7071 | 34.5354 | 34.4759 | 34.7488 | 35.6121 | 35.8152 | 36.279 | 36.7874 | 37.0496 | 27.6272 | 26.6709 | 92.2683 | 33.5032 | 33.5814 | 35.2881 | 33.9229 | 33.6112 | 33.9107 | 35.2641 | 34.6989 | 34.4887 | 37.3721 | 36.3171 | 33.914 | 34.5943 | 36.3104 | 36.7908 | 37.5035 | 36.3075 | 33.9258 | 32.8701 | 34.5652 | 34.9993 | 32.8563 | 34.4538 | 34.335 | 33.2159 | 34.3777 | 34.4713 | 34.4474 | 33.8798 | 34.3588 | 35.4475 | 35.604 | 35.8241 | 35.7343 | 33.8334 | 92.6321 | 92.7352 | 92.8563
2022-09-08 01:20 | 3:30 | 13.2102 | 14.5712 | 16.7539 | 33.5191 | 34.421 | 34.2356 | 35.0427 | 35.5727 | 36.6799 | 37.3467 | 36.8112 | 37.7205 | 34.528 | 34.466 | 34.7665 | 35.6003 | 35.7974 | 36.2925 | 36.7514 | 37.0258 | 28.0524 | 27.2025 | 92.1011 | 33.5725 | 33.5759 | 35.2909 | 33.9195 | 33.622 | 33.915 | 35.2756 | 34.7105 | 34.5009 | 37.3661 | 36.3125 | 33.9108 | 34.5922 | 36.3052 | 36.7869 | 37.5191 | 36.3094 | 33.921 | 32.8631 | 34.5875 | 35.0069 | 32.8485 | 34.4558 | 34.3701 | 33.263 | 34.3644 | 34.4616 | 34.4783 | 33.8881 | 34.3777 | 35.4467 | 35.604 | 35.8195 | 35.7502 | 33.8207 | 92.4769 | 92.5915 | 92.746
2022-09-08 01:20 | 3:30 | 13.0352 | 14.4135 | 16.6083 | 33.432 | 34.4118 | 34.2286 | 35.0454 | 35.5881 | 36.6662 | 37.339 | 36.8134 | 37.7129 | 34.5302 | 34.4876 | 34.76 | 35.6157 | 35.7921 | 36.2882 | 36.7624 | 37.0546 | 28.4223 | 27.6518 | 92.151 | 33.6515 | 33.5929 | 35.2914 | 33.9079 | 33.6282 | 33.9114 | 35.2565 | 34.7007 | 34.4892 | 37.3713 | 36.2893 | 33.9049 | 34.5898 | 36.3171 | 36.7817 | 37.5086 | 36.316 | 33.9116 | 32.8807 | 34.5633 | 34.9955 | 32.8495 | 34.4425 | 34.3582 | 33.244 | 34.3685 | 34.4672 | 34.469 | 33.8764 | 34.3644 | 35.4391 | 35.601 | 35.7916 | 35.7219 | 33.8217 | 92.3402 | 92.4956 | 92.6517
2022-09-08 01:20 | 3:30 | 12.9324 | 14.2952 | 16.4967 | 33.6297 | 34.4243 | 34.2332 | 35.0306 | 35.5762 | 36.6643 | 37.3371 | 36.8019 | 37.7227 | 34.5091 | 34.484 | 34.7678 | 35.6213 | 35.7874 | 36.2901 | 36.7768 | 37.042 | 28.764 | 28.0381 | 91.9125 | 33.7534 | 33.5851 | 35.2983 | 33.92 | 33.6229 | 33.8957 | 35.2741 | 34.7019 | 34.507 | 37.363 | 36.303 | 33.9042 | 34.5898 | 36.3125 | 36.7935 | 37.4961 | 36.3104 | 33.9075 | 32.8545 | 34.5712 | 34.9836 | 32.8543 | 34.4436 | 34.3366 | 33.2441 | 34.3754 | 34.4415 | 34.4585 | 33.8801 | 34.3685 | 35.4567 | 35.5858 | 35.7962 | 35.7449 | 33.854 | 92.2675 | 92.3586 | 92.5873
2022-09-08 01:20 | 3:30 | 12.7738 | 14.176 | 16.3748 | 33.5032 | 34.4173 | 34.216 | 35.0217 | 35.5718 | 36.6733 | 37.3249 | 36.7953 | 37.7184 | 34.5243 | 34.4972 | 34.7547 | 35.6054 | 35.7944 | 36.2782 | 36.7629 | 37.0492 | 29.0269 | 28.3791 | 91.9746 | 33.7345 | 33.5872 | 35.2888 | 33.9258 | 33.6359 | 33.914 | 35.2711 | 34.6849 | 34.5008 | 37.3684 | 36.2942 | 33.8884 | 34.5757 | 36.2893 | 36.7786 | 37.5211 | 36.3052 | 33.9074 | 32.8685 | 34.5783 | 35.0128 | 32.8719 | 34.435 | 34.3695 | 33.2385 | 34.3604 | 34.4315 | 34.4428 | 33.9057 | 34.3754 | 35.4462 | 35.5952 | 35.815 | 35.7619 | 33.838 | 92.0997 | 92.1949 | 92.4144
2022-09-08 01:21 | 3:31 | 12.663 | 14.0351 | 16.2703 | 33.5052 | 34.4247 | 34.2157 | 35.0298 | 35.5774 | 36.685 | 37.3211 | 36.805 | 37.7135 | 34.5286 | 34.4734 | 34.754 | 35.6034 | 35.7824 | 36.2782 | 36.7467 | 37.0339 | 29.2707 | 28.6681 | 92.0795 | 33.7409 | 33.5611 | 35.2825 | 33.921 | 33.6218 | 33.9108 | 35.2653 | 34.694 | 34.4963 | 37.3714 | 36.3046 | 33.9032 | 34.5897 | 36.303 | 36.7754 | 37.5163 | 36.3171 | 33.8955 | 32.8688 | 34.5938 | 35.0211 | 32.8602 | 34.4296 | 34.3447 | 33.2382 | 34.3679 | 34.4031 | 34.4408 | 33.8945 | 34.3604 | 35.453 | 35.5999 | 35.8217 | 35.7494 | 33.8357 | 92.0326 | 92.0189 | 92.4008
2022-09-08 01:21 | 3:31 | 12.5381 | 13.905 | 16.1669 | 33.6354 | 34.4217 | 34.2134 | 35.0204 | 35.561 | 36.6674 | 37.3366 | 36.7909 | 37.7067 | 34.52 | 34.4966 | 34.7602 | 35.6103 | 35.7767 | 36.2794 | 36.7458 | 37.028 | 29.4808 | 28.9013 | 91.9712 | 33.7791 | 33.5679 | 35.2615 | 33.9116 | 33.6353 | 33.9049 | 35.2727 | 34.7135 | 34.4981 | 37.3622 | 36.2967 | 33.8996 | 34.5922 | 36.2942 | 36.7765 | 37.5259 | 36.3125 | 33.8863 | 32.8631 | 34.5961 | 35.0046 | 32.8567 | 34.456 | 34.3517 | 33.2447 | 34.3635 | 34.4401 | 34.4549 | 33.892 | 34.3679 | 35.4674 | 35.5984 | 35.8096 | 35.7659 | 33.831 | 91.9118 | 91.9352 | 92.3819
2022-09-08 01:21 | 3:31 | 12.447 | 13.7966 | 16.0417 | 33.5102 | 34.426 | 34.1983 | 35.025 | 35.562 | 36.6758 | 37.3198 | 36.805 | 37.7282 | 34.5276 | 34.4726 | 34.7411 | 35.6001 | 35.7693 | 36.2916 | 36.7473 | 37.0185 | 29.669 | 29.1178 | 92.1122 | 33.872 | 33.5639 | 35.28 | 33.9075 | 33.6419 | 33.9042 | 35.2584 | 34.6893 | 34.4881 | 37.357 | 36.2737 | 33.8904 | 34.5776 | 36.3046 | 36.7743 | 37.5041 | 36.2893 | 33.8936 | 32.8724 | 34.5762 | 35.0061 | 32.8592 | 34.4484 | 34.3428 | 33.249 | 34.3662 | 34.4203 | 34.4617 | 33.8721 | 34.3635 | 35.4689 | 35.5863 | 35.8142 | 35.7538 | 33.8482 | 91.7554 | 91.7934 | 92.2481
2022-09-08 01:21 | 3:31 | 12.3454 | 13.6641 | 15.9428 | 33.4755 | 34.4297 | 34.1873 | 34.9894 | 35.5566 | 36.6684 | 37.3429 | 36.7888 | 37.7204 | 34.5259 | 34.4718 | 34.7371 | 35.5926 | 35.7613 | 36.2813 | 36.7473 | 37.0452 | 29.8273 | 29.3005 | 92.2251 | 33.8678 | 33.5844 | 35.2672 | 33.9074 | 33.6253 | 33.8884 | 35.2791 | 34.676 | 34.4993 | 37.3637 | 36.2906 | 33.891 | 34.5854 | 36.2967 | 36.7735 | 37.5185 | 36.303 | 33.9019 | 32.8641 | 34.5901 | 35.0214 | 32.8752 | 34.4498 | 34.3549 | 33.2407 | 34.3678 | 34.4203 | 34.4611 | 33.8858 | 34.3662 | 35.457 | 35.5882 | 35.8204 | 35.7576 | 33.8379 | 91.7097 | 91.6616 | 92.1647
2022-09-08 01:21 | 3:31 | 12.2368 | 13.557 | 15.8568 | 33.5468 | 34.441 | 34.1983 | 35.007 | 35.5732 | 36.6798 | 37.3346 | 36.7846 | 37.7133 | 34.5264 | 34.4814 | 34.7515 | 35.5961 | 35.7614 | 36.2685 | 36.7288 | 37.0213 | 29.9465 | 29.4755 | 92.2224 | 33.8821 | 33.5662 | 35.2931 | 33.8955 | 33.6232 | 33.9032 | 35.2616 | 34.6855 | 34.486 | 37.3589 | 36.2826 | 33.9001 | 34.5589 | 36.2737 | 36.7746 | 37.5156 | 36.2942 | 33.8843 | 32.8583 | 34.5825 | 35.0175 | 32.8956 | 34.4566 | 34.3454 | 33.248 | 34.3684 | 34.4028 | 34.4674 | 33.8877 | 34.3678 | 35.4695 | 35.5805 | 35.8229 | 35.75 | 33.8341 | 91.7144 | 91.71 | 92.2539
2022-09-08 01:21 | 3:31 | 12.1154 | 13.425 | 15.6815 | 33.378 | 34.4365 | 34.1913 | 34.9918 | 35.5636 | 36.6493 | 37.3194 | 36.7874 | 37.7149 | 34.5164 | 34.4913 | 34.7276 | 35.5899 | 35.7671 | 36.2694 | 36.7454 | 37.028 | 30.0928 | 29.618 | 92.3122 | 33.9813 | 33.5762 | 35.2617 | 33.8863 | 33.6251 | 33.8996 | 35.2633 | 34.6904 | 34.5046 | 37.3634 | 36.2828 | 33.8959 | 34.577 | 36.2906 | 36.7804 | 37.5027 | 36.3046 | 33.8892 | 32.8806 | 34.599 | 35.0174 | 32.8785 | 34.4573 | 34.3573 | 33.2374 | 34.3735 | 34.41 | 34.4669 | 33.885 | 34.3684 | 35.4494 | 35.5843 | 35.8308 | 35.7582 | 33.8261 | 91.7666 | 91.7445 | 92.3219
2022-09-08 01:22 | 3:32 | 12.0512 | 13.3588 | 15.6404 | 33.3997 | 34.4279 | 34.1749 | 34.9775 | 35.5367 | 36.6599 | 37.3274 | 36.7949 | 37.7273 | 34.5196 | 34.4938 | 34.7406 | 35.5952 | 35.7607 | 36.268 | 36.7363 | 37.0297 | 30.1664 | 29.7381 | 92.3838 | 33.9515 | 33.5704 | 35.2572 | 33.8936 | 33.6043 | 33.8904 | 35.2454 | 34.6775 | 34.4724 | 37.3436 | 36.2688 | 33.8736 | 34.5565 | 36.2826 | 36.7768 | 37.5032 | 36.2967 | 33.8754 | 32.8602 | 34.5975 | 35.0128 | 32.8847 | 34.4673 | 34.3704 | 33.2545 | 34.3545 | 34.4062 | 34.4645 | 33.8889 | 34.3735 | 35.475 | 35.5714 | 35.8191 | 35.7601 | 33.84 | 91.8901 | 91.8662 | 92.3367
2022-09-08 01:22 | 3:32 | 11.9133 | 13.2578 | 15.5504 | 33.4013 | 34.437 | 34.1736 | 34.9725 | 35.5354 | 36.6406 | 37.3249 | 36.7849 | 37.7185 | 34.5234 | 34.4729 | 34.7263 | 35.5854 | 35.7498 | 36.2642 | 36.7154 | 37.0245 | 30.2823 | 29.8447 | 92.2933 | 33.9797 | 33.5617 | 35.2686 | 33.9019 | 33.6157 | 33.891 | 35.253 | 34.6789 | 34.465 | 37.3395 | 36.2932 | 33.8788 | 34.5476 | 36.2828 | 36.7833 | 37.5035 | 36.2737 | 33.8869 | 32.8727 | 34.6155 | 34.9997 | 32.8932 | 34.4607 | 34.3557 | 33.231 | 34.3578 | 34.4086 | 34.4557 | 33.884 | 34.3545 | 35.4761 | 35.5821 | 35.8278 | 35.7672 | 33.8258 | 91.9925 | 92.0406 | 92.4926
2022-09-08 01:22 | 3:32 | 11.8493 | 13.0624 | 15.4507 | 33.4256 | 34.4252 | 34.1562 | 34.9464 | 35.5463 | 36.6584 | 37.3329 | 36.7727 | 37.7099 | 34.5318 | 34.4853 | 34.7251 | 35.5905 | 35.7435 | 36.2582 | 36.7137 | 37.0218 | 30.3612 | 29.9488 | 92.4348 | 33.918 | 33.5707 | 35.265 | 33.8843 | 33.6273 | 33.9001 | 35.2756 | 34.6754 | 34.4638 | 37.3406 | 36.2809 | 33.8962 | 34.5576 | 36.2688 | 36.7666 | 37.4997 | 36.2906 | 33.8755 | 32.8941 | 34.5958 | 35.0042 | 32.8927 | 34.4703 | 34.349 | 33.2295 | 34.3728 | 34.3894 | 34.453 | 33.8666 | 34.3578 | 35.4622 | 35.5836 | 35.8115 | 35.7477 | 33.8258 | 92.0632 | 92.1985 | 92.5065
2022-09-08 01:22 | 3:32 | 10.9022 | 11.2147 | 14.9095 | 33.3237 | 34.4519 | 34.1844 | 34.9578 | 35.5393 | 36.6387 | 37.3375 | 36.7948 | 37.7301 | 34.523 | 34.5006 | 34.716 | 35.5868 | 35.7385 | 36.2617 | 36.7149 | 37.0209 | 30.3942 | 30.0141 | 92.5516 | 33.9695 | 33.5591 | 35.2585 | 33.8892 | 33.5959 | 33.8959 | 35.2625 | 34.6732 | 34.4665 | 37.3395 | 36.2765 | 33.8851 | 34.5551 | 36.2932 | 36.7668 | 37.5121 | 36.2826 | 33.8649 | 32.875 | 34.6027 | 34.9916 | 32.8851 | 34.4463 | 34.3421 | 33.2278 | 34.3603 | 34.3925 | 34.4808 | 33.8795 | 34.3728 | 35.4579 | 35.5838 | 35.8142 | 35.7485 | 33.8291 | 92.184 | 92.3227 | 92.5519
2022-09-08 01:22 | 3:32 | 13.1407 | 11.3947 | 16.0413 | 33.2786 | 34.4396 | 34.1529 | 34.961 | 35.5328 | 36.6555 | 37.3361 | 36.7757 | 37.6925 | 34.5256 | 34.4899 | 34.6949 | 35.5832 | 35.7417 | 36.2666 | 36.7091 | 37.03 | 30.417 | 30.0976 | 92.5988 | 34.0396 | 33.5622 | 35.2267 | 33.8754 | 33.6108 | 33.8736 | 35.25 | 34.6738 | 34.4675 | 37.3414 | 36.2765 | 33.8965 | 34.5392 | 36.2809 | 36.7793 | 37.4954 | 36.2828 | 33.8732 | 32.8634 | 34.604 | 35.0057 | 32.9037 | 34.4606 | 34.34 | 33.2451 | 34.3712 | 34.3826 | 34.4654 | 33.8909 | 34.3603 | 35.448 | 35.5739 | 35.8095 | 35.7525 | 33.8256 | 92.346 | 92.5303 | 92.6266
2022-09-08 01:22 | 3:32 | 15.1312 | 12.7204 | 17.7794 | 33.4355 | 34.4511 | 34.1514 | 34.9545 | 35.5296 | 36.6249 | 37.3182 | 36.7861 | 37.7026 | 34.5383 | 34.4851 | 34.7059 | 35.5791 | 35.7106 | 36.2572 | 36.7078 | 37.0191 | 30.4834 | 30.1481 | 92.6183 | 34.0365 | 33.557 | 35.2439 | 33.8869 | 33.6008 | 33.8788 | 35.2451 | 34.6806 | 34.4578 | 37.3255 | 36.2762 | 33.8802 | 34.547 | 36.2765 | 36.7682 | 37.5152 | 36.2688 | 33.8573 | 32.8712 | 34.6036 | 34.9948 | 32.9131 | 34.4605 | 34.3432 | 33.2282 | 34.3591 | 34.3957 | 34.4572 | 33.8795 | 34.3712 | 35.4455 | 35.5924 | 35.8162 | 35.7627 | 33.8188 | 92.5401 | 92.6861 | 92.8005
2022-09-08 01:23 | 3:32 | 16.7365 | 14.3074 | 19.4529 | 33.4872 | 34.4442 | 34.1473 | 34.9271 | 35.5231 | 36.6405 | 37.3128 | 36.7754 | 37.6883 | 34.5317 | 34.4887 | 34.7148 | 35.5803 | 35.7198 | 36.2506 | 36.7108 | 37.0175 | 30.5466 | 30.2352 | 92.7549 | 34.0889 | 33.5503 | 35.2307 | 33.8755 | 33.5932 | 33.8962 | 35.2518 | 34.6603 | 34.4692 | 37.3433 | 36.2735 | 33.8845 | 34.5405 | 36.2765 | 36.7556 | 37.4993 | 36.2932 | 33.8782 | 32.8703 | 34.6077 | 34.9953 | 32.9174 | 34.4524 | 34.3653 | 33.2293 | 34.3628 | 34.4073 | 34.4861 | 33.8736 | 34.3591 | 35.4708 | 35.5917 | 35.8174 | 35.759 | 33.8128 | 92.6801 | 92.8279 | 92.8682
2022-09-08 01:23 | 3:33 | 18.3379 | 16.0585 | 20.9387 | 33.6947 | 34.4433 | 34.1711 | 34.9417 | 35.4999 | 36.632 | 37.3235 | 36.7666 | 37.7081 | 34.5299 | 34.4995 | 34.7017 | 35.5756 | 35.7094 | 36.2487 | 36.7193 | 37.0176 | 30.6172 | 30.3024 | 92.8053 | 34.1774 | 33.5769 | 35.2401 | 33.8649 | 33.6013 | 33.8851 | 35.252 | 34.6672 | 34.4716 | 37.3635 | 36.2583 | 33.8726 | 34.5296 | 36.2762 | 36.7543 | 37.5052 | 36.2809 | 33.867 | 32.8649 | 34.6192 | 35.013 | 32.8936 | 34.4588 | 34.3685 | 33.2189 | 34.3625 | 34.3946 | 34.4672 | 33.8643 | 34.3628 | 35.4549 | 35.5941 | 35.8099 | 35.7509 | 33.8031 | 92.7536 | 93.0131 | 92.9168
2022-09-08 01:23 | 3:33 | 19.3921 | 17.7193 | 22.2149 | 33.7646 | 34.4596 | 34.1464 | 34.9412 | 35.519 | 36.646 | 37.3286 | 36.7885 | 37.7096 | 34.5159 | 34.4841 | 34.7227 | 35.5646 | 35.7125 | 36.2389 | 36.7324 | 37.0075 | 30.6835 | 30.3655 | 92.8591 | 34.1413 | 33.5867 | 35.2237 | 33.8732 | 33.6146 | 33.8965 | 35.2606 | 34.6785 | 34.4484 | 37.3266 | 36.2629 | 33.8867 | 34.5274 | 36.2735 | 36.7738 | 37.5001 | 36.2765 | 33.8572 | 32.8954 | 34.6012 | 35.021 | 32.9266 | 34.4566 | 34.3612 | 33.2456 | 34.3835 | 34.3862 | 34.4714 | 33.8789 | 34.3625 | 35.4686 | 35.5702 | 35.7983 | 35.7638 | 33.8286 | 92.9878 | 93.1374 | 93.024
2022-09-08 01:23 | 3:33 | 20.3805 | 19.3011 | 23.3085 | 34.0538 | 34.4457 | 34.1586 | 34.9396 | 35.5183 | 36.6375 | 37.3132 | 36.7769 | 37.7009 | 34.5281 | 34.4864 | 34.7006 | 35.5807 | 35.7149 | 36.2647 | 36.7195 | 37.0037 | 30.7442 | 30.4246 | 92.8788 | 34.2322 | 33.5598 | 35.2377 | 33.8573 | 33.6054 | 33.8802 | 35.2619 | 34.6455 | 34.448 | 37.3435 | 36.2579 | 33.8836 | 34.5307 | 36.2583 | 36.7583 | 37.5074 | 36.2765 | 33.8592 | 32.8767 | 34.6184 | 35.0006 | 32.9294 | 34.4531 | 34.3607 | 33.2426 | 34.3499 | 34.3777 | 34.4702 | 33.8823 | 34.3835 | 35.467 | 35.5661 | 35.8083 | 35.7628 | 33.8155 | 93.192 | 93.3152 | 93.2017
2022-09-08 01:23 | 3:33 | 21.2766 | 20.7126 | 24.2505 | 34.0228 | 34.4453 | 34.1535 | 34.9415 | 35.5264 | 36.6377 | 37.3467 | 36.7644 | 37.7144 | 34.5265 | 34.4901 | 34.6973 | 35.5665 | 35.7026 | 36.2402 | 36.7401 | 37.0155 | 30.8031 | 30.4946 | 92.9131 | 34.158 | 33.5598 | 35.2339 | 33.8782 | 33.6024 | 33.8845 | 35.2616 | 34.6548 | 34.4682 | 37.3195 | 36.2769 | 33.8807 | 34.5294 | 36.2629 | 36.7693 | 37.4896 | 36.2762 | 33.8588 | 32.9049 | 34.6247 | 34.9856 | 32.9519 | 34.4613 | 34.3558 | 33.2182 | 34.3518 | 34.3956 | 34.468 | 33.8834 | 34.3499 | 35.4637 | 35.5812 | 35.8378 | 35.7523 | 33.8131 | 93.2475 | 93.492 | 93.2276
2022-09-08 01:23 | 3:33 | 22.0971 | 21.9901 | 24.9752 | 34.1504 | 34.4519 | 34.1491 | 34.9363 | 35.537 | 36.6412 | 37.3363 | 36.7549 | 37.7074 | 34.5041 | 34.4906 | 34.6977 | 35.5608 | 35.6959 | 36.2603 | 36.7364 | 37.0406 | 30.8208 | 30.5395 | 93.0136 | 34.2185 | 33.5581 | 35.2254 | 33.867 | 33.5842 | 33.8726 | 35.2647 | 34.6615 | 34.4455 | 37.3407 | 36.2707 | 33.8929 | 34.535 | 36.2579 | 36.7669 | 37.4867 | 36.2735 | 33.8486 | 32.8766 | 34.6155 | 35.0081 | 32.9159 | 34.4599 | 34.3766 | 33.2298 | 34.3533 | 34.3873 | 34.4695 | 33.8731 | 34.3518 | 35.4744 | 35.5632 | 35.8291 | 35.7553 | 33.8142 | 93.4659 | 93.6801 | 93.3304
2022-09-08 01:24 | 3:34 | 22.8511 | 23.1507 | 25.7121 | 34.2512 | 34.4597 | 34.1546 | 34.945 | 35.5001 | 36.6348 | 37.336 | 36.7559 | 37.6878 | 34.5163 | 34.4638 | 34.6901 | 35.5628 | 35.6995 | 36.2627 | 36.754 | 37.0106 | 30.8842 | 30.5976 | 93.0574 | 34.2959 | 33.5551 | 35.247 | 33.8572 | 33.5945 | 33.8867 | 35.2547 | 34.6389 | 34.4524 | 37.3273 | 36.2629 | 33.8744 | 34.5414 | 36.2769 | 36.7497 | 37.4902 | 36.2583 | 33.8498 | 32.8847 | 34.6427 | 35.0132 | 32.9479 | 34.4566 | 34.3529 | 33.2307 | 34.3676 | 34.3965 | 34.4764 | 33.8735 | 34.3533 | 35.4559 | 35.5674 | 35.8166 | 35.7404 | 33.7949 | 93.6038 | 93.8085 | 93.4545
2022-09-08 01:24 | 3:34 | 24.1836 | 20.2383 | 26.2765 | 34.2766 | 34.4354 | 34.1519 | 34.9545 | 35.5316 | 36.6307 | 37.3438 | 36.7793 | 37.7088 | 34.5282 | 34.4935 | 34.7131 | 35.5636 | 35.6823 | 36.2616 | 36.763 | 37.0234 | 30.8414 | 25.0913 | 92.8603 | 34.3264 | 33.5723 | 35.2412 | 33.8592 | 33.6116 | 33.8836 | 35.2689 | 34.6521 | 34.4466 | 37.3391 | 36.2647 | 33.8735 | 34.5364 | 36.2707 | 36.759 | 37.4936 | 36.2629 | 33.8604 | 32.8841 | 34.6274 | 35.0257 | 32.9543 | 34.4399 | 34.3656 | 33.2416 | 34.3614 | 34.3668 | 34.4903 | 33.8871 | 34.3676 | 35.4713 | 35.5648 | 35.8301 | 35.7655 | 33.8092 | 93.771 | 94.0211 | 93.5552
2022-09-08 01:24 | 3:34 | 26.9813 | 26.9203 | 26.5316 | 34.4001 | 34.465 | 34.1583 | 34.9744 | 35.5252 | 36.6375 | 37.3371 | 36.7722 | 37.7057 | 34.5365 | 34.4833 | 34.6848 | 35.5717 | 35.684 | 36.2572 | 36.7699 | 37.0138 | 30.7819 | 26.5229 | 93.0015 | 34.2937 | 33.5352 | 35.2334 | 33.8588 | 33.5811 | 33.8807 | 35.2669 | 34.654 | 34.4453 | 37.3412 | 36.2722 | 33.8683 | 34.5386 | 36.2629 | 36.7529 | 37.518 | 36.2579 | 33.8579 | 32.9005 | 34.6386 | 35.0288 | 32.957 | 34.4585 | 34.3706 | 33.2506 | 34.3413 | 34.3864 | 34.4759 | 33.8935 | 34.3614 | 35.4729 | 35.5526 | 35.8223 | 35.7705 | 33.7961 | 93.9679 | 94.1043 | 93.6346
2022-09-08 01:24 | 3:34 | 29.8954 | 29.1484 | 27.6544 | 34.4444 | 34.4532 | 34.1561 | 34.9647 | 35.5181 | 36.6397 | 37.343 | 36.7809 | 37.7048 | 34.5052 | 34.4706 | 34.6891 | 35.5682 | 35.6914 | 36.2517 | 36.7621 | 37.0233 | 31.266 | 28.0803 | 93.2407 | 34.2889 | 33.5428 | 35.2322 | 33.8486 | 33.5955 | 33.8929 | 35.2528 | 34.6606 | 34.452 | 37.3194 | 36.265 | 33.8592 | 34.5423 | 36.2647 | 36.7534 | 37.5025 | 36.2769 | 33.8399 | 32.8959 | 34.6323 | 35.0172 | 32.9677 | 34.4658 | 34.3792 | 33.2288 | 34.3613 | 34.3865 | 34.466 | 33.8822 | 34.3413 | 35.4654 | 35.5631 | 35.8369 | 35.7533 | 33.8051 | 94.1831 | 94.2736 | 93.8162
2022-09-08 01:24 | 3:34 | 31.085 | 29.7027 | 28.5227 | 34.5801 | 34.4507 | 34.1605 | 34.9679 | 35.5333 | 36.6367 | 37.3457 | 36.7809 | 37.6994 | 34.5077 | 34.4778 | 34.6975 | 35.5752 | 35.6686 | 36.2492 | 36.7743 | 37.0098 | 32.0045 | 29.1589 | 93.4999 | 34.3654 | 33.5461 | 35.2309 | 33.8498 | 33.5986 | 33.8744 | 35.2675 | 34.6623 | 34.4472 | 37.3281 | 36.2573 | 33.8687 | 34.5405 | 36.2722 | 36.7173 | 37.4873 | 36.2707 | 33.8518 | 32.8889 | 34.6283 | 35.0114 | 32.9782 | 34.4669 | 34.3865 | 33.2437 | 34.3661 | 34.3892 | 34.4876 | 33.8923 | 34.3613 | 35.4712 | 35.5634 | 35.8103 | 35.7603 | 33.8071 | 94.3347 | 94.3744 | 93.8976
2022-09-08 01:24 | 3:34 | 31.63 | 29.9835 | 29.1466 | 34.6844 | 34.458 | 34.1745 | 34.9842 | 35.5283 | 36.6504 | 37.3373 | 36.7628 | 37.7028 | 34.5046 | 34.453 | 34.6872 | 35.5712 | 35.6743 | 36.2406 | 36.7467 | 37.0109 | 32.7795 | 29.6872 | 93.5206 | 34.3367 | 33.5626 | 35.2341 | 33.8604 | 33.5907 | 33.8735 | 35.2611 | 34.6598 | 34.4493 | 37.327 | 36.2449 | 33.8813 | 34.5395 | 36.265 | 36.7457 | 37.5181 | 36.2629 | 33.8606 | 32.8955 | 34.6407 | 35.0166 | 32.9759 | 34.4386 | 34.3806 | 33.2399 | 34.3659 | 34.3744 | 34.484 | 33.8912 | 34.3661 | 35.4548 | 35.5606 | 35.829 | 35.772 | 33.7971 | 94.3956 | 94.5281 | 93.9215
2022-09-08 01:25 | 3:34 | 32.0907 | 30.163 | 29.6116 | 34.8627 | 34.4474 | 34.1699 | 34.9815 | 35.5351 | 36.6207 | 37.3457 | 36.7785 | 37.7123 | 34.5253 | 34.4804 | 34.7065 | 35.5574 | 35.6795 | 36.252 | 36.777 | 37.012 | 33.4587 | 30.0737 | 93.8356 | 34.4344 | 33.5445 | 35.2433 | 33.8579 | 33.5966 | 33.8683 | 35.2545 | 34.6394 | 34.4576 | 37.3207 | 36.2689 | 33.8818 | 34.5348 | 36.2573 | 36.7538 | 37.4963 | 36.2647 | 33.8566 | 32.9004 | 34.6303 | 35.025 | 32.9764 | 34.4348 | 34.3863 | 33.2545 | 34.361 | 34.3846 | 34.4972 | 33.8864 | 34.3659 | 35.4758 | 35.5513 | 35.8277 | 35.765 | 33.8013 | 94.5611 | 94.6765 | 93.9829
2022-09-08 01:25 | 3:35 | 32.2996 | 30.3423 | 29.9579 | 34.8787 | 34.4783 | 34.1825 | 34.9873 | 35.5437 | 36.6352 | 37.345 | 36.761 | 37.713 | 34.4931 | 34.4565 | 34.6762 | 35.5626 | 35.6637 | 36.2487 | 36.7806 | 37.0037 | 33.8454 | 30.3694 | 93.7522 | 34.4569 | 33.5342 | 35.2237 | 33.8399 | 33.593 | 33.8592 | 35.2626 | 34.6505 | 34.4407 | 37.3169 | 36.2803 | 33.8635 | 34.5339 | 36.2449 | 36.755 | 37.4896 | 36.2722 | 33.858 | 32.9024 | 34.6452 | 35.0265 | 32.9847 | 34.4526 | 34.392 | 33.2534 | 34.3587 | 34.3785 | 34.4734 | 33.8834 | 34.361 | 35.4838 | 35.559 | 35.8291 | 35.7685 | 33.7899 | 94.7095 | 94.7465 | 94.045
2022-09-08 01:25 | 3:35 | 32.4772 | 30.4808 | 30.2186 | 34.8298 | 34.469 | 34.1798 | 35.0112 | 35.5268 | 36.6407 | 37.3378 | 36.7664 | 37.7015 | 34.502 | 34.4695 | 34.6876 | 35.5694 | 35.6723 | 36.2358 | 36.7831 | 36.9846 | 33.9302 | 30.5805 | 93.7783 | 34.5435 | 33.5215 | 35.2092 | 33.8518 | 33.5934 | 33.8687 | 35.2485 | 34.6359 | 34.4332 | 37.3152 | 36.2704 | 33.8596 | 34.5465 | 36.2689 | 36.7564 | 37.4977 | 36.265 | 33.8217 | 32.9179 | 34.6446 | 35.0185 | 32.9708 | 34.4639 | 34.3833 | 33.234 | 34.3718 | 34.3644 | 34.4966 | 33.8824 | 34.3587 | 35.4685 | 35.5453 | 35.8152 | 35.7558 | 33.7862 | 94.8085 | 94.808 | 94.1558
2022-09-08 01:25 | 3:35 | 32.5802 | 30.5838 | 30.46 | 35.0715 | 34.4585 | 34.1755 | 35.0122 | 35.5448 | 36.6391 | 37.3578 | 36.7752 | 37.7037 | 34.4957 | 34.4558 | 34.6789 | 35.5667 | 35.6642 | 36.2524 | 36.7941 | 37.0055 | 33.9132 | 30.7417 | 93.8013 | 34.5559 | 33.5471 | 35.2167 | 33.8606 | 33.6063 | 33.8813 | 35.2694 | 34.6454 | 34.4302 | 37.328 | 36.2713 | 33.8555 | 34.5629 | 36.2803 | 36.7542 | 37.4948 | 36.2573 | 33.8515 | 32.9057 | 34.6584 | 35.0178 | 32.9944 | 34.4518 | 34.3823 | 33.225 | 34.3258 | 34.3547 | 34.4726 | 33.8827 | 34.3718 | 35.4788 | 35.5516 | 35.8097 | 35.7597 | 33.7925 | 94.8859 | 94.8302 | 94.1849
2022-09-08 01:25 | 3:35 | 32.7174 | 30.6668 | 30.5952 | 35.1236 | 34.4428 | 34.1758 | 35.0117 | 35.5413 | 36.631 | 37.3404 | 36.7776 | 37.7026 | 34.4831 | 34.4459 | 34.7051 | 35.5598 | 35.6659 | 36.2461 | 36.8064 | 36.9968 | 33.8553 | 30.8504 | 94.0196 | 34.5317 | 33.5245 | 35.2024 | 33.8566 | 33.5867 | 33.8818 | 35.255 | 34.6354 | 34.4221 | 37.328 | 36.2597 | 33.869 | 34.5544 | 36.2704 | 36.7517 | 37.4885 | 36.2449 | 33.846 | 32.9075 | 34.6628 | 35.0215 | 32.9888 | 34.4512 | 34.4017 | 33.2488 | 34.368 | 34.3855 | 34.4718 | 33.8915 | 34.3258 | 35.4486 | 35.5317 | 35.8101 | 35.7734 | 33.7938 | 94.9756 | 94.9475 | 94.22
2022-09-08 01:25 | 3:35 | 32.8853 | 30.7695 | 30.776 | 35.1076 | 34.4408 | 34.1726 | 35.0156 | 35.5471 | 36.6292 | 37.37 | 36.767 | 37.6953 | 34.4669 | 34.4397 | 34.6717 | 35.5576 | 35.644 | 36.2339 | 36.7842 | 36.9862 | 33.8269 | 30.9766 | 93.9487 | 34.5807 | 33.552 | 35.2282 | 33.858 | 33.5827 | 33.8635 | 35.2602 | 34.64 | 34.4351 | 37.3143 | 36.2663 | 33.874 | 34.5345 | 36.2713 | 36.7555 | 37.4994 | 36.2689 | 33.8341 | 32.9216 | 34.6478 | 35.0191 | 33.0165 | 34.4588 | 34.3862 | 33.243 | 34.3634 | 34.3825 | 34.4814 | 33.8957 | 34.368 | 35.4636 | 35.5376 | 35.8284 | 35.7599 | 33.7901 | 95.0816 | 94.9528 | 94.299
2022-09-08 01:26 | 3:36 | 33.0026 | 30.8668 | 30.9218 | 35.1621 | 34.4549 | 34.1599 | 35.0053 | 35.5306 | 36.6139 | 37.3479 | 36.764 | 37.6893 | 34.4927 | 34.4423 | 34.6568 | 35.5534 | 35.6471 | 36.2503 | 36.8023 | 36.9841 | 33.8074 | 31.0608 | 93.8899 | 34.5532 | 33.5222 | 35.2296 | 33.8217 | 33.6099 | 33.8596 | 35.2318 | 34.6207 | 34.4297 | 37.3066 | 36.2514 | 33.8533 | 34.5506 | 36.2597 | 36.7282 | 37.5023 | 36.2803 | 33.8367 | 32.8985 | 34.6463 | 35.0125 | 33.0201 | 34.4357 | 34.3773 | 33.2313 | 34.3498 | 34.3695 | 34.4913 | 33.8963 | 34.3634 | 35.4552 | 35.5469 | 35.823 | 35.751 | 33.7701 | 95.0349 | 94.906 | 94.2772
2022-09-08 01:26 | 3:36 | 33.0905 | 30.9295 | 31.0738 | 35.2081 | 34.4617 | 34.1707 | 35.007 | 35.532 | 36.6174 | 37.3384 | 36.7838 | 37.6958 | 34.4716 | 34.443 | 34.6788 | 35.5388 | 35.6375 | 36.2439 | 36.8061 | 36.9789 | 33.7892 | 31.1039 | 93.7173 | 34.6431 | 33.5183 | 35.2235 | 33.8515 | 33.5915 | 33.8555 | 35.2574 | 34.6437 | 34.4203 | 37.3084 | 36.2652 | 33.8572 | 34.5488 | 36.2663 | 36.7242 | 37.496 | 36.2704 | 33.8391 | 32.9024 | 34.6582 | 35.0244 | 33.02 | 34.4351 | 34.4033 | 33.2455 | 34.3538 | 34.3678 | 34.4938 | 33.9031 | 34.3498 | 35.4622 | 35.5446 | 35.8128 | 35.7608 | 33.7844 | 94.8331 | 94.8691 | 94.1386
2022-09-08 01:26 | 3:36 | 33.1994 | 31.0312 | 31.2006 | 35.2254 | 34.4611 | 34.179 | 35.0098 | 35.5577 | 36.6224 | 37.3377 | 36.7764 | 37.6928 | 34.4777 | 34.4518 | 34.6568 | 35.5647 | 35.6384 | 36.2492 | 36.793 | 36.9706 | 33.7409 | 31.1688 | 93.5454 | 34.564 | 33.515 | 35.2247 | 33.846 | 33.5986 | 33.869 | 35.253 | 34.6546 | 34.4165 | 37.2974 | 36.2655 | 33.8523 | 34.5369 | 36.2514 | 36.7346 | 37.4961 | 36.2713 | 33.8365 | 32.9022 | 34.669 | 35.0044 | 33.0337 | 34.4514 | 34.4073 | 33.256 | 34.3479 | 34.3802 | 34.4729 | 33.9063 | 34.3538 | 35.4511 | 35.5325 | 35.8268 | 35.7594 | 33.7747 | 94.6236 | 94.669 | 94.0066
2022-09-08 01:26 | 3:36 | 33.261 | 31.0829 | 31.3134 | 35.3662 | 34.4674 | 34.1638 | 35.0285 | 35.5524 | 36.6183 | 37.3459 | 36.7787 | 37.7152 | 34.472 | 34.437 | 34.6567 | 35.5439 | 35.6399 | 36.2606 | 36.8065 | 36.9808 | 33.702 | 31.2213 | 93.3869 | 34.5941 | 33.5029 | 35.2211 | 33.8341 | 33.6076 | 33.874 | 35.2352 | 34.6552 | 34.4102 | 37.3081 | 36.27 | 33.8679 | 34.5318 | 36.2652 | 36.7443 | 37.4757 | 36.2597 | 33.8512 | 32.9109 | 34.6631 | 34.9839 | 33.0428 | 34.4522 | 34.4149 | 33.2487 | 34.3627 | 34.3605 | 34.4853 | 33.8928 | 34.3479 | 35.4448 | 35.5261 | 35.8176 | 35.7575 | 33.7406 | 94.3418 | 94.4955 | 93.8608
2022-09-08 01:26 | 3:36 | 33.2837 | 31.1578 | 31.377 | 35.3055 | 34.4669 | 34.1763 | 35.0068 | 35.5352 | 36.606 | 37.3525 | 36.7633 | 37.6932 | 34.4674 | 34.4467 | 34.6603 | 35.5455 | 35.6387 | 36.2517 | 36.804 | 36.9763 | 33.6638 | 31.2587 | 93.3753 | 34.6327 | 33.5284 | 35.2074 | 33.8367 | 33.5787 | 33.8533 | 35.2367 | 34.6587 | 34.4079 | 37.3058 | 36.2655 | 33.8624 | 34.5402 | 36.2655 | 36.7245 | 37.4865 | 36.2663 | 33.8396 | 32.9142 | 34.6773 | 35.0088 | 33.0383 | 34.4491 | 34.408 | 33.2379 | 34.3617 | 34.3851 | 34.5006 | 33.8802 | 34.3627 | 35.447 | 35.5349 | 35.8253 | 35.7532 | 33.7557 | 94.1303 | 94.2937 | 93.7528
2022-09-08 01:26 | 3:36 | 33.3202 | 31.1804 | 31.4905 | 35.4742 | 34.4645 | 34.1655 | 35.0104 | 35.5314 | 36.6316 | 37.3614 | 36.7649 | 37.6987 | 34.462 | 34.429 | 34.6583 | 35.5442 | 35.644 | 36.254 | 36.8086 | 36.9812 | 33.6279 | 31.2833 | 93.245 | 34.6784 | 33.5415 | 35.2074 | 33.8391 | 33.5941 | 33.8572 | 35.2716 | 34.6428 | 34.4194 | 37.3033 | 36.2712 | 33.8518 | 34.5374 | 36.27 | 36.7483 | 37.4892 | 36.2514 | 33.8289 | 32.921 | 34.6678 | 35.0201 | 33.0489 | 34.4293 | 34.4058 | 33.2289 | 34.3503 | 34.373 | 34.4899 | 33.8908 | 34.3617 | 35.4576 | 35.5217 | 35.8166 | 35.7532 | 33.7607 | 94.0031 | 94.0962 | 93.6269
2022-09-08 01:27 | 3:36 | 33.3394 | 31.2254 | 31.573 | 35.4502 | 34.4557 | 34.1749 | 35.0184 | 35.5345 | 36.6225 | 37.3582 | 36.7676 | 37.7105 | 34.4595 | 34.4404 | 34.6522 | 35.5592 | 35.6286 | 36.2483 | 36.8229 | 36.9741 | 33.6005 | 31.3063 | 93.1781 | 34.7224 | 33.5207 | 35.2035 | 33.8365 | 33.5999 | 33.8523 | 35.2413 | 34.6426 | 34.4072 | 37.3036 | 36.2625 | 33.8734 | 34.5363 | 36.2655 | 36.725 | 37.4808 | 36.2652 | 33.8251 | 32.9214 | 34.6641 | 35.0034 | 33.0476 | 34.4311 | 34.4159 | 33.2431 | 34.3367 | 34.387 | 34.4851 | 33.8925 | 34.3503 | 35.4446 | 35.5245 | 35.832 | 35.7569 | 33.781 | 93.8747 | 93.9789 | 93.5697
2022-09-08 01:27 | 3:37 | 33.4479 | 31.2782 | 31.6438 | 35.4984 | 34.453 | 34.1819 | 35.0239 | 35.5445 | 36.6264 | 37.3589 | 36.78 | 37.6919 | 34.4501 | 34.4295 | 34.6625 | 35.5437 | 35.6423 | 36.2443 | 36.8118 | 36.9831 | 33.5972 | 31.319 | 93.1428 | 34.7514 | 33.5212 | 35.2119 | 33.8512 | 33.5906 | 33.8679 | 35.2359 | 34.6568 | 34.4077 | 37.296 | 36.2775 | 33.8677 | 34.549 | 36.2712 | 36.7321 | 37.4802 | 36.2655 | 33.8415 | 32.9315 | 34.6611 | 35.0126 | 33.085 | 34.4192 | 34.4064 | 33.2353 | 34.3436 | 34.3648 | 34.4887 | 33.8979 | 34.3367 | 35.4521 | 35.5313 | 35.8318 | 35.7713 | 33.7715 | 93.7648 | 93.8774 | 93.5648
2022-09-08 01:27 | 3:37 | 33.5025 | 31.3248 | 31.7407 | 35.5067 | 34.4808 | 34.1745 | 35.0403 | 35.5509 | 36.6122 | 37.3708 | 36.7641 | 37.6985 | 34.4713 | 34.4351 | 34.6647 | 35.5522 | 35.6262 | 36.2592 | 36.8012 | 36.9733 | 33.5591 | 31.3476 | 93.0909 | 34.7245 | 33.5202 | 35.2058 | 33.8396 | 33.5902 | 33.8624 | 35.2479 | 34.6475 | 34.4171 | 37.3018 | 36.2736 | 33.8551 | 34.5427 | 36.2625 | 36.7389 | 37.4902 | 36.27 | 33.8215 | 32.9548 | 34.7077 | 35.025 | 33.0678 | 34.4235 | 34.4028 | 33.2493 | 34.3611 | 34.3713 | 34.4995 | 33.9131 | 34.3436 | 35.4457 | 35.5309 | 35.8282 | 35.761 | 33.7659 | 93.6783 | 93.7748 | 93.4802
2022-09-08 01:27 | 3:37 | 33.4956 | 31.3503 | 31.8163 | 35.5553 | 34.4654 | 34.182 | 35.0286 | 35.5261 | 36.6063 | 37.3677 | 36.779 | 37.6896 | 34.4616 | 34.4223 | 34.6555 | 35.5556 | 35.6275 | 36.2473 | 36.8141 | 36.9768 | 33.5105 | 31.3798 | 92.9114 | 34.7824 | 33.5333 | 35.2335 | 33.8289 | 33.5779 | 33.8518 | 35.2625 | 34.6483 | 34.4153 | 37.3096 | 36.2788 | 33.8597 | 34.557 | 36.2775 | 36.7544 | 37.4982 | 36.2655 | 33.8314 | 32.9196 | 34.6798 | 35.0158 | 33.0742 | 34.4295 | 34.4004 | 33.254 | 34.364 | 34.3747 | 34.4841 | 33.9016 | 34.3611 | 35.457 | 35.5486 | 35.8234 | 35.7499 | 33.7542 | 93.5632 | 93.6535 | 93.3751
2022-09-08 01:27 | 3:37 | 33.5707 | 31.3863 | 31.8801 | 35.6054 | 34.4572 | 34.1852 | 35.0411 | 35.5523 | 36.6279 | 37.3837 | 36.7769 | 37.7167 | 34.4672 | 34.4075 | 34.6564 | 35.5614 | 35.6378 | 36.2492 | 36.8309 | 36.9655 | 33.5242 | 31.4046 | 92.9347 | 34.8327 | 33.5359 | 35.2148 | 33.8251 | 33.5969 | 33.8734 | 35.2302 | 34.6563 | 34.4066 | 37.3088 | 36.2755 | 33.8616 | 34.5605 | 36.2736 | 36.7343 | 37.4995 | 36.2712 | 33.8409 | 32.9433 | 34.69 | 35.0245 | 33.1097 | 34.4147 | 34.3999 | 33.261 | 34.3409 | 34.3605 | 34.4864 | 33.9022 | 34.364 | 35.4671 | 35.5341 | 35.828 | 35.7643 | 33.7493 | 93.4915 | 93.5948 | 93.3921
2022-09-08 01:27 | 3:37 | 33.6839 | 31.4158 | 31.9447 | 35.6382 | 34.4861 | 34.1716 | 35.0286 | 35.5484 | 36.6049 | 37.3862 | 36.7777 | 37.7069 | 34.4415 | 34.4201 | 34.6774 | 35.5471 | 35.6157 | 36.2617 | 36.8213 | 36.968 | 33.5734 | 31.4112 | 92.9392 | 34.8472 | 33.5344 | 35.2167 | 33.8415 | 33.5801 | 33.8677 | 35.2428 | 34.6602 | 34.4217 | 37.309 | 36.2662 | 33.8507 | 34.5565 | 36.2788 | 36.7318 | 37.4934 | 36.2625 | 33.8257 | 32.9589 | 34.6948 | 35.029 | 33.0976 | 34.4111 | 34.4069 | 33.2706 | 34.3465 | 34.3467 | 34.4901 | 33.9198 | 34.3409 | 35.4502 | 35.5117 | 35.8305 | 35.7722 | 33.7589 | 93.4327 | 93.553 | 93.3265
2022-09-08 01:28 | 3:38 | 33.8022 | 31.42 | 32.0213 | 35.6679 | 34.4672 | 34.1811 | 35.0309 | 35.5508 | 36.6018 | 37.3672 | 36.7821 | 37.7139 | 34.4315 | 34.4168 | 34.6593 | 35.544 | 35.6155 | 36.2627 | 36.8467 | 36.9678 | 33.6417 | 31.4301 | 92.8346 | 34.8366 | 33.5348 | 35.2223 | 33.8215 | 33.605 | 33.8551 | 35.239 | 34.6376 | 34.415 | 37.3034 | 36.2806 | 33.8695 | 34.5437 | 36.2755 | 36.7419 | 37.4855 | 36.2775 | 33.8374 | 32.9611 | 34.7072 | 35.0153 | 33.0909 | 34.4196 | 34.4079 | 33.2665 | 34.3507 | 34.3521 | 34.4906 | 33.8835 | 34.3465 | 35.4646 | 35.5339 | 35.8302 | 35.7729 | 33.7608 | 93.3478 | 93.526 | 93.2627
2022-09-08 01:28 | 3:38 | 33.9038 | 31.46 | 32.0692 | 35.6149 | 34.4714 | 34.1804 | 35.0318 | 35.5469 | 36.6123 | 37.3722 | 36.7949 | 37.7081 | 34.4031 | 34.4184 | 34.6556 | 35.555 | 35.6414 | 36.2506 | 36.8319 | 36.9886 | 33.7088 | 31.4419 | 92.9119 | 34.8941 | 33.533 | 35.2248 | 33.8314 | 33.589 | 33.8597 | 35.2516 | 34.6436 | 34.3954 | 37.2979 | 36.2874 | 33.8717 | 34.5496 | 36.2662 | 36.7298 | 37.522 | 36.2736 | 33.8299 | 32.9505 | 34.7062 | 35.0271 | 33.1049 | 34.4169 | 34.414 | 33.2804 | 34.3516 | 34.365 | 34.4638 | 33.9075 | 34.3507 | 35.4519 | 35.5224 | 35.8435 | 35.7662 | 33.7678 | 93.2201 | 93.4315 | 93.2506
2022-09-08 01:28 | 3:38 | 33.9484 | 31.4962 | 32.134 | 35.7846 | 34.4702 | 34.1968 | 35.0221 | 35.5569 | 36.5903 | 37.3736 | 36.7742 | 37.7225 | 34.4401 | 34.4179 | 34.66 | 35.5484 | 35.6267 | 36.2797 | 36.8376 | 36.9846 | 33.774 | 31.4374 | 92.8664 | 34.8551 | 33.5298 | 35.2114 | 33.8409 | 33.6029 | 33.8616 | 35.2601 | 34.654 | 34.419 | 37.3247 | 36.269 | 33.8644 | 34.5629 | 36.2806 | 36.7416 | 37.5107 | 36.2788 | 33.8364 | 32.9739 | 34.7085 | 35.0425 | 33.1308 | 34.4227 | 34.4321 | 33.2781 | 34.335 | 34.376 | 34.4935 | 33.8989 | 34.3516 | 35.4815 | 35.5271 | 35.8431 | 35.7623 | 33.7555 | 93.2113 | 93.3135 | 93.2313
2022-09-08 01:28 | 3:38 | 34.0654 | 31.512 | 32.1695 | 35.7992 | 34.468 | 34.1787 | 35.0214 | 35.5647 | 36.61 | 37.3865 | 36.7852 | 37.7206 | 34.4203 | 34.3846 | 34.6517 | 35.559 | 35.6368 | 36.2556 | 36.833 | 36.9658 | 33.7817 | 31.4389 | 92.619 | 34.8028 | 33.5279 | 35.2149 | 33.8257 | 33.5958 | 33.8507 | 35.2446 | 34.6273 | 34.4154 | 37.3171 | 36.2879 | 33.8633 | 34.5538 | 36.2874 | 36.7401 | 37.5108 | 36.2755 | 33.839 | 32.9484 | 34.7144 | 35.0385 | 33.1263 | 34.4045 | 34.4082 | 33.2784 | 34.3701 | 34.3753 | 34.4833 | 33.9186 | 34.335 | 35.4731 | 35.5188 | 35.8291 | 35.7495 | 33.759 | 93.1121 | 93.2749 | 93.1949
2022-09-08 01:28 | 3:38 | 32.0158 | 31.2889 | 32.0882 | 35.6848 | 34.4695 | 34.2067 | 35.0271 | 35.5708 | 36.6202 | 37.3782 | 36.793 | 37.7196 | 34.4203 | 34.3978 | 34.6654 | 35.5574 | 35.6458 | 36.2651 | 36.8405 | 36.9947 | 31.5435 | 31.312 | 92.7137 | 34.8897 | 33.5061 | 35.2323 | 33.8374 | 33.6132 | 33.8695 | 35.2639 | 34.6224 | 34.4169 | 37.318 | 36.2852 | 33.8541 | 34.5597 | 36.269 | 36.736 | 37.5232 | 36.2662 | 33.814 | 32.9571 | 34.7317 | 35.0622 | 33.1306 | 34.4023 | 34.4182 | 33.2776 | 34.3582 | 34.3558 | 34.4706 | 33.9265 | 34.3701 | 35.4772 | 35.5424 | 35.8269 | 35.7704 | 33.7685 | 92.9219 | 93.1878 | 92.9496
2022-09-08 01:28 | 3:38 | 30.9281 | 28.7681 | 31.7346 | 35.6974 | 34.4764 | 34.1874 | 35.0316 | 35.5665 | 36.6194 | 37.38 | 36.8087 | 37.7141 | 34.4028 | 34.3915 | 34.6477 | 35.5268 | 35.6398 | 36.2772 | 36.8358 | 36.9787 | 27.5633 | 30.9918 | 92.6332 | 34.8583 | 33.5317 | 35.2276 | 33.8299 | 33.5941 | 33.8717 | 35.2369 | 34.651 | 34.4203 | 37.2948 | 36.294 | 33.87 | 34.543 | 36.2879 | 36.7517 | 37.4959 | 36.2806 | 33.8286 | 32.9716 | 34.7198 | 35.0905 | 33.1307 | 34.4059 | 34.4147 | 33.2693 | 34.3366 | 34.3558 | 34.4778 | 33.9326 | 34.3582 | 35.4933 | 35.5172 | 35.8323 | 35.7973 | 33.7808 | 92.868 | 93.091 | 93.0046
2022-09-08 01:29 | 3:38 | 31.493 | 20.7163 | 31.6727 | 35.8015 | 34.4903 | 34.1673 | 35.0341 | 35.5649 | 36.6112 | 37.3758 | 36.7911 | 37.7233 | 34.41 | 34.4027 | 34.6579 | 35.5459 | 35.627 | 36.2746 | 36.8438 | 36.9907 | 27.8439 | 31.1171 | 92.5092 | 34.8135 | 33.5286 | 35.2116 | 33.8364 | 33.5856 | 33.8644 | 35.2479 | 34.6654 | 34.4123 | 37.3233 | 36.2985 | 33.8698 | 34.549 | 36.2852 | 36.7308 | 37.5088 | 36.2874 | 33.8498 | 32.99 | 34.725 | 35.0962 | 33.1256 | 34.3945 | 34.4103 | 33.2657 | 34.3695 | 34.3663 | 34.453 | 33.9142 | 34.3366 | 35.4884 | 35.5303 | 35.8187 | 35.7714 | 33.7805 | 92.8687 | 93.1132 | 92.946
2022-09-08 01:29 | 3:39 | 31.6266 | 23.8719 | 31.7999 | 35.8432 | 34.4759 | 34.2006 | 35.0282 | 35.5602 | 36.6188 | 37.3825 | 36.7957 | 37.7387 | 34.4062 | 34.404 | 34.6699 | 35.5593 | 35.6183 | 36.2594 | 36.8372 | 36.9903 | 28.5816 | 31.0339 | 92.3581 | 34.9131 | 33.5246 | 35.2301 | 33.839 | 33.5973 | 33.8633 | 35.237 | 34.6636 | 34.4408 | 37.3141 | 36.2815 | 33.864 | 34.553 | 36.294 | 36.7252 | 37.5118 | 36.269 | 33.8364 | 32.9824 | 34.7146 | 35.0682 | 33.1562 | 34.3932 | 34.4113 | 33.283 | 34.3447 | 34.3631 | 34.4804 | 33.9092 | 34.3695 | 35.4786 | 35.5249 | 35.8324 | 35.7845 | 33.7861 | 92.7511 | 92.9693 | 92.8874
2022-09-08 01:29 | 3:39 | 31.6457 | 26.4416 | 31.8872 | 35.8684 | 34.466 | 34.1795 | 35.0227 | 35.5393 | 36.6114 | 37.3899 | 36.7936 | 37.7249 | 34.4086 | 34.394 | 34.6599 | 35.5737 | 35.6252 | 36.27 | 36.8569 | 36.9942 | 29.2366 | 30.9969 | 92.3787 | 34.8618 | 33.5479 | 35.2197 | 33.814 | 33.5952 | 33.8541 | 35.2488 | 34.666 | 34.4146 | 37.3039 | 36.3007 | 33.8624 | 34.5546 | 36.2985 | 36.7388 | 37.5104 | 36.2879 | 33.836 | 32.9676 | 34.7411 | 35.0905 | 33.1516 | 34.3857 | 34.4163 | 33.313 | 34.3517 | 34.3711 | 34.4565 | 33.9243 | 34.3447 | 35.464 | 35.5288 | 35.8396 | 35.8012 | 33.7794 | 92.6795 | 92.8408 | 92.7476
2022-09-08 01:29 | 3:39 | 31.6827 | 28.0735 | 31.9192 | 35.9217 | 34.4876 | 34.1893 | 35.0461 | 35.5621 | 36.6157 | 37.3843 | 36.7938 | 37.7306 | 34.3894 | 34.3853 | 34.6526 | 35.5421 | 35.6254 | 36.2761 | 36.8528 | 36.9843 | 29.7795 | 31.0133 | 92.2605 | 34.8595 | 33.5487 | 35.2437 | 33.8286 | 33.5799 | 33.87 | 35.2458 | 34.6444 | 34.4132 | 37.3224 | 36.2968 | 33.8764 | 34.5673 | 36.2815 | 36.7493 | 37.5218 | 36.2852 | 33.8369 | 32.9705 | 34.7346 | 35.1016 | 33.1463 | 34.3916 | 34.4302 | 33.3151 | 34.3428 | 34.3757 | 34.4695 | 33.9091 | 34.3517 | 35.4812 | 35.5245 | 35.8501 | 35.8076 | 33.7795 | 92.5813 | 92.7561 | 92.6662
2022-09-08 01:29 | 3:39 | 31.7219 | 29.1548 | 31.971 | 35.8908 | 34.484 | 34.1956 | 35.047 | 35.5581 | 36.6237 | 37.4085 | 36.7976 | 37.7333 | 34.3925 | 34.4028 | 34.6536 | 35.5571 | 35.64 | 36.2619 | 36.8331 | 36.974 | 30.2762 | 31.0039 | 92.2169 | 34.9026 | 33.5252 | 35.2092 | 33.8498 | 33.5989 | 33.8698 | 35.2347 | 34.6456 | 34.4062 | 37.3186 | 36.2723 | 33.8704 | 34.544 | 36.3007 | 36.7433 | 37.5272 | 36.294 | 33.8452 | 33.0129 | 34.7511 | 35.0949 | 33.1664 | 34.3824 | 34.4363 | 33.3118 | 34.3549 | 34.361 | 34.4558 | 33.9046 | 34.3428 | 35.5074 | 35.5219 | 35.8503 | 35.7886 | 33.7952 | 92.4282 | 92.6222 | 92.5567
2022-09-08 01:29 | 3:39 | 31.7627 | 29.8255 | 31.9974 | 35.9529 | 34.4972 | 34.1864 | 35.0508 | 35.5616 | 36.6214 | 37.3768 | 36.7872 | 37.7361 | 34.3826 | 34.3963 | 34.6682 | 35.5604 | 35.6369 | 36.2661 | 36.8704 | 36.9875 | 30.6298 | 31.0492 | 92.2343 | 34.9079 | 33.5538 | 35.2327 | 33.8364 | 33.5884 | 33.864 | 35.2546 | 34.6375 | 34.4231 | 37.3186 | 36.285 | 33.8659 | 34.5806 | 36.2968 | 36.7489 | 37.5163 | 36.2985 | 33.8357 | 32.9938 | 34.7642 | 35.0988 | 33.1905 | 34.4062 | 34.4237 | 33.3293 | 34.3454 | 34.3565 | 34.4459 | 33.9243 | 34.3549 | 35.4997 | 35.522 | 35.8459 | 35.7887 | 33.7842 | 92.3629 | 92.4797 | 92.5572
2022-09-08 01:30 | 3:40 | 31.8414 | 30.2797 | 32.0504 | 35.928 | 34.4734 | 34.1844 | 35.0318 | 35.5481 | 36.6289 | 37.4242 | 36.7781 | 37.7285 | 34.3957 | 34.3786 | 34.6655 | 35.5534 | 35.6155 | 36.2677 | 36.8696 | 37.0158 | 30.9183 | 31.1107 | 92.2097 | 34.9552 | 33.5414 | 35.2251 | 33.836 | 33.5817 | 33.8624 | 35.2388 | 34.6383 | 34.4217 | 37.3318 | 36.2854 | 33.8573 | 34.569 | 36.2723 | 36.7496 | 37.5381 | 36.2815 | 33.8205 | 33.0052 | 34.7569 | 35.1113 | 33.1836 | 34.3742 | 34.4293 | 33.3328 | 34.3573 | 34.3704 | 34.4397 | 33.9497 | 34.3454 | 35.4764 | 35.521 | 35.8466 | 35.7817 | 33.7918 | 92.2567 | 92.36 | 92.494
2022-09-08 01:30 | 3:40 | 31.8959 | 30.5865 | 32.0733 | 36.0176 | 34.4966 | 34.1853 | 35.0489 | 35.5557 | 36.6362 | 37.4057 | 36.7836 | 37.7371 | 34.4073 | 34.3816 | 34.6598 | 35.5541 | 35.6214 | 36.2711 | 36.875 | 36.9993 | 31.1332 | 31.1536 | 92.0808 | 34.9611 | 33.5468 | 35.2508 | 33.8369 | 33.5946 | 33.8764 | 35.2561 | 34.6359 | 34.4081 | 37.3157 | 36.2802 | 33.8583 | 34.5585 | 36.285 | 36.7623 | 37.5282 | 36.3007 | 33.8297 | 33.0044 | 34.7863 | 35.1077 | 33.1874 | 34.372 | 34.4425 | 33.2897 | 34.3704 | 34.3687 | 34.4423 | 33.944 | 34.3573 | 35.5103 | 35.5079 | 35.8588 | 35.8049 | 33.7763 | 92.1207 | 92.2705 | 92.3841
2022-09-08 01:30 | 3:40 | 31.933 | 30.7907 | 32.1008 | 36.0055 | 34.4726 | 34.1906 | 35.0391 | 35.5615 | 36.6324 | 37.3989 | 36.808 | 37.7351 | 34.3946 | 34.3742 | 34.6711 | 35.5476 | 35.6253 | 36.2644 | 36.8683 | 36.9999 | 31.3296 | 31.1665 | 92.009 | 35.0067 | 33.5399 | 35.2395 | 33.8452 | 33.5812 | 33.8704 | 35.2618 | 34.6589 | 34.4258 | 37.3225 | 36.2964 | 33.8543 | 34.5548 | 36.2854 | 36.747 | 37.5274 | 36.2968 | 33.8383 | 33.0419 | 34.7839 | 35.0993 | 33.1861 | 34.3765 | 34.4411 | 33.3275 | 34.3557 | 34.3704 | 34.443 | 33.9426 | 34.3704 | 35.5242 | 35.5124 | 35.8383 | 35.7946 | 33.7819 | 91.9567 | 92.1547 | 92.2068
2022-09-08 01:30 | 3:40 | 31.9976 | 30.9558 | 32.132 | 35.9945 | 34.4718 | 34.1822 | 35.0371 | 35.5617 | 36.6238 | 37.406 | 36.7852 | 37.7469 | 34.3862 | 34.369 | 34.6529 | 35.5694 | 35.6445 | 36.2811 | 36.8779 | 36.9858 | 31.4658 | 31.1846 | 91.8475 | 34.9823 | 33.5545 | 35.2306 | 33.8357 | 33.5836 | 33.8659 | 35.249 | 34.6539 | 34.4068 | 37.3425 | 36.2863 | 33.8823 | 34.5669 | 36.2802 | 36.7398 | 37.5459 | 36.2723 | 33.8453 | 33.0128 | 34.7832 | 35.1193 | 33.1976 | 34.3802 | 34.424 | 33.3478 | 34.349 | 34.3681 | 34.4518 | 33.9675 | 34.3557 | 35.5102 | 35.5086 | 35.8299 | 35.801 | 33.8092 | 91.7906 | 92.0111 | 92.2493
2022-09-08 01:30 | 3:40 | 32.0624 | 31.0656 | 32.1444 | 35.9875 | 34.4814 | 34.1652 | 35.0437 | 35.5624 | 36.6233 | 37.4046 | 36.7694 | 37.7431 | 34.3777 | 34.3625 | 34.6641 | 35.5543 | 35.6276 | 36.2666 | 36.8735 | 36.994 | 31.6156 | 31.2262 | 91.8821 | 35.0389 | 33.5306 | 35.2288 | 33.8205 | 33.6068 | 33.8573 | 35.2723 | 34.6531 | 34.43 | 37.3361 | 36.2895 | 33.8694 | 34.5603 | 36.2964 | 36.738 | 37.5362 | 36.285 | 33.8214 | 33.0109 | 34.7768 | 35.1499 | 33.1851 | 34.3848 | 34.44 | 33.3344 | 34.3421 | 34.3673 | 34.437 | 33.9477 | 34.349 | 35.5059 | 35.5026 | 35.8855 | 35.8233 | 33.8104 | 91.7242 | 91.859 | 92.1133
2022-09-08 01:30 | 3:40 | 32.0946 | 31.1547 | 32.1695 | 36.0746 | 34.4913 | 34.1791 | 35.0475 | 35.5695 | 36.6229 | 37.4262 | 36.7912 | 37.736 | 34.3956 | 34.3686 | 34.658 | 35.5352 | 35.6288 | 36.2845 | 36.8793 | 36.9996 | 31.7062 | 31.2566 | 91.8555 | 35.0308 | 33.5416 | 35.2236 | 33.8297 | 33.5795 | 33.8583 | 35.2517 | 34.6487 | 34.4357 | 37.3288 | 36.302 | 33.8662 | 34.5588 | 36.2863 | 36.743 | 37.5392 | 36.2854 | 33.83 | 33.024 | 34.8025 | 35.1257 | 33.1766 | 34.3537 | 34.4454 | 33.309 | 34.34 | 34.3464 | 34.4467 | 33.9532 | 34.3421 | 35.5236 | 35.4995 | 35.8577 | 35.8096 | 33.8001 | 91.593 | 91.7284 | 92.0583
2022-09-08 01:31 | 3:41 | 32.131 | 31.2338 | 32.2248 | 36.0513 | 34.4938 | 34.1994 | 35.0416 | 35.5692 | 36.6373 | 37.4151 | 36.784 | 37.7479 | 34.3873 | 34.3632 | 34.6642 | 35.5488 | 35.6218 | 36.2659 | 36.8818 | 36.9878 | 31.79 | 31.2872 | 91.8085 | 34.9878 | 33.5594 | 35.2448 | 33.8383 | 33.5848 | 33.8543 | 35.2493 | 34.6642 | 34.4173 | 37.3222 | 36.2889 | 33.8692 | 34.5664 | 36.2895 | 36.7282 | 37.5432 | 36.2802 | 33.848 | 33.0339 | 34.8108 | 35.1342 | 33.2088 | 34.3558 | 34.4384 | 33.3467 | 34.3432 | 34.3669 | 34.429 | 33.9341 | 34.34 | 35.5369 | 35.5102 | 35.8383 | 35.8181 | 33.8067 | 91.4768 | 91.6248 | 91.9539
2022-09-08 01:31 | 3:41 | 32.1792 | 31.261 | 32.2076 | 36.0284 | 34.4729 | 34.1808 | 35.0501 | 35.5633 | 36.6258 | 37.4091 | 36.7954 | 37.7288 | 34.3965 | 34.3732 | 34.6479 | 35.5516 | 35.642 | 36.2826 | 36.876 | 36.9855 | 31.8365 | 31.2778 | 91.9224 | 35.042 | 33.5483 | 35.232 | 33.8453 | 33.5761 | 33.8823 | 35.2491 | 34.6404 | 34.4011 | 37.3163 | 36.3069 | 33.8496 | 34.5695 | 36.302 | 36.747 | 37.5358 | 36.2964 | 33.8349 | 33.0477 | 34.8121 | 35.1328 | 33.2238 | 34.3596 | 34.4509 | 33.3462 | 34.3653 | 34.3738 | 34.4404 | 33.9618 | 34.3432 | 35.5136 | 35.5167 | 35.8454 | 35.8148 | 33.8284 | 91.4176 | 91.5797 | 91.9164
2022-09-08 01:31 | 3:41 | 32.22 | 31.3203 | 32.2204 | 36.1133 | 34.4853 | 34.1648 | 35.0382 | 35.556 | 36.6241 | 37.4229 | 36.7908 | 37.7306 | 34.3668 | 34.3588 | 34.6544 | 35.5489 | 35.6258 | 36.2781 | 36.8863 | 37.0145 | 31.9184 | 31.3128 | 91.9282 | 35.0846 | 33.5679 | 35.225 | 33.8214 | 33.5925 | 33.8694 | 35.2566 | 34.6267 | 34.4212 | 37.3265 | 36.2851 | 33.8599 | 34.5545 | 36.2889 | 36.7442 | 37.5258 | 36.2863 | 33.8347 | 33.0639 | 34.8196 | 35.1478 | 33.2121 | 34.3644 | 34.4368 | 33.3348 | 34.3685 | 34.3554 | 34.4295 | 33.9238 | 34.3653 | 35.5328 | 35.5154 | 35.842 | 35.8372 | 33.8258 | 91.3899 | 91.5434 | 91.9149
2022-09-08 01:31 | 3:41 | 32.2538 | 31.3844 | 32.2493 | 36.0649 | 34.5006 | 34.1691 | 35.0377 | 35.5629 | 36.6359 | 37.4235 | 36.7933 | 37.7351 | 34.3864 | 34.3777 | 34.6613 | 35.5451 | 35.6353 | 36.266 | 36.8781 | 36.9877 | 32.0311 | 31.3353 | 91.8897 | 35.1587 | 33.5432 | 35.2453 | 33.83 | 33.582 | 33.8662 | 35.2571 | 34.6375 | 34.4021 | 37.3103 | 36.2795 | 33.8606 | 34.5704 | 36.3069 | 36.7381 | 37.5264 | 36.2895 | 33.8359 | 33.05 | 34.8351 | 35.1461 | 33.2131 | 34.3478 | 34.4566 | 33.3477 | 34.3612 | 34.3501 | 34.4351 | 33.9632 | 34.3685 | 35.5288 | 35.503 | 35.8514 | 35.8116 | 33.8216 | 91.4772 | 91.6365 | 91.9615
2022-09-08 01:31 | 3:41 | 32.3075 | 31.4088 | 32.2686 | 36.0953 | 34.4899 | 34.1749 | 35.0263 | 35.5836 | 36.6362 | 37.4296 | 36.787 | 37.7361 | 34.3865 | 34.3644 | 34.6662 | 35.5544 | 35.6155 | 36.2599 | 36.8835 | 36.9885 | 32.1678 | 31.3501 | 91.9539 | 35.1974 | 33.5328 | 35.2261 | 33.848 | 33.6025 | 33.8692 | 35.269 | 34.6248 | 34.4104 | 37.3223 | 36.2903 | 33.8733 | 34.5482 | 36.2851 | 36.745 | 37.5362 | 36.302 | 33.8351 | 33.0464 | 34.822 | 35.1241 | 33.2373 | 34.3682 | 34.4528 | 33.3492 | 34.3607 | 34.3571 | 34.4223 | 33.9496 | 34.3612 | 35.5421 | 35.5043 | 35.8503 | 35.8191 | 33.8119 | 91.6217 | 91.7811 | 92.1072
2022-09-08 01:31 | 3:41 | 32.3346 | 31.4537 | 32.2978 | 36.153 | 34.4851 | 34.1916 | 35.0328 | 35.5851 | 36.64 | 37.4109 | 36.7828 | 37.7266 | 34.3892 | 34.3685 | 34.6711 | 35.5509 | 35.626 | 36.2745 | 36.8813 | 37.0213 | 32.3451 | 31.3698 | 92.0966 | 35.1227 | 33.5301 | 35.2322 | 33.8349 | 33.5774 | 33.8496 | 35.2469 | 34.6342 | 34.4079 | 37.3092 | 36.2843 | 33.8562 | 34.5675 | 36.2795 | 36.7367 | 37.5489 | 36.2889 | 33.8194 | 33.0532 | 34.8161 | 35.1359 | 33.224 | 34.3529 | 34.4496 | 33.3525 | 34.3558 | 34.3721 | 34.4075 | 33.9389 | 34.3607 | 35.5263 | 35.4952 | 35.8478 | 35.8126 | 33.7956 | 91.6943 | 91.9327 | 92.098
2022-09-08 01:32 | 3:41 | 32.4893 | 31.6769 | 32.3613 | 36.08 | 34.4887 | 34.1615 | 35.0285 | 35.5708 | 36.6291 | 37.4208 | 36.775 | 37.7216 | 34.3744 | 34.3754 | 34.672 | 35.5574 | 35.6275 | 36.2683 | 36.8969 | 36.9878 | 32.8717 | 31.7997 | 92.1729 | 35.1332 | 33.5553 | 35.23 | 33.8347 | 33.59 | 33.8599 | 35.2415 | 34.6241 | 34.3888 | 37.3041 | 36.2904 | 33.8337 | 34.5434 | 36.2903 | 36.724 | 37.553 | 36.3069 | 33.8498 | 33.066 | 34.8327 | 35.1523 | 33.2387 | 34.3551 | 34.4403 | 33.3569 | 34.3766 | 34.3577 | 34.4201 | 33.9681 | 34.3558 | 35.5252 | 35.5034 | 35.8557 | 35.8067 | 33.8274 | 91.8475 | 92.1172 | 92.2083
2022-09-08 01:32 | 3:42 | 33.2042 | 31.7001 | 32.4445 | 36.1131 | 34.4995 | 34.176 | 35.032 | 35.5633 | 36.6344 | 37.4083 | 36.7698 | 37.7355 | 34.3846 | 34.3604 | 34.6765 | 35.5436 | 35.6205 | 36.2695 | 36.8724 | 36.9946 | 33.3754 | 31.6844 | 92.2643 | 35.1663 | 33.5422 | 35.2181 | 33.8359 | 33.5806 | 33.8606 | 35.2422 | 34.6153 | 34.3979 | 37.3175 | 36.2756 | 33.851 | 34.5697 | 36.2843 | 36.7364 | 37.5448 | 36.2851 | 33.8327 | 33.0804 | 34.8365 | 35.1517 | 33.2294 | 34.3425 | 34.4414 | 33.3459 | 34.3529 | 34.3799 | 34.4168 | 33.9684 | 34.3766 | 35.5268 | 35.4872 | 35.8546 | 35.8083 | 33.792 | 92.1304 | 92.2648 | 92.4503
2022-09-08 01:32 | 3:42 | 33.989 | 31.7016 | 32.5535 | 36.1387 | 34.4841 | 34.1604 | 35.0263 | 35.5684 | 36.6293 | 37.4142 | 36.7854 | 37.73 | 34.3785 | 34.3679 | 34.6461 | 35.5527 | 35.6217 | 36.2874 | 36.8816 | 37.0031 | 33.9352 | 31.6622 | 92.3074 | 35.1746 | 33.5399 | 35.2022 | 33.8351 | 33.5673 | 33.8733 | 35.2432 | 34.6095 | 34.3812 | 37.3037 | 36.2969 | 33.8605 | 34.5345 | 36.2904 | 36.7429 | 37.5636 | 36.2795 | 33.8366 | 33.0639 | 34.8335 | 35.1634 | 33.2595 | 34.3567 | 34.4326 | 33.3444 | 34.3656 | 34.3784 | 34.4184 | 33.9749 | 34.3529 | 35.5168 | 35.5063 | 35.8532 | 35.8155 | 33.8246 | 92.305 | 92.4708 | 92.5323
2022-09-08 01:32 | 3:42 | 34.5021 | 31.6869 | 32.6649 | 36.1655 | 34.4864 | 34.1557 | 35.02 | 35.5533 | 36.6135 | 37.4147 | 36.7769 | 37.7211 | 34.3644 | 34.3635 | 34.6702 | 35.5251 | 35.6211 | 36.26 | 36.8862 | 36.9871 | 34.3295 | 31.6467 | 92.2224 | 35.1986 | 33.568 | 35.2068 | 33.8194 | 33.5965 | 33.8562 | 35.2652 | 34.6178 | 34.3783 | 37.3147 | 36.2991 | 33.8561 | 34.5438 | 36.2756 | 36.7256 | 37.5485 | 36.2903 | 33.828 | 33.0576 | 34.836 | 35.1561 | 33.2595 | 34.3457 | 34.458 | 33.3545 | 34.3706 | 34.3816 | 34.4179 | 33.9586 | 34.3656 | 35.5235 | 35.4912 | 35.8574 | 35.8257 | 33.8207 | 92.5183 | 92.6432 | 92.6448
2022-09-08 01:32 | 3:42 | 34.6807 | 31.6854 | 32.7401 | 36.102 | 34.4901 | 34.1569 | 35.0164 | 35.5673 | 36.6186 | 37.4247 | 36.7815 | 37.7435 | 34.3547 | 34.3662 | 34.6587 | 35.527 | 35.6262 | 36.2577 | 36.8843 | 36.9995 | 34.4134 | 31.626 | 92.343 | 35.2707 | 33.5451 | 35.225 | 33.8498 | 33.5657 | 33.8337 | 35.2478 | 34.6116 | 34.3952 | 37.3114 | 36.291 | 33.8634 | 34.5419 | 36.2969 | 36.7221 | 37.5562 | 36.2843 | 33.848 | 33.049 | 34.8363 | 35.1681 | 33.2827 | 34.3453 | 34.4617 | 33.3524 | 34.3792 | 34.3632 | 34.3846 | 33.9641 | 34.3706 | 35.5226 | 35.4852 | 35.8494 | 35.8174 | 33.814 | 92.6795 | 92.7353 | 92.7408
2022-09-08 01:32 | 3:42 | 34.7593 | 31.6946 | 32.7843 | 36.172 | 34.4906 | 34.152 | 35.03 | 35.5431 | 36.6243 | 37.4117 | 36.765 | 37.7353 | 34.3855 | 34.3678 | 34.6651 | 35.5376 | 35.6213 | 36.2434 | 36.8841 | 37.017 | 34.5216 | 31.6354 | 92.4281 | 35.3046 | 33.5379 | 35.2311 | 33.8327 | 33.5822 | 33.851 | 35.2689 | 34.6212 | 34.3749 | 37.3257 | 36.2919 | 33.8666 | 34.5418 | 36.2991 | 36.7299 | 37.5663 | 36.2904 | 33.8188 | 33.07 | 34.8492 | 35.1628 | 33.2793 | 34.3452 | 34.4287 | 33.3769 | 34.3865 | 34.3705 | 34.3978 | 33.9768 | 34.3792 | 35.5251 | 35.4824 | 35.8483 | 35.8094 | 33.8309 | 92.7749 | 92.9072 | 92.7814
2022-09-08 01:33 | 3:43 | 34.8136 | 31.7017 | 32.8527 | 36.2284 | 34.4638 | 34.1444 | 35.0286 | 35.5795 | 36.6266 | 37.4162 | 36.7683 | 37.7279 | 34.3825 | 34.3684 | 34.661 | 35.5313 | 35.6334 | 36.2621 | 36.8969 | 36.9967 | 34.5953 | 31.6263 | 92.4376 | 35.2456 | 33.5567 | 35.2219 | 33.8366 | 33.5791 | 33.8605 | 35.2593 | 34.6221 | 34.3847 | 37.2974 | 36.2906 | 33.8363 | 34.5493 | 36.291 | 36.7338 | 37.5521 | 36.2756 | 33.8354 | 33.0721 | 34.8511 | 35.1658 | 33.2918 | 34.3377 | 34.4475 | 33.3731 | 34.3806 | 34.3728 | 34.3915 | 33.983 | 34.3865 | 35.5282 | 35.4974 | 35.8565 | 35.8273 | 33.8296 | 92.9825 | 93.0935 | 92.8496
2022-09-08 01:33 | 3:43 | 34.8028 | 31.6962 | 32.8683 | 36.1813 | 34.4935 | 34.1505 | 35.0178 | 35.5706 | 36.6449 | 37.4172 | 36.77 | 37.7192 | 34.3695 | 34.3735 | 34.6608 | 35.5204 | 35.6216 | 36.2469 | 36.8785 | 37.0085 | 34.5728 | 31.6467 | 92.6252 | 35.3812 | 33.5465 | 35.2392 | 33.828 | 33.573 | 33.8561 | 35.271 | 34.6018 | 34.4021 | 37.319 | 36.2967 | 33.8449 | 34.5417 | 36.2919 | 36.7249 | 37.5609 | 36.2969 | 33.8218 | 33.0706 | 34.8661 | 35.1545 | 33.3005 | 34.3544 | 34.4374 | 33.3651 | 34.3863 | 34.3638 | 34.4027 | 33.9883 | 34.3806 | 35.5408 | 35.4866 | 35.8499 | 35.8194 | 33.8315 | 93.1673 | 93.2647 | 93.0516
2022-09-08 01:33 | 3:43 | 34.7448 | 31.7047 | 32.7916 | 36.233 | 34.4833 | 34.1505 | 35.017 | 35.5536 | 36.6329 | 37.4336 | 36.7734 | 37.7348 | 34.3678 | 34.3545 | 34.6612 | 35.5195 | 35.6176 | 36.2691 | 36.8875 | 37.0177 | 34.5513 | 31.6398 | 92.687 | 35.3085 | 33.5546 | 35.2097 | 33.848 | 33.5957 | 33.8634 | 35.2732 | 34.6028 | 34.3941 | 37.3333 | 36.3137 | 33.8704 | 34.5355 | 36.2906 | 36.7322 | 37.5516 | 36.2991 | 33.8215 | 33.0831 | 34.8583 | 35.1644 | 33.3039 | 34.3551 | 34.4538 | 33.3803 | 34.392 | 34.3801 | 34.404 | 33.9672 | 34.3863 | 35.5445 | 35.4915 | 35.8667 | 35.8283 | 33.8205 | 93.3923 | 93.4597 | 93.1222
2022-09-08 01:33 | 3:43 | 34.7182 | 31.7244 | 32.7152 | 36.2116 | 34.4706 | 34.1552 | 35.0268 | 35.5589 | 36.6429 | 37.4287 | 36.7665 | 37.7289 | 34.3802 | 34.3578 | 34.6675 | 35.5188 | 35.6283 | 36.2538 | 36.8863 | 37.0018 | 34.5775 | 31.6201 | 92.7718 | 35.3402 | 33.575 | 35.2159 | 33.8188 | 33.5539 | 33.8666 | 35.2622 | 34.617 | 34.388 | 37.3117 | 36.3069 | 33.8372 | 34.5372 | 36.2967 | 36.755 | 37.5739 | 36.291 | 33.8225 | 33.0846 | 34.8436 | 35.1648 | 33.3131 | 34.3407 | 34.4558 | 33.3706 | 34.3833 | 34.3706 | 34.394 | 33.9751 | 34.392 | 35.5391 | 35.5028 | 35.8562 | 35.831 | 33.8167 | 93.6108 | 93.6584 | 93.1743
2022-09-08 01:33 | 3:43 | 34.6909 | 31.7169 | 32.6229 | 36.3653 | 34.4778 | 34.1452 | 35.013 | 35.5526 | 36.6418 | 37.4301 | 36.7564 | 37.725 | 34.3605 | 34.3728 | 34.6745 | 35.5405 | 35.6199 | 36.2675 | 36.8843 | 37.0085 | 34.5727 | 31.6428 | 92.7439 | 35.3483 | 33.568 | 35.2222 | 33.8354 | 33.5704 | 33.8363 | 35.2704 | 34.6116 | 34.3944 | 37.314 | 36.3032 | 33.8487 | 34.5261 | 36.3137 | 36.7312 | 37.5705 | 36.2919 | 33.8229 | 33.1037 | 34.8717 | 35.1684 | 33.3095 | 34.3234 | 34.4425 | 33.3655 | 34.3823 | 34.366 | 34.3853 | 33.9553 | 34.3833 | 35.5266 | 35.4845 | 35.8619 | 35.8333 | 33.8084 | 93.7299 | 93.8898 | 93.3152
2022-09-08 01:33 | 3:43 | 34.6349 | 31.7329 | 32.6107 | 36.3313 | 34.453 | 34.1516 | 35.0125 | 35.5464 | 36.6353 | 37.4398 | 36.7696 | 37.7194 | 34.3851 | 34.3603 | 34.6644 | 35.533 | 35.5962 | 36.2509 | 36.8989 | 37.016 | 34.5741 | 31.6647 | 92.9738 | 35.3485 | 33.5748 | 35.2374 | 33.8218 | 33.5648 | 33.8449 | 35.2587 | 34.6218 | 34.3862 | 37.3107 | 36.3123 | 33.857 | 34.5394 | 36.3069 | 36.7284 | 37.585 | 36.2906 | 33.8285 | 33.0933 | 34.8578 | 35.1848 | 33.3301 | 34.3609 | 34.4436 | 33.3767 | 34.4017 | 34.3873 | 34.4028 | 33.982 | 34.3823 | 35.5468 | 35.4874 | 35.8554 | 35.8276 | 33.8375 | 93.933 | 94.057 | 93.4272
2022-09-08 01:34 | 3:43 | 34.6398 | 31.7255 | 32.6102 | 36.3039 | 34.4804 | 34.1238 | 35.0266 | 35.549 | 36.6445 | 37.4326 | 36.7879 | 37.742 | 34.373 | 34.3712 | 34.6744 | 35.5415 | 35.6164 | 36.245 | 36.8854 | 37.0148 | 34.5847 | 31.6513 | 93.1507 | 35.3819 | 33.5504 | 35.2183 | 33.8215 | 33.5625 | 33.8704 | 35.2479 | 34.5979 | 34.3832 | 37.3047 | 36.3121 | 33.8623 | 34.5398 | 36.3032 | 36.7362 | 37.5891 | 36.2967 | 33.8313 | 33.1102 | 34.8664 | 35.1603 | 33.3135 | 34.3622 | 34.435 | 33.3916 | 34.3862 | 34.3551 | 34.3963 | 33.9807 | 34.4017 | 35.5528 | 35.4957 | 35.8703 | 35.8353 | 33.8286 | 94.1101 | 94.3186 | 93.5442
2022-09-08 01:34 | 3:44 | 34.7182 | 31.7369 | 32.7112 | 36.2545 | 34.4565 | 34.146 | 35.0027 | 35.5551 | 36.6502 | 37.4277 | 36.7619 | 37.724 | 34.387 | 34.3591 | 34.6565 | 35.5317 | 35.602 | 36.2722 | 36.8923 | 37.017 | 34.6468 | 31.6345 | 93.2473 | 35.3998 | 33.5655 | 35.2461 | 33.8225 | 33.5901 | 33.8372 | 35.266 | 34.5974 | 34.3871 | 37.3021 | 36.3094 | 33.8525 | 34.5362 | 36.3123 | 36.7244 | 37.5705 | 36.3137 | 33.8247 | 33.1131 | 34.8774 | 35.1965 | 33.3385 | 34.3494 | 34.4296 | 33.3796 | 34.3773 | 34.3778 | 34.3786 | 33.9872 | 34.3862 | 35.5498 | 35.4936 | 35.8531 | 35.8353 | 33.831 | 94.2859 | 94.4698 | 93.6522
2022-09-08 01:34 | 3:44 | 34.8446 | 31.7503 | 32.8378 | 36.2946 | 34.4695 | 34.1358 | 35.0273 | 35.5547 | 36.6203 | 37.4274 | 36.7706 | 37.7221 | 34.3648 | 34.3628 | 34.6542 | 35.5362 | 35.6129 | 36.2769 | 36.901 | 37.0025 | 34.7075 | 31.6419 | 93.4568 | 35.3582 | 33.5579 | 35.2166 | 33.8229 | 33.5788 | 33.8487 | 35.2649 | 34.6277 | 34.3795 | 37.3143 | 36.307 | 33.8582 | 34.5314 | 36.3121 | 36.726 | 37.5694 | 36.3069 | 33.8187 | 33.1243 | 34.9078 | 35.1991 | 33.3384 | 34.363 | 34.456 | 33.3808 | 34.4033 | 34.3713 | 34.3816 | 33.9774 | 34.3773 | 35.545 | 35.4798 | 35.8558 | 35.8406 | 33.8075 | 94.4071 | 94.6418 | 93.9168
2022-09-08 01:34 | 3:44 | 34.9035 | 31.7652 | 32.9282 | 36.4605 | 34.4558 | 34.131 | 34.9983 | 35.5519 | 36.6436 | 37.4353 | 36.7807 | 37.7158 | 34.3713 | 34.3625 | 34.6641 | 35.5318 | 35.6132 | 36.2549 | 36.8972 | 37.0075 | 34.7706 | 31.6489 | 93.6567 | 35.3865 | 33.5662 | 35.2242 | 33.8285 | 33.5652 | 33.857 | 35.2602 | 34.6026 | 34.3821 | 37.3096 | 36.299 | 33.8612 | 34.5295 | 36.3094 | 36.7206 | 37.5777 | 36.3032 | 33.8368 | 33.1048 | 34.9008 | 35.1951 | 33.3528 | 34.3474 | 34.4484 | 33.3861 | 34.4073 | 34.3633 | 34.3742 | 33.9973 | 34.4033 | 35.5422 | 35.4976 | 35.8601 | 35.8453 | 33.8128 | 94.5787 | 94.7599 | 93.9543
2022-09-08 01:34 | 3:44 | 34.9754 | 31.7886 | 32.9845 | 36.3434 | 34.4459 | 34.1517 | 35.0021 | 35.5441 | 36.6387 | 37.4499 | 36.7443 | 37.7207 | 34.3747 | 34.3835 | 34.6639 | 35.5192 | 35.6242 | 36.2514 | 36.8964 | 36.9885 | 34.7847 | 31.6519 | 93.8274 | 35.4113 | 33.5507 | 35.2218 | 33.8313 | 33.5798 | 33.8623 | 35.2525 | 34.5911 | 34.3874 | 37.305 | 36.3026 | 33.8477 | 34.5244 | 36.307 | 36.7268 | 37.5725 | 36.3123 | 33.8197 | 33.1125 | 34.8848 | 35.1843 | 33.3662 | 34.3508 | 34.4498 | 33.4038 | 34.4149 | 34.3766 | 34.369 | 33.9942 | 34.4073 | 35.5252 | 35.4868 | 35.8641 | 35.8501 | 33.8156 | 94.7826 | 94.8995 | 94.1089
2022-09-08 01:34 | 3:44 | 35.0125 | 31.7776 | 33.0336 | 36.4121 | 34.4397 | 34.1327 | 35.0111 | 35.5618 | 36.6345 | 37.4239 | 36.7631 | 37.727 | 34.3605 | 34.3499 | 34.6694 | 35.5401 | 35.6251 | 36.2414 | 36.8897 | 36.9854 | 34.793 | 31.6479 | 93.8362 | 35.4577 | 33.5526 | 35.222 | 33.8247 | 33.5752 | 33.8525 | 35.2671 | 34.5949 | 34.3856 | 37.3228 | 36.2987 | 33.8655 | 34.53 | 36.299 | 36.7245 | 37.5718 | 36.3121 | 33.8337 | 33.1169 | 34.8923 | 35.179 | 33.3499 | 34.3715 | 34.4566 | 33.401 | 34.408 | 34.3783 | 34.3625 | 33.9931 | 34.4149 | 35.5523 | 35.4815 | 35.8608 | 35.8282 | 33.8368 | 94.886 | 94.9922 | 94.2082
2022-09-08 01:35 | 3:45 | 35.0043 | 31.7889 | 33.0339 | 36.433 | 34.4423 | 34.1269 | 34.9993 | 35.5459 | 36.6367 | 37.4235 | 36.7477 | 37.7249 | 34.3467 | 34.3518 | 34.6611 | 35.5197 | 35.6107 | 36.2464 | 36.8876 | 36.9977 | 34.7662 | 31.6596 | 93.8965 | 35.5135 | 33.5516 | 35.2332 | 33.8187 | 33.5801 | 33.8582 | 35.2722 | 34.6061 | 34.3796 | 37.3132 | 36.3079 | 33.8686 | 34.5194 | 36.3026 | 36.7136 | 37.5655 | 36.3094 | 33.845 | 33.1301 | 34.8983 | 35.2097 | 33.3757 | 34.3569 | 34.4573 | 33.3999 | 34.4058 | 34.3802 | 34.3686 | 33.9989 | 34.408 | 35.5551 | 35.506 | 35.8564 | 35.8396 | 33.8253 | 94.9524 | 95.0931 | 94.2035
2022-09-08 01:35 | 3:45 | 34.9843 | 31.7921 | 33.1188 | 36.3706 | 34.443 | 34.1258 | 35.0056 | 35.5498 | 36.6349 | 37.4357 | 36.7655 | 37.7168 | 34.3521 | 34.3533 | 34.6785 | 35.5187 | 35.6095 | 36.2413 | 36.892 | 37.0019 | 34.7424 | 31.6621 | 93.9954 | 35.4404 | 33.5522 | 35.2245 | 33.8368 | 33.5763 | 33.8612 | 35.2666 | 34.5997 | 34.3608 | 37.3312 | 36.3292 | 33.8528 | 34.5062 | 36.2987 | 36.7155 | 37.5792 | 36.307 | 33.83 | 33.1447 | 34.9036 | 35.2095 | 33.3968 | 34.3462 | 34.4673 | 33.393 | 34.4159 | 34.3824 | 34.3632 | 34.0189 | 34.4058 | 35.5519 | 35.4918 | 35.8669 | 35.8238 | 33.8132 | 94.9796 | 95.1741 | 94.1967
2022-09-08 01:35 | 3:45 | 35.0181 | 31.7985 | 33.1823 | 36.3603 | 34.4518 | 34.1224 | 35.0167 | 35.5709 | 36.6528 | 37.418 | 36.7713 | 37.7263 | 34.365 | 34.3676 | 34.671 | 35.5174 | 35.6022 | 36.2377 | 36.8981 | 36.9911 | 34.7348 | 31.6698 | 94.0548 | 35.5006 | 33.5673 | 35.2293 | 33.8197 | 33.5795 | 33.8477 | 35.2469 | 34.6022 | 34.3683 | 37.3059 | 36.3254 | 33.8618 | 34.533 | 36.3079 | 36.7035 | 37.5857 | 36.299 | 33.8306 | 33.1202 | 34.9371 | 35.1918 | 33.3835 | 34.3559 | 34.4607 | 33.4178 | 34.4064 | 34.3835 | 34.3732 | 34.0045 | 34.4159 | 35.5456 | 35.488 | 35.8677 | 35.8427 | 33.8236 | 94.9735 | 95.1283 | 94.1223
2022-09-08 01:35 | 3:45 | 35.0887 | 31.7934 | 33.2732 | 36.4766 | 34.437 | 34.1361 | 35.0038 | 35.5509 | 36.6407 | 37.4429 | 36.7797 | 37.7291 | 34.376 | 34.3614 | 34.6521 | 35.5254 | 35.6189 | 36.2538 | 36.9019 | 36.9788 | 34.7974 | 31.6713 | 94.1389 | 35.5577 | 33.5632 | 35.2314 | 33.8337 | 33.5768 | 33.8655 | 35.2573 | 34.5857 | 34.3641 | 37.3245 | 36.3308 | 33.8607 | 34.5102 | 36.3292 | 36.7171 | 37.5779 | 36.3026 | 33.8347 | 33.1422 | 34.9013 | 35.2207 | 33.3922 | 34.3773 | 34.4703 | 33.4282 | 34.4028 | 34.3919 | 34.3588 | 34.01 | 34.4064 | 35.5538 | 35.498 | 35.8691 | 35.8298 | 33.8108 | 94.8092 | 95.0541 | 94.0672
2022-09-08 01:35 | 3:45 | 35.0983 | 31.8097 | 33.284 | 36.4924 | 34.4467 | 34.1493 | 34.9755 | 35.5539 | 36.6295 | 37.4294 | 36.7505 | 37.7189 | 34.3753 | 34.3413 | 34.6598 | 35.537 | 35.6055 | 36.2508 | 36.8994 | 36.9781 | 34.8181 | 31.6547 | 94.006 | 35.4922 | 33.5675 | 35.2414 | 33.845 | 33.5869 | 33.8686 | 35.2382 | 34.5958 | 34.3735 | 37.2843 | 36.349 | 33.854 | 34.5314 | 36.3254 | 36.7116 | 37.5817 | 36.2987 | 33.8186 | 33.159 | 34.8943 | 35.1998 | 33.3898 | 34.3603 | 34.4463 | 33.4122 | 34.4004 | 34.3925 | 34.3777 | 33.9955 | 34.4028 | 35.5472 | 35.4915 | 35.8505 | 35.8324 | 33.8093 | 94.5998 | 94.8285 | 93.9137
2022-09-08 01:35 | 3:45 | 35.0341 | 31.82 | 33.3184 | 36.4342 | 34.429 | 34.1522 | 34.9969 | 35.5498 | 36.6179 | 37.4262 | 36.7562 | 37.7066 | 34.3558 | 34.3613 | 34.665 | 35.5061 | 35.6143 | 36.2336 | 36.9064 | 36.9889 | 34.7995 | 31.6568 | 93.7573 | 35.5376 | 33.5451 | 35.2382 | 33.83 | 33.5553 | 33.8528 | 35.2532 | 34.5909 | 34.3675 | 37.3229 | 36.34 | 33.8639 | 34.5242 | 36.3308 | 36.7091 | 37.5689 | 36.3079 | 33.8289 | 33.1338 | 34.9233 | 35.2193 | 33.4214 | 34.3519 | 34.4606 | 34.4908 | 34.3999 | 34.3942 | 34.3644 | 34.0013 | 34.4004 | 35.5611 | 35.482 | 35.8705 | 35.8362 | 33.8182 | 94.4106 | 94.6392 | 93.7865
2022-09-08 01:36 | 3:45 | 33.9579 | 31.7629 | 33.2222 | 36.5123 | 34.4404 | 34.1222 | 34.9999 | 35.5441 | 36.6284 | 37.4234 | 36.7632 | 37.7136 | 34.3558 | 34.3661 | 34.6433 | 35.5275 | 35.6243 | 36.2361 | 36.875 | 36.9931 | 33.3594 | 31.6071 | 93.6487 | 35.4997 | 33.5724 | 35.2359 | 33.8306 | 33.56 | 33.8618 | 35.2493 | 34.6083 | 34.3833 | 37.304 | 36.3213 | 33.8556 | 34.5056 | 36.349 | 36.7205 | 37.5649 | 36.3292 | 33.8272 | 33.1718 | 34.8884 | 35.2177 | 33.4305 | 34.3494 | 34.4605 | 34.4978 | 34.4069 | 34.3892 | 34.3685 | 33.9931 | 34.3999 | 35.516 | 35.4925 | 35.8476 | 35.8359 | 33.8248 | 94.2093 | 94.4163 | 93.6911
2022-09-08 01:36 | 3:46 | 29.9772 | 30.7924 | 32.6189 | 36.4885 | 34.4295 | 34.1377 | 35.0075 | 35.5286 | 36.6393 | 37.4154 | 36.737 | 37.7146 | 34.3663 | 34.3659 | 34.6356 | 35.5144 | 35.6171 | 36.2384 | 36.8878 | 36.9726 | 29.2564 | 31.5425 | 93.6098 | 35.465 | 33.5502 | 35.2207 | 33.8347 | 33.5545 | 33.8607 | 35.2456 | 34.5744 | 34.3609 | 37.3203 | 36.3291 | 33.865 | 34.5205 | 36.34 | 36.7182 | 37.5697 | 36.3254 | 33.825 | 33.1443 | 34.8994 | 35.1962 | 33.4464 | 34.3616 | 34.4524 | 34.4957 | 34.4079 | 34.3941 | 34.3754 | 33.987 | 34.4069 | 35.5568 | 35.4888 | 35.8527 | 35.8431 | 33.7884 | 94.0703 | 94.172 | 93.6217
2022-09-08 01:36 | 3:46 | 31.619 | 29.2604 | 32.3747 | 36.5428 | 34.4351 | 34.1183 | 35.005 | 35.5602 | 36.6415 | 37.4161 | 36.7646 | 37.7336 | 34.3631 | 34.361 | 34.6465 | 35.5119 | 35.6101 | 36.217 | 36.8605 | 36.9786 | 28.2626 | 31.5346 | 93.5009 | 35.424 | 33.547 | 35.2441 | 33.8186 | 33.5828 | 33.854 | 35.2512 | 34.5853 | 34.3773 | 37.3265 | 36.3391 | 33.8606 | 34.5207 | 36.3213 | 36.7028 | 37.5842 | 36.3308 | 33.8374 | 33.1589 | 34.9335 | 35.2194 | 33.4466 | 34.3484 | 34.4588 | 34.4833 | 34.414 | 34.4079 | 34.3604 | 34.022 | 34.4079 | 35.5379 | 35.4871 | 35.8395 | 35.8465 | 33.8041 | 93.9616 | 94.0438 | 93.5678
2022-09-08 01:36 | 3:46 | 31.7571 | 28.1602 | 31.903 | 36.3588 | 34.4223 | 34.1359 | 34.9929 | 35.5697 | 36.6291 | 37.4293 | 36.7406 | 37.7189 | 34.3711 | 34.3587 | 34.6554 | 35.5283 | 35.626 | 36.2234 | 36.8877 | 36.9691 | 29.3681 | 28.3559 | 93.4293 | 35.4105 | 33.5606 | 35.2375 | 33.8289 | 33.5645 | 33.8639 | 35.246 | 34.5946 | 34.3716 | 37.3042 | 36.3333 | 33.8491 | 34.5179 | 36.3291 | 36.7085 | 37.5823 | 36.349 | 33.8485 | 33.1627 | 34.9091 | 35.214 | 33.4428 | 34.3568 | 34.4566 | 34.4959 | 34.4321 | 34.413 | 34.3679 | 33.9851 | 34.414 | 35.5551 | 35.4841 | 35.8682 | 35.8538 | 33.8025 | 93.8784 | 93.9583 | 93.5127
2022-09-08 01:36 | 3:46 | 31.6916 | 27.5397 | 31.673 | 36.3358 | 34.4075 | 34.129 | 35.017 | 35.5442 | 36.6211 | 37.4059 | 36.7722 | 37.7163 | 34.3757 | 34.3718 | 34.6554 | 35.5033 | 35.6184 | 36.2354 | 36.8926 | 36.9649 | 29.8267 | 27.2574 | 93.4113 | 35.2974 | 33.533 | 35.259 | 33.8272 | 33.5476 | 33.8556 | 35.2376 | 34.5733 | 34.3784 | 37.3186 | 36.332 | 33.8467 | 34.5227 | 36.3391 | 36.7167 | 37.565 | 36.34 | 33.8302 | 33.1482 | 34.9214 | 35.2052 | 33.4421 | 34.3324 | 34.4531 | 34.4665 | 34.4082 | 34.4139 | 34.3635 | 34.0137 | 34.4321 | 35.5437 | 35.4988 | 35.8793 | 35.8391 | 33.7978 | 93.7133 | 93.8451 | 93.3645
2022-09-08 01:36 | 3:46 | 31.5444 | 27.6977 | 31.5035 | 36.3329 | 34.4201 | 34.1283 | 35.0249 | 35.5548 | 36.6319 | 37.4204 | 36.7514 | 37.7335 | 34.361 | 34.3258 | 34.6477 | 35.5247 | 35.6199 | 36.2325 | 36.8779 | 36.9753 | 30.0834 | 26.684 | 93.3921 | 35.2623 | 33.5543 | 35.2279 | 33.825 | 33.5751 | 33.865 | 35.2383 | 34.5923 | 34.3675 | 37.3088 | 36.335 | 33.8486 | 34.5395 | 36.3333 | 36.7155 | 37.5681 | 36.3213 | 33.8455 | 33.1639 | 34.9313 | 35.2247 | 33.4362 | 34.3554 | 34.4613 | 34.4603 | 34.4182 | 34.4005 | 34.3662 | 34.0268 | 34.4082 | 35.5306 | 35.4748 | 35.8702 | 35.8217 | 33.7962 | 93.6587 | 93.7636 | 93.3431
2022-09-08 01:37 | 3:47 | 31.3712 | 27.6034 | 31.3322 | 36.3347 | 34.4168 | 34.1314 | 35.0524 | 35.5575 | 36.6234 | 37.4055 | 36.7649 | 37.7141 | 34.3565 | 34.368 | 34.6372 | 35.5155 | 35.6266 | 36.2208 | 36.8855 | 36.993 | 30.2909 | 26.2968 | 93.3636 | 35.2873 | 33.5657 | 35.2573 | 33.8374 | 33.569 | 33.8606 | 35.245 | 34.6045 | 34.3821 | 37.3055 | 36.3362 | 33.8444 | 34.5399 | 36.332 | 36.7167 | 37.591 | 36.3291 | 33.8408 | 33.1712 | 34.9328 | 35.2299 | 33.4801 | 34.3674 | 34.4599 | 34.4801 | 34.4147 | 34.4228 | 34.3678 | 34.0013 | 34.4182 | 35.5429 | 35.4915 | 35.8538 | 35.8543 | 33.7968 | 93.5123 | 93.6645 | 93.3272
2022-09-08 01:37 | 3:47 | 31.2139 | 27.6263 | 31.2375 | 36.5066 | 34.4184 | 34.1428 | 35.0411 | 35.5569 | 36.645 | 37.4179 | 36.7736 | 37.7191 | 34.3704 | 34.3634 | 34.6363 | 35.5314 | 35.6033 | 36.2382 | 36.8906 | 36.98 | 30.3007 | 26.1058 | 93.3937 | 35.2814 | 33.5316 | 35.247 | 33.8485 | 33.5677 | 33.8491 | 35.2511 | 34.5859 | 34.3733 | 37.3044 | 36.3362 | 33.8559 | 34.5312 | 36.335 | 36.6937 | 37.5738 | 36.3391 | 33.8427 | 33.1746 | 34.9184 | 35.2196 | 33.4629 | 34.3575 | 34.4566 | 34.4601 | 34.4103 | 34.428 | 34.3684 | 34.0043 | 34.4147 | 35.5349 | 35.4873 | 35.8744 | 35.8417 | 33.7932 | 93.4063 | 93.5558 | 93.2296
2022-09-08 01:37 | 3:47 | 31.0936 | 27.7055 | 31.1816 | 36.4689 | 34.4179 | 34.1507 | 35.0543 | 35.5543 | 36.6407 | 37.4094 | 36.7688 | 37.7092 | 34.3687 | 34.3498 | 34.6437 | 35.5022 | 35.6234 | 36.2253 | 36.876 | 36.9617 | 30.1351 | 25.9695 | 93.3689 | 35.2625 | 33.5528 | 35.2446 | 33.8302 | 33.563 | 33.8467 | 35.2484 | 34.6215 | 34.375 | 37.2993 | 36.3471 | 33.8523 | 34.5249 | 36.3362 | 36.7096 | 37.5686 | 36.3333 | 33.8327 | 33.1563 | 34.9192 | 35.1987 | 33.4655 | 34.353 | 34.4399 | 34.469 | 34.4113 | 34.4127 | 34.3735 | 34.0311 | 34.4103 | 35.5336 | 35.4924 | 35.8798 | 35.852 | 33.7893 | 93.4355 | 93.4873 | 93.2352
2022-09-08 01:37 | 3:47 | 30.9103 | 27.7338 | 31.0994 | 36.5003 | 34.3846 | 34.1372 | 35.0647 | 35.5537 | 36.6295 | 37.4301 | 36.7526 | 37.7256 | 34.3704 | 34.3538 | 34.6569 | 35.5225 | 35.638 | 36.2219 | 36.8763 | 36.964 | 29.9919 | 25.847 | 93.4077 | 35.2126 | 33.5485 | 35.2383 | 33.8455 | 33.5629 | 33.8486 | 35.2183 | 34.6073 | 34.3728 | 37.3207 | 36.3472 | 33.8525 | 34.5286 | 36.3362 | 36.7264 | 37.5881 | 36.332 | 33.8375 | 33.1525 | 34.9212 | 35.2186 | 33.4592 | 34.3742 | 34.4585 | 34.4537 | 34.4163 | 34.4023 | 34.3545 | 34.0206 | 34.4113 | 35.5477 | 35.4689 | 35.8755 | 35.8291 | 33.8096 | 93.4338 | 93.4449 | 93.2243
2022-09-08 01:37 | 3:47 | 30.8806 | 27.7705 | 31.0532 | 36.3478 | 34.3978 | 34.1307 | 35.0654 | 35.5826 | 36.6589 | 37.4363 | 36.7555 | 37.7137 | 34.3681 | 34.3479 | 34.6567 | 35.5198 | 35.6289 | 36.2201 | 36.8693 | 36.9521 | 29.8331 | 25.7018 | 93.3888 | 35.1866 | 33.5431 | 35.2476 | 33.8408 | 33.5853 | 33.8444 | 35.2427 | 34.5877 | 34.3755 | 37.3165 | 36.3542 | 33.8627 | 34.5222 | 36.3471 | 36.7192 | 37.5738 | 36.335 | 33.8584 | 33.1678 | 34.9242 | 35.23 | 33.448 | 34.3594 | 34.4658 | 34.4765 | 34.4302 | 34.421 | 34.3578 | 34.0254 | 34.4163 | 35.5394 | 35.4957 | 35.8724 | 35.8515 | 33.8063 | 93.3805 | 93.4405 | 93.2977
2022-09-08 01:37 | 3:47 | 29.9769 | 27.7354 | 30.5598 | 36.4428 | 34.3915 | 34.1411 | 35.0866 | 35.5635 | 36.641 | 37.4068 | 36.7597 | 37.7349 | 34.3673 | 34.3627 | 34.6408 | 35.5344 | 35.6196 | 36.2325 | 36.8926 | 36.9765 | 29.6814 | 25.6037 | 93.2324 | 35.1882 | 33.5681 | 35.2539 | 33.8427 | 33.5727 | 33.8559 | 35.2259 | 34.6054 | 34.3911 | 37.317 | 36.363 | 33.8614 | 34.5331 | 36.3472 | 36.7239 | 37.5917 | 36.3362 | 33.8415 | 33.1793 | 34.9309 | 35.2374 | 33.4747 | 34.3448 | 34.4669 | 34.4607 | 34.4363 | 34.4118 | 34.3728 | 34.0351 | 34.4302 | 35.5447 | 35.4942 | 35.8657 | 35.8582 | 33.8013 | 93.3828 | 93.4083 | 93.1161
2022-09-08 01:38 | 3:47 | 26.737 | 27.6591 | 29.882 | 36.4347 | 34.4027 | 34.1432 | 35.0825 | 35.5731 | 36.6519 | 37.4087 | 36.7751 | 37.7306 | 34.3464 | 34.3617 | 34.6469 | 35.5132 | 35.6306 | 36.2129 | 36.874 | 36.962 | 29.5311 | 25.4828 | 93.2229 | 35.1832 | 33.5529 | 35.2572 | 33.8327 | 33.5717 | 33.8523 | 35.2465 | 34.587 | 34.3851 | 37.3172 | 36.3789 | 33.8659 | 34.5351 | 36.3542 | 36.7123 | 37.5725 | 36.3362 | 33.8481 | 33.1783 | 34.936 | 35.2379 | 33.4637 | 34.3777 | 34.4386 | 34.4725 | 34.4237 | 34.4243 | 34.3603 | 34.0335 | 34.4363 | 35.5376 | 35.4893 | 35.8723 | 35.8512 | 33.7989 | 93.2502 | 93.3519 | 93.046
2022-09-08 01:38 | 3:48 | 26.1395 | 27.4204 | 29.4816 | 36.4239 | 34.404 | 34.1264 | 35.0828 | 35.5588 | 36.6405 | 37.4148 | 36.7723 | 37.7233 | 34.3669 | 34.3503 | 34.6698 | 35.5536 | 35.6428 | 36.2142 | 36.8917 | 36.9522 | 29.3855 | 25.3697 | 93.2483 | 35.1033 | 33.5427 | 35.2711 | 33.8375 | 33.5713 | 33.8525 | 35.234 | 34.6026 | 34.3753 | 37.3235 | 36.3606 | 33.8606 | 34.5295 | 36.363 | 36.7205 | 37.5804 | 36.3471 | 33.8572 | 33.1655 | 34.9423 | 35.2261 | 33.4764 | 34.367 | 34.4348 | 34.462 | 34.4293 | 34.4173 | 34.3712 | 34.0206 | 34.4237 | 35.5517 | 35.4851 | 35.8821 | 35.8666 | 33.7989 | 93.1008 | 93.2738 | 92.9083
2022-09-08 01:38 | 3:48 | 25.8943 | 27.2137 | 29.2913 | 36.3862 | 34.394 | 34.1351 | 35.0963 | 35.5778 | 36.6296 | 37.4245 | 36.7922 | 37.7265 | 34.3738 | 34.3367 | 34.6517 | 35.5304 | 35.6302 | 36.2281 | 36.8874 | 36.9619 | 29.2305 | 25.2865 | 93.1411 | 35.1096 | 33.5374 | 35.2823 | 33.8584 | 33.5673 | 33.8627 | 35.2303 | 34.6113 | 34.3734 | 37.3032 | 36.3768 | 33.8536 | 34.5578 | 36.3789 | 36.7193 | 37.5919 | 36.3472 | 33.8737 | 33.1977 | 34.9315 | 35.235 | 33.4734 | 34.3611 | 34.4526 | 34.4569 | 34.4425 | 34.4247 | 34.3591 | 34.0406 | 34.4293 | 35.5318 | 35.5019 | 35.8924 | 35.8596 | 33.8141 | 93.0341 | 93.237 | 92.9313
2022-09-08 01:38 | 3:48 | 25.695 | 26.9826 | 29.0686 | 36.3673 | 34.3853 | 34.1389 | 35.0879 | 35.5868 | 36.653 | 37.4179 | 36.7768 | 37.7478 | 34.3554 | 34.3436 | 34.6513 | 35.5438 | 35.6595 | 36.2324 | 36.8807 | 36.9734 | 29.0577 | 25.1493 | 93.0643 | 35.0415 | 33.543 | 35.262 | 33.8415 | 33.5643 | 33.8614 | 35.2313 | 34.5855 | 34.3803 | 37.3347 | 36.3675 | 33.8534 | 34.5418 | 36.3606 | 36.7233 | 37.5967 | 36.3542 | 33.8641 | 33.1803 | 34.9456 | 35.2228 | 33.4693 | 34.3637 | 34.4639 | 34.4577 | 34.4411 | 34.4217 | 34.3628 | 34.0361 | 34.4425 | 35.551 | 35.4842 | 35.8553 | 35.8641 | 33.8331 | 93.06 | 93.1882 | 93.0145
2022-09-08 01:38 | 3:48 | 25.4047 | 26.7165 | 28.7933 | 36.3002 | 34.4028 | 34.1392 | 35.1013 | 35.5723 | 36.6479 | 37.4107 | 36.7793 | 37.7248 | 34.3501 | 34.3611 | 34.6519 | 35.527 | 35.6568 | 36.23 | 36.8981 | 36.9668 | 28.8585 | 24.9451 | 93.0506 | 35.136 | 33.5471 | 35.2551 | 33.8481 | 33.5924 | 33.8659 | 35.2158 | 34.6002 | 34.3971 | 37.3176 | 36.3413 | 33.8531 | 34.52 | 36.3768 | 36.718 | 37.5955 | 36.363 | 33.8551 | 33.1889 | 34.9578 | 35.2394 | 33.471 | 34.3526 | 34.4518 | 34.4593 | 34.424 | 34.426 | 34.3625 | 34.0499 | 34.4411 | 35.5701 | 35.4806 | 35.8658 | 35.8639 | 33.8054 | 93.0021 | 93.1368 | 92.9855
2022-09-08 01:38 | 3:48 | 25.2351 | 26.4985 | 28.5883 | 36.261 | 34.3963 | 34.1259 | 35.0859 | 35.573 | 36.6454 | 37.4237 | 36.7825 | 37.7283 | 34.3571 | 34.364 | 34.6682 | 35.5465 | 35.6564 | 36.2296 | 36.867 | 36.9734 | 28.6829 | 24.8355 | 93.0067 | 35.0833 | 33.5596 | 35.2741 | 33.8572 | 33.5662 | 33.8606 | 35.2367 | 34.6031 | 34.3844 | 37.3293 | 36.3649 | 33.8527 | 34.5279 | 36.3675 | 36.7096 | 37.5778 | 36.3789 | 33.8625 | 33.1945 | 34.9229 | 35.2463 | 33.4662 | 34.3495 | 34.4512 | 34.4451 | 34.44 | 34.4297 | 34.3835 | 34.0359 | 34.424 | 35.5543 | 35.4915 | 35.8917 | 35.8629 | 33.8323 | 92.9192 | 93.0726 | 92.8422
2022-09-08 01:39 | 3:49 | 25.0638 | 26.2998 | 28.3838 | 36.2836 | 34.3786 | 34.1411 | 35.0932 | 35.5666 | 36.6643 | 37.4204 | 36.7615 | 37.7235 | 34.3721 | 34.3409 | 34.6576 | 35.5287 | 35.6481 | 36.2119 | 36.8634 | 36.995 | 28.4811 | 24.6644 | 93.0289 | 35.0026 | 33.5386 | 35.2677 | 33.8737 | 33.577 | 33.8536 | 35.2341 | 34.5887 | 34.3822 | 37.3329 | 36.3539 | 33.8426 | 34.5339 | 36.3413 | 36.7176 | 37.5846 | 36.3606 | 33.874 | 33.1889 | 34.9447 | 35.2447 | 33.4726 | 34.3526 | 34.4588 | 34.4578 | 34.4454 | 34.441 | 34.3499 | 34.0477 | 34.44 | 35.5544 | 35.4913 | 35.9025 | 35.8663 | 33.8106 | 92.8048 | 92.9822 | 92.7577
2022-09-08 01:39 | 3:49 | 24.8968 | 26.1041 | 28.1699 | 36.1693 | 34.3816 | 34.1444 | 35.0806 | 35.5748 | 36.636 | 37.4266 | 36.7856 | 37.7141 | 34.3577 | 34.3465 | 34.645 | 35.5388 | 35.6618 | 36.204 | 36.8744 | 36.9652 | 28.2823 | 24.5261 | 92.8461 | 34.9938 | 33.5412 | 35.276 | 33.8641 | 33.5826 | 33.8534 | 35.2129 | 34.599 | 34.4096 | 37.3183 | 36.3646 | 33.8625 | 34.5452 | 36.3649 | 36.7154 | 37.5883 | 36.3768 | 33.8716 | 33.2039 | 34.9601 | 35.2547 | 33.4745 | 34.3604 | 34.4357 | 34.4566 | 34.4384 | 34.4365 | 34.3518 | 34.0475 | 34.4454 | 35.5508 | 35.4787 | 35.8681 | 35.8661 | 33.8126 | 92.6578 | 92.8739 | 92.5696
2022-09-08 01:39 | 3:49 | 24.6725 | 25.8718 | 27.9933 | 36.1874 | 34.3742 | 34.1428 | 35.0792 | 35.5782 | 36.67 | 37.428 | 36.7591 | 37.7494 | 34.3799 | 34.3507 | 34.663 | 35.5408 | 35.6649 | 36.207 | 36.8514 | 36.9871 | 28.057 | 24.3748 | 92.7132 | 35.0522 | 33.5471 | 35.2882 | 33.8551 | 33.5707 | 33.8531 | 35.2342 | 34.6197 | 34.3909 | 37.3347 | 36.357 | 33.8708 | 34.5296 | 36.3539 | 36.7235 | 37.6061 | 36.3675 | 33.8611 | 33.2044 | 34.9455 | 35.2538 | 33.4739 | 34.3449 | 34.4351 | 34.4468 | 34.4509 | 34.4279 | 34.3533 | 34.043 | 34.4384 | 35.574 | 35.4878 | 35.89 | 35.8553 | 33.8311 | 92.5417 | 92.7635 | 92.6291
2022-09-08 01:39 | 3:49 | 24.5396 | 25.7031 | 27.8709 | 36.1936 | 34.369 | 34.1376 | 35.0866 | 35.5685 | 36.6646 | 37.4113 | 36.7831 | 37.7433 | 34.3784 | 34.3516 | 34.6615 | 35.5414 | 35.6504 | 36.2075 | 36.8557 | 36.9802 | 27.8266 | 24.225 | 92.5902 | 34.9164 | 33.539 | 35.2691 | 33.8625 | 33.5713 | 33.8527 | 35.2246 | 34.6069 | 34.409 | 37.3314 | 36.3773 | 33.8658 | 34.5373 | 36.3646 | 36.7137 | 37.5977 | 36.3413 | 33.8608 | 33.2062 | 34.9445 | 35.2696 | 33.4764 | 34.3454 | 34.4514 | 34.4566 | 34.4368 | 34.437 | 34.3676 | 34.0329 | 34.4509 | 35.5656 | 35.4898 | 35.8892 | 35.8723 | 33.8267 | 92.4572 | 92.6535 | 92.4533
2022-09-08 01:39 | 3:49 | 24.3746 | 25.4511 | 27.6896 | 36.1994 | 34.3625 | 34.1359 | 35.1022 | 35.5657 | 36.6522 | 37.4138 | 36.7987 | 37.7308 | 34.3816 | 34.335 | 34.6658 | 35.5572 | 35.6618 | 36.2046 | 36.8625 | 36.9865 | 27.5645 | 24.039 | 92.4934 | 34.8317 | 33.5437 | 35.279 | 33.874 | 33.5748 | 33.8426 | 35.2178 | 34.5928 | 34.3884 | 37.3349 | 36.3653 | 33.8584 | 34.5236 | 36.357 | 36.7289 | 37.6014 | 36.3649 | 33.8622 | 33.2095 | 34.9282 | 35.2561 | 33.4727 | 34.3481 | 34.4522 | 34.4503 | 34.4566 | 34.4252 | 34.3614 | 34.0604 | 34.4368 | 35.5808 | 35.4773 | 35.8941 | 35.8633 | 33.8092 | 92.3569 | 92.5911 | 92.3981
2022-09-08 01:39 | 3:49 | 24.1408 | 25.2361 | 27.4957 | 36.112 | 34.3686 | 34.1287 | 35.1003 | 35.5737 | 36.6763 | 37.4355 | 36.7841 | 37.7365 | 34.3632 | 34.3701 | 34.6711 | 35.5603 | 35.6649 | 36.2116 | 36.8404 | 36.951 | 27.3479 | 23.9117 | 92.4549 | 34.9665 | 33.5496 | 35.2911 | 33.8716 | 33.5762 | 33.8625 | 35.2126 | 34.5939 | 34.4179 | 37.3613 | 36.3692 | 33.8514 | 34.5414 | 36.3773 | 36.7232 | 37.6064 | 36.3539 | 33.8735 | 33.2166 | 34.9354 | 35.2743 | 33.47 | 34.37 | 34.4491 | 34.4472 | 34.4528 | 34.4519 | 34.3413 | 34.0597 | 34.4566 | 35.566 | 35.4708 | 35.9069 | 35.8704 | 33.8239 | 92.233 | 92.4136 | 92.2812
2022-09-08 01:40 | 3:49 | 24.0469 | 25.1263 | 27.2871 | 36.1141 | 34.3632 | 34.135 | 35.0795 | 35.5729 | 36.6806 | 37.4224 | 36.7858 | 37.7499 | 34.3705 | 34.3582 | 34.6587 | 35.5346 | 35.6678 | 36.1984 | 36.8463 | 36.9734 | 27.1258 | 23.783 | 92.3551 | 34.9056 | 33.5333 | 35.2962 | 33.8611 | 33.569 | 33.8708 | 35.2201 | 34.6088 | 34.3891 | 37.3364 | 36.3764 | 33.8737 | 34.5128 | 36.3653 | 36.7239 | 37.5971 | 36.3646 | 33.8773 | 33.1887 | 34.9326 | 35.2706 | 33.4797 | 34.3598 | 34.4293 | 34.4433 | 34.4496 | 34.4396 | 34.3613 | 34.062 | 34.4528 | 35.5735 | 35.4924 | 35.9072 | 35.8723 | 33.8346 | 92.135 | 92.2755 | 92.2718
2022-09-08 01:40 | 3:50 | 23.8153 | 24.8566 | 27.1139 | 36.026 | 34.3732 | 34.1251 | 35.0972 | 35.5671 | 36.6651 | 37.4182 | 36.7776 | 37.7621 | 34.3728 | 34.3366 | 34.6604 | 35.547 | 35.6495 | 36.1918 | 36.8547 | 36.9931 | 26.8713 | 23.56 | 92.2857 | 34.7747 | 33.546 | 35.2807 | 33.8608 | 33.5656 | 33.8658 | 35.2144 | 34.5878 | 34.4098 | 37.3415 | 36.3864 | 33.8721 | 34.5218 | 36.3692 | 36.7312 | 37.6153 | 36.357 | 33.8498 | 33.2038 | 34.9305 | 35.2643 | 33.4863 | 34.3728 | 34.4311 | 34.4488 | 34.4403 | 34.4511 | 34.3661 | 34.0507 | 34.4496 | 35.5945 | 35.478 | 35.9027 | 35.8831 | 33.8367 | 92.0566 | 92.1921 | 92.1896
2022-09-08 01:40 | 3:50 | 23.7174 | 24.7122 | 27.0535 | 36.0262 | 34.3588 | 34.1142 | 35.0988 | 35.5856 | 36.6726 | 37.4257 | 36.7738 | 37.7609 | 34.3638 | 34.3695 | 34.6779 | 35.5501 | 35.661 | 36.2026 | 36.8441 | 36.988 | 26.7442 | 23.4334 | 92.2278 | 34.7421 | 33.5418 | 35.2863 | 33.8622 | 33.5576 | 33.8584 | 35.2245 | 34.5923 | 34.4107 | 37.337 | 36.3639 | 33.8523 | 34.5417 | 36.3764 | 36.7339 | 37.6107 | 36.3773 | 33.8777 | 33.2131 | 34.9342 | 35.2791 | 33.4547 | 34.3541 | 34.4192 | 34.4307 | 34.4414 | 34.4442 | 34.3659 | 34.0625 | 34.4403 | 35.5949 | 35.4772 | 35.8879 | 35.8599 | 33.8481 | 92.0643 | 92.1631 | 92.2318
2022-09-08 01:40 | 3:50 | 23.5153 | 24.5214 | 26.8349 | 36.1117 | 34.3777 | 34.1414 | 35.0863 | 35.5699 | 36.6825 | 37.4213 | 36.7852 | 37.7635 | 34.3801 | 34.3447 | 34.6696 | 35.5378 | 35.6612 | 36.2049 | 36.8647 | 36.975 | 26.6112 | 23.3171 | 92.2012 | 34.9077 | 33.5401 | 35.2879 | 33.8735 | 33.5672 | 33.8514 | 35.2188 | 34.6082 | 34.4085 | 37.3447 | 36.3672 | 33.8526 | 34.5476 | 36.3864 | 36.7268 | 37.6208 | 36.3653 | 33.8711 | 33.2124 | 34.9369 | 35.2725 | 33.4636 | 34.3684 | 34.4235 | 34.4567 | 34.4326 | 34.4433 | 34.361 | 34.0612 | 34.4414 | 35.599 | 35.4451 | 35.9016 | 35.8796 | 33.8355 | 92.1358 | 92.2741 | 92.4117
2022-09-08 01:40 | 3:50 | 23.392 | 24.3495 | 26.6971 | 35.924 | 34.3644 | 34.1393 | 35.0803 | 35.5795 | 36.6836 | 37.4246 | 36.7691 | 37.7559 | 34.3706 | 34.3517 | 34.6832 | 35.5402 | 35.6675 | 36.1964 | 36.8321 | 36.9957 | 26.3247 | 23.1555 | 92.3415 | 34.811 | 33.5553 | 35.3053 | 33.8773 | 33.5666 | 33.8737 | 35.2266 | 34.5832 | 34.4072 | 37.3512 | 36.3674 | 33.8548 | 34.5463 | 36.3639 | 36.7219 | 37.6237 | 36.3692 | 33.8611 | 33.2121 | 34.9429 | 35.2896 | 33.4779 | 34.3537 | 34.4295 | 34.4334 | 34.458 | 34.4596 | 34.3587 | 34.0729 | 34.4326 | 35.586 | 35.4766 | 35.9096 | 35.8679 | 33.8225 | 92.2773 | 92.3797 | 92.4765
2022-09-08 01:40 | 3:50 | 23.2671 | 24.2243 | 26.5117 | 35.9304 | 34.3685 | 34.1401 | 35.0791 | 35.5717 | 36.6716 | 37.4227 | 36.7875 | 37.7521 | 34.366 | 34.3428 | 34.6649 | 35.5554 | 35.6536 | 36.206 | 36.8398 | 36.9877 | 26.0264 | 23.0041 | 92.3575 | 34.6206 | 33.5376 | 35.3012 | 33.8498 | 33.5572 | 33.8721 | 35.2216 | 34.5877 | 34.3876 | 37.3451 | 36.3914 | 33.875 | 34.527 | 36.3672 | 36.7206 | 37.6085 | 36.3764 | 33.8585 | 33.2185 | 34.93 | 35.2972 | 33.4542 | 34.3535 | 34.4147 | 34.4463 | 34.4617 | 34.4457 | 34.3718 | 34.0703 | 34.458 | 35.5918 | 35.4792 | 35.8904 | 35.8763 | 33.8318 | 92.3515 | 92.5199 | 92.5584
2022-09-08 01:41 | 3:50 | 23.1122 | 23.9684 | 26.4087 | 35.9857 | 34.3754 | 34.1233 | 35.09 | 35.5944 | 36.6921 | 37.4272 | 36.7689 | 37.7542 | 34.3873 | 34.3549 | 34.6771 | 35.535 | 35.6784 | 36.1994 | 36.8291 | 36.9698 | 25.6924 | 22.8348 | 92.3543 | 34.6728 | 33.541 | 35.2901 | 33.8777 | 33.5617 | 33.8523 | 35.2216 | 34.603 | 34.4019 | 37.3527 | 36.3774 | 33.851 | 34.5261 | 36.3674 | 36.7336 | 37.6071 | 36.3864 | 33.8627 | 33.2018 | 34.9415 | 35.2821 | 33.4631 | 34.3607 | 34.4111 | 34.4521 | 34.4287 | 34.4453 | 34.3258 | 34.0683 | 34.4617 | 35.5893 | 35.4651 | 35.8949 | 35.8861 | 33.8507 | 92.4782 | 92.6214 | 92.5241
2022-09-08 01:41 | 3:51 | 22.8395 | 23.7643 | 26.2957 | 35.9634 | 34.3604 | 34.1425 | 35.0821 | 35.571 | 36.6988 | 37.4251 | 36.7801 | 37.7574 | 34.3551 | 34.3454 | 34.6667 | 35.5507 | 35.6813 | 36.2052 | 36.8371 | 36.9788 | 25.3376 | 22.549 | 92.3788 | 34.7812 | 33.5463 | 35.2794 | 33.8711 | 33.56 | 33.8526 | 35.2221 | 34.5898 | 34.3969 | 37.354 | 36.3662 | 33.8376 | 34.5221 | 36.3914 | 36.7202 | 37.5925 | 36.3639 | 33.865 | 33.197 | 34.9426 | 35.2762 | 33.4616 | 34.36 | 34.4196 | 34.4561 | 34.4475 | 34.4519 | 34.368 | 34.0778 | 34.4287 | 35.5766 | 35.4913 | 35.9184 | 35.8755 | 33.8319 | 92.5685 | 92.7382 | 92.6075
2022-09-08 01:41 | 3:51 | 22.6898 | 23.5644 | 26.1132 | 36.0744 | 34.3679 | 34.1341 | 35.0642 | 35.5612 | 36.6767 | 37.4082 | 36.7869 | 37.7403 | 34.3778 | 34.3573 | 34.657 | 35.5493 | 35.6746 | 36.1951 | 36.8329 | 37.004 | 25.0085 | 22.4389 | 92.4068 | 34.635 | 33.5461 | 35.2945 | 33.8611 | 33.5435 | 33.8548 | 35.2238 | 34.5829 | 34.4029 | 37.3397 | 36.3804 | 33.8374 | 34.5267 | 36.3774 | 36.7164 | 37.6046 | 36.3672 | 33.869 | 33.2062 | 34.9475 | 35.2978 | 33.4534 | 34.3436 | 34.4169 | 34.4321 | 34.4374 | 34.4597 | 34.3634 | 34.0814 | 34.4475 | 35.5954 | 35.4817 | 35.8947 | 35.8932 | 33.8552 | 92.7123 | 92.8816 | 92.696
2022-09-08 01:41 | 3:51 | 22.5115 | 23.424 | 25.939 | 35.9323 | 34.3635 | 34.1292 | 35.0735 | 35.5656 | 36.6931 | 37.4161 | 36.7796 | 37.7534 | 34.3713 | 34.3704 | 34.6575 | 35.5307 | 35.6714 | 36.1892 | 36.8392 | 36.9713 | 24.7203 | 22.2187 | 92.4796 | 34.5481 | 33.5335 | 35.2754 | 33.8585 | 33.537 | 33.875 | 35.2032 | 34.6092 | 34.3976 | 37.3494 | 36.3766 | 33.8586 | 34.5181 | 36.3662 | 36.7375 | 37.6099 | 36.3674 | 33.8581 | 33.2007 | 34.9064 | 35.2894 | 33.4475 | 34.3616 | 34.4227 | 34.439 | 34.4538 | 34.4354 | 34.3498 | 34.0793 | 34.4374 | 35.6027 | 35.4551 | 35.8932 | 35.8824 | 33.8674 | 92.9169 | 93.0585 | 92.894
2022-09-08 01:41 | 3:51 | 22.5174 | 23.23 | 25.5926 | 35.9475 | 34.3662 | 34.1204 | 35.059 | 35.5672 | 36.7065 | 37.4244 | 36.7896 | 37.7392 | 34.3633 | 34.3557 | 34.6627 | 35.5393 | 35.6693 | 36.1888 | 36.8277 | 36.9705 | 24.4112 | 22.1051 | 92.5795 | 34.5196 | 33.539 | 35.2959 | 33.8627 | 33.5433 | 33.851 | 35.241 | 34.5896 | 34.3916 | 37.3494 | 36.3742 | 33.8615 | 34.525 | 36.3804 | 36.7095 | 37.6237 | 36.3914 | 33.8556 | 33.1961 | 34.9434 | 35.2714 | 33.4377 | 34.3513 | 34.4045 | 34.4377 | 34.4558 | 34.465 | 34.3538 | 34.077 | 34.4538 | 35.6044 | 35.4578 | 35.9013 | 35.876 | 33.8653 | 93.0299 | 93.2525 | 92.9739
2022-09-08 01:41 | 3:51 | 22.3403 | 23.0193 | 25.536 | 35.8577 | 34.3678 | 34.0982 | 35.0608 | 35.5633 | 36.6866 | 37.4202 | 36.7804 | 37.7268 | 34.3766 | 34.349 | 34.6646 | 35.5459 | 35.6689 | 36.1849 | 36.8144 | 36.9832 | 24.1333 | 21.8369 | 92.6505 | 34.3789 | 33.5429 | 35.2832 | 33.865 | 33.5186 | 33.8376 | 35.2123 | 34.5705 | 34.3895 | 37.3513 | 36.3713 | 33.847 | 34.5254 | 36.3766 | 36.7228 | 37.6215 | 36.3774 | 33.8712 | 33.1915 | 34.9068 | 35.2738 | 33.433 | 34.3606 | 34.4023 | 34.4175 | 34.4425 | 34.4532 | 34.3479 | 34.0798 | 34.4558 | 35.5984 | 35.4441 | 35.9113 | 35.8751 | 33.8495 | 93.2325 | 93.4125 | 93.1108
2022-09-08 01:42 | 3:52 | 22.0257 | 22.7948 | 25.4005 | 35.6433 | 34.3684 | 34.1018 | 35.054 | 35.5602 | 36.6797 | 37.4309 | 36.7856 | 37.7459 | 34.3783 | 34.3421 | 34.6563 | 35.5292 | 35.6688 | 36.1686 | 36.8173 | 36.9716 | 23.815 | 21.5905 | 92.7079 | 34.3922 | 33.5176 | 35.2737 | 33.869 | 33.5018 | 33.8374 | 35.227 | 34.5667 | 34.3885 | 37.3387 | 36.3803 | 33.8481 | 34.5103 | 36.3742 | 36.7146 | 37.6062 | 36.3662 | 33.8503 | 33.182 | 34.9129 | 35.2719 | 33.4342 | 34.3507 | 34.4059 | 34.4455 | 34.4436 | 34.4507 | 34.3627 | 34.0799 | 34.4425 | 35.5933 | 35.4672 | 35.8971 | 35.9031 | 33.8549 | 93.2961 | 93.554 | 93.0989
2022-09-08 01:42 | 3:52 | 21.8865 | 22.6694 | 25.3205 | 35.7784 | 34.3735 | 34.1249 | 35.0661 | 35.5635 | 36.6744 | 37.4215 | 36.7818 | 37.745 | 34.3802 | 34.34 | 34.6491 | 35.5394 | 35.6777 | 36.1911 | 36.8153 | 36.9779 | 23.5835 | 21.4376 | 92.8086 | 34.3427 | 33.5047 | 35.2842 | 33.8581 | 33.5169 | 33.8586 | 35.2217 | 34.5861 | 34.3739 | 37.3389 | 36.3655 | 33.8512 | 34.5121 | 36.3713 | 36.7172 | 37.6154 | 36.3804 | 33.8616 | 33.1967 | 34.8979 | 35.2589 | 33.4199 | 34.36 | 34.3945 | 34.4333 | 34.435 | 34.458 | 34.3617 | 34.0658 | 34.4436 | 35.5956 | 35.4524 | 35.8869 | 35.9118 | 33.8489 | 93.4324 | 93.7622 | 93.2655
2022-09-08 01:42 | 3:52 | 21.665 | 22.4691 | 25.1028 | 35.7345 | 34.3545 | 34.1345 | 35.0633 | 35.5564 | 36.6909 | 37.4085 | 36.78 | 37.7518 | 34.3824 | 34.3432 | 34.6547 | 35.5228 | 35.6615 | 36.1756 | 36.8036 | 36.9719 | 23.3574 | 21.19 | 92.8319 | 34.4473 | 33.5259 | 35.2629 | 33.8556 | 33.5121 | 33.8615 | 35.2311 | 34.559 | 34.3892 | 37.339 | 36.3756 | 33.8341 | 34.514 | 36.3803 | 36.7144 | 37.6009 | 36.3766 | 33.8455 | 33.1792 | 34.9026 | 35.2584 | 33.4292 | 34.357 | 34.3932 | 34.4184 | 34.4296 | 34.4474 | 34.3503 | 34.0556 | 34.435 | 35.5983 | 35.4719 | 35.9104 | 35.8897 | 33.8453 | 93.6395 | 93.9747 | 93.3546
2022-09-08 01:42 | 3:52 | 21.5273 | 22.3534 | 24.9675 | 35.7969 | 34.3578 | 34.1131 | 35.041 | 35.556 | 36.6893 | 37.4094 | 36.7903 | 37.7406 | 34.3835 | 34.3653 | 34.657 | 35.5449 | 35.6753 | 36.1487 | 36.8181 | 36.9831 | 23.1803 | 20.9913 | 92.9131 | 34.3435 | 33.5281 | 35.2874 | 33.8712 | 33.5076 | 33.847 | 35.2263 | 34.5506 | 34.3896 | 37.3343 | 36.3667 | 33.856 | 34.4985 | 36.3655 | 36.692 | 37.6255 | 36.3742 | 33.847 | 33.1498 | 34.9014 | 35.2722 | 33.4067 | 34.3604 | 34.3857 | 34.4355 | 34.456 | 34.4783 | 34.3367 | 34.0803 | 34.4296 | 35.5958 | 35.4527 | 35.9203 | 35.885 | 33.834 | 93.825 | 94.1304 | 93.4834
2022-09-08 01:42 | 3:52 | 21.3943 | 22.2079 | 24.7246 | 35.728 | 34.3728 | 34.1161 | 35.0471 | 35.5681 | 36.6889 | 37.4284 | 36.7665 | 37.7265 | 34.3919 | 34.3685 | 34.6506 | 35.53 | 35.6745 | 36.1796 | 36.7946 | 36.9852 | 23.0356 | 20.8002 | 92.9967 | 34.3085 | 33.5307 | 35.2684 | 33.8503 | 33.5159 | 33.8481 | 35.2228 | 34.5615 | 34.3717 | 37.3353 | 36.3777 | 33.8514 | 34.4987 | 36.3756 | 36.7163 | 37.6213 | 36.3713 | 33.8466 | 33.178 | 34.887 | 35.2446 | 33.4266 | 34.3585 | 34.3916 | 34.4332 | 34.4484 | 34.469 | 34.3436 | 34.07 | 34.456 | 35.6052 | 35.463 | 35.9128 | 35.8942 | 33.8385 | 93.9712 | 94.3215 | 93.6199
2022-09-08 01:42 | 3:52 | 21.2378 | 22.0292 | 24.6679 | 35.6726 | 34.3603 | 34.1215 | 35.0515 | 35.5324 | 36.6897 | 37.4155 | 36.7703 | 37.7187 | 34.3925 | 34.3612 | 34.6686 | 35.541 | 35.6797 | 36.1616 | 36.7872 | 36.9939 | 22.9162 | 20.6491 | 93.0802 | 34.2498 | 33.5305 | 35.2639 | 33.8616 | 33.4965 | 33.8512 | 35.2152 | 34.5525 | 34.3755 | 37.3354 | 36.3741 | 33.8419 | 34.5334 | 36.3667 | 36.7169 | 37.6289 | 36.3803 | 33.8491 | 33.1565 | 34.8988 | 35.2665 | 33.4034 | 34.3602 | 34.3824 | 34.4265 | 34.4498 | 34.4585 | 34.3611 | 34.0632 | 34.4484 | 35.6104 | 35.4622 | 35.9139 | 35.9132 | 33.8455 | 94.128 | 94.5011 | 93.735
2022-09-08 01:43 | 3:52 | 21.2671 | 21.875 | 24.4852 | 35.5883 | 34.3712 | 34.1067 | 35.0404 | 35.5778 | 36.6904 | 37.39 | 36.7658 | 37.7461 | 34.3942 | 34.3607 | 34.6587 | 35.5306 | 35.6906 | 36.1559 | 36.7952 | 36.9811 | 22.7977 | 20.5027 | 93.2199 | 34.2216 | 33.5256 | 35.2802 | 33.8455 | 33.5003 | 33.8341 | 35.2174 | 34.5727 | 34.3666 | 37.3425 | 36.3498 | 33.8464 | 34.5275 | 36.3777 | 36.7201 | 37.5993 | 36.3655 | 33.8579 | 33.1835 | 34.8915 | 35.2619 | 33.4007 | 34.3558 | 34.4062 | 34.4158 | 34.4566 | 34.4428 | 34.364 | 34.0615 | 34.4498 | 35.589 | 35.4743 | 35.9068 | 35.8897 | 33.8335 | 94.3243 | 94.6829 | 93.847
2022-09-08 01:43 | 3:53 | 21.0196 | 21.8088 | 24.391 | 35.7221 | 34.3591 | 34.1157 | 35.0412 | 35.5583 | 36.6874 | 37.3965 | 36.7673 | 37.7419 | 34.3892 | 34.3558 | 34.6559 | 35.5151 | 35.6688 | 36.1552 | 36.8105 | 36.9671 | 22.6989 | 20.4171 | 93.3169 | 34.2684 | 33.5217 | 35.2983 | 33.847 | 33.4818 | 33.856 | 35.2119 | 34.573 | 34.3794 | 37.3391 | 36.3705 | 33.8566 | 34.511 | 36.3741 | 36.707 | 37.6155 | 36.3756 | 33.849 | 33.1521 | 34.8849 | 35.25 | 33.3946 | 34.369 | 34.3742 | 34.4145 | 34.4573 | 34.4408 | 34.3409 | 34.0796 | 34.4566 | 35.61 | 35.4735 | 35.8957 | 35.8857 | 33.8426 | 94.4507 | 94.9249 | 94.0553
2022-09-08 01:43 | 3:53 | 20.8025 | 21.6123 | 24.3225 | 35.6412 | 34.3628 | 34.1092 | 35.0483 | 35.5528 | 36.7017 | 37.4165 | 36.7751 | 37.7339 | 34.3941 | 34.3766 | 34.6495 | 35.5279 | 35.6652 | 36.168 | 36.7908 | 36.9869 | 22.5861 | 20.2904 | 93.4858 | 34.1523 | 33.5019 | 35.2694 | 33.8466 | 33.4956 | 33.8514 | 35.2138 | 34.5651 | 34.3773 | 37.3371 | 36.3944 | 33.8261 | 34.51 | 36.3498 | 36.7167 | 37.6301 | 36.3667 | 33.8649 | 33.1577 | 34.8784 | 35.2591 | 33.3835 | 34.3595 | 34.372 | 34.4145 | 34.4673 | 34.4549 | 34.3465 | 34.0561 | 34.4573 | 35.6131 | 35.47 | 35.9237 | 35.8947 | 33.8372 | 94.6533 | 95.1 | 94.1116
2022-09-08 01:43 | 3:53 | 20.6731 | 21.5217 | 24.2368 | 35.5046 | 34.3625 | 34.1065 | 35.0415 | 35.566 | 36.6932 | 37.4112 | 36.7703 | 37.7219 | 34.4079 | 34.3529 | 34.6632 | 35.5087 | 35.6658 | 36.1615 | 36.7975 | 36.9729 | 22.4925 | 20.129 | 93.5372 | 34.0546 | 33.5352 | 35.2749 | 33.8491 | 33.4796 | 33.8419 | 35.2308 | 34.5768 | 34.3751 | 37.3195 | 36.3805 | 33.8456 | 34.5061 | 36.3705 | 36.7153 | 37.6259 | 36.3777 | 33.837 | 33.1375 | 34.8786 | 35.2617 | 33.3864 | 34.3511 | 34.3765 | 34.4227 | 34.4607 | 34.4617 | 34.3507 | 34.0703 | 34.4673 | 35.5935 | 35.4593 | 35.9221 | 35.8715 | 33.8455 | 94.7612 | 95.2451 | 94.2103
2022-09-08 01:43 | 3:53 | 20.5869 | 21.4343 | 24.0407 | 35.5915 | 34.3835 | 34.1142 | 35.03 | 35.5568 | 36.6958 | 37.414 | 36.7728 | 37.7362 | 34.413 | 34.3656 | 34.6538 | 35.5203 | 35.6679 | 36.1471 | 36.7671 | 36.9675 | 22.4184 | 20.0439 | 93.6156 | 34.1155 | 33.513 | 35.2609 | 33.8579 | 33.4925 | 33.8464 | 35.2241 | 34.5542 | 34.3919 | 37.3518 | 36.3829 | 33.8483 | 34.5009 | 36.3944 | 36.7216 | 37.6179 | 36.3741 | 33.8607 | 33.1331 | 34.8648 | 35.2446 | 33.383 | 34.3678 | 34.3802 | 34.4188 | 34.4703 | 34.4611 | 34.3516 | 34.0604 | 34.4607 | 35.5995 | 35.4593 | 35.9267 | 35.8973 | 33.8394 | 94.9667 | 95.3992 | 94.409
2022-09-08 01:43 | 3:53 | 20.512 | 21.3216 | 24.0303 | 35.435 | 34.3499 | 34.1202 | 35.0343 | 35.5691 | 36.6839 | 37.4115 | 36.785 | 37.7377 | 34.4139 | 34.3706 | 34.6535 | 35.5306 | 35.6651 | 36.15 | 36.7774 | 36.9578 | 22.3762 | 19.9153 | 93.7349 | 34.0317 | 33.5163 | 35.2635 | 33.849 | 33.4796 | 33.8566 | 35.2171 | 34.5543 | 34.3865 | 37.3409 | 36.3782 | 33.8396 | 34.5085 | 36.3805 | 36.7041 | 37.6077 | 36.3498 | 33.8576 | 33.1442 | 34.8631 | 35.2359 | 33.3844 | 34.3485 | 34.3848 | 34.3866 | 34.4463 | 34.4674 | 34.335 | 34.0707 | 34.4703 | 35.6154 | 35.4668 | 35.9127 | 35.9181 | 33.8435 | 95.1849 | 95.5438 | 94.4438
2022-09-08 01:44 | 3:54 | 20.2865 | 21.0884 | 23.8839 | 35.7346 | 34.3518 | 34.1063 | 35.0271 | 35.5559 | 36.703 | 37.4087 | 36.766 | 37.7391 | 34.4005 | 34.3792 | 34.6574 | 35.5044 | 35.6681 | 36.1542 | 36.7723 | 36.9597 | 22.3165 | 19.7391 | 93.7869 | 33.9863 | 33.537 | 35.2766 | 33.8649 | 33.4844 | 33.8261 | 35.2223 | 34.5561 | 34.3888 | 37.3365 | 36.393 | 33.8359 | 34.4982 | 36.3829 | 36.7077 | 37.625 | 36.3705 | 33.8421 | 33.1582 | 34.8366 | 35.2293 | 33.3636 | 34.3715 | 34.3537 | 34.4416 | 34.4606 | 34.4669 | 34.3701 | 34.0724 | 34.4463 | 35.6209 | 35.4542 | 35.9077 | 35.9068 | 33.8471 | 95.2074 | 95.6429 | 94.5255
2022-09-08 01:44 | 3:54 | 20.2305 | 20.978 | 23.6595 | 35.4844 | 34.3533 | 34.1114 | 35.0386 | 35.563 | 36.6872 | 37.3982 | 36.7619 | 37.7325 | 34.4228 | 34.3865 | 34.6502 | 35.526 | 35.6697 | 36.1441 | 36.7747 | 36.9527 | 22.257 | 19.725 | 93.9734 | 34.1242 | 33.5175 | 35.2826 | 33.837 | 33.4849 | 33.8456 | 35.2274 | 34.5523 | 34.3815 | 37.3338 | 36.3664 | 33.8293 | 34.5065 | 36.3782 | 36.6971 | 37.6211 | 36.3944 | 33.8436 | 33.141 | 34.8601 | 35.2279 | 33.369 | 34.3544 | 34.3558 | 34.4127 | 34.4605 | 34.4645 | 34.3582 | 34.0628 | 34.4606 | 35.6021 | 35.4609 | 35.9162 | 35.8754 | 33.8267 | 95.2159 | 95.7039 | 94.5568
2022-09-08 01:44 | 3:54 | 20.2034 | 20.9569 | 23.5294 | 35.5014 | 34.3676 | 34.0974 | 35.0157 | 35.5684 | 36.672 | 37.414 | 36.7722 | 37.7337 | 34.428 | 34.3806 | 34.6585 | 35.5155 | 35.6568 | 36.1324 | 36.7747 | 36.9755 | 22.231 | 19.596 | 94.0256 | 33.9894 | 33.4896 | 35.3008 | 33.8607 | 33.4722 | 33.8483 | 35.2075 | 34.5384 | 34.3813 | 37.3325 | 36.379 | 33.8358 | 34.4935 | 36.393 | 36.7063 | 37.6114 | 36.3805 | 33.8466 | 33.1279 | 34.8479 | 35.2367 | 33.3698 | 34.3497 | 34.3596 | 34.4259 | 34.4524 | 34.4557 | 34.3366 | 34.0869 | 34.4605 | 35.6107 | 35.4677 | 35.9148 | 35.8882 | 33.8196 | 95.4149 | 95.8498 | 94.7455
2022-09-08 01:44 | 3:54 | 20.0263 | 20.8229 | 23.4082 | 35.3543 | 34.3614 | 34.108 | 35.0226 | 35.5389 | 36.6845 | 37.3907 | 36.7684 | 37.7442 | 34.4127 | 34.3863 | 34.6419 | 35.5303 | 35.6623 | 36.1488 | 36.7772 | 36.9647 | 22.185 | 19.4861 | 94.1934 | 33.7929 | 33.5196 | 35.285 | 33.8576 | 33.4776 | 33.8396 | 35.2001 | 34.555 | 34.378 | 37.3501 | 36.3617 | 33.8344 | 34.4966 | 36.3664 | 36.7112 | 37.6119 | 36.3829 | 33.8457 | 33.1299 | 34.8306 | 35.2341 | 33.3525 | 34.3436 | 34.3644 | 34.4147 | 34.4588 | 34.453 | 34.3695 | 34.0628 | 34.4524 | 35.5955 | 35.4611 | 35.9162 | 35.9003 | 33.8274 | 95.4159 | 95.8327 | 94.6934
2022-09-08 01:44 | 3:54 | 19.94 | 20.694 | 23.2998 | 35.4538 | 34.3413 | 34.0977 | 35.0008 | 35.5644 | 36.6871 | 37.4041 | 36.784 | 37.7455 | 34.4023 | 34.392 | 34.6308 | 35.5302 | 35.6564 | 36.1478 | 36.7742 | 36.9613 | 22.3881 | 19.3978 | 94.1665 | 33.8971 | 33.4967 | 35.2716 | 33.8421 | 33.4592 | 33.8359 | 35.1923 | 34.5446 | 34.3747 | 37.337 | 36.3726 | 33.8433 | 34.5206 | 36.379 | 36.7253 | 37.6137 | 36.3782 | 33.856 | 33.1305 | 34.8143 | 35.2273 | 33.3408 | 34.3677 | 34.3478 | 34.406 | 34.4566 | 34.4808 | 34.3447 | 34.0866 | 34.4588 | 35.5816 | 35.4809 | 35.9059 | 35.8846 | 33.8241 | 95.3512 | 95.7544 | 94.5735
2022-09-08 01:44 | 3:54 | 19.8393 | 20.5636 | 23.1028 | 35.4176 | 34.3613 | 34.0999 | 35.0213 | 35.5466 | 36.7082 | 37.4049 | 36.7604 | 37.7399 | 34.421 | 34.3833 | 34.6376 | 35.5184 | 35.6795 | 36.1281 | 36.7861 | 36.9532 | 22.3658 | 19.3939 | 94.2602 | 33.7994 | 33.5024 | 35.274 | 33.8436 | 33.4605 | 33.8293 | 35.2026 | 34.5549 | 34.3764 | 37.3509 | 36.3715 | 33.848 | 34.5011 | 36.3617 | 36.6972 | 37.6128 | 36.393 | 33.8619 | 33.1151 | 34.8332 | 35.226 | 33.3446 | 34.3647 | 34.3682 | 34.4066 | 34.4531 | 34.4654 | 34.3517 | 34.0536 | 34.4566 | 35.6004 | 35.4524 | 35.901 | 35.8973 | 33.8075 | 95.1142 | 95.4993 | 94.3782
2022-09-08 01:45 | 3:54 | 19.7742 | 20.5587 | 23.06 | 35.447 | 34.3661 | 34.0944 | 34.9983 | 35.5393 | 36.6849 | 37.3815 | 36.764 | 37.7325 | 34.4118 | 34.3823 | 34.6444 | 35.5257 | 35.6573 | 36.1357 | 36.7622 | 36.9728 | 22.192 | 19.277 | 94.3579 | 33.9377 | 33.4893 | 35.291 | 33.8466 | 33.4628 | 33.8358 | 35.1746 | 34.5486 | 34.3662 | 37.3202 | 36.3728 | 33.8289 | 34.5056 | 36.3726 | 36.7058 | 37.6007 | 36.3664 | 33.8397 | 33.1147 | 34.8125 | 35.2199 | 33.3344 | 34.3769 | 34.3529 | 34.4136 | 34.4613 | 34.4572 | 34.3428 | 34.0657 | 34.4531 | 35.5817 | 35.4658 | 35.9142 | 35.895 | 33.8387 | 94.8874 | 95.2567 | 94.2381
2022-09-08 01:45 | 3:55 | 19.6949 | 20.4415 | 22.9605 | 35.2479 | 34.3659 | 34.1075 | 35.016 | 35.5525 | 36.697 | 37.3808 | 36.7789 | 37.7373 | 34.4243 | 34.4017 | 34.6211 | 35.4997 | 35.6592 | 36.1302 | 36.7519 | 36.9535 | 22.1143 | 19.2057 | 94.3678 | 33.8233 | 33.4793 | 35.2591 | 33.8457 | 33.4697 | 33.8344 | 35.2023 | 34.563 | 34.3797 | 37.3428 | 36.3738 | 33.8225 | 34.4986 | 36.3715 | 36.6954 | 37.5938 | 36.379 | 33.84 | 33.0847 | 34.83 | 35.2045 | 33.3466 | 34.3774 | 34.3551 | 34.3965 | 34.4599 | 34.4861 | 34.3549 | 34.0716 | 34.4613 | 35.6201 | 35.4497 | 35.9316 | 35.901 | 33.8194 | 94.7001 | 94.9997 | 94.0898
2022-09-08 01:45 | 3:55 | 19.5435 | 20.3035 | 22.8652 | 35.2439 | 34.361 | 34.0909 | 35.0097 | 35.5498 | 36.6908 | 37.3833 | 36.7639 | 37.732 | 34.4173 | 34.3862 | 34.6214 | 35.5066 | 35.6542 | 36.1172 | 36.7578 | 36.9445 | 22.0883 | 19.115 | 94.3599 | 33.8484 | 33.4969 | 35.2835 | 33.856 | 33.4727 | 33.8433 | 35.1877 | 34.5403 | 34.379 | 37.3312 | 36.3703 | 33.8422 | 34.5061 | 36.3728 | 36.6989 | 37.5952 | 36.3617 | 33.8364 | 33.1156 | 34.8056 | 35.1969 | 33.3439 | 34.3715 | 34.3425 | 34.4198 | 34.4566 | 34.4672 | 34.3454 | 34.0532 | 34.4599 | 35.5906 | 35.4552 | 35.915 | 35.8987 | 33.7958 | 94.5014 | 94.7917 | 93.9312
2022-09-08 01:45 | 3:55 | 19.5692 | 20.2564 | 22.7037 | 35.3642 | 34.3587 | 34.1077 | 35.0205 | 35.5457 | 36.6925 | 37.3856 | 36.7614 | 37.7466 | 34.4247 | 34.3773 | 34.6258 | 35.4897 | 35.6493 | 36.1226 | 36.7411 | 36.9573 | 22.2592 | 19.0251 | 94.1274 | 33.9152 | 33.4905 | 35.2749 | 33.8619 | 33.4545 | 33.848 | 35.1666 | 34.5447 | 34.3759 | 37.3067 | 36.3858 | 33.8364 | 34.5145 | 36.3738 | 36.7156 | 37.5842 | 36.3726 | 33.8454 | 33.1072 | 34.8096 | 35.1903 | 33.3509 | 34.3838 | 34.3567 | 34.4169 | 34.4399 | 34.4714 | 34.3573 | 34.0622 | 34.4566 | 35.5754 | 35.4742 | 35.9319 | 35.888 | 33.8138 | 94.3231 | 94.6525 | 93.8106
2022-09-08 01:45 | 3:55 | 19.4377 | 20.1302 | 22.7478 | 35.3123 | 34.3718 | 34.0801 | 34.9908 | 35.5319 | 36.6774 | 37.3819 | 36.752 | 37.7253 | 34.4217 | 34.4033 | 34.622 | 35.5225 | 35.6506 | 36.1116 | 36.7373 | 36.9421 | 22.2526 | 18.9143 | 93.9743 | 33.9464 | 33.4922 | 35.2695 | 33.8397 | 33.4744 | 33.8289 | 35.1925 | 34.5532 | 34.3575 | 37.3337 | 36.3851 | 33.8265 | 34.503 | 36.3703 | 36.7088 | 37.5859 | 36.3715 | 33.8382 | 33.0887 | 34.781 | 35.1988 | 33.3238 | 34.3832 | 34.3457 | 34.4241 | 34.4585 | 34.4702 | 34.3704 | 34.0515 | 34.4399 | 35.5754 | 35.4566 | 35.9298 | 35.8867 | 33.7947 | 94.1863 | 94.5124 | 93.7991
2022-09-08 01:45 | 3:55 | 19.3371 | 20.0187 | 22.7394 | 35.2187 | 34.3258 | 34.0968 | 35.0166 | 35.5313 | 36.6767 | 37.3897 | 36.7612 | 37.7349 | 34.426 | 34.4073 | 34.6255 | 35.5138 | 35.6565 | 36.1113 | 36.7249 | 36.9294 | 22.08 | 18.8018 | 93.8061 | 33.7448 | 33.4799 | 35.2654 | 33.84 | 33.4531 | 33.8225 | 35.167 | 34.5554 | 34.3644 | 37.2971 | 36.3652 | 33.832 | 34.5098 | 36.3858 | 36.6867 | 37.5897 | 36.3728 | 33.8406 | 33.0869 | 34.7974 | 35.1857 | 33.3332 | 34.3645 | 34.3453 | 34.4261 | 34.4658 | 34.468 | 34.3557 | 34.0505 | 34.4585 | 35.5738 | 35.4455 | 35.9238 | 35.8886 | 33.8016 | 94.116 | 94.3764 | 93.7429
2022-09-08 01:46 | 3:56 | 19.2945 | 19.9925 | 22.5759 | 35.2179 | 34.368 | 34.0891 | 34.9949 | 35.5237 | 36.6719 | 37.3632 | 36.7636 | 37.7494 | 34.4297 | 34.4149 | 34.617 | 35.5088 | 35.6522 | 36.1064 | 36.7085 | 36.9416 | 22.0381 | 18.7796 | 93.7845 | 33.934 | 33.4925 | 35.2778 | 33.8364 | 33.4642 | 33.8422 | 35.184 | 34.5511 | 34.3821 | 37.3157 | 36.3772 | 33.8242 | 34.5012 | 36.3851 | 36.6833 | 37.5721 | 36.3738 | 33.851 | 33.0638 | 34.7754 | 35.183 | 33.3048 | 34.396 | 34.3452 | 34.409 | 34.4669 | 34.4695 | 34.349 | 34.0244 | 34.4658 | 35.5809 | 35.4431 | 35.9246 | 35.8781 | 33.7903 | 93.9839 | 94.2939 | 93.6759
2022-09-08 01:46 | 3:56 | 19.2086 | 19.9003 | 22.5626 | 35.3027 | 34.3634 | 34.08 | 34.9973 | 35.5392 | 36.6867 | 37.3619 | 36.7674 | 37.7319 | 34.441 | 34.408 | 34.6087 | 35.5121 | 35.6647 | 36.0915 | 36.719 | 36.9148 | 22.0273 | 18.7577 | 93.7697 | 33.6207 | 33.4727 | 35.2768 | 33.8454 | 33.4299 | 33.8364 | 35.1718 | 34.5462 | 34.3685 | 37.3275 | 36.3669 | 33.8115 | 34.5026 | 36.3652 | 36.6881 | 37.5713 | 36.3703 | 33.829 | 33.0724 | 34.7904 | 35.1718 | 33.3 | 34.3882 | 34.3377 | 34.4133 | 34.4386 | 34.4764 | 34.3421 | 34.0185 | 34.4669 | 35.568 | 35.4528 | 35.9245 | 35.8896 | 33.7687 | 93.926 | 94.2097 | 93.6678
2022-09-08 01:46 | 3:56 | 19.1904 | 19.8081 | 22.5229 | 35.3006 | 34.3498 | 34.0826 | 34.9795 | 35.532 | 36.6811 | 37.3657 | 36.7551 | 37.7518 | 34.4365 | 34.4058 | 34.6062 | 35.5064 | 35.6397 | 36.0976 | 36.7083 | 36.9239 | 22.0094 | 18.7105 | 93.6804 | 33.6092 | 33.4732 | 35.2863 | 33.8382 | 33.4536 | 33.8265 | 35.1547 | 34.5392 | 34.3468 | 37.3261 | 36.3726 | 33.8285 | 34.5086 | 36.3772 | 36.6935 | 37.5942 | 36.3858 | 33.8543 | 33.0506 | 34.763 | 35.1721 | 33.2876 | 34.3826 | 34.3544 | 34.4082 | 34.4348 | 34.4903 | 34.34 | 34.0307 | 34.4386 | 35.5639 | 35.4702 | 35.9114 | 35.8717 | 33.7707 | 93.8024 | 94.0885 | 93.5994
2022-09-08 01:46 | 3:56 | 19.0405 | 19.7537 | 22.4488 | 35.3433 | 34.3538 | 34.0897 | 34.9973 | 35.5375 | 36.6716 | 37.359 | 36.7762 | 37.7345 | 34.4279 | 34.4159 | 34.6083 | 35.5029 | 35.6606 | 36.1109 | 36.7079 | 36.9319 | 21.9931 | 18.5965 | 93.6449 | 33.6865 | 33.4991 | 35.2927 | 33.8406 | 33.437 | 33.832 | 35.1588 | 34.5574 | 34.3645 | 37.3181 | 36.3718 | 33.8257 | 34.5 | 36.3669 | 36.6922 | 37.581 | 36.3851 | 33.8282 | 33.0503 | 34.7603 | 35.1707 | 33.3044 | 34.3866 | 34.3551 | 34.4096 | 34.4526 | 34.4759 | 34.3432 | 34.031 | 34.4348 | 35.5757 | 35.4607 | 35.9165 | 35.8805 | 33.7785 | 93.7599 | 94.0301 | 93.526
2022-09-08 01:46 | 3:56 | 19.1095 | 19.7107 | 22.3149 | 35.2567 | 34.3479 | 34.0871 | 34.9845 | 35.5405 | 36.6844 | 37.3501 | 36.7872 | 37.7467 | 34.437 | 34.4064 | 34.6107 | 35.5073 | 35.6513 | 36.0968 | 36.7162 | 36.9111 | 21.9679 | 18.5786 | 93.6091 | 33.6894 | 33.4819 | 35.2694 | 33.851 | 33.448 | 33.8242 | 35.1516 | 34.5518 | 34.3676 | 37.329 | 36.3596 | 33.8149 | 34.5166 | 36.3726 | 36.7001 | 37.5754 | 36.3652 | 33.8311 | 33.0517 | 34.7671 | 35.1553 | 33.2905 | 34.3785 | 34.3407 | 34.4053 | 34.4639 | 34.466 | 34.3653 | 34.0404 | 34.4526 | 35.5765 | 35.4487 | 35.9177 | 35.8832 | 33.7676 | 93.7008 | 93.9569 | 93.5562
2022-09-08 01:46 | 3:56 | 18.9795 | 19.5823 | 22.2362 | 35.1533 | 34.3627 | 34.0889 | 34.9757 | 35.532 | 36.6735 | 37.3632 | 36.7931 | 37.7287 | 34.4252 | 34.4028 | 34.614 | 35.4934 | 35.6566 | 36.0861 | 36.7024 | 36.9101 | 21.9797 | 18.5182 | 93.5666 | 33.6748 | 33.4625 | 35.2754 | 33.829 | 33.453 | 33.8115 | 35.1604 | 34.5534 | 34.3564 | 37.3117 | 36.3811 | 33.8105 | 34.5109 | 36.3718 | 36.6984 | 37.5575 | 36.3772 | 33.8356 | 33.056 | 34.7532 | 35.1476 | 33.2881 | 34.3945 | 34.3234 | 34.4288 | 34.4518 | 34.4876 | 34.3685 | 34.0219 | 34.4639 | 35.5654 | 35.4499 | 35.9264 | 35.8913 | 33.7728 | 93.6174 | 93.8888 | 93.4682
2022-09-08 01:47 | 3:56 | 18.9659 | 19.5698 | 22.1149 | 35.1079 | 34.3617 | 34.0983 | 34.9818 | 35.5356 | 36.6519 | 37.3592 | 36.7647 | 37.7206 | 34.4519 | 34.4004 | 34.5827 | 35.502 | 35.6338 | 36.0711 | 36.7007 | 36.9367 | 21.9364 | 18.4678 | 93.6524 | 33.7384 | 33.4863 | 35.2822 | 33.8543 | 33.441 | 33.8285 | 35.1693 | 34.5603 | 34.3463 | 37.3204 | 36.3614 | 33.8162 | 34.51 | 36.3596 | 36.6949 | 37.5735 | 36.3669 | 33.8392 | 33.0325 | 34.7297 | 35.1613 | 33.2979 | 34.3847 | 34.3609 | 34.4007 | 34.4512 | 34.484 | 34.3612 | 34.0373 | 34.4518 | 35.5573 | 35.4813 | 35.9272 | 35.8851 | 33.7656 | 93.5743 | 93.8947 | 93.3905
2022-09-08 01:47 | 3:57 | 18.9144 | 19.4614 | 21.9571 | 35.2531 | 34.3503 | 34.0742 | 34.9988 | 35.5254 | 36.6731 | 37.365 | 36.7693 | 37.7351 | 34.4396 | 34.3999 | 34.6134 | 35.4929 | 35.6533 | 36.0879 | 36.6873 | 36.9374 | 21.9155 | 18.4624 | 93.5312 | 33.5297 | 33.449 | 35.2809 | 33.8282 | 33.4437 | 33.8257 | 35.1481 | 34.5595 | 34.3676 | 37.3259 | 36.3555 | 33.8136 | 34.5097 | 36.3811 | 36.686 | 37.5697 | 36.3726 | 33.8516 | 33.0204 | 34.7563 | 35.1504 | 33.2896 | 34.397 | 34.3622 | 34.4162 | 34.4588 | 34.4972 | 34.3607 | 34.0324 | 34.4512 | 35.5591 | 35.479 | 35.9242 | 35.8851 | 33.7578 | 93.5622 | 93.828 | 93.4216
2022-09-08 01:47 | 3:57 | 18.8722 | 19.4296 | 21.9837 | 35.1022 | 34.3367 | 34.0979 | 34.9715 | 35.5255 | 36.666 | 37.3582 | 36.7642 | 37.752 | 34.4511 | 34.4069 | 34.614 | 35.49 | 35.6391 | 36.1018 | 36.7044 | 36.916 | 21.8555 | 18.3838 | 93.5286 | 33.678 | 33.4557 | 35.277 | 33.8311 | 33.4324 | 33.8149 | 35.1504 | 34.5643 | 34.3806 | 37.3224 | 36.3599 | 33.8311 | 34.4985 | 36.3614 | 36.7027 | 37.5596 | 36.3718 | 33.8467 | 33.0487 | 34.7529 | 35.1645 | 33.2867 | 34.3948 | 34.3494 | 34.4172 | 34.4357 | 34.4734 | 34.3558 | 34.0305 | 34.4588 | 35.5623 | 35.4708 | 35.9191 | 35.8924 | 33.7538 | 93.5589 | 93.7531 | 93.4391
2022-09-08 01:47 | 3:57 | 18.741 | 19.3451 | 21.8912 | 35.186 | 34.3436 | 34.0844 | 34.9867 | 35.5399 | 36.6718 | 37.3559 | 36.7698 | 37.7518 | 34.4442 | 34.4079 | 34.6059 | 35.5043 | 35.6491 | 36.0807 | 36.6906 | 36.9218 | 21.8529 | 18.2988 | 93.5341 | 33.562 | 33.4709 | 35.3 | 33.8356 | 33.4337 | 33.8105 | 35.178 | 34.5616 | 34.3728 | 37.3137 | 36.3726 | 33.8184 | 34.5088 | 36.3555 | 36.6986 | 37.5391 | 36.3596 | 33.8416 | 33.0251 | 34.7149 | 35.1361 | 33.2669 | 34.3973 | 34.363 | 34.4061 | 34.4351 | 34.4966 | 34.3766 | 34.0197 | 34.4357 | 35.5606 | 35.471 | 35.9393 | 35.8696 | 33.7762 | 93.493 | 93.6472 | 93.3521
2022-09-08 01:47 | 3:57 | 18.7858 | 19.3104 | 21.8444 | 35.1404 | 34.3611 | 34.0988 | 34.96 | 35.5279 | 36.6677 | 37.3596 | 36.7659 | 37.7505 | 34.4433 | 34.414 | 34.603 | 35.4939 | 35.6418 | 36.073 | 36.691 | 36.9253 | 21.835 | 18.3144 | 93.5125 | 33.7277 | 33.4571 | 35.2775 | 33.8392 | 33.419 | 33.8162 | 35.1482 | 34.5554 | 34.3836 | 37.3241 | 36.3703 | 33.8159 | 34.5099 | 36.3599 | 36.696 | 37.5518 | 36.3811 | 33.8409 | 33.0251 | 34.7192 | 35.1453 | 33.2736 | 34.3962 | 34.3474 | 34.4011 | 34.4514 | 34.4726 | 34.3529 | 34.0192 | 34.4351 | 35.5726 | 35.4428 | 35.9377 | 35.9088 | 33.7745 | 93.382 | 93.5431 | 93.235
2022-09-08 01:47 | 3:57 | 18.701 | 19.2367 | 21.8791 | 35.1523 | 34.364 | 34.0949 | 34.9799 | 35.5471 | 36.6489 | 37.3552 | 36.7897 | 37.7556 | 34.4596 | 34.4321 | 34.5899 | 35.5091 | 35.6556 | 36.085 | 36.678 | 36.9223 | 21.8002 | 18.2816 | 93.367 | 33.6617 | 33.4518 | 35.2943 | 33.8516 | 33.4395 | 33.8136 | 35.1619 | 34.5737 | 34.3707 | 37.3195 | 36.3696 | 33.8443 | 34.513 | 36.3726 | 36.6988 | 37.5581 | 36.3614 | 33.837 | 33.0286 | 34.7322 | 35.1413 | 33.27 | 34.4005 | 34.3508 | 34.4159 | 34.4522 | 34.4718 | 34.3656 | 34.0311 | 34.4514 | 35.5808 | 35.4721 | 35.9299 | 35.8862 | 33.7654 | 93.256 | 93.4777 | 93.1431
2022-09-08 01:48 | 3:58 | 18.7019 | 19.2455 | 21.7869 | 35.1396 | 34.3409 | 34.0967 | 34.9689 | 35.5323 | 36.6745 | 37.362 | 36.7864 | 37.7521 | 34.4457 | 34.4082 | 34.6051 | 35.4934 | 35.6489 | 36.0818 | 36.6985 | 36.9136 | 21.7458 | 18.242 | 93.3078 | 33.5371 | 33.4619 | 35.3014 | 33.8467 | 33.4399 | 33.8311 | 35.1631 | 34.55 | 34.3689 | 37.328 | 36.3943 | 33.819 | 34.5107 | 36.3703 | 36.6918 | 37.5694 | 36.3555 | 33.8446 | 33.0011 | 34.7234 | 35.1553 | 33.2685 | 34.3961 | 34.3715 | 34.418 | 34.4491 | 34.4814 | 34.3706 | 34.0358 | 34.4522 | 35.5601 | 35.4606 | 35.952 | 35.8913 | 33.7752 | 93.1731 | 93.4059 | 93.1335
2022-09-08 01:48 | 3:58 | 18.6032 | 19.1552 | 21.6854 | 35.0599 | 34.3465 | 34.0802 | 34.9695 | 35.5226 | 36.6702 | 37.3411 | 36.7804 | 37.7366 | 34.4453 | 34.4182 | 34.5959 | 35.4765 | 35.6516 | 36.0883 | 36.6951 | 36.9154 | 21.7428 | 18.1677 | 93.3418 | 33.4673 | 33.4442 | 35.289 | 33.8416 | 33.425 | 33.8184 | 35.1439 | 34.5674 | 34.3716 | 37.3258 | 36.3627 | 33.8093 | 34.5135 | 36.3696 | 36.6851 | 37.5575 | 36.3599 | 33.8586 | 33.0192 | 34.7199 | 35.1534 | 33.2667 | 34.4038 | 34.3569 | 34.4385 | 34.4293 | 34.4913 | 34.3792 | 34.033 | 34.4491 | 35.5721 | 35.4654 | 35.9234 | 35.8926 | 33.7649 | 93.1263 | 93.3084 | 93.0639
2022-09-08 01:48 | 3:58 | 18.5818 | 19.0636 | 21.5826 | 35.0523 | 34.3507 | 34.0806 | 34.9885 | 35.5439 | 36.6829 | 37.3411 | 36.7879 | 37.757 | 34.4519 | 34.4147 | 34.5728 | 35.4917 | 35.6504 | 36.066 | 36.6687 | 36.9182 | 21.7063 | 18.1423 | 93.2615 | 33.4292 | 33.4607 | 35.2987 | 33.8409 | 33.4435 | 33.8159 | 35.1508 | 34.5649 | 34.3699 | 37.325 | 36.3749 | 33.825 | 34.5156 | 36.3943 | 36.6922 | 37.5616 | 36.3726 | 33.8443 | 33.0146 | 34.7171 | 35.1539 | 33.2634 | 34.3986 | 34.3462 | 34.423 | 34.4311 | 34.4938 | 34.3865 | 33.9963 | 34.4293 | 35.5827 | 35.4635 | 35.9421 | 35.9205 | 33.7679 | 93.053 | 93.2246 | 92.9989
2022-09-08 01:48 | 3:58 | 18.5672 | 19.0642 | 21.4743 | 34.9637 | 34.3516 | 34.0924 | 34.9833 | 35.5442 | 36.6676 | 37.3551 | 36.804 | 37.7573 | 34.4597 | 34.4103 | 34.5903 | 35.497 | 35.649 | 36.0766 | 36.6868 | 36.9222 | 21.6579 | 18.1635 | 93.1915 | 33.488 | 33.4619 | 35.2994 | 33.837 | 33.4391 | 33.8443 | 35.1512 | 34.5658 | 34.3655 | 37.3387 | 36.3862 | 33.8122 | 34.5169 | 36.3627 | 36.692 | 37.5677 | 36.3703 | 33.8347 | 33.0366 | 34.7239 | 35.152 | 33.2446 | 34.3906 | 34.3559 | 34.4348 | 34.4192 | 34.4729 | 34.3806 | 34.0166 | 34.4311 | 35.5666 | 35.4791 | 35.9405 | 35.9077 | 33.7696 | 92.8872 | 93.056 | 92.9177
2022-09-08 01:48 | 3:58 | 18.4445 | 18.9588 | 21.4214 | 34.9531 | 34.335 | 34.1161 | 34.9619 | 35.5418 | 36.6928 | 37.3452 | 36.8038 | 37.7622 | 34.4354 | 34.4113 | 34.6022 | 35.4954 | 35.6512 | 36.0683 | 36.673 | 36.9178 | 21.6311 | 18.1117 | 93.159 | 33.6046 | 33.449 | 35.283 | 33.8446 | 33.4284 | 33.819 | 35.1465 | 34.566 | 34.3895 | 37.348 | 36.3859 | 33.8064 | 34.4949 | 36.3749 | 36.7054 | 37.5586 | 36.3696 | 33.8487 | 33.0047 | 34.7007 | 35.1455 | 33.2701 | 34.4128 | 34.3773 | 34.426 | 34.4235 | 34.4853 | 34.3863 | 34.0268 | 34.4192 | 35.5915 | 35.4495 | 35.9162 | 35.9066 | 33.7623 | 92.7622 | 92.9423 | 92.8679
2022-09-08 01:48 | 3:58 | 18.443 | 18.9189 | 21.3385 | 35.0077 | 34.3701 | 34.0844 | 34.9528 | 35.5393 | 36.6725 | 37.3592 | 36.7929 | 37.7615 | 34.465 | 34.4163 | 34.5726 | 35.4959 | 35.6558 | 36.0784 | 36.6766 | 36.9195 | 21.6015 | 18.0009 | 93.0404 | 33.5992 | 33.4376 | 35.2704 | 33.8586 | 33.4344 | 33.8093 | 35.1511 | 34.5608 | 34.3869 | 37.3189 | 36.3681 | 33.82 | 34.5165 | 36.3862 | 36.6951 | 37.5569 | 36.3943 | 33.8445 | 32.9936 | 34.6925 | 35.1493 | 33.232 | 34.416 | 34.3603 | 34.422 | 34.4295 | 34.5006 | 34.392 | 34.0303 | 34.4235 | 35.5883 | 35.4704 | 35.9257 | 35.8962 | 33.7725 | 92.6841 | 92.8211 | 92.7432
2022-09-08 01:49 | 3:58 | 18.3944 | 18.8993 | 21.2875 | 35.0021 | 34.3582 | 34.1116 | 34.9786 | 35.5538 | 36.6689 | 37.3603 | 36.8099 | 37.756 | 34.4532 | 34.4302 | 34.5864 | 35.4928 | 35.641 | 36.0761 | 36.6655 | 36.9308 | 21.5732 | 17.9898 | 92.9357 | 33.3468 | 33.4627 | 35.2837 | 33.8443 | 33.4344 | 33.825 | 35.1661 | 34.5689 | 34.39 | 37.3399 | 36.3573 | 33.8051 | 34.5166 | 36.3859 | 36.704 | 37.5666 | 36.3627 | 33.8409 | 33.01 | 34.7036 | 35.1376 | 33.2509 | 34.4246 | 34.3519 | 34.4314 | 34.4147 | 34.4899 | 34.3833 | 34.0059 | 34.4295 | 35.5778 | 35.4646 | 35.9247 | 35.9039 | 33.7747 | 92.5291 | 92.6393 | 92.6497
2022-09-08 01:49 | 3:59 | 18.2915 | 18.8217 | 21.2816 | 34.9413 | 34.3366 | 34.0813 | 34.9837 | 35.5312 | 36.6855 | 37.3585 | 36.8034 | 37.7704 | 34.4507 | 34.4363 | 34.5869 | 35.4923 | 35.6478 | 36.0791 | 36.6928 | 36.9166 | 21.5494 | 17.9172 | 92.9441 | 33.3858 | 33.4412 | 35.2882 | 33.8347 | 33.4402 | 33.8122 | 35.1493 | 34.5641 | 34.3848 | 37.3341 | 36.3808 | 33.8125 | 34.5247 | 36.3681 | 36.7054 | 37.5568 | 36.3749 | 33.8397 | 32.965 | 34.7218 | 35.1581 | 33.209 | 34.4275 | 34.3494 | 34.4409 | 34.4111 | 34.4851 | 34.3823 | 34.0011 | 34.4147 | 35.6051 | 35.4706 | 35.9356 | 35.8948 | 33.7784 | 92.4095 | 92.5676 | 92.5617
2022-09-08 01:49 | 3:59 | 18.222 | 18.7439 | 21.1894 | 34.9552 | 34.3695 | 34.0983 | 34.9545 | 35.5361 | 36.68 | 37.3446 | 36.8019 | 37.7604 | 34.458 | 34.4237 | 34.5782 | 35.4915 | 35.6435 | 36.0693 | 36.6769 | 36.9234 | 21.5462 | 17.8741 | 92.828 | 33.3004 | 33.4368 | 35.2809 | 33.8487 | 33.4202 | 33.8064 | 35.1494 | 34.5686 | 34.3779 | 37.3492 | 36.3782 | 33.8009 | 34.5231 | 36.3573 | 36.6964 | 37.5451 | 36.3862 | 33.821 | 32.9902 | 34.7039 | 35.1497 | 33.2094 | 34.4067 | 34.3616 | 34.4174 | 34.4196 | 34.4887 | 34.4017 | 34.0209 | 34.4111 | 35.5733 | 35.4459 | 35.9394 | 35.8973 | 33.7752 | 92.2462 | 92.3647 | 92.4749
2022-09-08 01:49 | 3:59 | 18.1865 | 18.6919 | 21.1892 | 34.9053 | 34.3447 | 34.109 | 34.9556 | 35.529 | 36.6766 | 37.3528 | 36.7997 | 37.7617 | 34.4474 | 34.4293 | 34.587 | 35.4917 | 35.6463 | 36.0632 | 36.6928 | 36.9141 | 21.5304 | 17.8244 | 92.7053 | 33.3282 | 33.4505 | 35.2837 | 33.8445 | 33.4423 | 33.82 | 35.1542 | 34.5701 | 34.4011 | 37.3309 | 36.3803 | 33.8033 | 34.5086 | 36.3808 | 36.7025 | 37.5428 | 36.3859 | 33.8346 | 32.9867 | 34.6892 | 35.1442 | 33.2342 | 34.4096 | 34.3484 | 34.4221 | 34.4169 | 34.4995 | 34.3862 | 34.0179 | 34.4196 | 35.5837 | 35.473 | 35.9387 | 35.9124 | 33.7868 | 92.1373 | 92.2286 | 92.3454
2022-09-08 01:49 | 3:59 | 18.2149 | 18.7066 | 21.1688 | 34.9255 | 34.3517 | 34.1049 | 34.9696 | 35.5416 | 36.6755 | 37.3457 | 36.7894 | 37.75 | 34.4783 | 34.4425 | 34.6017 | 35.4888 | 35.6557 | 36.0823 | 36.6807 | 36.9219 | 21.5112 | 17.8505 | 92.6543 | 33.2891 | 33.4567 | 35.2751 | 33.8409 | 33.4194 | 33.8051 | 35.1378 | 34.58 | 34.3872 | 37.3392 | 36.3663 | 33.8058 | 34.5173 | 36.3782 | 36.7028 | 37.5368 | 36.3681 | 33.8313 | 32.9839 | 34.6884 | 35.1333 | 33.2203 | 34.4138 | 34.3568 | 34.4384 | 34.4227 | 34.4841 | 34.3773 | 34.0067 | 34.4169 | 35.5816 | 35.4646 | 35.926 | 35.8939 | 33.794 | 92.0472 | 92.1638 | 92.2994
2022-09-08 01:49 | 3:59 | 18.1063 | 18.5898 | 21.0673 | 34.7662 | 34.3428 | 34.1041 | 34.9607 | 35.5425 | 36.6953 | 37.3359 | 36.8082 | 37.7859 | 34.469 | 34.4411 | 34.5838 | 35.4935 | 35.6552 | 36.0654 | 36.6742 | 36.9361 | 21.492 | 17.7827 | 92.5564 | 33.3007 | 33.4363 | 35.3008 | 33.8397 | 33.4154 | 33.8125 | 35.1438 | 34.5737 | 34.3843 | 37.3507 | 36.3662 | 33.81 | 34.5359 | 36.3803 | 36.6994 | 37.5426 | 36.3573 | 33.8264 | 32.9731 | 34.6975 | 35.1384 | 33.2018 | 34.4143 | 34.3324 | 34.4187 | 34.4045 | 34.4864 | 34.4033 | 34.0252 | 34.4227 | 35.5923 | 35.4568 | 35.9271 | 35.9111 | 33.7873 | 92.1206 | 92.1908 | 92.4776
2022-09-08 01:50 | 3:59 | 18.1187 | 18.5923 | 21.0298 | 34.8893 | 34.3549 | 34.0909 | 34.9707 | 35.5277 | 36.6722 | 37.3328 | 36.8124 | 37.7798 | 34.4585 | 34.424 | 34.5972 | 35.4781 | 35.6529 | 36.0638 | 36.6915 | 36.9049 | 21.4986 | 17.7607 | 92.488 | 33.2316 | 33.4389 | 35.2903 | 33.821 | 33.4256 | 33.8009 | 35.138 | 34.5749 | 34.3735 | 37.335 | 36.3807 | 33.802 | 34.5239 | 36.3663 | 36.7094 | 37.5534 | 36.3808 | 33.8383 | 32.9741 | 34.6868 | 35.1318 | 33.2008 | 34.4023 | 34.3554 | 34.4511 | 34.4023 | 34.4901 | 34.4073 | 34.0187 | 34.4045 | 35.6005 | 35.4589 | 35.9769 | 35.9084 | 33.8025 | 92.1762 | 92.2573 | 92.4039
2022-09-08 01:50 | 4:00 | 18.0899 | 18.5938 | 21.0103 | 34.8408 | 34.3454 | 34.1071 | 34.9528 | 35.5646 | 36.6826 | 37.3565 | 36.8148 | 37.794 | 34.4428 | 34.44 | 34.5884 | 35.4978 | 35.6426 | 36.0557 | 36.6626 | 36.9149 | 21.4806 | 17.7161 | 92.4595 | 33.4189 | 33.4353 | 35.2884 | 33.8346 | 33.4329 | 33.8033 | 35.1471 | 34.5651 | 34.3845 | 37.3517 | 36.3704 | 33.8019 | 34.5179 | 36.3662 | 36.7181 | 37.5476 | 36.3782 | 33.8227 | 32.9696 | 34.6961 | 35.1488 | 33.2029 | 34.4117 | 34.3674 | 34.4283 | 34.4059 | 34.4906 | 34.4149 | 34.0154 | 34.4023 | 35.5896 | 35.4738 | 35.9406 | 35.8957 | 33.7916 | 92.2738 | 92.352 | 92.5886
2022-09-08 01:50 | 4:00 | 18.0475 | 18.5141 | 20.9892 | 34.8165 | 34.3573 | 34.112 | 34.9777 | 35.5431 | 36.6722 | 37.3515 | 36.8142 | 37.793 | 34.4408 | 34.4454 | 34.5804 | 35.4734 | 35.6475 | 36.072 | 36.6531 | 36.9183 | 21.4629 | 17.7119 | 92.3941 | 33.23 | 33.4459 | 35.2912 | 33.8313 | 33.4286 | 33.8058 | 35.146 | 34.5765 | 34.3991 | 37.3401 | 36.3649 | 33.8046 | 34.5379 | 36.3807 | 36.7092 | 37.5506 | 36.3803 | 33.8278 | 32.9799 | 34.6977 | 35.138 | 33.1981 | 34.4269 | 34.3575 | 34.4471 | 34.3945 | 34.4638 | 34.408 | 34.0112 | 34.4059 | 35.604 | 35.4626 | 35.9667 | 35.906 | 33.7792 | 92.3438 | 92.497 | 92.6243
2022-09-08 01:50 | 4:00 | 18.0072 | 18.4497 | 20.937 | 34.8621 | 34.3704 | 34.1119 | 34.9518 | 35.5536 | 36.6877 | 37.3359 | 36.8115 | 37.7867 | 34.4549 | 34.4384 | 34.5793 | 35.4868 | 35.6703 | 36.0509 | 36.6726 | 36.9111 | 21.4695 | 17.664 | 92.5048 | 33.4769 | 33.4438 | 35.2967 | 33.8264 | 33.4185 | 33.81 | 35.1541 | 34.58 | 34.3985 | 37.3349 | 36.3651 | 33.813 | 34.5237 | 36.3704 | 36.7142 | 37.551 | 36.3663 | 33.8246 | 32.9737 | 34.6826 | 35.1532 | 33.1839 | 34.4253 | 34.353 | 34.4458 | 34.3932 | 34.4935 | 34.4058 | 34.017 | 34.3945 | 35.6029 | 35.4664 | 35.9773 | 35.9098 | 33.7851 | 92.5671 | 92.6665 | 92.7844
2022-09-08 01:50 | 4:00 | 17.9719 | 18.4177 | 20.897 | 34.7772 | 34.3557 | 34.0996 | 34.9523 | 35.5362 | 36.6735 | 37.3438 | 36.8043 | 37.7968 | 34.4617 | 34.4509 | 34.593 | 35.4805 | 35.665 | 36.0652 | 36.6762 | 36.9342 | 21.4483 | 17.6213 | 92.4374 | 33.2926 | 33.4412 | 35.2808 | 33.8383 | 33.4276 | 33.802 | 35.1432 | 34.5662 | 34.4058 | 37.3345 | 36.3444 | 33.8007 | 34.5272 | 36.3649 | 36.6974 | 37.5379 | 36.3662 | 33.8035 | 32.9585 | 34.666 | 35.1311 | 33.1721 | 34.4159 | 34.3742 | 34.4488 | 34.3857 | 34.4833 | 34.4159 | 34.018 | 34.3932 | 35.6112 | 35.4522 | 35.956 | 35.9165 | 33.7717 | 92.6412 | 92.7569 | 92.7116
2022-09-08 01:50 | 4:00 | 17.9241 | 18.3743 | 20.7806 | 34.8202 | 34.349 | 34.104 | 34.9728 | 35.533 | 36.6953 | 37.3613 | 36.808 | 37.7942 | 34.4611 | 34.4368 | 34.5923 | 35.4677 | 35.6638 | 36.067 | 36.673 | 36.9346 | 21.417 | 17.6144 | 92.439 | 33.2859 | 33.4299 | 35.2826 | 33.8227 | 33.4248 | 33.8019 | 35.1268 | 34.5658 | 34.396 | 37.3239 | 36.3502 | 33.8048 | 34.5221 | 36.3651 | 36.718 | 37.5572 | 36.3807 | 33.8182 | 32.9546 | 34.6741 | 35.1333 | 33.1763 | 34.4239 | 34.3594 | 34.4568 | 34.3916 | 34.4706 | 34.4064 | 34.011 | 34.3857 | 35.6209 | 35.4705 | 35.9616 | 35.9074 | 33.7894 | 92.7401 | 92.8933 | 92.8455
2022-09-08 01:51 | 4:01 | 17.9007 | 18.3505 | 20.762 | 34.7404 | 34.3421 | 34.0892 | 34.9533 | 35.532 | 36.6693 | 37.3588 | 36.8091 | 37.7898 | 34.4674 | 34.4566 | 34.5664 | 35.4754 | 35.6549 | 36.0719 | 36.6562 | 36.917 | 21.363 | 17.5883 | 92.5091 | 33.3646 | 33.4173 | 35.2807 | 33.8278 | 33.4339 | 33.8046 | 35.142 | 34.5843 | 34.3807 | 37.3201 | 36.3615 | 33.7881 | 34.5122 | 36.3444 | 36.6868 | 37.5322 | 36.3704 | 33.7943 | 32.9604 | 34.6753 | 35.1525 | 33.1417 | 34.4084 | 34.3448 | 34.4473 | 34.3824 | 34.4778 | 34.4028 | 34.0031 | 34.3916 | 35.6063 | 35.4515 | 35.9518 | 35.9338 | 33.7962 | 92.8565 | 93.0378 | 92.885
2022-09-08 01:51 | 4:01 | 17.8146 | 18.3061 | 20.7183 | 34.6701 | 34.34 | 34.0939 | 34.9548 | 35.5314 | 36.6886 | 37.3488 | 36.8064 | 37.7699 | 34.4669 | 34.4528 | 34.5773 | 35.4829 | 35.6516 | 36.092 | 36.6559 | 36.9156 | 21.3217 | 17.5499 | 92.6388 | 33.211 | 33.4417 | 35.285 | 33.8246 | 33.4185 | 33.813 | 35.1295 | 34.5716 | 34.3679 | 37.34 | 36.3474 | 33.802 | 34.5167 | 36.3502 | 36.701 | 37.5472 | 36.3649 | 33.7929 | 32.9478 | 34.6784 | 35.14 | 33.1532 | 34.4261 | 34.3777 | 34.4623 | 34.4062 | 34.453 | 34.4004 | 34.0019 | 34.3824 | 35.6287 | 35.4427 | 35.9464 | 35.9212 | 33.7924 | 92.9753 | 93.1826 | 92.9911
2022-09-08 01:51 | 4:01 | 17.7806 | 18.2641 | 20.7021 | 34.7312 | 34.3432 | 34.1007 | 34.9413 | 35.5258 | 36.6734 | 37.3402 | 36.8015 | 37.7735 | 34.4645 | 34.4496 | 34.572 | 35.4841 | 35.6486 | 36.0446 | 36.6421 | 36.9059 | 21.2883 | 17.5093 | 92.6545 | 33.265 | 33.4261 | 35.2716 | 33.8035 | 33.4128 | 33.8007 | 35.137 | 34.5563 | 34.3953 | 37.3366 | 36.3254 | 33.7882 | 34.5089 | 36.3615 | 36.7061 | 37.5428 | 36.3651 | 33.793 | 32.926 | 34.6762 | 35.1398 | 33.1595 | 34.4365 | 34.367 | 34.4505 | 34.3742 | 34.4804 | 34.3999 | 34.0174 | 34.4062 | 35.6136 | 35.4451 | 35.9541 | 35.9263 | 33.7828 | 93.1606 | 93.3605 | 93.1763
2022-09-08 01:51 | 4:01 | 17.8274 | 18.3063 | 20.6255 | 34.7481 | 34.3653 | 34.0994 | 34.9441 | 35.5462 | 36.6822 | 37.354 | 36.8066 | 37.8023 | 34.4557 | 34.4403 | 34.5599 | 35.4784 | 35.6498 | 36.0572 | 36.6292 | 36.9194 | 21.2527 | 17.5342 | 92.6752 | 33.1324 | 33.428 | 35.2583 | 33.8182 | 33.408 | 33.8048 | 35.1429 | 34.5732 | 34.384 | 37.3391 | 36.3485 | 33.8093 | 34.5114 | 36.3474 | 36.703 | 37.5401 | 36.3444 | 33.7727 | 32.9359 | 34.668 | 35.1274 | 33.1331 | 34.4316 | 34.3611 | 34.4601 | 34.372 | 34.4565 | 34.4069 | 34.0051 | 34.3742 | 35.5937 | 35.4463 | 35.9698 | 35.9017 | 33.7851 | 93.3178 | 93.5425 | 93.2819
2022-09-08 01:51 | 4:01 | 17.7632 | 18.2184 | 20.6179 | 34.8013 | 34.3685 | 34.0793 | 34.944 | 35.5368 | 36.677 | 37.3307 | 36.8128 | 37.7831 | 34.453 | 34.4414 | 34.5595 | 35.4568 | 35.6383 | 36.0609 | 36.65 | 36.9229 | 21.2246 | 17.4225 | 92.7141 | 33.25 | 33.4397 | 35.2657 | 33.7943 | 33.4133 | 33.7881 | 35.1041 | 34.5563 | 34.3806 | 37.356 | 36.3352 | 33.7905 | 34.5083 | 36.3254 | 36.6988 | 37.5563 | 36.3502 | 33.8009 | 32.9277 | 34.647 | 35.122 | 33.136 | 34.4185 | 34.3637 | 34.4486 | 34.3765 | 34.4695 | 34.4079 | 33.996 | 34.372 | 35.5999 | 35.4518 | 35.9492 | 35.9066 | 33.7856 | 93.4756 | 93.7225 | 93.3981
2022-09-08 01:51 | 4:01 | 17.735 | 18.1561 | 20.6076 | 34.7017 | 34.3612 | 34.0981 | 34.9236 | 35.5322 | 36.6844 | 37.3466 | 36.8102 | 37.7733 | 34.4808 | 34.4326 | 34.5387 | 35.4635 | 35.6276 | 36.0445 | 36.6541 | 36.9088 | 21.1617 | 17.4422 | 92.8276 | 33.2264 | 33.4135 | 35.2743 | 33.7929 | 33.4094 | 33.802 | 35.1401 | 34.5612 | 34.3834 | 37.319 | 36.3327 | 33.782 | 34.5133 | 36.3485 | 36.6907 | 37.533 | 36.3615 | 33.805 | 32.9229 | 34.6382 | 35.1104 | 33.125 | 34.4278 | 34.3526 | 34.4761 | 34.3802 | 34.4558 | 34.414 | 34.004 | 34.3765 | 35.6228 | 35.4622 | 35.9682 | 35.9177 | 33.7785 | 93.5947 | 93.9124 | 93.4693
2022-09-08 01:52 | 4:01 | 17.7157 | 18.1008 | 20.5329 | 34.6875 | 34.3607 | 34.0847 | 34.936 | 35.5252 | 36.6772 | 37.3406 | 36.7761 | 37.7802 | 34.4654 | 34.458 | 34.5615 | 35.4756 | 35.6265 | 36.0609 | 36.6458 | 36.9213 | 21.1652 | 17.4608 | 92.8733 | 33.1913 | 33.4143 | 35.2627 | 33.793 | 33.3931 | 33.7882 | 35.1435 | 34.5585 | 34.3717 | 37.3343 | 36.3374 | 33.7814 | 34.5083 | 36.3352 | 36.6805 | 37.5294 | 36.3474 | 33.7812 | 32.9187 | 34.6356 | 35.1376 | 33.1201 | 34.4263 | 34.3495 | 34.4657 | 34.3848 | 34.4459 | 34.4321 | 34.0182 | 34.3802 | 35.6101 | 35.4411 | 35.9675 | 35.9228 | 33.7849 | 93.7431 | 94.0597 | 93.5522
2022-09-08 01:52 | 4:02 | 17.7265 | 18.14 | 20.492 | 34.6616 | 34.3558 | 34.0697 | 34.9312 | 35.5402 | 36.6747 | 37.3525 | 36.7988 | 37.7876 | 34.4572 | 34.4617 | 34.5373 | 35.4511 | 35.6267 | 36.0503 | 36.6354 | 36.9063 | 21.1505 | 17.3712 | 92.9638 | 33.2326 | 33.4099 | 35.2615 | 33.7727 | 33.3939 | 33.8093 | 35.1352 | 34.5535 | 34.3659 | 37.3181 | 36.3447 | 33.7977 | 34.5184 | 36.3327 | 36.6909 | 37.5398 | 36.3254 | 33.7809 | 32.9071 | 34.6465 | 35.1282 | 33.0855 | 34.4305 | 34.3526 | 34.469 | 34.3537 | 34.4397 | 34.4082 | 33.9996 | 34.3848 | 35.6172 | 35.4461 | 35.942 | 35.9285 | 33.7843 | 93.8829 | 94.2256 | 93.6223
2022-09-08 01:52 | 4:02 | 17.6379 | 18.0575 | 20.4658 | 34.7197 | 34.3766 | 34.0893 | 34.9257 | 35.5207 | 36.678 | 37.3336 | 36.7904 | 37.77 | 34.4861 | 34.4287 | 34.5536 | 35.4301 | 35.6416 | 36.0353 | 36.637 | 36.9108 | 21.1095 | 17.3627 | 93.095 | 33.1752 | 33.4162 | 35.2531 | 33.8009 | 33.3947 | 33.7905 | 35.1151 | 34.5466 | 34.3589 | 37.3298 | 36.3218 | 33.7824 | 34.5169 | 36.3374 | 36.6838 | 37.547 | 36.3485 | 33.784 | 32.9097 | 34.6475 | 35.1178 | 33.1043 | 34.4318 | 34.3604 | 34.4839 | 34.3558 | 34.4423 | 34.4182 | 34.0016 | 34.3537 | 35.5951 | 35.43 | 35.9694 | 35.9126 | 33.7757 | 94.0144 | 94.3589 | 93.7516
2022-09-08 01:52 | 4:02 | 17.5958 | 18.0587 | 20.4284 | 34.6869 | 34.3529 | 34.0832 | 34.9201 | 35.5251 | 36.6671 | 37.3334 | 36.7825 | 37.7727 | 34.4672 | 34.4475 | 34.5342 | 35.4324 | 35.6151 | 36.0455 | 36.6374 | 36.9229 | 21.1089 | 17.3679 | 93.0868 | 33.2072 | 33.4353 | 35.266 | 33.805 | 33.4089 | 33.782 | 35.138 | 34.5537 | 34.3732 | 37.3069 | 36.3144 | 33.7886 | 34.5161 | 36.3447 | 36.7118 | 37.5374 | 36.3352 | 33.7911 | 32.8917 | 34.6335 | 35.1175 | 33.0941 | 34.438 | 34.3449 | 34.4885 | 34.3596 | 34.443 | 34.4147 | 33.9833 | 34.3558 | 35.6131 | 35.4452 | 35.9595 | 35.9105 | 33.7781 | 94.1412 | 94.5672 | 93.9086
2022-09-08 01:52 | 4:02 | 17.5924 | 18.0502 | 20.4579 | 34.6313 | 34.3656 | 34.0794 | 34.9285 | 35.5136 | 36.6657 | 37.3287 | 36.7925 | 37.7795 | 34.4714 | 34.4374 | 34.5527 | 35.4476 | 35.6276 | 36.0636 | 36.6314 | 36.9207 | 21.0676 | 17.3094 | 93.1962 | 33.1027 | 33.4107 | 35.255 | 33.7812 | 33.406 | 33.7814 | 35.1333 | 34.5513 | 34.3674 | 37.317 | 36.3094 | 33.7925 | 34.5044 | 36.3218 | 36.6972 | 37.533 | 36.3327 | 33.7777 | 32.9132 | 34.6151 | 35.0626 | 33.0815 | 34.4235 | 34.3454 | 34.4627 | 34.3644 | 34.4518 | 34.4103 | 33.9901 | 34.3596 | 35.6065 | 35.4345 | 35.9592 | 35.9253 | 33.7754 | 94.4053 | 94.7942 | 94.0282
2022-09-08 01:52 | 4:02 | 17.5334 | 17.9558 | 20.3777 | 34.6838 | 34.3706 | 34.0679 | 34.9122 | 35.5326 | 36.6724 | 37.3342 | 36.7877 | 37.7679 | 34.4702 | 34.4538 | 34.527 | 35.4287 | 35.6146 | 36.0426 | 36.626 | 36.9131 | 21.0207 | 17.2878 | 93.3367 | 32.9369 | 33.4088 | 35.2366 | 33.7809 | 33.3837 | 33.7977 | 35.1363 | 34.5398 | 34.3621 | 37.3197 | 36.3298 | 33.7816 | 34.5006 | 36.3144 | 36.6885 | 37.522 | 36.3374 | 33.7713 | 32.8799 | 34.6281 | 35.1008 | 33.0806 | 34.4273 | 34.3481 | 34.4792 | 34.3478 | 34.437 | 34.4113 | 33.9935 | 34.3644 | 35.5936 | 35.4468 | 35.9507 | 35.9012 | 33.7564 | 94.559 | 95.005 | 94.2154
2022-09-08 01:53 | 4:03 | 17.5307 | 17.9432 | 20.3261 | 34.7034 | 34.3792 | 34.0775 | 34.9123 | 35.5229 | 36.6835 | 37.363 | 36.796 | 37.7742 | 34.468 | 34.4558 | 34.5448 | 35.4355 | 35.6086 | 36.0323 | 36.6302 | 36.9412 | 20.9976 | 17.2701 | 93.4439 | 33.0289 | 33.4203 | 35.2451 | 33.784 | 33.3789 | 33.7824 | 35.123 | 34.5674 | 34.3604 | 37.3343 | 36.3383 | 33.786 | 34.4899 | 36.3094 | 36.6987 | 37.534 | 36.3447 | 33.7614 | 32.874 | 34.6039 | 35.0913 | 33.0773 | 34.4287 | 34.37 | 34.484 | 34.3682 | 34.4467 | 34.4163 | 33.9892 | 34.3478 | 35.6124 | 35.4305 | 35.9682 | 35.9281 | 33.7687 | 94.6748 | 95.1583 | 94.1946
2022-09-08 01:53 | 4:03 | 17.533 | 17.9465 | 20.3361 | 34.7202 | 34.3865 | 34.08 | 34.93 | 35.52 | 36.6725 | 37.3444 | 36.7929 | 37.7676 | 34.4695 | 34.4425 | 34.5328 | 35.427 | 35.6309 | 36.0353 | 36.638 | 36.9334 | 20.9655 | 17.243 | 93.5259 | 33.0064 | 33.4067 | 35.2465 | 33.7911 | 33.3993 | 33.7886 | 35.1265 | 34.5523 | 34.3591 | 37.3139 | 36.3104 | 33.7822 | 34.5073 | 36.3298 | 36.7066 | 37.529 | 36.3218 | 33.7929 | 32.8868 | 34.5978 | 35.1029 | 33.0756 | 34.4297 | 34.3598 | 34.4718 | 34.3529 | 34.429 | 34.4302 | 33.9694 | 34.3682 | 35.5982 | 35.4358 | 35.9688 | 35.9318 | 33.7684 | 94.7901 | 95.2997 | 94.312
2022-09-08 01:53 | 4:03 | 17.4832 | 17.9041 | 20.2972 | 34.4817 | 34.3806 | 34.054 | 34.9174 | 35.52 | 36.6674 | 37.3497 | 36.791 | 37.7862 | 34.4764 | 34.4436 | 34.5403 | 35.4288 | 35.605 | 36.0381 | 36.6195 | 36.9055 | 20.9171 | 17.2281 | 93.5598 | 33.1234 | 33.3951 | 35.2332 | 33.7777 | 33.383 | 33.7925 | 35.1203 | 34.5417 | 34.3701 | 37.3387 | 36.3248 | 33.7873 | 34.5048 | 36.3383 | 36.6959 | 37.5266 | 36.3144 | 33.7739 | 32.8642 | 34.6147 | 35.0774 | 33.0744 | 34.4286 | 34.3728 | 34.4673 | 34.3551 | 34.4404 | 34.4363 | 33.9831 | 34.3529 | 35.5941 | 35.4253 | 35.9709 | 35.9255 | 33.7483 | 94.9751 | 95.4452 | 94.4434
2022-09-08 01:53 | 4:03 | 17.4771 | 17.9014 | 20.268 | 34.6343 | 34.3863 | 34.0803 | 34.9171 | 35.5359 | 36.6654 | 37.3369 | 36.7903 | 37.7695 | 34.4903 | 34.435 | 34.5367 | 35.42 | 35.6198 | 36.0366 | 36.6231 | 36.9166 | 20.9276 | 17.2349 | 93.6711 | 33.1124 | 33.4044 | 35.2351 | 33.7713 | 33.4043 | 33.7816 | 35.1301 | 34.5564 | 34.3612 | 37.3071 | 36.3199 | 33.7758 | 34.4957 | 36.3104 | 36.6922 | 37.5137 | 36.3094 | 33.7792 | 32.8517 | 34.6009 | 35.0753 | 33.0284 | 34.4217 | 34.3541 | 34.5022 | 34.3425 | 34.4295 | 34.4237 | 33.9625 | 34.3551 | 35.6078 | 35.4397 | 35.965 | 35.9215 | 33.775 | 95.1476 | 95.5945 | 94.5313
2022-09-08 01:53 | 4:03 | 17.4817 | 17.9248 | 20.2353 | 34.5318 | 34.392 | 34.0755 | 34.8956 | 35.5139 | 36.6581 | 37.3407 | 36.7849 | 37.7868 | 34.4759 | 34.4296 | 34.531 | 35.4306 | 35.5895 | 36.0366 | 36.5937 | 36.92 | 20.918 | 17.2106 | 93.4174 | 33.0185 | 33.3916 | 35.2468 | 33.7614 | 33.4067 | 33.786 | 35.1462 | 34.5459 | 34.3597 | 37.306 | 36.3153 | 33.7785 | 34.5036 | 36.3248 | 36.6876 | 37.5321 | 36.3298 | 33.7744 | 32.8742 | 34.5677 | 35.0671 | 33.0569 | 34.4325 | 34.3684 | 34.4804 | 34.3567 | 34.4351 | 34.4293 | 33.9808 | 34.3425 | 35.6164 | 35.4415 | 35.9801 | 35.9078 | 33.751 | 95.2829 | 95.713 | 94.5983
2022-09-08 01:53 | 4:03 | 17.433 | 17.8785 | 20.2304 | 34.637 | 34.3833 | 34.0738 | 34.916 | 35.5314 | 36.6669 | 37.3378 | 36.7903 | 37.7782 | 34.466 | 34.456 | 34.5377 | 35.4368 | 35.6214 | 36.0237 | 36.621 | 36.9172 | 20.9041 | 17.214 | 93.6582 | 33.2346 | 33.3997 | 35.2429 | 33.7929 | 33.3726 | 33.7822 | 35.1136 | 34.5389 | 34.364 | 37.3225 | 36.3266 | 33.779 | 34.5214 | 36.3199 | 36.7068 | 37.5176 | 36.3383 | 33.7739 | 32.8612 | 34.5973 | 35.0584 | 33.0544 | 34.4243 | 34.3537 | 34.4997 | 34.3457 | 34.4223 | 34.4425 | 33.9786 | 34.3567 | 35.6164 | 35.4232 | 35.9614 | 35.9115 | 33.7704 | 95.3936 | 95.7794 | 94.6607
2022-09-08 01:54 | 4:03 | 17.4004 | 17.8507 | 20.2467 | 34.4725 | 34.3823 | 34.0615 | 34.8982 | 35.5175 | 36.6623 | 37.3433 | 36.8105 | 37.7688 | 34.4876 | 34.4484 | 34.5217 | 35.4256 | 35.6052 | 36.0303 | 36.6265 | 36.8994 | 20.9115 | 17.1779 | 93.7472 | 33.1139 | 33.4143 | 35.2192 | 33.7739 | 33.3889 | 33.7873 | 35.1359 | 34.5391 | 34.354 | 37.3206 | 36.3156 | 33.7619 | 34.4922 | 36.3153 | 36.706 | 37.5225 | 36.3104 | 33.7663 | 32.8474 | 34.5714 | 35.0598 | 33.0544 | 34.4221 | 34.3535 | 34.4834 | 34.3453 | 34.4075 | 34.4411 | 33.9696 | 34.3457 | 35.5923 | 35.4465 | 35.9547 | 35.9316 | 33.7525 | 95.433 | 95.8465 | 94.7971
2022-09-08 01:54 | 4:04 | 17.3595 | 17.7796 | 20.1731 | 34.4848 | 34.4017 | 34.0841 | 34.9089 | 35.5222 | 36.6708 | 37.3446 | 36.7967 | 37.7659 | 34.484 | 34.4498 | 34.5117 | 35.4283 | 35.6056 | 36.0177 | 36.6281 | 36.9217 | 20.9101 | 17.1385 | 94.0172 | 32.9686 | 33.4129 | 35.2388 | 33.7792 | 33.3767 | 33.7758 | 35.1198 | 34.5339 | 34.3777 | 37.3162 | 36.3135 | 33.7694 | 34.4851 | 36.3266 | 36.6769 | 37.5215 | 36.3248 | 33.7687 | 32.8379 | 34.5614 | 35.0583 | 33.0256 | 34.4357 | 34.3607 | 34.5132 | 34.3452 | 34.4201 | 34.424 | 33.9766 | 34.3453 | 35.6082 | 35.4377 | 35.9488 | 35.8999 | 33.7599 | 95.3171 | 95.7775 | 94.763
2022-09-08 01:54 | 4:04 | 17.3917 | 17.8067 | 20.1518 | 34.6385 | 34.3862 | 34.0709 | 34.9219 | 35.5229 | 36.6707 | 37.3313 | 36.7979 | 37.7677 | 34.4972 | 34.4566 | 34.5233 | 35.403 | 35.6101 | 36.0112 | 36.6032 | 36.9001 | 20.8818 | 17.1103 | 93.9735 | 32.8576 | 33.3713 | 35.2209 | 33.7744 | 33.3834 | 33.7785 | 35.1241 | 34.5513 | 34.3453 | 37.3147 | 36.3122 | 33.7577 | 34.5041 | 36.3156 | 36.682 | 37.5221 | 36.3199 | 33.7463 | 32.8362 | 34.5674 | 35.0661 | 33.0481 | 34.442 | 34.36 | 34.4918 | 34.3377 | 34.4168 | 34.44 | 33.9574 | 34.3452 | 35.5954 | 35.4324 | 35.9703 | 35.9126 | 33.751 | 95.2229 | 95.6566 | 94.6515
2022-09-08 01:54 | 4:04 | 17.3482 | 17.7996 | 20.1419 | 34.5179 | 34.3773 | 34.068 | 34.9014 | 35.5103 | 36.6502 | 37.3168 | 36.7856 | 37.7706 | 34.4734 | 34.4573 | 34.5225 | 35.4115 | 35.5905 | 36.0137 | 36.6067 | 36.909 | 20.8839 | 17.1368 | 94.2016 | 33.0053 | 33.3823 | 35.2301 | 33.7739 | 33.3612 | 33.779 | 35.1264 | 34.5472 | 34.3531 | 37.3206 | 36.3299 | 33.7383 | 34.4887 | 36.3135 | 36.683 | 37.5175 | 36.3153 | 33.7579 | 32.8272 | 34.5661 | 35.066 | 33.0231 | 34.4356 | 34.3436 | 34.5001 | 34.3544 | 34.4184 | 34.4454 | 33.9608 | 34.3377 | 35.5996 | 35.4256 | 35.9715 | 35.9165 | 33.7219 | 94.9878 | 95.4346 | 94.4077
2022-09-08 01:54 | 4:04 | 17.3545 | 17.7843 | 20.119 | 34.6777 | 34.4033 | 34.0548 | 34.9173 | 35.5142 | 36.6669 | 37.3415 | 36.7844 | 37.7728 | 34.4966 | 34.4673 | 34.5131 | 35.4194 | 35.5904 | 35.9907 | 36.5884 | 36.9026 | 20.878 | 17.1059 | 94.1512 | 32.9761 | 33.3728 | 35.2264 | 33.7663 | 33.3807 | 33.7619 | 35.1046 | 34.5374 | 34.3509 | 37.2987 | 36.3167 | 33.7453 | 34.4895 | 36.3122 | 36.6827 | 37.4907 | 36.3266 | 33.756 | 32.8115 | 34.5676 | 35.0566 | 33.0158 | 34.4194 | 34.3616 | 34.4813 | 34.3551 | 34.4179 | 34.4384 | 33.9733 | 34.3544 | 35.5802 | 35.4236 | 35.9623 | 35.9188 | 33.7448 | 94.7795 | 95.1833 | 94.3015
2022-09-08 01:54 | 4:04 | 17.3636 | 17.8315 | 20.1051 | 34.5919 | 34.4073 | 34.0617 | 34.909 | 35.5042 | 36.6507 | 37.3238 | 36.7842 | 37.7612 | 34.4726 | 34.4607 | 34.5016 | 35.4107 | 35.5849 | 36.0246 | 36.5911 | 36.8898 | 20.895 | 17.1264 | 94.1563 | 32.8792 | 33.3723 | 35.2053 | 33.7687 | 33.3905 | 33.7694 | 35.1017 | 34.5379 | 34.3522 | 37.3154 | 36.3263 | 33.7818 | 34.5028 | 36.3299 | 36.6921 | 37.4953 | 36.3156 | 33.7559 | 32.8124 | 34.5584 | 35.0256 | 33.0293 | 34.4393 | 34.3513 | 34.5003 | 34.3407 | 34.3846 | 34.4509 | 33.9675 | 34.3551 | 35.6014 | 35.4532 | 35.9641 | 35.9063 | 33.711 | 94.6205 | 94.9455 | 94.1512
2022-09-08 01:55 | 4:05 | 17.3518 | 17.787 | 20.0761 | 34.5116 | 34.4149 | 34.0626 | 34.9059 | 35.4988 | 36.6472 | 37.3357 | 36.7873 | 37.7694 | 34.4718 | 34.4703 | 34.5157 | 35.4071 | 35.5722 | 35.9876 | 36.5874 | 36.9038 | 20.8702 | 17.1021 | 94.3867 | 32.9951 | 33.364 | 35.2345 | 33.7463 | 33.385 | 33.7577 | 35.1075 | 34.5312 | 34.3506 | 37.2938 | 36.3235 | 33.7553 | 34.4978 | 36.3167 | 36.6671 | 37.508 | 36.3135 | 33.7433 | 32.8204 | 34.5739 | 35.0265 | 33.0373 | 34.4234 | 34.3606 | 34.5073 | 34.3234 | 34.3978 | 34.4368 | 33.9694 | 34.3407 | 35.579 | 35.4175 | 35.9686 | 35.8921 | 33.7089 | 94.4863 | 94.7928 | 94.0883
2022-09-08 01:55 | 4:05 | 17.3739 | 17.7515 | 20.0454 | 34.5652 | 34.408 | 34.0638 | 34.9048 | 35.5169 | 36.6658 | 37.3238 | 36.7943 | 37.7849 | 34.4814 | 34.4463 | 34.4929 | 35.3801 | 35.5888 | 36.0073 | 36.58 | 36.8795 | 20.8705 | 17.0739 | 94.3796 | 33.0945 | 33.3728 | 35.2104 | 33.7579 | 33.367 | 33.7383 | 35.0939 | 34.5174 | 34.3401 | 37.3014 | 36.2996 | 33.7567 | 34.4842 | 36.3263 | 36.6897 | 37.4835 | 36.3122 | 33.7521 | 32.8087 | 34.5452 | 35.0378 | 33.0033 | 34.4298 | 34.3507 | 34.4845 | 34.3609 | 34.3915 | 34.4566 | 33.9616 | 34.3234 | 35.5936 | 35.4233 | 35.9646 | 35.9215 | 33.7261 | 94.4488 | 94.6588 | 94.1074
2022-09-08 01:55 | 4:05 | 17.263 | 17.6815 | 20.0416 | 34.4717 | 34.4058 | 34.0527 | 34.8939 | 35.519 | 36.6414 | 37.3345 | 36.7865 | 37.7717 | 34.4913 | 34.4606 | 34.4743 | 35.3756 | 35.5758 | 35.9931 | 36.5638 | 36.8854 | 20.8375 | 17.066 | 94.1605 | 32.9598 | 33.3594 | 35.2285 | 33.756 | 33.3597 | 33.7453 | 35.099 | 34.5236 | 34.3711 | 37.3179 | 36.3016 | 33.7534 | 34.4899 | 36.3235 | 36.6781 | 37.5143 | 36.3299 | 33.7403 | 32.815 | 34.5507 | 35.0139 | 33.0072 | 34.4169 | 34.36 | 34.524 | 34.3622 | 34.4027 | 34.4528 | 33.9518 | 34.3609 | 35.5898 | 35.4196 | 35.9579 | 35.9167 | 33.7248 | 94.3034 | 94.5832 | 93.8823
2022-09-08 01:55 | 4:05 | 17.2188 | 17.6711 | 19.9801 | 34.5356 | 34.4159 | 34.0458 | 34.8872 | 35.5398 | 36.6519 | 37.3227 | 36.779 | 37.7732 | 34.4938 | 34.4605 | 34.4831 | 35.3944 | 35.5587 | 35.9976 | 36.5681 | 36.8882 | 20.8508 | 17.0187 | 94.0406 | 32.9117 | 33.3531 | 35.2162 | 33.7559 | 33.3874 | 33.7818 | 35.0801 | 34.5181 | 34.3242 | 37.2963 | 36.3034 | 33.7398 | 34.4953 | 36.2996 | 36.6857 | 37.4837 | 36.3167 | 33.7296 | 32.8139 | 34.5317 | 35.0165 | 32.9932 | 34.4185 | 34.357 | 34.5103 | 34.3494 | 34.404 | 34.4496 | 33.9648 | 34.3622 | 35.5809 | 35.4235 | 35.974 | 35.9248 | 33.7038 | 94.1329 | 94.408 | 93.8559
2022-09-08 01:55 | 4:05 | 17.2741 | 17.7012 | 19.9944 | 34.4689 | 34.4064 | 34.066 | 34.8865 | 35.5028 | 36.6462 | 37.3165 | 36.7934 | 37.7541 | 34.4729 | 34.4524 | 34.4846 | 35.3752 | 35.5648 | 35.9908 | 36.5571 | 36.8706 | 20.841 | 16.9902 | 93.8095 | 32.9323 | 33.3473 | 35.2104 | 33.7433 | 33.3722 | 33.7553 | 35.1064 | 34.5317 | 34.3304 | 37.2929 | 36.2969 | 33.7505 | 34.497 | 36.3016 | 36.6823 | 37.4796 | 36.3263 | 33.7411 | 32.788 | 34.5156 | 35.0124 | 32.9928 | 34.4361 | 34.3604 | 34.5049 | 34.363 | 34.394 | 34.4403 | 33.9539 | 34.3494 | 35.5824 | 35.4245 | 35.9386 | 35.8845 | 33.6973 | 94.0162 | 94.3106 | 93.7028
2022-09-08 01:55 | 4:05 | 17.2324 | 17.6815 | 19.9637 | 34.3734 | 34.4028 | 34.0561 | 34.8864 | 35.5096 | 36.6402 | 37.3189 | 36.7816 | 37.762 | 34.4853 | 34.4588 | 34.4721 | 35.3705 | 35.5593 | 35.9886 | 36.5641 | 36.873 | 20.8616 | 16.9973 | 93.751 | 33.0772 | 33.3466 | 35.22 | 33.7521 | 33.3566 | 33.7567 | 35.0941 | 34.5311 | 34.3316 | 37.2997 | 36.3095 | 33.7441 | 34.488 | 36.3034 | 36.6487 | 37.491 | 36.3235 | 33.7182 | 32.7869 | 34.5225 | 35.0038 | 32.9698 | 34.4201 | 34.3585 | 34.4975 | 34.3474 | 34.3853 | 34.4414 | 33.9549 | 34.363 | 35.5686 | 35.4232 | 35.9618 | 35.9078 | 33.692 | 93.9837 | 94.2482 | 93.7687
2022-09-08 01:56 | 4:05 | 17.2474 | 17.6958 | 19.9457 | 34.4916 | 34.4004 | 34.0376 | 34.8858 | 35.4939 | 36.6412 | 37.3212 | 36.7778 | 37.7561 | 34.5006 | 34.4566 | 34.4823 | 35.3865 | 35.5689 | 35.9889 | 36.5493 | 36.8797 | 20.8705 | 16.9418 | 93.6794 | 32.7979 | 33.3652 | 35.2165 | 33.7403 | 33.3802 | 33.7534 | 35.0894 | 34.5275 | 34.3291 | 37.2929 | 36.3124 | 33.7284 | 34.4843 | 36.2969 | 36.678 | 37.4814 | 36.2996 | 33.7422 | 32.7574 | 34.5146 | 35.0085 | 32.9618 | 34.4205 | 34.3602 | 34.4876 | 34.3508 | 34.4028 | 34.4326 | 33.9655 | 34.3474 | 35.5746 | 35.4286 | 35.9535 | 35.9055 | 33.6754 | 93.946 | 94.1911 | 93.8002
2022-09-08 01:56 | 4:06 | 17.2126 | 17.66 | 19.9229 | 34.4042 | 34.3999 | 34.0397 | 34.8903 | 35.5126 | 36.6295 | 37.3205 | 36.7888 | 37.7515 | 34.4899 | 34.4531 | 34.4597 | 35.3735 | 35.5509 | 35.9755 | 36.551 | 36.858 | 20.919 | 16.9257 | 93.6396 | 32.958 | 33.3526 | 35.2219 | 33.7296 | 33.3745 | 33.7398 | 35.0793 | 34.5299 | 34.3462 | 37.3009 | 36.3051 | 33.7428 | 34.4978 | 36.3095 | 36.6661 | 37.472 | 36.3016 | 33.7389 | 32.7838 | 34.5009 | 34.9883 | 32.9703 | 34.4312 | 34.3558 | 34.5055 | 34.3715 | 34.3963 | 34.458 | 33.9506 | 34.3508 | 35.5665 | 35.4278 | 35.9662 | 35.9079 | 33.6703 | 93.8419 | 94.1011 | 93.6646
2022-09-08 01:56 | 4:06 | 17.2387 | 17.6379 | 19.8969 | 34.3907 | 34.4069 | 34.0533 | 34.8958 | 35.5084 | 36.6182 | 37.3121 | 36.7904 | 37.7697 | 34.4851 | 34.4613 | 34.4671 | 35.3754 | 35.5619 | 35.9742 | 36.5531 | 36.8538 | 20.9286 | 16.9472 | 93.5721 | 33.1545 | 33.3531 | 35.2266 | 33.7411 | 33.3603 | 33.7505 | 35.0775 | 34.5319 | 34.3303 | 37.2901 | 36.304 | 33.7354 | 34.5009 | 36.3124 | 36.6438 | 37.4661 | 36.3034 | 33.7299 | 32.7681 | 34.4996 | 34.9775 | 32.9628 | 34.4222 | 34.369 | 34.5152 | 34.3569 | 34.3786 | 34.4617 | 33.9664 | 34.3715 | 35.5572 | 35.4224 | 35.9812 | 35.9204 | 33.6789 | 93.794 | 94.0348 | 93.5636
2022-09-08 01:56 | 4:06 | 17.2222 | 17.6447 | 19.84 | 34.412 | 34.4079 | 34.0718 | 34.8824 | 35.4898 | 36.6391 | 37.3125 | 36.7947 | 37.7758 | 34.4887 | 34.4599 | 34.4727 | 35.3694 | 35.5659 | 35.9749 | 36.5715 | 36.8738 | 20.9436 | 16.9335 | 93.4554 | 32.9605 | 33.3454 | 35.1995 | 33.7182 | 33.3476 | 33.7441 | 35.0883 | 34.5411 | 34.3214 | 37.2892 | 36.2932 | 33.7225 | 34.4962 | 36.3051 | 36.6604 | 37.4883 | 36.2969 | 33.7322 | 32.7725 | 34.4875 | 34.9844 | 32.9615 | 34.4228 | 34.3595 | 34.511 | 34.3462 | 34.3816 | 34.4287 | 33.9219 | 34.3569 | 35.5653 | 35.4119 | 35.9563 | 35.9037 | 33.6805 | 93.7813 | 93.95 | 93.6462
2022-09-08 01:56 | 4:06 | 17.2538 | 17.6254 | 19.8669 | 34.4522 | 34.414 | 34.0581 | 34.8948 | 35.5118 | 36.6381 | 37.2931 | 36.7874 | 37.7739 | 34.4995 | 34.4566 | 34.4495 | 35.3511 | 35.5569 | 35.9763 | 36.5535 | 36.8626 | 20.9612 | 16.9251 | 93.45 | 32.8432 | 33.3367 | 35.2159 | 33.7422 | 33.3483 | 33.7284 | 35.0838 | 34.5418 | 34.3282 | 37.2787 | 36.3166 | 33.7301 | 34.4752 | 36.304 | 36.6644 | 37.4676 | 36.3095 | 33.7389 | 32.7652 | 34.481 | 34.9812 | 32.9673 | 34.4155 | 34.3511 | 34.4948 | 34.3559 | 34.3742 | 34.4475 | 33.9297 | 34.3462 | 35.5334 | 35.4259 | 35.9638 | 35.9196 | 33.6786 | 93.6876 | 93.8874 | 93.5927
2022-09-08 01:56 | 4:06 | 17.1525 | 17.5305 | 19.8301 | 34.3573 | 34.4321 | 34.0558 | 34.885 | 35.4992 | 36.6384 | 37.306 | 36.7957 | 37.7679 | 34.4841 | 34.4399 | 34.4605 | 35.3898 | 35.5562 | 35.9699 | 36.5425 | 36.8554 | 20.9839 | 16.9524 | 93.2319 | 32.8985 | 33.3317 | 35.201 | 33.7389 | 33.3503 | 33.7428 | 35.0829 | 34.5483 | 34.3324 | 37.2925 | 36.3053 | 33.7214 | 34.4994 | 36.2932 | 36.657 | 37.4633 | 36.3124 | 33.7332 | 32.7387 | 34.4995 | 34.9997 | 32.9544 | 34.4156 | 34.3678 | 34.5159 | 34.3773 | 34.369 | 34.4374 | 33.9274 | 34.3559 | 35.5549 | 35.4447 | 35.9807 | 35.8994 | 33.6824 | 93.6369 | 93.7841 | 93.6462
2022-09-08 01:57 | 4:07 | 17.1849 | 17.6022 | 19.8663 | 34.3985 | 34.4082 | 34.0517 | 34.8718 | 35.4818 | 36.6222 | 37.288 | 36.7824 | 37.77 | 34.4864 | 34.4585 | 34.4496 | 35.3752 | 35.5555 | 35.9618 | 36.5536 | 36.8484 | 20.9623 | 16.9084 | 93.3573 | 32.7948 | 33.338 | 35.186 | 33.7299 | 33.3626 | 33.7354 | 35.0735 | 34.5211 | 34.3297 | 37.2927 | 36.3142 | 33.7348 | 34.4777 | 36.3166 | 36.6842 | 37.4587 | 36.3051 | 33.735 | 32.7587 | 34.4988 | 34.9891 | 32.9731 | 34.4286 | 34.3485 | 34.5105 | 34.3603 | 34.3625 | 34.4538 | 33.9236 | 34.3773 | 35.5615 | 35.4143 | 35.9652 | 35.9007 | 33.6689 | 93.6042 | 93.6939 | 93.5229
2022-09-08 01:57 | 4:07 | 17.2019 | 17.5748 | 19.7939 | 34.4451 | 34.4182 | 34.0381 | 34.8645 | 35.5014 | 36.624 | 37.3126 | 36.793 | 37.7762 | 34.4901 | 34.4658 | 34.4404 | 35.3728 | 35.5581 | 35.9575 | 36.5482 | 36.8414 | 20.963 | 16.9493 | 93.2794 | 32.9089 | 33.3236 | 35.1981 | 33.7322 | 33.3651 | 33.7225 | 35.089 | 34.5292 | 34.3362 | 37.2784 | 36.3085 | 33.7463 | 34.4759 | 36.3053 | 36.6644 | 37.4603 | 36.304 | 33.731 | 32.7294 | 34.4971 | 34.9744 | 32.9695 | 34.4215 | 34.3715 | 34.5205 | 34.3519 | 34.3686 | 34.4558 | 33.9175 | 34.3603 | 35.5788 | 35.4215 | 35.9592 | 35.9112 | 33.6659 | 93.5735 | 93.6382 | 93.5148
2022-09-08 01:57 | 4:07 | 17.1213 | 17.5519 | 19.7973 | 34.3536 | 34.4147 | 34.0665 | 34.8831 | 35.4952 | 36.6386 | 37.2982 | 36.7906 | 37.7761 | 34.4906 | 34.4669 | 34.4638 | 35.3789 | 35.5418 | 35.957 | 36.5353 | 36.8453 | 20.9396 | 16.8705 | 93.1051 | 32.9669 | 33.3277 | 35.191 | 33.7389 | 33.3545 | 33.7301 | 35.092 | 34.5132 | 34.3485 | 37.2898 | 36.2964 | 33.7296 | 34.4877 | 36.3142 | 36.6641 | 37.4536 | 36.2932 | 33.7276 | 32.7252 | 34.4875 | 34.9727 | 32.9498 | 34.4055 | 34.3544 | 34.524 | 34.3494 | 34.3632 | 34.4425 | 33.9253 | 34.3519 | 35.5623 | 35.4255 | 35.9689 | 35.9106 | 33.6586 | 93.4532 | 93.5306 | 93.3939
2022-09-08 01:57 | 4:07 | 17.1903 | 17.5587 | 19.7938 | 34.4413 | 34.4103 | 34.0632 | 34.8634 | 35.4909 | 36.6317 | 37.2952 | 36.8041 | 37.7699 | 34.4638 | 34.4386 | 34.4515 | 35.3837 | 35.5469 | 35.9618 | 36.5566 | 36.8427 | 20.9123 | 16.9053 | 93.0889 | 32.9993 | 33.3285 | 35.2082 | 33.7332 | 33.3555 | 33.7214 | 35.09 | 34.5273 | 34.338 | 37.2904 | 36.3082 | 33.7224 | 34.5035 | 36.3085 | 36.6623 | 37.453 | 36.3166 | 33.7231 | 32.729 | 34.4924 | 34.968 | 32.9526 | 34.4186 | 34.3497 | 34.5166 | 34.3616 | 34.3732 | 34.4436 | 33.9134 | 34.3494 | 35.5582 | 35.4355 | 35.968 | 35.899 | 33.6787 | 93.3907 | 93.4768 | 93.3759
2022-09-08 01:57 | 4:07 | 17.1483 | 17.5747 | 19.7923 | 34.4205 | 34.4113 | 34.0605 | 34.8827 | 35.4921 | 36.6396 | 37.2798 | 36.8056 | 37.7745 | 34.4935 | 34.4348 | 34.4545 | 35.352 | 35.5496 | 35.9551 | 36.5376 | 36.8541 | 20.9334 | 16.8608 | 93.1614 | 32.9014 | 33.3272 | 35.2198 | 33.735 | 33.3492 | 33.7348 | 35.089 | 34.5291 | 34.312 | 37.2984 | 36.2913 | 33.7276 | 34.4842 | 36.2964 | 36.6439 | 37.4579 | 36.3053 | 33.7127 | 32.7315 | 34.4715 | 34.9729 | 32.9552 | 34.4088 | 34.3436 | 34.5186 | 34.3484 | 34.3588 | 34.435 | 33.935 | 34.3616 | 35.5525 | 35.4268 | 35.9882 | 35.8964 | 33.6708 | 93.3436 | 93.3925 | 93.3519
2022-09-08 01:57 | 4:07 | 17.1108 | 17.5355 | 19.78 | 34.4563 | 34.4163 | 34.062 | 34.8862 | 35.5087 | 36.6218 | 37.306 | 36.8157 | 37.7734 | 34.4833 | 34.4526 | 34.4326 | 35.3502 | 35.5413 | 35.9591 | 36.5293 | 36.8552 | 20.9235 | 16.8602 | 93.1942 | 32.7676 | 33.332 | 35.2077 | 33.731 | 33.3605 | 33.7463 | 35.0922 | 34.5542 | 34.3249 | 37.2963 | 36.305 | 33.719 | 34.4895 | 36.3082 | 36.6713 | 37.4625 | 36.3142 | 33.725 | 32.73 | 34.478 | 34.9602 | 32.9247 | 34.4159 | 34.3677 | 34.5311 | 34.3568 | 34.3777 | 34.4296 | 33.9223 | 34.3484 | 35.5694 | 35.4308 | 36.0024 | 35.9199 | 33.6637 | 93.2433 | 93.3875 | 93.2899
2022-09-08 01:58 | 4:08 | 17.1976 | 17.5456 | 19.7914 | 34.4345 | 34.4302 | 34.0457 | 34.8777 | 35.4929 | 36.6406 | 37.2852 | 36.8069 | 37.7913 | 34.4706 | 34.4639 | 34.4421 | 35.3597 | 35.5348 | 35.9567 | 36.5329 | 36.8541 | 20.9236 | 16.878 | 93.097 | 32.955 | 33.3137 | 35.2059 | 33.7276 | 33.3527 | 33.7296 | 35.0792 | 34.538 | 34.3385 | 37.2869 | 36.2949 | 33.7224 | 34.508 | 36.2913 | 36.6656 | 37.4413 | 36.3085 | 33.7135 | 32.7139 | 34.4605 | 34.9659 | 32.9361 | 34.4246 | 34.3647 | 34.529 | 34.3324 | 34.3644 | 34.456 | 33.9113 | 34.3568 | 35.5842 | 35.4101 | 35.9807 | 35.906 | 33.6634 | 93.1137 | 93.3199 | 93.2317
2022-09-08 01:58 | 4:08 | 17.1011 | 17.5312 | 19.8006 | 34.33 | 34.4363 | 34.0473 | 34.8606 | 35.5005 | 36.6262 | 37.2935 | 36.8077 | 37.8101 | 34.4778 | 34.4518 | 34.4514 | 35.3414 | 35.552 | 35.9722 | 36.5498 | 36.8487 | 20.9189 | 16.8842 | 93.0227 | 32.7466 | 33.3138 | 35.2184 | 33.7231 | 33.3529 | 33.7224 | 35.0793 | 34.5448 | 34.3366 | 37.2853 | 36.3025 | 33.7315 | 34.4929 | 36.305 | 36.6702 | 37.4538 | 36.2964 | 33.721 | 32.7263 | 34.4641 | 34.97 | 32.9137 | 34.4184 | 34.3769 | 34.515 | 34.3554 | 34.3685 | 34.4484 | 33.9272 | 34.3324 | 35.5723 | 35.4337 | 35.9753 | 35.9144 | 33.6712 | 93.057 | 93.1885 | 93.1628
2022-09-08 01:58 | 4:08 | 17.0177 | 17.4364 | 19.7253 | 34.4164 | 34.4237 | 34.0644 | 34.859 | 35.4939 | 36.6054 | 37.3157 | 36.8054 | 37.7845 | 34.453 | 34.4512 | 34.4455 | 35.3764 | 35.5549 | 35.9768 | 36.5424 | 36.8556 | 20.9121 | 16.8147 | 92.8941 | 32.8531 | 33.337 | 35.1917 | 33.7127 | 33.372 | 33.7276 | 35.0766 | 34.5533 | 34.3357 | 37.2957 | 36.2993 | 33.7402 | 34.513 | 36.2949 | 36.672 | 37.4618 | 36.3082 | 33.7251 | 32.6989 | 34.4512 | 34.9873 | 32.9102 | 34.4199 | 34.3774 | 34.5234 | 34.3674 | 34.3754 | 34.4498 | 33.9283 | 34.3554 | 35.5741 | 35.4347 | 35.9749 | 35.9207 | 33.6729 | 92.923 | 93.0501 | 93.106
2022-09-08 01:58 | 4:08 | 17.0846 | 17.4518 | 19.7178 | 34.2275 | 34.4293 | 34.0655 | 34.8777 | 35.5077 | 36.6244 | 37.2951 | 36.8103 | 37.7897 | 34.4804 | 34.4588 | 34.4406 | 35.3542 | 35.5313 | 35.9674 | 36.5506 | 36.8592 | 20.873 | 16.8128 | 92.8125 | 32.9806 | 33.3066 | 35.1949 | 33.725 | 33.3501 | 33.719 | 35.0726 | 34.5361 | 34.3279 | 37.3001 | 36.3007 | 33.7303 | 34.4892 | 36.3025 | 36.664 | 37.4565 | 36.2913 | 33.7214 | 32.7033 | 34.4693 | 34.971 | 32.921 | 34.4174 | 34.3715 | 34.5235 | 34.3575 | 34.3604 | 34.4566 | 33.919 | 34.3674 | 35.5756 | 35.4067 | 35.9699 | 35.9168 | 33.6438 | 92.8657 | 92.9614 | 93.0475
2022-09-08 01:58 | 4:08 | 17.0421 | 17.4385 | 19.6791 | 34.2692 | 34.4425 | 34.0508 | 34.8719 | 35.4888 | 36.6136 | 37.2842 | 36.8047 | 37.7956 | 34.4565 | 34.4357 | 34.436 | 35.3402 | 35.5415 | 35.9613 | 36.5299 | 36.8687 | 20.8742 | 16.8054 | 92.6549 | 32.8096 | 33.3117 | 35.1964 | 33.7135 | 33.3537 | 33.7224 | 35.0906 | 34.5519 | 34.3231 | 37.2818 | 36.3111 | 33.7282 | 34.5041 | 36.2993 | 36.6596 | 37.4534 | 36.305 | 33.7071 | 32.713 | 34.4615 | 34.9594 | 32.9209 | 34.4156 | 34.3838 | 34.5212 | 34.353 | 34.3679 | 34.4573 | 33.8943 | 34.3575 | 35.5651 | 35.4019 | 35.9806 | 35.8978 | 33.6795 | 92.716 | 92.7624 | 92.8898
2022-09-08 01:58 | 4:08 | 17.003 | 17.3922 | 19.6619 | 34.3813 | 34.4411 | 34.0401 | 34.8586 | 35.5133 | 36.6479 | 37.2971 | 36.8178 | 37.7991 | 34.4695 | 34.4351 | 34.4399 | 35.3327 | 35.5412 | 35.9665 | 36.5349 | 36.8484 | 20.8576 | 16.7676 | 92.5161 | 32.8392 | 33.3115 | 35.1971 | 33.721 | 33.3336 | 33.7315 | 35.0795 | 34.553 | 34.3455 | 37.2894 | 36.3 | 33.7115 | 34.5152 | 36.3007 | 36.6706 | 37.4539 | 36.2949 | 33.7092 | 32.7111 | 34.461 | 34.9528 | 32.9155 | 34.4161 | 34.3832 | 34.5264 | 34.3742 | 34.3635 | 34.4673 | 33.8957 | 34.353 | 35.5788 | 35.4186 | 35.9729 | 35.9098 | 33.6693 | 92.6093 | 92.6397 | 92.8425
2022-09-08 01:59 | 4:08 | 16.9981 | 17.4103 | 19.6293 | 34.3317 | 34.424 | 34.0386 | 34.8838 | 35.4663 | 36.6191 | 37.2956 | 36.8272 | 37.8008 | 34.4558 | 34.4514 | 34.4282 | 35.3472 | 35.5359 | 35.9819 | 36.5371 | 36.8586 | 20.819 | 16.7726 | 92.4897 | 32.6118 | 33.3139 | 35.199 | 33.7251 | 33.348 | 33.7402 | 35.0679 | 34.5473 | 34.3328 | 37.2998 | 36.2868 | 33.7217 | 34.5136 | 36.3111 | 36.6745 | 37.4712 | 36.3025 | 33.7061 | 32.6849 | 34.4539 | 34.9455 | 32.906 | 34.3989 | 34.3645 | 34.532 | 34.3594 | 34.3662 | 34.4607 | 33.9036 | 34.3742 | 35.5744 | 35.4021 | 35.9649 | 35.9156 | 33.657 | 92.5396 | 92.5549 | 92.7875
2022-09-08 01:59 | 4:09 | 16.9644 | 17.3864 | 19.5881 | 34.2518 | 34.44 | 34.0565 | 34.8732 | 35.5039 | 36.6476 | 37.2995 | 36.8272 | 37.7958 | 34.4459 | 34.4522 | 34.4483 | 35.3556 | 35.554 | 35.9595 | 36.5379 | 36.8577 | 20.8272 | 16.7633 | 92.49 | 32.858 | 33.3128 | 35.2024 | 33.7214 | 33.3308 | 33.7303 | 35.065 | 34.5415 | 34.3272 | 37.3153 | 36.2934 | 33.7112 | 34.4985 | 36.3 | 36.6694 | 37.443 | 36.2993 | 33.727 | 32.7118 | 34.4513 | 34.9666 | 32.8974 | 34.4235 | 34.396 | 34.5422 | 34.3448 | 34.3678 | 34.4703 | 33.9006 | 34.3594 | 35.5706 | 35.4168 | 35.9767 | 35.9223 | 33.6615 | 92.4476 | 92.4384 | 92.7506
2022-09-08 01:59 | 4:09 | 16.9677 | 17.3097 | 19.5912 | 34.2895 | 34.4454 | 34.0519 | 34.8665 | 35.4985 | 36.6254 | 37.3078 | 36.829 | 37.7938 | 34.4397 | 34.4491 | 34.4317 | 35.3491 | 35.5272 | 35.975 | 36.5403 | 36.863 | 20.8107 | 16.7276 | 92.3574 | 32.8402 | 33.2949 | 35.2127 | 33.7071 | 33.35 | 33.7282 | 35.0617 | 34.5594 | 34.3387 | 37.2963 | 36.2764 | 33.7101 | 34.5121 | 36.2868 | 36.6602 | 37.4523 | 36.3007 | 33.6969 | 32.6908 | 34.462 | 34.9672 | 32.892 | 34.3951 | 34.3882 | 34.5447 | 34.3777 | 34.3684 | 34.4463 | 33.9108 | 34.3448 | 35.5883 | 35.4039 | 35.9942 | 35.9172 | 33.6778 | 92.3264 | 92.3208 | 92.6806
2022-09-08 01:59 | 4:09 | 16.8703 | 17.2611 | 19.5705 | 34.4008 | 34.4384 | 34.05 | 34.874 | 35.5058 | 36.6093 | 37.2992 | 36.8162 | 37.8044 | 34.4423 | 34.4293 | 34.4379 | 35.3511 | 35.5409 | 35.9679 | 36.5374 | 36.8617 | 20.7849 | 16.6603 | 92.3912 | 32.8198 | 33.298 | 35.1828 | 33.7092 | 33.3241 | 33.7115 | 35.0817 | 34.5323 | 34.3433 | 37.3091 | 36.2924 | 33.7183 | 34.5118 | 36.2934 | 36.6736 | 37.459 | 36.3111 | 33.702 | 32.6935 | 34.4465 | 34.9897 | 32.8807 | 34.4199 | 34.3826 | 34.5512 | 34.367 | 34.3735 | 34.4606 | 33.8969 | 34.3777 | 35.5934 | 35.4164 | 35.9875 | 35.9171 | 33.6668 | 92.2805 | 92.2324 | 92.6096
2022-09-08 01:59 | 4:09 | 16.8895 | 17.2692 | 19.6017 | 34.2735 | 34.4509 | 34.0386 | 34.871 | 35.4844 | 36.6196 | 37.2805 | 36.8249 | 37.7999 | 34.443 | 34.4311 | 34.4464 | 35.3493 | 35.5343 | 35.9616 | 36.5321 | 36.865 | 20.7934 | 16.7074 | 92.2646 | 32.7266 | 33.3074 | 35.1953 | 33.7061 | 33.3551 | 33.7217 | 35.0766 | 34.5491 | 34.3166 | 37.2954 | 36.2902 | 33.7214 | 34.5166 | 36.2764 | 36.6709 | 37.4431 | 36.3 | 33.6965 | 32.6935 | 34.4582 | 34.9555 | 32.8937 | 34.4204 | 34.3866 | 34.5315 | 34.3611 | 34.3545 | 34.4605 | 33.9082 | 34.367 | 35.5975 | 35.3976 | 35.9739 | 35.9095 | 33.6811 | 92.0908 | 92.0923 | 92.4551
2022-09-08 01:59 | 4:09 | 16.9472 | 17.3409 | 19.5988 | 34.2702 | 34.4368 | 34.056 | 34.8612 | 35.4968 | 36.6141 | 37.2874 | 36.8345 | 37.816 | 34.4518 | 34.4192 | 34.4427 | 35.3343 | 35.5207 | 35.9607 | 36.5162 | 36.8671 | 20.7647 | 16.7089 | 92.1368 | 32.8719 | 33.3012 | 35.1951 | 33.727 | 33.3278 | 33.7112 | 35.0647 | 34.5503 | 34.3396 | 37.305 | 36.2785 | 33.7128 | 34.5123 | 36.2924 | 36.6863 | 37.4501 | 36.2868 | 33.7023 | 32.6792 | 34.4577 | 34.9491 | 32.8643 | 34.3865 | 34.3785 | 34.5338 | 34.3637 | 34.3578 | 34.4524 | 33.899 | 34.3611 | 35.5951 | 35.4085 | 35.9882 | 35.9195 | 33.6876 | 91.8738 | 91.9058 | 92.338
2022-09-08 02:00 | 4:10 | 16.9125 | 17.3176 | 19.604 | 34.3747 | 34.4566 | 34.0349 | 34.8592 | 35.5086 | 36.6316 | 37.3016 | 36.8291 | 37.8025 | 34.437 | 34.4235 | 34.4091 | 35.3342 | 35.52 | 35.9781 | 36.5341 | 36.8602 | 20.7684 | 16.7135 | 92.0596 | 32.9459 | 33.3128 | 35.1879 | 33.6969 | 33.3397 | 33.7101 | 35.0629 | 34.5633 | 34.3291 | 37.2998 | 36.3048 | 33.7138 | 34.505 | 36.2902 | 36.6753 | 37.461 | 36.2934 | 33.6932 | 32.678 | 34.4613 | 34.9729 | 32.8605 | 34.415 | 34.3945 | 34.5333 | 34.3526 | 34.3728 | 34.4588 | 33.8935 | 34.3637 | 35.5668 | 35.3973 | 35.9804 | 35.9077 | 33.66 | 91.7797 | 91.7805 | 92.3116
2022-09-08 02:00 | 4:10 | 16.8243 | 17.2528 | 19.5187 | 34.2945 | 34.4528 | 34.0417 | 34.873 | 35.5081 | 36.62 | 37.2988 | 36.8215 | 37.8149 | 34.4467 | 34.4295 | 34.4371 | 35.336 | 35.5477 | 35.9535 | 36.5399 | 36.8465 | 20.7413 | 16.6458 | 92.0207 | 32.8246 | 33.2989 | 35.1892 | 33.702 | 33.3465 | 33.7183 | 35.0703 | 34.5518 | 34.3419 | 37.2687 | 36.2762 | 33.7007 | 34.5008 | 36.2785 | 36.6629 | 37.4588 | 36.2764 | 33.6902 | 32.6807 | 34.4469 | 34.9719 | 32.8658 | 34.4065 | 34.3847 | 34.538 | 34.3495 | 34.3603 | 34.4566 | 33.8933 | 34.3526 | 35.5933 | 35.4081 | 35.9888 | 35.9159 | 33.6651 | 91.7223 | 91.7047 | 92.24
2022-09-08 02:00 | 4:10 | 16.7824 | 17.1274 | 19.4994 | 34.3701 | 34.4496 | 34.0444 | 34.8562 | 35.5012 | 36.6237 | 37.311 | 36.84 | 37.8124 | 34.429 | 34.4147 | 34.4212 | 35.3332 | 35.5129 | 35.9765 | 36.5281 | 36.8623 | 20.7464 | 16.6241 | 91.9936 | 32.9154 | 33.3121 | 35.1887 | 33.6965 | 33.3318 | 33.7214 | 35.0624 | 34.5383 | 34.3523 | 37.3001 | 36.2749 | 33.6951 | 34.5106 | 36.3048 | 36.659 | 37.4609 | 36.2924 | 33.6953 | 32.6844 | 34.4263 | 34.9496 | 32.8508 | 34.3895 | 34.397 | 34.5456 | 34.3526 | 34.3712 | 34.4531 | 33.8966 | 34.3495 | 35.6062 | 35.4012 | 35.9792 | 35.9016 | 33.6563 | 91.7182 | 91.7239 | 92.3143
2022-09-08 02:00 | 4:10 | 16.8364 | 17.1728 | 19.4688 | 34.2354 | 34.4403 | 34.0388 | 34.8708 | 35.4908 | 36.6091 | 37.3033 | 36.821 | 37.7839 | 34.4404 | 34.4111 | 34.4328 | 35.3429 | 35.5168 | 35.9638 | 36.5215 | 36.8779 | 20.7405 | 16.635 | 92.0061 | 32.7016 | 33.2993 | 35.1849 | 33.7023 | 33.3429 | 33.7128 | 35.0739 | 34.5455 | 34.3328 | 37.2895 | 36.2413 | 33.7158 | 34.4947 | 36.2762 | 36.6768 | 37.4457 | 36.2902 | 33.6828 | 32.6955 | 34.4627 | 34.9562 | 32.8312 | 34.3977 | 34.3948 | 34.5389 | 34.3604 | 34.3591 | 34.4613 | 33.8861 | 34.3526 | 35.6079 | 35.4072 | 35.9889 | 35.925 | 33.6555 | 91.7918 | 91.788 | 92.3451
2022-09-08 02:00 | 4:10 | 16.8591 | 17.2258 | 19.4796 | 34.2321 | 34.4414 | 34.0557 | 34.8466 | 35.4936 | 36.6328 | 37.301 | 36.8261 | 37.8012 | 34.4295 | 34.4196 | 34.4197 | 35.3186 | 35.5378 | 35.9485 | 36.5378 | 36.8435 | 20.7323 | 16.6514 | 92.1636 | 32.7211 | 33.2978 | 35.1896 | 33.6932 | 33.3431 | 33.7138 | 35.0684 | 34.5355 | 34.3294 | 37.2975 | 36.2674 | 33.7072 | 34.5028 | 36.2749 | 36.6796 | 37.4535 | 36.2785 | 33.6921 | 32.6681 | 34.4499 | 34.983 | 32.8289 | 34.3806 | 34.3973 | 34.558 | 34.3449 | 34.3628 | 34.4599 | 33.9042 | 34.3604 | 35.5844 | 35.3885 | 35.9924 | 35.9078 | 33.6606 | 91.9688 | 91.9348 | 92.4785
2022-09-08 02:00 | 4:10 | 16.821 | 17.1836 | 19.4851 | 34.2486 | 34.4326 | 34.0379 | 34.8483 | 35.488 | 36.6261 | 37.2951 | 36.8302 | 37.7956 | 34.4351 | 34.4169 | 34.4201 | 35.3488 | 35.5213 | 35.9658 | 36.5278 | 36.8643 | 20.7105 | 16.6498 | 92.1957 | 32.8418 | 33.3053 | 35.1648 | 33.6902 | 33.3283 | 33.7007 | 35.0625 | 34.543 | 34.3512 | 37.2889 | 36.2566 | 33.7027 | 34.5002 | 36.2413 | 36.6769 | 37.4427 | 36.3048 | 33.6878 | 32.6561 | 34.439 | 34.9493 | 32.8411 | 34.3956 | 34.3962 | 34.5571 | 34.3454 | 34.3625 | 34.4566 | 33.8928 | 34.3449 | 35.5948 | 35.3871 | 35.9952 | 35.9157 | 33.6654 | 92.0162 | 92.0004 | 92.4862
2022-09-08 02:01 | 4:10 | 16.8236 | 17.1603 | 19.4242 | 34.2048 | 34.458 | 34.0157 | 34.8518 | 35.4877 | 36.6231 | 37.3072 | 36.8156 | 37.8115 | 34.4223 | 34.4227 | 34.4204 | 35.3186 | 35.5198 | 35.9519 | 36.5314 | 36.8545 | 20.6888 | 16.581 | 92.194 | 32.7915 | 33.298 | 35.1658 | 33.6953 | 33.3394 | 33.6951 | 35.0746 | 34.5466 | 34.3209 | 37.2799 | 36.2629 | 33.6905 | 34.4862 | 36.2674 | 36.6559 | 37.4381 | 36.2762 | 33.6742 | 32.6673 | 34.4372 | 34.9417 | 32.7987 | 34.3714 | 34.4005 | 34.5525 | 34.3481 | 34.3835 | 34.4399 | 33.8761 | 34.3454 | 35.5899 | 35.3823 | 35.9954 | 35.9336 | 33.663 | 92.1669 | 92.1259 | 92.535
2022-09-08 02:01 | 4:11 | 16.8097 | 17.1432 | 19.436 | 34.1122 | 34.4617 | 34.0205 | 34.8585 | 35.4996 | 36.599 | 37.3081 | 36.8124 | 37.8071 | 34.4075 | 34.4045 | 34.419 | 35.3171 | 35.5178 | 35.9463 | 36.5256 | 36.8475 | 20.6398 | 16.5772 | 92.2931 | 32.659 | 33.315 | 35.1898 | 33.6828 | 33.3208 | 33.7158 | 35.071 | 34.541 | 34.3221 | 37.2918 | 36.2439 | 33.6987 | 34.4964 | 36.2566 | 36.6631 | 37.4507 | 36.2749 | 33.6542 | 32.6676 | 34.4228 | 34.9559 | 32.8279 | 34.3959 | 34.3961 | 34.5464 | 34.37 | 34.3499 | 34.4585 | 33.8932 | 34.3481 | 35.5978 | 35.3806 | 35.9799 | 35.94 | 33.6372 | 92.2322 | 92.2239 | 92.5801
2022-09-08 02:01 | 4:11 | 16.7707 | 17.1906 | 19.4931 | 34.2297 | 34.4287 | 34.0378 | 34.8505 | 35.4882 | 36.6049 | 37.2955 | 36.8106 | 37.7944 | 34.4201 | 34.4023 | 34.4246 | 35.3122 | 35.4918 | 35.9349 | 36.515 | 36.8524 | 20.6601 | 16.6905 | 92.3207 | 32.7236 | 33.2982 | 35.1855 | 33.6921 | 33.317 | 33.7072 | 35.0666 | 34.5375 | 34.325 | 37.2969 | 36.2557 | 33.6741 | 34.4985 | 36.2629 | 36.66 | 37.443 | 36.2413 | 33.6628 | 32.6579 | 34.4107 | 34.951 | 32.8052 | 34.3591 | 34.4038 | 34.5564 | 34.3598 | 34.3518 | 34.4658 | 33.8732 | 34.37 | 35.6069 | 35.3954 | 35.9811 | 35.9262 | 33.658 | 92.3514 | 92.2943 | 92.6458
2022-09-08 02:01 | 4:11 | 15.4153 | 16.6574 | 19.0061 | 34.1367 | 34.4475 | 34.0091 | 34.8363 | 35.4827 | 36.6048 | 37.3079 | 36.8043 | 37.8105 | 34.4168 | 34.4059 | 34.4239 | 35.3089 | 35.4973 | 35.9416 | 36.5135 | 36.8531 | 20.7925 | 17.2944 | 92.3792 | 32.9278 | 33.2829 | 35.1613 | 33.6878 | 33.296 | 33.7027 | 35.0604 | 34.547 | 34.3049 | 37.2866 | 36.2514 | 33.6846 | 34.4749 | 36.2439 | 36.6603 | 37.4617 | 36.2674 | 33.6624 | 32.643 | 34.4174 | 34.9571 | 32.7842 | 34.3593 | 34.3986 | 34.5572 | 34.3728 | 34.3533 | 34.4669 | 33.8789 | 34.3598 | 35.5829 | 35.3693 | 35.9953 | 35.925 | 33.6578 | 92.4018 | 92.4118 | 92.6956
2022-09-08 02:01 | 4:11 | 15.194 | 16.442 | 18.7253 | 34.0457 | 34.4374 | 34.0139 | 34.8304 | 35.499 | 36.6067 | 37.2973 | 36.8298 | 37.7998 | 34.4184 | 34.3945 | 34.4155 | 35.2817 | 35.4972 | 35.9445 | 36.5146 | 36.8525 | 21.2791 | 18.1506 | 92.4338 | 33.0582 | 33.2921 | 35.1597 | 33.6742 | 33.3241 | 33.6905 | 35.0374 | 34.5281 | 34.3156 | 37.2964 | 36.241 | 33.6718 | 34.4658 | 36.2557 | 36.6651 | 37.4311 | 36.2566 | 33.6609 | 32.6544 | 34.406 | 34.9326 | 32.7898 | 34.3825 | 34.3906 | 34.5596 | 34.3541 | 34.3676 | 34.4386 | 33.8689 | 34.3728 | 35.5987 | 35.3729 | 36.0033 | 35.9058 | 33.6649 | 92.4969 | 92.4515 | 92.768
2022-09-08 02:01 | 4:11 | 14.9011 | 16.2041 | 18.5173 | 34.0921 | 34.4538 | 34.0049 | 34.828 | 35.4868 | 36.6099 | 37.299 | 36.794 | 37.8019 | 34.4179 | 34.3932 | 34.4081 | 35.309 | 35.4916 | 35.9535 | 36.5155 | 36.8467 | 21.9713 | 19.2638 | 92.422 | 33.0408 | 33.2933 | 35.1601 | 33.6542 | 33.3082 | 33.6987 | 35.0565 | 34.5303 | 34.3163 | 37.2814 | 36.2527 | 33.6819 | 34.475 | 36.2514 | 36.6654 | 37.4333 | 36.2629 | 33.6426 | 32.6474 | 34.427 | 34.9305 | 32.7885 | 34.3662 | 34.4128 | 34.5483 | 34.3684 | 34.3614 | 34.4348 | 33.8631 | 34.3541 | 35.5936 | 35.3761 | 35.9872 | 35.9159 | 33.6247 | 92.6147 | 92.5598 | 92.8195
2022-09-08 02:02 | 4:12 | 14.5647 | 16.0059 | 18.2947 | 34.0456 | 34.4558 | 34.0104 | 34.8335 | 35.4688 | 36.5922 | 37.2788 | 36.8101 | 37.8092 | 34.3846 | 34.3857 | 34.4201 | 35.3016 | 35.4863 | 35.9444 | 36.511 | 36.8471 | 22.7597 | 20.4647 | 92.4683 | 33.1837 | 33.2863 | 35.1513 | 33.6628 | 33.3083 | 33.6741 | 35.0723 | 34.5268 | 34.3018 | 37.2859 | 36.2628 | 33.6872 | 34.4659 | 36.241 | 36.6529 | 37.4323 | 36.2439 | 33.6492 | 32.6304 | 34.4092 | 34.9355 | 32.7898 | 34.3616 | 34.416 | 34.5636 | 34.3537 | 34.3413 | 34.4526 | 33.8647 | 34.3684 | 35.5882 | 35.3796 | 35.981 | 35.9052 | 33.6326 | 92.7791 | 92.6989 | 92.857
2022-09-08 02:02 | 4:12 | 14.3929 | 15.8266 | 18.1106 | 33.9261 | 34.4425 | 34.0145 | 34.806 | 35.4763 | 36.6116 | 37.2999 | 36.823 | 37.8006 | 34.3978 | 34.3916 | 34.4033 | 35.3111 | 35.4878 | 35.9395 | 36.5223 | 36.8479 | 23.5865 | 21.6575 | 92.6133 | 33.2618 | 33.2771 | 35.1508 | 33.6624 | 33.3151 | 33.6846 | 35.0581 | 34.5168 | 34.2977 | 37.2728 | 36.246 | 33.6728 | 34.4849 | 36.2527 | 36.6544 | 37.4372 | 36.2557 | 33.6557 | 32.6367 | 34.4036 | 34.9195 | 32.79 | 34.3556 | 34.4246 | 34.568 | 34.3535 | 34.3613 | 34.4639 | 33.8643 | 34.3537 | 35.5972 | 35.4041 | 36.005 | 35.925 | 33.6605 | 92.8132 | 92.8206 | 92.9432
2022-09-08 02:02 | 4:12 | 14.171 | 15.7016 | 17.9114 | 33.9903 | 34.4436 | 34.0088 | 34.8064 | 35.4518 | 36.6033 | 37.2807 | 36.8064 | 37.8055 | 34.3915 | 34.3824 | 34.4024 | 35.3006 | 35.4694 | 35.9331 | 36.5243 | 36.8501 | 24.4157 | 22.7839 | 92.8095 | 33.3839 | 33.2712 | 35.1489 | 33.6609 | 33.3089 | 33.6718 | 35.0647 | 34.5144 | 34.303 | 37.2756 | 36.2512 | 33.6657 | 34.4674 | 36.2628 | 36.6602 | 37.4262 | 36.2514 | 33.6272 | 32.61 | 34.4115 | 34.9133 | 32.7986 | 34.3568 | 34.4275 | 34.5542 | 34.3607 | 34.3661 | 34.4518 | 33.8584 | 34.3535 | 35.5898 | 35.38 | 35.9901 | 35.9226 | 33.646 | 92.9668 | 92.9642 | 93.0628
2022-09-08 02:02 | 4:12 | 14.0294 | 15.5114 | 17.7922 | 33.9999 | 34.435 | 33.991 | 34.8099 | 35.471 | 36.591 | 37.2849 | 36.8117 | 37.7801 | 34.4027 | 34.4062 | 34.4133 | 35.3068 | 35.4709 | 35.9351 | 36.5234 | 36.852 | 25.1622 | 23.8127 | 92.7994 | 33.3182 | 33.3076 | 35.1368 | 33.6426 | 33.3235 | 33.6819 | 35.0644 | 34.5104 | 34.2917 | 37.2758 | 36.2556 | 33.6704 | 34.4669 | 36.246 | 36.668 | 37.432 | 36.241 | 33.6517 | 32.6116 | 34.41 | 34.9312 | 32.7965 | 34.3491 | 34.4067 | 34.5784 | 34.36 | 34.3659 | 34.4512 | 33.8628 | 34.3607 | 35.5828 | 35.3665 | 35.9893 | 35.9298 | 33.6482 | 93.0709 | 93.094 | 93.0741
2022-09-08 02:02 | 4:12 | 13.8914 | 15.3904 | 17.6599 | 33.865 | 34.4296 | 34.0036 | 34.7932 | 35.4639 | 36.5799 | 37.2913 | 36.8124 | 37.8007 | 34.404 | 34.3742 | 34.411 | 35.2846 | 35.4675 | 35.94 | 36.508 | 36.8382 | 25.8337 | 24.7012 | 92.8237 | 33.5659 | 33.2866 | 35.1493 | 33.6492 | 33.3135 | 33.6872 | 35.0557 | 34.5223 | 34.3125 | 37.2845 | 36.2405 | 33.6887 | 34.4837 | 36.2512 | 36.6453 | 37.435 | 36.2527 | 33.6462 | 32.6279 | 34.4115 | 34.9267 | 32.782 | 34.3578 | 34.4096 | 34.5839 | 34.3436 | 34.361 | 34.4588 | 33.8765 | 34.36 | 35.6002 | 35.3978 | 35.9736 | 35.934 | 33.6524 | 93.1373 | 93.1413 | 93.0789
2022-09-08 02:02 | 4:12 | 13.7956 | 15.2688 | 17.4964 | 33.9716 | 34.456 | 33.9904 | 34.8005 | 35.4648 | 36.6025 | 37.3011 | 36.7949 | 37.7876 | 34.394 | 34.372 | 34.401 | 35.2871 | 35.4809 | 35.9419 | 36.5197 | 36.8492 | 26.4649 | 25.4843 | 92.9102 | 33.5292 | 33.2981 | 35.1472 | 33.6557 | 33.3289 | 33.6728 | 35.0602 | 34.5277 | 34.2976 | 37.2772 | 36.2413 | 33.6759 | 34.4679 | 36.2556 | 36.6544 | 37.4335 | 36.2628 | 33.6455 | 32.6224 | 34.4089 | 34.9048 | 32.7869 | 34.3323 | 34.4138 | 34.5676 | 34.3616 | 34.3587 | 34.4357 | 33.847 | 34.3436 | 35.611 | 35.3793 | 36.0022 | 35.9171 | 33.6524 | 93.2878 | 93.2634 | 93.2031
2022-09-08 02:03 | 4:12 | 13.6486 | 15.1271 | 17.378 | 33.9796 | 34.4484 | 33.9813 | 34.8109 | 35.4778 | 36.6051 | 37.3018 | 36.8115 | 37.7823 | 34.3853 | 34.3765 | 34.3958 | 35.2863 | 35.4509 | 35.9271 | 36.5178 | 36.8486 | 27.0368 | 26.161 | 93.1285 | 33.5866 | 33.3021 | 35.149 | 33.6272 | 33.3297 | 33.6657 | 35.0677 | 34.5157 | 34.2943 | 37.2692 | 36.2458 | 33.6654 | 34.4747 | 36.2405 | 36.6502 | 37.4189 | 36.246 | 33.6477 | 32.6172 | 34.4027 | 34.9068 | 32.8088 | 34.3552 | 34.4143 | 34.5672 | 34.3513 | 34.3718 | 34.4351 | 33.8697 | 34.3616 | 35.5847 | 35.3823 | 35.9932 | 35.9308 | 33.642 | 93.5485 | 93.4172 | 93.4249
2022-09-08 02:03 | 4:13 | 13.5378 | 14.9979 | 17.2039 | 33.9845 | 34.4498 | 33.9753 | 34.7954 | 35.4486 | 36.5935 | 37.2908 | 36.7849 | 37.7782 | 34.4028 | 34.3802 | 34.3998 | 35.2823 | 35.4534 | 35.9264 | 36.5081 | 36.8493 | 27.5221 | 26.7441 | 93.325 | 33.6383 | 33.2981 | 35.1514 | 33.6517 | 33.3212 | 33.6704 | 35.0545 | 34.507 | 34.2908 | 37.2847 | 36.2643 | 33.6746 | 34.4678 | 36.2413 | 36.6725 | 37.4235 | 36.2512 | 33.6226 | 32.6102 | 34.424 | 34.9057 | 32.8008 | 34.3319 | 34.4023 | 34.5646 | 34.3606 | 34.3258 | 34.4514 | 33.8711 | 34.3513 | 35.5903 | 35.3869 | 35.9967 | 35.9187 | 33.6378 | 93.6363 | 93.5679 | 93.5
2022-09-08 02:03 | 4:13 | 13.4214 | 14.8602 | 17.1065 | 33.8133 | 34.4566 | 33.9904 | 34.7791 | 35.4576 | 36.5816 | 37.3035 | 36.8151 | 37.7874 | 34.3963 | 34.3848 | 34.4009 | 35.2846 | 35.4568 | 35.9087 | 36.5087 | 36.8518 | 27.9443 | 27.2403 | 93.1331 | 33.7058 | 33.3097 | 35.1257 | 33.6462 | 33.3113 | 33.6887 | 35.0566 | 34.517 | 34.2782 | 37.2787 | 36.2599 | 33.6677 | 34.4614 | 36.2458 | 36.6559 | 37.4477 | 36.2556 | 33.6227 | 32.6194 | 34.4279 | 34.9299 | 32.8142 | 34.3425 | 34.4117 | 34.5722 | 34.3507 | 34.368 | 34.4522 | 33.8662 | 34.3606 | 35.6092 | 35.3877 | 35.9952 | 35.9336 | 33.6461 | 93.8571 | 93.7135 | 93.5252
2022-09-08 02:03 | 4:13 | 13.2788 | 14.7704 | 17.0002 | 33.8491 | 34.4573 | 33.9908 | 34.7728 | 35.4452 | 36.5962 | 37.3006 | 36.8257 | 37.8009 | 34.3786 | 34.3537 | 34.3966 | 35.2918 | 35.4534 | 35.9366 | 36.5074 | 36.8472 | 28.3421 | 27.6972 | 93.2662 | 33.6998 | 33.3127 | 35.1571 | 33.6455 | 33.3408 | 33.6759 | 35.0527 | 34.5175 | 34.3035 | 37.2634 | 36.2491 | 33.6812 | 34.4589 | 36.2643 | 36.6542 | 37.4408 | 36.2405 | 33.632 | 32.6288 | 34.4184 | 34.9102 | 32.8066 | 34.3407 | 34.4269 | 34.5739 | 34.36 | 34.3634 | 34.4491 | 33.8694 | 34.3507 | 35.5992 | 35.3611 | 35.9879 | 35.9162 | 33.6486 | 93.9867 | 93.9017 | 93.604
2022-09-08 02:03 | 4:13 | 13.2252 | 14.6582 | 16.9504 | 33.9743 | 34.4673 | 33.9744 | 34.7623 | 35.4531 | 36.5856 | 37.2831 | 36.8151 | 37.8105 | 34.3816 | 34.3558 | 34.3897 | 35.2611 | 35.467 | 35.9026 | 36.508 | 36.8467 | 28.6668 | 28.0421 | 93.1855 | 33.6528 | 33.299 | 35.143 | 33.6477 | 33.3241 | 33.6654 | 35.0614 | 34.5128 | 34.2806 | 37.258 | 36.2309 | 33.6624 | 34.4631 | 36.2599 | 36.6571 | 37.4256 | 36.2413 | 33.6206 | 32.624 | 34.4056 | 34.9132 | 32.8354 | 34.3325 | 34.4253 | 34.5524 | 34.357 | 34.3498 | 34.4293 | 33.8613 | 34.36 | 35.5941 | 35.3558 | 35.987 | 35.9195 | 33.6455 | 94.1528 | 94.1003 | 93.671
2022-09-08 02:03 | 4:13 | 13.0911 | 14.5647 | 16.8447 | 33.7765 | 34.4607 | 33.95 | 34.7786 | 35.4508 | 36.5691 | 37.2872 | 36.7864 | 37.7829 | 34.3742 | 34.3596 | 34.3794 | 35.2787 | 35.4413 | 35.9206 | 36.4886 | 36.839 | 28.9406 | 28.3508 | 93.4657 | 33.7533 | 33.2951 | 35.1429 | 33.6226 | 33.3344 | 33.6746 | 35.0505 | 34.521 | 34.2971 | 37.2608 | 36.253 | 33.6805 | 34.4446 | 36.2491 | 36.6697 | 37.4342 | 36.2458 | 33.6238 | 32.6239 | 34.4345 | 34.9303 | 32.8183 | 34.334 | 34.4159 | 34.5728 | 34.3604 | 34.3538 | 34.4311 | 33.867 | 34.357 | 35.6093 | 35.3812 | 35.9903 | 35.9283 | 33.648 | 94.2691 | 94.2446 | 93.7784
2022-09-08 02:04 | 4:14 | 13.0141 | 14.431 | 16.7773 | 33.8306 | 34.4703 | 33.9766 | 34.7714 | 35.4419 | 36.59 | 37.2812 | 36.7863 | 37.7977 | 34.369 | 34.3644 | 34.3738 | 35.2814 | 35.4263 | 35.9029 | 36.5111 | 36.8557 | 29.1874 | 28.6302 | 93.5994 | 33.892 | 33.2961 | 35.1504 | 33.6227 | 33.3162 | 33.6677 | 35.046 | 34.4903 | 34.2831 | 37.2646 | 36.2267 | 33.6589 | 34.4301 | 36.2309 | 36.645 | 37.4229 | 36.2643 | 33.6105 | 32.6148 | 34.4108 | 34.9301 | 32.8262 | 34.3285 | 34.4239 | 34.58 | 34.3585 | 34.3479 | 34.4192 | 33.8711 | 34.3604 | 35.6102 | 35.3719 | 36.0039 | 35.9302 | 33.6378 | 94.4332 | 94.3484 | 93.9486
2022-09-08 02:04 | 4:14 | 12.9055 | 14.3463 | 16.7023 | 33.8946 | 34.4463 | 33.9782 | 34.7652 | 35.449 | 36.6079 | 37.2806 | 36.7915 | 37.8134 | 34.3625 | 34.3478 | 34.3777 | 35.2628 | 35.4469 | 35.9282 | 36.5107 | 36.8434 | 29.4157 | 28.8615 | 93.7118 | 33.8978 | 33.2931 | 35.1334 | 33.632 | 33.3265 | 33.6812 | 35.0525 | 34.5088 | 34.2889 | 37.2609 | 36.2308 | 33.6584 | 34.4489 | 36.253 | 36.6436 | 37.4119 | 36.2599 | 33.6285 | 32.6348 | 34.4583 | 34.9081 | 32.8367 | 34.3383 | 34.4084 | 34.5568 | 34.3602 | 34.3627 | 34.4235 | 33.8522 | 34.3585 | 35.6004 | 35.3814 | 36.0008 | 35.9228 | 33.628 | 94.5375 | 94.4858 | 94.0032
2022-09-08 02:04 | 4:14 | 12.799 | 14.2423 | 16.5646 | 33.7809 | 34.4606 | 33.9593 | 34.7488 | 35.4517 | 36.5695 | 37.262 | 36.7975 | 37.7886 | 34.3686 | 34.3682 | 34.3725 | 35.2723 | 35.4258 | 35.8892 | 36.507 | 36.8393 | 29.5999 | 29.0826 | 93.7963 | 33.8859 | 33.2943 | 35.1465 | 33.6206 | 33.3377 | 33.6624 | 35.0581 | 34.4924 | 34.2629 | 37.2673 | 36.2264 | 33.6756 | 34.4459 | 36.2267 | 36.6533 | 37.4183 | 36.2491 | 33.629 | 32.6259 | 34.4209 | 34.9125 | 32.8382 | 34.3337 | 34.4261 | 34.5423 | 34.3558 | 34.3617 | 34.4295 | 33.8463 | 34.3602 | 35.5901 | 35.399 | 35.9863 | 35.9186 | 33.634 | 94.6632 | 94.7036 | 94.1424
2022-09-08 02:04 | 4:14 | 12.7126 | 14.1411 | 16.4813 | 33.6871 | 34.4605 | 33.9593 | 34.7653 | 35.4447 | 36.5689 | 37.2788 | 36.8093 | 37.7946 | 34.3632 | 34.3529 | 34.3656 | 35.2811 | 35.4346 | 35.9006 | 36.5097 | 36.8307 | 29.751 | 29.2529 | 94.0181 | 33.959 | 33.2832 | 35.1376 | 33.6238 | 33.3445 | 33.6805 | 35.0529 | 34.5052 | 34.2883 | 37.2708 | 36.228 | 33.6669 | 34.4494 | 36.2308 | 36.6538 | 37.4152 | 36.2309 | 33.6094 | 32.6094 | 34.4178 | 34.9246 | 32.8424 | 34.323 | 34.4365 | 34.5566 | 34.369 | 34.3503 | 34.4147 | 33.8798 | 34.3558 | 35.5885 | 35.3727 | 36.0053 | 35.9362 | 33.6242 | 94.68 | 94.8738 | 94.1682
2022-09-08 02:04 | 4:14 | 12.5908 | 14.0387 | 16.4052 | 33.7094 | 34.4524 | 33.9536 | 34.7345 | 35.4381 | 36.5737 | 37.2708 | 36.7861 | 37.7784 | 34.3732 | 34.3551 | 34.365 | 35.2652 | 35.4268 | 35.8971 | 36.4851 | 36.8288 | 29.9093 | 29.415 | 94.0075 | 33.9457 | 33.2706 | 35.1497 | 33.6105 | 33.3448 | 33.6589 | 35.0689 | 34.507 | 34.2692 | 37.257 | 36.217 | 33.6615 | 34.4453 | 36.2264 | 36.6527 | 37.4194 | 36.253 | 33.6112 | 32.624 | 34.4287 | 34.8931 | 32.8378 | 34.3129 | 34.4316 | 34.5833 | 34.3595 | 34.3367 | 34.4111 | 33.8543 | 34.369 | 35.6093 | 35.3846 | 36.0082 | 35.9282 | 33.6322 | 94.8965 | 94.9191 | 94.2787
2022-09-08 02:04 | 4:14 | 12.5873 | 13.9747 | 16.2972 | 33.7408 | 34.4588 | 33.9432 | 34.7282 | 35.4365 | 36.5785 | 37.2681 | 36.7939 | 37.7848 | 34.3588 | 34.3425 | 34.3689 | 35.2775 | 35.4168 | 35.9125 | 36.4893 | 36.8081 | 30.041 | 29.572 | 93.9078 | 33.9853 | 33.2916 | 35.1426 | 33.6285 | 33.3441 | 33.6584 | 35.0503 | 34.5175 | 34.2718 | 37.2517 | 36.2331 | 33.6604 | 34.4268 | 36.228 | 36.6318 | 37.4252 | 36.2267 | 33.6091 | 32.627 | 34.4354 | 34.883 | 32.8401 | 34.3253 | 34.4185 | 34.5597 | 34.3511 | 34.3436 | 34.4196 | 33.8517 | 34.3595 | 35.6021 | 35.3821 | 35.9867 | 35.9365 | 33.6281 | 94.9375 | 95.0359 | 94.3061
2022-09-08 02:05 | 4:14 | 12.4263 | 13.8501 | 16.1994 | 33.6795 | 34.4566 | 33.9505 | 34.7432 | 35.4294 | 36.5761 | 37.2523 | 36.7978 | 37.796 | 34.3777 | 34.3567 | 34.3526 | 35.2404 | 35.4023 | 35.8881 | 36.4823 | 36.7962 | 30.1613 | 29.6881 | 93.9755 | 34.0824 | 33.2848 | 35.1335 | 33.629 | 33.3473 | 33.6756 | 35.0481 | 34.5007 | 34.2741 | 37.265 | 36.2167 | 33.6507 | 34.4382 | 36.217 | 36.642 | 37.4117 | 36.2308 | 33.6211 | 32.6194 | 34.4324 | 34.9082 | 32.8536 | 34.3222 | 34.4278 | 34.5408 | 34.3678 | 34.3611 | 34.4169 | 33.8644 | 34.3511 | 35.5921 | 35.3775 | 36.0045 | 35.9256 | 33.6117 | 94.9277 | 94.9754 | 94.2597
2022-09-08 02:05 | 4:15 | 12.3435 | 13.7534 | 16.1432 | 33.5641 | 34.4531 | 33.9477 | 34.725 | 35.4257 | 36.5682 | 37.2658 | 36.795 | 37.772 | 34.3644 | 34.3457 | 34.3556 | 35.2408 | 35.4158 | 35.8888 | 36.4718 | 36.7946 | 30.2748 | 29.7974 | 94.016 | 34.0818 | 33.2946 | 35.1282 | 33.6094 | 33.3247 | 33.6669 | 35.0501 | 34.4922 | 34.2654 | 37.2566 | 36.2093 | 33.6431 | 34.4376 | 36.2331 | 36.6268 | 37.416 | 36.2264 | 33.6097 | 32.6339 | 34.4261 | 34.9085 | 32.8609 | 34.3077 | 34.4263 | 34.5539 | 34.3485 | 34.364 | 34.4227 | 33.8712 | 34.3678 | 35.589 | 35.3941 | 35.9963 | 35.9076 | 33.621 | 94.7917 | 94.9249 | 94.2057
2022-09-08 02:05 | 4:15 | 12.2668 | 13.6486 | 16.0162 | 33.7121 | 34.4613 | 33.9395 | 34.726 | 35.4385 | 36.5808 | 37.2566 | 36.8049 | 37.7841 | 34.3685 | 34.3453 | 34.3517 | 35.2372 | 35.4149 | 35.8843 | 36.4738 | 36.8155 | 30.3446 | 29.9141 | 93.9355 | 34.12 | 33.2676 | 35.125 | 33.6112 | 33.3405 | 33.6615 | 35.0512 | 34.5074 | 34.2838 | 37.2377 | 36.2468 | 33.6497 | 34.4263 | 36.2167 | 36.6205 | 37.3961 | 36.228 | 33.6101 | 32.6166 | 34.4408 | 34.9151 | 32.8707 | 34.3097 | 34.4305 | 34.5292 | 34.3715 | 34.3409 | 34.4045 | 33.8628 | 34.3485 | 35.5881 | 35.3882 | 35.9987 | 35.9368 | 33.6175 | 94.5934 | 94.8143 | 94.0658
2022-09-08 02:05 | 4:15 | 11.4438 | 11.9071 | 15.5336 | 33.6771 | 34.4599 | 33.9375 | 34.71 | 35.4172 | 36.5463 | 37.2434 | 36.7833 | 37.7935 | 34.3754 | 34.3452 | 34.3492 | 35.2468 | 35.3987 | 35.8906 | 36.4588 | 36.7953 | 30.3919 | 29.967 | 93.8007 | 34.1703 | 33.275 | 35.1303 | 33.6091 | 33.3387 | 33.6604 | 35.0499 | 34.5001 | 34.2654 | 37.2473 | 36.2135 | 33.6526 | 34.4297 | 36.2093 | 36.6375 | 37.3876 | 36.217 | 33.6074 | 32.6311 | 34.4258 | 34.8842 | 32.8659 | 34.2916 | 34.4318 | 34.5408 | 34.3544 | 34.3465 | 34.4023 | 33.845 | 34.3715 | 35.5852 | 35.3902 | 35.998 | 35.9199 | 33.607 | 94.3515 | 94.5947 | 93.9163
2022-09-08 02:05 | 4:15 | 13.647 | 11.5424 | 16.343 | 33.5925 | 34.4566 | 33.9385 | 34.7114 | 35.4174 | 36.553 | 37.2477 | 36.798 | 37.758 | 34.3604 | 34.3377 | 34.3409 | 35.2484 | 35.3896 | 35.8581 | 36.4629 | 36.7906 | 30.4241 | 30.05 | 93.6531 | 34.0927 | 33.2716 | 35.1244 | 33.6211 | 33.3109 | 33.6507 | 35.0377 | 34.5102 | 34.2627 | 37.2368 | 36.2269 | 33.6617 | 34.4285 | 36.2468 | 36.6422 | 37.4026 | 36.2331 | 33.6067 | 32.6394 | 34.456 | 34.9057 | 32.8628 | 34.3064 | 34.438 | 34.5173 | 34.3497 | 34.3507 | 34.4059 | 33.8428 | 34.3544 | 35.5922 | 35.4076 | 35.9961 | 35.929 | 33.6205 | 94.2102 | 94.4256 | 93.79
2022-09-08 02:05 | 4:15 | 15.6834 | 12.8239 | 18.173 | 33.6971 | 34.4399 | 33.9196 | 34.6811 | 35.4266 | 36.5576 | 37.2512 | 36.7876 | 37.7658 | 34.3679 | 34.3544 | 34.3391 | 35.2348 | 35.3938 | 35.8801 | 36.4721 | 36.7844 | 30.4974 | 30.1086 | 93.6131 | 34.1771 | 33.2549 | 35.1242 | 33.6097 | 33.3173 | 33.6431 | 35.0386 | 34.5127 | 34.2715 | 37.2424 | 36.2326 | 33.6475 | 34.4238 | 36.2135 | 36.6305 | 37.4048 | 36.2167 | 33.5977 | 32.6518 | 34.4577 | 34.9034 | 32.8724 | 34.3171 | 34.4235 | 34.5357 | 34.3436 | 34.3516 | 34.3945 | 33.8474 | 34.3497 | 35.5748 | 35.3855 | 35.9919 | 35.9207 | 33.5964 | 94.0882 | 94.2629 | 93.7861
2022-09-08 02:06 | 4:16 | 17.2957 | 14.4438 | 19.9614 | 33.7417 | 34.4585 | 33.9188 | 34.6789 | 35.3982 | 36.5386 | 37.2534 | 36.7941 | 37.7885 | 34.3635 | 34.3551 | 34.3361 | 35.2355 | 35.3886 | 35.8889 | 36.4612 | 36.7841 | 30.576 | 30.2075 | 93.6102 | 34.2069 | 33.268 | 35.1271 | 33.6101 | 33.3293 | 33.6497 | 35.0356 | 34.5028 | 34.2515 | 37.245 | 36.2202 | 33.6301 | 34.4214 | 36.2269 | 36.6388 | 37.4155 | 36.2093 | 33.6023 | 32.6542 | 34.4389 | 34.8986 | 32.886 | 34.304 | 34.4273 | 34.5425 | 34.3677 | 34.335 | 34.3932 | 33.8463 | 34.3436 | 35.5774 | 35.3642 | 36.0127 | 35.9235 | 33.6052 | 93.991 | 94.2074 | 93.7158
2022-09-08 02:06 | 4:16 | 18.6784 | 16.199 | 21.5328 | 33.9194 | 34.4658 | 33.9296 | 34.6837 | 35.3949 | 36.546 | 37.2452 | 36.7981 | 37.7588 | 34.3662 | 34.3407 | 34.318 | 35.2257 | 35.3801 | 35.8716 | 36.4727 | 36.7757 | 30.6493 | 30.2573 | 93.4015 | 34.2366 | 33.2606 | 35.1212 | 33.6074 | 33.3363 | 33.6526 | 35.0326 | 34.5041 | 34.2673 | 37.2482 | 36.2408 | 33.6556 | 34.4063 | 36.2326 | 36.6178 | 37.3863 | 36.2468 | 33.5916 | 32.6419 | 34.4464 | 34.9026 | 32.8936 | 34.3302 | 34.4287 | 34.5249 | 34.3647 | 34.3701 | 34.3857 | 33.8483 | 34.3677 | 35.5774 | 35.3754 | 35.994 | 35.9361 | 33.5955 | 93.8743 | 94.0199 | 93.6562
2022-09-08 02:06 | 4:16 | 19.8458 | 17.854 | 22.8317 | 34.0338 | 34.4669 | 33.9328 | 34.6935 | 35.3951 | 36.5359 | 37.2489 | 36.7923 | 37.7799 | 34.3678 | 34.3234 | 34.3108 | 35.239 | 35.3671 | 35.871 | 36.4588 | 36.7821 | 30.705 | 30.3144 | 93.2322 | 34.2514 | 33.2565 | 35.1244 | 33.6067 | 33.3379 | 33.6617 | 35.0264 | 34.495 | 34.262 | 37.2475 | 36.2352 | 33.6574 | 34.4097 | 36.2202 | 36.6213 | 37.3943 | 36.2135 | 33.6099 | 32.6403 | 34.4469 | 34.8909 | 32.878 | 34.3257 | 34.4297 | 34.5307 | 34.3769 | 34.3582 | 34.3916 | 33.8475 | 34.3647 | 35.5881 | 35.3796 | 35.9954 | 35.918 | 33.5814 | 93.7183 | 93.9294 | 93.5924
2022-09-08 02:06 | 4:16 | 20.8862 | 19.4353 | 24.024 | 34.1952 | 34.4386 | 33.9337 | 34.6902 | 35.418 | 36.5449 | 37.2359 | 36.8005 | 37.785 | 34.3684 | 34.3609 | 34.3175 | 35.2362 | 35.3858 | 35.873 | 36.4606 | 36.7786 | 30.7906 | 30.3965 | 93.2829 | 34.3086 | 33.2728 | 35.138 | 33.5977 | 33.3269 | 33.6475 | 35.0336 | 34.4981 | 34.2723 | 37.2425 | 36.2526 | 33.6462 | 34.4302 | 36.2408 | 36.6163 | 37.387 | 36.2269 | 33.6155 | 32.6381 | 34.4606 | 34.9082 | 32.9219 | 34.3133 | 34.4286 | 34.5005 | 34.3774 | 34.3366 | 34.3824 | 33.8364 | 34.3769 | 35.5776 | 35.3781 | 35.9859 | 35.923 | 33.587 | 93.6361 | 93.8203 | 93.5426
2022-09-08 02:06 | 4:16 | 21.7918 | 20.9 | 25.0251 | 34.2515 | 34.4348 | 33.9383 | 34.6869 | 35.4347 | 36.5454 | 37.2463 | 36.8 | 37.7854 | 34.3735 | 34.3622 | 34.3174 | 35.2473 | 35.3891 | 35.8943 | 36.4742 | 36.773 | 30.8456 | 30.4433 | 93.1842 | 34.3959 | 33.2649 | 35.1179 | 33.6023 | 33.3248 | 33.6301 | 35.0194 | 34.4991 | 34.26 | 37.2612 | 36.2403 | 33.6471 | 34.4276 | 36.2352 | 36.6339 | 37.3805 | 36.2326 | 33.6013 | 32.6188 | 34.4719 | 34.9014 | 32.9167 | 34.3169 | 34.4217 | 34.5194 | 34.3715 | 34.3695 | 34.4062 | 33.8436 | 34.3774 | 35.5677 | 35.39 | 36.0002 | 35.9305 | 33.5983 | 93.625 | 93.6753 | 93.5209
2022-09-08 02:06 | 4:16 | 22.6269 | 22.1629 | 25.8614 | 34.4455 | 34.4526 | 33.9425 | 34.7118 | 35.4046 | 36.541 | 37.2383 | 36.7894 | 37.8 | 34.3545 | 34.3494 | 34.3138 | 35.2411 | 35.3638 | 35.8705 | 36.4727 | 36.7755 | 30.9127 | 30.5083 | 93.1194 | 34.3863 | 33.2778 | 35.1328 | 33.5916 | 33.3142 | 33.6556 | 35.0278 | 34.508 | 34.2487 | 37.2281 | 36.2332 | 33.6402 | 34.4441 | 36.2526 | 36.6308 | 37.3873 | 36.2202 | 33.6008 | 32.6309 | 34.4686 | 34.8908 | 32.9167 | 34.2931 | 34.4325 | 34.5104 | 34.3838 | 34.3447 | 34.3742 | 33.8476 | 34.3715 | 35.5628 | 35.3704 | 35.999 | 35.9316 | 33.5807 | 93.5765 | 93.6668 | 93.5
2022-09-08 02:07 | 4:16 | 23.3886 | 23.3367 | 26.6148 | 34.4511 | 34.4639 | 33.9408 | 34.7107 | 35.4105 | 36.545 | 37.2434 | 36.7913 | 37.7758 | 34.3578 | 34.363 | 34.3183 | 35.2493 | 35.3762 | 35.878 | 36.4665 | 36.7892 | 30.9733 | 30.5732 | 93.2059 | 34.3222 | 33.2633 | 35.1367 | 33.6099 | 33.3443 | 33.6574 | 35.0403 | 34.5159 | 34.2518 | 37.2408 | 36.2395 | 33.6571 | 34.4356 | 36.2403 | 36.6187 | 37.394 | 36.2408 | 33.613 | 32.647 | 34.4682 | 34.9058 | 32.9229 | 34.3144 | 34.4243 | 34.4991 | 34.3832 | 34.3517 | 34.372 | 33.8375 | 34.3838 | 35.5733 | 35.3675 | 35.9939 | 35.928 | 33.5798 | 93.5436 | 93.6015 | 93.4555
2022-09-08 02:07 | 4:17 | 24.0689 | 24.3456 | 27.1349 | 34.5014 | 34.4518 | 33.9533 | 34.6969 | 35.4122 | 36.5532 | 37.2782 | 36.7984 | 37.7887 | 34.3728 | 34.3474 | 34.322 | 35.2438 | 35.3713 | 35.8849 | 36.5046 | 36.7834 | 31.0293 | 30.6208 | 93.1117 | 34.4249 | 33.2741 | 35.122 | 33.6155 | 33.3302 | 33.6462 | 35.048 | 34.527 | 34.2656 | 37.248 | 36.2412 | 33.6568 | 34.4363 | 36.2332 | 36.6362 | 37.3896 | 36.2352 | 33.5908 | 32.6551 | 34.4895 | 34.9086 | 32.9185 | 34.304 | 34.4221 | 34.4986 | 34.3645 | 34.3428 | 34.3765 | 33.8519 | 34.3832 | 35.584 | 35.3894 | 35.9983 | 35.9295 | 33.5991 | 93.3856 | 93.5614 | 93.3909
2022-09-08 02:07 | 4:17 | 25.4215 | 22.908 | 27.2979 | 34.5427 | 34.4512 | 33.948 | 34.7198 | 35.4119 | 36.5469 | 37.2588 | 36.8035 | 37.805 | 34.3603 | 34.3508 | 34.3154 | 35.2471 | 35.3735 | 35.8851 | 36.4949 | 36.7685 | 30.8711 | 25.4245 | 93.0625 | 34.492 | 33.2653 | 35.13 | 33.6013 | 33.3257 | 33.6471 | 35.0325 | 34.4997 | 34.2634 | 37.2496 | 36.2256 | 33.642 | 34.4421 | 36.2395 | 36.6245 | 37.4085 | 36.2526 | 33.5906 | 32.6597 | 34.4686 | 34.9199 | 32.936 | 34.3186 | 34.4357 | 34.5005 | 34.396 | 34.3549 | 34.3802 | 33.8714 | 34.3645 | 35.588 | 35.3771 | 36.0024 | 35.9454 | 33.5896 | 93.3123 | 93.4425 | 93.2741
2022-09-08 02:07 | 4:17 | 28.1738 | 28.263 | 27.8733 | 34.6571 | 34.4588 | 33.9496 | 34.7215 | 35.4278 | 36.5451 | 37.261 | 36.8114 | 37.7979 | 34.3712 | 34.3715 | 34.291 | 35.2402 | 35.378 | 35.8874 | 36.5006 | 36.7679 | 30.8542 | 27.3386 | 93.05 | 34.3121 | 33.2637 | 35.121 | 33.6008 | 33.336 | 33.6402 | 35.0401 | 34.5042 | 34.253 | 37.241 | 36.2447 | 33.6545 | 34.4392 | 36.2412 | 36.6195 | 37.389 | 36.2403 | 33.6061 | 32.6473 | 34.4843 | 34.8961 | 32.9492 | 34.3119 | 34.442 | 34.4877 | 34.3882 | 34.3454 | 34.3848 | 33.8468 | 34.396 | 35.5856 | 35.3911 | 35.9906 | 35.9303 | 33.6032 | 93.1139 | 93.4907 | 93.1916
2022-09-08 02:07 | 4:17 | 30.2879 | 29.833 | 28.7953 | 34.7018 | 34.4357 | 33.9671 | 34.7491 | 35.4253 | 36.5396 | 37.2677 | 36.8019 | 37.7996 | 34.3591 | 34.3569 | 34.3197 | 35.242 | 35.3672 | 35.893 | 36.4861 | 36.7749 | 31.464 | 29.2783 | 93.0679 | 34.4189 | 33.2596 | 35.1493 | 33.613 | 33.3407 | 33.6571 | 35.0274 | 34.5068 | 34.2521 | 37.2377 | 36.2375 | 33.6452 | 34.4657 | 36.2256 | 36.6195 | 37.3883 | 36.2332 | 33.6116 | 32.6761 | 34.4798 | 34.9114 | 32.937 | 34.3025 | 34.4356 | 34.4942 | 34.3826 | 34.3573 | 34.3537 | 33.8549 | 34.3882 | 35.5651 | 35.373 | 36.0125 | 35.9333 | 33.5622 | 93.0893 | 93.4086 | 93.2164
2022-09-08 02:07 | 4:17 | 31.21 | 30.264 | 29.4893 | 34.9126 | 34.4351 | 33.9584 | 34.7553 | 35.4417 | 36.5463 | 37.2878 | 36.8206 | 37.8012 | 34.3628 | 34.3462 | 34.3159 | 35.246 | 35.3685 | 35.895 | 36.5086 | 36.793 | 32.2517 | 30.0501 | 92.8903 | 34.4474 | 33.2685 | 35.1137 | 33.5908 | 33.3409 | 33.6568 | 35.0372 | 34.52 | 34.2619 | 37.2431 | 36.2312 | 33.6462 | 34.4527 | 36.2447 | 36.6352 | 37.3993 | 36.2395 | 33.6131 | 32.6648 | 34.4942 | 34.9112 | 32.9556 | 34.3256 | 34.4194 | 34.4987 | 34.3866 | 34.3704 | 34.3558 | 33.8585 | 34.3826 | 35.5872 | 35.3917 | 36.0043 | 35.9381 | 33.5787 | 93.014 | 93.3072 | 93.1359
2022-09-08 02:08 | 4:17 | 31.7455 | 30.5096 | 29.8838 | 34.9574 | 34.4514 | 33.9746 | 34.7632 | 35.4294 | 36.5538 | 37.2655 | 36.8068 | 37.8017 | 34.3625 | 34.3559 | 34.3264 | 35.2503 | 35.3713 | 35.8944 | 36.5326 | 36.7867 | 33.0436 | 30.3746 | 92.8387 | 34.4552 | 33.2664 | 35.1214 | 33.5906 | 33.3389 | 33.642 | 35.0285 | 34.5293 | 34.2705 | 37.2533 | 36.2098 | 33.649 | 34.4554 | 36.2375 | 36.6174 | 37.3881 | 36.2412 | 33.5957 | 32.6669 | 34.4971 | 34.9332 | 32.9604 | 34.308 | 34.4393 | 34.4771 | 34.3785 | 34.3557 | 34.3596 | 33.8559 | 34.3866 | 35.5922 | 35.3675 | 35.9921 | 35.9507 | 33.5684 | 92.9446 | 93.1968 | 93.0496
2022-09-08 02:08 | 4:18 | 32.1823 | 30.6603 | 30.3375 | 35.0068 | 34.4522 | 33.9661 | 34.7571 | 35.4453 | 36.5305 | 37.2846 | 36.8043 | 37.7972 | 34.3835 | 34.3773 | 34.3195 | 35.2435 | 35.3606 | 35.8814 | 36.5291 | 36.7744 | 33.6761 | 30.5897 | 92.7869 | 34.5186 | 33.271 | 35.1322 | 33.6061 | 33.3557 | 33.6545 | 35.0169 | 34.5247 | 34.2435 | 37.2504 | 36.2496 | 33.636 | 34.4575 | 36.2312 | 36.6218 | 37.4089 | 36.2256 | 33.6085 | 32.6694 | 34.4925 | 34.928 | 32.9633 | 34.3271 | 34.4234 | 34.4866 | 34.3945 | 34.349 | 34.3644 | 33.8625 | 34.3785 | 35.6038 | 35.37 | 36.0011 | 35.9469 | 33.5875 | 92.8626 | 93.049 | 92.89
2022-09-08 02:08 | 4:18 | 32.4628 | 30.7748 | 30.567 | 35.0871 | 34.4491 | 33.9899 | 34.7663 | 35.4327 | 36.5355 | 37.2721 | 36.803 | 37.7955 | 34.3499 | 34.3603 | 34.3292 | 35.2647 | 35.3597 | 35.8872 | 36.5295 | 36.7759 | 34.0617 | 30.7863 | 92.6759 | 34.5602 | 33.2679 | 35.1369 | 33.6116 | 33.3496 | 33.6452 | 35.0253 | 34.518 | 34.2584 | 37.24 | 36.2453 | 33.6479 | 34.4697 | 36.2098 | 36.6273 | 37.386 | 36.2447 | 33.5919 | 32.6637 | 34.5037 | 34.9297 | 32.9799 | 34.3227 | 34.4298 | 34.4769 | 34.3847 | 34.3421 | 34.3478 | 33.8581 | 34.3945 | 35.6045 | 35.374 | 36.0139 | 35.9331 | 33.5855 | 92.7847 | 92.9084 | 92.8609
2022-09-08 02:08 | 4:18 | 32.7414 | 30.8748 | 30.8356 | 35.188 | 34.4293 | 33.9883 | 34.7715 | 35.4258 | 36.5602 | 37.2894 | 36.8155 | 37.8076 | 34.3518 | 34.3519 | 34.3109 | 35.2532 | 35.3627 | 35.9088 | 36.5444 | 36.7886 | 34.2376 | 30.9474 | 92.6072 | 34.7041 | 33.2623 | 35.1395 | 33.6131 | 33.356 | 33.6462 | 35.0378 | 34.5154 | 34.2428 | 37.2544 | 36.236 | 33.6587 | 34.4388 | 36.2496 | 36.6154 | 37.3954 | 36.2375 | 33.5853 | 32.6689 | 34.5 | 34.9351 | 32.9963 | 34.3273 | 34.4169 | 34.4737 | 34.397 | 34.34 | 34.3682 | 33.8602 | 34.3847 | 35.6025 | 35.37 | 36.0105 | 35.9518 | 33.6033 | 92.6033 | 92.7739 | 92.811
2022-09-08 02:08 | 4:18 | 33.021 | 30.9584 | 30.9975 | 35.0829 | 34.4311 | 33.9937 | 34.7848 | 35.4365 | 36.5379 | 37.2825 | 36.8242 | 37.8026 | 34.3533 | 34.3494 | 34.3343 | 35.2351 | 35.3659 | 35.9085 | 36.5501 | 36.7724 | 34.2784 | 31.0744 | 92.4561 | 34.6557 | 33.2864 | 35.1414 | 33.5957 | 33.3427 | 33.649 | 35.0401 | 34.5213 | 34.2585 | 37.2478 | 36.2321 | 33.6561 | 34.4809 | 36.2453 | 36.6257 | 37.3883 | 36.2312 | 33.6108 | 32.6889 | 34.504 | 34.9409 | 33.0081 | 34.3233 | 34.4185 | 34.4859 | 34.3948 | 34.3432 | 34.3529 | 33.8757 | 34.397 | 35.5905 | 35.3505 | 36.0086 | 35.9376 | 33.6013 | 92.4813 | 92.6841 | 92.7064
2022-09-08 02:08 | 4:18 | 33.1358 | 30.9881 | 31.1282 | 35.2405 | 34.4192 | 33.982 | 34.8005 | 35.4205 | 36.5369 | 37.2736 | 36.8236 | 37.8155 | 34.3676 | 34.3616 | 34.3319 | 35.269 | 35.3661 | 35.9149 | 36.5579 | 36.7927 | 34.2635 | 31.1531 | 92.38 | 34.6689 | 33.2552 | 35.1173 | 33.6085 | 33.3571 | 33.636 | 35.0265 | 34.531 | 34.2626 | 37.2234 | 36.2198 | 33.6383 | 34.4668 | 36.236 | 36.6389 | 37.3966 | 36.2098 | 33.5951 | 32.6809 | 34.5156 | 34.9451 | 32.9932 | 34.3017 | 34.4361 | 34.4734 | 34.3973 | 34.3653 | 34.3551 | 33.8618 | 34.3948 | 35.5958 | 35.3617 | 36.0198 | 35.9387 | 33.6011 | 92.3791 | 92.5036 | 92.6682
2022-09-08 02:09 | 4:19 | 33.3045 | 31.0687 | 31.3169 | 35.3436 | 34.4235 | 34.0002 | 34.8123 | 35.4515 | 36.5485 | 37.3014 | 36.8265 | 37.8119 | 34.3614 | 34.3484 | 34.3229 | 35.2667 | 35.3581 | 35.9129 | 36.5686 | 36.7894 | 34.2408 | 31.223 | 92.232 | 34.6839 | 33.2718 | 35.1378 | 33.5919 | 33.3517 | 33.6479 | 35.0292 | 34.535 | 34.2651 | 37.2656 | 36.2366 | 33.6482 | 34.4701 | 36.2321 | 36.6325 | 37.3987 | 36.2496 | 33.5954 | 32.6847 | 34.5346 | 34.9481 | 32.9993 | 34.3313 | 34.4201 | 34.4576 | 34.3962 | 34.3685 | 34.3425 | 33.8702 | 34.3973 | 35.5961 | 35.3717 | 36.0166 | 35.9465 | 33.6024 | 92.2315 | 92.4619 | 92.5466
2022-09-08 02:09 | 4:19 | 33.4224 | 31.1471 | 31.3793 | 35.3778 | 34.4295 | 34.0064 | 34.8147 | 35.4643 | 36.542 | 37.2949 | 36.8206 | 37.8014 | 34.3413 | 34.3568 | 34.3309 | 35.2595 | 35.3623 | 35.9066 | 36.5762 | 36.8008 | 34.2332 | 31.2603 | 92.1916 | 34.6525 | 33.2651 | 35.117 | 33.5853 | 33.361 | 33.6587 | 35.0566 | 34.5197 | 34.2599 | 37.2597 | 36.2438 | 33.6477 | 34.466 | 36.2198 | 36.6489 | 37.3983 | 36.2453 | 33.5796 | 32.692 | 34.5269 | 34.9749 | 32.9988 | 34.3329 | 34.4205 | 34.4557 | 34.4005 | 34.3612 | 34.3567 | 33.8777 | 34.3962 | 35.6177 | 35.3712 | 36.0318 | 35.946 | 33.6157 | 92.1023 | 92.3423 | 92.3688
2022-09-08 02:09 | 4:19 | 33.5075 | 31.2076 | 31.477 | 35.4009 | 34.4147 | 34.0049 | 34.8103 | 35.4575 | 36.5604 | 37.321 | 36.824 | 37.8371 | 34.3613 | 34.3324 | 34.33 | 35.2503 | 35.3447 | 35.9175 | 36.5733 | 36.786 | 34.1853 | 31.2976 | 92.0898 | 34.7195 | 33.2729 | 35.1261 | 33.6108 | 33.3709 | 33.6561 | 35.0442 | 34.519 | 34.2603 | 37.2313 | 36.2406 | 33.6604 | 34.4756 | 36.2366 | 36.6415 | 37.4065 | 36.236 | 33.6085 | 32.7062 | 34.5376 | 34.9726 | 33.0025 | 34.3225 | 34.4312 | 34.4537 | 34.3961 | 34.3607 | 34.3457 | 33.8653 | 34.4005 | 35.6019 | 35.3594 | 36.0044 | 35.9423 | 33.6189 | 91.989 | 92.1938 | 92.3905
2022-09-08 02:09 | 4:19 | 33.5613 | 31.2555 | 31.6002 | 35.4108 | 34.4111 | 33.9917 | 34.8196 | 35.4528 | 36.5364 | 37.3072 | 36.8187 | 37.822 | 34.3661 | 34.3554 | 34.3367 | 35.2595 | 35.3478 | 35.9366 | 36.5807 | 36.8125 | 34.1394 | 31.3388 | 92.0779 | 34.7564 | 33.2658 | 35.1328 | 33.5951 | 33.3602 | 33.6383 | 35.049 | 34.5434 | 34.2664 | 37.2604 | 36.2253 | 33.6504 | 34.4829 | 36.2438 | 36.6329 | 37.4111 | 36.2321 | 33.5941 | 32.727 | 34.5413 | 34.9761 | 33.0257 | 34.313 | 34.4222 | 34.428 | 34.4038 | 34.3558 | 34.3453 | 33.8727 | 34.3961 | 35.6128 | 35.3509 | 36.0174 | 35.9586 | 33.6199 | 91.8822 | 92.0424 | 92.2937
2022-09-08 02:09 | 4:19 | 33.5657 | 31.3165 | 31.7612 | 35.4427 | 34.4196 | 33.9916 | 34.8058 | 35.4676 | 36.5528 | 37.3207 | 36.8343 | 37.8173 | 34.3659 | 34.3674 | 34.3262 | 35.2416 | 35.3741 | 35.9225 | 36.595 | 36.7967 | 34.0535 | 31.3556 | 91.9656 | 34.7508 | 33.2687 | 35.1386 | 33.5954 | 33.3614 | 33.6482 | 35.0229 | 34.5203 | 34.2535 | 37.2468 | 36.2489 | 33.6457 | 34.4672 | 36.2406 | 36.6271 | 37.4183 | 36.2198 | 33.6041 | 32.7241 | 34.557 | 34.9876 | 33.0128 | 34.3182 | 34.4228 | 34.4265 | 34.3986 | 34.3766 | 34.3452 | 33.9034 | 34.4038 | 35.6147 | 35.3615 | 35.9996 | 35.9713 | 33.6131 | 91.7251 | 91.9613 | 92.0831
2022-09-08 02:09 | 4:19 | 33.6226 | 31.3707 | 31.8191 | 35.5814 | 34.4169 | 34.0095 | 34.8112 | 35.4544 | 36.5553 | 37.3155 | 36.8364 | 37.8255 | 34.361 | 34.3575 | 34.351 | 35.2642 | 35.3692 | 35.9318 | 36.6015 | 36.8035 | 33.9481 | 31.3825 | 91.8823 | 34.8344 | 33.2652 | 35.1349 | 33.5796 | 33.3569 | 33.6477 | 35.0617 | 34.5139 | 34.2652 | 37.2479 | 36.232 | 33.6608 | 34.4731 | 36.2253 | 36.654 | 37.4205 | 36.2366 | 33.5951 | 32.7214 | 34.568 | 34.9897 | 33.0316 | 34.338 | 34.4155 | 34.4303 | 34.3906 | 34.3529 | 34.3377 | 33.8692 | 34.3986 | 35.6148 | 35.3572 | 36.0163 | 35.9562 | 33.624 | 91.5964 | 91.7994 | 92.0321
2022-09-08 02:10 | 4:19 | 33.7047 | 31.3821 | 31.9371 | 35.7244 | 34.4227 | 33.9966 | 34.8233 | 35.4544 | 36.5649 | 37.3341 | 36.8183 | 37.8333 | 34.3587 | 34.353 | 34.3188 | 35.2583 | 35.3642 | 35.9329 | 36.5978 | 36.8229 | 33.8959 | 31.4268 | 91.7789 | 34.8251 | 33.2798 | 35.1345 | 33.6085 | 33.3778 | 33.6604 | 35.0557 | 34.5225 | 34.2378 | 37.2414 | 36.2337 | 33.6584 | 34.484 | 36.2489 | 36.6374 | 37.4147 | 36.2438 | 33.6066 | 32.7265 | 34.5552 | 34.9974 | 33.0562 | 34.3344 | 34.4156 | 34.433 | 34.4128 | 34.3656 | 34.3544 | 33.9123 | 34.3906 | 35.6353 | 35.3712 | 36.0226 | 35.9701 | 33.6349 | 91.5297 | 91.7117 | 92.0286
2022-09-08 02:10 | 4:20 | 33.7593 | 31.4208 | 32.0059 | 35.7052 | 34.4045 | 34.0053 | 34.8289 | 35.4658 | 36.5538 | 37.3125 | 36.8276 | 37.8287 | 34.3718 | 34.3742 | 34.3377 | 35.2757 | 35.3698 | 35.945 | 36.608 | 36.8211 | 33.8158 | 31.4287 | 91.8175 | 34.8682 | 33.2672 | 35.1299 | 33.5941 | 33.3463 | 33.6504 | 35.0412 | 34.5171 | 34.2771 | 37.2487 | 36.2289 | 33.6443 | 34.479 | 36.232 | 36.6415 | 37.4195 | 36.2406 | 33.591 | 32.7215 | 34.5734 | 35.0083 | 33.0467 | 34.3374 | 34.4286 | 34.4242 | 34.416 | 34.3706 | 34.3551 | 33.8849 | 34.4128 | 35.625 | 35.3747 | 36.0307 | 35.9714 | 33.6422 | 91.5276 | 91.7026 | 92.0586
2022-09-08 02:10 | 4:20 | 33.7987 | 31.4582 | 32.0799 | 35.7061 | 34.4023 | 34.0045 | 34.835 | 35.4702 | 36.567 | 37.3523 | 36.8265 | 37.8158 | 34.3258 | 34.3594 | 34.3504 | 35.2499 | 35.344 | 35.9606 | 36.6184 | 36.8141 | 33.768 | 31.4443 | 91.7609 | 34.8413 | 33.2888 | 35.1375 | 33.6041 | 33.3742 | 33.6457 | 35.0599 | 34.5182 | 34.2703 | 37.2548 | 36.2397 | 33.6384 | 34.4718 | 36.2337 | 36.6542 | 37.4344 | 36.2253 | 33.6 | 32.7378 | 34.5908 | 34.9939 | 33.0483 | 34.3303 | 34.4215 | 34.4164 | 34.4246 | 34.3792 | 34.3407 | 33.8975 | 34.416 | 35.6502 | 35.3673 | 36.0307 | 35.9797 | 33.6466 | 91.5163 | 91.7657 | 92.0966
2022-09-08 02:10 | 4:20 | 33.8006 | 31.4977 | 32.1259 | 35.7277 | 34.4059 | 33.9958 | 34.8422 | 35.4583 | 36.5599 | 37.3135 | 36.8376 | 37.8424 | 34.368 | 34.3448 | 34.3392 | 35.2688 | 35.3584 | 35.9447 | 36.6003 | 36.8261 | 33.6903 | 31.4485 | 91.8948 | 34.8654 | 33.2752 | 35.1217 | 33.5951 | 33.3612 | 33.6608 | 35.0442 | 34.5209 | 34.2526 | 37.263 | 36.2412 | 33.6459 | 34.473 | 36.2289 | 36.6528 | 37.4203 | 36.2489 | 33.5879 | 32.7308 | 34.5895 | 35.009 | 33.047 | 34.3228 | 34.4055 | 34.407 | 34.4275 | 34.3865 | 34.3234 | 33.8815 | 34.4246 | 35.6479 | 35.3714 | 36.0328 | 35.9874 | 33.6286 | 91.6103 | 91.8143 | 92.1564
2022-09-08 02:10 | 4:20 | 33.8597 | 31.5304 | 32.1987 | 35.8652 | 34.3945 | 34.0026 | 34.8139 | 35.4763 | 36.5625 | 37.3382 | 36.8328 | 37.8281 | 34.3634 | 34.3777 | 34.3305 | 35.2548 | 35.347 | 35.9356 | 36.6165 | 36.8124 | 33.6757 | 31.4672 | 91.9654 | 34.8765 | 33.278 | 35.1202 | 33.6066 | 33.343 | 33.6584 | 35.0423 | 34.5287 | 34.2627 | 37.253 | 36.2329 | 33.6442 | 34.4699 | 36.2397 | 36.6619 | 37.4418 | 36.232 | 33.5778 | 32.7325 | 34.5871 | 35.0152 | 33.0673 | 34.3372 | 34.4186 | 34.4045 | 34.4067 | 34.3806 | 34.3609 | 33.8861 | 34.4275 | 35.663 | 35.3786 | 36.0352 | 35.9543 | 33.6466 | 91.6769 | 92.0125 | 92.1049
2022-09-08 02:10 | 4:20 | 33.9851 | 31.5402 | 32.2343 | 35.8351 | 34.3932 | 34.0027 | 34.8357 | 35.4772 | 36.5665 | 37.3285 | 36.8343 | 37.8355 | 34.3498 | 34.367 | 34.3483 | 35.2729 | 35.3601 | 35.9537 | 36.6144 | 36.8194 | 33.7669 | 31.4754 | 91.943 | 34.9107 | 33.2879 | 35.1096 | 33.591 | 33.3484 | 33.6443 | 35.0639 | 34.5216 | 34.2441 | 37.2583 | 36.2171 | 33.6458 | 34.4701 | 36.2412 | 36.6382 | 37.4317 | 36.2337 | 33.5774 | 32.744 | 34.5897 | 35.0127 | 33.0515 | 34.3556 | 34.4088 | 34.4054 | 34.4096 | 34.3863 | 34.3622 | 33.8934 | 34.4067 | 35.6557 | 35.3544 | 36.0097 | 35.9805 | 33.6584 | 91.7855 | 92.0667 | 92.2373
2022-09-08 02:11 | 4:21 | 34.1303 | 31.5664 | 32.337 | 35.9215 | 34.3857 | 33.9925 | 34.8309 | 35.4854 | 36.5532 | 37.3405 | 36.8191 | 37.8292 | 34.3538 | 34.3611 | 34.3436 | 35.2715 | 35.3615 | 35.9455 | 36.6322 | 36.8309 | 33.8488 | 31.4652 | 91.984 | 34.892 | 33.3088 | 35.1164 | 33.6 | 33.3608 | 33.6384 | 35.0596 | 34.5003 | 34.2453 | 37.2466 | 36.2336 | 33.6344 | 34.482 | 36.2329 | 36.6485 | 37.4355 | 36.2289 | 33.5688 | 32.7421 | 34.5909 | 35.0012 | 33.0712 | 34.3421 | 34.4159 | 34.399 | 34.4138 | 34.392 | 34.3494 | 33.907 | 34.4096 | 35.6521 | 35.3565 | 36.0082 | 35.9833 | 33.631 | 91.8996 | 92.1352 | 92.3735
2022-09-08 02:11 | 4:21 | 34.2454 | 31.5778 | 32.4211 | 35.8882 | 34.3916 | 33.9939 | 34.8186 | 35.4797 | 36.562 | 37.3418 | 36.8235 | 37.82 | 34.3479 | 34.3637 | 34.3429 | 35.2546 | 35.3496 | 35.9402 | 36.6225 | 36.8349 | 33.9036 | 31.468 | 91.8822 | 35.019 | 33.2773 | 35.1044 | 33.5879 | 33.3526 | 33.6459 | 35.0348 | 34.5157 | 34.2516 | 37.251 | 36.2135 | 33.6429 | 34.4734 | 36.2171 | 36.6411 | 37.4452 | 36.2397 | 33.5732 | 32.7336 | 34.6013 | 35.0307 | 33.0609 | 34.3439 | 34.4246 | 34.4106 | 34.4143 | 34.3833 | 34.363 | 33.9115 | 34.4138 | 35.6477 | 35.3457 | 36.0076 | 35.974 | 33.6297 | 92.0215 | 92.2043 | 92.2854
2022-09-08 02:11 | 4:21 | 34.3089 | 31.601 | 32.4751 | 35.8774 | 34.3824 | 33.9959 | 34.8254 | 35.4813 | 36.5435 | 37.354 | 36.8046 | 37.828 | 34.3627 | 34.3526 | 34.3479 | 35.2426 | 35.36 | 35.9665 | 36.6264 | 36.8319 | 34.0052 | 31.4804 | 92.0471 | 35.0153 | 33.2863 | 35.097 | 33.5778 | 33.3471 | 33.6442 | 35.0624 | 34.5026 | 34.2446 | 37.2529 | 36.2135 | 33.6376 | 34.4748 | 36.2336 | 36.6303 | 37.4396 | 36.2412 | 33.5763 | 32.7616 | 34.6035 | 35.0312 | 33.0879 | 34.3364 | 34.4184 | 34.3932 | 34.4023 | 34.3823 | 34.3474 | 33.9126 | 34.4143 | 35.6491 | 35.3646 | 36.0061 | 35.9453 | 33.6396 | 92.0949 | 92.3565 | 92.3656
2022-09-08 02:11 | 4:21 | 34.3546 | 31.6082 | 32.5334 | 35.9518 | 34.4062 | 33.9913 | 34.8118 | 35.4503 | 36.5522 | 37.3752 | 36.8122 | 37.8276 | 34.3617 | 34.3495 | 34.3332 | 35.2506 | 35.3352 | 35.953 | 36.6285 | 36.8115 | 34.0763 | 31.4899 | 92.0645 | 34.9573 | 33.298 | 35.1213 | 33.5774 | 33.3678 | 33.6458 | 35.0519 | 34.5007 | 34.246 | 37.2452 | 36.2121 | 33.6375 | 34.4517 | 36.2135 | 36.6238 | 37.4421 | 36.2329 | 33.59 | 32.7638 | 34.615 | 35.0292 | 33.065 | 34.3341 | 34.4199 | 34.4041 | 34.4117 | 34.4017 | 34.3508 | 33.9139 | 34.4023 | 35.6646 | 35.3656 | 36.0321 | 35.9676 | 33.6602 | 92.1983 | 92.4251 | 92.4395
2022-09-08 02:11 | 4:21 | 34.3892 | 31.629 | 32.5681 | 35.8965 | 34.3742 | 33.9736 | 34.8217 | 35.4661 | 36.5558 | 37.3527 | 36.8168 | 37.8115 | 34.3503 | 34.3526 | 34.3269 | 35.2415 | 35.3379 | 35.9523 | 36.6378 | 36.8218 | 34.1312 | 31.5013 | 92.2435 | 34.9916 | 33.2961 | 35.0973 | 33.5688 | 33.3561 | 33.6344 | 35.0554 | 34.5119 | 34.2493 | 37.2586 | 36.2163 | 33.6463 | 34.4697 | 36.2135 | 36.6363 | 37.4482 | 36.2171 | 33.5846 | 32.7432 | 34.6266 | 35.0272 | 33.0718 | 34.3359 | 34.4174 | 34.4192 | 34.4269 | 34.3862 | 34.3715 | 33.8963 | 34.4117 | 35.6594 | 35.3426 | 36.02 | 35.9803 | 33.6468 | 92.2901 | 92.4623 | 92.5168
2022-09-08 02:11 | 4:21 | 31.9749 | 31.3556 | 32.3576 | 35.976 | 34.372 | 33.9846 | 34.8201 | 35.469 | 36.5462 | 37.366 | 36.7904 | 37.8098 | 34.3367 | 34.3604 | 34.3516 | 35.2423 | 35.3539 | 35.9367 | 36.6376 | 36.8317 | 31.3349 | 31.3247 | 92.176 | 34.9707 | 33.3006 | 35.104 | 33.5732 | 33.3491 | 33.6429 | 35.0365 | 34.484 | 34.2573 | 37.2483 | 36.2224 | 33.6401 | 34.459 | 36.2121 | 36.6344 | 37.4634 | 36.2336 | 33.5758 | 32.7424 | 34.6113 | 35.0498 | 33.0583 | 34.3354 | 34.4156 | 34.4095 | 34.4253 | 34.3773 | 34.3569 | 33.9182 | 34.4269 | 35.6304 | 35.3403 | 36.0213 | 35.9718 | 33.6584 | 92.3976 | 92.5622 | 92.5458
2022-09-08 02:12 | 4:21 | 29.9609 | 28.7958 | 31.8035 | 35.9704 | 34.3765 | 33.9773 | 34.8287 | 35.4894 | 36.5496 | 37.3617 | 36.7888 | 37.8109 | 34.3436 | 34.3449 | 34.3171 | 35.2297 | 35.3278 | 35.9282 | 36.6504 | 36.8406 | 27.1451 | 31.0784 | 92.2995 | 35.0112 | 33.2832 | 35.1081 | 33.5763 | 33.3635 | 33.6376 | 35.0562 | 34.4872 | 34.2325 | 37.2523 | 36.2326 | 33.6397 | 34.474 | 36.2163 | 36.6225 | 37.4307 | 36.2135 | 33.5703 | 32.7583 | 34.6352 | 35.0587 | 33.0998 | 34.3367 | 34.4161 | 34.4173 | 34.4159 | 34.4033 | 34.3462 | 33.9343 | 34.4253 | 35.6523 | 35.3494 | 36.0173 | 35.9888 | 33.6614 | 92.4814 | 92.6616 | 92.6459
2022-09-08 02:12 | 4:22 | 31.3245 | 20.2055 | 31.8162 | 36.0283 | 34.3802 | 34.0012 | 34.8209 | 35.4746 | 36.5589 | 37.3569 | 36.7954 | 37.8342 | 34.3611 | 34.3454 | 34.323 | 35.2238 | 35.3381 | 35.946 | 36.6499 | 36.8136 | 27.5409 | 31.1648 | 92.3931 | 34.9961 | 33.2893 | 35.1129 | 33.59 | 33.3508 | 33.6375 | 35.0727 | 34.4873 | 34.2325 | 37.2363 | 36.2083 | 33.6385 | 34.4604 | 36.2224 | 36.646 | 37.4519 | 36.2135 | 33.5807 | 32.7628 | 34.6311 | 35.0438 | 33.095 | 34.3326 | 34.3989 | 34.408 | 34.4239 | 34.4073 | 34.3559 | 33.9068 | 34.4159 | 35.655 | 35.3241 | 36.0078 | 35.9883 | 33.6395 | 92.6018 | 92.7941 | 92.7199
2022-09-08 02:12 | 4:22 | 31.6368 | 23.6069 | 32.0037 | 35.9843 | 34.3848 | 33.9827 | 34.8165 | 35.4776 | 36.555 | 37.3797 | 36.8014 | 37.8204 | 34.364 | 34.3481 | 34.3329 | 35.2238 | 35.3337 | 35.9351 | 36.6402 | 36.8341 | 28.3067 | 31.1606 | 92.5078 | 34.9824 | 33.2748 | 35.104 | 33.5846 | 33.3696 | 33.6463 | 35.0784 | 34.4993 | 34.2204 | 37.2434 | 36.2168 | 33.6345 | 34.446 | 36.2326 | 36.6387 | 37.4506 | 36.2121 | 33.5995 | 32.7797 | 34.6318 | 35.063 | 33.1177 | 34.3327 | 34.4235 | 34.411 | 34.4084 | 34.4149 | 34.3773 | 33.9087 | 34.4239 | 35.6565 | 35.3089 | 36.0205 | 35.9877 | 33.6452 | 92.8303 | 92.925 | 92.8741
2022-09-08 02:12 | 4:22 | 31.7682 | 26.3193 | 32.1225 | 36.0479 | 34.3537 | 33.9943 | 34.8294 | 35.4704 | 36.5432 | 37.3696 | 36.8051 | 37.8074 | 34.3409 | 34.37 | 34.325 | 35.2226 | 35.3446 | 35.9556 | 36.6415 | 36.8486 | 29.0465 | 31.1323 | 92.7681 | 34.9764 | 33.3028 | 35.0931 | 33.5758 | 33.3436 | 33.6401 | 35.0549 | 34.4868 | 34.2407 | 37.2535 | 36.2318 | 33.648 | 34.4809 | 36.2083 | 36.6436 | 37.4504 | 36.2163 | 33.5827 | 32.7769 | 34.6109 | 35.0504 | 33.0949 | 34.3509 | 34.3951 | 34.3913 | 34.4261 | 34.408 | 34.3603 | 33.9201 | 34.4084 | 35.6789 | 35.3321 | 36.0279 | 35.9889 | 33.6701 | 93.0145 | 93.0298 | 92.9823
2022-09-08 02:12 | 4:22 | 31.8669 | 28.0969 | 32.2048 | 36.0228 | 34.3558 | 33.9807 | 34.8172 | 35.4817 | 36.5626 | 37.3753 | 36.7967 | 37.816 | 34.3465 | 34.3598 | 34.3554 | 35.2091 | 35.3456 | 35.955 | 36.6398 | 36.8383 | 29.6727 | 31.1633 | 92.8903 | 34.9544 | 33.2945 | 35.1167 | 33.5703 | 33.359 | 33.6397 | 35.0613 | 34.497 | 34.2196 | 37.2467 | 36.2189 | 33.6356 | 34.4395 | 36.2168 | 36.623 | 37.4588 | 36.2224 | 33.5764 | 32.7841 | 34.6343 | 35.0634 | 33.1121 | 34.3416 | 34.4199 | 34.3945 | 34.4365 | 34.4058 | 34.3519 | 33.8868 | 34.4261 | 35.6483 | 35.3426 | 36.0308 | 35.9727 | 33.6718 | 93.1282 | 93.2568 | 93.0091
2022-09-08 02:12 | 4:22 | 31.9826 | 29.1956 | 32.2511 | 35.9759 | 34.3596 | 33.9847 | 34.8274 | 35.476 | 36.5425 | 37.3776 | 36.7926 | 37.8022 | 34.3507 | 34.3728 | 34.3406 | 35.2119 | 35.3326 | 35.9425 | 36.6569 | 36.8274 | 30.166 | 31.1889 | 92.7814 | 35.0242 | 33.2984 | 35.1064 | 33.5807 | 33.3604 | 33.6385 | 35.0581 | 34.4904 | 34.2161 | 37.2505 | 36.2269 | 33.64 | 34.4442 | 36.2318 | 36.6418 | 37.4615 | 36.2326 | 33.5684 | 32.7679 | 34.6503 | 35.072 | 33.0954 | 34.3402 | 34.4204 | 34.3949 | 34.4316 | 34.4159 | 34.3494 | 33.914 | 34.4365 | 35.6457 | 35.3323 | 36.0032 | 35.9741 | 33.6412 | 93.246 | 93.4903 | 93.1482
2022-09-08 02:13 | 4:23 | 32.0492 | 29.8943 | 32.2925 | 36.0796 | 34.3644 | 33.9851 | 34.8338 | 35.4668 | 36.5666 | 37.3824 | 36.793 | 37.821 | 34.3516 | 34.3541 | 34.3582 | 35.2074 | 35.3661 | 35.9457 | 36.6645 | 36.8401 | 30.5666 | 31.2032 | 92.8103 | 34.9874 | 33.286 | 35.0917 | 33.5995 | 33.3449 | 33.6345 | 35.0701 | 34.4804 | 34.2268 | 37.2459 | 36.2412 | 33.6426 | 34.475 | 36.2189 | 36.6311 | 37.4487 | 36.2083 | 33.5643 | 32.7754 | 34.635 | 35.0425 | 33.1243 | 34.3494 | 34.3865 | 34.401 | 34.4185 | 34.4064 | 34.3616 | 33.9265 | 34.4316 | 35.6742 | 35.35 | 36.0215 | 35.979 | 33.6425 | 93.3645 | 93.6018 | 93.1757
2022-09-08 02:13 | 4:23 | 32.1294 | 30.3455 | 32.3688 | 36.193 | 34.3478 | 33.9809 | 34.8206 | 35.4679 | 36.543 | 37.3786 | 36.7933 | 37.7962 | 34.335 | 34.3684 | 34.335 | 35.2133 | 35.3334 | 35.944 | 36.6528 | 36.8547 | 30.9082 | 31.2364 | 92.7182 | 35.045 | 33.3008 | 35.0954 | 33.5827 | 33.3219 | 33.648 | 35.0673 | 34.4746 | 34.2052 | 37.2472 | 36.2274 | 33.6396 | 34.4591 | 36.2269 | 36.6299 | 37.4601 | 36.2168 | 33.5665 | 32.7699 | 34.649 | 35.0394 | 33.1291 | 34.3382 | 34.415 | 34.3877 | 34.4278 | 34.4028 | 34.3484 | 33.9256 | 34.4185 | 35.6399 | 35.3366 | 36.0358 | 35.9865 | 33.6471 | 93.6085 | 93.6648 | 93.2644
2022-09-08 02:13 | 4:23 | 32.1893 | 30.6306 | 32.3941 | 36.116 | 34.3682 | 33.9809 | 34.8274 | 35.457 | 36.5615 | 37.3689 | 36.7818 | 37.8023 | 34.3701 | 34.3537 | 34.3556 | 35.2217 | 35.3296 | 35.9315 | 36.6653 | 36.8261 | 31.1584 | 31.2676 | 92.9427 | 35.0728 | 33.2981 | 35.1005 | 33.5764 | 33.3768 | 33.6356 | 35.047 | 34.4886 | 34.211 | 37.2479 | 36.2127 | 33.6623 | 34.4491 | 36.2412 | 36.6366 | 37.4523 | 36.2318 | 33.5761 | 32.7956 | 34.6561 | 35.063 | 33.1389 | 34.3397 | 34.4065 | 34.3966 | 34.4263 | 34.4004 | 34.3568 | 33.9364 | 34.4278 | 35.6729 | 35.323 | 35.9972 | 36.0033 | 33.6693 | 93.7827 | 93.8766 | 93.3894
2022-09-08 02:13 | 4:23 | 32.2806 | 30.8378 | 32.4163 | 36.1202 | 34.3529 | 33.9795 | 34.8 | 35.4609 | 36.5528 | 37.3991 | 36.7945 | 37.8185 | 34.3582 | 34.3535 | 34.3514 | 35.2252 | 35.336 | 35.938 | 36.6372 | 36.8374 | 31.3377 | 31.2617 | 93.1676 | 35.0633 | 33.2873 | 35.1071 | 33.5684 | 33.3425 | 33.64 | 35.0741 | 34.4848 | 34.2208 | 37.2508 | 36.2253 | 33.6344 | 34.4597 | 36.2274 | 36.6431 | 37.4706 | 36.2189 | 33.5659 | 32.8027 | 34.654 | 35.0626 | 33.1518 | 34.3627 | 34.3895 | 34.3931 | 34.4305 | 34.3999 | 34.3324 | 33.9213 | 34.4263 | 35.6569 | 35.3403 | 36.0186 | 35.9856 | 33.6675 | 93.9218 | 94.0655 | 93.5539
2022-09-08 02:13 | 4:23 | 32.321 | 30.976 | 32.451 | 36.2372 | 34.3551 | 33.9751 | 34.8194 | 35.4831 | 36.5575 | 37.3864 | 36.8049 | 37.7951 | 34.3366 | 34.3607 | 34.352 | 35.2337 | 35.3315 | 35.9243 | 36.6432 | 36.8335 | 31.5006 | 31.2825 | 93.1912 | 35.0745 | 33.2945 | 35.0929 | 33.5643 | 33.3408 | 33.6426 | 35.0721 | 34.486 | 34.212 | 37.2405 | 36.2323 | 33.6376 | 34.4528 | 36.2127 | 36.6382 | 37.4673 | 36.2269 | 33.569 | 32.8062 | 34.636 | 35.0511 | 33.1405 | 34.3474 | 34.3977 | 34.42 | 34.4318 | 34.4069 | 34.3554 | 33.9233 | 34.4305 | 35.6474 | 35.3108 | 36.0236 | 36.0087 | 33.6454 | 94.1636 | 94.2823 | 93.6188
2022-09-08 02:13 | 4:23 | 32.3562 | 31.1034 | 32.4503 | 36.1542 | 34.3425 | 33.9683 | 34.8094 | 35.4663 | 36.5547 | 37.3843 | 36.8057 | 37.8171 | 34.3695 | 34.36 | 34.3405 | 35.2159 | 35.3178 | 35.9432 | 36.6404 | 36.8382 | 31.6655 | 31.3092 | 93.0262 | 35.1614 | 33.2867 | 35.1038 | 33.5665 | 33.3696 | 33.6396 | 35.0718 | 34.4897 | 34.2187 | 37.2361 | 36.2377 | 33.6443 | 34.4583 | 36.2253 | 36.6238 | 37.4821 | 36.2412 | 33.5663 | 32.7868 | 34.6567 | 35.0764 | 33.1376 | 34.3434 | 34.3806 | 34.3828 | 34.438 | 34.4079 | 34.3674 | 33.9154 | 34.4318 | 35.6711 | 35.3204 | 36.0232 | 35.9848 | 33.657 | 94.2919 | 94.4437 | 93.5982
2022-09-08 02:14 | 4:23 | 32.3894 | 31.1697 | 32.4879 | 36.1578 | 34.3567 | 33.9577 | 34.8096 | 35.4633 | 36.557 | 37.3821 | 36.7967 | 37.8258 | 34.3447 | 34.3436 | 34.3312 | 35.2139 | 35.3307 | 35.9552 | 36.6494 | 36.8322 | 31.7701 | 31.3305 | 93.332 | 35.1839 | 33.3086 | 35.0713 | 33.5761 | 33.3364 | 33.6623 | 35.0673 | 34.4568 | 34.2105 | 37.2271 | 36.2264 | 33.6306 | 34.4368 | 36.2323 | 36.6424 | 37.4789 | 36.2274 | 33.5721 | 32.8321 | 34.6603 | 35.0712 | 33.1593 | 34.3519 | 34.3956 | 34.3939 | 34.4235 | 34.414 | 34.3575 | 33.9244 | 34.438 | 35.6618 | 35.3399 | 36.0355 | 35.9929 | 33.6455 | 94.4237 | 94.5231 | 93.7666
2022-09-08 02:14 | 4:24 | 32.418 | 31.2402 | 32.521 | 36.1549 | 34.3457 | 33.9702 | 34.8023 | 35.4612 | 36.5794 | 37.3639 | 36.7871 | 37.8253 | 34.3517 | 34.3616 | 34.3373 | 35.2062 | 35.3415 | 35.939 | 36.6454 | 36.8408 | 31.8595 | 31.3559 | 93.6343 | 35.1538 | 33.3115 | 35.0981 | 33.5659 | 33.3492 | 33.6344 | 35.0661 | 34.4726 | 34.198 | 37.2344 | 36.2444 | 33.6465 | 34.45 | 36.2377 | 36.6412 | 37.4661 | 36.2127 | 33.5678 | 32.8094 | 34.6794 | 35.0906 | 33.1758 | 34.3529 | 34.3714 | 34.4055 | 34.4273 | 34.4321 | 34.353 | 33.9206 | 34.4235 | 35.6798 | 35.3291 | 36.0171 | 35.9898 | 33.6452 | 94.5108 | 94.5814 | 93.9165
2022-09-08 02:14 | 4:24 | 32.458 | 31.3055 | 32.5442 | 36.2903 | 34.3453 | 33.9733 | 34.805 | 35.4628 | 36.5721 | 37.3777 | 36.7859 | 37.8091 | 34.3428 | 34.3513 | 34.3467 | 35.2205 | 35.3189 | 35.9264 | 36.6616 | 36.8204 | 31.9423 | 31.3477 | 93.5375 | 35.123 | 33.2959 | 35.0896 | 33.569 | 33.3564 | 33.6376 | 35.0589 | 34.4715 | 34.2184 | 37.248 | 36.2405 | 33.6175 | 34.4346 | 36.2264 | 36.6221 | 37.4641 | 36.2253 | 33.5753 | 32.8123 | 34.6794 | 35.0797 | 33.1665 | 34.3565 | 34.3959 | 34.3849 | 34.4287 | 34.4082 | 34.3742 | 33.9375 | 34.4273 | 35.6529 | 35.3179 | 36.0144 | 35.9912 | 33.6592 | 94.6188 | 94.7426 | 93.9778
2022-09-08 02:14 | 4:24 | 32.4888 | 31.3536 | 32.5489 | 36.1589 | 34.3452 | 33.97 | 34.8077 | 35.4614 | 36.5514 | 37.3817 | 36.7811 | 37.8321 | 34.3549 | 34.3606 | 34.3401 | 35.1985 | 35.3369 | 35.9352 | 36.6409 | 36.8269 | 32.0172 | 31.3769 | 93.5326 | 35.1534 | 33.2976 | 35.1041 | 33.5663 | 33.3421 | 33.6443 | 35.0782 | 34.4755 | 34.2102 | 37.2349 | 36.241 | 33.6399 | 34.4536 | 36.2444 | 36.6125 | 37.4534 | 36.2323 | 33.581 | 32.8251 | 34.6676 | 35.0528 | 33.1536 | 34.3655 | 34.3591 | 34.4143 | 34.4297 | 34.4182 | 34.3594 | 33.935 | 34.4287 | 35.6487 | 35.3143 | 36.0306 | 36.0062 | 33.6503 | 94.7734 | 94.8032 | 93.9406
2022-09-08 02:14 | 4:24 | 32.5212 | 31.3889 | 32.5727 | 36.208 | 34.3377 | 33.9624 | 34.8143 | 35.4616 | 36.5489 | 37.3919 | 36.7927 | 37.8116 | 34.3454 | 34.3507 | 34.3356 | 35.2122 | 35.3293 | 35.9268 | 36.661 | 36.8166 | 32.1236 | 31.3912 | 93.6008 | 35.1338 | 33.2954 | 35.0858 | 33.5721 | 33.3446 | 33.6306 | 35.0563 | 34.4568 | 34.2038 | 37.2435 | 36.2292 | 33.6199 | 34.4448 | 36.2405 | 36.6144 | 37.4708 | 36.2377 | 33.5769 | 32.8239 | 34.6913 | 35.0496 | 33.1872 | 34.347 | 34.3593 | 34.3972 | 34.4286 | 34.4147 | 34.3448 | 33.9391 | 34.4297 | 35.6927 | 35.3308 | 36.0241 | 35.9866 | 33.6522 | 94.7726 | 94.9408 | 94.0164
2022-09-08 02:14 | 4:24 | 32.5986 | 30.3025 | 32.6089 | 36.3144 | 34.3544 | 33.9729 | 34.8083 | 35.459 | 36.558 | 37.3772 | 36.8081 | 37.8113 | 34.3573 | 34.36 | 34.3451 | 35.2042 | 35.3361 | 35.9241 | 36.6413 | 36.8033 | 32.4372 | 31.4092 | 93.4511 | 35.2136 | 33.2864 | 35.1151 | 33.5678 | 33.3427 | 33.6465 | 35.0582 | 34.4686 | 34.2081 | 37.2481 | 36.2371 | 33.6334 | 34.4536 | 36.241 | 36.6207 | 37.4571 | 36.2264 | 33.5557 | 32.8235 | 34.6828 | 35.0635 | 33.1972 | 34.3498 | 34.3825 | 34.3841 | 34.4217 | 34.4103 | 34.3777 | 33.9311 | 34.4286 | 35.6616 | 35.3367 | 36.0231 | 35.9992 | 33.6352 | 94.7925 | 94.999 | 94.0377
2022-09-08 02:15 | 4:25 | 32.4701 | 30.7489 | 32.4977 | 36.3042 | 34.3551 | 33.9646 | 34.8003 | 35.4667 | 36.5578 | 37.3689 | 36.7925 | 37.8054 | 34.3704 | 34.357 | 34.3105 | 35.2057 | 35.3182 | 35.9114 | 36.6554 | 36.82 | 32.8317 | 31.8907 | 93.6968 | 35.2397 | 33.305 | 35.1103 | 33.5753 | 33.347 | 33.6175 | 35.0414 | 34.4881 | 34.197 | 37.2186 | 36.2325 | 33.6219 | 34.4345 | 36.2292 | 36.6169 | 37.452 | 36.2444 | 33.5753 | 32.84 | 34.6668 | 35.0645 | 33.2112 | 34.3728 | 34.3662 | 34.3941 | 34.4325 | 34.4113 | 34.367 | 33.9368 | 34.4217 | 35.6655 | 35.3263 | 36.0334 | 35.9896 | 33.651 | 94.6791 | 94.9691 | 93.9727
2022-09-08 02:15 | 4:25 | 33.1265 | 31.3502 | 32.7209 | 36.2802 | 34.3407 | 33.9862 | 34.8003 | 35.4567 | 36.5535 | 37.3581 | 36.819 | 37.8092 | 34.3557 | 34.3604 | 34.3221 | 35.1949 | 35.3303 | 35.9377 | 36.642 | 36.81 | 33.249 | 31.8815 | 93.6168 | 35.1859 | 33.286 | 35.0954 | 33.581 | 33.3494 | 33.6399 | 35.0589 | 34.4427 | 34.2048 | 37.2168 | 36.2547 | 33.625 | 34.4496 | 36.2371 | 36.6294 | 37.4615 | 36.2405 | 33.5867 | 32.8313 | 34.6907 | 35.0708 | 33.2112 | 34.3644 | 34.3616 | 34.4037 | 34.4243 | 34.4163 | 34.3611 | 33.9424 | 34.4325 | 35.6796 | 35.3224 | 36.0134 | 35.998 | 33.6419 | 94.4448 | 94.7614 | 93.8021
2022-09-08 02:15 | 4:25 | 34.0172 | 31.4504 | 32.9438 | 36.443 | 34.3234 | 33.9743 | 34.8216 | 35.4543 | 36.5331 | 37.3755 | 36.7948 | 37.8219 | 34.349 | 34.3585 | 34.3056 | 35.21 | 35.3361 | 35.9307 | 36.6464 | 36.7948 | 33.829 | 31.8087 | 93.3274 | 35.2511 | 33.2989 | 35.1048 | 33.5769 | 33.3458 | 33.6199 | 35.0587 | 34.4688 | 34.2071 | 37.2379 | 36.2504 | 33.6255 | 34.4483 | 36.2325 | 36.6097 | 37.4707 | 36.241 | 33.5667 | 32.8399 | 34.6974 | 35.071 | 33.2186 | 34.3415 | 34.3556 | 34.3853 | 34.4221 | 34.4302 | 34.3637 | 33.9345 | 34.4243 | 35.6547 | 35.3334 | 36.0225 | 35.9998 | 33.6372 | 94.219 | 94.5065 | 93.7002
2022-09-08 02:15 | 4:25 | 34.7255 | 31.489 | 33.1254 | 36.3138 | 34.3609 | 33.9768 | 34.8273 | 35.4503 | 36.545 | 37.3647 | 36.7738 | 37.7946 | 34.3421 | 34.3602 | 34.3183 | 35.2047 | 35.3165 | 35.9192 | 36.6361 | 36.8151 | 34.4413 | 31.7286 | 93.2999 | 35.2691 | 33.2921 | 35.1118 | 33.5557 | 33.367 | 33.6334 | 35.043 | 34.4632 | 34.1901 | 37.2403 | 36.2755 | 33.6388 | 34.4379 | 36.2547 | 36.6158 | 37.4643 | 36.2292 | 33.5844 | 32.8429 | 34.6895 | 35.0844 | 33.2213 | 34.3632 | 34.3568 | 34.3991 | 34.4357 | 34.4363 | 34.3526 | 33.9294 | 34.4221 | 35.6596 | 35.3313 | 36.0444 | 35.9857 | 33.6414 | 94.0178 | 94.2563 | 93.5403
2022-09-08 02:15 | 4:25 | 35.0715 | 31.5273 | 33.249 | 36.299 | 34.3622 | 33.9707 | 34.8175 | 35.4761 | 36.5406 | 37.3586 | 36.7693 | 37.8156 | 34.34 | 34.3558 | 34.3081 | 35.1977 | 35.3041 | 35.9385 | 36.6559 | 36.7993 | 34.768 | 31.6786 | 93.2507 | 35.3484 | 33.2793 | 35.1248 | 33.5753 | 33.3391 | 33.6219 | 35.042 | 34.4677 | 34.2148 | 37.2494 | 36.2557 | 33.6304 | 34.4379 | 36.2504 | 36.6106 | 37.4633 | 36.2371 | 33.5823 | 32.8581 | 34.7002 | 35.0817 | 33.2482 | 34.3614 | 34.3491 | 34.3877 | 34.442 | 34.4237 | 34.3495 | 33.9473 | 34.4357 | 35.6479 | 35.3199 | 36.0094 | 35.9866 | 33.6313 | 93.8493 | 94.0368 | 93.474
2022-09-08 02:15 | 4:25 | 35.1242 | 31.551 | 33.2636 | 36.4382 | 34.3494 | 33.9721 | 34.8289 | 35.4658 | 36.5454 | 37.3578 | 36.7961 | 37.8097 | 34.3432 | 34.369 | 34.3136 | 35.1939 | 35.331 | 35.9252 | 36.6442 | 36.8012 | 34.8274 | 31.6664 | 93.1805 | 35.4002 | 33.2817 | 35.0958 | 33.5867 | 33.3444 | 33.625 | 35.055 | 34.452 | 34.196 | 37.23 | 36.2446 | 33.6469 | 34.4425 | 36.2755 | 36.5859 | 37.4529 | 36.2325 | 33.5764 | 32.8364 | 34.687 | 35.0697 | 33.2532 | 34.3662 | 34.3578 | 34.3896 | 34.4356 | 34.4293 | 34.3526 | 33.9273 | 34.442 | 35.6536 | 35.3262 | 36.0122 | 35.986 | 33.63 | 93.7341 | 93.849 | 93.3989
2022-09-08 02:16 | 4:26 | 35.0495 | 31.5852 | 33.2742 | 36.3599 | 34.363 | 33.9915 | 34.8156 | 35.4546 | 36.5373 | 37.3512 | 36.7957 | 37.8113 | 34.3653 | 34.3595 | 34.3183 | 35.218 | 35.3145 | 35.937 | 36.6249 | 36.7898 | 34.7991 | 31.6623 | 93.1076 | 35.3655 | 33.3002 | 35.0979 | 33.5667 | 33.3505 | 33.6255 | 35.0406 | 34.4766 | 34.1993 | 37.2285 | 36.2585 | 33.622 | 34.4483 | 36.2557 | 36.6194 | 37.4475 | 36.2547 | 33.5769 | 32.8541 | 34.6942 | 35.0726 | 33.2542 | 34.3685 | 34.3323 | 34.3913 | 34.4194 | 34.4425 | 34.3604 | 33.9213 | 34.4356 | 35.6476 | 35.3205 | 36.0181 | 35.9902 | 33.6403 | 93.6213 | 93.7887 | 93.2659
2022-09-08 02:16 | 4:26 | 34.9192 | 31.6045 | 33.1158 | 36.4932 | 34.3474 | 33.9772 | 34.831 | 35.459 | 36.5401 | 37.3649 | 36.7761 | 37.8148 | 34.3685 | 34.3511 | 34.3185 | 35.2018 | 35.3406 | 35.9293 | 36.6538 | 36.7895 | 34.8447 | 31.6892 | 93.1291 | 35.3015 | 33.2737 | 35.1132 | 33.5844 | 33.3518 | 33.6388 | 35.0374 | 34.4681 | 34.2158 | 37.2281 | 36.2583 | 33.6319 | 34.4449 | 36.2446 | 36.596 | 37.456 | 36.2504 | 33.5826 | 32.8689 | 34.6977 | 35.0552 | 33.284 | 34.3496 | 34.3552 | 34.3937 | 34.4393 | 34.4411 | 34.3449 | 33.9457 | 34.4194 | 35.6504 | 35.3395 | 36.0221 | 36.0159 | 33.6196 | 93.575 | 93.7329 | 93.256
2022-09-08 02:16 | 4:26 | 34.97 | 31.6459 | 33.1194 | 36.4575 | 34.3508 | 33.973 | 34.8156 | 35.4826 | 36.5461 | 37.374 | 36.7739 | 37.7929 | 34.3612 | 34.3678 | 34.3261 | 35.2062 | 35.3217 | 35.9269 | 36.6462 | 36.7998 | 34.8466 | 31.6859 | 92.9326 | 35.4223 | 33.3039 | 35.1085 | 33.5823 | 33.3602 | 33.6304 | 35.0581 | 34.4686 | 34.2017 | 37.2346 | 36.2615 | 33.6288 | 34.455 | 36.2585 | 36.6004 | 37.4654 | 36.2755 | 33.5772 | 32.8531 | 34.7134 | 35.0728 | 33.2555 | 34.3672 | 34.3319 | 34.382 | 34.4234 | 34.424 | 34.3454 | 33.9409 | 34.4393 | 35.6663 | 35.3062 | 36.0083 | 35.9933 | 33.6267 | 93.5358 | 93.6268 | 93.1232
2022-09-08 02:16 | 4:26 | 34.9788 | 31.6648 | 33.115 | 36.465 | 34.3715 | 33.9701 | 34.8407 | 35.4682 | 36.5471 | 37.3687 | 36.8006 | 37.8204 | 34.3607 | 34.3485 | 34.319 | 35.2063 | 35.3269 | 35.9271 | 36.6419 | 36.7861 | 34.9002 | 31.6725 | 92.9966 | 35.4385 | 33.3148 | 35.1092 | 33.5764 | 33.3729 | 33.6469 | 35.0464 | 34.4674 | 34.1996 | 37.2382 | 36.2615 | 33.645 | 34.4611 | 36.2583 | 36.6237 | 37.4528 | 36.2557 | 33.5917 | 32.865 | 34.7082 | 35.0805 | 33.2816 | 34.3824 | 34.3425 | 34.3771 | 34.4298 | 34.44 | 34.3481 | 33.9491 | 34.4234 | 35.6426 | 35.3327 | 36.0307 | 36.0087 | 33.6388 | 93.441 | 93.5763 | 93.0933
2022-09-08 02:16 | 4:26 | 35.0542 | 31.6545 | 33.1084 | 36.4824 | 34.3569 | 33.9719 | 34.8332 | 35.4729 | 36.5575 | 37.3607 | 36.8105 | 37.8098 | 34.3558 | 34.3715 | 34.3207 | 35.1993 | 35.3586 | 35.903 | 36.6562 | 36.7966 | 34.9589 | 31.6897 | 92.8419 | 35.4077 | 33.3018 | 35.1134 | 33.5769 | 33.3469 | 33.622 | 35.0374 | 34.4707 | 34.2107 | 37.2313 | 36.2725 | 33.6373 | 34.4333 | 36.2615 | 36.6165 | 37.4691 | 36.2446 | 33.6101 | 32.8699 | 34.7134 | 35.0913 | 33.29 | 34.3666 | 34.3407 | 34.411 | 34.4169 | 34.4454 | 34.37 | 33.9439 | 34.4298 | 35.653 | 35.318 | 36.035 | 35.9998 | 33.6211 | 93.351 | 93.5043 | 93.0483
2022-09-08 02:16 | 4:26 | 35.0966 | 31.694 | 33.1852 | 36.4244 | 34.3462 | 33.9807 | 34.843 | 35.4736 | 36.5481 | 37.3725 | 36.7824 | 37.8069 | 34.3766 | 34.3544 | 34.3208 | 35.2027 | 35.3422 | 35.923 | 36.6449 | 36.7939 | 34.9894 | 31.6927 | 92.9357 | 35.4614 | 33.284 | 35.1159 | 33.5826 | 33.3555 | 33.6319 | 35.0499 | 34.4593 | 34.2253 | 37.2434 | 36.2505 | 33.6353 | 34.4476 | 36.2615 | 36.6035 | 37.4572 | 36.2585 | 33.6007 | 32.8644 | 34.7205 | 35.0971 | 33.3148 | 34.366 | 34.3325 | 34.3903 | 34.4185 | 34.4384 | 34.3598 | 33.9604 | 34.4169 | 35.6407 | 35.3234 | 36.0293 | 35.9893 | 33.6247 | 93.2863 | 93.4584 | 93.1087
2022-09-08 02:17 | 4:26 | 35.1721 | 31.7063 | 33.1913 | 36.4928 | 34.3559 | 33.9752 | 34.8241 | 35.4796 | 36.5578 | 37.3696 | 36.7966 | 37.8103 | 34.3529 | 34.3497 | 34.3112 | 35.1971 | 35.3494 | 35.9191 | 36.6624 | 36.7951 | 35.0301 | 31.6879 | 92.8358 | 35.4497 | 33.2981 | 35.1178 | 33.5772 | 33.3473 | 33.6288 | 35.0397 | 34.4837 | 34.2105 | 37.2406 | 36.2652 | 33.6234 | 34.4399 | 36.2725 | 36.6201 | 37.471 | 36.2583 | 33.5907 | 32.8772 | 34.7428 | 35.0904 | 33.2972 | 34.355 | 34.334 | 34.3847 | 34.4361 | 34.4509 | 34.3728 | 33.9493 | 34.4185 | 35.6654 | 35.3265 | 36.0449 | 36.0213 | 33.6424 | 93.2298 | 93.3819 | 92.9305
2022-09-08 02:17 | 4:27 | 35.2166 | 31.7139 | 33.2851 | 36.4963 | 34.3773 | 33.9717 | 34.8387 | 35.4789 | 36.5606 | 37.3701 | 36.803 | 37.8123 | 34.3656 | 34.3436 | 34.3192 | 35.2055 | 35.3406 | 35.9415 | 36.6658 | 36.7743 | 35.0468 | 31.6943 | 92.8442 | 35.4541 | 33.294 | 35.1177 | 33.5917 | 33.3652 | 33.645 | 35.0533 | 34.4763 | 34.2048 | 37.2495 | 36.2613 | 33.6322 | 34.4592 | 36.2505 | 36.6189 | 37.4904 | 36.2615 | 33.5855 | 32.8874 | 34.7279 | 35.1228 | 33.3167 | 34.3646 | 34.3285 | 34.3867 | 34.4201 | 34.4368 | 34.3541 | 33.9629 | 34.4361 | 35.6454 | 35.3239 | 36.0266 | 36.0024 | 33.6314 | 93.1373 | 93.2871 | 93.0116
2022-09-08 02:17 | 4:27 | 35.2952 | 31.7281 | 33.3798 | 36.464 | 34.3603 | 33.9855 | 34.8197 | 35.4603 | 36.5745 | 37.3792 | 36.8023 | 37.8231 | 34.3706 | 34.3677 | 34.3265 | 35.2188 | 35.3382 | 35.938 | 36.6593 | 36.7968 | 35.0941 | 31.7028 | 92.7422 | 35.4905 | 33.2891 | 35.1281 | 33.6101 | 33.3546 | 33.6373 | 35.0518 | 34.4671 | 34.2134 | 37.2429 | 36.2786 | 33.6578 | 34.4553 | 36.2652 | 36.628 | 37.4727 | 36.2615 | 33.587 | 32.8985 | 34.7335 | 35.1073 | 33.3373 | 34.3808 | 34.3383 | 34.3794 | 34.4205 | 34.4566 | 34.3684 | 33.9551 | 34.4201 | 35.6629 | 35.3123 | 36.0254 | 36.015 | 33.6481 | 93.0549 | 93.2154 | 92.8458
2022-09-08 02:17 | 4:27 | 35.342 | 31.7368 | 33.5722 | 36.4933 | 34.3519 | 33.974 | 34.8421 | 35.4693 | 36.5665 | 37.3755 | 36.8169 | 37.8309 | 34.3792 | 34.3647 | 34.3195 | 35.2017 | 35.3391 | 35.9292 | 36.676 | 36.8088 | 35.1088 | 31.716 | 92.6992 | 35.4792 | 33.3186 | 35.125 | 33.6007 | 33.3509 | 33.6353 | 35.052 | 34.4715 | 34.2084 | 37.2482 | 36.2749 | 33.6417 | 34.4565 | 36.2613 | 36.6234 | 37.4778 | 36.2725 | 33.6039 | 32.8804 | 34.7449 | 35.1177 | 33.34 | 34.3791 | 34.3337 | 34.3867 | 34.4312 | 34.4528 | 34.3537 | 33.9733 | 34.4205 | 35.6635 | 35.3222 | 36.04 | 36.006 | 33.6537 | 92.9761 | 93.1276 | 92.883
2022-09-08 02:17 | 4:27 | 35.3596 | 31.7642 | 33.5964 | 36.544 | 34.3494 | 33.993 | 34.841 | 35.4791 | 36.5416 | 37.3796 | 36.8153 | 37.8253 | 34.3865 | 34.3769 | 34.3342 | 35.2037 | 35.3482 | 35.9138 | 36.6805 | 36.8058 | 34.9373 | 31.6466 | 92.7065 | 35.5448 | 33.3006 | 35.127 | 33.5907 | 33.3565 | 33.6234 | 35.0283 | 34.4737 | 34.2106 | 37.2558 | 36.2774 | 33.6501 | 34.4597 | 36.2786 | 36.6303 | 37.4855 | 36.2505 | 33.5983 | 32.9013 | 34.7563 | 35.1251 | 33.3216 | 34.3903 | 34.323 | 34.3824 | 34.4222 | 34.4496 | 34.3535 | 33.9703 | 34.4312 | 35.6754 | 35.3449 | 36.0162 | 36.0035 | 33.6463 | 92.8742 | 93.0658 | 92.8326
2022-09-08 02:17 | 4:27 | 31.1887 | 31.3327 | 32.9562 | 36.541 | 34.3616 | 33.9978 | 34.8205 | 35.4696 | 36.544 | 37.3741 | 36.8246 | 37.8135 | 34.3806 | 34.3774 | 34.3541 | 35.2321 | 35.3545 | 35.9519 | 36.6691 | 36.804 | 30.6074 | 31.5133 | 92.7114 | 35.4466 | 33.3176 | 35.1365 | 33.5855 | 33.3602 | 33.6322 | 35.0749 | 34.4739 | 34.2205 | 37.2599 | 36.2792 | 33.6442 | 34.4648 | 36.2749 | 36.6318 | 37.4764 | 36.2652 | 33.611 | 32.9194 | 34.7844 | 35.1258 | 33.3523 | 34.3563 | 34.3129 | 34.369 | 34.4228 | 34.4403 | 34.3607 | 33.9721 | 34.4222 | 35.663 | 35.3325 | 36.0343 | 36.0062 | 33.6561 | 92.8606 | 93.0605 | 92.8243
2022-09-08 02:18 | 4:28 | 30.2875 | 29.6905 | 32.1408 | 36.5132 | 34.3484 | 33.98 | 34.8554 | 35.4794 | 36.5557 | 37.3901 | 36.7993 | 37.8152 | 34.3863 | 34.3715 | 34.3349 | 35.208 | 35.3639 | 35.9282 | 36.6765 | 36.7958 | 28.3355 | 31.1045 | 92.6878 | 35.5039 | 33.3055 | 35.1109 | 33.587 | 33.3713 | 33.6578 | 35.0432 | 34.4684 | 34.193 | 37.2409 | 36.2692 | 33.6488 | 34.4564 | 36.2774 | 36.6258 | 37.5033 | 36.2613 | 33.5959 | 32.9182 | 34.7805 | 35.1387 | 33.3476 | 34.3596 | 34.3253 | 34.3826 | 34.4155 | 34.4414 | 34.36 | 33.9808 | 34.4228 | 35.6808 | 35.3376 | 36.0535 | 36.0188 | 33.6692 | 92.7903 | 93.0327 | 92.768
2022-09-08 02:18 | 4:28 | 31.2102 | 27.813 | 31.7278 | 36.499 | 34.3568 | 33.9721 | 34.8615 | 35.4858 | 36.5537 | 37.3796 | 36.8115 | 37.8206 | 34.392 | 34.3838 | 34.335 | 35.2062 | 35.3574 | 35.9397 | 36.6741 | 36.8159 | 28.6725 | 30.8793 | 92.6757 | 35.4756 | 33.3172 | 35.1552 | 33.6039 | 33.3715 | 33.6417 | 35.0578 | 34.484 | 34.2242 | 37.2421 | 36.2872 | 33.6465 | 34.4513 | 36.2792 | 36.6156 | 37.4867 | 36.2786 | 33.6114 | 32.9306 | 34.777 | 35.1389 | 33.3587 | 34.3643 | 34.3222 | 34.3901 | 34.4156 | 34.4326 | 34.3436 | 33.9792 | 34.4155 | 35.6559 | 35.3192 | 36.0385 | 36.0272 | 33.6492 | 92.7773 | 92.9827 | 92.7181
2022-09-08 02:18 | 4:28 | 30.5605 | 27.6825 | 31.247 | 36.4478 | 34.3324 | 33.9774 | 34.8439 | 35.48 | 36.5591 | 37.3809 | 36.805 | 37.8322 | 34.3833 | 34.3832 | 34.3422 | 35.2203 | 35.36 | 35.9306 | 36.6691 | 36.7982 | 29.089 | 30.8643 | 92.7324 | 35.385 | 33.3068 | 35.1585 | 33.5983 | 33.3713 | 33.6501 | 35.039 | 34.4896 | 34.217 | 37.2457 | 36.2857 | 33.6373 | 34.4654 | 36.2692 | 36.6107 | 37.4822 | 36.2749 | 33.614 | 32.9252 | 34.7826 | 35.1403 | 33.3695 | 34.3538 | 34.3077 | 34.3802 | 34.4286 | 34.458 | 34.3616 | 33.9719 | 34.4156 | 35.6643 | 35.3226 | 36.042 | 36.0173 | 33.6689 | 92.7903 | 92.9573 | 92.7065
2022-09-08 02:18 | 4:28 | 24.1539 | 27.4684 | 29.5475 | 36.3451 | 34.3554 | 33.9908 | 34.8514 | 35.4889 | 36.5665 | 37.3887 | 36.8053 | 37.8258 | 34.3823 | 34.3645 | 34.3413 | 35.1882 | 35.3641 | 35.9391 | 36.6573 | 36.7942 | 29.525 | 30.8791 | 92.5985 | 35.524 | 33.3148 | 35.1573 | 33.611 | 33.3681 | 33.6442 | 35.0496 | 34.4881 | 34.2169 | 37.2489 | 36.2887 | 33.632 | 34.4552 | 36.2872 | 36.6265 | 37.4836 | 36.2774 | 33.6009 | 32.9219 | 34.7799 | 35.1635 | 33.3728 | 34.3796 | 34.3097 | 34.3905 | 34.4215 | 34.4617 | 34.3513 | 33.9873 | 34.4286 | 35.6705 | 35.308 | 36.0231 | 36.0048 | 33.6564 | 92.6797 | 92.8753 | 92.5789
2022-09-08 02:18 | 4:28 | 22.4944 | 26.69 | 28.4239 | 36.2809 | 34.3674 | 33.9844 | 34.8396 | 35.4796 | 36.566 | 37.3896 | 36.813 | 37.8406 | 34.4017 | 34.396 | 34.3494 | 35.2118 | 35.3578 | 35.9381 | 36.6669 | 36.8166 | 29.9362 | 30.9639 | 92.4894 | 35.557 | 33.3226 | 35.1483 | 33.5959 | 33.3706 | 33.6488 | 35.0575 | 34.4764 | 34.2292 | 37.2365 | 36.2877 | 33.6371 | 34.4854 | 36.2857 | 36.6372 | 37.4899 | 36.2792 | 33.6043 | 32.9453 | 34.8056 | 35.1496 | 33.3763 | 34.3631 | 34.2916 | 34.3869 | 34.4055 | 34.4287 | 34.3606 | 33.9912 | 34.4215 | 35.6889 | 35.3331 | 36.0656 | 36.03 | 33.6811 | 92.5918 | 92.7732 | 92.4975
2022-09-08 02:18 | 4:28 | 23.589 | 26.2053 | 27.8644 | 36.0949 | 34.3575 | 33.987 | 34.8414 | 35.4715 | 36.579 | 37.3815 | 36.8182 | 37.8321 | 34.3862 | 34.3882 | 34.3571 | 35.1992 | 35.3411 | 35.9396 | 36.6713 | 36.8369 | 30.8085 | 28.3991 | 92.5107 | 35.4611 | 33.3213 | 35.1499 | 33.6114 | 33.3668 | 33.6465 | 35.0451 | 34.4847 | 34.2174 | 37.2521 | 36.2709 | 33.6504 | 34.4639 | 36.2887 | 36.623 | 37.4979 | 36.2692 | 33.6063 | 32.9496 | 34.8054 | 35.1939 | 33.3963 | 34.3827 | 34.3064 | 34.3754 | 34.4186 | 34.4475 | 34.3507 | 33.9676 | 34.4055 | 35.6987 | 35.3347 | 36.0643 | 36.0351 | 33.6812 | 92.466 | 92.6721 | 92.5218
2022-09-08 02:19 | 4:28 | 24.9655 | 26.4051 | 28.288 | 36.1743 | 34.353 | 33.9851 | 34.8164 | 35.4856 | 36.5974 | 37.3831 | 36.816 | 37.8342 | 34.3773 | 34.3826 | 34.3477 | 35.2206 | 35.3702 | 35.9138 | 36.6479 | 36.8046 | 30.2648 | 27.4798 | 92.4122 | 35.3291 | 33.3311 | 35.1572 | 33.614 | 33.3861 | 33.6373 | 35.0545 | 34.488 | 34.2071 | 37.2587 | 36.3025 | 33.6652 | 34.4735 | 36.2877 | 36.6299 | 37.512 | 36.2872 | 33.6026 | 32.9569 | 34.7949 | 35.1756 | 33.3802 | 34.3615 | 34.3171 | 34.3833 | 34.4088 | 34.4374 | 34.36 | 33.9987 | 34.4186 | 35.7143 | 35.3081 | 36.0617 | 36.0411 | 33.6736 | 92.3836 | 92.6056 | 92.3813
2022-09-08 02:19 | 4:29 | 25.1669 | 26.3936 | 28.1689 | 36.1652 | 34.3742 | 33.9851 | 34.8161 | 35.4697 | 36.5774 | 37.3871 | 36.8318 | 37.8383 | 34.4033 | 34.3866 | 34.3458 | 35.2025 | 35.3677 | 35.9448 | 36.6843 | 36.8104 | 29.6493 | 26.6122 | 92.323 | 35.3577 | 33.3235 | 35.1615 | 33.6009 | 33.3607 | 33.632 | 35.0358 | 34.4855 | 34.226 | 37.2484 | 36.2942 | 33.6467 | 34.4693 | 36.2709 | 36.6231 | 37.4988 | 36.2857 | 33.5865 | 32.9455 | 34.8115 | 35.1875 | 33.4025 | 34.3912 | 34.304 | 34.3724 | 34.4159 | 34.4538 | 34.357 | 34.007 | 34.4088 | 35.7011 | 35.3281 | 36.0376 | 36.0438 | 33.6807 | 92.2634 | 92.487 | 92.2974
2022-09-08 02:19 | 4:29 | 24.9862 | 25.9093 | 27.9754 | 36.0824 | 34.3594 | 33.9787 | 34.8246 | 35.4721 | 36.5766 | 37.3877 | 36.8118 | 37.8534 | 34.4073 | 34.3785 | 34.3412 | 35.2029 | 35.3671 | 35.9177 | 36.6616 | 36.8233 | 29.6276 | 25.8442 | 92.2274 | 35.2672 | 33.3315 | 35.1372 | 33.6043 | 33.3666 | 33.6371 | 35.0351 | 34.4897 | 34.2194 | 37.2759 | 36.3147 | 33.6561 | 34.4714 | 36.3025 | 36.6486 | 37.4977 | 36.2887 | 33.6103 | 32.9736 | 34.7966 | 35.1956 | 33.4118 | 34.3688 | 34.3302 | 34.3781 | 34.4246 | 34.4558 | 34.3604 | 34.0186 | 34.4159 | 35.71 | 35.3453 | 36.0637 | 36.0366 | 33.7049 | 92.1484 | 92.3338 | 92.2538
2022-09-08 02:19 | 4:29 | 24.6578 | 25.68 | 27.7704 | 36.0993 | 34.3448 | 33.9736 | 34.8397 | 35.4755 | 36.577 | 37.4072 | 36.8279 | 37.8523 | 34.4149 | 34.3945 | 34.3494 | 35.2202 | 35.3702 | 35.9273 | 36.6723 | 36.8143 | 29.6364 | 25.3975 | 92.2261 | 35.3152 | 33.3119 | 35.1442 | 33.6063 | 33.3824 | 33.6504 | 35.0618 | 34.4823 | 34.2214 | 37.2713 | 36.3181 | 33.6487 | 34.4728 | 36.2942 | 36.6479 | 37.5053 | 36.2877 | 33.6067 | 32.9777 | 34.8021 | 35.1805 | 33.3965 | 34.3942 | 34.3257 | 34.3773 | 34.4184 | 34.4425 | 34.3585 | 33.9721 | 34.4246 | 35.6956 | 35.3056 | 36.0496 | 36.0267 | 33.6805 | 92.0292 | 92.1525 | 92.2233
2022-09-08 02:19 | 4:29 | 24.5069 | 25.5592 | 27.5735 | 36.1412 | 34.3777 | 33.9792 | 34.8318 | 35.4713 | 36.6004 | 37.3799 | 36.8144 | 37.8263 | 34.408 | 34.3847 | 34.3601 | 35.2174 | 35.372 | 35.9327 | 36.6503 | 36.8249 | 29.4965 | 25.1216 | 92.1131 | 35.2514 | 33.3167 | 35.1653 | 33.6026 | 33.3661 | 33.6652 | 35.0455 | 34.4629 | 34.2293 | 37.2665 | 36.3045 | 33.6477 | 34.4473 | 36.3147 | 36.642 | 37.5272 | 36.2709 | 33.6122 | 32.9539 | 34.8188 | 35.2006 | 33.4062 | 34.4051 | 34.3133 | 34.3834 | 34.4199 | 34.4436 | 34.3602 | 33.9973 | 34.4184 | 35.7197 | 35.3218 | 36.0523 | 36.0572 | 33.6901 | 91.9074 | 92.0708 | 92.0043
2022-09-08 02:19 | 4:29 | 24.4305 | 25.4832 | 27.5788 | 36.0695 | 34.367 | 33.9842 | 34.8466 | 35.4966 | 36.5896 | 37.4036 | 36.8327 | 37.8475 | 34.4058 | 34.397 | 34.3408 | 35.2293 | 35.3802 | 35.9309 | 36.6513 | 36.8276 | 29.3119 | 24.9564 | 92.0726 | 35.1351 | 33.3355 | 35.1578 | 33.5865 | 33.3669 | 33.6467 | 35.0444 | 34.4707 | 34.2177 | 37.276 | 36.3069 | 33.6455 | 34.4614 | 36.3181 | 36.6349 | 37.5155 | 36.3025 | 33.6107 | 32.9669 | 34.8032 | 35.1823 | 33.3968 | 34.3891 | 34.3169 | 34.3858 | 34.4174 | 34.435 | 34.3558 | 34.0053 | 34.4199 | 35.7215 | 35.334 | 36.0567 | 36.0436 | 33.686 | 91.8319 | 91.9982 | 91.9786
2022-09-08 02:20 | 4:30 | 24.3152 | 25.3239 | 27.4388 | 36.0299 | 34.3611 | 33.9864 | 34.8344 | 35.4769 | 36.584 | 37.3992 | 36.8279 | 37.8573 | 34.4159 | 34.3948 | 34.3507 | 35.2049 | 35.3826 | 35.936 | 36.6656 | 36.8287 | 29.1126 | 24.7956 | 92.0519 | 35.1654 | 33.3274 | 35.1553 | 33.6103 | 33.3806 | 33.6561 | 35.0414 | 34.4731 | 34.2392 | 37.2884 | 36.3084 | 33.6503 | 34.4701 | 36.3045 | 36.6311 | 37.5018 | 36.2942 | 33.6 | 32.9862 | 34.819 | 35.2105 | 33.4176 | 34.3939 | 34.2931 | 34.3911 | 34.4156 | 34.4296 | 34.369 | 34.0361 | 34.4174 | 35.7112 | 35.3248 | 36.0764 | 36.0368 | 33.712 | 91.8462 | 92.011 | 91.9802
2022-09-08 02:20 | 4:30 | 24.2301 | 25.1936 | 27.2074 | 36.0899 | 34.3637 | 33.9667 | 34.8465 | 35.496 | 36.6017 | 37.3955 | 36.8202 | 37.8491 | 34.4064 | 34.3973 | 34.3566 | 35.2058 | 35.3871 | 35.9119 | 36.6561 | 36.8152 | 28.8611 | 24.6554 | 92.1575 | 35.1057 | 33.3298 | 35.1795 | 33.6067 | 33.3729 | 33.6487 | 35.0411 | 34.4689 | 34.2216 | 37.2835 | 36.3098 | 33.6648 | 34.4361 | 36.3069 | 36.6164 | 37.5225 | 36.3147 | 33.611 | 32.9815 | 34.8261 | 35.2205 | 33.3994 | 34.4034 | 34.3144 | 34.3682 | 34.4161 | 34.456 | 34.3595 | 34.0194 | 34.4156 | 35.7156 | 35.3277 | 36.0538 | 36.0477 | 33.6925 | 91.9026 | 92.086 | 92.0984
2022-09-08 02:20 | 4:30 | 24.159 | 25.0498 | 27.173 | 36.0788 | 34.3526 | 33.9758 | 34.8384 | 35.4749 | 36.5932 | 37.3799 | 36.8207 | 37.8416 | 34.4028 | 34.3962 | 34.3559 | 35.2324 | 35.373 | 35.8975 | 36.653 | 36.8224 | 28.6388 | 24.4868 | 92.2453 | 35.1028 | 33.3186 | 35.1472 | 33.6122 | 33.3717 | 33.6477 | 35.054 | 34.4816 | 34.245 | 37.2818 | 36.308 | 33.6481 | 34.4605 | 36.3084 | 36.6391 | 37.5243 | 36.3181 | 33.6214 | 32.9663 | 34.827 | 35.1962 | 33.3969 | 34.3994 | 34.304 | 34.3718 | 34.3989 | 34.4484 | 34.3511 | 34.0251 | 34.4161 | 35.7245 | 35.3331 | 36.0553 | 36.0498 | 33.7181 | 92.0293 | 92.1918 | 92.2132
2022-09-08 02:20 | 4:30 | 24.0574 | 24.9174 | 27.0271 | 36.021 | 34.3495 | 33.9703 | 34.8249 | 35.475 | 36.6075 | 37.3857 | 36.8254 | 37.857 | 34.4004 | 34.4005 | 34.3586 | 35.2055 | 35.3925 | 35.9127 | 36.6458 | 36.8241 | 28.3917 | 24.3207 | 92.2672 | 35.0789 | 33.3049 | 35.1731 | 33.6107 | 33.3684 | 33.6455 | 35.0662 | 34.4731 | 34.2242 | 37.2681 | 36.3019 | 33.6333 | 34.4614 | 36.3098 | 36.6345 | 37.5242 | 36.3045 | 33.6208 | 32.9927 | 34.8224 | 35.2199 | 33.388 | 34.3919 | 34.3186 | 34.3734 | 34.4235 | 34.4498 | 34.3678 | 34.0436 | 34.3989 | 35.7498 | 35.3313 | 36.0387 | 36.0587 | 33.6873 | 92.0989 | 92.3593 | 92.2831
2022-09-08 02:20 | 4:30 | 24.0144 | 24.7518 | 26.8912 | 35.9812 | 34.3526 | 33.9654 | 34.8526 | 35.4822 | 36.5943 | 37.384 | 36.8111 | 37.8371 | 34.3999 | 34.3961 | 34.347 | 35.2234 | 35.377 | 35.9096 | 36.643 | 36.8098 | 28.1762 | 24.184 | 92.2887 | 35.0761 | 33.319 | 35.1513 | 33.6 | 33.3768 | 33.6503 | 35.0391 | 34.4796 | 34.2338 | 37.2837 | 36.3076 | 33.6584 | 34.4635 | 36.308 | 36.632 | 37.519 | 36.3069 | 33.5959 | 32.997 | 34.8222 | 35.2098 | 33.3882 | 34.3947 | 34.3119 | 34.3861 | 34.3951 | 34.4566 | 34.3485 | 34.0174 | 34.4235 | 35.714 | 35.297 | 36.0712 | 36.0506 | 33.6893 | 92.1955 | 92.4624 | 92.3645
2022-09-08 02:20 | 4:30 | 23.8008 | 24.6049 | 26.7218 | 35.9538 | 34.3604 | 33.957 | 34.8743 | 35.4725 | 36.5939 | 37.3884 | 36.8236 | 37.8388 | 34.4069 | 34.4038 | 34.3423 | 35.2082 | 35.3724 | 35.9221 | 36.6484 | 36.8395 | 27.9058 | 24.0048 | 92.3915 | 35.0865 | 33.3311 | 35.1502 | 33.611 | 33.3595 | 33.6648 | 35.0412 | 34.4671 | 34.2304 | 37.276 | 36.3147 | 33.6251 | 34.4749 | 36.3019 | 36.6179 | 37.5258 | 36.3084 | 33.6047 | 33.0132 | 34.8147 | 35.1994 | 33.3933 | 34.4015 | 34.3025 | 34.3814 | 34.4199 | 34.4573 | 34.3715 | 34.0254 | 34.3951 | 35.7122 | 35.3214 | 36.0695 | 36.0781 | 33.7038 | 92.3843 | 92.5791 | 92.4467
2022-09-08 02:21 | 4:30 | 23.6835 | 24.4103 | 26.6416 | 35.9567 | 34.3449 | 33.9665 | 34.8402 | 35.4835 | 36.6048 | 37.3816 | 36.8177 | 37.8347 | 34.4079 | 34.3986 | 34.3543 | 35.2122 | 35.3736 | 35.9079 | 36.6436 | 36.8226 | 27.6614 | 23.8702 | 92.4715 | 35.016 | 33.321 | 35.1442 | 33.6214 | 33.3659 | 33.6481 | 35.0556 | 34.4758 | 34.2179 | 37.2654 | 36.3 | 33.6585 | 34.4377 | 36.3076 | 36.6482 | 37.5292 | 36.3098 | 33.6077 | 32.9716 | 34.8167 | 35.2109 | 33.393 | 34.3819 | 34.3256 | 34.3775 | 34.4204 | 34.4673 | 34.3544 | 34.0073 | 34.4199 | 35.725 | 35.3293 | 36.0682 | 36.0591 | 33.7101 | 92.4692 | 92.7405 | 92.5512
2022-09-08 02:21 | 4:31 | 23.5387 | 24.291 | 26.5477 | 35.929 | 34.3454 | 33.9667 | 34.8401 | 35.4842 | 36.5907 | 37.3655 | 36.8095 | 37.845 | 34.414 | 34.3906 | 34.3677 | 35.2115 | 35.3842 | 35.9046 | 36.6329 | 36.8228 | 27.4692 | 23.7339 | 92.616 | 34.961 | 33.3108 | 35.1606 | 33.6208 | 33.3581 | 33.6333 | 35.0493 | 34.4702 | 34.2192 | 37.2374 | 36.3037 | 33.6421 | 34.4525 | 36.3147 | 36.6445 | 37.5424 | 36.308 | 33.5913 | 32.986 | 34.8105 | 35.1974 | 33.3961 | 34.3962 | 34.308 | 34.392 | 34.3865 | 34.4607 | 34.3497 | 34.0329 | 34.4204 | 35.7194 | 35.3168 | 36.0585 | 36.0558 | 33.72 | 92.652 | 92.8851 | 92.6635
2022-09-08 02:21 | 4:31 | 23.394 | 24.142 | 26.3614 | 35.9493 | 34.3481 | 33.9557 | 34.8337 | 35.4631 | 36.6095 | 37.3851 | 36.8173 | 37.8386 | 34.4321 | 34.4128 | 34.3527 | 35.206 | 35.3783 | 35.897 | 36.6354 | 36.8191 | 27.2591 | 23.5859 | 92.7127 | 34.8636 | 33.3326 | 35.1405 | 33.5959 | 33.3472 | 33.6584 | 35.041 | 34.461 | 34.2193 | 37.2514 | 36.2926 | 33.6376 | 34.4473 | 36.3 | 36.6237 | 37.5449 | 36.3019 | 33.6153 | 33.0138 | 34.8212 | 35.2084 | 33.3963 | 34.4025 | 34.3271 | 34.3765 | 34.415 | 34.4703 | 34.3436 | 34.0339 | 34.3865 | 35.7337 | 35.3268 | 36.0669 | 36.0462 | 33.6978 | 92.7764 | 93.0017 | 92.7335
2022-09-08 02:21 | 4:31 | 23.2835 | 23.9912 | 26.2452 | 35.9534 | 34.37 | 33.9562 | 34.8359 | 35.4905 | 36.6124 | 37.3901 | 36.7973 | 37.8299 | 34.4082 | 34.416 | 34.3586 | 35.2109 | 35.3861 | 35.9149 | 36.6421 | 36.8116 | 27.0207 | 23.4622 | 92.7348 | 34.8831 | 33.2893 | 35.171 | 33.6047 | 33.3387 | 33.6251 | 35.0421 | 34.4677 | 34.2253 | 37.2634 | 36.3066 | 33.6282 | 34.4478 | 36.3037 | 36.6265 | 37.53 | 36.3076 | 33.6115 | 33.0122 | 34.8004 | 35.2097 | 33.3995 | 34.4213 | 34.3227 | 34.3869 | 34.4065 | 34.4463 | 34.3677 | 34.0131 | 34.415 | 35.7312 | 35.3283 | 36.0547 | 36.0369 | 33.7129 | 92.9039 | 93.1725 | 92.7609
2022-09-08 02:21 | 4:31 | 23.1723 | 23.893 | 26.1184 | 35.9416 | 34.3598 | 33.9542 | 34.8209 | 35.4957 | 36.5816 | 37.3711 | 36.8109 | 37.8124 | 34.4182 | 34.4246 | 34.3438 | 35.2019 | 35.3734 | 35.8856 | 36.6143 | 36.8333 | 26.7126 | 23.3385 | 92.82 | 34.8776 | 33.304 | 35.1551 | 33.6077 | 33.3503 | 33.6585 | 35.0647 | 34.465 | 34.214 | 37.2599 | 36.2917 | 33.6376 | 34.4451 | 36.2926 | 36.6364 | 37.5296 | 36.3147 | 33.6001 | 32.9772 | 34.8162 | 35.2257 | 33.3941 | 34.4119 | 34.3273 | 34.3803 | 34.3895 | 34.4606 | 34.3647 | 34.0312 | 34.4065 | 35.7131 | 35.3323 | 36.0629 | 36.0775 | 33.7103 | 92.9892 | 93.2943 | 92.8155
2022-09-08 02:21 | 4:31 | 22.9998 | 23.7297 | 26.023 | 35.8312 | 34.3728 | 33.9526 | 34.8335 | 35.4748 | 36.5994 | 37.3728 | 36.8073 | 37.8362 | 34.4147 | 34.4275 | 34.3637 | 35.2077 | 35.3813 | 35.9102 | 36.6206 | 36.8327 | 26.3954 | 23.1935 | 92.8657 | 34.8159 | 33.3141 | 35.1505 | 33.5913 | 33.3483 | 33.6421 | 35.0512 | 34.4479 | 34.2199 | 37.267 | 36.3143 | 33.6433 | 34.4319 | 36.3066 | 36.6319 | 37.5316 | 36.3 | 33.6054 | 32.9851 | 34.8041 | 35.2067 | 33.3919 | 34.4074 | 34.3233 | 34.3792 | 34.3977 | 34.4605 | 34.3769 | 34.0306 | 34.3895 | 35.7174 | 35.3346 | 36.065 | 36.0558 | 33.6943 | 93.1332 | 93.4705 | 92.9671
2022-09-08 02:22 | 4:32 | 22.8983 | 23.5543 | 25.9505 | 35.853 | 34.3541 | 33.9554 | 34.8373 | 35.4912 | 36.6038 | 37.3884 | 36.8061 | 37.8291 | 34.4103 | 34.4067 | 34.3398 | 35.2201 | 35.3861 | 35.8981 | 36.6111 | 36.8384 | 26.1324 | 23.0465 | 92.9837 | 34.7914 | 33.2975 | 35.1511 | 33.6153 | 33.336 | 33.6376 | 35.0378 | 34.4563 | 34.2049 | 37.2676 | 36.2835 | 33.647 | 34.4436 | 36.2917 | 36.632 | 37.5402 | 36.3037 | 33.5932 | 32.9708 | 34.7866 | 35.1957 | 33.3695 | 34.4132 | 34.3017 | 34.3854 | 34.3806 | 34.4524 | 34.3774 | 34.0242 | 34.3977 | 35.7516 | 35.307 | 36.0694 | 36.0621 | 33.6996 | 93.3067 | 93.6025 | 93.1047
2022-09-08 02:22 | 4:32 | 22.7202 | 23.3688 | 25.7816 | 35.8194 | 34.3684 | 33.9475 | 34.8365 | 35.4819 | 36.5947 | 37.3929 | 36.7977 | 37.8142 | 34.4113 | 34.4096 | 34.3682 | 35.1975 | 35.3794 | 35.9002 | 36.6175 | 36.8261 | 25.8953 | 22.8889 | 93.0367 | 34.7679 | 33.3179 | 35.1559 | 33.6115 | 33.3295 | 33.6282 | 35.0587 | 34.4621 | 34.2139 | 37.274 | 36.3047 | 33.6251 | 34.4408 | 36.3143 | 36.6209 | 37.5331 | 36.2926 | 33.6087 | 32.967 | 34.7863 | 35.2036 | 33.3729 | 34.4166 | 34.3313 | 34.3719 | 34.3956 | 34.4588 | 34.3715 | 34.04 | 34.3806 | 35.7194 | 35.3058 | 36.0603 | 36.0821 | 33.6962 | 93.381 | 93.769 | 93.1686
2022-09-08 02:22 | 4:32 | 22.6563 | 23.2704 | 25.6708 | 35.8344 | 34.3537 | 33.9593 | 34.8322 | 35.4676 | 36.6054 | 37.3856 | 36.8065 | 37.8305 | 34.4163 | 34.4138 | 34.3421 | 35.2097 | 35.3738 | 35.8863 | 36.623 | 36.8229 | 25.5811 | 22.7137 | 93.2069 | 34.7182 | 33.309 | 35.1529 | 33.6001 | 33.3377 | 33.6376 | 35.0419 | 34.453 | 34.212 | 37.2567 | 36.3184 | 33.6415 | 34.428 | 36.2835 | 36.6241 | 37.5442 | 36.3066 | 33.6035 | 32.9832 | 34.8052 | 35.2021 | 33.3624 | 34.4133 | 34.3329 | 34.3863 | 34.3714 | 34.4566 | 34.3838 | 34.0304 | 34.3956 | 35.7155 | 35.3109 | 36.0571 | 36.0644 | 33.7041 | 93.6064 | 93.9582 | 93.2961
2022-09-08 02:22 | 4:32 | 22.3845 | 23.0382 | 25.5313 | 35.7963 | 34.3535 | 33.9573 | 34.8299 | 35.4708 | 36.5924 | 37.3802 | 36.7784 | 37.8287 | 34.4302 | 34.4143 | 34.3846 | 35.2045 | 35.3959 | 35.8922 | 36.5899 | 36.8308 | 25.1602 | 22.4998 | 93.3372 | 34.6458 | 33.3113 | 35.1457 | 33.6054 | 33.3244 | 33.6433 | 35.047 | 34.4365 | 34.2024 | 37.2605 | 36.2966 | 33.6412 | 34.4376 | 36.3047 | 36.6243 | 37.5193 | 36.2917 | 33.6294 | 32.9749 | 34.7833 | 35.1976 | 33.3568 | 34.421 | 34.3225 | 34.3726 | 34.3959 | 34.4531 | 34.3832 | 34.0274 | 34.3714 | 35.7478 | 35.3143 | 36.0675 | 36.0686 | 33.7165 | 93.7621 | 94.1662 | 93.452
2022-09-08 02:22 | 4:32 | 22.2881 | 22.9363 | 25.4162 | 35.8005 | 34.3607 | 33.944 | 34.8498 | 35.4873 | 36.6002 | 37.3973 | 36.8058 | 37.8156 | 34.4363 | 34.4023 | 34.3471 | 35.1992 | 35.3638 | 35.891 | 36.6045 | 36.8306 | 24.8093 | 22.3806 | 93.4863 | 34.66 | 33.303 | 35.1391 | 33.5932 | 33.3145 | 33.647 | 35.0554 | 34.4352 | 34.2045 | 37.2454 | 36.3205 | 33.6352 | 34.4372 | 36.3184 | 36.634 | 37.5337 | 36.3143 | 33.5994 | 32.983 | 34.7758 | 35.1887 | 33.3518 | 34.4104 | 34.313 | 34.3944 | 34.3591 | 34.4613 | 34.3645 | 34.0475 | 34.3959 | 35.7238 | 35.3298 | 36.0844 | 36.0497 | 33.6801 | 93.9091 | 94.3492 | 93.5703
2022-09-08 02:22 | 4:32 | 22.1711 | 22.8323 | 25.2786 | 35.7875 | 34.36 | 33.9472 | 34.8353 | 35.4681 | 36.6043 | 37.3838 | 36.7952 | 37.846 | 34.4237 | 34.4117 | 34.3605 | 35.1871 | 35.3824 | 35.8798 | 36.6034 | 36.8373 | 24.4296 | 22.1991 | 93.5884 | 34.5689 | 33.2983 | 35.1491 | 33.6087 | 33.3162 | 33.6251 | 35.057 | 34.4515 | 34.2109 | 37.2628 | 36.2934 | 33.6302 | 34.4389 | 36.2966 | 36.6269 | 37.5279 | 36.2835 | 33.6103 | 32.9554 | 34.7676 | 35.2075 | 33.3655 | 34.4134 | 34.3182 | 34.385 | 34.3593 | 34.4599 | 34.396 | 34.031 | 34.3591 | 35.7298 | 35.3004 | 36.0705 | 36.0546 | 33.6767 | 94.1218 | 94.5469 | 93.714
2022-09-08 02:23 | 4:32 | 21.9487 | 22.6615 | 25.1253 | 35.7777 | 34.3436 | 33.9462 | 34.8395 | 35.4734 | 36.6176 | 37.3868 | 36.8065 | 37.816 | 34.4293 | 34.4269 | 34.3583 | 35.1858 | 35.3969 | 35.9138 | 36.6059 | 36.82 | 24.0943 | 22.0052 | 93.692 | 34.5808 | 33.3061 | 35.1523 | 33.6035 | 33.3326 | 33.6415 | 35.0411 | 34.443 | 34.2108 | 37.2608 | 36.309 | 33.6335 | 34.4486 | 36.3205 | 36.6134 | 37.5284 | 36.3047 | 33.6231 | 32.955 | 34.7738 | 35.1897 | 33.3547 | 34.4025 | 34.338 | 34.3849 | 34.3825 | 34.4566 | 34.3882 | 34.0401 | 34.3593 | 35.7199 | 35.3168 | 36.0751 | 36.0559 | 33.6943 | 94.2733 | 94.7067 | 93.7499
2022-09-08 02:23 | 4:33 | 21.8322 | 22.4873 | 24.9935 | 35.6104 | 34.3616 | 33.953 | 34.849 | 35.4693 | 36.612 | 37.3857 | 36.7809 | 37.8023 | 34.4425 | 34.4253 | 34.3505 | 35.1999 | 35.38 | 35.8794 | 36.5981 | 36.8163 | 23.7754 | 21.7879 | 93.8249 | 34.4099 | 33.3052 | 35.1514 | 33.6294 | 33.318 | 33.6412 | 35.0448 | 34.4392 | 34.2171 | 37.2547 | 36.3149 | 33.6332 | 34.45 | 36.2934 | 36.6054 | 37.5348 | 36.3184 | 33.6069 | 32.9577 | 34.7648 | 35.1788 | 33.3536 | 34.4135 | 34.3344 | 34.4131 | 34.3662 | 34.4399 | 34.3826 | 34.0299 | 34.3825 | 35.7308 | 35.3162 | 36.0711 | 36.069 | 33.6935 | 94.4082 | 94.9133 | 93.9391
2022-09-08 02:23 | 4:33 | 21.6976 | 22.3813 | 24.8389 | 35.6984 | 34.3513 | 33.948 | 34.8389 | 35.4578 | 36.6069 | 37.367 | 36.794 | 37.8194 | 34.4411 | 34.4159 | 34.3444 | 35.2064 | 35.382 | 35.8871 | 36.6046 | 36.8222 | 23.4595 | 21.6155 | 93.8831 | 34.386 | 33.3068 | 35.1416 | 33.5994 | 33.2923 | 33.6352 | 35.0254 | 34.4608 | 34.2144 | 37.2782 | 36.2994 | 33.6259 | 34.4323 | 36.309 | 36.6278 | 37.5207 | 36.2966 | 33.6015 | 32.9646 | 34.7693 | 35.1776 | 33.3502 | 34.4239 | 34.3374 | 34.394 | 34.3616 | 34.4585 | 34.3866 | 34.0154 | 34.3662 | 35.7244 | 35.312 | 36.0794 | 36.0528 | 33.6686 | 94.5964 | 95.0276 | 94.0523
2022-09-08 02:23 | 4:33 | 21.5075 | 22.1924 | 24.7077 | 35.6413 | 34.3606 | 33.9541 | 34.8235 | 35.4618 | 36.5978 | 37.365 | 36.782 | 37.8165 | 34.424 | 34.4239 | 34.3443 | 35.1995 | 35.3745 | 35.8805 | 36.5788 | 36.8068 | 23.1892 | 21.4607 | 93.9663 | 34.5288 | 33.3143 | 35.1365 | 33.6103 | 33.3019 | 33.6302 | 35.0365 | 34.4449 | 34.1894 | 37.2558 | 36.3086 | 33.6335 | 34.4179 | 36.3149 | 36.624 | 37.5468 | 36.3205 | 33.608 | 32.9617 | 34.7737 | 35.1744 | 33.3556 | 34.4111 | 34.3303 | 34.3927 | 34.3556 | 34.4658 | 34.3785 | 34.024 | 34.3616 | 35.7229 | 35.3038 | 36.082 | 36.0398 | 33.6809 | 94.727 | 95.1974 | 94.147
2022-09-08 02:23 | 4:33 | 21.4082 | 22.0701 | 24.5871 | 35.7289 | 34.3507 | 33.9292 | 34.8228 | 35.486 | 36.6054 | 37.3871 | 36.8071 | 37.8379 | 34.44 | 34.4084 | 34.3382 | 35.1925 | 35.3803 | 35.8942 | 36.5855 | 36.8196 | 22.9299 | 21.1898 | 94.0408 | 34.462 | 33.2878 | 35.1535 | 33.6231 | 33.3104 | 33.6335 | 35.0347 | 34.4304 | 34.1786 | 37.2604 | 36.3113 | 33.6277 | 34.4246 | 36.2994 | 36.6221 | 37.534 | 36.2934 | 33.6275 | 32.9491 | 34.7605 | 35.1777 | 33.3387 | 34.4036 | 34.3228 | 34.4089 | 34.3568 | 34.4669 | 34.3945 | 34.0227 | 34.3556 | 35.721 | 35.3068 | 36.076 | 36.0347 | 33.6856 | 94.8948 | 95.301 | 94.2403
2022-09-08 02:23 | 4:33 | 21.2644 | 21.9384 | 24.4253 | 35.6014 | 34.36 | 33.9268 | 34.827 | 35.4767 | 36.6154 | 37.3623 | 36.8117 | 37.8339 | 34.4454 | 34.4261 | 34.3526 | 35.1821 | 35.3836 | 35.8712 | 36.5853 | 36.8051 | 22.7107 | 21.0397 | 94.131 | 34.4815 | 33.2895 | 35.1514 | 33.6069 | 33.2843 | 33.6332 | 35.0304 | 34.4249 | 34.1966 | 37.2563 | 36.3056 | 33.6454 | 34.422 | 36.3086 | 36.6065 | 37.544 | 36.309 | 33.6179 | 32.9408 | 34.751 | 35.1606 | 33.3319 | 34.4305 | 34.3372 | 34.4066 | 34.3491 | 34.4386 | 34.3847 | 34.0439 | 34.3568 | 35.7014 | 35.3105 | 36.0744 | 36.0455 | 33.6703 | 95.0491 | 95.4433 | 94.3392
2022-09-08 02:24 | 4:34 | 21.0982 | 21.8023 | 24.3128 | 35.6641 | 34.357 | 33.9426 | 34.8308 | 35.4562 | 36.6078 | 37.3683 | 36.7762 | 37.8275 | 34.4384 | 34.4365 | 34.3515 | 35.2012 | 35.3725 | 35.8933 | 36.5722 | 36.8124 | 22.5764 | 20.8463 | 94.2258 | 34.3572 | 33.2938 | 35.1438 | 33.6015 | 33.2777 | 33.6259 | 35.0333 | 34.426 | 34.1891 | 37.2516 | 36.3047 | 33.6228 | 34.4303 | 36.3113 | 36.6118 | 37.532 | 36.3149 | 33.6054 | 32.9454 | 34.7545 | 35.163 | 33.3351 | 34.4159 | 34.3556 | 34.4207 | 34.3578 | 34.4348 | 34.397 | 34.0311 | 34.3491 | 35.732 | 35.3105 | 36.0673 | 36.0517 | 33.6666 | 95.0673 | 95.5195 | 94.3991
2022-09-08 02:24 | 4:34 | 21.1792 | 21.7132 | 24.1117 | 35.5607 | 34.3604 | 33.9194 | 34.8252 | 35.4854 | 36.6209 | 37.3693 | 36.7856 | 37.8246 | 34.4509 | 34.4316 | 34.3462 | 35.1956 | 35.3725 | 35.866 | 36.5743 | 36.8045 | 22.4524 | 20.6551 | 94.3131 | 34.3629 | 33.2802 | 35.1472 | 33.608 | 33.2843 | 33.6335 | 35.0371 | 34.4276 | 34.1932 | 37.2487 | 36.321 | 33.6161 | 34.4257 | 36.3056 | 36.6089 | 37.5303 | 36.2994 | 33.6001 | 32.9467 | 34.7402 | 35.158 | 33.333 | 34.4245 | 34.3421 | 34.409 | 34.3323 | 34.4526 | 34.3948 | 34.0304 | 34.3578 | 35.6955 | 35.3206 | 36.0738 | 36.0429 | 33.6691 | 95.1602 | 95.5621 | 94.3774
2022-09-08 02:24 | 4:34 | 20.8805 | 21.5428 | 23.9994 | 35.5754 | 34.3585 | 33.9327 | 34.8318 | 35.4642 | 36.5954 | 37.3725 | 36.7873 | 37.8317 | 34.4368 | 34.4185 | 34.3308 | 35.2064 | 35.3646 | 35.8624 | 36.5764 | 36.79 | 22.3614 | 20.4645 | 94.3237 | 34.2179 | 33.2918 | 35.1537 | 33.6275 | 33.2914 | 33.6277 | 35.0263 | 34.4496 | 34.2182 | 37.2608 | 36.3222 | 33.6304 | 34.4238 | 36.3047 | 36.6166 | 37.5225 | 36.3086 | 33.6142 | 32.9481 | 34.7433 | 35.1517 | 33.3226 | 34.4136 | 34.3439 | 34.411 | 34.3552 | 34.4639 | 34.3973 | 34.0235 | 34.3323 | 35.7102 | 35.3042 | 36.0647 | 36.0534 | 33.6625 | 95.1596 | 95.609 | 94.3989
2022-09-08 02:24 | 4:34 | 20.7376 | 21.4536 | 23.9328 | 35.5632 | 34.3602 | 33.9442 | 34.8136 | 35.4745 | 36.6093 | 37.3509 | 36.8039 | 37.8255 | 34.4566 | 34.4278 | 34.3401 | 35.203 | 35.3834 | 35.8556 | 36.5543 | 36.8099 | 22.3013 | 20.312 | 94.198 | 34.2665 | 33.2797 | 35.1521 | 33.6179 | 33.2643 | 33.6454 | 35.0409 | 34.4282 | 34.1896 | 37.2673 | 36.3098 | 33.6156 | 34.4245 | 36.321 | 36.6041 | 37.5107 | 36.3113 | 33.5927 | 32.931 | 34.734 | 35.1395 | 33.3259 | 34.4269 | 34.3364 | 34.4179 | 34.3319 | 34.4518 | 34.3962 | 34.0294 | 34.3552 | 35.7167 | 35.3077 | 36.0563 | 36.046 | 33.6589 | 95.0224 | 95.4805 | 94.3003
2022-09-08 02:24 | 4:34 | 20.5472 | 21.2252 | 23.8292 | 35.5197 | 34.3558 | 33.934 | 34.8222 | 35.4598 | 36.5819 | 37.3521 | 36.7824 | 37.8401 | 34.4528 | 34.4263 | 34.338 | 35.189 | 35.3913 | 35.8646 | 36.5668 | 36.7944 | 22.2243 | 20.1651 | 94.0718 | 34.1755 | 33.2949 | 35.1477 | 33.6054 | 33.2991 | 33.6228 | 35.0154 | 34.4297 | 34.2049 | 37.256 | 36.323 | 33.6249 | 34.4144 | 36.3222 | 36.6091 | 37.5247 | 36.3056 | 33.5971 | 32.9242 | 34.7115 | 35.1429 | 33.3193 | 34.4188 | 34.3341 | 34.3964 | 34.3425 | 34.4512 | 34.4005 | 34.0319 | 34.3319 | 35.7271 | 35.2894 | 36.0799 | 36.0381 | 33.6655 | 94.7051 | 95.2063 | 94.0974
2022-09-08 02:24 | 4:34 | 20.4577 | 21.1762 | 23.7342 | 35.5823 | 34.369 | 33.9394 | 34.8297 | 35.4576 | 36.6155 | 37.3459 | 36.7861 | 37.83 | 34.4496 | 34.4305 | 34.3522 | 35.1882 | 35.3861 | 35.829 | 36.5504 | 36.7773 | 22.1774 | 20.0091 | 93.9677 | 34.153 | 33.2631 | 35.1571 | 33.6001 | 33.2828 | 33.6161 | 35.0183 | 34.4324 | 34.1956 | 37.2479 | 36.2854 | 33.6343 | 34.4221 | 36.3098 | 36.5947 | 37.5196 | 36.3047 | 33.6031 | 32.9289 | 34.7243 | 35.1545 | 33.3081 | 34.4209 | 34.3359 | 34.4229 | 34.3407 | 34.4588 | 34.3961 | 34.0123 | 34.3425 | 35.6974 | 35.2947 | 36.0768 | 36.0504 | 33.6604 | 94.5296 | 95.0262 | 93.9596
2022-09-08 02:25 | 4:34 | 20.4605 | 21.1109 | 23.6762 | 35.5267 | 34.3595 | 33.9277 | 34.806 | 35.4759 | 36.5977 | 37.3623 | 36.7997 | 37.8324 | 34.4403 | 34.4318 | 34.3278 | 35.192 | 35.3923 | 35.8634 | 36.5412 | 36.7829 | 22.1543 | 19.8909 | 93.8985 | 34.0907 | 33.2888 | 35.1394 | 33.6142 | 33.2781 | 33.6304 | 35.0164 | 34.432 | 34.1895 | 37.2665 | 36.3184 | 33.6309 | 34.4254 | 36.323 | 36.6167 | 37.5016 | 36.321 | 33.5984 | 32.9102 | 34.704 | 35.1305 | 33.3027 | 34.4249 | 34.3354 | 34.4296 | 34.3325 | 34.4357 | 34.4038 | 34.0088 | 34.3407 | 35.6913 | 35.3181 | 36.0746 | 36.0722 | 33.6536 | 94.3666 | 94.7769 | 93.9043
2022-09-08 02:25 | 4:35 | 20.2076 | 20.9331 | 23.5395 | 35.3614 | 34.3511 | 33.9337 | 34.8064 | 35.4533 | 36.6006 | 37.3281 | 36.8071 | 37.8215 | 34.4414 | 34.438 | 34.3406 | 35.1794 | 35.3565 | 35.8496 | 36.5504 | 36.783 | 22.1403 | 19.757 | 93.7255 | 33.9368 | 33.2749 | 35.1739 | 33.5927 | 33.2765 | 33.6156 | 34.9992 | 34.4386 | 34.1718 | 37.2434 | 36.304 | 33.6113 | 34.4215 | 36.2854 | 36.6041 | 37.5126 | 36.3222 | 33.5975 | 32.9354 | 34.6939 | 35.1456 | 33.2997 | 34.4249 | 34.3367 | 34.4419 | 34.334 | 34.4351 | 34.3986 | 34.0334 | 34.3325 | 35.7024 | 35.2857 | 36.0733 | 36.0404 | 33.6525 | 94.2344 | 94.5915 | 93.7199
2022-09-08 02:25 | 4:35 | 20.2304 | 20.8632 | 23.3704 | 35.4642 | 34.3678 | 33.9252 | 34.8173 | 35.4462 | 36.5823 | 37.3456 | 36.7916 | 37.8092 | 34.4326 | 34.4235 | 34.3367 | 35.1722 | 35.3812 | 35.8553 | 36.5306 | 36.7853 | 22.1109 | 19.7578 | 93.7393 | 34.1586 | 33.2768 | 35.1781 | 33.5971 | 33.2777 | 33.6249 | 35.0271 | 34.425 | 34.1894 | 37.2548 | 36.3264 | 33.625 | 34.4236 | 36.3184 | 36.6051 | 37.4982 | 36.3098 | 33.6084 | 32.9133 | 34.6987 | 35.1184 | 33.2765 | 34.4237 | 34.3326 | 34.44 | 34.3285 | 34.4514 | 34.3906 | 34.0164 | 34.334 | 35.6996 | 35.3105 | 36.0584 | 36.0399 | 33.6435 | 94.1258 | 94.5036 | 93.7072
2022-09-08 02:25 | 4:35 | 20.0951 | 20.774 | 23.3043 | 35.3624 | 34.3485 | 33.9474 | 34.828 | 35.4533 | 36.6057 | 37.34 | 36.7762 | 37.8455 | 34.458 | 34.4273 | 34.3299 | 35.1967 | 35.3714 | 35.844 | 36.5286 | 36.7941 | 22.0962 | 19.5724 | 93.6782 | 34.1175 | 33.268 | 35.1751 | 33.6031 | 33.2779 | 33.6343 | 35.0142 | 34.4537 | 34.1874 | 37.2408 | 36.324 | 33.6175 | 34.4182 | 36.304 | 36.5988 | 37.4876 | 36.323 | 33.6171 | 32.9207 | 34.6891 | 35.1272 | 33.2861 | 34.412 | 34.3327 | 34.4337 | 34.3383 | 34.4522 | 34.4128 | 34.0064 | 34.3285 | 35.7009 | 35.3106 | 36.0802 | 36.0325 | 33.6458 | 94.0214 | 94.3756 | 93.6311
2022-09-08 02:25 | 4:35 | 19.9765 | 20.6401 | 23.1844 | 35.4759 | 34.3715 | 33.948 | 34.7904 | 35.4641 | 36.5894 | 37.3088 | 36.7904 | 37.8051 | 34.4617 | 34.4287 | 34.333 | 35.181 | 35.3598 | 35.8255 | 36.5292 | 36.7724 | 22.0625 | 19.417 | 93.664 | 34.0611 | 33.2651 | 35.1676 | 33.5984 | 33.2698 | 33.6309 | 35.0148 | 34.4346 | 34.1869 | 37.2585 | 36.3524 | 33.6234 | 34.4317 | 36.3264 | 36.5751 | 37.5022 | 36.2854 | 33.6154 | 32.8967 | 34.6648 | 35.1043 | 33.2932 | 34.4337 | 34.3509 | 34.4416 | 34.3337 | 34.4491 | 34.416 | 34.0154 | 34.3383 | 35.7017 | 35.3104 | 36.0632 | 36.0366 | 33.6379 | 93.9821 | 94.2712 | 93.7373
2022-09-08 02:25 | 4:35 | 19.9409 | 20.5607 | 23.1669 | 35.2588 | 34.3544 | 33.9282 | 34.8014 | 35.4354 | 36.5873 | 37.3289 | 36.7809 | 37.8252 | 34.4287 | 34.4297 | 34.3291 | 35.1666 | 35.382 | 35.8241 | 36.5117 | 36.7673 | 22.0526 | 19.3991 | 93.6341 | 34.102 | 33.2641 | 35.1522 | 33.5975 | 33.2827 | 33.6113 | 35.0118 | 34.4225 | 34.1825 | 37.2552 | 36.3042 | 33.6111 | 34.4194 | 36.324 | 36.6083 | 37.4867 | 36.3184 | 33.6153 | 32.9032 | 34.6702 | 35.1064 | 33.2844 | 34.4367 | 34.3416 | 34.456 | 34.323 | 34.4293 | 34.4246 | 34.0252 | 34.3337 | 35.7053 | 35.31 | 36.065 | 36.0538 | 33.6353 | 93.8686 | 94.1733 | 93.5834
2022-09-08 02:26 | 4:35 | 19.763 | 20.4497 | 23.0067 | 35.3012 | 34.3497 | 33.9332 | 34.81 | 35.4462 | 36.6027 | 37.3233 | 36.7827 | 37.8214 | 34.4475 | 34.4286 | 34.3268 | 35.19 | 35.3796 | 35.8312 | 36.5279 | 36.7662 | 22.0066 | 19.2844 | 93.569 | 34.0895 | 33.2484 | 35.1556 | 33.6084 | 33.2849 | 33.625 | 35.0134 | 34.4289 | 34.1972 | 37.2649 | 36.3312 | 33.6114 | 34.4419 | 36.3524 | 36.5979 | 37.4944 | 36.304 | 33.6009 | 32.8969 | 34.6686 | 35.1135 | 33.2647 | 34.4328 | 34.3402 | 34.4223 | 34.3129 | 34.4311 | 34.4275 | 34.0093 | 34.323 | 35.6858 | 35.3067 | 36.0727 | 36.0238 | 33.6392 | 93.8514 | 94.1058 | 93.5942
2022-09-08 02:26 | 4:36 | 19.7146 | 20.3681 | 22.9118 | 35.3131 | 34.3436 | 33.9408 | 34.802 | 35.4551 | 36.5945 | 37.3101 | 36.7981 | 37.8291 | 34.4374 | 34.4217 | 34.2987 | 35.1932 | 35.3515 | 35.8305 | 36.5283 | 36.7524 | 21.9897 | 19.1759 | 93.6116 | 33.9688 | 33.266 | 35.1798 | 33.6171 | 33.2781 | 33.6175 | 34.9904 | 34.424 | 34.1935 | 37.2604 | 36.3189 | 33.6221 | 34.4156 | 36.3042 | 36.584 | 37.4755 | 36.3264 | 33.5877 | 32.8858 | 34.6622 | 35.104 | 33.2772 | 34.4064 | 34.3494 | 34.4529 | 34.3253 | 34.4192 | 34.4067 | 34.0139 | 34.3129 | 35.709 | 35.3034 | 36.0588 | 36.0388 | 33.6301 | 93.8912 | 94.0725 | 93.6436
2022-09-08 02:26 | 4:36 | 19.615 | 20.232 | 22.807 | 35.286 | 34.3677 | 33.9318 | 34.7916 | 35.4539 | 36.6039 | 37.3183 | 36.8033 | 37.836 | 34.4538 | 34.4325 | 34.3295 | 35.1924 | 35.3677 | 35.8267 | 36.5245 | 36.755 | 21.9438 | 19.0876 | 93.5593 | 34.0515 | 33.2781 | 35.1608 | 33.6154 | 33.2651 | 33.6234 | 34.9945 | 34.4133 | 34.1777 | 37.2529 | 36.3269 | 33.6113 | 34.4348 | 36.3312 | 36.605 | 37.4965 | 36.324 | 33.597 | 32.8785 | 34.6366 | 35.1188 | 33.264 | 34.4295 | 34.3382 | 34.4382 | 34.3222 | 34.4235 | 34.4096 | 33.9982 | 34.3253 | 35.6954 | 35.2938 | 36.0735 | 36.0629 | 33.6262 | 93.7868 | 94.044 | 93.52
2022-09-08 02:26 | 4:36 | 19.4915 | 20.1276 | 22.7507 | 35.3445 | 34.3647 | 33.9248 | 34.7879 | 35.4453 | 36.5918 | 37.3317 | 36.8036 | 37.8299 | 34.4558 | 34.4243 | 34.3093 | 35.207 | 35.3857 | 35.8265 | 36.5047 | 36.7645 | 21.8998 | 19.0077 | 93.5886 | 33.867 | 33.2709 | 35.1763 | 33.6153 | 33.2644 | 33.6111 | 34.9818 | 34.4471 | 34.1861 | 37.2407 | 36.3206 | 33.6112 | 34.4632 | 36.3189 | 36.6022 | 37.4935 | 36.3524 | 33.6273 | 32.8787 | 34.654 | 35.1042 | 33.2761 | 34.4129 | 34.3397 | 34.4355 | 34.3077 | 34.4295 | 34.4138 | 34.0112 | 34.3222 | 35.7039 | 35.3207 | 36.0702 | 36.0436 | 33.6437 | 93.7626 | 94.003 | 93.5792
2022-09-08 02:26 | 4:36 | 19.4501 | 20.0936 | 22.6835 | 35.1384 | 34.3769 | 33.9347 | 34.7996 | 35.4467 | 36.5994 | 37.3286 | 36.8011 | 37.8174 | 34.4425 | 34.4221 | 34.3255 | 35.1886 | 35.3881 | 35.8145 | 36.5108 | 36.7665 | 21.8646 | 18.9123 | 93.5412 | 33.9579 | 33.2635 | 35.1896 | 33.6009 | 33.2666 | 33.6114 | 34.9849 | 34.4458 | 34.2066 | 37.2642 | 36.3344 | 33.6008 | 34.4416 | 36.3269 | 36.5891 | 37.4872 | 36.3042 | 33.6225 | 32.8651 | 34.6439 | 35.1093 | 33.2664 | 34.4178 | 34.3627 | 34.4299 | 34.3097 | 34.4147 | 34.4143 | 34.0082 | 34.3077 | 35.6985 | 35.3174 | 36.0739 | 36.0476 | 33.63 | 93.7662 | 93.9148 | 93.5067
2022-09-08 02:26 | 4:36 | 19.4832 | 20.0582 | 22.6118 | 35.2882 | 34.3774 | 33.9533 | 34.7918 | 35.4479 | 36.5857 | 37.3243 | 36.8102 | 37.8358 | 34.4436 | 34.4357 | 34.3302 | 35.2036 | 35.3618 | 35.8321 | 36.5137 | 36.747 | 21.8592 | 18.9236 | 93.416 | 33.8388 | 33.2567 | 35.1772 | 33.5877 | 33.2652 | 33.6221 | 34.9831 | 34.4303 | 34.193 | 37.2576 | 36.3272 | 33.5919 | 34.4444 | 36.3206 | 36.6004 | 37.504 | 36.3312 | 33.6043 | 32.8639 | 34.652 | 35.1343 | 33.2662 | 34.4223 | 34.3474 | 34.443 | 34.2916 | 34.4111 | 34.4023 | 34.0088 | 34.3097 | 35.6889 | 35.3067 | 36.0728 | 36.0256 | 33.6334 | 93.6584 | 93.8602 | 93.3676
2022-09-08 02:27 | 4:37 | 19.3244 | 19.9668 | 22.5637 | 35.2677 | 34.3715 | 33.9535 | 34.8018 | 35.4354 | 36.5772 | 37.316 | 36.8074 | 37.8375 | 34.435 | 34.442 | 34.3002 | 35.2062 | 35.3871 | 35.8241 | 36.5242 | 36.7689 | 21.8215 | 18.8178 | 93.4408 | 33.7104 | 33.2771 | 35.1746 | 33.597 | 33.2599 | 33.6113 | 34.9852 | 34.4349 | 34.2019 | 37.2593 | 36.3301 | 33.6084 | 34.4326 | 36.3344 | 36.5986 | 37.4697 | 36.3189 | 33.6174 | 32.8544 | 34.655 | 35.1004 | 33.2591 | 34.4268 | 34.3434 | 34.4311 | 34.3064 | 34.4196 | 34.4117 | 33.9966 | 34.2916 | 35.6955 | 35.2959 | 36.0834 | 36.0349 | 33.6077 | 93.59 | 93.7607 | 93.3756
2022-09-08 02:27 | 4:37 | 19.2016 | 19.8198 | 22.5159 | 35.1504 | 34.3838 | 33.9434 | 34.7874 | 35.4583 | 36.5951 | 37.3392 | 36.8338 | 37.8439 | 34.4296 | 34.4356 | 34.3224 | 35.1981 | 35.3958 | 35.8249 | 36.5114 | 36.7497 | 21.7746 | 18.7774 | 93.4213 | 33.8236 | 33.2514 | 35.166 | 33.6273 | 33.2494 | 33.6112 | 34.9926 | 34.4307 | 34.2002 | 37.2637 | 36.3166 | 33.607 | 34.4329 | 36.3272 | 36.6008 | 37.4981 | 36.3269 | 33.6215 | 32.8669 | 34.6334 | 35.1104 | 33.259 | 34.4336 | 34.3519 | 34.4389 | 34.3171 | 34.4169 | 34.4269 | 34.0108 | 34.3064 | 35.6901 | 35.3115 | 36.087 | 36.0455 | 33.6179 | 93.4798 | 93.6952 | 93.3475
2022-09-08 02:27 | 4:37 | 19.1612 | 19.7502 | 22.4085 | 35.1586 | 34.3832 | 33.9468 | 34.7953 | 35.453 | 36.6024 | 37.3287 | 36.8226 | 37.8376 | 34.456 | 34.4194 | 34.3131 | 35.2001 | 35.3737 | 35.8179 | 36.5082 | 36.7461 | 21.7314 | 18.6494 | 93.3019 | 33.7452 | 33.2435 | 35.1794 | 33.6225 | 33.2533 | 33.6008 | 34.983 | 34.4535 | 34.1986 | 37.2684 | 36.3372 | 33.6208 | 34.4515 | 36.3301 | 36.5907 | 37.4843 | 36.3206 | 33.6045 | 32.8597 | 34.6397 | 35.1063 | 33.2508 | 34.4344 | 34.3529 | 34.4469 | 34.304 | 34.4227 | 34.4253 | 34.0242 | 34.3171 | 35.7025 | 35.2979 | 36.0752 | 36.0461 | 33.6409 | 93.3962 | 93.5802 | 93.1928
2022-09-08 02:27 | 4:37 | 19.0715 | 19.6893 | 22.272 | 35.1525 | 34.3645 | 33.9461 | 34.7829 | 35.4482 | 36.6067 | 37.3097 | 36.8155 | 37.8401 | 34.4484 | 34.4393 | 34.3286 | 35.1742 | 35.3885 | 35.8224 | 36.5104 | 36.7686 | 21.7078 | 18.5844 | 93.2606 | 33.6243 | 33.2467 | 35.1694 | 33.6043 | 33.2669 | 33.5919 | 34.9823 | 34.4458 | 34.2163 | 37.2773 | 36.3198 | 33.6013 | 34.4342 | 36.3166 | 36.6226 | 37.5041 | 36.3344 | 33.6098 | 32.8493 | 34.6157 | 35.1007 | 33.2423 | 34.4054 | 34.3565 | 34.4404 | 34.3302 | 34.4045 | 34.4159 | 34.013 | 34.304 | 35.6987 | 35.3064 | 36.1018 | 36.0609 | 33.6431 | 93.3031 | 93.5102 | 93.151
2022-09-08 02:27 | 4:37 | 19.0237 | 19.6103 | 22.2563 | 35.1307 | 34.396 | 33.9349 | 34.8081 | 35.4564 | 36.6012 | 37.3391 | 36.8349 | 37.8568 | 34.4498 | 34.4234 | 34.3045 | 35.1889 | 35.3698 | 35.8291 | 36.5244 | 36.7517 | 21.6506 | 18.4846 | 93.197 | 33.7714 | 33.2544 | 35.1674 | 33.6174 | 33.2684 | 33.6084 | 34.9703 | 34.4544 | 34.1983 | 37.2593 | 36.3239 | 33.6004 | 34.4275 | 36.3372 | 36.6005 | 37.475 | 36.3272 | 33.6308 | 32.8802 | 34.6335 | 35.1011 | 33.24 | 34.42 | 34.3655 | 34.4671 | 34.3257 | 34.4023 | 34.4239 | 33.9921 | 34.3302 | 35.7039 | 35.3118 | 36.1019 | 36.0672 | 33.6257 | 93.194 | 93.4167 | 93.0786
2022-09-08 02:27 | 4:37 | 18.9904 | 19.547 | 22.2142 | 35.0423 | 34.3882 | 33.9444 | 34.8011 | 35.4565 | 36.5731 | 37.3172 | 36.8257 | 37.8391 | 34.4566 | 34.4298 | 34.3156 | 35.1936 | 35.388 | 35.8329 | 36.5055 | 36.7697 | 21.6328 | 18.4639 | 93.1997 | 33.8774 | 33.2532 | 35.1705 | 33.6215 | 33.2668 | 33.607 | 34.9731 | 34.4507 | 34.212 | 37.2563 | 36.3222 | 33.6035 | 34.4462 | 36.3198 | 36.6123 | 37.4821 | 36.3301 | 33.6082 | 32.8663 | 34.6221 | 35.0944 | 33.2443 | 34.4248 | 34.347 | 34.4465 | 34.3133 | 34.4059 | 34.4084 | 34.0044 | 34.3257 | 35.6901 | 35.3262 | 36.093 | 36.0672 | 33.6382 | 93.1903 | 93.35 | 93.1616
2022-09-08 02:28 | 4:37 | 18.8904 | 19.4477 | 22.1771 | 35.0872 | 34.3826 | 33.9392 | 34.7999 | 35.4522 | 36.5939 | 37.3215 | 36.8244 | 37.8503 | 34.4573 | 34.4169 | 34.3242 | 35.2 | 35.3741 | 35.8266 | 36.4905 | 36.7433 | 21.6045 | 18.3851 | 93.1535 | 33.6999 | 33.2273 | 35.1771 | 33.6045 | 33.2586 | 33.6208 | 34.9943 | 34.4406 | 34.2053 | 37.273 | 36.3232 | 33.6018 | 34.4414 | 36.3239 | 36.5979 | 37.4797 | 36.3166 | 33.6339 | 32.8292 | 34.6403 | 35.1162 | 33.2284 | 34.4016 | 34.3498 | 34.465 | 34.3169 | 34.3945 | 34.4261 | 34.0159 | 34.3133 | 35.7013 | 35.3036 | 36.0809 | 36.0509 | 33.6255 | 93.1585 | 93.268 | 93.1336
2022-09-08 02:28 | 4:38 | 18.7912 | 19.3912 | 22.0753 | 35.1817 | 34.3866 | 33.9298 | 34.8091 | 35.4511 | 36.6205 | 37.3203 | 36.8219 | 37.8446 | 34.4673 | 34.4185 | 34.3219 | 35.2076 | 35.3835 | 35.8334 | 36.498 | 36.7475 | 21.5665 | 18.3585 | 93.0365 | 33.7461 | 33.245 | 35.1751 | 33.6098 | 33.2579 | 33.6013 | 34.9734 | 34.4662 | 34.2213 | 37.2716 | 36.3279 | 33.5991 | 34.4595 | 36.3222 | 36.6178 | 37.4901 | 36.3372 | 33.6126 | 32.8499 | 34.6224 | 35.0863 | 33.225 | 34.4262 | 34.3728 | 34.471 | 34.2931 | 34.3932 | 34.4365 | 34.0042 | 34.3169 | 35.6926 | 35.3148 | 36.1028 | 36.0446 | 33.6274 | 93.0329 | 93.1535 | 92.9819
2022-09-08 02:28 | 4:38 | 18.7963 | 19.3141 | 21.9968 | 35.1262 | 34.3785 | 33.9515 | 34.7968 | 35.4592 | 36.5951 | 37.3193 | 36.8269 | 37.8478 | 34.4607 | 34.4361 | 34.309 | 35.1938 | 35.4007 | 35.8204 | 36.4997 | 36.7636 | 21.5574 | 18.2447 | 92.894 | 33.7105 | 33.267 | 35.171 | 33.6308 | 33.2747 | 33.6004 | 34.9681 | 34.4545 | 34.2239 | 37.2719 | 36.3047 | 33.6025 | 34.4373 | 36.3232 | 36.6015 | 37.4849 | 36.3198 | 33.5984 | 32.8398 | 34.6197 | 35.1018 | 33.2304 | 34.4062 | 34.3644 | 34.4436 | 34.3144 | 34.3857 | 34.4316 | 34.0057 | 34.2931 | 35.7017 | 35.2948 | 36.0911 | 36.0562 | 33.6319 | 92.8461 | 93.0378 | 92.8635
2022-09-08 02:28 | 4:38 | 18.6902 | 19.268 | 21.9368 | 34.951 | 34.3945 | 33.9397 | 34.777 | 35.4526 | 36.601 | 37.3157 | 36.836 | 37.8688 | 34.4703 | 34.4201 | 34.3349 | 35.2076 | 35.3831 | 35.8223 | 36.4933 | 36.7614 | 21.5043 | 18.1851 | 92.8241 | 33.6036 | 33.2498 | 35.1827 | 33.6082 | 33.2515 | 33.6035 | 34.9667 | 34.466 | 34.1933 | 37.2701 | 36.3227 | 33.5991 | 34.4415 | 36.3279 | 36.6005 | 37.4889 | 36.3239 | 33.6288 | 32.8542 | 34.6188 | 35.0879 | 33.2102 | 34.4174 | 34.3415 | 34.4717 | 34.304 | 34.3916 | 34.4185 | 33.9959 | 34.3144 | 35.7154 | 35.3204 | 36.0889 | 36.0518 | 33.6487 | 92.7155 | 92.9279 | 92.722
2022-09-08 02:28 | 4:38 | 18.6179 | 19.1625 | 21.8693 | 35.0598 | 34.3847 | 33.9457 | 34.8018 | 35.4543 | 36.6077 | 37.3152 | 36.8255 | 37.8512 | 34.4463 | 34.4205 | 34.3151 | 35.2122 | 35.3823 | 35.7974 | 36.4915 | 36.7526 | 21.5005 | 18.1756 | 92.8303 | 33.5439 | 33.24 | 35.171 | 33.6339 | 33.2694 | 33.6018 | 34.9761 | 34.4517 | 34.2139 | 37.2536 | 36.3394 | 33.5984 | 34.4481 | 36.3047 | 36.5969 | 37.4923 | 36.3222 | 33.6171 | 32.8283 | 34.6339 | 35.09 | 33.221 | 34.4225 | 34.3632 | 34.4547 | 34.3186 | 34.3824 | 34.4278 | 34.0056 | 34.304 | 35.7223 | 35.3276 | 36.075 | 36.0448 | 33.639 | 92.6635 | 92.7722 | 92.7235
2022-09-08 02:28 | 4:38 | 18.5966 | 19.1279 | 21.7848 | 34.9369 | 34.397 | 33.9521 | 34.7939 | 35.4599 | 36.5952 | 37.3267 | 36.8347 | 37.8554 | 34.4606 | 34.4312 | 34.3116 | 35.1921 | 35.3831 | 35.8115 | 36.4853 | 36.7607 | 21.4591 | 18.1012 | 92.6653 | 33.7481 | 33.2419 | 35.162 | 33.6126 | 33.2564 | 33.5991 | 34.9832 | 34.4609 | 34.1962 | 37.2717 | 36.3398 | 33.616 | 34.4386 | 36.3227 | 36.6037 | 37.4783 | 36.3232 | 33.6131 | 32.8415 | 34.6276 | 35.0816 | 33.2079 | 34.3985 | 34.3614 | 34.459 | 34.3119 | 34.4062 | 34.4263 | 34.0202 | 34.3186 | 35.7191 | 35.3104 | 36.0999 | 36.0618 | 33.631 | 92.4484 | 92.622 | 92.5626
2022-09-08 02:29 | 4:39 | 18.5851 | 19.096 | 21.7298 | 35.1145 | 34.3948 | 33.9531 | 34.7942 | 35.4568 | 36.6073 | 37.3293 | 36.8302 | 37.8419 | 34.4605 | 34.4222 | 34.3212 | 35.2101 | 35.3776 | 35.8204 | 36.4896 | 36.7543 | 21.422 | 18.0345 | 92.5851 | 33.5171 | 33.2536 | 35.1837 | 33.5984 | 33.2454 | 33.6025 | 34.9713 | 34.4501 | 34.2147 | 37.2657 | 36.3049 | 33.6015 | 34.4392 | 36.3394 | 36.5984 | 37.4819 | 36.3279 | 33.6076 | 32.8334 | 34.6178 | 35.1002 | 33.1886 | 34.4203 | 34.3662 | 34.4436 | 34.3025 | 34.3742 | 34.4305 | 33.995 | 34.3119 | 35.7235 | 35.3127 | 36.0806 | 36.0684 | 33.6245 | 92.3774 | 92.506 | 92.5564
2022-09-08 02:29 | 4:39 | 18.5062 | 19.0166 | 21.671 | 34.9647 | 34.3973 | 33.9592 | 34.7907 | 35.4695 | 36.6166 | 37.3213 | 36.8473 | 37.8559 | 34.4524 | 34.4228 | 34.312 | 35.2035 | 35.3888 | 35.8157 | 36.4831 | 36.7518 | 21.3718 | 17.9748 | 92.5595 | 33.5305 | 33.2544 | 35.1714 | 33.6288 | 33.2439 | 33.5991 | 34.9807 | 34.4659 | 34.2143 | 37.2643 | 36.3188 | 33.5967 | 34.4563 | 36.3398 | 36.6118 | 37.4859 | 36.3047 | 33.6217 | 32.8316 | 34.6163 | 35.0995 | 33.1821 | 34.409 | 34.3685 | 34.4778 | 34.3256 | 34.372 | 34.4318 | 33.9929 | 34.3025 | 35.7326 | 35.313 | 36.1116 | 36.0591 | 33.6461 | 92.2988 | 92.4262 | 92.4313
2022-09-08 02:29 | 4:39 | 18.5292 | 18.9787 | 21.6104 | 34.9195 | 34.3962 | 33.9492 | 34.7816 | 35.4605 | 36.6082 | 37.3098 | 36.848 | 37.8512 | 34.4588 | 34.4155 | 34.3119 | 35.1822 | 35.383 | 35.818 | 36.4959 | 36.7697 | 21.3516 | 17.9342 | 92.4748 | 33.612 | 33.2394 | 35.1939 | 33.6171 | 33.2494 | 33.5984 | 34.9677 | 34.4668 | 34.2086 | 37.284 | 36.3277 | 33.6377 | 34.4483 | 36.3049 | 36.611 | 37.4899 | 36.3227 | 33.6068 | 32.8204 | 34.6005 | 35.0795 | 33.1777 | 34.4133 | 34.3496 | 34.48 | 34.308 | 34.3765 | 34.438 | 34.0153 | 34.3256 | 35.7322 | 35.3068 | 36.1146 | 36.0631 | 33.644 | 92.1952 | 92.3292 | 92.4178
2022-09-08 02:29 | 4:39 | 18.3794 | 18.8674 | 21.5252 | 34.8549 | 34.4005 | 33.955 | 34.7783 | 35.4655 | 36.614 | 37.3117 | 36.8494 | 37.8575 | 34.4566 | 34.4156 | 34.3273 | 35.187 | 35.3822 | 35.8161 | 36.4846 | 36.7834 | 21.3405 | 17.9362 | 92.5121 | 33.5596 | 33.2292 | 35.1862 | 33.6131 | 33.2483 | 33.616 | 34.9704 | 34.4677 | 34.2174 | 37.2771 | 36.3124 | 33.5987 | 34.4707 | 36.3188 | 36.5998 | 37.4631 | 36.3394 | 33.6061 | 32.8186 | 34.6001 | 35.0994 | 33.196 | 34.4091 | 34.3672 | 34.4678 | 34.3271 | 34.3802 | 34.4235 | 33.9892 | 34.308 | 35.7413 | 35.3236 | 36.1073 | 36.0688 | 33.6463 | 92.1421 | 92.2297 | 92.3435
2022-09-08 02:29 | 4:39 | 18.4567 | 18.8744 | 21.4641 | 34.9733 | 34.3961 | 33.9649 | 34.7732 | 35.454 | 36.6223 | 37.3225 | 36.842 | 37.8743 | 34.4531 | 34.4286 | 34.3199 | 35.19 | 35.3824 | 35.8096 | 36.5118 | 36.7699 | 21.3175 | 17.8498 | 92.4255 | 33.3753 | 33.238 | 35.1887 | 33.6076 | 33.2651 | 33.6015 | 34.973 | 34.4437 | 34.1984 | 37.2667 | 36.3151 | 33.5999 | 34.4652 | 36.3277 | 36.5918 | 37.4754 | 36.3398 | 33.6089 | 32.8129 | 34.5995 | 35.0988 | 33.1821 | 34.4104 | 34.3824 | 34.486 | 34.3227 | 34.3848 | 34.4273 | 33.9891 | 34.3271 | 35.7449 | 35.3143 | 36.0903 | 36.0749 | 33.6483 | 92.1101 | 92.1887 | 92.2996
2022-09-08 02:29 | 4:39 | 18.2708 | 18.759 | 21.4338 | 34.9365 | 34.4038 | 33.9539 | 34.7757 | 35.4591 | 36.621 | 37.3186 | 36.8426 | 37.8624 | 34.4613 | 34.4215 | 34.3371 | 35.2277 | 35.3828 | 35.8029 | 36.4966 | 36.7801 | 21.2792 | 17.823 | 92.3346 | 33.4781 | 33.2537 | 35.1697 | 33.6217 | 33.2503 | 33.5967 | 34.9768 | 34.4581 | 34.217 | 37.2896 | 36.3113 | 33.6048 | 34.4495 | 36.3124 | 36.6293 | 37.4812 | 36.3049 | 33.5877 | 32.7994 | 34.6172 | 35.0876 | 33.1647 | 34.409 | 34.3666 | 34.4632 | 34.3273 | 34.3537 | 34.4287 | 33.9946 | 34.3227 | 35.7297 | 35.3109 | 36.1043 | 36.0708 | 33.6471 | 92.1266 | 92.2322 | 92.2866
2022-09-08 02:30 | 4:39 | 18.2885 | 18.6978 | 21.3864 | 34.8973 | 34.3986 | 33.9531 | 34.7651 | 35.4795 | 36.618 | 37.3327 | 36.8316 | 37.8768 | 34.4599 | 34.4055 | 34.32 | 35.223 | 35.3868 | 35.799 | 36.4708 | 36.7631 | 21.2354 | 17.773 | 92.388 | 33.5364 | 33.2414 | 35.1702 | 33.6068 | 33.2563 | 33.6377 | 34.9718 | 34.4453 | 34.2081 | 37.2858 | 36.3102 | 33.5844 | 34.4538 | 36.3151 | 36.6048 | 37.4772 | 36.3188 | 33.5855 | 32.8113 | 34.5751 | 35.1186 | 33.1588 | 34.4054 | 34.366 | 34.4693 | 34.3233 | 34.3558 | 34.4297 | 33.9963 | 34.3273 | 35.7315 | 35.3153 | 36.1008 | 36.0699 | 33.6644 | 92.2119 | 92.3666 | 92.3584
2022-09-08 02:30 | 4:40 | 18.2447 | 18.6626 | 21.3059 | 34.7889 | 34.3906 | 33.9605 | 34.7882 | 35.4603 | 36.5946 | 37.3087 | 36.8469 | 37.8654 | 34.4566 | 34.4186 | 34.3337 | 35.192 | 35.3686 | 35.8165 | 36.4638 | 36.7653 | 21.2032 | 17.7476 | 92.5067 | 33.4949 | 33.2473 | 35.1582 | 33.6061 | 33.2323 | 33.5987 | 34.9774 | 34.4636 | 34.2075 | 37.2585 | 36.3107 | 33.6041 | 34.4482 | 36.3113 | 36.6191 | 37.4964 | 36.3277 | 33.6016 | 32.8013 | 34.5866 | 35.1145 | 33.1339 | 34.3984 | 34.355 | 34.499 | 34.3017 | 34.3596 | 34.4286 | 33.9988 | 34.3233 | 35.7261 | 35.3017 | 36.1091 | 36.0861 | 33.6412 | 92.2966 | 92.4252 | 92.4598
2022-09-08 02:30 | 4:40 | 18.1562 | 18.627 | 21.2736 | 34.8122 | 34.4128 | 33.9625 | 34.7789 | 35.467 | 36.6022 | 37.3191 | 36.8259 | 37.8819 | 34.4399 | 34.4088 | 34.3234 | 35.1938 | 35.3768 | 35.8132 | 36.4654 | 36.7561 | 21.1538 | 17.6843 | 92.5662 | 33.3111 | 33.2387 | 35.1677 | 33.6089 | 33.2452 | 33.5999 | 34.9661 | 34.451 | 34.2066 | 37.2844 | 36.3085 | 33.5928 | 34.4524 | 36.3102 | 36.6013 | 37.4692 | 36.3124 | 33.5967 | 32.8032 | 34.5797 | 35.0858 | 33.1385 | 34.4037 | 34.3646 | 34.49 | 34.3313 | 34.3644 | 34.4217 | 34.0055 | 34.3017 | 35.7375 | 35.3161 | 36.1096 | 36.0761 | 33.6661 | 92.3606 | 92.5291 | 92.4668
2022-09-08 02:30 | 4:40 | 18.1241 | 18.5692 | 21.2593 | 34.9093 | 34.416 | 33.9463 | 34.7923 | 35.4714 | 36.6115 | 37.3179 | 36.8513 | 37.8681 | 34.4585 | 34.4159 | 34.3141 | 35.1996 | 35.3838 | 35.8128 | 36.4995 | 36.7565 | 21.1113 | 17.681 | 92.5711 | 33.5235 | 33.2299 | 35.1708 | 33.5877 | 33.2653 | 33.6048 | 34.9562 | 34.4344 | 34.2022 | 37.2719 | 36.3062 | 33.5965 | 34.4363 | 36.3107 | 36.6051 | 37.4697 | 36.3151 | 33.5971 | 32.7869 | 34.5637 | 35.0731 | 33.1498 | 34.4099 | 34.3808 | 34.4802 | 34.3329 | 34.3478 | 34.4325 | 33.9888 | 34.3313 | 35.7433 | 35.307 | 36.0985 | 36.0804 | 33.6478 | 92.4454 | 92.6292 | 92.5142
2022-09-08 02:30 | 4:40 | 18.0386 | 18.5186 | 21.1933 | 34.878 | 34.4246 | 33.936 | 34.7631 | 35.4639 | 36.6178 | 37.3236 | 36.8359 | 37.8709 | 34.4658 | 34.4246 | 34.3266 | 35.2024 | 35.3761 | 35.8122 | 36.4809 | 36.7695 | 21.0822 | 17.6591 | 92.6489 | 33.3899 | 33.2331 | 35.175 | 33.5855 | 33.234 | 33.5844 | 34.961 | 34.4398 | 34.2254 | 37.287 | 36.2909 | 33.5731 | 34.4402 | 36.3085 | 36.6165 | 37.4678 | 36.3113 | 33.5846 | 32.7867 | 34.5745 | 35.1026 | 33.1225 | 34.4007 | 34.3791 | 34.4823 | 34.3225 | 34.3682 | 34.4243 | 33.9925 | 34.3329 | 35.733 | 35.3083 | 36.0942 | 36.0712 | 33.654 | 92.5988 | 92.7922 | 92.661
2022-09-08 02:30 | 4:40 | 18.0908 | 18.5065 | 21.1348 | 34.8013 | 34.4275 | 33.9498 | 34.7797 | 35.4709 | 36.609 | 37.3163 | 36.8224 | 37.8618 | 34.4669 | 34.4184 | 34.3159 | 35.2121 | 35.3908 | 35.7945 | 36.4703 | 36.7538 | 21.0518 | 17.6125 | 92.7422 | 33.5006 | 33.2434 | 35.1748 | 33.6016 | 33.251 | 33.6041 | 34.9554 | 34.4309 | 34.2042 | 37.2669 | 36.2812 | 33.5788 | 34.4451 | 36.3062 | 36.6095 | 37.4797 | 36.3102 | 33.5795 | 32.7632 | 34.5652 | 35.0725 | 33.1258 | 34.3993 | 34.3903 | 34.4894 | 34.313 | 34.3529 | 34.4221 | 33.9993 | 34.3225 | 35.7336 | 35.3048 | 36.1278 | 36.0701 | 33.6597 | 92.7166 | 92.9418 | 92.7626
2022-09-08 02:31 | 4:41 | 18.0341 | 18.4513 | 21.1153 | 35.011 | 34.4067 | 33.9528 | 34.7699 | 35.4562 | 36.6026 | 37.3183 | 36.8355 | 37.8542 | 34.4386 | 34.4199 | 34.3186 | 35.2002 | 35.3598 | 35.8062 | 36.462 | 36.7511 | 21.0234 | 17.5307 | 92.8225 | 33.4439 | 33.227 | 35.1337 | 33.5967 | 33.2476 | 33.5928 | 34.9615 | 34.4534 | 34.2055 | 37.2512 | 36.2883 | 33.5877 | 34.4284 | 36.2909 | 36.5964 | 37.4891 | 36.3107 | 33.5638 | 32.7826 | 34.5731 | 35.0763 | 33.1146 | 34.4127 | 34.3563 | 34.4669 | 34.3182 | 34.3551 | 34.4357 | 33.9973 | 34.313 | 35.7304 | 35.2995 | 36.1069 | 36.0696 | 33.6352 | 92.8189 | 93.0512 | 92.8705
2022-09-08 02:31 | 4:41 | 18.0505 | 18.4364 | 21.0421 | 34.7634 | 34.4096 | 33.9298 | 34.7604 | 35.4666 | 36.604 | 37.3206 | 36.8268 | 37.8619 | 34.4348 | 34.4174 | 34.2901 | 35.1812 | 35.3474 | 35.7994 | 36.4712 | 36.7598 | 20.9876 | 17.5396 | 92.8873 | 33.3714 | 33.2201 | 35.1631 | 33.5971 | 33.2304 | 33.5965 | 34.9611 | 34.4399 | 34.209 | 37.2645 | 36.2949 | 33.5841 | 34.4451 | 36.2812 | 36.6044 | 37.4837 | 36.3085 | 33.5682 | 32.7741 | 34.5496 | 35.0603 | 33.075 | 34.3996 | 34.3596 | 34.4876 | 34.338 | 34.3425 | 34.442 | 33.9995 | 34.3182 | 35.7456 | 35.2841 | 36.0961 | 36.078 | 33.6502 | 92.9506 | 93.1837 | 93.0294
2022-09-08 02:31 | 4:41 | 17.9127 | 18.3444 | 21.0029 | 34.7912 | 34.4138 | 33.9272 | 34.7687 | 35.4614 | 36.6172 | 37.2979 | 36.8348 | 37.8631 | 34.4526 | 34.4156 | 34.309 | 35.1872 | 35.3659 | 35.8016 | 36.4626 | 36.7686 | 20.9424 | 17.5023 | 93.0078 | 33.2501 | 33.2409 | 35.14 | 33.5846 | 33.2318 | 33.5731 | 34.9479 | 34.4292 | 34.1928 | 37.2513 | 36.3051 | 33.5892 | 34.4326 | 36.2883 | 36.6037 | 37.4706 | 36.3062 | 33.5831 | 32.7616 | 34.552 | 35.0716 | 33.0884 | 34.3892 | 34.3643 | 34.4797 | 34.3344 | 34.3567 | 34.4356 | 33.976 | 34.338 | 35.7411 | 35.3064 | 36.1275 | 36.0621 | 33.6465 | 93.0525 | 93.2869 | 93.0498
2022-09-08 02:31 | 4:41 | 17.8521 | 18.2763 | 20.9717 | 34.7514 | 34.4143 | 33.9452 | 34.7833 | 35.4427 | 36.5961 | 37.3174 | 36.8208 | 37.8424 | 34.4639 | 34.4161 | 34.3062 | 35.1829 | 35.3637 | 35.7903 | 36.4553 | 36.7644 | 20.8909 | 17.4262 | 93.1166 | 33.3831 | 33.2118 | 35.1515 | 33.5795 | 33.2309 | 33.5788 | 34.97 | 34.4398 | 34.212 | 37.2661 | 36.2866 | 33.5877 | 34.419 | 36.2949 | 36.6071 | 37.4755 | 36.2909 | 33.568 | 32.7559 | 34.5491 | 35.0665 | 33.1027 | 34.4122 | 34.3538 | 34.4893 | 34.3374 | 34.3457 | 34.4194 | 33.9656 | 34.3344 | 35.7349 | 35.3015 | 36.1014 | 36.0821 | 33.6355 | 93.2105 | 93.3939 | 93.1744
2022-09-08 02:31 | 4:41 | 17.8727 | 18.2927 | 20.9601 | 34.7368 | 34.4023 | 33.9387 | 34.7538 | 35.4355 | 36.5896 | 37.308 | 36.8425 | 37.8629 | 34.4518 | 34.3989 | 34.2953 | 35.1854 | 35.3731 | 35.7951 | 36.4643 | 36.7629 | 20.8862 | 17.4591 | 93.216 | 33.3941 | 33.2193 | 35.1469 | 33.5638 | 33.236 | 33.5877 | 34.9616 | 34.4398 | 34.1988 | 37.2647 | 36.2874 | 33.5681 | 34.4292 | 36.3051 | 36.6118 | 37.4534 | 36.2812 | 33.5575 | 32.7579 | 34.5523 | 35.068 | 33.0913 | 34.3923 | 34.3796 | 34.4851 | 34.3303 | 34.3453 | 34.4393 | 33.9676 | 34.3374 | 35.7436 | 35.3075 | 36.1161 | 36.0752 | 33.6385 | 93.2862 | 93.5348 | 93.2212
2022-09-08 02:31 | 4:41 | 17.7589 | 18.1976 | 20.921 | 34.8016 | 34.4117 | 33.9222 | 34.748 | 35.4552 | 36.592 | 37.3108 | 36.8156 | 37.8492 | 34.4512 | 34.4235 | 34.3105 | 35.1838 | 35.3713 | 35.7953 | 36.4713 | 36.78 | 20.8394 | 17.3667 | 93.3193 | 33.212 | 33.2272 | 35.1586 | 33.5682 | 33.2165 | 33.5841 | 34.9676 | 34.4312 | 34.1833 | 37.2392 | 36.2936 | 33.5845 | 34.4326 | 36.2866 | 36.6041 | 37.4695 | 36.2883 | 33.5674 | 32.7467 | 34.5428 | 35.0558 | 33.0756 | 34.401 | 34.3631 | 34.4894 | 34.3228 | 34.3452 | 34.4234 | 33.9526 | 34.3303 | 35.738 | 35.3036 | 36.1141 | 36.0581 | 33.6389 | 93.4351 | 93.6457 | 93.2809
2022-09-08 02:32 | 4:41 | 17.7763 | 18.2003 | 20.7862 | 34.8112 | 34.4269 | 33.9422 | 34.7645 | 35.4478 | 36.6074 | 37.2992 | 36.8378 | 37.8534 | 34.4588 | 34.3951 | 34.2933 | 35.1831 | 35.37 | 35.7973 | 36.4637 | 36.7477 | 20.8224 | 17.3304 | 93.4817 | 33.4233 | 33.2085 | 35.1575 | 33.5831 | 33.2216 | 33.5892 | 34.9532 | 34.4452 | 34.2064 | 37.2552 | 36.2924 | 33.5925 | 34.4269 | 36.2874 | 36.5926 | 37.4714 | 36.2949 | 33.5571 | 32.7383 | 34.5337 | 35.0596 | 33.0747 | 34.3783 | 34.3827 | 34.4819 | 34.3372 | 34.3377 | 34.4298 | 33.9759 | 34.3228 | 35.7464 | 35.282 | 36.1042 | 36.0683 | 33.6401 | 93.5628 | 93.8217 | 93.4398
2022-09-08 02:32 | 4:42 | 17.7313 | 18.167 | 20.7604 | 34.7561 | 34.4253 | 33.9457 | 34.7613 | 35.4358 | 36.6049 | 37.3312 | 36.8356 | 37.8571 | 34.4357 | 34.4199 | 34.2953 | 35.1706 | 35.3632 | 35.7852 | 36.4512 | 36.7681 | 20.8241 | 17.3512 | 93.5407 | 33.306 | 33.2138 | 35.153 | 33.568 | 33.2259 | 33.5877 | 34.9513 | 34.4204 | 34.2015 | 37.2432 | 36.2737 | 33.5836 | 34.4433 | 36.2936 | 36.5974 | 37.4573 | 36.3051 | 33.5543 | 32.7394 | 34.5242 | 35.0554 | 33.0576 | 34.3928 | 34.3615 | 34.5033 | 34.3556 | 34.3544 | 34.4169 | 33.9797 | 34.3372 | 35.7519 | 35.2918 | 36.1201 | 36.0701 | 33.6504 | 93.7554 | 94.0212 | 93.5994
2022-09-08 02:32 | 4:42 | 17.6922 | 18.1698 | 20.7431 | 34.8184 | 34.4159 | 33.9278 | 34.7571 | 35.456 | 36.5947 | 37.3101 | 36.827 | 37.855 | 34.4351 | 34.4204 | 34.3134 | 35.1659 | 35.36 | 35.8107 | 36.4426 | 36.7694 | 20.8025 | 17.3149 | 93.4927 | 33.2486 | 33.2283 | 35.1252 | 33.5575 | 33.2223 | 33.5681 | 34.9509 | 34.422 | 34.2106 | 37.2501 | 36.2838 | 33.5846 | 34.4412 | 36.2924 | 36.6033 | 37.4726 | 36.2866 | 33.5468 | 32.7237 | 34.5255 | 35.0362 | 33.0419 | 34.3933 | 34.3912 | 34.5032 | 34.3421 | 34.3551 | 34.4185 | 33.9603 | 34.3556 | 35.7483 | 35.2994 | 36.1333 | 36.0705 | 33.6343 | 93.9796 | 94.1923 | 93.6751
2022-09-08 02:32 | 4:42 | 17.7362 | 18.1472 | 20.7319 | 34.6324 | 34.4239 | 33.9092 | 34.7524 | 35.4362 | 36.5842 | 37.3167 | 36.8213 | 37.8516 | 34.4514 | 34.3865 | 34.3081 | 35.1866 | 35.3481 | 35.7907 | 36.4652 | 36.7581 | 20.7743 | 17.2388 | 93.5737 | 33.3678 | 33.2062 | 35.1343 | 33.5674 | 33.2083 | 33.5845 | 34.9747 | 34.4343 | 34.1999 | 37.2599 | 36.2648 | 33.5829 | 34.4285 | 36.2737 | 36.6092 | 37.4642 | 36.2874 | 33.5376 | 32.7358 | 34.5215 | 35.04 | 33.0422 | 34.3804 | 34.3688 | 34.5095 | 34.3439 | 34.3407 | 34.4361 | 33.9695 | 34.3421 | 35.7493 | 35.2997 | 36.1015 | 36.0681 | 33.6398 | 94.0566 | 94.3253 | 93.6979
2022-09-08 02:32 | 4:42 | 17.6803 | 18.1043 | 20.6349 | 34.7446 | 34.4084 | 33.9242 | 34.7577 | 35.4522 | 36.6047 | 37.3015 | 36.8188 | 37.8544 | 34.4522 | 34.415 | 34.294 | 35.1833 | 35.3533 | 35.7883 | 36.4476 | 36.748 | 20.7566 | 17.2868 | 93.6734 | 33.2421 | 33.2131 | 35.1475 | 33.5571 | 33.2168 | 33.5925 | 34.9602 | 34.4325 | 34.1928 | 37.2492 | 36.2749 | 33.5916 | 34.4336 | 36.2838 | 36.595 | 37.4494 | 36.2936 | 33.5397 | 32.7119 | 34.5231 | 35.0285 | 33.0437 | 34.4116 | 34.3942 | 34.4768 | 34.3364 | 34.3234 | 34.4201 | 33.9666 | 34.3439 | 35.7475 | 35.2836 | 36.1119 | 36.0709 | 33.6436 | 94.2417 | 94.4943 | 93.8623
2022-09-08 02:32 | 4:42 | 17.6971 | 18.0957 | 20.6463 | 34.666 | 34.4261 | 33.9366 | 34.7376 | 35.4568 | 36.6103 | 37.316 | 36.8293 | 37.8794 | 34.4491 | 34.4065 | 34.2964 | 35.1849 | 35.3715 | 35.7925 | 36.4422 | 36.7646 | 20.706 | 17.2909 | 93.7966 | 33.2724 | 33.2103 | 35.1407 | 33.5543 | 33.2362 | 33.5836 | 34.9497 | 34.4235 | 34.198 | 37.2505 | 36.2726 | 33.5866 | 34.4281 | 36.2648 | 36.6069 | 37.4505 | 36.2924 | 33.5514 | 32.7013 | 34.5082 | 35.0356 | 33.0354 | 34.3854 | 34.4051 | 34.5128 | 34.3341 | 34.3609 | 34.4205 | 33.9523 | 34.3364 | 35.7478 | 35.2847 | 36.116 | 36.0655 | 33.6292 | 94.3629 | 94.7131 | 93.9401
2022-09-08 02:33 | 4:43 | 17.6446 | 18.079 | 20.6143 | 34.6531 | 34.4365 | 33.9354 | 34.7327 | 35.4428 | 36.6028 | 37.3208 | 36.8343 | 37.8671 | 34.4293 | 34.3895 | 34.2992 | 35.1569 | 35.3615 | 35.7707 | 36.4219 | 36.7696 | 20.7178 | 17.21 | 93.8807 | 33.184 | 33.2174 | 35.1493 | 33.5468 | 33.2249 | 33.5846 | 34.9689 | 34.4464 | 34.1858 | 37.2639 | 36.2773 | 33.5791 | 34.4131 | 36.2749 | 36.6006 | 37.4583 | 36.2737 | 33.5464 | 32.7068 | 34.4961 | 35.0296 | 33.0455 | 34.4085 | 34.3891 | 34.4866 | 34.3359 | 34.3622 | 34.4312 | 33.9609 | 34.3341 | 35.7358 | 35.2918 | 36.1063 | 36.0746 | 33.6262 | 94.4731 | 94.8796 | 94.104
2022-09-08 02:33 | 4:43 | 17.7037 | 18.0626 | 20.5937 | 34.7428 | 34.4316 | 33.9262 | 34.7396 | 35.4378 | 36.6047 | 37.2818 | 36.8157 | 37.8428 | 34.4311 | 34.3977 | 34.284 | 35.1593 | 35.3484 | 35.7664 | 36.4358 | 36.7611 | 20.6874 | 17.2336 | 94.019 | 33.2505 | 33.1941 | 35.115 | 33.5376 | 33.1932 | 33.5829 | 34.9758 | 34.4253 | 34.199 | 37.273 | 36.274 | 33.5656 | 34.437 | 36.2726 | 36.5938 | 37.4508 | 36.2838 | 33.5451 | 32.701 | 34.4873 | 35.0398 | 33.0192 | 34.3962 | 34.3939 | 34.4986 | 34.3354 | 34.3494 | 34.4222 | 33.9399 | 34.3359 | 35.7275 | 35.2774 | 36.1178 | 36.0623 | 33.6318 | 94.6593 | 95.055 | 94.171
2022-09-08 02:33 | 4:43 | 17.7075 | 18.0417 | 20.5583 | 34.6392 | 34.4185 | 33.9204 | 34.7488 | 35.428 | 36.5929 | 37.3072 | 36.8193 | 37.8432 | 34.4192 | 34.3806 | 34.2952 | 35.166 | 35.3552 | 35.7828 | 36.4298 | 36.7518 | 20.674 | 17.2528 | 94.1385 | 33.2094 | 33.1896 | 35.1467 | 33.5397 | 33.2063 | 33.5916 | 34.9809 | 34.4083 | 34.1995 | 37.2439 | 36.2659 | 33.5653 | 34.4322 | 36.2773 | 36.5951 | 37.449 | 36.2648 | 33.5605 | 32.7187 | 34.5027 | 35.0143 | 33.0364 | 34.3828 | 34.4034 | 34.5178 | 34.3367 | 34.363 | 34.4228 | 33.9578 | 34.3354 | 35.7265 | 35.298 | 36.1126 | 36.0675 | 33.6261 | 94.7715 | 95.2333 | 94.3918
2022-09-08 02:33 | 4:43 | 17.5205 | 17.9663 | 20.5013 | 34.6807 | 34.4278 | 33.9288 | 34.7494 | 35.455 | 36.5982 | 37.3105 | 36.8149 | 37.838 | 34.4235 | 34.3956 | 34.2708 | 35.1587 | 35.3524 | 35.7642 | 36.4241 | 36.7478 | 20.6694 | 17.2149 | 94.2289 | 33.2117 | 33.2152 | 35.1169 | 33.5514 | 33.1965 | 33.5866 | 34.9596 | 34.4216 | 34.1988 | 37.2444 | 36.2904 | 33.5742 | 34.4266 | 36.274 | 36.6063 | 37.4657 | 36.2749 | 33.5358 | 32.6887 | 34.4939 | 35.0146 | 33.0282 | 34.371 | 34.3994 | 34.5075 | 34.3326 | 34.3474 | 34.4155 | 33.9559 | 34.3367 | 35.7369 | 35.2981 | 36.1055 | 36.0641 | 33.6149 | 94.8947 | 95.3101 | 94.3661
2022-09-08 02:33 | 4:43 | 17.5943 | 17.9435 | 20.5148 | 34.6874 | 34.4263 | 33.93 | 34.7394 | 35.4202 | 36.5979 | 37.313 | 36.8274 | 37.857 | 34.4295 | 34.3714 | 34.2683 | 35.1639 | 35.3416 | 35.7732 | 36.4274 | 36.7539 | 20.6531 | 17.2087 | 94.3579 | 33.2121 | 33.1956 | 35.1345 | 33.5464 | 33.23 | 33.5791 | 34.9499 | 34.4198 | 34.1738 | 37.256 | 36.2555 | 33.5677 | 34.4273 | 36.2659 | 36.6 | 37.4252 | 36.2726 | 33.544 | 32.6841 | 34.4855 | 35.0243 | 33.0004 | 34.3776 | 34.3919 | 34.5197 | 34.3327 | 34.3508 | 34.4156 | 33.9343 | 34.3326 | 35.7133 | 35.2917 | 36.1003 | 36.0574 | 33.6189 | 94.997 | 95.4905 | 94.4774
2022-09-08 02:33 | 4:43 | 17.5291 | 17.9587 | 20.5358 | 34.4927 | 34.4305 | 33.9056 | 34.732 | 35.4285 | 36.5956 | 37.3095 | 36.828 | 37.858 | 34.4147 | 34.3959 | 34.2726 | 35.1446 | 35.3215 | 35.7551 | 36.4264 | 36.7383 | 20.6347 | 17.1402 | 94.3639 | 33.1958 | 33.2048 | 35.1272 | 33.5451 | 33.2047 | 33.5656 | 34.9416 | 34.4123 | 34.1816 | 37.2317 | 36.2818 | 33.5668 | 34.425 | 36.2904 | 36.5817 | 37.4434 | 36.2773 | 33.5547 | 32.6846 | 34.4863 | 35.0086 | 33.0212 | 34.3658 | 34.3947 | 34.5078 | 34.3509 | 34.3715 | 34.4286 | 33.9426 | 34.3327 | 35.7219 | 35.2916 | 36.1017 | 36.0758 | 33.6091 | 95.0752 | 95.5617 | 94.5884
2022-09-08 02:34 | 4:44 | 17.5045 | 17.9291 | 20.5009 | 34.5976 | 34.4318 | 33.9322 | 34.7407 | 35.4605 | 36.5778 | 37.292 | 36.8237 | 37.8612 | 34.4111 | 34.3591 | 34.2852 | 35.1534 | 35.3281 | 35.749 | 36.4329 | 36.7452 | 20.6231 | 17.1498 | 94.4511 | 33.2088 | 33.1877 | 35.1172 | 33.5605 | 33.2088 | 33.5653 | 34.9627 | 34.421 | 34.1858 | 37.2327 | 36.2664 | 33.5645 | 34.4413 | 36.2555 | 36.5934 | 37.441 | 36.274 | 33.5441 | 32.6714 | 34.4705 | 35.0095 | 33.0202 | 34.3654 | 34.4015 | 34.5153 | 34.3416 | 34.3569 | 34.4215 | 33.9585 | 34.3509 | 35.73 | 35.3072 | 36.1185 | 36.0561 | 33.6151 | 95.2249 | 95.6418 | 94.6064
2022-09-08 02:34 | 4:44 | 17.4723 | 17.8724 | 20.4078 | 34.6194 | 34.438 | 33.9174 | 34.7329 | 35.4376 | 36.5994 | 37.299 | 36.8159 | 37.8543 | 34.4196 | 34.3593 | 34.2815 | 35.1396 | 35.3456 | 35.7708 | 36.4141 | 36.7391 | 20.6178 | 17.1141 | 94.4861 | 33.2234 | 33.19 | 35.1247 | 33.5358 | 33.1986 | 33.5742 | 34.9344 | 34.4247 | 34.18 | 37.2518 | 36.2694 | 33.5643 | 34.4219 | 36.2818 | 36.6193 | 37.4199 | 36.2659 | 33.5472 | 32.6756 | 34.4609 | 34.9985 | 32.9756 | 34.3778 | 34.3819 | 34.5134 | 34.3402 | 34.3462 | 34.4055 | 33.9342 | 34.3416 | 35.7098 | 35.2882 | 36.1146 | 36.0863 | 33.5972 | 95.2675 | 95.7083 | 94.5819
2022-09-08 02:34 | 4:44 | 17.4493 | 17.8554 | 20.4341 | 34.6781 | 34.4235 | 33.9205 | 34.7237 | 35.429 | 36.5864 | 37.3036 | 36.8209 | 37.8446 | 34.4169 | 34.3825 | 34.2681 | 35.1631 | 35.3407 | 35.766 | 36.402 | 36.7559 | 20.6043 | 17.0844 | 94.5609 | 33.1604 | 33.1784 | 35.1387 | 33.544 | 33.1961 | 33.5677 | 34.9382 | 34.4323 | 34.1972 | 37.2498 | 36.2732 | 33.5617 | 34.4207 | 36.2664 | 36.585 | 37.4463 | 36.2904 | 33.5331 | 32.6888 | 34.458 | 35.0012 | 32.9908 | 34.3642 | 34.3962 | 34.5185 | 34.3494 | 34.3559 | 34.4186 | 33.9344 | 34.3402 | 35.6903 | 35.2953 | 36.0911 | 36.0621 | 33.6039 | 95.1921 | 95.6027 | 94.5953
2022-09-08 02:34 | 4:44 | 17.4296 | 17.8548 | 20.4185 | 34.5027 | 34.4273 | 33.9128 | 34.7312 | 35.4194 | 36.5851 | 37.3063 | 36.8232 | 37.8554 | 34.4227 | 34.3662 | 34.2775 | 35.1561 | 35.3362 | 35.7618 | 36.4156 | 36.7212 | 20.6074 | 17.0318 | 94.313 | 33.1221 | 33.1778 | 35.1237 | 33.5547 | 33.1988 | 33.5668 | 34.9248 | 34.3963 | 34.1795 | 37.2228 | 36.2725 | 33.5639 | 34.4078 | 36.2694 | 36.5984 | 37.4318 | 36.2555 | 33.5233 | 32.6451 | 34.4444 | 34.9726 | 32.9861 | 34.359 | 34.4025 | 34.5114 | 34.3382 | 34.3773 | 34.4088 | 33.9433 | 34.3494 | 35.7193 | 35.2912 | 36.1193 | 36.0653 | 33.583 | 94.9846 | 95.3484 | 94.3495
2022-09-08 02:34 | 4:44 | 17.4143 | 17.8475 | 20.3238 | 34.614 | 34.4287 | 33.9211 | 34.7262 | 35.448 | 36.5765 | 37.2901 | 36.8242 | 37.8482 | 34.4045 | 34.3616 | 34.2639 | 35.1582 | 35.324 | 35.7557 | 36.4161 | 36.7236 | 20.6335 | 17.0209 | 94.1697 | 33.2129 | 33.1709 | 35.13 | 33.5441 | 33.1985 | 33.5645 | 34.935 | 34.4107 | 34.1893 | 37.2437 | 36.2629 | 33.5619 | 34.4057 | 36.2732 | 36.5996 | 37.4261 | 36.2818 | 33.5272 | 32.6484 | 34.4331 | 34.9834 | 32.9743 | 34.3712 | 34.4213 | 34.5304 | 34.3397 | 34.3603 | 34.4159 | 33.9347 | 34.3382 | 35.7166 | 35.2831 | 36.1099 | 36.0529 | 33.5857 | 94.7197 | 95.0756 | 94.1723
2022-09-08 02:34 | 4:44 | 17.3791 | 17.7734 | 20.3128 | 34.5198 | 34.4297 | 33.8999 | 34.7485 | 35.4173 | 36.5746 | 37.2951 | 36.8097 | 37.8569 | 34.4023 | 34.3556 | 34.272 | 35.1543 | 35.3312 | 35.7534 | 36.3925 | 36.7076 | 20.6641 | 17.029 | 94.07 | 33.0944 | 33.1853 | 35.1244 | 33.5472 | 33.1877 | 33.5643 | 34.937 | 34.4319 | 34.1907 | 37.2369 | 36.279 | 33.559 | 34.419 | 36.2725 | 36.5799 | 37.4119 | 36.2664 | 33.538 | 32.6514 | 34.4361 | 34.9631 | 32.9636 | 34.3432 | 34.4119 | 34.5156 | 34.3627 | 34.3519 | 34.4246 | 33.9281 | 34.3397 | 35.7179 | 35.2926 | 36.1009 | 36.0682 | 33.5695 | 94.5493 | 94.8827 | 94.1052
2022-09-08 02:35 | 4:44 | 17.3665 | 17.7737 | 20.2502 | 34.6266 | 34.4286 | 33.9039 | 34.7316 | 35.4291 | 36.5785 | 37.2689 | 36.8233 | 37.8395 | 34.4059 | 34.3568 | 34.2483 | 35.1377 | 35.3257 | 35.7382 | 36.3967 | 36.7038 | 20.6921 | 16.9778 | 93.981 | 33.1778 | 33.1526 | 35.1225 | 33.5331 | 33.1802 | 33.5617 | 34.9338 | 34.423 | 34.1608 | 37.2414 | 36.2823 | 33.5465 | 34.4074 | 36.2629 | 36.5782 | 37.3946 | 36.2694 | 33.5115 | 32.6598 | 34.4273 | 34.9571 | 32.9604 | 34.3388 | 34.4074 | 34.5354 | 34.3474 | 34.3494 | 34.4184 | 33.9126 | 34.3627 | 35.6994 | 35.2831 | 36.1106 | 36.0628 | 33.5684 | 94.3685 | 94.6942 | 93.9484
2022-09-08 02:35 | 4:45 | 17.3586 | 17.7686 | 20.2263 | 34.5502 | 34.4217 | 33.8901 | 34.7172 | 35.4343 | 36.5666 | 37.2681 | 36.8036 | 37.8189 | 34.3945 | 34.3491 | 34.252 | 35.1448 | 35.3157 | 35.7443 | 36.3929 | 36.7059 | 20.7163 | 16.9904 | 93.8817 | 33.3154 | 33.1568 | 35.1265 | 33.5233 | 33.1804 | 33.5639 | 34.9361 | 34.4215 | 34.17 | 37.2469 | 36.2581 | 33.5521 | 34.4231 | 36.279 | 36.5803 | 37.4076 | 36.2732 | 33.5156 | 32.6465 | 34.3996 | 34.9591 | 32.9729 | 34.3559 | 34.4132 | 34.528 | 34.3434 | 34.3616 | 34.4199 | 33.9242 | 34.3474 | 35.6988 | 35.2906 | 36.1058 | 36.0612 | 33.5725 | 94.2953 | 94.5673 | 93.8575
2022-09-08 02:35 | 4:45 | 17.4204 | 17.753 | 20.2479 | 34.5045 | 34.4325 | 33.9066 | 34.7115 | 35.4178 | 36.561 | 37.2835 | 36.8114 | 37.844 | 34.3932 | 34.3578 | 34.2562 | 35.1405 | 35.3193 | 35.7183 | 36.3947 | 36.7245 | 20.7295 | 17.0093 | 93.8504 | 32.9949 | 33.1627 | 35.1041 | 33.5272 | 33.1811 | 33.5619 | 34.9232 | 34.4222 | 34.1763 | 37.2327 | 36.2776 | 33.553 | 34.4233 | 36.2823 | 36.5844 | 37.4162 | 36.2725 | 33.5292 | 32.6331 | 34.4196 | 34.9512 | 32.9388 | 34.3475 | 34.4166 | 34.5302 | 34.3519 | 34.3484 | 34.4174 | 33.918 | 34.3434 | 35.6909 | 35.2835 | 36.1058 | 36.0422 | 33.5653 | 94.2035 | 94.4621 | 93.8768
2022-09-08 02:35 | 4:45 | 17.473 | 17.8125 | 20.2909 | 34.3729 | 34.4243 | 33.9172 | 34.7147 | 35.4269 | 36.5621 | 37.2671 | 36.8457 | 37.843 | 34.3857 | 34.3323 | 34.2534 | 35.1298 | 35.3247 | 35.7317 | 36.3619 | 36.7024 | 20.7771 | 16.934 | 93.8213 | 33.1818 | 33.1607 | 35.1315 | 33.538 | 33.1547 | 33.559 | 34.9194 | 34.4227 | 34.1638 | 37.2384 | 36.2624 | 33.5456 | 34.4096 | 36.2581 | 36.5694 | 37.402 | 36.2629 | 33.5271 | 32.615 | 34.425 | 34.9461 | 32.9567 | 34.3447 | 34.4133 | 34.5091 | 34.3529 | 34.3568 | 34.4156 | 33.9149 | 34.3519 | 35.6945 | 35.282 | 36.106 | 36.0492 | 33.5703 | 94.0987 | 94.4071 | 93.7827
2022-09-08 02:35 | 4:45 | 17.426 | 17.7054 | 20.2788 | 34.5667 | 34.4221 | 33.915 | 34.7143 | 35.4218 | 36.5689 | 37.2642 | 36.8417 | 37.8375 | 34.3916 | 34.3552 | 34.2562 | 35.1453 | 35.3149 | 35.7493 | 36.3724 | 36.7262 | 20.7868 | 17.0041 | 93.7656 | 33.1605 | 33.1551 | 35.1079 | 33.5115 | 33.1714 | 33.5465 | 34.9346 | 34.4178 | 34.1668 | 37.246 | 36.2823 | 33.5571 | 34.4197 | 36.2776 | 36.5894 | 37.4107 | 36.279 | 33.5136 | 32.6309 | 34.4105 | 34.9278 | 32.9477 | 34.3582 | 34.421 | 34.5243 | 34.3565 | 34.3324 | 34.4161 | 33.9264 | 34.3529 | 35.6752 | 35.294 | 36.116 | 36.062 | 33.5599 | 93.9985 | 94.2587 | 93.7377
2022-09-08 02:35 | 4:45 | 17.3267 | 17.6441 | 20.2165 | 34.4622 | 34.4357 | 33.9092 | 34.7335 | 35.4302 | 36.575 | 37.2693 | 36.8245 | 37.8391 | 34.3824 | 34.3319 | 34.245 | 35.1598 | 35.302 | 35.7178 | 36.3962 | 36.7099 | 20.7911 | 16.9229 | 93.7449 | 33.1315 | 33.1338 | 35.1275 | 33.5156 | 33.1906 | 33.5521 | 34.9113 | 34.4224 | 34.1711 | 37.2197 | 36.2654 | 33.5641 | 34.4211 | 36.2624 | 36.5884 | 37.381 | 36.2823 | 33.537 | 32.6321 | 34.4006 | 34.9277 | 32.9526 | 34.3384 | 34.4104 | 34.5286 | 34.3655 | 34.3554 | 34.3989 | 33.9056 | 34.3565 | 35.6958 | 35.267 | 36.1228 | 36.0435 | 33.5498 | 93.9221 | 94.1682 | 93.7317
2022-09-08 02:36 | 4:46 | 17.3186 | 17.6525 | 20.2399 | 34.3414 | 34.442 | 33.8976 | 34.7083 | 35.4197 | 36.5761 | 37.2733 | 36.8193 | 37.8392 | 34.4062 | 34.3425 | 34.2296 | 35.1493 | 35.2953 | 35.7145 | 36.3635 | 36.7022 | 20.7951 | 16.9318 | 93.7451 | 33.0755 | 33.1609 | 35.1255 | 33.5292 | 33.1849 | 33.553 | 34.9188 | 34.4416 | 34.1671 | 37.2228 | 36.2677 | 33.5495 | 34.4184 | 36.2823 | 36.5792 | 37.3952 | 36.2581 | 33.5089 | 32.6217 | 34.4196 | 34.9245 | 32.9403 | 34.3388 | 34.4134 | 34.52 | 34.347 | 34.3674 | 34.4235 | 33.9059 | 34.3655 | 35.6932 | 35.2918 | 36.1318 | 36.0698 | 33.5457 | 93.9242 | 94.1175 | 93.7389
2022-09-08 02:36 | 4:46 | 17.3659 | 17.702 | 20.181 | 34.4669 | 34.4356 | 33.9243 | 34.7155 | 35.4447 | 36.5579 | 37.2715 | 36.8173 | 37.8425 | 34.3742 | 34.3407 | 34.2405 | 35.1321 | 35.3176 | 35.7301 | 36.3853 | 36.7126 | 20.8029 | 16.9201 | 93.6309 | 33.1438 | 33.1649 | 35.1063 | 33.5271 | 33.1876 | 33.5456 | 34.9187 | 34.4176 | 34.1801 | 37.2297 | 36.2609 | 33.5323 | 34.4216 | 36.2654 | 36.5737 | 37.3944 | 36.2776 | 33.5228 | 32.581 | 34.3892 | 34.94 | 32.9523 | 34.3219 | 34.4025 | 34.5276 | 34.3498 | 34.3575 | 34.3951 | 33.9055 | 34.347 | 35.6803 | 35.2963 | 36.1167 | 36.0671 | 33.5568 | 93.8375 | 94.0518 | 93.6245
2022-09-08 02:36 | 4:46 | 17.3073 | 17.691 | 20.198 | 34.3947 | 34.4194 | 33.9224 | 34.7028 | 35.4383 | 36.5457 | 37.2649 | 36.8182 | 37.8568 | 34.372 | 34.3325 | 34.2338 | 35.1496 | 35.3066 | 35.7385 | 36.3601 | 36.6917 | 20.8092 | 16.9512 | 93.6373 | 33.0917 | 33.1504 | 35.1202 | 33.5136 | 33.1782 | 33.5571 | 34.9204 | 34.4165 | 34.184 | 37.2121 | 36.2545 | 33.5364 | 34.4099 | 36.2677 | 36.5841 | 37.4041 | 36.2624 | 33.5223 | 32.6093 | 34.394 | 34.926 | 32.9464 | 34.3218 | 34.4135 | 34.5259 | 34.3728 | 34.353 | 34.4199 | 33.8964 | 34.3498 | 35.6987 | 35.2642 | 36.1144 | 36.0516 | 33.5338 | 93.8276 | 94.0257 | 93.6505
2022-09-08 02:36 | 4:46 | 17.236 | 17.5901 | 20.1482 | 34.4669 | 34.4393 | 33.9194 | 34.7258 | 35.4294 | 36.5513 | 37.2581 | 36.8388 | 37.8394 | 34.3765 | 34.334 | 34.2369 | 35.1407 | 35.3034 | 35.7486 | 36.3734 | 36.6939 | 20.8005 | 16.8837 | 93.5897 | 33.1303 | 33.1487 | 35.1365 | 33.537 | 33.1847 | 33.5641 | 34.9031 | 34.412 | 34.1893 | 37.2287 | 36.2692 | 33.5488 | 34.4392 | 36.2609 | 36.5863 | 37.412 | 36.2823 | 33.5176 | 32.6064 | 34.4085 | 34.9253 | 32.9315 | 34.3323 | 34.4239 | 34.5264 | 34.3644 | 34.3742 | 34.4204 | 33.8855 | 34.3728 | 35.6888 | 35.2853 | 36.1146 | 36.0533 | 33.5438 | 93.7478 | 93.9734 | 93.5323
2022-09-08 02:36 | 4:46 | 17.2086 | 17.541 | 20.1448 | 34.4828 | 34.4234 | 33.9055 | 34.7154 | 35.4215 | 36.5564 | 37.2638 | 36.8383 | 37.8595 | 34.3802 | 34.3285 | 34.2212 | 35.1563 | 35.2948 | 35.7117 | 36.3727 | 36.7037 | 20.7835 | 16.868 | 93.5629 | 33.0236 | 33.1398 | 35.1228 | 33.5089 | 33.1823 | 33.5495 | 34.8856 | 34.428 | 34.1637 | 37.2323 | 36.2592 | 33.5504 | 34.4471 | 36.2545 | 36.5821 | 37.3966 | 36.2654 | 33.5378 | 32.5971 | 34.3932 | 34.907 | 32.9312 | 34.345 | 34.4111 | 34.5164 | 34.3415 | 34.3594 | 34.3865 | 33.898 | 34.3644 | 35.6951 | 35.3075 | 36.1237 | 36.041 | 33.5418 | 93.698 | 93.9163 | 93.5621
2022-09-08 02:36 | 4:46 | 17.2221 | 17.5929 | 20.1321 | 34.3565 | 34.4298 | 33.9129 | 34.704 | 35.4515 | 36.5531 | 37.2551 | 36.8537 | 37.854 | 34.3848 | 34.3383 | 34.2302 | 35.153 | 35.2932 | 35.744 | 36.3849 | 36.6905 | 20.7602 | 16.8795 | 93.537 | 33.1503 | 33.1225 | 35.124 | 33.5228 | 33.1854 | 33.5323 | 34.9131 | 34.416 | 34.1642 | 37.2319 | 36.2684 | 33.5431 | 34.4202 | 36.2692 | 36.5774 | 37.3763 | 36.2677 | 33.5137 | 32.5807 | 34.3837 | 34.918 | 32.9226 | 34.3195 | 34.4036 | 34.5196 | 34.3632 | 34.3448 | 34.415 | 33.9246 | 34.3415 | 35.6903 | 35.2724 | 36.1061 | 36.0493 | 33.5291 | 93.6463 | 93.8699 | 93.4626
2022-09-08 02:37 | 4:46 | 17.2629 | 17.581 | 20.1632 | 34.3909 | 34.4169 | 33.9065 | 34.717 | 35.4123 | 36.5445 | 37.2508 | 36.8366 | 37.8446 | 34.3537 | 34.3337 | 34.2438 | 35.16 | 35.3036 | 35.7202 | 36.3686 | 36.6944 | 20.7758 | 16.8548 | 93.5951 | 33.0475 | 33.1315 | 35.1369 | 33.5223 | 33.2023 | 33.5364 | 34.907 | 34.4245 | 34.1772 | 37.2204 | 36.2546 | 33.5411 | 34.4372 | 36.2592 | 36.58 | 37.404 | 36.2609 | 33.5169 | 32.5814 | 34.3796 | 34.9275 | 32.91 | 34.3116 | 34.4305 | 34.5234 | 34.3614 | 34.3777 | 34.4065 | 33.9001 | 34.3632 | 35.678 | 35.2768 | 36.1162 | 36.0543 | 33.5304 | 93.6388 | 93.7936 | 93.5037
2022-09-08 02:37 | 4:47 | 17.1797 | 17.5185 | 20.114 | 34.5035 | 34.4185 | 33.9341 | 34.7184 | 35.4304 | 36.5609 | 37.2681 | 36.8299 | 37.8599 | 34.3558 | 34.323 | 34.2296 | 35.1447 | 35.3023 | 35.718 | 36.3685 | 36.6941 | 20.7576 | 16.8431 | 93.5613 | 32.8862 | 33.1372 | 35.1236 | 33.5176 | 33.169 | 33.5488 | 34.9172 | 34.4431 | 34.1741 | 37.2321 | 36.265 | 33.5449 | 34.4239 | 36.2684 | 36.5811 | 37.3764 | 36.2545 | 33.52 | 32.5821 | 34.3734 | 34.9082 | 32.9147 | 34.3142 | 34.4159 | 34.5318 | 34.3662 | 34.367 | 34.3895 | 33.8888 | 34.3614 | 35.6923 | 35.2858 | 36.1305 | 36.0668 | 33.5415 | 93.5379 | 93.6818 | 93.4246
2022-09-08 02:37 | 4:47 | 17.1811 | 17.5092 | 20.0895 | 34.412 | 34.4361 | 33.9367 | 34.708 | 35.4181 | 36.5463 | 37.2618 | 36.845 | 37.8646 | 34.3596 | 34.3129 | 34.2239 | 35.1442 | 35.2968 | 35.7329 | 36.362 | 36.6883 | 20.7584 | 16.8095 | 93.4508 | 32.9799 | 33.1311 | 35.1132 | 33.5378 | 33.1804 | 33.5504 | 34.9122 | 34.4263 | 34.1828 | 37.2241 | 36.2629 | 33.5307 | 34.4375 | 36.2546 | 36.5505 | 37.3851 | 36.2692 | 33.5273 | 32.5939 | 34.3625 | 34.916 | 32.9155 | 34.3204 | 34.4245 | 34.523 | 34.3685 | 34.3611 | 34.3977 | 33.8964 | 34.3662 | 35.7068 | 35.2909 | 36.1261 | 36.0427 | 33.5464 | 93.4458 | 93.6298 | 93.4174
2022-09-08 02:37 | 4:47 | 17.1771 | 17.4731 | 20.0788 | 34.4433 | 34.4201 | 33.9172 | 34.7075 | 35.4187 | 36.5607 | 37.2463 | 36.8335 | 37.8553 | 34.3644 | 34.3253 | 34.2316 | 35.1568 | 35.3147 | 35.7217 | 36.3674 | 36.6909 | 20.7326 | 16.8268 | 93.3276 | 32.9625 | 33.1209 | 35.1136 | 33.5137 | 33.1802 | 33.5431 | 34.9216 | 34.4231 | 34.1872 | 37.223 | 36.263 | 33.5517 | 34.4338 | 36.265 | 36.5689 | 37.3962 | 36.2592 | 33.5092 | 32.5741 | 34.3691 | 34.9149 | 32.9134 | 34.3077 | 34.4136 | 34.5256 | 34.3496 | 34.3637 | 34.3806 | 33.8887 | 34.3685 | 35.6949 | 35.2822 | 36.1141 | 36.0541 | 33.5226 | 93.3242 | 93.5124 | 93.3489
2022-09-08 02:37 | 4:47 | 17.129 | 17.4401 | 20.0164 | 34.4355 | 34.4205 | 33.9042 | 34.7136 | 35.4407 | 36.5644 | 37.2662 | 36.8325 | 37.854 | 34.3478 | 34.3222 | 34.2263 | 35.127 | 35.2962 | 35.738 | 36.3612 | 36.7009 | 20.7232 | 16.7642 | 93.2525 | 33.0034 | 33.1303 | 35.1161 | 33.5169 | 33.1814 | 33.5411 | 34.9168 | 34.4243 | 34.1841 | 37.2502 | 36.2552 | 33.5342 | 34.4317 | 36.2629 | 36.5809 | 37.3955 | 36.2684 | 33.5039 | 32.5666 | 34.3583 | 34.9248 | 32.8848 | 34.314 | 34.4269 | 34.5383 | 34.3672 | 34.3526 | 34.3956 | 33.8761 | 34.3496 | 35.7069 | 35.2743 | 36.139 | 36.0613 | 33.5362 | 93.2134 | 93.3272 | 93.298
2022-09-08 02:37 | 4:47 | 17.0696 | 17.409 | 19.9614 | 34.4229 | 34.4312 | 33.9057 | 34.703 | 35.4423 | 36.5357 | 37.2648 | 36.8654 | 37.8564 | 34.3682 | 34.3077 | 34.2454 | 35.1405 | 35.2964 | 35.7231 | 36.3723 | 36.7076 | 20.7224 | 16.7737 | 93.16 | 32.8415 | 33.1293 | 35.1186 | 33.52 | 33.1798 | 33.5449 | 34.9003 | 34.4233 | 34.1802 | 37.2256 | 36.2745 | 33.5204 | 34.4293 | 36.263 | 36.5945 | 37.4006 | 36.2546 | 33.5069 | 32.5637 | 34.3625 | 34.9096 | 32.9132 | 34.3132 | 34.4188 | 34.5317 | 34.3824 | 34.3495 | 34.3714 | 33.9034 | 34.3672 | 35.6739 | 35.2851 | 36.1222 | 36.066 | 33.5412 | 93.1386 | 93.1339 | 93.1954
2022-09-08 02:38 | 4:48 | 17.0769 | 17.4384 | 19.9825 | 34.4132 | 34.4222 | 33.9112 | 34.7109 | 35.4082 | 36.5679 | 37.2757 | 36.8367 | 37.8691 | 34.3529 | 34.3097 | 34.2183 | 35.1588 | 35.2906 | 35.734 | 36.3476 | 36.6945 | 20.69 | 16.7668 | 93.0645 | 33.0216 | 33.1207 | 35.1233 | 33.5273 | 33.1705 | 33.5307 | 34.9032 | 34.4492 | 34.1756 | 37.2321 | 36.2502 | 33.5387 | 34.4357 | 36.2552 | 36.5945 | 37.3889 | 36.265 | 33.5123 | 32.569 | 34.3653 | 34.936 | 32.8889 | 34.2918 | 34.4209 | 34.5299 | 34.3666 | 34.3526 | 34.3959 | 33.8825 | 34.3824 | 35.6902 | 35.2759 | 36.1151 | 36.0466 | 33.545 | 93.0204 | 92.9904 | 93.1478
2022-09-08 02:38 | 4:48 | 17.1118 | 17.4232 | 19.9771 | 34.3134 | 34.4228 | 33.9249 | 34.7118 | 35.4309 | 36.5699 | 37.2625 | 36.8567 | 37.8524 | 34.3551 | 34.2916 | 34.2224 | 35.1334 | 35.3033 | 35.7229 | 36.3705 | 36.696 | 20.7056 | 16.7257 | 92.9832 | 32.9173 | 33.1217 | 35.1211 | 33.5092 | 33.1598 | 33.5517 | 34.8888 | 34.4327 | 34.1744 | 37.2276 | 36.2502 | 33.5178 | 34.4339 | 36.2745 | 36.5803 | 37.377 | 36.2629 | 33.4995 | 32.5658 | 34.3773 | 34.9094 | 32.8743 | 34.2875 | 34.4249 | 34.5159 | 34.366 | 34.3604 | 34.3591 | 33.8834 | 34.3666 | 35.6933 | 35.2602 | 36.1195 | 36.0727 | 33.5644 | 92.8687 | 92.9331 | 93.0462
2022-09-08 02:38 | 4:48 | 17.137 | 17.4123 | 19.9794 | 34.4279 | 34.4155 | 33.9157 | 34.7033 | 35.4184 | 36.5714 | 37.2751 | 36.8516 | 37.8687 | 34.3425 | 34.3064 | 34.227 | 35.1544 | 35.3027 | 35.7392 | 36.3456 | 36.7091 | 20.6798 | 16.7714 | 92.8705 | 32.8756 | 33.128 | 35.1153 | 33.5039 | 33.1749 | 33.5342 | 34.9043 | 34.4166 | 34.1748 | 37.2291 | 36.2555 | 33.5414 | 34.4477 | 36.2502 | 36.5763 | 37.3904 | 36.263 | 33.506 | 32.5678 | 34.3569 | 34.9024 | 32.8655 | 34.292 | 34.4249 | 34.5281 | 34.355 | 34.3449 | 34.3593 | 33.8986 | 34.366 | 35.7116 | 35.2888 | 36.136 | 36.0529 | 33.5437 | 92.6425 | 92.8414 | 92.8571
2022-09-08 02:38 | 4:48 | 17.1233 | 17.4436 | 19.9659 | 34.361 | 34.4156 | 33.8998 | 34.7076 | 35.4049 | 36.5654 | 37.2795 | 36.8389 | 37.855 | 34.3567 | 34.3171 | 34.2468 | 35.1606 | 35.296 | 35.7069 | 36.3767 | 36.6985 | 20.6878 | 16.7349 | 92.6963 | 32.9752 | 33.1307 | 35.109 | 33.5069 | 33.1844 | 33.5204 | 34.9016 | 34.4594 | 34.1633 | 37.2373 | 36.2382 | 33.5467 | 34.4518 | 36.2502 | 36.5793 | 37.3997 | 36.2552 | 33.5 | 32.548 | 34.37 | 34.8982 | 32.8685 | 34.2984 | 34.4237 | 34.5265 | 34.3646 | 34.3454 | 34.3825 | 33.8898 | 34.355 | 35.6918 | 35.286 | 36.1183 | 36.0573 | 33.5526 | 92.514 | 92.6527 | 92.7666
2022-09-08 02:38 | 4:48 | 17.0954 | 17.4023 | 19.9429 | 34.358 | 34.4286 | 33.9155 | 34.7088 | 35.4062 | 36.5592 | 37.2632 | 36.8402 | 37.8933 | 34.3457 | 34.304 | 34.2349 | 35.1296 | 35.3084 | 35.7147 | 36.3708 | 36.6947 | 20.6871 | 16.7172 | 92.6452 | 32.9653 | 33.1202 | 35.1149 | 33.5123 | 33.1816 | 33.5387 | 34.8886 | 34.4321 | 34.1853 | 37.2386 | 36.2428 | 33.5399 | 34.4381 | 36.2555 | 36.5976 | 37.3837 | 36.2745 | 33.5015 | 32.545 | 34.369 | 34.9193 | 32.8746 | 34.3025 | 34.412 | 34.5041 | 34.3808 | 34.3481 | 34.3662 | 33.8969 | 34.3646 | 35.7184 | 35.2868 | 36.1058 | 36.0499 | 33.5548 | 92.4217 | 92.5012 | 92.7692
2022-09-08 02:38 | 4:48 | 17.0021 | 17.3453 | 19.8682 | 34.3635 | 34.4215 | 33.9272 | 34.6977 | 35.4137 | 36.5499 | 37.2687 | 36.8459 | 37.8835 | 34.3453 | 34.3302 | 34.236 | 35.1487 | 35.3133 | 35.7191 | 36.3623 | 36.7012 | 20.6771 | 16.6894 | 92.3567 | 33.0684 | 33.1373 | 35.1133 | 33.4995 | 33.1586 | 33.5178 | 34.9113 | 34.4393 | 34.1974 | 37.2396 | 36.2608 | 33.539 | 34.446 | 36.2382 | 36.5869 | 37.4014 | 36.2502 | 33.506 | 32.5445 | 34.3391 | 34.9055 | 32.8531 | 34.2946 | 34.4337 | 34.5163 | 34.3791 | 34.37 | 34.3616 | 33.8915 | 34.3808 | 35.7115 | 35.2734 | 36.1329 | 36.0717 | 33.5403 | 92.2314 | 92.3295 | 92.6919
2022-09-08 02:39 | 4:48 | 16.9485 | 17.31 | 19.8386 | 34.3494 | 34.4055 | 33.9337 | 34.6999 | 35.4394 | 36.5481 | 37.272 | 36.8602 | 37.875 | 34.3452 | 34.3257 | 34.2254 | 35.1565 | 35.2931 | 35.7258 | 36.3447 | 36.6986 | 20.632 | 16.6122 | 92.4164 | 32.9132 | 33.1146 | 35.1058 | 33.506 | 33.1839 | 33.5414 | 34.9088 | 34.4393 | 34.1883 | 37.2464 | 36.2407 | 33.5474 | 34.434 | 36.2428 | 36.5833 | 37.3766 | 36.2502 | 33.4872 | 32.5193 | 34.364 | 34.9113 | 32.8582 | 34.2906 | 34.4367 | 34.5282 | 34.3903 | 34.3598 | 34.3556 | 33.8828 | 34.3791 | 35.7058 | 35.2722 | 36.1349 | 36.0518 | 33.5414 | 92.1836 | 92.2617 | 92.6133
2022-09-08 02:39 | 4:49 | 16.9183 | 17.2848 | 19.8834 | 34.2684 | 34.4186 | 33.9228 | 34.706 | 35.4327 | 36.5619 | 37.2701 | 36.8515 | 37.8713 | 34.3377 | 34.3133 | 34.2201 | 35.1498 | 35.2934 | 35.7289 | 36.3744 | 36.6982 | 20.6251 | 16.5828 | 92.3216 | 33.0066 | 33.1265 | 35.0939 | 33.5 | 33.1504 | 33.5467 | 34.8865 | 34.4531 | 34.1812 | 37.2311 | 36.251 | 33.5356 | 34.4436 | 36.2608 | 36.5945 | 37.383 | 36.2555 | 33.4957 | 32.528 | 34.3336 | 34.8984 | 32.8401 | 34.2902 | 34.4328 | 34.5365 | 34.3563 | 34.3728 | 34.3568 | 33.8902 | 34.3903 | 35.7092 | 35.2642 | 36.1231 | 36.0548 | 33.5463 | 92.0177 | 92.0783 | 92.482
2022-09-08 02:39 | 4:49 | 17.0793 | 17.2491 | 19.7978 | 34.3877 | 34.4088 | 33.9127 | 34.6899 | 35.4397 | 36.5541 | 37.2758 | 36.8475 | 37.894 | 34.3544 | 34.3169 | 34.2225 | 35.1237 | 35.2913 | 35.7102 | 36.3511 | 36.7047 | 20.6059 | 16.5965 | 92.1806 | 33.046 | 33.1233 | 35.0941 | 33.5015 | 33.176 | 33.5399 | 34.9082 | 34.4406 | 34.1946 | 37.2426 | 36.2441 | 33.5359 | 34.4425 | 36.2407 | 36.5732 | 37.4017 | 36.2382 | 33.5004 | 32.5317 | 34.3567 | 34.9114 | 32.8482 | 34.2858 | 34.4064 | 34.5052 | 34.3596 | 34.3541 | 34.3491 | 33.8833 | 34.3563 | 35.7112 | 35.2683 | 36.1386 | 36.0771 | 33.5304 | 91.9076 | 91.9402 | 92.405
2022-09-08 02:39 | 4:49 | 17.0568 | 17.2677 | 19.8325 | 34.2546 | 34.4159 | 33.9006 | 34.6949 | 35.4394 | 36.5473 | 37.2674 | 36.8579 | 37.8954 | 34.3551 | 34.2931 | 34.216 | 35.1344 | 35.2863 | 35.7284 | 36.3751 | 36.7085 | 20.6141 | 16.575 | 92.213 | 32.9653 | 33.1046 | 35.1019 | 33.506 | 33.1768 | 33.539 | 34.8903 | 34.4418 | 34.2125 | 37.2486 | 36.2361 | 33.5078 | 34.4314 | 36.251 | 36.6003 | 37.3893 | 36.2428 | 33.4821 | 32.5144 | 34.3379 | 34.8932 | 32.8369 | 34.286 | 34.4295 | 34.5077 | 34.3643 | 34.3684 | 34.3578 | 33.8854 | 34.3596 | 35.7021 | 35.2652 | 36.1315 | 36.072 | 33.544 | 91.9094 | 91.8641 | 92.3192
2022-09-08 02:39 | 4:49 | 16.9571 | 17.2337 | 19.8073 | 34.3574 | 34.4246 | 33.9048 | 34.7025 | 35.4381 | 36.5471 | 37.2541 | 36.8634 | 37.879 | 34.3407 | 34.3144 | 34.2233 | 35.1311 | 35.3039 | 35.7474 | 36.3612 | 36.699 | 20.6188 | 16.5941 | 92.2409 | 33.0221 | 33.1238 | 35.0849 | 33.4872 | 33.1776 | 33.5474 | 34.9093 | 34.444 | 34.1681 | 37.2347 | 36.2334 | 33.5182 | 34.444 | 36.2441 | 36.587 | 37.3863 | 36.2608 | 33.4783 | 32.5311 | 34.3216 | 34.9117 | 32.8239 | 34.2851 | 34.4129 | 34.5046 | 34.3538 | 34.3537 | 34.3323 | 33.8697 | 34.3643 | 35.7257 | 35.2752 | 36.1335 | 36.073 | 33.5486 | 91.9301 | 91.9124 | 92.4299
2022-09-08 02:39 | 4:49 | 16.9493 | 17.2397 | 19.8101 | 34.2899 | 34.4184 | 33.9077 | 34.694 | 35.4315 | 36.5508 | 37.2615 | 36.8781 | 37.8875 | 34.3234 | 34.304 | 34.2148 | 35.1414 | 35.2837 | 35.7206 | 36.3643 | 36.6896 | 20.6176 | 16.6028 | 92.2706 | 32.9095 | 33.1292 | 35.1063 | 33.4957 | 33.1694 | 33.5356 | 34.8894 | 34.4271 | 34.1634 | 37.2418 | 36.2439 | 33.5258 | 34.4436 | 36.2361 | 36.6031 | 37.3785 | 36.2407 | 33.4745 | 32.5075 | 34.346 | 34.9136 | 32.8212 | 34.2716 | 34.4178 | 34.5253 | 34.3796 | 34.3535 | 34.3552 | 33.8713 | 34.3538 | 35.7325 | 35.2717 | 36.1434 | 36.0748 | 33.5451 | 91.9492 | 91.9705 | 92.5255
2022-09-08 02:40 | 4:50 | 17.004 | 17.2576 | 19.8031 | 34.3564 | 34.4199 | 33.9094 | 34.6943 | 35.4262 | 36.576 | 37.2737 | 36.8724 | 37.8894 | 34.3609 | 34.3186 | 34.2369 | 35.1371 | 35.285 | 35.7293 | 36.3677 | 36.7241 | 20.6066 | 16.6191 | 92.2549 | 32.9298 | 33.109 | 35.1001 | 33.5004 | 33.176 | 33.5359 | 34.8918 | 34.4507 | 34.1979 | 37.2354 | 36.2266 | 33.5027 | 34.434 | 36.2334 | 36.6055 | 37.3979 | 36.251 | 33.4898 | 32.5296 | 34.3453 | 34.9192 | 32.8166 | 34.2707 | 34.4223 | 34.4931 | 34.3631 | 34.3607 | 34.3319 | 33.8828 | 34.3796 | 35.7256 | 35.277 | 36.1172 | 36.0798 | 33.5502 | 92.022 | 92.0331 | 92.4834
2022-09-08 02:40 | 4:50 | 16.8598 | 17.1498 | 19.7436 | 34.3308 | 34.4174 | 33.8992 | 34.7021 | 35.4205 | 36.5492 | 37.2808 | 36.8545 | 37.8843 | 34.3622 | 34.3119 | 34.2175 | 35.1341 | 35.3015 | 35.7177 | 36.365 | 36.721 | 20.5814 | 16.5932 | 92.1717 | 32.8926 | 33.1068 | 35.091 | 33.4821 | 33.1725 | 33.5078 | 34.9042 | 34.4273 | 34.1766 | 37.2288 | 36.2431 | 33.5185 | 34.4456 | 36.2439 | 36.5967 | 37.3651 | 36.2441 | 33.4584 | 32.5216 | 34.3487 | 34.9014 | 32.807 | 34.2963 | 34.4268 | 34.502 | 34.3827 | 34.36 | 34.3425 | 33.887 | 34.3631 | 35.7086 | 35.27 | 36.1321 | 36.0711 | 33.542 | 91.9933 | 92.1604 | 92.5438
2022-09-08 02:40 | 4:50 | 16.8735 | 17.1678 | 19.7103 | 34.3693 | 34.4156 | 33.9072 | 34.6988 | 35.4172 | 36.5483 | 37.2735 | 36.8623 | 37.8837 | 34.3494 | 34.3025 | 34.2331 | 35.1133 | 35.279 | 35.7191 | 36.3509 | 36.7134 | 20.5567 | 16.5158 | 92.3491 | 32.8265 | 33.09 | 35.0882 | 33.4783 | 33.1393 | 33.5182 | 34.8883 | 34.4365 | 34.1716 | 37.2355 | 36.2257 | 33.5105 | 34.4281 | 36.2266 | 36.5787 | 37.3784 | 36.2361 | 33.4689 | 32.4994 | 34.3282 | 34.9138 | 32.7983 | 34.2767 | 34.4336 | 34.4957 | 34.3615 | 34.3436 | 34.3407 | 33.8776 | 34.3827 | 35.7168 | 35.2683 | 36.1268 | 36.0662 | 33.5353 | 92.1475 | 92.2053 | 92.6419
2022-09-08 02:40 | 4:50 | 16.7858 | 17.1092 | 19.6549 | 34.2638 | 34.4161 | 33.9027 | 34.6913 | 35.4379 | 36.5511 | 37.2681 | 36.8465 | 37.8982 | 34.363 | 34.3256 | 34.214 | 35.1452 | 35.2854 | 35.707 | 36.3497 | 36.7101 | 20.5258 | 16.4902 | 92.5198 | 32.899 | 33.0871 | 35.094 | 33.4745 | 33.1512 | 33.5258 | 34.8927 | 34.4315 | 34.176 | 37.2384 | 36.2069 | 33.5106 | 34.4317 | 36.2431 | 36.5899 | 37.3717 | 36.2334 | 33.4569 | 32.4802 | 34.3368 | 34.894 | 32.7897 | 34.2881 | 34.4344 | 34.4831 | 34.3912 | 34.3616 | 34.3325 | 33.8605 | 34.3615 | 35.7139 | 35.2687 | 36.1217 | 36.0763 | 33.5675 | 92.3074 | 92.3389 | 92.7588
2022-09-08 02:40 | 4:50 | 16.8118 | 17.1849 | 19.7119 | 34.2136 | 34.3989 | 33.8861 | 34.6966 | 35.4145 | 36.5419 | 37.268 | 36.8578 | 37.8725 | 34.3474 | 34.308 | 34.2291 | 35.1129 | 35.2768 | 35.7112 | 36.3458 | 36.696 | 20.5048 | 16.609 | 92.5209 | 33.0057 | 33.0787 | 35.0682 | 33.4898 | 33.1526 | 33.5027 | 34.9067 | 34.4408 | 34.1831 | 37.2246 | 36.2322 | 33.5108 | 34.4123 | 36.2257 | 36.5778 | 37.3755 | 36.2439 | 33.4614 | 32.5014 | 34.3194 | 34.9008 | 32.8103 | 34.2839 | 34.4054 | 34.4669 | 34.3688 | 34.3513 | 34.334 | 33.8918 | 34.3912 | 35.7151 | 35.2596 | 36.1453 | 36.0743 | 33.5334 | 92.5201 | 92.4624 | 92.808
2022-09-08 02:40 | 4:50 | 15.5467 | 16.7355 | 19.3497 | 34.2195 | 34.4235 | 33.8834 | 34.6946 | 35.4171 | 36.5513 | 37.2576 | 36.8453 | 37.8743 | 34.3508 | 34.3271 | 34.2083 | 35.1121 | 35.2621 | 35.7158 | 36.3346 | 36.69 | 20.6454 | 17.1028 | 92.6025 | 32.9867 | 33.0962 | 35.0611 | 33.4584 | 33.1292 | 33.5185 | 34.8892 | 34.4226 | 34.1714 | 37.2272 | 36.2235 | 33.5118 | 34.4251 | 36.2069 | 36.5857 | 37.3798 | 36.2266 | 33.444 | 32.4924 | 34.322 | 34.8852 | 32.7926 | 34.2905 | 34.42 | 34.4927 | 34.3942 | 34.3606 | 34.3285 | 33.846 | 34.3688 | 35.697 | 35.2736 | 36.1369 | 36.0718 | 33.5335 | 92.5767 | 92.5257 | 92.8334
2022-09-08 02:41 | 4:50 | 15.2573 | 16.485 | 19.0903 | 34.2228 | 34.3951 | 33.8751 | 34.6873 | 35.4082 | 36.5314 | 37.2552 | 36.8483 | 37.8618 | 34.3715 | 34.3227 | 34.216 | 35.1197 | 35.2644 | 35.6948 | 36.3414 | 36.7036 | 21.1065 | 17.9565 | 92.5559 | 33.1262 | 33.0912 | 35.048 | 33.4689 | 33.1287 | 33.5105 | 34.89 | 34.42 | 34.1597 | 37.2206 | 36.1995 | 33.5112 | 34.4404 | 36.2322 | 36.5773 | 37.3816 | 36.2431 | 33.4535 | 32.4894 | 34.3015 | 34.8827 | 32.7689 | 34.2812 | 34.4248 | 34.4716 | 34.4051 | 34.3507 | 34.3383 | 33.8783 | 34.3942 | 35.7085 | 35.2796 | 36.1412 | 36.0565 | 33.5412 | 92.6493 | 92.631 | 92.881
2022-09-08 02:41 | 4:51 | 14.9857 | 16.2936 | 18.8688 | 34.0414 | 34.4199 | 33.8754 | 34.6745 | 35.4006 | 36.5192 | 37.2804 | 36.8358 | 37.8594 | 34.3569 | 34.3273 | 34.2198 | 35.1287 | 35.2574 | 35.7161 | 36.3201 | 36.7068 | 21.7923 | 19.0492 | 92.6477 | 33.2432 | 33.1008 | 35.0817 | 33.4569 | 33.1379 | 33.5106 | 34.8887 | 34.4068 | 34.1609 | 37.1943 | 36.2073 | 33.5224 | 34.4322 | 36.2235 | 36.5866 | 37.3507 | 36.2257 | 33.4432 | 32.466 | 34.3243 | 34.8738 | 32.7561 | 34.2769 | 34.4016 | 34.4777 | 34.3891 | 34.36 | 34.3337 | 33.8823 | 34.4051 | 35.6995 | 35.2623 | 36.1295 | 36.0624 | 33.5273 | 92.677 | 92.8143 | 92.9282
2022-09-08 02:41 | 4:51 | 14.7308 | 16.0699 | 18.6413 | 34.138 | 34.4204 | 33.8698 | 34.667 | 35.4157 | 36.5534 | 37.2517 | 36.8426 | 37.8881 | 34.3462 | 34.3233 | 34.2314 | 35.0996 | 35.2477 | 35.7052 | 36.3276 | 36.7058 | 22.5646 | 20.2443 | 92.6384 | 33.3136 | 33.1105 | 35.068 | 33.4614 | 33.1462 | 33.5108 | 34.8899 | 34.4258 | 34.1566 | 37.2308 | 36.2178 | 33.4928 | 34.433 | 36.1995 | 36.5714 | 37.3664 | 36.2069 | 33.4483 | 32.4948 | 34.3065 | 34.8631 | 32.7726 | 34.2715 | 34.4262 | 34.472 | 34.3939 | 34.357 | 34.323 | 33.8537 | 34.3891 | 35.6995 | 35.2544 | 36.1377 | 36.0786 | 33.5306 | 92.8239 | 92.9265 | 93.0704
2022-09-08 02:41 | 4:51 | 14.5595 | 15.9052 | 18.5371 | 34.1292 | 34.3865 | 33.8797 | 34.664 | 35.4067 | 36.5372 | 37.2618 | 36.853 | 37.876 | 34.3559 | 34.3017 | 34.2017 | 35.1094 | 35.2482 | 35.6891 | 36.3632 | 36.6915 | 23.3959 | 21.4733 | 92.6758 | 33.2734 | 33.1007 | 35.0702 | 33.444 | 33.1277 | 33.5118 | 34.8873 | 34.4092 | 34.1606 | 37.2164 | 36.2112 | 33.4989 | 34.4184 | 36.2073 | 36.584 | 37.3832 | 36.2322 | 33.4353 | 32.4568 | 34.3102 | 34.8737 | 32.7504 | 34.2877 | 34.4062 | 34.4674 | 34.4034 | 34.3604 | 34.3129 | 33.8513 | 34.3939 | 35.7112 | 35.2391 | 36.1355 | 36.071 | 33.5524 | 92.9078 | 93.0029 | 93.0223
2022-09-08 02:41 | 4:51 | 14.3941 | 15.7667 | 18.4119 | 33.9092 | 34.415 | 33.867 | 34.6519 | 35.393 | 36.5455 | 37.2661 | 36.8466 | 37.8872 | 34.3773 | 34.3313 | 34.2146 | 35.1144 | 35.2452 | 35.6983 | 36.3423 | 36.6962 | 24.1881 | 22.568 | 92.8205 | 33.3649 | 33.0992 | 35.0665 | 33.4535 | 33.1471 | 33.5112 | 34.8954 | 34.4106 | 34.1665 | 37.2179 | 36.1975 | 33.4993 | 34.4109 | 36.2178 | 36.5718 | 37.3737 | 36.2235 | 33.4247 | 32.4791 | 34.316 | 34.8709 | 32.7627 | 34.2848 | 34.4174 | 34.462 | 34.3994 | 34.3585 | 34.3253 | 33.8815 | 34.4034 | 35.6993 | 35.2593 | 36.1466 | 36.0676 | 33.5178 | 93.0812 | 93.0907 | 93.1342
2022-09-08 02:41 | 4:51 | 14.2107 | 15.5887 | 18.2312 | 34.0246 | 34.4065 | 33.8963 | 34.6663 | 35.399 | 36.5302 | 37.2633 | 36.8363 | 37.8753 | 34.3603 | 34.3329 | 34.2016 | 35.094 | 35.2471 | 35.6805 | 36.3564 | 36.6906 | 24.9745 | 23.6121 | 92.8106 | 33.449 | 33.1059 | 35.0627 | 33.4432 | 33.1644 | 33.5224 | 34.9041 | 34.4065 | 34.1635 | 37.2157 | 36.2041 | 33.5114 | 34.4045 | 36.2112 | 36.5693 | 37.3508 | 36.1995 | 33.4463 | 32.4535 | 34.3005 | 34.8494 | 32.7836 | 34.2906 | 34.4225 | 34.4595 | 34.3919 | 34.3602 | 34.3222 | 33.8733 | 34.3994 | 35.7065 | 35.2657 | 36.1337 | 36.0614 | 33.5281 | 93.2529 | 93.2034 | 93.2531
2022-09-08 02:42 | 4:52 | 14.104 | 15.5043 | 18.1003 | 34.0171 | 34.3895 | 33.8541 | 34.6513 | 35.4216 | 36.5278 | 37.2562 | 36.8259 | 37.8562 | 34.3519 | 34.3225 | 34.217 | 35.1214 | 35.2344 | 35.6891 | 36.3447 | 36.7056 | 25.658 | 24.5224 | 92.8126 | 33.4085 | 33.1145 | 35.0588 | 33.4483 | 33.1488 | 33.4928 | 34.8961 | 34.4184 | 34.1553 | 37.2094 | 36.209 | 33.4998 | 34.4088 | 36.1975 | 36.5794 | 37.3698 | 36.2073 | 33.4519 | 32.474 | 34.3105 | 34.8521 | 32.7653 | 34.2847 | 34.3985 | 34.4501 | 34.3947 | 34.3558 | 34.3077 | 33.8384 | 34.3919 | 35.7084 | 35.248 | 36.114 | 36.0828 | 33.525 | 93.2594 | 93.3315 | 93.1557
2022-09-08 02:42 | 4:52 | 13.9598 | 15.335 | 17.9522 | 34.0037 | 34.3977 | 33.8735 | 34.6384 | 35.3931 | 36.5541 | 37.2515 | 36.8366 | 37.8593 | 34.3494 | 34.313 | 34.2013 | 35.1199 | 35.2267 | 35.6873 | 36.3513 | 36.7047 | 26.2921 | 25.3343 | 92.9969 | 33.5381 | 33.114 | 35.0683 | 33.4353 | 33.1696 | 33.4989 | 34.9018 | 34.3981 | 34.1487 | 37.2094 | 36.2039 | 33.52 | 34.4123 | 36.2041 | 36.5781 | 37.3475 | 36.2178 | 33.4255 | 32.4787 | 34.3199 | 34.8647 | 32.7708 | 34.2827 | 34.4203 | 34.4713 | 34.4015 | 34.369 | 34.3097 | 33.8621 | 34.3947 | 35.722 | 35.2607 | 36.1505 | 36.0762 | 33.5228 | 93.4008 | 93.4981 | 93.3596
2022-09-08 02:42 | 4:52 | 13.7881 | 15.2302 | 17.796 | 33.911 | 34.3806 | 33.853 | 34.6437 | 35.4123 | 36.5292 | 37.2558 | 36.8502 | 37.8631 | 34.3616 | 34.3182 | 34.2024 | 35.1114 | 35.227 | 35.6866 | 36.3543 | 36.693 | 26.8548 | 26.0255 | 93.1424 | 33.6604 | 33.1225 | 35.0755 | 33.4247 | 33.1513 | 33.4993 | 34.8981 | 34.4097 | 34.1317 | 37.2161 | 36.2018 | 33.5061 | 34.4024 | 36.209 | 36.5802 | 37.3619 | 36.2112 | 33.4351 | 32.4615 | 34.3239 | 34.8628 | 32.7805 | 34.2799 | 34.409 | 34.4616 | 34.3819 | 34.3595 | 34.2916 | 33.8438 | 34.4015 | 35.7345 | 35.249 | 36.137 | 36.0643 | 33.5319 | 93.577 | 93.6431 | 93.4831
2022-09-08 02:42 | 4:52 | 13.7122 | 15.0803 | 17.7141 | 33.8849 | 34.3956 | 33.8634 | 34.6324 | 35.3738 | 36.5438 | 37.245 | 36.8238 | 37.8537 | 34.3484 | 34.338 | 34.2002 | 35.101 | 35.2296 | 35.6824 | 36.3447 | 36.686 | 27.3546 | 26.6163 | 93.2992 | 33.616 | 33.1007 | 35.0507 | 33.4463 | 33.1574 | 33.5114 | 34.892 | 34.4175 | 34.1669 | 37.2134 | 36.194 | 33.4885 | 34.4033 | 36.2039 | 36.5878 | 37.3575 | 36.1975 | 33.4266 | 32.4511 | 34.3049 | 34.8494 | 32.7864 | 34.2827 | 34.4133 | 34.4672 | 34.3962 | 34.3511 | 34.3064 | 33.845 | 34.3819 | 35.7135 | 35.2501 | 36.1522 | 36.0548 | 33.5158 | 93.7541 | 93.7574 | 93.5517
2022-09-08 02:42 | 4:52 | 13.5851 | 14.973 | 17.565 | 33.916 | 34.3714 | 33.8427 | 34.6099 | 35.3869 | 36.5242 | 37.2388 | 36.8498 | 37.8863 | 34.3568 | 34.3344 | 34.1972 | 35.1068 | 35.237 | 35.6992 | 36.3454 | 36.7008 | 27.7892 | 27.1185 | 93.3686 | 33.6583 | 33.1195 | 35.0586 | 33.4519 | 33.1563 | 33.4998 | 34.8861 | 34.4111 | 34.1613 | 37.2031 | 36.185 | 33.5053 | 34.3931 | 36.2018 | 36.5695 | 37.381 | 36.2041 | 33.4353 | 32.4562 | 34.3197 | 34.866 | 32.7856 | 34.2812 | 34.4091 | 34.4415 | 34.4025 | 34.3678 | 34.3171 | 33.8612 | 34.3962 | 35.7276 | 35.2579 | 36.1575 | 36.0837 | 33.5346 | 93.9425 | 93.9552 | 93.6606
2022-09-08 02:42 | 4:52 | 13.466 | 14.8401 | 17.4535 | 33.8785 | 34.3959 | 33.8491 | 34.6312 | 35.39 | 36.5191 | 37.2595 | 36.8252 | 37.8548 | 34.3324 | 34.3374 | 34.1942 | 35.0825 | 35.203 | 35.6948 | 36.3345 | 36.6947 | 28.168 | 27.5449 | 93.2892 | 33.7649 | 33.1089 | 35.0664 | 33.4255 | 33.1822 | 33.52 | 34.8945 | 34.4058 | 34.1279 | 37.2207 | 36.1825 | 33.5078 | 34.3932 | 36.194 | 36.5751 | 37.3625 | 36.209 | 33.4125 | 32.4712 | 34.3389 | 34.8771 | 32.7866 | 34.2935 | 34.4104 | 34.4315 | 34.4213 | 34.3485 | 34.304 | 33.8379 | 34.4025 | 35.7148 | 35.2627 | 36.134 | 36.0955 | 33.5209 | 94.0921 | 94.1637 | 93.8107
2022-09-08 02:43 | 4:52 | 13.3979 | 14.7565 | 17.3669 | 33.8497 | 34.3591 | 33.8253 | 34.6043 | 35.3853 | 36.5277 | 37.2707 | 36.8344 | 37.8742 | 34.3554 | 34.3303 | 34.1886 | 35.071 | 35.213 | 35.6867 | 36.3353 | 36.6859 | 28.5195 | 27.9259 | 93.5015 | 33.8085 | 33.1062 | 35.0471 | 33.4351 | 33.1677 | 33.5061 | 34.8965 | 34.4061 | 34.1393 | 37.2041 | 36.1805 | 33.5043 | 34.3865 | 36.185 | 36.5823 | 37.3673 | 36.2039 | 33.4246 | 32.4441 | 34.309 | 34.8752 | 32.7833 | 34.3064 | 34.409 | 34.4031 | 34.4119 | 34.3715 | 34.3302 | 33.8278 | 34.4213 | 35.7009 | 35.2551 | 36.1463 | 36.0785 | 33.5329 | 94.2435 | 94.2869 | 93.8814
2022-09-08 02:43 | 4:53 | 13.259 | 14.6049 | 17.2655 | 33.8804 | 34.3593 | 33.8453 | 34.6158 | 35.3842 | 36.516 | 37.2423 | 36.8398 | 37.8502 | 34.3674 | 34.3228 | 34.1988 | 35.0753 | 35.2089 | 35.6776 | 36.3235 | 36.6723 | 28.795 | 28.2304 | 93.5491 | 33.8262 | 33.0999 | 35.0549 | 33.4266 | 33.1873 | 33.4885 | 34.8979 | 34.4 | 34.1505 | 37.1974 | 36.1914 | 33.4898 | 34.394 | 36.1825 | 36.5666 | 37.3776 | 36.2018 | 33.4199 | 32.4507 | 34.3221 | 34.8481 | 32.8095 | 34.2832 | 34.4054 | 34.4401 | 34.4074 | 34.3544 | 34.3257 | 33.8479 | 34.4119 | 35.726 | 35.2623 | 36.1448 | 36.0793 | 33.5252 | 94.4002 | 94.4701 | 93.923
2022-09-08 02:43 | 4:53 | 13.1244 | 14.5133 | 17.1498 | 33.8998 | 34.3825 | 33.8367 | 34.6159 | 35.3751 | 36.5219 | 37.2419 | 36.8347 | 37.8604 | 34.3575 | 34.3372 | 34.1898 | 35.0794 | 35.2144 | 35.6821 | 36.343 | 36.7001 | 29.0501 | 28.5176 | 93.6941 | 33.9631 | 33.1215 | 35.0451 | 33.4353 | 33.1728 | 33.5053 | 34.8872 | 34.4037 | 34.1393 | 37.2171 | 36.2018 | 33.4993 | 34.3781 | 36.1805 | 36.5841 | 37.3687 | 36.194 | 33.4329 | 32.4777 | 34.3349 | 34.8709 | 32.8087 | 34.3067 | 34.3984 | 34.4203 | 34.4132 | 34.3497 | 34.3133 | 33.8522 | 34.4074 | 35.7109 | 35.2516 | 36.1505 | 36.08 | 33.5249 | 94.5831 | 94.5695 | 94.0938
2022-09-08 02:43 | 4:53 | 13.052 | 14.4243 | 17.0285 | 33.8372 | 34.3662 | 33.8266 | 34.6033 | 35.3855 | 36.5266 | 37.2516 | 36.8428 | 37.8611 | 34.353 | 34.3556 | 34.183 | 35.0849 | 35.1948 | 35.6818 | 36.3256 | 36.6688 | 29.2729 | 28.7492 | 93.8987 | 33.8465 | 33.1 | 35.0246 | 33.4125 | 33.1778 | 33.5078 | 34.8819 | 34.4079 | 34.1477 | 37.1861 | 36.1751 | 33.5013 | 34.3862 | 36.1914 | 36.5684 | 37.3622 | 36.185 | 33.4109 | 32.4696 | 34.3299 | 34.8578 | 32.7997 | 34.304 | 34.4037 | 34.4203 | 34.4166 | 34.3436 | 34.3169 | 33.8345 | 34.4132 | 35.7203 | 35.2631 | 36.1316 | 36.0658 | 33.5229 | 94.75 | 94.7465 | 94.2159
2022-09-08 02:43 | 4:53 | 12.9221 | 14.3205 | 16.8769 | 33.735 | 34.3616 | 33.8351 | 34.5881 | 35.3832 | 36.5048 | 37.2326 | 36.8249 | 37.8602 | 34.3742 | 34.3421 | 34.1733 | 35.0934 | 35.2146 | 35.6563 | 36.311 | 36.661 | 29.4799 | 28.9656 | 93.9463 | 33.9582 | 33.0976 | 35.0414 | 33.4246 | 33.1778 | 33.5043 | 34.8878 | 34.401 | 34.13 | 37.1893 | 36.1893 | 33.5048 | 34.3835 | 36.2018 | 36.5363 | 37.3593 | 36.1825 | 33.3935 | 32.4752 | 34.3347 | 34.8605 | 32.8175 | 34.3165 | 34.4099 | 34.4028 | 34.4133 | 34.3677 | 34.2931 | 33.8419 | 34.4166 | 35.7101 | 35.2561 | 36.1409 | 36.0746 | 33.5303 | 94.8513 | 94.8489 | 94.2391
2022-09-08 02:43 | 4:53 | 12.9147 | 14.23 | 16.8068 | 33.7212 | 34.3556 | 33.8283 | 34.5997 | 35.3769 | 36.4984 | 37.246 | 36.8329 | 37.8652 | 34.3594 | 34.3439 | 34.1718 | 35.0823 | 35.231 | 35.6636 | 36.3284 | 36.6865 | 29.6464 | 29.1528 | 94.0055 | 34.0536 | 33.1003 | 35.052 | 33.4199 | 33.1739 | 33.4898 | 34.8995 | 34.4047 | 34.1408 | 37.1847 | 36.177 | 33.4772 | 34.3797 | 36.1751 | 36.5571 | 37.3493 | 36.1805 | 33.4055 | 32.4664 | 34.3304 | 34.8705 | 32.809 | 34.296 | 34.4007 | 34.41 | 34.421 | 34.3647 | 34.3144 | 33.8481 | 34.4133 | 35.7082 | 35.26 | 36.1363 | 36.089 | 33.5284 | 94.8946 | 94.8987 | 94.3093
2022-09-08 02:44 | 4:53 | 12.8 | 14.1281 | 16.6168 | 33.697 | 34.3568 | 33.8271 | 34.5773 | 35.3788 | 36.5027 | 37.2604 | 36.8422 | 37.8822 | 34.3448 | 34.3364 | 34.1813 | 35.0847 | 35.2067 | 35.6824 | 36.3257 | 36.6742 | 29.7999 | 29.3268 | 94.0173 | 34.002 | 33.0924 | 35.0284 | 33.4329 | 33.1906 | 33.4993 | 34.8792 | 34.406 | 34.1445 | 37.218 | 36.1934 | 33.4894 | 34.3836 | 36.1893 | 36.5599 | 37.3474 | 36.1914 | 33.412 | 32.4718 | 34.3153 | 34.8484 | 32.808 | 34.2982 | 34.3993 | 34.4062 | 34.4104 | 34.3769 | 34.304 | 33.8359 | 34.421 | 35.723 | 35.2712 | 36.1371 | 36.0725 | 33.514 | 94.9613 | 95.0292 | 94.3803
2022-09-08 02:44 | 4:54 | 12.675 | 14.008 | 16.5001 | 33.819 | 34.3491 | 33.8399 | 34.5893 | 35.3554 | 36.5106 | 37.2501 | 36.8333 | 37.8758 | 34.3777 | 34.3341 | 34.1743 | 35.0888 | 35.1894 | 35.6655 | 36.3211 | 36.6651 | 29.9325 | 29.4916 | 94.1787 | 34.073 | 33.0889 | 35.0421 | 33.4109 | 33.1666 | 33.5013 | 34.8894 | 34.395 | 34.1396 | 37.182 | 36.1899 | 33.4663 | 34.3798 | 36.177 | 36.5667 | 37.342 | 36.2018 | 33.3954 | 32.4755 | 34.335 | 34.8595 | 32.8317 | 34.3148 | 34.4127 | 34.4086 | 34.4134 | 34.3774 | 34.3186 | 33.8368 | 34.4104 | 35.7105 | 35.265 | 36.1237 | 36.0801 | 33.4977 | 95.0315 | 95.0657 | 94.4257
2022-09-08 02:44 | 4:54 | 12.5982 | 13.9299 | 16.5021 | 33.8473 | 34.3578 | 33.8253 | 34.5862 | 35.363 | 36.4986 | 37.2475 | 36.8166 | 37.8621 | 34.367 | 34.3359 | 34.1636 | 35.089 | 35.1841 | 35.6781 | 36.3142 | 36.6422 | 30.0512 | 29.5911 | 94.253 | 34.1523 | 33.0945 | 35.045 | 33.3935 | 33.165 | 33.5048 | 34.8918 | 34.4054 | 34.1384 | 37.1724 | 36.1811 | 33.4553 | 34.3721 | 36.1934 | 36.5559 | 37.3532 | 36.1751 | 33.3986 | 32.4676 | 34.345 | 34.8456 | 32.8254 | 34.2949 | 34.3996 | 34.3894 | 34.4025 | 34.3715 | 34.3119 | 33.846 | 34.4134 | 35.7031 | 35.2664 | 36.1476 | 36.0713 | 33.5128 | 94.9755 | 95.0157 | 94.3689
2022-09-08 02:44 | 4:54 | 12.4559 | 13.8103 | 16.3291 | 33.6731 | 34.3323 | 33.8162 | 34.5747 | 35.3563 | 36.5048 | 37.2373 | 36.8277 | 37.8612 | 34.3611 | 34.3354 | 34.1629 | 35.0774 | 35.1741 | 35.6442 | 36.285 | 36.6727 | 30.1425 | 29.7178 | 94.0439 | 34.1635 | 33.0939 | 35.0537 | 33.4055 | 33.1742 | 33.4772 | 34.8704 | 34.3969 | 34.132 | 37.1841 | 36.2007 | 33.4832 | 34.3603 | 36.1899 | 36.5589 | 37.3296 | 36.1893 | 33.4218 | 32.4594 | 34.3331 | 34.8504 | 32.8313 | 34.3084 | 34.3892 | 34.3925 | 34.4135 | 34.3838 | 34.3025 | 33.8479 | 34.4025 | 35.719 | 35.2591 | 36.1435 | 36.0818 | 33.4763 | 94.7375 | 94.9206 | 94.2124
2022-09-08 02:44 | 4:54 | 12.3762 | 13.6975 | 16.1721 | 33.7244 | 34.3552 | 33.8062 | 34.5721 | 35.3659 | 36.4983 | 37.2405 | 36.8448 | 37.8507 | 34.3637 | 34.3367 | 34.1519 | 35.079 | 35.1792 | 35.646 | 36.2968 | 36.6641 | 30.2488 | 29.8155 | 93.8788 | 34.2118 | 33.1097 | 35.0571 | 33.412 | 33.179 | 33.4894 | 34.8627 | 34.4008 | 34.1351 | 37.1721 | 36.2018 | 33.4854 | 34.3757 | 36.1811 | 36.5448 | 37.3297 | 36.177 | 33.4055 | 32.4829 | 34.3315 | 34.8493 | 32.8455 | 34.2919 | 34.4122 | 34.3826 | 34.4239 | 34.3832 | 34.3256 | 33.8386 | 34.4135 | 35.7098 | 35.2472 | 36.1401 | 36.0672 | 33.493 | 94.563 | 94.7132 | 94.0027
2022-09-08 02:44 | 4:54 | 12.2843 | 13.6227 | 16.0902 | 33.6626 | 34.3319 | 33.8295 | 34.5606 | 35.3654 | 36.4916 | 37.2148 | 36.8163 | 37.8584 | 34.3526 | 34.3326 | 34.1521 | 35.0742 | 35.1803 | 35.649 | 36.292 | 36.641 | 30.354 | 29.9197 | 93.7516 | 34.1436 | 33.1123 | 35.0465 | 33.3954 | 33.1617 | 33.4663 | 34.8711 | 34.3913 | 34.1191 | 37.1618 | 36.1823 | 33.475 | 34.3784 | 36.2007 | 36.5529 | 37.3407 | 36.1934 | 33.3958 | 32.4799 | 34.3404 | 34.8245 | 32.8222 | 34.3071 | 34.3923 | 34.3957 | 34.4111 | 34.3645 | 34.308 | 33.8316 | 34.4239 | 35.7017 | 35.2599 | 36.144 | 36.0667 | 33.4949 | 94.3098 | 94.4791 | 93.917
2022-09-08 02:45 | 4:55 | 12.1192 | 13.3047 | 16.0331 | 33.7632 | 34.3425 | 33.8028 | 34.5549 | 35.341 | 36.4893 | 37.2213 | 36.8191 | 37.8396 | 34.3495 | 34.3327 | 34.157 | 35.0707 | 35.1685 | 35.6286 | 36.297 | 36.6279 | 30.4226 | 29.9967 | 93.5593 | 34.1459 | 33.0823 | 35.0485 | 33.3986 | 33.1664 | 33.4553 | 34.8766 | 34.3959 | 34.1318 | 37.184 | 36.1906 | 33.4969 | 34.3748 | 36.2018 | 36.5591 | 37.3349 | 36.1899 | 33.4043 | 32.4881 | 34.3428 | 34.8447 | 32.8519 | 34.3096 | 34.401 | 34.4073 | 34.4036 | 34.396 | 34.3271 | 33.8612 | 34.4111 | 35.6962 | 35.2522 | 36.1387 | 36.0784 | 33.4945 | 94.1539 | 94.3219 | 93.7591
2022-09-08 02:45 | 4:55 | 11.6382 | 11.4408 | 15.4265 | 33.6263 | 34.3407 | 33.8214 | 34.557 | 35.3575 | 36.4788 | 37.2274 | 36.8221 | 37.8426 | 34.3526 | 34.3509 | 34.1379 | 35.0874 | 35.1735 | 35.6634 | 36.2957 | 36.6322 | 30.4323 | 30.0432 | 93.5674 | 34.158 | 33.0836 | 35.0261 | 33.4218 | 33.1741 | 33.4832 | 34.8728 | 34.407 | 34.1101 | 37.1822 | 36.197 | 33.4794 | 34.3693 | 36.1823 | 36.5531 | 37.3348 | 36.1811 | 33.3941 | 32.4586 | 34.3299 | 34.8402 | 32.8691 | 34.3162 | 34.3783 | 34.3946 | 34.4305 | 34.3882 | 34.3227 | 33.8406 | 34.4036 | 35.6972 | 35.2616 | 36.1213 | 36.0579 | 33.4963 | 94.0133 | 94.167 | 93.75
2022-09-08 02:45 | 4:55 | 14.1847 | 12.0611 | 17.0638 | 33.589 | 34.3325 | 33.8147 | 34.5489 | 35.3528 | 36.4727 | 37.2102 | 36.8238 | 37.8472 | 34.3604 | 34.3416 | 34.1554 | 35.0649 | 35.1498 | 35.6409 | 36.2855 | 36.6441 | 30.5183 | 30.1109 | 93.5833 | 34.202 | 33.0865 | 35.045 | 33.4055 | 33.1602 | 33.4854 | 34.8733 | 34.3826 | 34.1233 | 37.1808 | 36.1793 | 33.4634 | 34.3689 | 36.1906 | 36.5534 | 37.3245 | 36.2007 | 33.41 | 32.4796 | 34.3308 | 34.836 | 32.8609 | 34.321 | 34.3928 | 34.3862 | 34.4159 | 34.3826 | 34.3273 | 33.8133 | 34.4305 | 35.694 | 35.257 | 36.1343 | 36.0698 | 33.4785 | 93.9379 | 94.0331 | 93.7212
2022-09-08 02:45 | 4:55 | 16.2215 | 13.3963 | 18.8976 | 33.7545 | 34.334 | 33.7957 | 34.5326 | 35.3462 | 36.4811 | 37.2206 | 36.824 | 37.8444 | 34.3449 | 34.3402 | 34.1372 | 35.0661 | 35.1529 | 35.6414 | 36.2715 | 36.632 | 30.5727 | 30.191 | 93.5161 | 34.2435 | 33.0856 | 35.0395 | 33.3958 | 33.1779 | 33.475 | 34.8689 | 34.3864 | 34.1247 | 37.1735 | 36.191 | 33.4779 | 34.375 | 36.197 | 36.5376 | 37.3226 | 36.2018 | 33.4007 | 32.4821 | 34.3489 | 34.8542 | 32.876 | 34.3144 | 34.3933 | 34.3777 | 34.4245 | 34.3866 | 34.3233 | 33.8323 | 34.4159 | 35.6989 | 35.262 | 36.1168 | 36.0756 | 33.4878 | 93.8885 | 93.9946 | 93.7276
2022-09-08 02:45 | 4:55 | 17.7975 | 14.981 | 20.5826 | 33.9385 | 34.3285 | 33.8056 | 34.5245 | 35.3498 | 36.4806 | 37.2211 | 36.8179 | 37.8686 | 34.3454 | 34.3494 | 34.1246 | 35.0716 | 35.1565 | 35.6423 | 36.3023 | 36.6233 | 30.6342 | 30.2493 | 93.5334 | 34.3089 | 33.0804 | 35.0561 | 33.4043 | 33.1903 | 33.4969 | 34.8723 | 34.3956 | 34.1183 | 37.1925 | 36.1924 | 33.472 | 34.3665 | 36.1793 | 36.5461 | 37.3183 | 36.1823 | 33.4007 | 32.4871 | 34.3494 | 34.8537 | 32.8697 | 34.318 | 34.3804 | 34.3956 | 34.4136 | 34.3785 | 34.3017 | 33.8301 | 34.4245 | 35.6746 | 35.2752 | 36.1475 | 36.0736 | 33.4859 | 93.8417 | 93.9681 | 93.6865
2022-09-08 02:45 | 4:55 | 19.0943 | 16.586 | 21.9546 | 33.9971 | 34.3383 | 33.8045 | 34.5322 | 35.3327 | 36.4828 | 37.2222 | 36.8477 | 37.8403 | 34.3481 | 34.3382 | 34.1365 | 35.0748 | 35.1422 | 35.6405 | 36.2928 | 36.6144 | 30.7063 | 30.3158 | 93.4088 | 34.3181 | 33.0868 | 35.0413 | 33.3941 | 33.1802 | 33.4794 | 34.8497 | 34.4142 | 34.1236 | 37.186 | 36.1911 | 33.4862 | 34.3731 | 36.191 | 36.5535 | 37.3467 | 36.1906 | 33.4083 | 32.4989 | 34.3543 | 34.8363 | 32.8768 | 34.3345 | 34.4116 | 34.3873 | 34.4269 | 34.3945 | 34.3313 | 33.8379 | 34.4136 | 35.6868 | 35.2676 | 36.1412 | 36.0699 | 33.4801 | 93.7325 | 93.8655 | 93.5745
2022-09-08 02:46 | 4:55 | 20.2526 | 18.1876 | 23.1731 | 34.1525 | 34.3337 | 33.7992 | 34.5389 | 35.3269 | 36.4762 | 37.2235 | 36.8397 | 37.8476 | 34.37 | 34.3397 | 34.1408 | 35.0736 | 35.1472 | 35.66 | 36.2915 | 36.6277 | 30.7517 | 30.3694 | 93.3853 | 34.2541 | 33.0854 | 35.0406 | 33.41 | 33.1836 | 33.4634 | 34.8674 | 34.4099 | 34.1192 | 37.1748 | 36.1972 | 33.4682 | 34.3702 | 36.1924 | 36.5442 | 37.3101 | 36.197 | 33.3982 | 32.4862 | 34.3716 | 34.8507 | 32.8661 | 34.3127 | 34.3854 | 34.3965 | 34.4188 | 34.3847 | 34.3329 | 33.8385 | 34.4269 | 35.6975 | 35.2565 | 36.1336 | 36.0623 | 33.4819 | 93.6381 | 93.7864 | 93.5375
2022-09-08 02:46 | 4:56 | 21.2128 | 19.6851 | 24.1751 | 34.0957 | 34.323 | 33.8012 | 34.5247 | 35.3415 | 36.4736 | 37.2246 | 36.8376 | 37.8494 | 34.3598 | 34.3627 | 34.1242 | 35.0788 | 35.1625 | 35.6458 | 36.3082 | 36.6313 | 30.8296 | 30.4249 | 93.113 | 34.4041 | 33.075 | 35.0361 | 33.4007 | 33.2035 | 33.4779 | 34.882 | 34.4072 | 34.1259 | 37.1709 | 36.1904 | 33.4829 | 34.3739 | 36.1911 | 36.5653 | 37.3258 | 36.1793 | 33.4008 | 32.5061 | 34.3553 | 34.8688 | 32.8863 | 34.3299 | 34.4085 | 34.3668 | 34.4209 | 34.397 | 34.3225 | 33.8385 | 34.4188 | 35.6883 | 35.2641 | 36.1541 | 36.0608 | 33.4736 | 93.5025 | 93.6815 | 93.4595
2022-09-08 02:46 | 4:56 | 22.0782 | 21.0439 | 25.1777 | 34.2557 | 34.3129 | 33.8204 | 34.5391 | 35.3422 | 36.479 | 37.2289 | 36.84 | 37.8654 | 34.3728 | 34.3474 | 34.1284 | 35.0926 | 35.1408 | 35.6657 | 36.3027 | 36.6167 | 30.8902 | 30.4922 | 93.1651 | 34.4507 | 33.0822 | 35.0369 | 33.4007 | 33.1815 | 33.472 | 34.8578 | 34.3995 | 34.136 | 37.1626 | 36.2006 | 33.4651 | 34.3641 | 36.1972 | 36.5429 | 37.3264 | 36.191 | 33.4193 | 32.5073 | 34.3665 | 34.8622 | 32.907 | 34.3448 | 34.3962 | 34.3864 | 34.4249 | 34.3948 | 34.313 | 33.8349 | 34.4209 | 35.6879 | 35.2684 | 36.1302 | 36.0932 | 33.4703 | 93.466 | 93.6952 | 93.4752
2022-09-08 02:46 | 4:56 | 22.865 | 22.2894 | 25.9741 | 34.3267 | 34.3253 | 33.8028 | 34.5421 | 35.3588 | 36.4697 | 37.224 | 36.8481 | 37.8653 | 34.3541 | 34.3434 | 34.1281 | 35.0836 | 35.1536 | 35.6592 | 36.303 | 36.6237 | 30.9443 | 30.5475 | 93.1934 | 34.4948 | 33.0681 | 35.0533 | 33.4083 | 33.1633 | 33.4862 | 34.8599 | 34.4248 | 34.132 | 37.1672 | 36.2011 | 33.4574 | 34.382 | 36.1904 | 36.5354 | 37.3197 | 36.1924 | 33.4077 | 32.4985 | 34.362 | 34.8655 | 32.9041 | 34.3212 | 34.3828 | 34.3865 | 34.4249 | 34.3973 | 34.3182 | 33.8306 | 34.4249 | 35.6684 | 35.2522 | 36.1609 | 36.0852 | 33.4676 | 93.4403 | 93.5943 | 93.4392
2022-09-08 02:46 | 4:56 | 23.5863 | 23.3839 | 26.6228 | 34.4116 | 34.3222 | 33.8175 | 34.5405 | 35.3555 | 36.4905 | 37.2181 | 36.8343 | 37.862 | 34.3684 | 34.3519 | 34.1274 | 35.0693 | 35.1664 | 35.6498 | 36.3314 | 36.621 | 31.0078 | 30.6013 | 93.173 | 34.4972 | 33.0898 | 35.0625 | 33.3982 | 33.1975 | 33.4682 | 34.8595 | 34.4088 | 34.1223 | 37.1757 | 36.2019 | 33.4795 | 34.3719 | 36.2006 | 36.5483 | 37.3107 | 36.1911 | 33.3867 | 32.4892 | 34.3695 | 34.8702 | 32.9054 | 34.3263 | 34.371 | 34.3892 | 34.4237 | 34.3962 | 34.338 | 33.8434 | 34.4249 | 35.7108 | 35.2497 | 36.1383 | 36.0774 | 33.4902 | 93.3566 | 93.5223 | 93.3611
2022-09-08 02:46 | 4:56 | 24.7727 | 20.7255 | 27.0888 | 34.5165 | 34.3077 | 33.8305 | 34.5597 | 35.3426 | 36.4783 | 37.2267 | 36.8381 | 37.8659 | 34.3537 | 34.3529 | 34.1399 | 35.1006 | 35.1568 | 35.6615 | 36.3156 | 36.6219 | 30.9731 | 25.2974 | 93.1346 | 34.4131 | 33.0844 | 35.0321 | 33.4008 | 33.1844 | 33.4829 | 34.8649 | 34.4155 | 34.1373 | 37.1742 | 36.1875 | 33.4913 | 34.4027 | 36.2011 | 36.5588 | 37.3071 | 36.1972 | 33.4083 | 32.5275 | 34.3909 | 34.86 | 32.9328 | 34.3437 | 34.3776 | 34.3744 | 34.412 | 34.4005 | 34.3344 | 33.8306 | 34.4237 | 35.7004 | 35.2442 | 36.1374 | 36.0828 | 33.488 | 93.3208 | 93.4405 | 93.3452
2022-09-08 02:47 | 4:57 | 26.3513 | 26.4264 | 27.411 | 34.6498 | 34.3097 | 33.8276 | 34.5686 | 35.3584 | 36.464 | 37.2379 | 36.8361 | 37.8689 | 34.3535 | 34.3565 | 34.1231 | 35.0625 | 35.1462 | 35.6527 | 36.3199 | 36.6116 | 30.7983 | 26.6834 | 93.0864 | 34.3914 | 33.1037 | 35.0507 | 33.4193 | 33.2008 | 33.4651 | 34.8816 | 34.4151 | 34.1226 | 37.1745 | 36.203 | 33.4731 | 34.392 | 36.2019 | 36.5547 | 37.3112 | 36.1904 | 33.4008 | 32.5033 | 34.3683 | 34.8608 | 32.9193 | 34.331 | 34.3658 | 34.3846 | 34.4337 | 34.3961 | 34.3374 | 33.8287 | 34.412 | 35.7118 | 35.2353 | 36.1262 | 36.0762 | 33.4779 | 93.2522 | 93.3757 | 93.2291
2022-09-08 02:47 | 4:57 | 29.3141 | 29.223 | 28.0446 | 34.8601 | 34.2916 | 33.8319 | 34.574 | 35.3619 | 36.484 | 37.2449 | 36.8386 | 37.8669 | 34.3607 | 34.3655 | 34.1149 | 35.0817 | 35.1459 | 35.6533 | 36.3201 | 36.6474 | 31.0995 | 29.2003 | 92.9907 | 34.4036 | 33.0783 | 35.0498 | 33.4077 | 33.173 | 33.4574 | 34.861 | 34.4219 | 34.1369 | 37.1762 | 36.1957 | 33.4875 | 34.4049 | 36.1875 | 36.5365 | 37.3296 | 36.2006 | 33.3998 | 32.5147 | 34.3833 | 34.8724 | 32.9407 | 34.3357 | 34.3654 | 34.3785 | 34.4367 | 34.4038 | 34.3303 | 33.8559 | 34.4337 | 35.7138 | 35.2425 | 36.1563 | 36.0938 | 33.4771 | 93.201 | 93.2847 | 93.2215
2022-09-08 02:47 | 4:57 | 30.7421 | 29.9865 | 29.1323 | 34.8824 | 34.3064 | 33.8341 | 34.5861 | 35.3578 | 36.4734 | 37.2439 | 36.8535 | 37.8643 | 34.36 | 34.347 | 34.1137 | 35.0595 | 35.1622 | 35.66 | 36.3503 | 36.6378 | 31.9078 | 29.989 | 92.9666 | 34.5311 | 33.0974 | 35.0399 | 33.3867 | 33.1778 | 33.4795 | 34.8663 | 34.3981 | 34.1154 | 37.1909 | 36.2066 | 33.4735 | 34.398 | 36.203 | 36.5529 | 37.3332 | 36.2011 | 33.3993 | 32.5294 | 34.399 | 34.8761 | 32.926 | 34.3207 | 34.3778 | 34.3644 | 34.4328 | 34.3986 | 34.3228 | 33.8422 | 34.4367 | 35.7074 | 35.2545 | 36.1487 | 36.0843 | 33.4681 | 93.1184 | 93.2037 | 93.1679
2022-09-08 02:47 | 4:57 | 31.4134 | 30.2727 | 29.5869 | 34.9385 | 34.3171 | 33.8367 | 34.6065 | 35.3801 | 36.479 | 37.2443 | 36.8381 | 37.8572 | 34.3436 | 34.3498 | 34.1308 | 35.0701 | 35.1579 | 35.6596 | 36.3462 | 36.6176 | 32.6938 | 30.1966 | 92.8347 | 34.633 | 33.0929 | 35.0405 | 33.4083 | 33.1885 | 33.4913 | 34.8485 | 34.3901 | 34.1277 | 37.194 | 36.1878 | 33.4738 | 34.4094 | 36.1957 | 36.5594 | 37.3382 | 36.2019 | 33.403 | 32.535 | 34.3828 | 34.869 | 32.9469 | 34.3302 | 34.3642 | 34.3547 | 34.4064 | 34.3906 | 34.3372 | 33.8549 | 34.4328 | 35.7081 | 35.2537 | 36.1595 | 36.0878 | 33.4871 | 93.0213 | 93.0669 | 93.0687
2022-09-08 02:47 | 4:57 | 31.9223 | 30.4687 | 29.9859 | 34.9361 | 34.304 | 33.8455 | 34.6205 | 35.3751 | 36.4864 | 37.2402 | 36.8463 | 37.8785 | 34.3616 | 34.3728 | 34.1256 | 35.0949 | 35.1328 | 35.6553 | 36.3595 | 36.6466 | 33.3915 | 30.3602 | 92.7606 | 34.5909 | 33.0839 | 35.0436 | 33.4008 | 33.1998 | 33.4731 | 34.8791 | 34.4184 | 34.1336 | 37.1811 | 36.2047 | 33.4893 | 34.403 | 36.2066 | 36.5605 | 37.3231 | 36.1875 | 33.3884 | 32.5199 | 34.4071 | 34.8791 | 32.9478 | 34.3411 | 34.359 | 34.3855 | 34.4295 | 34.4128 | 34.3556 | 33.8424 | 34.4064 | 35.7092 | 35.2583 | 36.1599 | 36.0946 | 33.4785 | 92.847 | 92.9842 | 93.0107
2022-09-08 02:47 | 4:57 | 32.3299 | 30.6175 | 30.1513 | 35.1191 | 34.3302 | 33.8504 | 34.6144 | 35.368 | 36.4824 | 37.2569 | 36.8627 | 37.8948 | 34.3513 | 34.3644 | 34.1422 | 35.1136 | 35.1471 | 35.6707 | 36.3698 | 36.6362 | 33.9277 | 30.5011 | 92.6971 | 34.6072 | 33.1104 | 35.0604 | 33.3998 | 33.2022 | 33.4875 | 34.8692 | 34.4085 | 34.1249 | 37.1832 | 36.1884 | 33.4938 | 34.3927 | 36.1878 | 36.5795 | 37.3246 | 36.203 | 33.3941 | 32.5227 | 34.4096 | 34.894 | 32.9677 | 34.3387 | 34.3712 | 34.3825 | 34.4129 | 34.416 | 34.3421 | 33.849 | 34.4295 | 35.7145 | 35.2493 | 36.1545 | 36.0829 | 33.5072 | 92.7409 | 92.8651 | 92.8684
2022-09-08 02:48 | 4:57 | 32.6467 | 30.7136 | 30.4072 | 35.1323 | 34.3257 | 33.877 | 34.6052 | 35.3661 | 36.4826 | 37.2578 | 36.8659 | 37.8783 | 34.3606 | 34.3415 | 34.1425 | 35.0956 | 35.1521 | 35.6717 | 36.373 | 36.6322 | 34.2624 | 30.7155 | 92.6199 | 34.6358 | 33.0723 | 35.0573 | 33.3993 | 33.2103 | 33.4735 | 34.8784 | 34.4151 | 34.1458 | 37.1822 | 36.2085 | 33.4795 | 34.4207 | 36.2047 | 36.5613 | 37.3321 | 36.1957 | 33.405 | 32.5545 | 34.3963 | 34.9062 | 32.961 | 34.3405 | 34.3432 | 34.3695 | 34.4178 | 34.4246 | 34.3439 | 33.8519 | 34.4129 | 35.7142 | 35.2585 | 36.1452 | 36.0778 | 33.4911 | 92.6017 | 92.7582 | 92.7892
2022-09-08 02:48 | 4:58 | 32.9239 | 30.8184 | 30.5909 | 35.1455 | 34.3133 | 33.8803 | 34.6419 | 35.3815 | 36.4927 | 37.2464 | 36.8635 | 37.8642 | 34.3507 | 34.3632 | 34.1502 | 35.0947 | 35.1463 | 35.6733 | 36.3653 | 36.6662 | 34.4158 | 30.8295 | 92.6003 | 34.6554 | 33.1089 | 35.0419 | 33.403 | 33.2019 | 33.4738 | 34.8731 | 34.4428 | 34.1346 | 37.1949 | 36.1983 | 33.4851 | 34.4232 | 36.1884 | 36.5719 | 37.3265 | 36.2066 | 33.4065 | 32.5577 | 34.4224 | 34.9246 | 32.9691 | 34.3314 | 34.3388 | 34.3678 | 34.4223 | 34.4275 | 34.3364 | 33.8534 | 34.4178 | 35.7393 | 35.252 | 36.152 | 36.0859 | 33.4913 | 92.4666 | 92.5974 | 92.7105
2022-09-08 02:48 | 4:58 | 33.1332 | 30.8849 | 30.8483 | 35.2176 | 34.3169 | 33.869 | 34.6465 | 35.3743 | 36.4946 | 37.2764 | 36.8414 | 37.8757 | 34.36 | 34.3614 | 34.1308 | 35.1018 | 35.1533 | 35.6944 | 36.3867 | 36.6463 | 34.4298 | 30.9562 | 92.4467 | 34.697 | 33.1046 | 35.0139 | 33.3884 | 33.2032 | 33.4893 | 34.862 | 34.4052 | 34.141 | 37.1975 | 36.2099 | 33.5015 | 34.4001 | 36.2085 | 36.5666 | 37.3189 | 36.1878 | 33.3802 | 32.5575 | 34.4182 | 34.9029 | 32.9654 | 34.3627 | 34.3559 | 34.3802 | 34.4268 | 34.4067 | 34.3341 | 33.8415 | 34.4223 | 35.7328 | 35.2558 | 36.1624 | 36.099 | 33.5089 | 92.3326 | 92.4621 | 92.6625
2022-09-08 02:48 | 4:58 | 33.2322 | 30.9675 | 31.0347 | 35.2379 | 34.2931 | 33.8642 | 34.6264 | 35.3799 | 36.4827 | 37.276 | 36.8433 | 37.8897 | 34.357 | 34.3662 | 34.1319 | 35.0859 | 35.1345 | 35.6848 | 36.3925 | 36.653 | 34.4133 | 31.0551 | 92.3084 | 34.6712 | 33.0978 | 35.044 | 33.3941 | 33.2023 | 33.4938 | 34.8958 | 34.4133 | 34.1211 | 37.1844 | 36.2068 | 33.4799 | 34.4203 | 36.1983 | 36.5704 | 37.3281 | 36.2047 | 33.4169 | 32.5485 | 34.4325 | 34.9126 | 32.9792 | 34.3524 | 34.3475 | 34.3605 | 34.4336 | 34.4096 | 34.3359 | 33.8599 | 34.4268 | 35.7201 | 35.2559 | 36.1586 | 36.082 | 33.5039 | 92.2212 | 92.3506 | 92.5974
2022-09-08 02:48 | 4:58 | 33.3663 | 31.0288 | 31.2077 | 35.4057 | 34.3144 | 33.8636 | 34.6473 | 35.3745 | 36.4844 | 37.2786 | 36.8432 | 37.8942 | 34.3604 | 34.3685 | 34.1455 | 35.1028 | 35.1317 | 35.7062 | 36.3865 | 36.642 | 34.4125 | 31.1021 | 92.2197 | 34.7284 | 33.0945 | 35.0434 | 33.405 | 33.2061 | 33.4795 | 34.8922 | 34.4243 | 34.133 | 37.1942 | 36.2033 | 33.4732 | 34.4161 | 36.2099 | 36.5592 | 37.348 | 36.1884 | 33.41 | 32.5481 | 34.4346 | 34.906 | 32.9909 | 34.339 | 34.3447 | 34.3851 | 34.4344 | 34.4138 | 34.3354 | 33.8518 | 34.4336 | 35.7225 | 35.2567 | 36.1586 | 36.1109 | 33.5104 | 92.1338 | 92.2467 | 92.5021
2022-09-08 02:48 | 4:58 | 33.4692 | 31.1074 | 31.3301 | 35.3767 | 34.304 | 33.8655 | 34.6479 | 35.3916 | 36.4941 | 37.2694 | 36.8597 | 37.8941 | 34.3585 | 34.3496 | 34.1287 | 35.0857 | 35.1349 | 35.6891 | 36.3979 | 36.6517 | 34.3777 | 31.1866 | 92.0472 | 34.7228 | 33.1114 | 35.0545 | 33.4065 | 33.2163 | 33.4851 | 34.8775 | 34.4193 | 34.1398 | 37.1908 | 36.1922 | 33.479 | 34.4155 | 36.2068 | 36.5651 | 37.342 | 36.2085 | 33.401 | 32.5599 | 34.4415 | 34.922 | 32.9982 | 34.3447 | 34.3582 | 34.373 | 34.4054 | 34.4143 | 34.3367 | 33.8656 | 34.4344 | 35.7311 | 35.2398 | 36.1717 | 36.0957 | 33.4965 | 91.9392 | 92.0888 | 92.3257
2022-09-08 02:49 | 4:59 | 33.5784 | 31.1599 | 31.462 | 35.4533 | 34.3186 | 33.8657 | 34.6441 | 35.4006 | 36.4835 | 37.2745 | 36.8485 | 37.8856 | 34.3602 | 34.3672 | 34.1649 | 35.1006 | 35.1554 | 35.7054 | 36.4131 | 36.6412 | 34.3559 | 31.2054 | 92.0296 | 34.8069 | 33.1042 | 35.0452 | 33.3802 | 33.2009 | 33.5015 | 34.873 | 34.4339 | 34.1343 | 37.1959 | 36.1859 | 33.4735 | 34.4247 | 36.2033 | 36.5443 | 37.3559 | 36.1983 | 33.4034 | 32.577 | 34.4443 | 34.9372 | 33.0047 | 34.3445 | 34.3384 | 34.387 | 34.42 | 34.4023 | 34.3326 | 33.8625 | 34.4054 | 35.7404 | 35.2536 | 36.1519 | 36.1167 | 33.5277 | 91.8322 | 91.9554 | 92.259
2022-09-08 02:49 | 4:59 | 33.6327 | 31.214 | 31.6018 | 35.4757 | 34.3119 | 33.8816 | 34.6629 | 35.3922 | 36.4798 | 37.2789 | 36.8687 | 37.8924 | 34.3558 | 34.3824 | 34.1461 | 35.0925 | 35.142 | 35.7045 | 36.4257 | 36.6588 | 34.2869 | 31.2597 | 91.8934 | 34.8354 | 33.1095 | 35.0537 | 33.4169 | 33.2064 | 33.4799 | 34.8906 | 34.4392 | 34.118 | 37.2041 | 36.1978 | 33.4929 | 34.4177 | 36.1922 | 36.565 | 37.3521 | 36.2099 | 33.4203 | 32.585 | 34.4626 | 34.9437 | 33.0181 | 34.3313 | 34.3388 | 34.3648 | 34.4248 | 34.4117 | 34.3327 | 33.8828 | 34.42 | 35.7281 | 35.2393 | 36.1527 | 36.1243 | 33.5229 | 91.6974 | 91.8251 | 92.201
2022-09-08 02:49 | 4:59 | 33.685 | 31.2585 | 31.7233 | 35.4858 | 34.3025 | 33.8845 | 34.6472 | 35.4016 | 36.4836 | 37.2884 | 36.8599 | 37.8949 | 34.369 | 34.3666 | 34.1639 | 35.0922 | 35.1441 | 35.7019 | 36.4277 | 36.6656 | 34.2535 | 31.3077 | 91.9095 | 34.8028 | 33.0996 | 35.0534 | 33.41 | 33.2021 | 33.4732 | 34.8704 | 34.4357 | 34.1427 | 37.2011 | 36.2023 | 33.4721 | 34.4187 | 36.1859 | 36.5511 | 37.3458 | 36.2068 | 33.3952 | 32.5876 | 34.4646 | 34.964 | 33.0093 | 34.3636 | 34.3219 | 34.3713 | 34.4016 | 34.4269 | 34.3509 | 33.8778 | 34.4248 | 35.7362 | 35.2363 | 36.1667 | 36.1237 | 33.5414 | 91.6423 | 91.7743 | 92.2088
2022-09-08 02:49 | 4:59 | 33.6859 | 31.32 | 31.8228 | 35.5299 | 34.3256 | 33.8666 | 34.6661 | 35.4012 | 36.4932 | 37.2901 | 36.8479 | 37.8868 | 34.3595 | 34.366 | 34.1559 | 35.0829 | 35.1359 | 35.6814 | 36.4217 | 36.663 | 34.1899 | 31.3503 | 91.98 | 34.8769 | 33.1075 | 35.0419 | 33.401 | 33.2056 | 33.479 | 34.8794 | 34.4249 | 34.1409 | 37.2141 | 36.1889 | 33.4729 | 34.4141 | 36.1978 | 36.5719 | 37.342 | 36.2033 | 33.3915 | 32.5946 | 34.4637 | 34.9369 | 33.0274 | 34.3523 | 34.3218 | 34.3747 | 34.4262 | 34.4253 | 34.3416 | 33.8618 | 34.4016 | 35.741 | 35.2276 | 36.1813 | 36.1142 | 33.538 | 91.7092 | 91.8069 | 92.1857
2022-09-08 02:49 | 4:59 | 33.7324 | 31.3453 | 31.8764 | 35.6094 | 34.308 | 33.8799 | 34.6644 | 35.4075 | 36.5023 | 37.3011 | 36.8817 | 37.8929 | 34.3511 | 34.355 | 34.1647 | 35.0996 | 35.146 | 35.7219 | 36.435 | 36.6708 | 34.1221 | 31.3651 | 91.8741 | 34.8195 | 33.1048 | 35.0389 | 33.4034 | 33.2188 | 33.4735 | 34.8877 | 34.4088 | 34.1443 | 37.1797 | 36.1756 | 33.4729 | 34.4326 | 36.2023 | 36.5829 | 37.3597 | 36.1922 | 33.3932 | 32.5878 | 34.4641 | 34.9489 | 33.0229 | 34.3511 | 34.3323 | 34.3605 | 34.4062 | 34.4159 | 34.3402 | 33.8711 | 34.4262 | 35.7582 | 35.2302 | 36.1633 | 36.1142 | 33.5303 | 91.7732 | 91.8092 | 92.231
2022-09-08 02:49 | 4:59 | 33.8266 | 31.3977 | 31.9586 | 35.6022 | 34.3271 | 33.8795 | 34.6622 | 35.3832 | 36.4851 | 37.3182 | 36.8558 | 37.908 | 34.3678 | 34.3646 | 34.156 | 35.0849 | 35.1313 | 35.7112 | 36.4397 | 36.6625 | 34.0004 | 31.3965 | 91.9159 | 34.8627 | 33.1206 | 35.0406 | 33.4203 | 33.2163 | 33.4929 | 34.8881 | 34.4381 | 34.1393 | 37.2115 | 36.1981 | 33.494 | 34.4253 | 36.1889 | 36.5837 | 37.3594 | 36.1859 | 33.3937 | 32.5892 | 34.4908 | 34.9633 | 33.0229 | 34.3342 | 34.345 | 34.3467 | 34.4174 | 34.4239 | 34.3494 | 33.8778 | 34.4062 | 35.7474 | 35.2436 | 36.157 | 36.1298 | 33.528 | 91.7863 | 91.8711 | 92.2932
2022-09-08 02:50 | 4:59 | 33.8681 | 31.4152 | 32.0571 | 35.5929 | 34.3227 | 33.8763 | 34.6576 | 35.3872 | 36.4982 | 37.2905 | 36.8569 | 37.893 | 34.3485 | 34.3808 | 34.1618 | 35.1036 | 35.149 | 35.7189 | 36.4444 | 36.6671 | 33.9278 | 31.4101 | 91.9177 | 34.9503 | 33.1115 | 35.0391 | 33.3952 | 33.2092 | 33.4721 | 34.8802 | 34.4269 | 34.128 | 37.197 | 36.1838 | 33.4865 | 34.4238 | 36.1756 | 36.571 | 37.3597 | 36.1978 | 33.3885 | 32.59 | 34.5022 | 34.9823 | 33.0279 | 34.3608 | 34.3195 | 34.3521 | 34.4225 | 34.4084 | 34.3382 | 33.8941 | 34.4174 | 35.7768 | 35.2472 | 36.1595 | 36.1147 | 33.5325 | 91.849 | 91.9458 | 92.3244
2022-09-08 02:50 | 5:00 | 33.9268 | 31.447 | 32.1132 | 35.6508 | 34.3273 | 33.8705 | 34.6701 | 35.3962 | 36.4969 | 37.3085 | 36.843 | 37.8937 | 34.3715 | 34.3791 | 34.1611 | 35.0919 | 35.1393 | 35.7202 | 36.4492 | 36.67 | 33.8615 | 31.4269 | 91.9533 | 34.9474 | 33.1433 | 35.0409 | 33.3915 | 33.209 | 33.4729 | 34.8841 | 34.4026 | 34.1226 | 37.1917 | 36.1846 | 33.4817 | 34.4076 | 36.1981 | 36.5624 | 37.3727 | 36.2023 | 33.3881 | 32.5975 | 34.4826 | 34.9654 | 33.0369 | 34.3525 | 34.3116 | 34.365 | 34.3985 | 34.4261 | 34.3397 | 33.8725 | 34.4225 | 35.746 | 35.2454 | 36.1733 | 36.1202 | 33.5497 | 91.9396 | 92.0393 | 92.3852
2022-09-08 02:50 | 5:00 | 33.9874 | 31.474 | 32.1898 | 35.7626 | 34.3233 | 33.8714 | 34.6647 | 35.3992 | 36.4907 | 37.3032 | 36.8451 | 37.8923 | 34.3544 | 34.3903 | 34.1535 | 35.0838 | 35.1354 | 35.7087 | 36.4552 | 36.6657 | 33.8171 | 31.42 | 91.9873 | 34.942 | 33.1063 | 35.0276 | 33.3932 | 33.2296 | 33.4729 | 34.8931 | 34.4087 | 34.1225 | 37.183 | 36.187 | 33.489 | 34.4143 | 36.1838 | 36.5747 | 37.3637 | 36.1889 | 33.3876 | 32.5859 | 34.5094 | 34.9763 | 33.0453 | 34.3616 | 34.3142 | 34.376 | 34.4203 | 34.4365 | 34.3627 | 33.8747 | 34.3985 | 35.7578 | 35.2312 | 36.1608 | 36.1114 | 33.5348 | 92.0031 | 92.1115 | 92.4115
2022-09-08 02:50 | 5:00 | 34.108 | 31.4927 | 32.2532 | 35.8481 | 34.3017 | 33.8731 | 34.656 | 35.4136 | 36.4786 | 37.297 | 36.8436 | 37.8785 | 34.3497 | 34.3563 | 34.1566 | 35.0977 | 35.1374 | 35.7137 | 36.4629 | 36.678 | 33.8554 | 31.4413 | 92.1303 | 34.9335 | 33.1219 | 35.0202 | 33.3937 | 33.2166 | 33.494 | 34.8944 | 34.414 | 34.1298 | 37.2064 | 36.1663 | 33.4707 | 34.4238 | 36.1846 | 36.5657 | 37.377 | 36.1756 | 33.3839 | 32.5976 | 34.5123 | 34.9575 | 33.0369 | 34.3556 | 34.3204 | 34.3753 | 34.409 | 34.4316 | 34.3474 | 33.9028 | 34.4203 | 35.7594 | 35.2357 | 36.1615 | 36.1368 | 33.5566 | 92.1226 | 92.2519 | 92.4889
2022-09-08 02:50 | 5:00 | 34.2223 | 31.5199 | 32.3586 | 35.9313 | 34.3313 | 33.8536 | 34.671 | 35.4021 | 36.4823 | 37.3217 | 36.849 | 37.8884 | 34.3436 | 34.3596 | 34.164 | 35.0801 | 35.1293 | 35.709 | 36.4529 | 36.6703 | 33.9731 | 31.4519 | 92.2136 | 35.0344 | 33.1168 | 35.0358 | 33.3885 | 33.1916 | 33.4865 | 34.8887 | 34.42 | 34.1278 | 37.1866 | 36.1887 | 33.4836 | 34.399 | 36.187 | 36.575 | 37.3697 | 36.1981 | 33.3709 | 32.5959 | 34.523 | 34.9639 | 33.0362 | 34.3518 | 34.3077 | 34.3558 | 34.4133 | 34.4185 | 34.3434 | 33.8845 | 34.409 | 35.7576 | 35.2323 | 36.1608 | 36.1151 | 33.5496 | 92.249 | 92.4009 | 92.5474
2022-09-08 02:50 | 5:00 | 34.4064 | 31.5429 | 32.4513 | 35.8777 | 34.3329 | 33.8682 | 34.6559 | 35.4061 | 36.4859 | 37.3104 | 36.8373 | 37.8883 | 34.3677 | 34.3643 | 34.1695 | 35.0766 | 35.1259 | 35.7228 | 36.4528 | 36.6934 | 34.1134 | 31.4683 | 92.2236 | 34.9972 | 33.1106 | 35.0194 | 33.3881 | 33.2056 | 33.4817 | 34.8915 | 34.3938 | 34.114 | 37.1938 | 36.1929 | 33.4786 | 34.409 | 36.1663 | 36.5579 | 37.368 | 36.1838 | 33.3639 | 32.6097 | 34.5046 | 34.9762 | 33.0457 | 34.3473 | 34.314 | 34.3558 | 34.4091 | 34.4278 | 34.3519 | 33.8843 | 34.4133 | 35.7595 | 35.2354 | 36.1643 | 36.1368 | 33.5446 | 92.2658 | 92.4778 | 92.5123
2022-09-08 02:51 | 5:01 | 34.553 | 31.5686 | 32.5516 | 35.8736 | 34.3225 | 33.8645 | 34.6724 | 35.3925 | 36.4828 | 37.3199 | 36.8431 | 37.8933 | 34.3647 | 34.3538 | 34.1681 | 35.0728 | 35.1272 | 35.7121 | 36.4628 | 36.6754 | 34.2065 | 31.4622 | 92.2379 | 34.9819 | 33.1391 | 34.9939 | 33.3876 | 33.2052 | 33.489 | 34.8943 | 34.4241 | 34.1051 | 37.1958 | 36.2198 | 33.4783 | 34.4201 | 36.1887 | 36.5634 | 37.3796 | 36.1846 | 33.3506 | 32.6051 | 34.527 | 34.9895 | 33.0534 | 34.3631 | 34.3132 | 34.3663 | 34.4104 | 34.4263 | 34.3529 | 33.8791 | 34.4091 | 35.7764 | 35.2185 | 36.1506 | 36.1271 | 33.5554 | 92.3558 | 92.5751 | 92.6126
2022-09-08 02:51 | 5:01 | 34.5235 | 31.5957 | 32.6309 | 35.9239 | 34.313 | 33.8503 | 34.6553 | 35.3912 | 36.4744 | 37.3151 | 36.8372 | 37.8928 | 34.3769 | 34.3796 | 34.1699 | 35.0842 | 35.1185 | 35.7101 | 36.4534 | 36.6787 | 34.2792 | 31.4767 | 92.3824 | 35.0161 | 33.129 | 35.0133 | 33.3839 | 33.1824 | 33.4707 | 34.8972 | 34.4012 | 34.1201 | 37.1863 | 36.1775 | 33.4739 | 34.429 | 36.1929 | 36.5731 | 37.3897 | 36.187 | 33.3655 | 32.6239 | 34.5119 | 34.9839 | 33.0526 | 34.3588 | 34.2918 | 34.3631 | 34.409 | 34.4305 | 34.3565 | 33.9004 | 34.4104 | 35.7586 | 35.2286 | 36.1762 | 36.1142 | 33.56 | 92.4675 | 92.6713 | 92.6525
2022-09-08 02:51 | 5:01 | 33.115 | 31.5138 | 32.5331 | 35.8798 | 34.3182 | 33.8581 | 34.6618 | 35.3895 | 36.4925 | 37.3433 | 36.847 | 37.8979 | 34.3774 | 34.3631 | 34.1614 | 35.0571 | 35.1092 | 35.7092 | 36.4826 | 36.6811 | 32.4873 | 31.4118 | 92.4248 | 35.0655 | 33.1252 | 35.011 | 33.3709 | 33.2156 | 33.4836 | 34.8862 | 34.3907 | 34.1224 | 37.1932 | 36.2054 | 33.4841 | 34.4093 | 36.2198 | 36.5603 | 37.3713 | 36.1663 | 33.3737 | 32.6123 | 34.5102 | 34.9973 | 33.0498 | 34.3765 | 34.2875 | 34.3711 | 34.4054 | 34.4318 | 34.3655 | 33.8734 | 34.409 | 35.7681 | 35.2139 | 36.169 | 36.1082 | 33.5665 | 92.6136 | 92.7574 | 92.6864
2022-09-08 02:51 | 5:01 | 30.1746 | 30.4928 | 31.9787 | 35.9373 | 34.338 | 33.8651 | 34.6404 | 35.3941 | 36.4858 | 37.346 | 36.826 | 37.8993 | 34.3715 | 34.3827 | 34.1571 | 35.0698 | 35.1039 | 35.7122 | 36.4841 | 36.6861 | 29.0622 | 31.0396 | 92.4393 | 34.9845 | 33.1265 | 35.0022 | 33.3639 | 33.2011 | 33.4786 | 34.904 | 34.386 | 34.1181 | 37.1965 | 36.1724 | 33.4892 | 34.3974 | 36.1775 | 36.5388 | 37.3567 | 36.1887 | 33.3901 | 32.6092 | 34.5477 | 34.9915 | 33.0433 | 34.3375 | 34.292 | 34.3757 | 34.3984 | 34.438 | 34.347 | 33.8793 | 34.4054 | 35.7657 | 35.2241 | 36.1787 | 36.1322 | 33.5537 | 92.6762 | 92.8931 | 92.7039
2022-09-08 02:51 | 5:01 | 30.945 | 21.3396 | 31.7339 | 35.9126 | 34.3344 | 33.8529 | 34.6615 | 35.4004 | 36.4881 | 37.3294 | 36.8411 | 37.8803 | 34.3838 | 34.3615 | 34.184 | 35.0663 | 35.136 | 35.701 | 36.4976 | 36.7012 | 27.3898 | 30.76 | 92.5148 | 34.9771 | 33.1266 | 34.9922 | 33.3506 | 33.1999 | 33.4783 | 34.9004 | 34.3803 | 34.108 | 37.1821 | 36.1755 | 33.4876 | 34.4142 | 36.2054 | 36.5483 | 37.3753 | 36.1929 | 33.3589 | 32.6432 | 34.5369 | 35.0016 | 33.0929 | 34.3617 | 34.2984 | 34.361 | 34.4037 | 34.4235 | 34.3498 | 33.9076 | 34.3984 | 35.7374 | 35.2097 | 36.1805 | 36.1157 | 33.5458 | 92.8195 | 93.0084 | 92.8047
2022-09-08 02:51 | 5:01 | 31.5246 | 23.1864 | 31.9694 | 35.8168 | 34.3374 | 33.8481 | 34.6739 | 35.3938 | 36.4886 | 37.3253 | 36.8395 | 37.8811 | 34.3832 | 34.3912 | 34.1543 | 35.0707 | 35.1215 | 35.73 | 36.4737 | 36.7015 | 28.0711 | 30.7437 | 92.7182 | 34.9947 | 33.1178 | 35.0199 | 33.3655 | 33.2132 | 33.4739 | 34.8882 | 34.3964 | 34.1043 | 37.1739 | 36.1912 | 33.4772 | 34.3864 | 36.1724 | 36.5635 | 37.3937 | 36.2198 | 33.3831 | 32.6344 | 34.5489 | 35.0105 | 33.0819 | 34.362 | 34.3025 | 34.3565 | 34.4099 | 34.4273 | 34.3728 | 33.8896 | 34.4037 | 35.7804 | 35.2119 | 36.1397 | 36.1178 | 33.5655 | 92.967 | 93.1294 | 92.9844
2022-09-08 02:52 | 5:02 | 31.7142 | 25.9903 | 32.0825 | 35.963 | 34.3303 | 33.8572 | 34.6637 | 35.3979 | 36.4876 | 37.3278 | 36.84 | 37.8673 | 34.3645 | 34.3688 | 34.1632 | 35.0812 | 35.1064 | 35.7121 | 36.4633 | 36.6935 | 28.7749 | 30.7868 | 92.7975 | 35.0402 | 33.1129 | 35.0031 | 33.3737 | 33.2105 | 33.4841 | 34.8965 | 34.4027 | 34.1048 | 37.1933 | 36.2019 | 33.4759 | 34.4099 | 36.1755 | 36.5712 | 37.3931 | 36.1775 | 33.3563 | 32.6104 | 34.5464 | 35.0083 | 33.0767 | 34.3398 | 34.2946 | 34.3704 | 34.4007 | 34.4287 | 34.3644 | 33.9082 | 34.4099 | 35.7724 | 35.2078 | 36.1423 | 36.1384 | 33.5453 | 93.1587 | 93.3121 | 93.1226
2022-09-08 02:52 | 5:02 | 31.8274 | 27.863 | 32.1811 | 36.0394 | 34.3228 | 33.8569 | 34.6518 | 35.3919 | 36.499 | 37.3411 | 36.8315 | 37.8869 | 34.396 | 34.3942 | 34.1598 | 35.0758 | 35.1225 | 35.7058 | 36.4869 | 36.6856 | 29.4703 | 30.862 | 92.7681 | 35.0841 | 33.1357 | 35.0099 | 33.3901 | 33.2058 | 33.4892 | 34.922 | 34.3814 | 34.0993 | 37.1981 | 36.1944 | 33.487 | 34.4342 | 36.1912 | 36.5554 | 37.3925 | 36.2054 | 33.3536 | 32.6378 | 34.5419 | 35.0078 | 33.0788 | 34.3747 | 34.2906 | 34.3687 | 34.3993 | 34.4297 | 34.3415 | 33.8874 | 34.4007 | 35.774 | 35.2141 | 36.1502 | 36.1448 | 33.5535 | 93.3561 | 93.4274 | 93.1088
2022-09-08 02:52 | 5:02 | 31.9431 | 29.0056 | 32.2505 | 36.0918 | 34.3372 | 33.8457 | 34.6647 | 35.3983 | 36.4858 | 37.3424 | 36.8373 | 37.8804 | 34.3882 | 34.4051 | 34.1622 | 35.0687 | 35.1146 | 35.7311 | 36.4762 | 36.669 | 29.9835 | 30.925 | 92.8891 | 35.0421 | 33.13 | 35.0034 | 33.3589 | 33.1993 | 33.4876 | 34.9149 | 34.388 | 34.11 | 37.2104 | 36.188 | 33.4659 | 34.3802 | 36.2019 | 36.5515 | 37.3971 | 36.1724 | 33.378 | 32.6492 | 34.5498 | 35.0083 | 33.0985 | 34.3511 | 34.2902 | 34.3704 | 34.4127 | 34.4286 | 34.3632 | 33.9 | 34.3993 | 35.7954 | 35.2147 | 36.1489 | 36.123 | 33.5537 | 93.5392 | 93.6488 | 93.2547
2022-09-08 02:52 | 5:02 | 32.0269 | 29.7597 | 32.315 | 36.132 | 34.3556 | 33.8453 | 34.6545 | 35.3981 | 36.499 | 37.3477 | 36.8349 | 37.8837 | 34.3826 | 34.3891 | 34.187 | 35.0603 | 35.1002 | 35.7204 | 36.4759 | 36.6691 | 30.4311 | 30.9988 | 93.1783 | 35.0401 | 33.1315 | 35.0238 | 33.3831 | 33.2026 | 33.4772 | 34.9054 | 34.3944 | 34.1055 | 37.1812 | 36.174 | 33.4815 | 34.4049 | 36.1944 | 36.5747 | 37.4136 | 36.1755 | 33.3602 | 32.6592 | 34.5488 | 35.0151 | 33.0902 | 34.3657 | 34.2858 | 34.3681 | 34.3996 | 34.4217 | 34.3614 | 33.8938 | 34.4127 | 35.7907 | 35.2093 | 36.1492 | 36.1386 | 33.5781 | 93.7577 | 93.8131 | 93.5134
2022-09-08 02:52 | 5:02 | 32.0946 | 30.2326 | 32.3627 | 35.9533 | 34.3421 | 33.8611 | 34.6625 | 35.4114 | 36.4836 | 37.3363 | 36.8473 | 37.8733 | 34.3866 | 34.3939 | 34.1591 | 35.0738 | 35.1184 | 35.7321 | 36.4731 | 36.6897 | 30.8024 | 31.048 | 93.216 | 35.0425 | 33.1508 | 35.0117 | 33.3563 | 33.2212 | 33.4759 | 34.9171 | 34.3849 | 34.0911 | 37.1971 | 36.1805 | 33.4992 | 34.4014 | 36.188 | 36.5442 | 37.3909 | 36.1912 | 33.384 | 32.6529 | 34.5471 | 35.0142 | 33.1178 | 34.3894 | 34.286 | 34.3673 | 34.3892 | 34.4325 | 34.3662 | 33.902 | 34.3996 | 35.7835 | 35.2159 | 36.1527 | 36.1519 | 33.5884 | 93.9446 | 94.0412 | 93.5712
2022-09-08 02:52 | 5:02 | 32.1578 | 30.5339 | 32.403 | 36.1199 | 34.3439 | 33.8562 | 34.6538 | 35.38 | 36.4944 | 37.3342 | 36.811 | 37.8791 | 34.3785 | 34.4034 | 34.1566 | 35.059 | 35.1077 | 35.7133 | 36.4675 | 36.7 | 31.0799 | 31.123 | 93.3124 | 35.1319 | 33.1469 | 35.0005 | 33.3536 | 33.2044 | 33.487 | 34.9127 | 34.3897 | 34.1091 | 37.1833 | 36.2104 | 33.4926 | 34.402 | 36.174 | 36.5622 | 37.4056 | 36.2019 | 33.3669 | 32.661 | 34.5566 | 35.0177 | 33.1154 | 34.3594 | 34.2851 | 34.3464 | 34.4122 | 34.4243 | 34.3685 | 33.8826 | 34.3892 | 35.7728 | 35.2094 | 36.1625 | 36.1315 | 33.5413 | 94.178 | 94.1532 | 93.7035
2022-09-08 02:53 | 5:02 | 32.2122 | 30.7562 | 32.4212 | 36.0894 | 34.3364 | 33.8561 | 34.6524 | 35.4003 | 36.5035 | 37.3498 | 36.8328 | 37.8879 | 34.3945 | 34.3994 | 34.1754 | 35.0459 | 35.0985 | 35.7173 | 36.4868 | 36.6927 | 31.2993 | 31.1559 | 93.4581 | 35.1323 | 33.1411 | 35.0113 | 33.378 | 33.2068 | 33.4659 | 34.9078 | 34.3787 | 34.1015 | 37.1864 | 36.1926 | 33.4905 | 34.4014 | 36.1805 | 36.5677 | 37.4173 | 36.1944 | 33.3878 | 32.6524 | 34.5725 | 35.0335 | 33.1185 | 34.3858 | 34.2716 | 34.3669 | 34.3923 | 34.4221 | 34.3496 | 33.9263 | 34.4122 | 35.7845 | 35.2075 | 36.1648 | 36.1251 | 33.5462 | 94.3227 | 94.3436 | 93.7155
2022-09-08 02:53 | 5:03 | 32.2766 | 30.9244 | 32.4482 | 36.0844 | 34.3341 | 33.8566 | 34.6563 | 35.3702 | 36.499 | 37.3485 | 36.8488 | 37.8668 | 34.3847 | 34.3919 | 34.1809 | 35.0819 | 35.1318 | 35.7236 | 36.4799 | 36.6859 | 31.4762 | 31.1848 | 93.4315 | 35.129 | 33.1355 | 35.0062 | 33.3602 | 33.2098 | 33.4815 | 34.9148 | 34.3764 | 34.0871 | 37.1859 | 36.1748 | 33.4818 | 34.4163 | 36.2104 | 36.5457 | 37.4084 | 36.188 | 33.3821 | 32.6549 | 34.5667 | 35.0161 | 33.1136 | 34.3832 | 34.2707 | 34.3738 | 34.401 | 34.4357 | 34.3672 | 33.908 | 34.3923 | 35.7653 | 35.2105 | 36.1627 | 36.1194 | 33.5572 | 94.4192 | 94.4927 | 93.7242
2022-09-08 02:53 | 5:03 | 32.3148 | 31.0335 | 32.4812 | 36.112 | 34.3359 | 33.8614 | 34.6808 | 35.3986 | 36.5072 | 37.3579 | 36.8218 | 37.8917 | 34.397 | 34.3947 | 34.1856 | 35.0489 | 35.1163 | 35.7237 | 36.4925 | 36.6861 | 31.6495 | 31.2175 | 93.4795 | 35.1049 | 33.1265 | 35.0195 | 33.384 | 33.2128 | 33.4992 | 34.916 | 34.3703 | 34.0832 | 37.1815 | 36.1977 | 33.4742 | 34.3981 | 36.1926 | 36.5732 | 37.4042 | 36.174 | 33.3817 | 32.6852 | 34.5829 | 35.0223 | 33.1201 | 34.4034 | 34.2963 | 34.3554 | 34.3783 | 34.442 | 34.3824 | 33.8829 | 34.401 | 35.7804 | 35.216 | 36.1506 | 36.1219 | 33.5529 | 94.5367 | 94.6625 | 93.7587
2022-09-08 02:53 | 5:03 | 32.383 | 31.1064 | 32.5219 | 36.1635 | 34.3354 | 33.8445 | 34.6494 | 35.3851 | 36.4837 | 37.3359 | 36.8379 | 37.8846 | 34.3948 | 34.4015 | 34.1628 | 35.0555 | 35.12 | 35.7216 | 36.4771 | 36.6928 | 31.7734 | 31.2651 | 93.5791 | 35.1889 | 33.134 | 35.0154 | 33.3669 | 33.1971 | 33.4926 | 34.9119 | 34.3608 | 34.0997 | 37.1779 | 36.2162 | 33.488 | 34.4058 | 36.1748 | 36.5585 | 37.4195 | 36.1805 | 33.3793 | 32.6889 | 34.5694 | 35.0359 | 33.1417 | 34.3836 | 34.2767 | 34.3501 | 34.3928 | 34.4356 | 34.3666 | 33.9201 | 34.3783 | 35.7705 | 35.2147 | 36.1617 | 36.1457 | 33.5524 | 94.6725 | 94.7937 | 93.9808
2022-09-08 02:53 | 5:03 | 32.4263 | 31.1874 | 32.551 | 36.2327 | 34.3367 | 33.8418 | 34.6617 | 35.4035 | 36.4854 | 37.3497 | 36.8182 | 37.8876 | 34.3973 | 34.3819 | 34.1541 | 35.0598 | 35.1296 | 35.7175 | 36.4724 | 36.6718 | 31.8759 | 31.2782 | 93.7472 | 35.1643 | 33.1265 | 35.0101 | 33.3878 | 33.207 | 33.4905 | 34.9145 | 34.3714 | 34.0719 | 37.1806 | 36.188 | 33.4721 | 34.3986 | 36.1977 | 36.5557 | 37.3991 | 36.2104 | 33.3775 | 32.6759 | 34.5742 | 35.0313 | 33.1386 | 34.392 | 34.2881 | 34.3571 | 34.3933 | 34.4194 | 34.366 | 33.9109 | 34.3928 | 35.7879 | 35.1901 | 36.1536 | 36.1281 | 33.5607 | 94.7798 | 94.9059 | 94.1494
2022-09-08 02:53 | 5:03 | 32.4714 | 31.2163 | 32.5836 | 36.3029 | 34.3326 | 33.8414 | 34.6595 | 35.3979 | 36.4872 | 37.3391 | 36.8259 | 37.879 | 34.3962 | 34.3962 | 34.159 | 35.0587 | 35.1026 | 35.706 | 36.4987 | 36.6803 | 31.9772 | 31.3066 | 93.9157 | 35.2207 | 33.1273 | 35.0253 | 33.3821 | 33.1889 | 33.4818 | 34.9029 | 34.3743 | 34.0866 | 37.1786 | 36.2069 | 33.484 | 34.3819 | 36.2162 | 36.5501 | 37.4105 | 36.1926 | 33.3639 | 32.6895 | 34.568 | 35.0286 | 33.1502 | 34.3863 | 34.2839 | 34.3721 | 34.3804 | 34.4393 | 34.355 | 33.9057 | 34.3933 | 35.7807 | 35.2126 | 36.1619 | 36.1356 | 33.5676 | 94.7966 | 94.9354 | 94.1531
2022-09-08 02:54 | 5:04 | 32.4922 | 31.2876 | 32.6082 | 36.1402 | 34.3327 | 33.8445 | 34.6553 | 35.3798 | 36.4806 | 37.3462 | 36.8325 | 37.8687 | 34.4005 | 34.4025 | 34.1451 | 35.0627 | 35.1071 | 35.7298 | 36.4885 | 36.6915 | 32.0559 | 31.3361 | 93.8227 | 35.1865 | 33.1457 | 35.0062 | 33.3817 | 33.2094 | 33.4742 | 34.8941 | 34.379 | 34.0781 | 37.1922 | 36.1905 | 33.4634 | 34.3962 | 36.188 | 36.5558 | 37.3862 | 36.1748 | 33.3693 | 32.6974 | 34.5949 | 35.0476 | 33.1579 | 34.3792 | 34.2905 | 34.3577 | 34.4116 | 34.4234 | 34.3646 | 33.9162 | 34.3804 | 35.7561 | 35.2196 | 36.1689 | 36.14 | 33.5468 | 94.8742 | 94.9723 | 94.1908
2022-09-08 02:54 | 5:04 | 32.5234 | 31.3252 | 32.6269 | 36.2548 | 34.3509 | 33.8493 | 34.6597 | 35.3879 | 36.4924 | 37.3394 | 36.8025 | 37.879 | 34.3961 | 34.4213 | 34.1587 | 35.0544 | 35.09 | 35.7108 | 36.494 | 36.6628 | 32.1314 | 31.3534 | 93.7929 | 35.2007 | 33.1288 | 35.0255 | 33.3793 | 33.2049 | 33.488 | 34.9068 | 34.3764 | 34.0838 | 37.1865 | 36.2113 | 33.4702 | 34.4041 | 36.2069 | 36.5587 | 37.4035 | 36.1977 | 33.3797 | 32.6898 | 34.5844 | 35.0228 | 33.1567 | 34.3816 | 34.2812 | 34.3799 | 34.3854 | 34.4298 | 34.3808 | 33.9121 | 34.4116 | 35.7657 | 35.2023 | 36.1625 | 36.149 | 33.5383 | 94.8387 | 94.9973 | 94.1938
2022-09-08 02:54 | 5:04 | 32.5932 | 31.3817 | 32.6571 | 36.2189 | 34.3416 | 33.8281 | 34.6782 | 35.4054 | 36.4898 | 37.3418 | 36.8387 | 37.8809 | 34.4038 | 34.4119 | 34.1697 | 35.0532 | 35.1148 | 35.7306 | 36.4851 | 36.6688 | 32.2929 | 31.3694 | 93.812 | 35.23 | 33.1579 | 35.008 | 33.3775 | 33.1979 | 33.4721 | 34.8914 | 34.3727 | 34.0885 | 37.1841 | 36.211 | 33.4776 | 34.3942 | 36.1905 | 36.5536 | 37.3965 | 36.2162 | 33.3791 | 32.7023 | 34.5915 | 35.0335 | 33.1645 | 34.4022 | 34.2769 | 34.3784 | 34.4085 | 34.4169 | 34.3791 | 33.9186 | 34.3854 | 35.7643 | 35.1933 | 36.1602 | 36.1252 | 33.5291 | 94.728 | 94.8842 | 94.0356
2022-09-08 02:54 | 5:04 | 32.6477 | 31.4148 | 32.6604 | 36.3938 | 34.3402 | 33.8315 | 34.6506 | 35.3824 | 36.4972 | 37.3256 | 36.8202 | 37.8761 | 34.3986 | 34.4074 | 34.1659 | 35.0297 | 35.0919 | 35.7143 | 36.4772 | 36.6545 | 32.4372 | 31.4072 | 93.7376 | 35.3087 | 33.1132 | 35.0086 | 33.3639 | 33.1994 | 33.484 | 34.9037 | 34.3637 | 34.0786 | 37.1851 | 36.218 | 33.4683 | 34.3924 | 36.2113 | 36.5443 | 37.3991 | 36.188 | 33.3674 | 32.7044 | 34.5994 | 35.0098 | 33.1671 | 34.418 | 34.2715 | 34.3816 | 34.3962 | 34.4185 | 34.3903 | 33.9181 | 34.4085 | 35.764 | 35.2137 | 36.1664 | 36.1363 | 33.5397 | 94.5364 | 94.6829 | 93.894
2022-09-08 02:54 | 5:04 | 32.7065 | 31.7286 | 32.6826 | 36.2372 | 34.3494 | 33.8345 | 34.6472 | 35.3877 | 36.4924 | 37.3254 | 36.8028 | 37.8938 | 34.3906 | 34.4132 | 34.1518 | 35.0423 | 35.1135 | 35.7123 | 36.4815 | 36.6675 | 32.8543 | 31.9812 | 93.6404 | 35.249 | 33.1269 | 35.0288 | 33.3693 | 33.2117 | 33.4634 | 34.9054 | 34.3602 | 34.0924 | 37.1979 | 36.2088 | 33.4792 | 34.3985 | 36.211 | 36.5397 | 37.4108 | 36.2069 | 33.3871 | 32.6854 | 34.5789 | 35.0302 | 33.1772 | 34.3974 | 34.2877 | 34.3632 | 34.3828 | 34.4361 | 34.3563 | 33.937 | 34.3962 | 35.766 | 35.2113 | 36.1531 | 36.1211 | 33.5307 | 94.3438 | 94.4965 | 93.7882
2022-09-08 02:54 | 5:04 | 33.2432 | 31.6949 | 32.9363 | 36.3151 | 34.3382 | 33.846 | 34.6455 | 35.3949 | 36.4947 | 37.3339 | 36.8212 | 37.882 | 34.4128 | 34.4166 | 34.1561 | 35.0455 | 35.1298 | 35.7054 | 36.4764 | 36.6576 | 33.4175 | 32.1635 | 93.5391 | 35.2899 | 33.1369 | 35.0332 | 33.3797 | 33.2108 | 33.4702 | 34.8936 | 34.3694 | 34.0664 | 37.1763 | 36.2212 | 33.4859 | 34.3899 | 36.218 | 36.5479 | 37.3968 | 36.1905 | 33.3807 | 32.7102 | 34.5719 | 35.0234 | 33.1921 | 34.3967 | 34.2848 | 34.3705 | 34.371 | 34.4201 | 34.3596 | 33.9152 | 34.3828 | 35.7563 | 35.2091 | 36.1518 | 36.1561 | 33.541 | 94.0841 | 94.2783 | 93.5462
2022-09-08 02:55 | 5:04 | 34.3243 | 31.6738 | 33.1728 | 36.234 | 34.3397 | 33.8618 | 34.6653 | 35.3989 | 36.4959 | 37.3228 | 36.815 | 37.8951 | 34.416 | 34.4133 | 34.1554 | 35.0674 | 35.1174 | 35.684 | 36.4765 | 36.6672 | 34.274 | 32.0638 | 93.4141 | 35.3465 | 33.1463 | 35.0156 | 33.3791 | 33.217 | 33.4776 | 34.8911 | 34.3661 | 34.0808 | 37.1675 | 36.2318 | 33.4817 | 34.3939 | 36.2088 | 36.5311 | 37.3935 | 36.2113 | 33.387 | 32.7103 | 34.5932 | 35.0187 | 33.2017 | 34.3908 | 34.2906 | 34.3728 | 34.3776 | 34.4205 | 34.3643 | 33.9033 | 34.371 | 35.7632 | 35.2261 | 36.1651 | 36.1427 | 33.5262 | 93.9263 | 94.0955 | 93.5584
2022-09-08 02:55 | 5:05 | 34.9939 | 31.6751 | 33.4112 | 36.3849 | 34.3627 | 33.8465 | 34.6462 | 35.3848 | 36.5004 | 37.3346 | 36.8128 | 37.8842 | 34.4246 | 34.421 | 34.142 | 35.0514 | 35.1094 | 35.7038 | 36.4861 | 36.6525 | 34.8252 | 31.8334 | 93.3131 | 35.3049 | 33.1322 | 34.9946 | 33.3674 | 33.1745 | 33.4683 | 34.8954 | 34.3768 | 34.0868 | 37.1754 | 36.2254 | 33.4628 | 34.4004 | 36.2212 | 36.5408 | 37.3967 | 36.211 | 33.3871 | 32.7113 | 34.5997 | 35.0399 | 33.2156 | 34.4089 | 34.2847 | 34.3638 | 34.3658 | 34.4312 | 34.3538 | 33.9147 | 34.3776 | 35.7475 | 35.2122 | 36.174 | 36.1213 | 33.5312 | 93.7956 | 93.9923 | 93.4472
2022-09-08 02:55 | 5:05 | 35.2515 | 31.6745 | 33.5008 | 36.3428 | 34.3474 | 33.8396 | 34.646 | 35.4066 | 36.4788 | 37.3162 | 36.8118 | 37.8872 | 34.4275 | 34.4104 | 34.1495 | 35.0643 | 35.1124 | 35.7101 | 36.4827 | 36.6519 | 35.0256 | 31.7188 | 93.2319 | 35.3691 | 33.1323 | 35.0102 | 33.3871 | 33.1977 | 33.4792 | 34.8724 | 34.3703 | 34.1029 | 37.1886 | 36.2317 | 33.4789 | 34.3991 | 36.2318 | 36.5334 | 37.4109 | 36.218 | 33.3991 | 32.7115 | 34.5897 | 35.0295 | 33.2221 | 34.4226 | 34.2827 | 34.3801 | 34.3654 | 34.4222 | 34.3796 | 33.9034 | 34.3658 | 35.7649 | 35.2097 | 36.1793 | 36.1317 | 33.532 | 93.6765 | 93.8848 | 93.3616
2022-09-08 02:55 | 5:05 | 35.3559 | 31.6976 | 33.5465 | 36.3892 | 34.3434 | 33.8419 | 34.6486 | 35.407 | 36.4782 | 37.3315 | 36.8235 | 37.861 | 34.4067 | 34.4134 | 34.1355 | 35.0686 | 35.1066 | 35.7033 | 36.4969 | 36.6553 | 35.1215 | 31.7083 | 93.0062 | 35.3759 | 33.1278 | 35.0273 | 33.3807 | 33.2172 | 33.4859 | 34.8793 | 34.3811 | 34.0716 | 37.1872 | 36.2343 | 33.4724 | 34.4172 | 36.2254 | 36.5473 | 37.3909 | 36.2088 | 33.3873 | 32.7074 | 34.6161 | 35.0322 | 33.2397 | 34.4184 | 34.2799 | 34.3706 | 34.3778 | 34.4228 | 34.3631 | 33.9309 | 34.3654 | 35.7629 | 35.226 | 36.1758 | 36.1426 | 33.526 | 93.5647 | 93.7957 | 93.2662
2022-09-08 02:55 | 5:05 | 35.2457 | 31.7087 | 33.5174 | 36.3611 | 34.3519 | 33.852 | 34.6581 | 35.3856 | 36.496 | 37.3278 | 36.8272 | 37.8524 | 34.4096 | 34.4025 | 34.1483 | 35.0669 | 35.1163 | 35.6952 | 36.4843 | 36.6499 | 35.0815 | 31.6893 | 93.0868 | 35.4305 | 33.1347 | 35.0268 | 33.387 | 33.1979 | 33.4817 | 34.8908 | 34.3738 | 34.0834 | 37.1723 | 36.2304 | 33.4749 | 34.4116 | 36.2317 | 36.5345 | 37.4155 | 36.2212 | 33.3794 | 32.7259 | 34.6199 | 35.0288 | 33.2429 | 34.4196 | 34.2827 | 34.366 | 34.3642 | 34.4155 | 34.3827 | 33.9289 | 34.3778 | 35.7571 | 35.2205 | 36.1535 | 36.1344 | 33.5272 | 93.5071 | 93.6938 | 93.282
2022-09-08 02:55 | 5:05 | 35.1131 | 31.722 | 33.4017 | 36.3816 | 34.3529 | 33.8565 | 34.664 | 35.383 | 36.481 | 37.318 | 36.826 | 37.8742 | 34.4138 | 34.4135 | 34.1498 | 35.0615 | 35.1042 | 35.7146 | 36.4937 | 36.642 | 35.0583 | 31.6886 | 93.0417 | 35.388 | 33.1565 | 35.0319 | 33.3871 | 33.2152 | 33.4628 | 34.8762 | 34.3835 | 34.0895 | 37.1771 | 36.2341 | 33.4741 | 34.403 | 36.2343 | 36.531 | 37.415 | 36.2318 | 33.396 | 32.7278 | 34.6012 | 35.04 | 33.245 | 34.4232 | 34.2812 | 34.3873 | 34.359 | 34.4156 | 34.3615 | 33.93 | 34.3642 | 35.7589 | 35.2084 | 36.1842 | 36.1314 | 33.5296 | 93.4773 | 93.5699 | 93.2319
2022-09-08 02:56 | 5:06 | 34.9982 | 31.7093 | 33.2229 | 36.3175 | 34.3565 | 33.8644 | 34.6599 | 35.4033 | 36.4817 | 37.3256 | 36.8352 | 37.8835 | 34.4143 | 34.4239 | 34.1703 | 35.0548 | 35.128 | 35.6947 | 36.4888 | 36.6561 | 35.0017 | 31.6955 | 92.9118 | 35.4152 | 33.1519 | 35.0433 | 33.3991 | 33.1968 | 33.4789 | 34.8893 | 34.3844 | 34.0897 | 37.1706 | 36.2333 | 33.4869 | 34.3975 | 36.2304 | 36.5465 | 37.4211 | 36.2254 | 33.3873 | 32.7445 | 34.6126 | 35.0314 | 33.2706 | 34.4102 | 34.2935 | 34.3551 | 34.3712 | 34.4286 | 34.3912 | 33.9355 | 34.359 | 35.7593 | 35.2089 | 36.1833 | 36.1444 | 33.5399 | 93.4044 | 93.5514 | 93.2066
2022-09-08 02:56 | 5:06 | 34.3789 | 31.7339 | 33.1316 | 36.4 | 34.3655 | 33.8598 | 34.6568 | 35.3935 | 36.4758 | 37.3355 | 36.8574 | 37.8744 | 34.4023 | 34.4111 | 34.1572 | 35.063 | 35.1065 | 35.7096 | 36.5072 | 36.6612 | 34.9534 | 31.7151 | 92.9257 | 35.4029 | 33.1412 | 35.0284 | 33.3873 | 33.2123 | 33.4724 | 34.9122 | 34.3828 | 34.0918 | 37.1671 | 36.2274 | 33.4811 | 34.4026 | 36.2341 | 36.5441 | 37.4099 | 36.2317 | 33.3882 | 32.7366 | 34.6263 | 35.0334 | 33.2563 | 34.4409 | 34.3064 | 34.3778 | 34.3432 | 34.4215 | 34.3688 | 33.9218 | 34.3712 | 35.7653 | 35.2044 | 36.1466 | 36.1622 | 33.5372 | 93.3456 | 93.4763 | 93.1771
2022-09-08 02:56 | 5:06 | 34.2711 | 31.7529 | 33.1068 | 36.4924 | 34.347 | 33.8641 | 34.6607 | 35.4044 | 36.4718 | 37.3404 | 36.8318 | 37.9072 | 34.4117 | 34.4036 | 34.1396 | 35.0353 | 35.1169 | 35.718 | 36.5053 | 36.6556 | 34.9928 | 31.6977 | 92.8728 | 35.4333 | 33.1326 | 35.0335 | 33.3794 | 33.2157 | 33.4749 | 34.9047 | 34.3726 | 34.0871 | 37.1744 | 36.2454 | 33.4821 | 34.3922 | 36.2333 | 36.5445 | 37.4001 | 36.2343 | 33.4089 | 32.7544 | 34.6392 | 35.042 | 33.2807 | 34.4239 | 34.2832 | 34.3713 | 34.3388 | 34.4055 | 34.3942 | 33.9311 | 34.3432 | 35.7686 | 35.226 | 36.1491 | 36.1673 | 33.5428 | 93.2442 | 93.439 | 93.1186
2022-09-08 02:56 | 5:06 | 34.1436 | 31.739 | 33.1321 | 36.4042 | 34.3498 | 33.8601 | 34.6501 | 35.421 | 36.4969 | 37.3321 | 36.8362 | 37.8667 | 34.4269 | 34.4305 | 34.1593 | 35.065 | 35.1257 | 35.7052 | 36.5049 | 36.6608 | 34.9762 | 31.7085 | 92.9299 | 35.4511 | 33.1419 | 35.0426 | 33.396 | 33.2091 | 33.4741 | 34.8955 | 34.3924 | 34.0913 | 37.1904 | 36.2403 | 33.4902 | 34.4194 | 36.2274 | 36.5441 | 37.4025 | 36.2304 | 33.4023 | 32.7544 | 34.6425 | 35.065 | 33.2953 | 34.4106 | 34.3067 | 34.3633 | 34.3559 | 34.4186 | 34.4051 | 33.937 | 34.3388 | 35.7827 | 35.2161 | 36.1747 | 36.1355 | 33.5393 | 93.1979 | 93.3686 | 93.0894
2022-09-08 02:56 | 5:06 | 34.0055 | 31.7592 | 33.1394 | 36.3061 | 34.3728 | 33.8541 | 34.6664 | 35.3991 | 36.481 | 37.3495 | 36.832 | 37.8753 | 34.4253 | 34.4159 | 34.1543 | 35.0499 | 35.1369 | 35.7333 | 36.5127 | 36.6705 | 34.9862 | 31.7157 | 92.8978 | 35.4898 | 33.1602 | 35.053 | 33.3873 | 33.2108 | 33.4869 | 34.8882 | 34.3931 | 34.1017 | 37.1848 | 36.2455 | 33.5011 | 34.4 | 36.2454 | 36.5578 | 37.4067 | 36.2341 | 33.4032 | 32.7732 | 34.6485 | 35.071 | 33.2951 | 34.4389 | 34.304 | 34.3766 | 34.3475 | 34.4088 | 34.3891 | 33.9541 | 34.3559 | 35.7795 | 35.2187 | 36.1954 | 36.1557 | 33.5475 | 93.1181 | 93.2635 | 93.0056
2022-09-08 02:56 | 5:06 | 33.937 | 31.7565 | 33.1931 | 36.3358 | 34.3644 | 33.8563 | 34.6679 | 35.4051 | 36.4868 | 37.3569 | 36.8316 | 37.881 | 34.4159 | 34.4245 | 34.1611 | 35.0682 | 35.1228 | 35.7293 | 36.5048 | 36.6596 | 35.0447 | 31.7363 | 92.7411 | 35.4639 | 33.1582 | 35.0479 | 33.3882 | 33.2187 | 33.4811 | 34.8801 | 34.3897 | 34.0931 | 37.181 | 36.2456 | 33.4803 | 34.4113 | 36.2403 | 36.5561 | 37.4059 | 36.2333 | 33.3917 | 32.758 | 34.6492 | 35.0549 | 33.2993 | 34.4553 | 34.3165 | 34.3783 | 34.3447 | 34.4159 | 34.3939 | 33.9429 | 34.3475 | 35.7935 | 35.2232 | 36.1927 | 36.1604 | 33.5552 | 93.0384 | 93.1951 | 92.9706
2022-09-08 02:57 | 5:06 | 34.5343 | 31.7974 | 33.2043 | 36.4171 | 34.3415 | 33.8559 | 34.6541 | 35.3981 | 36.4873 | 37.3408 | 36.8386 | 37.8837 | 34.4239 | 34.4136 | 34.163 | 35.062 | 35.1309 | 35.7301 | 36.5196 | 36.6611 | 35.1383 | 31.7583 | 92.7174 | 35.4753 | 33.1435 | 35.0508 | 33.4089 | 33.2201 | 33.4821 | 34.8955 | 34.3903 | 34.117 | 37.1964 | 36.2536 | 33.4857 | 34.4056 | 36.2455 | 36.5527 | 37.4214 | 36.2274 | 33.4131 | 32.7754 | 34.6667 | 35.0761 | 33.3145 | 34.423 | 34.296 | 34.3802 | 34.3582 | 34.4246 | 34.4034 | 33.9407 | 34.3447 | 35.7922 | 35.2172 | 36.173 | 36.1596 | 33.5524 | 92.9873 | 93.0778 | 92.9095
2022-09-08 02:57 | 5:07 | 35.0515 | 31.7799 | 33.2704 | 36.4785 | 34.3632 | 33.8689 | 34.6716 | 35.4089 | 36.5006 | 37.3403 | 36.8462 | 37.9114 | 34.4084 | 34.4269 | 34.149 | 35.0863 | 35.1383 | 35.7277 | 36.5078 | 36.6698 | 35.2208 | 31.7708 | 92.7283 | 35.4831 | 33.1774 | 35.0472 | 33.4023 | 33.2308 | 33.4902 | 34.8832 | 34.3776 | 34.0903 | 37.183 | 36.2353 | 33.4877 | 34.4019 | 36.2456 | 36.5483 | 37.4238 | 36.2454 | 33.403 | 32.7662 | 34.6735 | 35.1029 | 33.3134 | 34.4346 | 34.2982 | 34.3824 | 34.3384 | 34.4184 | 34.3994 | 33.9503 | 34.3582 | 35.7937 | 35.2286 | 36.1825 | 36.1603 | 33.5712 | 92.9002 | 93.0136 | 92.8986
2022-09-08 02:57 | 5:07 | 35.1796 | 31.8112 | 33.2715 | 36.4031 | 34.3614 | 33.8646 | 34.6565 | 35.4151 | 36.5048 | 37.3533 | 36.8479 | 37.8968 | 34.4261 | 34.4188 | 34.1587 | 35.0631 | 35.1343 | 35.7272 | 36.5102 | 36.6759 | 35.2466 | 31.7951 | 92.6788 | 35.4626 | 33.1683 | 35.0462 | 33.4032 | 33.2239 | 33.5011 | 34.8886 | 34.4006 | 34.1067 | 37.2014 | 36.2614 | 33.5083 | 34.4095 | 36.2536 | 36.5465 | 37.4323 | 36.2403 | 33.4064 | 32.7921 | 34.6875 | 35.1086 | 33.3297 | 34.4469 | 34.3148 | 34.3835 | 34.3388 | 34.4199 | 34.3919 | 33.9425 | 34.3384 | 35.7833 | 35.2138 | 36.1936 | 36.1567 | 33.5674 | 92.7776 | 92.9275 | 92.797
2022-09-08 02:57 | 5:07 | 35.2799 | 31.826 | 33.3178 | 36.5129 | 34.3662 | 33.8845 | 34.6664 | 35.4017 | 36.5151 | 37.3736 | 36.8429 | 37.9054 | 34.4365 | 34.4209 | 34.1766 | 35.0595 | 35.1447 | 35.729 | 36.526 | 36.6672 | 35.2523 | 31.8138 | 92.5549 | 35.5111 | 33.1763 | 35.068 | 33.3917 | 33.239 | 33.4803 | 34.9061 | 34.389 | 34.1064 | 37.2151 | 36.2468 | 33.5065 | 34.4238 | 36.2353 | 36.5684 | 37.4414 | 36.2455 | 33.4015 | 32.7987 | 34.7026 | 35.0899 | 33.3409 | 34.4279 | 34.2949 | 34.3919 | 34.3219 | 34.4174 | 34.3947 | 33.9638 | 34.3388 | 35.8049 | 35.224 | 36.1649 | 36.1662 | 33.5683 | 92.6915 | 92.7979 | 92.758
2022-09-08 02:57 | 5:07 | 35.3966 | 31.851 | 33.4059 | 36.5838 | 34.3685 | 33.8623 | 34.6686 | 35.4136 | 36.5092 | 37.3533 | 36.8426 | 37.9032 | 34.4316 | 34.4249 | 34.1753 | 35.0838 | 35.1214 | 35.7227 | 36.5089 | 36.6778 | 35.2786 | 31.8312 | 92.4466 | 35.5196 | 33.1796 | 35.0677 | 33.4131 | 33.2416 | 33.4857 | 34.8973 | 34.3678 | 34.0993 | 37.2131 | 36.2468 | 33.5029 | 34.4174 | 36.2614 | 36.544 | 37.4241 | 36.2456 | 33.401 | 32.8039 | 34.6798 | 35.1175 | 33.3605 | 34.4279 | 34.3084 | 34.3925 | 34.3218 | 34.4156 | 34.4015 | 33.9526 | 34.3219 | 35.79 | 35.2424 | 36.1716 | 36.1512 | 33.5697 | 92.579 | 92.6886 | 92.6897
2022-09-08 02:57 | 5:07 | 35.4493 | 31.8565 | 33.5334 | 36.4789 | 34.3496 | 33.8794 | 34.6733 | 35.4184 | 36.4969 | 37.3456 | 36.8341 | 37.897 | 34.4185 | 34.4249 | 34.1854 | 35.062 | 35.144 | 35.7398 | 36.5162 | 36.6637 | 35.3135 | 31.8421 | 92.3723 | 35.567 | 33.1743 | 35.0699 | 33.403 | 33.2411 | 33.4877 | 34.8957 | 34.3882 | 34.094 | 37.2032 | 36.2398 | 33.4936 | 34.4003 | 36.2468 | 36.5512 | 37.4398 | 36.2536 | 33.4227 | 32.8074 | 34.6877 | 35.1187 | 33.355 | 34.4199 | 34.2919 | 34.3942 | 34.3323 | 34.4161 | 34.3819 | 33.9735 | 34.3218 | 35.8057 | 35.2179 | 36.1707 | 36.1666 | 33.5824 | 92.4511 | 92.643 | 92.4488
2022-09-08 02:58 | 5:08 | 35.4921 | 31.8706 | 33.5857 | 36.6046 | 34.3672 | 33.8772 | 34.6631 | 35.4093 | 36.5347 | 37.3644 | 36.8347 | 37.8864 | 34.4278 | 34.4237 | 34.1791 | 35.073 | 35.163 | 35.7264 | 36.5322 | 36.6815 | 35.2834 | 31.8787 | 92.326 | 35.5306 | 33.1649 | 35.0669 | 33.4064 | 33.2391 | 33.5083 | 34.8842 | 34.3824 | 34.1106 | 37.201 | 36.2654 | 33.5065 | 34.4273 | 36.2468 | 36.5662 | 37.4438 | 36.2353 | 33.4042 | 32.8132 | 34.7182 | 35.1091 | 33.3667 | 34.4316 | 34.3071 | 34.3892 | 34.345 | 34.3989 | 34.3962 | 33.9696 | 34.3323 | 35.8143 | 35.2195 | 36.1762 | 36.1739 | 33.5844 | 92.3042 | 92.5118 | 92.4405
2022-09-08 02:58 | 5:08 | 35.5561 | 31.893 | 33.6709 | 36.5255 | 34.3824 | 33.8784 | 34.6713 | 35.4237 | 36.5122 | 37.3686 | 36.8522 | 37.897 | 34.4263 | 34.412 | 34.1904 | 35.0858 | 35.1481 | 35.7453 | 36.5284 | 36.666 | 35.3051 | 31.8884 | 92.2688 | 35.6376 | 33.1723 | 35.0675 | 33.4015 | 33.2216 | 33.5065 | 34.892 | 34.398 | 34.0933 | 37.2057 | 36.2786 | 33.5016 | 34.4236 | 36.2398 | 36.5671 | 37.453 | 36.2614 | 33.4255 | 32.8132 | 34.7016 | 35.1337 | 33.374 | 34.4469 | 34.3096 | 34.3941 | 34.3195 | 34.4235 | 34.4025 | 33.9725 | 34.345 | 35.8252 | 35.2152 | 36.185 | 36.1707 | 33.5814 | 92.2045 | 92.4169 | 92.3795
2022-09-08 02:58 | 5:08 | 35.578 | 31.9075 | 33.779 | 36.5863 | 34.3666 | 33.8644 | 34.675 | 35.4047 | 36.5139 | 37.368 | 36.8616 | 37.9124 | 34.4305 | 34.4337 | 34.1667 | 35.0869 | 35.1494 | 35.7361 | 36.5209 | 36.6752 | 35.3209 | 31.8857 | 92.1967 | 35.5958 | 33.1825 | 35.0665 | 33.401 | 33.2338 | 33.5029 | 34.8923 | 34.3952 | 34.1068 | 37.2065 | 36.239 | 33.5103 | 34.4337 | 36.2654 | 36.5704 | 37.4509 | 36.2468 | 33.4259 | 32.8254 | 34.722 | 35.1354 | 33.3681 | 34.4431 | 34.3162 | 34.4079 | 34.3116 | 34.3951 | 34.4213 | 33.9749 | 34.3195 | 35.8123 | 35.2195 | 36.1896 | 36.1772 | 33.6083 | 92.106 | 92.3227 | 92.3232
2022-09-08 02:58 | 5:08 | 35.6307 | 31.9272 | 33.8969 | 36.5782 | 34.366 | 33.8863 | 34.6731 | 35.4088 | 36.5122 | 37.3663 | 36.8539 | 37.89 | 34.4318 | 34.4367 | 34.1948 | 35.0812 | 35.1699 | 35.741 | 36.5241 | 36.691 | 35.3552 | 31.9138 | 91.9566 | 35.6014 | 33.1628 | 35.0705 | 33.4227 | 33.2296 | 33.4936 | 34.9061 | 34.3769 | 34.1191 | 37.2007 | 36.2737 | 33.5041 | 34.4207 | 36.2786 | 36.5582 | 37.45 | 36.2468 | 33.4261 | 32.8342 | 34.7276 | 35.1527 | 33.3792 | 34.4472 | 34.321 | 34.413 | 34.3142 | 34.4199 | 34.4119 | 33.9746 | 34.3116 | 35.8113 | 35.2186 | 36.1837 | 36.176 | 33.5889 | 91.9626 | 92.1658 | 92.2199
2022-09-08 02:58 | 5:08 | 35.6734 | 31.9377 | 33.9819 | 36.6903 | 34.355 | 33.8871 | 34.7061 | 35.4228 | 36.5185 | 37.3693 | 36.8394 | 37.9174 | 34.438 | 34.4328 | 34.2053 | 35.0724 | 35.168 | 35.7209 | 36.539 | 36.6797 | 35.0072 | 31.8427 | 91.9425 | 35.6315 | 33.1603 | 35.0878 | 33.4042 | 33.2317 | 33.5065 | 34.9096 | 34.4011 | 34.1105 | 37.2098 | 36.2716 | 33.5157 | 34.4369 | 36.239 | 36.5543 | 37.4424 | 36.2398 | 33.4324 | 32.815 | 34.7355 | 35.1461 | 33.3702 | 34.4273 | 34.3144 | 34.4139 | 34.3204 | 34.4204 | 34.4074 | 33.9707 | 34.3142 | 35.8121 | 35.2288 | 36.1938 | 36.1864 | 33.6232 | 91.837 | 92.0064 | 92.2069
2022-09-08 02:58 | 5:08 | 31.1969 | 31.1899 | 33.1511 | 36.5942 | 34.3646 | 33.8861 | 34.685 | 35.4245 | 36.5101 | 37.3688 | 36.8452 | 37.9171 | 34.4235 | 34.4064 | 34.184 | 35.0845 | 35.1724 | 35.7469 | 36.5294 | 36.6936 | 30.4378 | 31.4989 | 91.7889 | 35.5878 | 33.1773 | 35.0733 | 33.4255 | 33.2417 | 33.5016 | 34.9184 | 34.3917 | 34.1193 | 37.2144 | 36.2625 | 33.5188 | 34.4274 | 36.2737 | 36.5543 | 37.4544 | 36.2654 | 33.4359 | 32.8088 | 34.7247 | 35.1409 | 33.3878 | 34.4391 | 34.318 | 34.4005 | 34.3077 | 34.3865 | 34.4132 | 33.9707 | 34.3204 | 35.8411 | 35.2279 | 36.1729 | 36.1929 | 33.617 | 91.7259 | 91.8713 | 92.0949
2022-09-08 02:59 | 5:08 | 30.7744 | 30.0913 | 32.1067 | 36.5431 | 34.3808 | 33.8998 | 34.6799 | 35.4216 | 36.5463 | 37.3652 | 36.8646 | 37.9102 | 34.4273 | 34.4295 | 34.2021 | 35.08 | 35.1676 | 35.7442 | 36.5289 | 36.6909 | 28.2983 | 29.4888 | 91.7628 | 35.5014 | 33.1991 | 35.078 | 33.4259 | 33.2562 | 33.5103 | 34.9058 | 34.3908 | 34.1175 | 37.2187 | 36.2859 | 33.5069 | 34.447 | 36.2716 | 36.5671 | 37.4581 | 36.2786 | 33.4376 | 32.8599 | 34.7375 | 35.1661 | 33.4143 | 34.4219 | 34.3345 | 34.4228 | 34.314 | 34.415 | 34.4166 | 33.9951 | 34.3077 | 35.8153 | 35.2315 | 36.1777 | 36.1994 | 33.598 | 91.6052 | 91.7423 | 92.0584
2022-09-08 02:59 | 5:09 | 31.4566 | 28.9151 | 31.8741 | 36.5859 | 34.3791 | 33.8512 | 34.6971 | 35.4334 | 36.525 | 37.38 | 36.8381 | 37.91 | 34.4287 | 34.4129 | 34.2101 | 35.0849 | 35.1544 | 35.7281 | 36.5482 | 36.6986 | 28.7707 | 28.0815 | 91.6162 | 35.4957 | 33.1986 | 35.0738 | 33.4261 | 33.2413 | 33.5041 | 34.9157 | 34.4016 | 34.1274 | 37.2025 | 36.2697 | 33.5067 | 34.4166 | 36.2625 | 36.5742 | 37.4537 | 36.239 | 33.4203 | 32.8659 | 34.7402 | 35.1734 | 33.3858 | 34.4269 | 34.3127 | 34.428 | 34.3132 | 34.4065 | 34.4133 | 33.9769 | 34.314 | 35.8336 | 35.2366 | 36.1751 | 36.1762 | 33.6164 | 91.524 | 91.6791 | 91.9937
2022-09-08 02:59 | 5:09 | 31.6424 | 28.4106 | 31.7919 | 36.5783 | 34.3903 | 33.8894 | 34.6906 | 35.4236 | 36.5305 | 37.3792 | 36.8651 | 37.9055 | 34.4297 | 34.4178 | 34.2025 | 35.0835 | 35.1663 | 35.7424 | 36.5348 | 36.699 | 29.1473 | 27.3709 | 91.6144 | 35.4328 | 33.1973 | 35.0712 | 33.4324 | 33.238 | 33.5157 | 34.9004 | 34.3871 | 34.1249 | 37.2219 | 36.2519 | 33.5057 | 34.4172 | 36.2859 | 36.5772 | 37.4751 | 36.2737 | 33.422 | 32.8348 | 34.7531 | 35.1664 | 33.3979 | 34.4476 | 34.3299 | 34.4127 | 34.2918 | 34.3895 | 34.421 | 34.015 | 34.3132 | 35.8486 | 35.2199 | 36.2074 | 36.1909 | 33.6175 | 91.4446 | 91.6216 | 92.0186
2022-09-08 02:59 | 5:09 | 31.5911 | 28.153 | 31.5667 | 36.6118 | 34.3563 | 33.8696 | 34.7185 | 35.4169 | 36.5413 | 37.3767 | 36.8368 | 37.9312 | 34.4286 | 34.4223 | 34.2231 | 35.0785 | 35.1685 | 35.7467 | 36.5524 | 36.6995 | 29.707 | 26.6376 | 91.6967 | 35.4041 | 33.2042 | 35.0714 | 33.4359 | 33.2415 | 33.5188 | 34.8896 | 34.403 | 34.1076 | 37.2503 | 36.2619 | 33.5222 | 34.4159 | 36.2697 | 36.5827 | 37.4565 | 36.2716 | 33.4162 | 32.8717 | 34.7792 | 35.1783 | 33.411 | 34.449 | 34.3448 | 34.4023 | 34.2875 | 34.3977 | 34.4104 | 33.9964 | 34.2918 | 35.8442 | 35.2134 | 36.2009 | 36.1896 | 33.609 | 91.5236 | 91.6727 | 92.0157
2022-09-08 02:59 | 5:09 | 31.5279 | 27.892 | 31.378 | 36.6611 | 34.3596 | 33.8703 | 34.7391 | 35.4314 | 36.5424 | 37.3831 | 36.8632 | 37.9072 | 34.4217 | 34.4268 | 34.2101 | 35.0931 | 35.1668 | 35.7447 | 36.5473 | 36.7292 | 29.9548 | 26.2823 | 91.8242 | 35.3797 | 33.1949 | 35.0554 | 33.4376 | 33.2198 | 33.5069 | 34.907 | 34.3887 | 34.1166 | 37.2222 | 36.2577 | 33.506 | 34.4189 | 36.2519 | 36.5849 | 37.4547 | 36.2625 | 33.4208 | 32.8685 | 34.778 | 35.212 | 33.4213 | 34.4414 | 34.3212 | 34.421 | 34.292 | 34.3806 | 34.4134 | 33.9994 | 34.2875 | 35.8366 | 35.2234 | 36.1904 | 36.2049 | 33.627 | 91.5779 | 91.7513 | 92.1265
2022-09-08 02:59 | 5:09 | 31.3869 | 27.8309 | 31.3096 | 36.6184 | 34.3643 | 33.8774 | 34.7466 | 35.4458 | 36.5338 | 37.3888 | 36.8396 | 37.9076 | 34.4325 | 34.4336 | 34.2141 | 35.0787 | 35.151 | 35.7414 | 36.543 | 36.7093 | 30.0135 | 26.1136 | 91.7124 | 35.2783 | 33.1944 | 35.0859 | 33.4203 | 33.2334 | 33.5067 | 34.9094 | 34.369 | 34.1041 | 37.2402 | 36.2657 | 33.5023 | 34.4129 | 36.2619 | 36.5799 | 37.4722 | 36.2859 | 33.4218 | 32.8878 | 34.7804 | 35.1886 | 33.3913 | 34.4258 | 34.3263 | 34.4118 | 34.2984 | 34.3956 | 34.4025 | 34.0078 | 34.292 | 35.8422 | 35.2107 | 36.192 | 36.191 | 33.6483 | 91.7144 | 91.8494 | 92.1664
2022-09-08 03:00 | 5:10 | 31.2939 | 27.8247 | 31.1561 | 36.6266 | 34.3538 | 33.8798 | 34.7341 | 35.4386 | 36.5531 | 37.3936 | 36.8465 | 37.9137 | 34.4243 | 34.4344 | 34.2152 | 35.0954 | 35.1811 | 35.7423 | 36.5524 | 36.7068 | 29.9561 | 25.9307 | 91.8974 | 35.2806 | 33.1641 | 35.0645 | 33.422 | 33.2452 | 33.5057 | 34.8955 | 34.3796 | 34.1096 | 37.2145 | 36.2707 | 33.5054 | 34.4322 | 36.2577 | 36.5719 | 37.475 | 36.2697 | 33.4233 | 32.8895 | 34.7579 | 35.2015 | 33.4216 | 34.4204 | 34.3437 | 34.4243 | 34.3025 | 34.3714 | 34.4135 | 34.0205 | 34.2984 | 35.8302 | 35.2181 | 36.1953 | 36.1802 | 33.6309 | 91.8443 | 91.9077 | 92.2003
2022-09-08 03:00 | 5:10 | 31.1293 | 27.8288 | 31.0869 | 36.5861 | 34.3796 | 33.8715 | 34.7421 | 35.4357 | 36.5491 | 37.3916 | 36.8316 | 37.9251 | 34.4221 | 34.4054 | 34.2148 | 35.0887 | 35.1514 | 35.7376 | 36.5392 | 36.6974 | 29.8073 | 25.8665 | 91.8918 | 35.2378 | 33.1843 | 35.0634 | 33.4162 | 33.2297 | 33.5222 | 34.9148 | 34.3758 | 34.1203 | 37.2415 | 36.2659 | 33.5014 | 34.4218 | 36.2657 | 36.5812 | 37.4768 | 36.2519 | 33.4201 | 32.8591 | 34.7664 | 35.1873 | 33.4188 | 34.4527 | 34.331 | 34.4173 | 34.2946 | 34.3959 | 34.4239 | 34.031 | 34.3025 | 35.8305 | 35.2052 | 36.2283 | 36.2178 | 33.6373 | 91.9719 | 92.0842 | 92.2819
2022-09-08 03:00 | 5:10 | 30.98 | 27.8251 | 31.058 | 36.5182 | 34.3631 | 33.8632 | 34.7638 | 35.4271 | 36.5392 | 37.3979 | 36.8453 | 37.9188 | 34.4357 | 34.42 | 34.1975 | 35.0757 | 35.1687 | 35.7386 | 36.5263 | 36.7296 | 29.6476 | 25.7418 | 92.1112 | 35.1713 | 33.1787 | 35.0687 | 33.4208 | 33.2356 | 33.506 | 34.9113 | 34.366 | 34.1194 | 37.2148 | 36.2686 | 33.5113 | 34.4142 | 36.2707 | 36.5757 | 37.4883 | 36.2619 | 33.4331 | 32.8736 | 34.7601 | 35.2009 | 33.4174 | 34.4404 | 34.3357 | 34.4247 | 34.2906 | 34.3591 | 34.4111 | 34.0016 | 34.2946 | 35.8649 | 35.2011 | 36.22 | 36.1889 | 33.6338 | 92.1512 | 92.2613 | 92.4278
2022-09-08 03:00 | 5:10 | 30.7021 | 27.7695 | 30.7664 | 36.5143 | 34.3827 | 33.8739 | 34.7782 | 35.4487 | 36.5529 | 37.3742 | 36.8351 | 37.9207 | 34.442 | 34.4248 | 34.2278 | 35.0692 | 35.1724 | 35.7261 | 36.524 | 36.7281 | 29.4889 | 25.5638 | 92.223 | 35.2466 | 33.1774 | 35.0675 | 33.4218 | 33.2362 | 33.5023 | 34.9132 | 34.3753 | 34.1259 | 37.2105 | 36.2604 | 33.4954 | 34.3957 | 36.2659 | 36.577 | 37.4771 | 36.2577 | 33.4116 | 32.8776 | 34.751 | 35.2104 | 33.3965 | 34.4387 | 34.3207 | 34.4217 | 34.2902 | 34.3593 | 34.4036 | 34.0141 | 34.2906 | 35.8433 | 35.196 | 36.186 | 36.1981 | 33.63 | 92.2734 | 92.4275 | 92.4569
2022-09-08 03:00 | 5:10 | 29.4748 | 27.7131 | 30.1975 | 36.3857 | 34.3615 | 33.8633 | 34.7768 | 35.4408 | 36.5284 | 37.3803 | 36.8335 | 37.8995 | 34.4356 | 34.4016 | 34.2135 | 35.0884 | 35.1723 | 35.7239 | 36.5239 | 36.7331 | 29.3232 | 25.4143 | 92.0711 | 35.1684 | 33.201 | 35.0642 | 33.4233 | 33.2275 | 33.5054 | 34.9049 | 34.374 | 34.1083 | 37.2194 | 36.2721 | 33.5094 | 34.4042 | 36.2686 | 36.5809 | 37.4806 | 36.2657 | 33.4238 | 32.8821 | 34.7648 | 35.2067 | 33.3844 | 34.4295 | 34.3302 | 34.426 | 34.2858 | 34.3825 | 34.4305 | 34.0176 | 34.2902 | 35.8407 | 35.1893 | 36.1985 | 36.1928 | 33.6433 | 92.3736 | 92.5353 | 92.5362
2022-09-08 03:00 | 5:10 | 26.4206 | 27.5424 | 29.5511 | 36.4967 | 34.3912 | 33.8675 | 34.7678 | 35.4492 | 36.5323 | 37.3933 | 36.8205 | 37.9057 | 34.4194 | 34.4262 | 34.2363 | 35.0739 | 35.174 | 35.739 | 36.5263 | 36.7274 | 29.1954 | 25.3191 | 92.058 | 35.2403 | 33.1942 | 35.0569 | 33.4201 | 33.2327 | 33.5014 | 34.9034 | 34.368 | 34.1236 | 37.21 | 36.2788 | 33.5065 | 34.4093 | 36.2604 | 36.5633 | 37.4819 | 36.2707 | 33.4211 | 32.9022 | 34.7471 | 35.2146 | 33.398 | 34.4209 | 34.3411 | 34.4297 | 34.286 | 34.3662 | 34.4159 | 34.0155 | 34.2858 | 35.8334 | 35.207 | 36.2078 | 36.2174 | 33.6627 | 92.5175 | 92.6699 | 92.558
2022-09-08 03:01 | 5:10 | 25.9829 | 27.2903 | 29.1515 | 36.4196 | 34.3688 | 33.8546 | 34.7838 | 35.4323 | 36.555 | 37.3897 | 36.8443 | 37.8966 | 34.4393 | 34.4062 | 34.2283 | 35.0957 | 35.1543 | 35.7182 | 36.5174 | 36.7181 | 29.0278 | 25.18 | 92.2891 | 35.1091 | 33.1838 | 35.07 | 33.4331 | 33.2328 | 33.5113 | 34.9279 | 34.3603 | 34.1049 | 37.2058 | 36.2834 | 33.5098 | 34.4039 | 36.2721 | 36.5639 | 37.4979 | 36.2659 | 33.4237 | 32.8817 | 34.771 | 35.2033 | 33.4023 | 34.4295 | 34.3387 | 34.441 | 34.2851 | 34.3616 | 34.4245 | 34.0208 | 34.286 | 35.8591 | 35.2057 | 36.194 | 36.2094 | 33.6343 | 92.4833 | 92.7993 | 92.579
2022-09-08 03:01 | 5:11 | 25.6805 | 27.0593 | 28.8713 | 36.4584 | 34.3942 | 33.8527 | 34.7808 | 35.447 | 36.5589 | 37.3939 | 36.8292 | 37.9001 | 34.4234 | 34.4174 | 34.2074 | 35.0749 | 35.1805 | 35.7197 | 36.5102 | 36.7292 | 28.835 | 25.036 | 92.2804 | 35.163 | 33.1979 | 35.0624 | 33.4116 | 33.2406 | 33.4954 | 34.9306 | 34.3464 | 34.0922 | 37.2364 | 36.2731 | 33.5016 | 34.3924 | 36.2788 | 36.539 | 37.4939 | 36.2686 | 33.4138 | 32.8937 | 34.7905 | 35.2178 | 33.3933 | 34.4387 | 34.3405 | 34.4365 | 34.2716 | 34.3556 | 34.4136 | 34.0168 | 34.2851 | 35.8404 | 35.2086 | 36.1962 | 36.1954 | 33.6414 | 92.6295 | 92.9329 | 92.6861
2022-09-08 03:01 | 5:11 | 25.4084 | 26.76 | 28.6 | 36.4152 | 34.4051 | 33.8673 | 34.7685 | 35.434 | 36.5395 | 37.3763 | 36.8267 | 37.8912 | 34.4298 | 34.4225 | 34.2184 | 35.0769 | 35.1833 | 35.7208 | 36.5249 | 36.7246 | 28.6454 | 24.9026 | 92.3658 | 35.1318 | 33.206 | 35.0742 | 33.4238 | 33.2166 | 33.5094 | 34.8993 | 34.353 | 34.1217 | 37.2249 | 36.2725 | 33.5074 | 34.4176 | 36.2834 | 36.5665 | 37.4807 | 36.2604 | 33.4235 | 32.8908 | 34.7629 | 35.2114 | 33.4046 | 34.4251 | 34.3314 | 34.4279 | 34.2707 | 34.3568 | 34.4269 | 34.0278 | 34.2716 | 35.8555 | 35.2054 | 36.1883 | 36.2035 | 33.6363 | 92.8436 | 93.0763 | 92.787
2022-09-08 03:01 | 5:11 | 25.1782 | 26.5146 | 28.4269 | 36.3365 | 34.3891 | 33.8695 | 34.7596 | 35.4256 | 36.5506 | 37.4056 | 36.8303 | 37.8978 | 34.4169 | 34.3985 | 34.2112 | 35.0752 | 35.1652 | 35.7304 | 36.5361 | 36.6952 | 28.4874 | 24.7316 | 92.4523 | 35.1093 | 33.1979 | 35.0474 | 33.4211 | 33.225 | 33.5065 | 34.9117 | 34.3604 | 34.1188 | 37.2379 | 36.2667 | 33.5323 | 34.4011 | 36.2731 | 36.5677 | 37.5091 | 36.2721 | 33.4267 | 32.8892 | 34.775 | 35.2126 | 33.3954 | 34.4089 | 34.3627 | 34.437 | 34.2963 | 34.3491 | 34.4188 | 34.012 | 34.2707 | 35.8452 | 35.2171 | 36.2036 | 36.2181 | 33.6477 | 92.9682 | 93.1728 | 92.8365
2022-09-08 03:01 | 5:11 | 25.0647 | 26.2788 | 28.2156 | 36.3606 | 34.3939 | 33.8469 | 34.7645 | 35.4419 | 36.5434 | 37.3934 | 36.8306 | 37.9095 | 34.4185 | 34.4203 | 34.252 | 35.0883 | 35.1814 | 35.7111 | 36.5035 | 36.7211 | 28.2553 | 24.6255 | 92.4196 | 35.0786 | 33.1959 | 35.0593 | 33.4237 | 33.2433 | 33.5098 | 34.9117 | 34.3515 | 34.1167 | 37.2319 | 36.2601 | 33.5229 | 34.404 | 36.2725 | 36.5596 | 37.5046 | 36.2788 | 33.4315 | 32.8907 | 34.7536 | 35.2059 | 33.3898 | 34.423 | 34.3524 | 34.4252 | 34.2767 | 34.3578 | 34.4209 | 34.0277 | 34.2963 | 35.8386 | 35.2263 | 36.1949 | 36.2137 | 33.6409 | 93.1715 | 93.2979 | 92.9228
2022-09-08 03:01 | 5:11 | 24.8869 | 26.0242 | 28.0438 | 36.3308 | 34.4034 | 33.8607 | 34.7663 | 35.4322 | 36.5341 | 37.3923 | 36.835 | 37.8983 | 34.4361 | 34.409 | 34.2259 | 35.0635 | 35.1682 | 35.723 | 36.5036 | 36.7203 | 28.0701 | 24.4614 | 92.8233 | 35.0297 | 33.191 | 35.0714 | 33.4138 | 33.2317 | 33.5016 | 34.9142 | 34.3643 | 34.0926 | 37.2433 | 36.2689 | 33.5146 | 34.3917 | 36.2667 | 36.5462 | 37.5002 | 36.2834 | 33.426 | 32.8806 | 34.7683 | 35.2 | 33.3891 | 34.4268 | 34.339 | 34.4519 | 34.2881 | 34.3323 | 34.4249 | 34.0154 | 34.2767 | 35.8638 | 35.2137 | 36.1988 | 36.203 | 33.6249 | 93.3967 | 93.5829 | 93.1598
2022-09-08 03:02 | 5:11 | 24.7456 | 25.8271 | 27.8363 | 36.3184 | 34.3994 | 33.8636 | 34.7526 | 35.4334 | 36.5654 | 37.3927 | 36.8297 | 37.9082 | 34.4201 | 34.4133 | 34.2322 | 35.0765 | 35.1782 | 35.7284 | 36.5073 | 36.7272 | 27.8585 | 24.3179 | 92.9959 | 35.0126 | 33.2034 | 35.0521 | 33.4235 | 33.2266 | 33.5074 | 34.8989 | 34.3692 | 34.0941 | 37.2427 | 36.2836 | 33.5131 | 34.3938 | 36.2601 | 36.5646 | 37.4994 | 36.2731 | 33.4218 | 32.9022 | 34.7796 | 35.2114 | 33.3947 | 34.4294 | 34.3447 | 34.4396 | 34.2839 | 34.3552 | 34.4249 | 34.0296 | 34.2881 | 35.8526 | 35.1984 | 36.1983 | 36.1991 | 33.6299 | 93.6755 | 93.8569 | 93.2472
2022-09-08 03:02 | 5:12 | 24.4878 | 25.6277 | 27.6163 | 36.3047 | 34.3919 | 33.8593 | 34.7527 | 35.4376 | 36.5472 | 37.3827 | 36.8107 | 37.8907 | 34.4205 | 34.4091 | 34.2261 | 35.0712 | 35.1927 | 35.7266 | 36.5152 | 36.7202 | 27.6985 | 24.1798 | 93.1762 | 34.9663 | 33.1792 | 35.0741 | 33.4267 | 33.2101 | 33.5323 | 34.9123 | 34.3518 | 34.0921 | 37.2063 | 36.2839 | 33.5153 | 34.3998 | 36.2689 | 36.5675 | 37.5057 | 36.2725 | 33.4329 | 32.8723 | 34.7435 | 35.2138 | 33.3928 | 34.4154 | 34.3445 | 34.4511 | 34.2905 | 34.3319 | 34.4237 | 34.0117 | 34.2839 | 35.8536 | 35.2035 | 36.1905 | 36.2202 | 33.6485 | 93.8935 | 94.1293 | 93.4214
2022-09-08 03:02 | 5:12 | 24.3774 | 25.4358 | 27.4636 | 36.1317 | 34.3947 | 33.8414 | 34.7627 | 35.4285 | 36.5553 | 37.3753 | 36.8235 | 37.8937 | 34.4312 | 34.4104 | 34.2372 | 35.0493 | 35.1994 | 35.7107 | 36.5107 | 36.7102 | 27.474 | 24.0146 | 93.3905 | 34.9853 | 33.1986 | 35.0738 | 33.4315 | 33.2203 | 33.5229 | 34.9177 | 34.3531 | 34.1004 | 37.2307 | 36.2829 | 33.5015 | 34.397 | 36.2836 | 36.5628 | 37.5059 | 36.2667 | 33.4262 | 32.9064 | 34.7735 | 35.1901 | 33.3935 | 34.4115 | 34.3313 | 34.4442 | 34.2812 | 34.3425 | 34.412 | 34.0291 | 34.2905 | 35.8453 | 35.1982 | 36.197 | 36.2178 | 33.6229 | 94.1436 | 94.4156 | 93.6633
2022-09-08 03:02 | 5:12 | 24.1171 | 25.1947 | 27.2546 | 36.2394 | 34.4015 | 33.8438 | 34.75 | 35.4201 | 36.5609 | 37.3935 | 36.8289 | 37.9273 | 34.4222 | 34.409 | 34.2297 | 35.0781 | 35.1594 | 35.719 | 36.5121 | 36.7006 | 27.1905 | 23.8883 | 93.4549 | 34.8704 | 33.1914 | 35.0688 | 33.426 | 33.2072 | 33.5146 | 34.9155 | 34.3526 | 34.0996 | 37.2052 | 36.2886 | 33.5104 | 34.4002 | 36.2839 | 36.5657 | 37.5112 | 36.2601 | 33.4144 | 32.8815 | 34.7628 | 35.2213 | 33.396 | 34.4068 | 34.3636 | 34.4433 | 34.2769 | 34.3407 | 34.4337 | 34.0294 | 34.2812 | 35.8713 | 35.1987 | 36.2078 | 36.215 | 33.6525 | 94.3424 | 94.6469 | 93.7281
2022-09-08 03:02 | 5:12 | 23.9548 | 24.993 | 27.06 | 36.1903 | 34.3819 | 33.8455 | 34.7539 | 35.4148 | 36.549 | 37.3933 | 36.8431 | 37.8873 | 34.4228 | 34.4054 | 34.2296 | 35.0699 | 35.1992 | 35.7267 | 36.4916 | 36.6907 | 26.9394 | 23.7122 | 93.6136 | 34.8813 | 33.2006 | 35.0648 | 33.4218 | 33.2074 | 33.5131 | 34.9028 | 34.3374 | 34.124 | 37.2329 | 36.2776 | 33.4945 | 34.3809 | 36.2829 | 36.5566 | 37.4972 | 36.2689 | 33.4212 | 32.8846 | 34.7467 | 35.1797 | 33.4049 | 34.425 | 34.3523 | 34.4596 | 34.2715 | 34.3325 | 34.4367 | 34.0424 | 34.2769 | 35.844 | 35.2157 | 36.2088 | 36.2174 | 33.632 | 94.5748 | 94.8619 | 93.9631
2022-09-08 03:02 | 5:12 | 23.7578 | 24.7854 | 26.9061 | 36.2149 | 34.3962 | 33.8423 | 34.7635 | 35.4169 | 36.5442 | 37.3808 | 36.8111 | 37.913 | 34.4155 | 34.3984 | 34.23 | 35.0562 | 35.1835 | 35.6988 | 36.4963 | 36.6968 | 26.7026 | 23.5311 | 93.8045 | 34.9391 | 33.2021 | 35.0674 | 33.4329 | 33.2298 | 33.5153 | 34.9096 | 34.3353 | 34.1084 | 37.2249 | 36.2858 | 33.5026 | 34.3739 | 36.2886 | 36.5568 | 37.4955 | 36.2836 | 33.4191 | 32.8896 | 34.7369 | 35.2033 | 33.4071 | 34.4166 | 34.3511 | 34.4457 | 34.2877 | 34.334 | 34.4328 | 34.0361 | 34.2715 | 35.8465 | 35.1999 | 36.2061 | 36.1909 | 33.6258 | 94.8024 | 95.0797 | 94.0341
2022-09-08 03:03 | 5:13 | 23.6894 | 24.6878 | 26.7945 | 36.0877 | 34.4025 | 33.8355 | 34.7472 | 35.4203 | 36.541 | 37.3923 | 36.8057 | 37.8968 | 34.4156 | 34.4037 | 34.2391 | 35.084 | 35.2002 | 35.7072 | 36.483 | 36.7077 | 26.4429 | 23.3989 | 93.9601 | 34.8898 | 33.1923 | 35.0687 | 33.4262 | 33.224 | 33.5015 | 34.9054 | 34.3494 | 34.1113 | 37.2291 | 36.2912 | 33.5176 | 34.3826 | 36.2776 | 36.5585 | 37.4936 | 36.2839 | 33.4218 | 32.9029 | 34.7538 | 35.1944 | 33.4013 | 34.4046 | 34.3342 | 34.4453 | 34.2848 | 34.3285 | 34.4064 | 34.0253 | 34.2877 | 35.8352 | 35.2013 | 36.1883 | 36.1989 | 33.6247 | 94.8375 | 95.2461 | 94.118
2022-09-08 03:03 | 5:13 | 23.5664 | 24.475 | 26.6629 | 36.214 | 34.4213 | 33.8496 | 34.7308 | 35.429 | 36.5393 | 37.3798 | 36.837 | 37.9035 | 34.4286 | 34.4099 | 34.2373 | 35.0795 | 35.1919 | 35.6763 | 36.4778 | 36.7061 | 26.2016 | 23.2758 | 94.0714 | 34.729 | 33.1946 | 35.056 | 33.4144 | 33.2224 | 33.5104 | 34.9104 | 34.3436 | 34.0992 | 37.2276 | 36.2911 | 33.4993 | 34.3777 | 36.2858 | 36.5489 | 37.4705 | 36.2829 | 33.4285 | 32.901 | 34.7308 | 35.1912 | 33.4091 | 34.3969 | 34.3608 | 34.4519 | 34.2906 | 34.3383 | 34.4295 | 34.0245 | 34.2848 | 35.8459 | 35.2026 | 36.215 | 36.2232 | 33.6297 | 94.8923 | 95.3549 | 94.1362
2022-09-08 03:03 | 5:13 | 23.3011 | 24.2106 | 26.4341 | 36.1316 | 34.4119 | 33.8373 | 34.7396 | 35.4326 | 36.5681 | 37.3711 | 36.8136 | 37.8843 | 34.4215 | 34.4007 | 34.2337 | 35.0768 | 35.1906 | 35.6963 | 36.4806 | 36.6807 | 25.8695 | 23.0185 | 94.1475 | 34.7725 | 33.1923 | 35.0762 | 33.4212 | 33.22 | 33.4945 | 34.9034 | 34.3542 | 34.0937 | 37.2175 | 36.2825 | 33.4937 | 34.3871 | 36.2912 | 36.5787 | 37.5049 | 36.2886 | 33.4172 | 32.8565 | 34.7326 | 35.1801 | 33.3916 | 34.3927 | 34.3525 | 34.4597 | 34.2847 | 34.3337 | 34.4129 | 34.0214 | 34.2906 | 35.8569 | 35.2068 | 36.1997 | 36.2041 | 33.6135 | 94.9915 | 95.4769 | 94.3227
2022-09-08 03:03 | 5:13 | 23.1906 | 24.1212 | 26.3599 | 36.0598 | 34.4074 | 33.8389 | 34.7416 | 35.4132 | 36.5509 | 37.3715 | 36.8125 | 37.8966 | 34.4055 | 34.3993 | 34.2188 | 35.0587 | 35.1864 | 35.6937 | 36.5046 | 36.7047 | 25.6121 | 22.8616 | 94.1354 | 34.8421 | 33.1754 | 35.0547 | 33.4191 | 33.2183 | 33.5026 | 34.9018 | 34.3225 | 34.0923 | 37.2142 | 36.3096 | 33.4949 | 34.3897 | 36.2911 | 36.5575 | 37.4925 | 36.2776 | 33.4375 | 32.8865 | 34.7228 | 35.1887 | 33.3833 | 34.3927 | 34.3616 | 34.4354 | 34.2827 | 34.323 | 34.4178 | 34.0474 | 34.2847 | 35.8631 | 35.2031 | 36.2028 | 36.1966 | 33.6215 | 95.0878 | 95.5303 | 94.3731
2022-09-08 03:03 | 5:13 | 23.0094 | 23.8932 | 26.188 | 35.9198 | 34.4132 | 33.8303 | 34.743 | 35.4305 | 36.5409 | 37.3533 | 36.8309 | 37.8881 | 34.4186 | 34.4127 | 34.2285 | 35.0765 | 35.2011 | 35.6798 | 36.4652 | 36.7081 | 25.3323 | 22.7215 | 94.156 | 34.7157 | 33.1847 | 35.0845 | 33.4218 | 33.2066 | 33.5176 | 34.909 | 34.3345 | 34.102 | 37.2385 | 36.2929 | 33.4995 | 34.3861 | 36.2825 | 36.5436 | 37.5027 | 36.2858 | 33.4289 | 32.8813 | 34.742 | 35.1671 | 33.3739 | 34.3944 | 34.3556 | 34.465 | 34.2799 | 34.3129 | 34.4223 | 34.0319 | 34.2827 | 35.8325 | 35.2092 | 36.2165 | 36.1963 | 33.6193 | 95.1435 | 95.5748 | 94.3815
2022-09-08 03:03 | 5:13 | 22.8799 | 23.7734 | 26.1231 | 35.9816 | 34.4166 | 33.8212 | 34.7405 | 35.4314 | 36.5585 | 37.3715 | 36.8197 | 37.8843 | 34.4088 | 34.3996 | 34.2108 | 35.0862 | 35.1866 | 35.6825 | 36.4695 | 36.6947 | 25.1346 | 22.565 | 94.1944 | 34.7099 | 33.1749 | 35.0664 | 33.4285 | 33.1975 | 33.4993 | 34.9003 | 34.3356 | 34.0943 | 37.2261 | 36.2969 | 33.4793 | 34.3978 | 36.3096 | 36.5524 | 37.4883 | 36.2912 | 33.4175 | 32.8651 | 34.718 | 35.1833 | 33.3781 | 34.4015 | 34.3518 | 34.4532 | 34.2827 | 34.3253 | 34.4268 | 34.0271 | 34.2799 | 35.8496 | 35.2083 | 36.2045 | 36.2031 | 33.6209 | 95.0856 | 95.553 | 94.3385
2022-09-08 03:04 | 5:13 | 22.6841 | 23.5674 | 25.8918 | 35.9516 | 34.4133 | 33.8232 | 34.7399 | 35.4184 | 36.548 | 37.3839 | 36.8265 | 37.8872 | 34.4159 | 34.3892 | 34.237 | 35.0619 | 35.1682 | 35.688 | 36.4673 | 36.6971 | 24.8556 | 22.3752 | 94.0554 | 34.7055 | 33.1858 | 35.0689 | 33.4172 | 33.1932 | 33.4937 | 34.894 | 34.3474 | 34.1021 | 37.2292 | 36.2911 | 33.4859 | 34.3955 | 36.2929 | 36.5658 | 37.4712 | 36.2911 | 33.4451 | 32.8807 | 34.6992 | 35.1694 | 33.3758 | 34.3947 | 34.3473 | 34.4507 | 34.2812 | 34.3222 | 34.4336 | 34.0301 | 34.2827 | 35.8326 | 35.2149 | 36.2094 | 36.1955 | 33.6084 | 94.8493 | 95.3613 | 94.1274
2022-09-08 03:04 | 5:14 | 22.5549 | 23.4044 | 25.7229 | 35.9762 | 34.421 | 33.8466 | 34.74 | 35.4134 | 36.531 | 37.3501 | 36.8021 | 37.897 | 34.4246 | 34.4122 | 34.2104 | 35.076 | 35.1795 | 35.6737 | 36.4563 | 36.6915 | 24.5613 | 22.1742 | 93.9312 | 34.6 | 33.1673 | 35.0751 | 33.4375 | 33.2069 | 33.4949 | 34.8887 | 34.3451 | 34.1104 | 37.2078 | 36.2862 | 33.5076 | 34.3821 | 36.2969 | 36.5444 | 37.4817 | 36.2825 | 33.4441 | 32.8858 | 34.7021 | 35.1677 | 33.3733 | 34.4125 | 34.3631 | 34.458 | 34.2935 | 34.3077 | 34.4344 | 34.0194 | 34.2812 | 35.8322 | 35.1831 | 36.2029 | 36.1996 | 33.6104 | 94.6605 | 95.1079 | 93.9224
2022-09-08 03:04 | 5:14 | 22.3434 | 23.2244 | 25.654 | 35.9136 | 34.4104 | 33.837 | 34.7349 | 35.4375 | 36.5489 | 37.3515 | 36.8273 | 37.8807 | 34.4184 | 34.3923 | 34.2245 | 35.0635 | 35.1771 | 35.6508 | 36.4477 | 36.68 | 24.295 | 21.9767 | 93.7537 | 34.6051 | 33.1724 | 35.0677 | 33.4289 | 33.2005 | 33.4995 | 34.889 | 34.3493 | 34.0948 | 37.2254 | 36.3036 | 33.5105 | 34.3905 | 36.2911 | 36.5418 | 37.4933 | 36.3096 | 33.4382 | 32.8796 | 34.7023 | 35.1718 | 33.374 | 34.4137 | 34.3588 | 34.4474 | 34.3064 | 34.3097 | 34.4054 | 34.0215 | 34.2935 | 35.8357 | 35.2009 | 36.2227 | 36.2061 | 33.6136 | 94.3764 | 94.8253 | 93.7503
2022-09-08 03:04 | 5:14 | 22.2457 | 23.1216 | 25.5824 | 35.8856 | 34.4134 | 33.8308 | 34.7203 | 35.4147 | 36.5332 | 37.3453 | 36.8141 | 37.8946 | 34.4199 | 34.401 | 34.2152 | 35.0816 | 35.1977 | 35.6545 | 36.4747 | 36.6886 | 24.0591 | 21.8107 | 93.7616 | 34.5385 | 33.1802 | 35.0854 | 33.4175 | 33.1992 | 33.4793 | 34.8852 | 34.3354 | 34.0727 | 37.2238 | 36.313 | 33.4772 | 34.3778 | 36.2862 | 36.5515 | 37.4974 | 36.2929 | 33.4185 | 32.8624 | 34.6887 | 35.1368 | 33.3753 | 34.3845 | 34.3765 | 34.4783 | 34.2832 | 34.2916 | 34.42 | 34.0263 | 34.3064 | 35.8234 | 35.211 | 36.1867 | 36.2234 | 33.5797 | 94.3028 | 94.6817 | 93.7947
2022-09-08 03:04 | 5:14 | 22.0157 | 22.8799 | 25.3157 | 35.926 | 34.4025 | 33.8494 | 34.7289 | 35.4037 | 36.5348 | 37.3434 | 36.8194 | 37.8957 | 34.4174 | 34.3783 | 34.2292 | 35.0525 | 35.1816 | 35.654 | 36.4278 | 36.6751 | 23.8527 | 21.6122 | 93.8141 | 34.521 | 33.171 | 35.0711 | 33.4451 | 33.1938 | 33.4859 | 34.8848 | 34.3405 | 34.109 | 37.2155 | 36.3056 | 33.4863 | 34.3851 | 36.3036 | 36.5459 | 37.4691 | 36.2969 | 33.4442 | 32.8599 | 34.7 | 35.1512 | 33.3495 | 34.4024 | 34.3375 | 34.469 | 34.3067 | 34.3064 | 34.4248 | 34.0055 | 34.2832 | 35.8192 | 35.2058 | 36.1945 | 36.1876 | 33.5933 | 94.2286 | 94.5175 | 93.7348
2022-09-08 03:04 | 5:14 | 21.8541 | 22.6673 | 25.1295 | 35.9252 | 34.4135 | 33.8354 | 34.7205 | 35.4083 | 36.5385 | 37.3561 | 36.8096 | 37.8899 | 34.4156 | 34.3928 | 34.2065 | 35.0484 | 35.1846 | 35.6671 | 36.4155 | 36.6657 | 23.6569 | 21.4287 | 93.6526 | 34.459 | 33.1569 | 35.0924 | 33.4441 | 33.1891 | 33.5076 | 34.8864 | 34.3407 | 34.0989 | 37.2135 | 36.2923 | 33.4796 | 34.3915 | 36.313 | 36.5443 | 37.4865 | 36.2911 | 33.4213 | 32.8646 | 34.6698 | 35.1371 | 33.3558 | 34.391 | 34.3617 | 34.4585 | 34.304 | 34.3171 | 34.4016 | 34.0093 | 34.3067 | 35.818 | 35.1985 | 36.1971 | 36.1955 | 33.5778 | 94.1096 | 94.4168 | 93.6193
2022-09-08 03:05 | 5:15 | 21.7307 | 22.551 | 24.9822 | 35.8711 | 34.4239 | 33.8284 | 34.7224 | 35.4066 | 36.5437 | 37.3419 | 36.8029 | 37.8938 | 34.4161 | 34.3933 | 34.2082 | 35.0604 | 35.1911 | 35.6749 | 36.4335 | 36.6539 | 23.5025 | 21.2386 | 93.6327 | 34.3253 | 33.1785 | 35.0768 | 33.4382 | 33.1856 | 33.5105 | 34.8859 | 34.3478 | 34.1022 | 37.2118 | 36.305 | 33.4875 | 34.3972 | 36.3056 | 36.5445 | 37.4786 | 36.2862 | 33.4254 | 32.8537 | 34.6844 | 35.1528 | 33.3478 | 34.3988 | 34.362 | 34.4428 | 34.3165 | 34.304 | 34.4262 | 34.0383 | 34.304 | 35.8209 | 35.2043 | 36.2032 | 36.1873 | 33.575 | 93.9651 | 94.3129 | 93.5956
2022-09-08 03:05 | 5:15 | 21.5623 | 22.3921 | 24.8451 | 35.7309 | 34.4111 | 33.8436 | 34.7373 | 35.4131 | 36.5521 | 37.3377 | 36.8231 | 37.888 | 34.3989 | 34.3804 | 34.201 | 35.0687 | 35.1872 | 35.6734 | 36.4273 | 36.6844 | 23.3403 | 21.0977 | 93.6324 | 34.4216 | 33.1642 | 35.0956 | 33.4185 | 33.2087 | 33.4772 | 34.8819 | 34.3437 | 34.1104 | 37.2228 | 36.3089 | 33.5098 | 34.3892 | 36.2923 | 36.5405 | 37.4819 | 36.3036 | 33.4476 | 32.8583 | 34.6802 | 35.1576 | 33.3601 | 34.4069 | 34.3398 | 34.4408 | 34.296 | 34.3302 | 34.4062 | 34.0071 | 34.3165 | 35.8359 | 35.1925 | 36.1842 | 36.1953 | 33.5748 | 93.9303 | 94.236 | 93.5557
2022-09-08 03:05 | 5:15 | 21.4525 | 22.2415 | 24.7136 | 35.7614 | 34.4036 | 33.8327 | 34.7152 | 35.4109 | 36.5406 | 37.3494 | 36.8229 | 37.8748 | 34.4235 | 34.4116 | 34.2025 | 35.0823 | 35.1922 | 35.6592 | 36.4255 | 36.6701 | 23.1997 | 20.9046 | 93.5361 | 34.4205 | 33.1492 | 35.0963 | 33.4442 | 33.1853 | 33.4863 | 34.8662 | 34.3589 | 34.1021 | 37.2156 | 36.3167 | 33.4879 | 34.4028 | 36.305 | 36.5334 | 37.4902 | 36.313 | 33.4568 | 32.8295 | 34.6692 | 35.142 | 33.334 | 34.3873 | 34.3747 | 34.4549 | 34.2982 | 34.3257 | 34.4174 | 34.0083 | 34.296 | 35.8266 | 35.2219 | 36.1984 | 36.1925 | 33.5769 | 93.8756 | 94.1601 | 93.5316
2022-09-08 03:05 | 5:15 | 21.2795 | 22.0625 | 24.4772 | 35.7714 | 34.4305 | 33.8293 | 34.716 | 35.4126 | 36.5433 | 37.3325 | 36.8197 | 37.8803 | 34.3951 | 34.3854 | 34.2028 | 35.0677 | 35.1965 | 35.6703 | 36.4232 | 36.6694 | 23.0944 | 20.7452 | 93.5768 | 34.3669 | 33.1646 | 35.0858 | 33.4213 | 33.184 | 33.4796 | 34.8709 | 34.3394 | 34.1129 | 37.2097 | 36.3066 | 33.4944 | 34.3924 | 36.3089 | 36.5585 | 37.4794 | 36.3056 | 33.4557 | 32.8522 | 34.6715 | 35.1282 | 33.3499 | 34.3816 | 34.3511 | 34.4617 | 34.3148 | 34.3133 | 34.4225 | 34.0082 | 34.2982 | 35.8221 | 35.2118 | 36.2076 | 36.1908 | 33.5778 | 93.8166 | 94.1121 | 93.5135
2022-09-08 03:05 | 5:15 | 21.113 | 21.9295 | 24.3743 | 35.6404 | 34.4159 | 33.8476 | 34.7248 | 35.4193 | 36.5284 | 37.3404 | 36.8271 | 37.8869 | 34.4199 | 34.4085 | 34.2301 | 35.0694 | 35.1831 | 35.6656 | 36.4207 | 36.6725 | 22.9665 | 20.5382 | 93.5081 | 34.3484 | 33.1582 | 35.1023 | 33.4254 | 33.1799 | 33.4875 | 34.873 | 34.3561 | 34.102 | 37.2166 | 36.3106 | 33.4858 | 34.3682 | 36.3167 | 36.5273 | 37.4746 | 36.2923 | 33.4595 | 32.8195 | 34.6691 | 35.1412 | 33.3388 | 34.398 | 34.3657 | 34.4611 | 34.2949 | 34.3169 | 34.3985 | 34.0191 | 34.3148 | 35.8241 | 35.2053 | 36.1987 | 36.1862 | 33.5552 | 93.7625 | 94.0333 | 93.3945
2022-09-08 03:05 | 5:15 | 21.0053 | 21.8074 | 24.2574 | 35.6467 | 34.4245 | 33.8547 | 34.736 | 35.4072 | 36.5542 | 37.3355 | 36.821 | 37.889 | 34.4204 | 34.3962 | 34.2221 | 35.0904 | 35.2007 | 35.6543 | 36.4113 | 36.6552 | 22.8261 | 20.4035 | 93.5083 | 34.3389 | 33.1576 | 35.0929 | 33.4476 | 33.1681 | 33.5098 | 34.8635 | 34.3671 | 34.0987 | 37.226 | 36.3202 | 33.4823 | 34.3867 | 36.3066 | 36.5464 | 37.4927 | 36.305 | 33.4493 | 32.8356 | 34.6553 | 35.1334 | 33.3427 | 34.3923 | 34.3894 | 34.4674 | 34.3084 | 34.2931 | 34.4203 | 34.0255 | 34.2949 | 35.8143 | 35.1961 | 36.2118 | 36.1858 | 33.5661 | 93.7161 | 93.9985 | 93.4623
2022-09-08 03:06 | 5:15 | 20.9443 | 21.6701 | 24.1448 | 35.5835 | 34.4136 | 33.8541 | 34.7212 | 35.4102 | 36.5564 | 37.3249 | 36.8164 | 37.8986 | 34.3865 | 34.3828 | 34.2018 | 35.0816 | 35.1945 | 35.6382 | 36.4148 | 36.6383 | 22.7401 | 20.2672 | 93.4806 | 34.2748 | 33.1594 | 35.1133 | 33.4568 | 33.173 | 33.4879 | 34.8608 | 34.3553 | 34.1057 | 37.2254 | 36.3171 | 33.5036 | 34.3777 | 36.3106 | 36.5359 | 37.4693 | 36.3089 | 33.4562 | 32.8338 | 34.6652 | 35.1281 | 33.3155 | 34.3978 | 34.3594 | 34.4669 | 34.2919 | 34.3144 | 34.409 | 34.0204 | 34.3084 | 35.8111 | 35.2107 | 36.196 | 36.1803 | 33.5884 | 93.6818 | 93.926 | 93.374
2022-09-08 03:06 | 5:16 | 20.7686 | 21.4808 | 24.003 | 35.6359 | 34.4269 | 33.8577 | 34.729 | 35.4234 | 36.5387 | 37.3381 | 36.8466 | 37.9079 | 34.415 | 34.371 | 34.2054 | 35.0786 | 35.1959 | 35.6472 | 36.4053 | 36.6512 | 22.6527 | 20.1597 | 93.4321 | 34.1335 | 33.145 | 35.0847 | 33.4557 | 33.17 | 33.4944 | 34.86 | 34.3654 | 34.0903 | 37.2235 | 36.3208 | 33.4961 | 34.3961 | 36.3202 | 36.5555 | 37.4702 | 36.3167 | 33.4521 | 32.8289 | 34.6532 | 35.133 | 33.3274 | 34.3691 | 34.3858 | 34.4645 | 34.3071 | 34.304 | 34.4133 | 34.0338 | 34.2919 | 35.8272 | 35.2017 | 36.2053 | 36.1908 | 33.5693 | 93.6153 | 93.8511 | 93.3483
2022-09-08 03:06 | 5:16 | 20.8103 | 21.3821 | 23.8912 | 35.574 | 34.4188 | 33.8423 | 34.7231 | 35.423 | 36.5371 | 37.331 | 36.832 | 37.8991 | 34.4065 | 34.3776 | 34.214 | 35.0905 | 35.2102 | 35.66 | 36.3882 | 36.6553 | 22.5719 | 20.012 | 93.4472 | 34.2203 | 33.1548 | 35.0988 | 33.4595 | 33.1668 | 33.4858 | 34.8583 | 34.3432 | 34.0956 | 37.2184 | 36.3388 | 33.4981 | 34.3988 | 36.3171 | 36.543 | 37.4693 | 36.3066 | 33.4692 | 32.8279 | 34.6546 | 35.115 | 33.3254 | 34.3905 | 34.3832 | 34.4557 | 34.3096 | 34.3186 | 34.4091 | 34.0271 | 34.3071 | 35.8246 | 35.1829 | 36.2144 | 36.1792 | 33.5853 | 93.5473 | 93.8083 | 93.3379
2022-09-08 03:06 | 5:16 | 20.4894 | 21.2116 | 23.7901 | 35.6212 | 34.4209 | 33.8471 | 34.7071 | 35.4182 | 36.5436 | 37.3196 | 36.8341 | 37.9047 | 34.3895 | 34.3658 | 34.2283 | 35.0886 | 35.2174 | 35.6618 | 36.4074 | 36.6605 | 22.488 | 19.9087 | 93.3252 | 34.1565 | 33.1742 | 35.0964 | 33.4493 | 33.1487 | 33.4823 | 34.8739 | 34.3473 | 34.0949 | 37.2302 | 36.3171 | 33.4907 | 34.41 | 36.3208 | 36.5552 | 37.4529 | 36.3106 | 33.4493 | 32.814 | 34.6307 | 35.1205 | 33.3463 | 34.3845 | 34.4034 | 34.453 | 34.3162 | 34.3119 | 34.4104 | 34.0172 | 34.3096 | 35.8232 | 35.201 | 36.2013 | 36.193 | 33.5591 | 93.518 | 93.7395 | 93.3188
2022-09-08 03:06 | 5:16 | 20.5248 | 21.1854 | 23.7409 | 35.4934 | 34.4249 | 33.858 | 34.7076 | 35.4143 | 36.5538 | 37.3237 | 36.8378 | 37.8988 | 34.3977 | 34.3654 | 34.2194 | 35.0814 | 35.1983 | 35.6562 | 36.416 | 36.6549 | 22.4478 | 19.8201 | 93.3664 | 34.1593 | 33.1481 | 35.097 | 33.4562 | 33.1718 | 33.5036 | 34.8496 | 34.3561 | 34.1047 | 37.2233 | 36.315 | 33.4917 | 34.3954 | 36.3388 | 36.5661 | 37.4647 | 36.3202 | 33.4484 | 32.8267 | 34.6371 | 35.1155 | 33.3092 | 34.3658 | 34.3836 | 34.4808 | 34.321 | 34.3025 | 34.409 | 34.0152 | 34.3162 | 35.8206 | 35.2121 | 36.202 | 36.1886 | 33.5707 | 93.4241 | 93.6538 | 93.2844
2022-09-08 03:06 | 5:16 | 20.3417 | 21.0119 | 23.6375 | 35.546 | 34.4249 | 33.8481 | 34.7057 | 35.4244 | 36.5713 | 37.3353 | 36.8496 | 37.9206 | 34.3806 | 34.3778 | 34.2069 | 35.0969 | 35.2 | 35.646 | 36.3937 | 36.658 | 22.4257 | 19.6731 | 93.2613 | 34.1282 | 33.1665 | 35.0885 | 33.4521 | 33.1663 | 33.4961 | 34.8637 | 34.3507 | 34.1225 | 37.2329 | 36.3068 | 33.4708 | 34.4035 | 36.3171 | 36.5707 | 37.473 | 36.3171 | 33.4426 | 32.8274 | 34.6423 | 35.1156 | 33.3041 | 34.3918 | 34.392 | 34.4654 | 34.3144 | 34.3256 | 34.4054 | 34.0005 | 34.321 | 35.8177 | 35.1951 | 36.2081 | 36.2141 | 33.5695 | 93.3239 | 93.5662 | 93.2047
2022-09-08 03:07 | 5:17 | 20.1692 | 20.8679 | 23.5117 | 35.5749 | 34.4237 | 33.8563 | 34.6981 | 35.4317 | 36.553 | 37.3146 | 36.8329 | 37.913 | 34.3956 | 34.3642 | 34.2163 | 35.0988 | 35.1983 | 35.6396 | 36.3924 | 36.6525 | 22.3657 | 19.5963 | 93.2875 | 34.0454 | 33.1763 | 35.1102 | 33.4692 | 33.1716 | 33.4981 | 34.8542 | 34.365 | 34.1025 | 37.23 | 36.306 | 33.4931 | 34.4141 | 36.315 | 36.5668 | 37.4769 | 36.3208 | 33.4599 | 32.8152 | 34.6371 | 35.1177 | 33.3128 | 34.3617 | 34.3863 | 34.4572 | 34.318 | 34.308 | 34.3984 | 34.013 | 34.3144 | 35.8348 | 35.2098 | 36.211 | 36.2044 | 33.5594 | 93.2615 | 93.4862 | 93.1792
2022-09-08 03:07 | 5:17 | 20.0795 | 20.7579 | 23.387 | 35.4484 | 34.412 | 33.8618 | 34.7118 | 35.4166 | 36.5388 | 37.3465 | 36.8648 | 37.9006 | 34.3714 | 34.359 | 34.1949 | 35.0859 | 35.2187 | 35.6713 | 36.3862 | 36.6642 | 22.3105 | 19.4607 | 93.2295 | 34.0783 | 33.1531 | 35.1207 | 33.4493 | 33.1453 | 33.4907 | 34.8511 | 34.3617 | 34.1338 | 37.2244 | 36.3208 | 33.5035 | 34.4172 | 36.3068 | 36.5625 | 37.4742 | 36.3388 | 33.4549 | 32.8189 | 34.6363 | 35.1356 | 33.3116 | 34.3536 | 34.3792 | 34.4861 | 34.3345 | 34.3271 | 34.4037 | 34.0178 | 34.318 | 35.8218 | 35.2104 | 36.2147 | 36.1852 | 33.5721 | 93.2185 | 93.3996 | 93.215
2022-09-08 03:07 | 5:17 | 19.9494 | 20.6472 | 23.1882 | 35.5184 | 34.4337 | 33.8464 | 34.7174 | 35.4068 | 36.5469 | 37.3268 | 36.858 | 37.9175 | 34.3959 | 34.3712 | 34.2157 | 35.0938 | 35.1982 | 35.6512 | 36.3998 | 36.655 | 22.2597 | 19.3994 | 93.0907 | 33.947 | 33.147 | 35.0981 | 33.4484 | 33.1521 | 33.4917 | 34.8404 | 34.3543 | 34.1232 | 37.2487 | 36.324 | 33.4784 | 34.4025 | 36.306 | 36.5466 | 37.4807 | 36.3171 | 33.4646 | 32.8282 | 34.6364 | 35.1422 | 33.3098 | 34.3628 | 34.3816 | 34.4672 | 34.3127 | 34.3227 | 34.4099 | 34.0006 | 34.3345 | 35.837 | 35.2116 | 36.211 | 36.1994 | 33.5733 | 93.1211 | 93.3262 | 93.0338
2022-09-08 03:07 | 5:17 | 19.8683 | 20.5493 | 23.1909 | 35.4595 | 34.4367 | 33.8715 | 34.6991 | 35.4249 | 36.5533 | 37.3203 | 36.852 | 37.9031 | 34.3591 | 34.3432 | 34.2269 | 35.0827 | 35.2061 | 35.6479 | 36.4019 | 36.6408 | 22.2177 | 19.2797 | 93.0826 | 34.0385 | 33.1562 | 35.1057 | 33.4426 | 33.1576 | 33.4708 | 34.8477 | 34.3675 | 34.1118 | 37.23 | 36.3169 | 33.4862 | 34.4209 | 36.3208 | 36.5539 | 37.4699 | 36.315 | 33.4539 | 32.8324 | 34.633 | 35.1152 | 33.2995 | 34.3686 | 34.4022 | 34.4714 | 34.3299 | 34.3273 | 34.4007 | 34.0105 | 34.3127 | 35.8355 | 35.2045 | 36.2156 | 36.1816 | 33.585 | 93.0479 | 93.2235 | 93.004
2022-09-08 03:07 | 5:17 | 19.8549 | 20.472 | 23.0547 | 35.3217 | 34.4328 | 33.8538 | 34.7051 | 35.4352 | 36.5671 | 37.3378 | 36.8456 | 37.9213 | 34.3593 | 34.3388 | 34.2162 | 35.0977 | 35.2142 | 35.6587 | 36.3959 | 36.6557 | 22.178 | 19.1739 | 92.9405 | 33.9994 | 33.1534 | 35.1014 | 33.4599 | 33.1579 | 33.4931 | 34.8358 | 34.3696 | 34.1286 | 37.2409 | 36.332 | 33.4944 | 34.427 | 36.324 | 36.5632 | 37.453 | 36.3068 | 33.4608 | 32.8032 | 34.6321 | 35.13 | 33.2893 | 34.3774 | 34.418 | 34.4702 | 34.3448 | 34.3233 | 34.3993 | 34.0336 | 34.3299 | 35.8288 | 35.2149 | 36.2317 | 36.1909 | 33.5937 | 92.9325 | 93.1058 | 92.8897
2022-09-08 03:07 | 5:17 | 19.6893 | 20.3567 | 22.9469 | 35.2497 | 34.4064 | 33.8453 | 34.7127 | 35.4305 | 36.5651 | 37.3406 | 36.8413 | 37.923 | 34.3825 | 34.3559 | 34.2181 | 35.082 | 35.22 | 35.6435 | 36.3961 | 36.6698 | 22.1401 | 19.1067 | 92.8254 | 33.8952 | 33.1278 | 35.123 | 33.4549 | 33.1606 | 33.5035 | 34.864 | 34.3645 | 34.128 | 37.2546 | 36.3215 | 33.483 | 34.3983 | 36.3169 | 36.5583 | 37.4864 | 36.306 | 33.4703 | 32.8106 | 34.6328 | 35.114 | 33.2977 | 34.3532 | 34.3974 | 34.468 | 34.3212 | 34.3017 | 34.4127 | 34.0334 | 34.3448 | 35.8535 | 35.2185 | 36.2156 | 36.2039 | 33.5857 | 92.7924 | 92.9818 | 92.7359
2022-09-08 03:08 | 5:17 | 19.6237 | 20.2854 | 22.863 | 35.4126 | 34.4295 | 33.8805 | 34.6993 | 35.4322 | 36.569 | 37.3203 | 36.8588 | 37.9198 | 34.3662 | 34.3475 | 34.2216 | 35.092 | 35.2254 | 35.6478 | 36.391 | 36.6674 | 22.112 | 19.0333 | 92.7826 | 34.0031 | 33.1465 | 35.1167 | 33.4646 | 33.1566 | 33.4784 | 34.8449 | 34.37 | 34.1123 | 37.2592 | 36.3087 | 33.4843 | 34.3993 | 36.332 | 36.5312 | 37.474 | 36.3208 | 33.4584 | 32.8084 | 34.6292 | 35.1202 | 33.2788 | 34.3604 | 34.3967 | 34.4695 | 34.3263 | 34.3313 | 34.3996 | 34.0198 | 34.3212 | 35.8507 | 35.2124 | 36.2067 | 36.2026 | 33.5982 | 92.703 | 92.8709 | 92.7209
2022-09-08 03:08 | 5:18 | 19.543 | 20.1623 | 22.7449 | 35.2627 | 34.4129 | 33.851 | 34.7099 | 35.4309 | 36.5669 | 37.3193 | 36.8543 | 37.9138 | 34.3616 | 34.3447 | 34.226 | 35.1133 | 35.2333 | 35.6499 | 36.3983 | 36.6601 | 22.0686 | 18.9388 | 92.7853 | 33.9076 | 33.1476 | 35.1139 | 33.4539 | 33.1446 | 33.4862 | 34.8525 | 34.3758 | 34.1076 | 37.252 | 36.3133 | 33.5063 | 34.4126 | 36.3215 | 36.561 | 37.4739 | 36.324 | 33.4537 | 32.8187 | 34.6253 | 35.1323 | 33.2521 | 34.3499 | 34.3908 | 34.4764 | 34.3437 | 34.3329 | 34.3892 | 34.0129 | 34.3263 | 35.8545 | 35.2018 | 36.2207 | 36.2274 | 33.586 | 92.6522 | 92.7704 | 92.7027
2022-09-08 03:08 | 5:18 | 19.4665 | 20.0744 | 22.607 | 35.3062 | 34.4178 | 33.886 | 34.6949 | 35.4295 | 36.5671 | 37.3279 | 36.8648 | 37.9081 | 34.3556 | 34.3582 | 34.2306 | 35.1168 | 35.2148 | 35.6735 | 36.3911 | 36.6518 | 22.0328 | 18.8837 | 92.6596 | 33.9296 | 33.1358 | 35.1131 | 33.4608 | 33.1343 | 33.4944 | 34.8458 | 34.3705 | 34.128 | 37.247 | 36.3233 | 33.4832 | 34.4047 | 36.3087 | 36.5703 | 37.4411 | 36.3169 | 33.4654 | 32.8037 | 34.6061 | 35.1319 | 33.2674 | 34.3373 | 34.4089 | 34.4903 | 34.331 | 34.3225 | 34.4122 | 34.0176 | 34.3437 | 35.8312 | 35.2116 | 36.2282 | 36.2143 | 33.5878 | 92.5632 | 92.661 | 92.6237
2022-09-08 03:08 | 5:18 | 19.3355 | 19.9572 | 22.4812 | 35.3755 | 34.4223 | 33.8759 | 34.7175 | 35.4209 | 36.5504 | 37.3091 | 36.8672 | 37.9376 | 34.3568 | 34.3384 | 34.2296 | 35.1041 | 35.2329 | 35.6393 | 36.3901 | 36.6597 | 21.9973 | 18.7478 | 92.7158 | 33.8646 | 33.149 | 35.1219 | 33.4703 | 33.1358 | 33.483 | 34.8531 | 34.3766 | 34.1182 | 37.2575 | 36.3142 | 33.4908 | 34.4152 | 36.3133 | 36.5721 | 37.4615 | 36.332 | 33.4444 | 32.7924 | 34.6066 | 35.1208 | 33.2701 | 34.3479 | 34.4226 | 34.4759 | 34.3357 | 34.313 | 34.3923 | 34.0275 | 34.331 | 35.8415 | 35.2267 | 36.2357 | 36.1907 | 33.5782 | 92.4834 | 92.4997 | 92.6155
2022-09-08 03:08 | 5:18 | 19.2203 | 19.8362 | 22.423 | 35.1879 | 34.4268 | 33.8488 | 34.7009 | 35.4345 | 36.5678 | 37.3149 | 36.8609 | 37.9274 | 34.3491 | 34.3388 | 34.2409 | 35.0885 | 35.2311 | 35.6519 | 36.3901 | 36.6585 | 21.964 | 18.645 | 92.5719 | 33.8234 | 33.1416 | 35.1099 | 33.4584 | 33.1392 | 33.4843 | 34.8512 | 34.3541 | 34.1234 | 37.2344 | 36.3148 | 33.4734 | 34.4179 | 36.3233 | 36.5685 | 37.4799 | 36.3215 | 33.4559 | 32.7938 | 34.6106 | 35.1142 | 33.2623 | 34.3418 | 34.4184 | 34.466 | 34.3207 | 34.3182 | 34.401 | 34.0328 | 34.3357 | 35.8466 | 35.2234 | 36.2221 | 36.2204 | 33.5841 | 92.317 | 92.3362 | 92.445
2022-09-08 03:08 | 5:18 | 19.2073 | 19.7967 | 22.4436 | 35.1884 | 34.4336 | 33.856 | 34.6878 | 35.4159 | 36.5669 | 37.3298 | 36.8459 | 37.9322 | 34.3578 | 34.3219 | 34.2357 | 35.102 | 35.2313 | 35.659 | 36.4017 | 36.6731 | 21.9016 | 18.5887 | 92.4465 | 33.9302 | 33.1484 | 35.1134 | 33.4537 | 33.1571 | 33.5063 | 34.8576 | 34.3739 | 34.1384 | 37.2567 | 36.3203 | 33.5103 | 34.4164 | 36.3142 | 36.56 | 37.4757 | 36.3087 | 33.4534 | 32.8031 | 34.6176 | 35.1352 | 33.2488 | 34.3498 | 34.4196 | 34.4876 | 34.3302 | 34.338 | 34.3783 | 34.0121 | 34.3207 | 35.8526 | 35.2285 | 36.2257 | 36.2078 | 33.5928 | 92.1525 | 92.2766 | 92.2644
2022-09-08 03:09 | 5:19 | 19.1138 | 19.6985 | 22.37 | 35.1866 | 34.4344 | 33.8636 | 34.6818 | 35.4323 | 36.5581 | 37.3168 | 36.8648 | 37.932 | 34.3323 | 34.3218 | 34.2357 | 35.0922 | 35.2408 | 35.6534 | 36.3911 | 36.6587 | 21.8778 | 18.5404 | 92.3188 | 33.9065 | 33.1429 | 35.1045 | 33.4654 | 33.1467 | 33.4832 | 34.8503 | 34.3655 | 34.1474 | 37.2709 | 36.3244 | 33.5025 | 34.4004 | 36.3148 | 36.5571 | 37.4653 | 36.3133 | 33.4622 | 32.7829 | 34.615 | 35.0975 | 33.2527 | 34.3176 | 34.4232 | 34.484 | 34.3411 | 34.3344 | 34.3928 | 34.0297 | 34.3302 | 35.8574 | 35.2139 | 36.2511 | 36.2087 | 33.6052 | 92.0565 | 92.1934 | 92.2578
2022-09-08 03:09 | 5:19 | 19.0508 | 19.6128 | 22.2597 | 35.1972 | 34.4054 | 33.8762 | 34.6948 | 35.4433 | 36.5798 | 37.3276 | 36.8671 | 37.9389 | 34.3552 | 34.3323 | 34.2407 | 35.1118 | 35.2199 | 35.6552 | 36.3848 | 36.6675 | 21.827 | 18.507 | 92.3347 | 33.8214 | 33.1397 | 35.1336 | 33.4444 | 33.1547 | 33.4908 | 34.8417 | 34.3648 | 34.1225 | 37.2431 | 36.3237 | 33.4809 | 34.407 | 36.3203 | 36.5581 | 37.4565 | 36.3233 | 33.4505 | 32.7772 | 34.6117 | 35.1331 | 33.2423 | 34.3354 | 34.4102 | 34.4972 | 34.3387 | 34.3374 | 34.3933 | 34.0233 | 34.3411 | 35.8644 | 35.2098 | 36.2274 | 36.206 | 33.6032 | 92.1511 | 92.2451 | 92.2453
2022-09-08 03:09 | 5:19 | 18.9181 | 19.5118 | 22.0957 | 35.2294 | 34.42 | 33.8659 | 34.6917 | 35.4294 | 36.5815 | 37.329 | 36.8672 | 37.9231 | 34.3319 | 34.345 | 34.2284 | 35.1171 | 35.2204 | 35.6445 | 36.3943 | 36.6824 | 21.8003 | 18.4464 | 92.3888 | 33.781 | 33.1529 | 35.1332 | 33.4559 | 33.132 | 33.4734 | 34.8373 | 34.3625 | 34.1377 | 37.261 | 36.3017 | 33.4768 | 34.4132 | 36.3244 | 36.5639 | 37.4664 | 36.3142 | 33.4691 | 32.8059 | 34.5883 | 35.1309 | 33.2242 | 34.3349 | 34.4409 | 34.4734 | 34.3405 | 34.3303 | 34.3804 | 34.028 | 34.3387 | 35.8508 | 35.2164 | 36.2358 | 36.2206 | 33.5829 | 92.1693 | 92.3201 | 92.3477
2022-09-08 03:09 | 5:19 | 18.9468 | 19.48 | 21.9902 | 35.1166 | 34.4248 | 33.8688 | 34.7058 | 35.4358 | 36.5545 | 37.3318 | 36.8759 | 37.9429 | 34.3425 | 34.3195 | 34.2212 | 35.1369 | 35.2226 | 35.6574 | 36.3697 | 36.6652 | 21.74 | 18.3948 | 92.4638 | 33.8881 | 33.1545 | 35.1265 | 33.4534 | 33.143 | 33.5103 | 34.8434 | 34.3779 | 34.1298 | 37.2649 | 36.3145 | 33.472 | 34.4302 | 36.3237 | 36.5473 | 37.4611 | 36.3148 | 33.4417 | 32.7754 | 34.6041 | 35.1264 | 33.2229 | 34.3052 | 34.4239 | 34.4966 | 34.3314 | 34.3228 | 34.4116 | 34.0315 | 34.3405 | 35.8651 | 35.2162 | 36.2261 | 36.2108 | 33.5979 | 92.285 | 92.4121 | 92.4031
2022-09-08 03:09 | 5:19 | 18.8102 | 19.3815 | 21.9011 | 35.1597 | 34.4016 | 33.8617 | 34.6994 | 35.4435 | 36.5665 | 37.3106 | 36.8718 | 37.9278 | 34.3407 | 34.3116 | 34.24 | 35.0968 | 35.2267 | 35.6439 | 36.382 | 36.6777 | 21.6833 | 18.317 | 92.4958 | 33.7416 | 33.1512 | 35.1001 | 33.4622 | 33.1376 | 33.5025 | 34.8419 | 34.3698 | 34.1233 | 37.2394 | 36.2986 | 33.4823 | 34.4082 | 36.3017 | 36.5562 | 37.4525 | 36.3203 | 33.4303 | 32.7517 | 34.5872 | 35.1282 | 33.2123 | 34.3244 | 34.4106 | 34.4726 | 34.3627 | 34.3372 | 34.3854 | 34.0003 | 34.3314 | 35.8695 | 35.2012 | 36.2394 | 36.212 | 33.6093 | 92.3608 | 92.5087 | 92.4467
2022-09-08 03:09 | 5:19 | 18.787 | 19.3062 | 21.9179 | 35.0405 | 34.4262 | 33.8644 | 34.6875 | 35.4366 | 36.5723 | 37.3309 | 36.8503 | 37.9413 | 34.3325 | 34.3142 | 34.2169 | 35.103 | 35.2391 | 35.6489 | 36.3744 | 36.6584 | 21.6317 | 18.2555 | 92.5299 | 33.7273 | 33.1239 | 35.0949 | 33.4505 | 33.1328 | 33.4809 | 34.8566 | 34.3812 | 34.1307 | 37.246 | 36.2951 | 33.4882 | 34.4048 | 36.3145 | 36.5644 | 37.469 | 36.3244 | 33.4229 | 32.7677 | 34.5847 | 35.1138 | 33.2263 | 34.3082 | 34.4389 | 34.4718 | 34.3524 | 34.3556 | 34.4085 | 34.0294 | 34.3627 | 35.8567 | 35.2043 | 36.241 | 36.2221 | 33.5954 | 92.3879 | 92.6073 | 92.5506
2022-09-08 03:10 | 5:20 | 18.6688 | 19.2066 | 21.874 | 35.0274 | 34.4062 | 33.8389 | 34.6814 | 35.43 | 36.5702 | 37.3216 | 36.8654 | 37.9381 | 34.334 | 34.3204 | 34.2425 | 35.1036 | 35.2237 | 35.6447 | 36.3765 | 36.6627 | 21.5785 | 18.1726 | 92.5605 | 33.675 | 33.1349 | 35.0955 | 33.4691 | 33.1365 | 33.4768 | 34.8407 | 34.3646 | 34.1243 | 37.2392 | 36.3071 | 33.4819 | 34.4009 | 36.2986 | 36.5657 | 37.4731 | 36.3237 | 33.4438 | 32.7604 | 34.585 | 35.1301 | 33.2045 | 34.3131 | 34.4553 | 34.4814 | 34.339 | 34.3421 | 34.3962 | 34.0294 | 34.3524 | 35.8589 | 35.2043 | 36.2271 | 36.2205 | 33.6063 | 92.5006 | 92.7073 | 92.5663
2022-09-08 03:10 | 5:20 | 18.648 | 19.1395 | 21.8122 | 35.1431 | 34.4174 | 33.8775 | 34.6813 | 35.4319 | 36.5599 | 37.3407 | 36.8598 | 37.9205 | 34.3285 | 34.3077 | 34.2063 | 35.1021 | 35.2262 | 35.6306 | 36.3623 | 36.662 | 21.5322 | 18.1541 | 92.6268 | 33.5785 | 33.1472 | 35.101 | 33.4417 | 33.1438 | 33.472 | 34.8358 | 34.3552 | 34.124 | 37.2584 | 36.2863 | 33.4757 | 34.3992 | 36.2951 | 36.5486 | 37.455 | 36.3017 | 33.423 | 32.7551 | 34.5769 | 35.1068 | 33.1967 | 34.2898 | 34.423 | 34.4913 | 34.3447 | 34.3439 | 34.3828 | 34.0354 | 34.339 | 35.8625 | 35.2149 | 36.2337 | 36.2194 | 33.6144 | 92.5775 | 92.7877 | 92.5984
2022-09-08 03:10 | 5:20 | 18.5922 | 19.1113 | 21.8188 | 35.1401 | 34.4225 | 33.8679 | 34.687 | 35.4317 | 36.5709 | 37.3195 | 36.8634 | 37.9327 | 34.3383 | 34.314 | 34.2214 | 35.1048 | 35.2199 | 35.6324 | 36.355 | 36.6735 | 21.4827 | 18.1066 | 92.7349 | 33.632 | 33.1467 | 35.1081 | 33.4303 | 33.1227 | 33.4823 | 34.8436 | 34.3628 | 34.1217 | 37.2466 | 36.2995 | 33.4822 | 34.4066 | 36.3071 | 36.5575 | 37.4698 | 36.3145 | 33.4222 | 32.7623 | 34.5698 | 35.1141 | 33.182 | 34.3036 | 34.4346 | 34.4938 | 34.3445 | 34.3364 | 34.371 | 34.018 | 34.3447 | 35.8526 | 35.1974 | 36.2327 | 36.2082 | 33.6113 | 92.6677 | 92.9094 | 92.7667
2022-09-08 03:10 | 5:20 | 18.4849 | 19.0077 | 21.7384 | 35.0134 | 34.3985 | 33.8471 | 34.6868 | 35.4236 | 36.5748 | 37.3234 | 36.8559 | 37.935 | 34.3337 | 34.3132 | 34.2193 | 35.0976 | 35.2226 | 35.6327 | 36.375 | 36.6728 | 21.4465 | 18.086 | 92.9676 | 33.7835 | 33.1471 | 35.1117 | 33.4229 | 33.1211 | 33.4882 | 34.8411 | 34.361 | 34.1176 | 37.2307 | 36.3091 | 33.4753 | 34.415 | 36.2863 | 36.548 | 37.4637 | 36.2986 | 33.4121 | 32.7378 | 34.5872 | 35.114 | 33.1832 | 34.3063 | 34.4469 | 34.4729 | 34.3313 | 34.3341 | 34.3776 | 34.0133 | 34.3445 | 35.8675 | 35.2044 | 36.2168 | 36.2262 | 33.5915 | 92.8555 | 93.0575 | 92.9475
2022-09-08 03:10 | 5:20 | 18.4475 | 18.9761 | 21.6668 | 35.041 | 34.4203 | 33.8551 | 34.69 | 35.4276 | 36.5645 | 37.3113 | 36.8519 | 37.9253 | 34.323 | 34.2918 | 34.2172 | 35.1042 | 35.2186 | 35.6052 | 36.3634 | 36.6745 | 21.384 | 17.9882 | 92.9509 | 33.7662 | 33.1428 | 35.1079 | 33.4438 | 33.1255 | 33.4819 | 34.8324 | 34.3502 | 34.1297 | 37.249 | 36.2943 | 33.4674 | 34.3997 | 36.2995 | 36.5408 | 37.46 | 36.2951 | 33.4451 | 32.7448 | 34.5747 | 35.0961 | 33.1769 | 34.3027 | 34.4279 | 34.4853 | 34.3636 | 34.3359 | 34.3658 | 34.0093 | 34.3313 | 35.8697 | 35.2105 | 36.2251 | 36.229 | 33.6188 | 92.9923 | 93.1817 | 92.9577
2022-09-08 03:10 | 5:20 | 18.4378 | 19.0047 | 21.5434 | 35.0464 | 34.409 | 33.8624 | 34.674 | 35.4324 | 36.5699 | 37.3258 | 36.8577 | 37.9306 | 34.3129 | 34.2875 | 34.2206 | 35.1015 | 35.2126 | 35.6381 | 36.3661 | 36.6608 | 21.3528 | 17.9784 | 93.0128 | 33.6632 | 33.1264 | 35.109 | 33.423 | 33.1196 | 33.4757 | 34.8401 | 34.3495 | 34.1255 | 37.2445 | 36.2789 | 33.4745 | 34.4024 | 36.3091 | 36.5623 | 37.4741 | 36.3071 | 33.436 | 32.7315 | 34.5459 | 35.1067 | 33.1585 | 34.2816 | 34.4279 | 34.5006 | 34.3523 | 34.3354 | 34.3654 | 34.0217 | 34.3636 | 35.8737 | 35.209 | 36.252 | 36.2257 | 33.5913 | 93.1118 | 93.2943 | 93.019
2022-09-08 03:11 | 5:20 | 18.3459 | 18.8622 | 21.447 | 34.9609 | 34.4133 | 33.8334 | 34.6599 | 35.4428 | 36.5779 | 37.3245 | 36.8609 | 37.9252 | 34.3253 | 34.292 | 34.2222 | 35.0868 | 35.2208 | 35.6247 | 36.3514 | 36.6595 | 21.3423 | 17.949 | 93.0299 | 33.5994 | 33.1389 | 35.0954 | 33.4222 | 33.1092 | 33.4822 | 34.8323 | 34.3371 | 34.1034 | 37.2438 | 36.3074 | 33.4857 | 34.3895 | 36.2943 | 36.5561 | 37.4566 | 36.2863 | 33.4277 | 32.7345 | 34.5493 | 35.0946 | 33.1816 | 34.2981 | 34.4199 | 34.4899 | 34.3511 | 34.3367 | 34.3778 | 34.0006 | 34.3523 | 35.8678 | 35.2017 | 36.2355 | 36.206 | 33.5988 | 93.1523 | 93.3954 | 93.0657
2022-09-08 03:11 | 5:21 | 18.265 | 18.8277 | 21.4605 | 34.9227 | 34.4091 | 33.8514 | 34.681 | 35.4344 | 36.5657 | 37.3242 | 36.8647 | 37.918 | 34.3222 | 34.2984 | 34.2239 | 35.0863 | 35.2063 | 35.6273 | 36.3572 | 36.669 | 21.2866 | 17.8867 | 93.0441 | 33.6431 | 33.115 | 35.0779 | 33.4121 | 33.0989 | 33.4753 | 34.8403 | 34.3539 | 34.1227 | 37.2357 | 36.284 | 33.4802 | 34.3901 | 36.2789 | 36.5509 | 37.4633 | 36.2995 | 33.4208 | 32.7185 | 34.5299 | 35.0711 | 33.1544 | 34.2981 | 34.4316 | 34.4851 | 34.3342 | 34.3326 | 34.3642 | 34.0054 | 34.3511 | 35.8532 | 35.221 | 36.2358 | 36.2171 | 33.6028 | 93.2479 | 93.4967 | 93.0932
2022-09-08 03:11 | 5:21 | 18.3089 | 18.8 | 21.5136 | 34.9715 | 34.4104 | 33.8486 | 34.6699 | 35.4287 | 36.58 | 37.3186 | 36.8419 | 37.9333 | 34.3077 | 34.3025 | 34.202 | 35.1018 | 35.2094 | 35.6141 | 36.3571 | 36.673 | 21.266 | 17.8138 | 93.2026 | 33.5267 | 33.1219 | 35.0693 | 33.4451 | 33.1334 | 33.4674 | 34.8443 | 34.347 | 34.1157 | 37.2389 | 36.2941 | 33.4837 | 34.396 | 36.3074 | 36.5521 | 37.4489 | 36.3091 | 33.4212 | 32.7295 | 34.5386 | 35.0856 | 33.1407 | 34.2827 | 34.4469 | 34.4887 | 34.3608 | 34.3327 | 34.359 | 34.0162 | 34.3342 | 35.8649 | 35.2185 | 36.2221 | 36.2342 | 33.5821 | 93.3752 | 93.6875 | 93.2047
2022-09-08 03:11 | 5:21 | 18.1737 | 18.6819 | 21.3676 | 34.9 | 34.409 | 33.8494 | 34.6643 | 35.4151 | 36.5889 | 37.3081 | 36.8463 | 37.9266 | 34.3097 | 34.2946 | 34.2243 | 35.0825 | 35.217 | 35.6272 | 36.3527 | 36.6745 | 21.2266 | 17.8423 | 93.2425 | 33.6742 | 33.1205 | 35.092 | 33.436 | 33.1156 | 33.4745 | 34.8269 | 34.3606 | 34.1109 | 37.219 | 36.2907 | 33.4742 | 34.4061 | 36.284 | 36.5539 | 37.4465 | 36.2943 | 33.4211 | 32.7146 | 34.5236 | 35.0667 | 33.1407 | 34.2957 | 34.4431 | 34.4995 | 34.3525 | 34.3509 | 34.3712 | 34.0042 | 34.3608 | 35.8773 | 35.2108 | 36.2197 | 36.2177 | 33.5968 | 93.5153 | 93.8311 | 93.3149
2022-09-08 03:11 | 5:21 | 18.1833 | 18.6468 | 21.3081 | 34.9175 | 34.4054 | 33.8642 | 34.6669 | 35.4235 | 36.5763 | 37.3108 | 36.8392 | 37.9017 | 34.2916 | 34.2906 | 34.2324 | 35.0906 | 35.2071 | 35.6154 | 36.3473 | 36.6893 | 21.2072 | 17.7802 | 93.3233 | 33.4514 | 33.1359 | 35.0781 | 33.4277 | 33.1151 | 33.4857 | 34.8287 | 34.3429 | 34.1071 | 37.2322 | 36.2998 | 33.4772 | 34.3961 | 36.2941 | 36.5399 | 37.4378 | 36.2789 | 33.4239 | 32.7098 | 34.5469 | 35.0494 | 33.132 | 34.2769 | 34.4472 | 34.4841 | 34.3616 | 34.3416 | 34.3432 | 34.0078 | 34.3525 | 35.8485 | 35.2028 | 36.237 | 36.227 | 33.5816 | 93.6282 | 93.9787 | 93.398
2022-09-08 03:11 | 5:21 | 18.1057 | 18.5953 | 21.2154 | 34.9086 | 34.3984 | 33.8715 | 34.6676 | 35.4162 | 36.5531 | 37.3151 | 36.8549 | 37.9156 | 34.3064 | 34.2902 | 34.2144 | 35.1082 | 35.2292 | 35.6088 | 36.3537 | 36.6664 | 21.1784 | 17.7196 | 93.3745 | 33.5237 | 33.1201 | 35.0794 | 33.4208 | 33.0884 | 33.4802 | 34.847 | 34.3382 | 34.1158 | 37.2474 | 36.2859 | 33.4752 | 34.3908 | 36.2907 | 36.5468 | 37.4617 | 36.3074 | 33.4194 | 32.7069 | 34.5181 | 35.0667 | 33.1285 | 34.2938 | 34.4273 | 34.4864 | 34.3556 | 34.3402 | 34.3388 | 33.9855 | 34.3616 | 35.8615 | 35.2002 | 36.2218 | 36.2116 | 33.6027 | 93.8442 | 94.2004 | 93.4878
2022-09-08 03:12 | 5:22 | 18.1691 | 18.5748 | 21.2444 | 34.8658 | 34.4037 | 33.8527 | 34.6862 | 35.4145 | 36.57 | 37.3033 | 36.8474 | 37.9171 | 34.3171 | 34.2858 | 34.2173 | 35.1083 | 35.1987 | 35.6145 | 36.3315 | 36.6666 | 21.1578 | 17.7234 | 93.5334 | 33.432 | 33.1215 | 35.0906 | 33.4212 | 33.116 | 33.4837 | 34.8298 | 34.3625 | 34.1187 | 37.2455 | 36.2863 | 33.4923 | 34.4087 | 36.2998 | 36.5558 | 37.4539 | 36.284 | 33.4106 | 32.6937 | 34.5182 | 35.0577 | 33.1166 | 34.2731 | 34.4391 | 34.4901 | 34.3518 | 34.3494 | 34.3559 | 34.0034 | 34.3556 | 35.849 | 35.1991 | 36.2392 | 36.2349 | 33.5931 | 94.0876 | 94.3665 | 93.6878
2022-09-08 03:12 | 5:22 | 18.0435 | 18.5096 | 21.2478 | 34.8907 | 34.4099 | 33.8598 | 34.6637 | 35.4225 | 36.5786 | 37.3195 | 36.8346 | 37.9162 | 34.304 | 34.286 | 34.2221 | 35.0972 | 35.2138 | 35.6221 | 36.3407 | 36.648 | 21.1339 | 17.7217 | 93.7068 | 33.2779 | 33.1074 | 35.0763 | 33.4211 | 33.0985 | 33.4742 | 34.8262 | 34.3401 | 34.118 | 37.2219 | 36.2859 | 33.4736 | 34.388 | 36.2859 | 36.5373 | 37.4438 | 36.2941 | 33.4169 | 32.7056 | 34.5164 | 35.0665 | 33.0988 | 34.2923 | 34.4219 | 34.4906 | 34.3473 | 34.3382 | 34.3475 | 33.9818 | 34.3518 | 35.8435 | 35.1952 | 36.2633 | 36.2034 | 33.5867 | 94.2464 | 94.5443 | 93.7885
2022-09-08 03:12 | 5:22 | 18.1013 | 18.4917 | 21.1699 | 34.7796 | 34.4007 | 33.8536 | 34.6727 | 35.4232 | 36.5665 | 37.3152 | 36.8762 | 37.9209 | 34.3302 | 34.2851 | 34.2124 | 35.0958 | 35.2105 | 35.6175 | 36.3312 | 36.6795 | 21.11 | 17.6554 | 93.7508 | 33.4804 | 33.1345 | 35.0873 | 33.4239 | 33.0881 | 33.4772 | 34.8264 | 34.3428 | 34.1074 | 37.2445 | 36.2641 | 33.4798 | 34.3994 | 36.2863 | 36.5439 | 37.4508 | 36.2907 | 33.4081 | 32.6874 | 34.5066 | 35.065 | 33.1008 | 34.2772 | 34.4269 | 34.4638 | 34.3631 | 34.3397 | 34.3447 | 33.9996 | 34.3473 | 35.8705 | 35.2022 | 36.245 | 36.2271 | 33.5892 | 94.3977 | 94.7272 | 93.9601
2022-09-08 03:12 | 5:22 | 17.9364 | 18.4284 | 21.0564 | 34.8526 | 34.3993 | 33.8649 | 34.6655 | 35.4329 | 36.5713 | 37.3071 | 36.8702 | 37.8948 | 34.3257 | 34.2716 | 34.2213 | 35.1054 | 35.1989 | 35.6173 | 36.3292 | 36.6587 | 21.0643 | 17.605 | 93.8689 | 33.3539 | 33.1129 | 35.0822 | 33.4194 | 33.1066 | 33.4752 | 34.8249 | 34.336 | 34.1316 | 37.227 | 36.2887 | 33.4786 | 34.3919 | 36.2859 | 36.5419 | 37.4528 | 36.2998 | 33.4206 | 32.698 | 34.4976 | 35.0626 | 33.1059 | 34.2701 | 34.4476 | 34.4935 | 34.3588 | 34.3627 | 34.3582 | 34.0093 | 34.3631 | 35.8663 | 35.1994 | 36.2362 | 36.205 | 33.5754 | 94.6153 | 94.9545 | 94.0357
2022-09-08 03:12 | 5:22 | 17.8817 | 18.3668 | 21.077 | 34.7928 | 34.4127 | 33.8466 | 34.6651 | 35.4205 | 36.5764 | 37.3214 | 36.8385 | 37.9336 | 34.3133 | 34.2707 | 34.2171 | 35.0807 | 35.2038 | 35.624 | 36.3231 | 36.6639 | 21.0596 | 17.568 | 94.0974 | 33.4436 | 33.1178 | 35.0861 | 33.4106 | 33.1052 | 33.4923 | 34.8426 | 34.3479 | 34.1023 | 37.2436 | 36.272 | 33.4739 | 34.3841 | 36.2641 | 36.5306 | 37.4583 | 36.2859 | 33.4111 | 32.6788 | 34.5118 | 35.0296 | 33.0976 | 34.2775 | 34.449 | 34.4833 | 34.3765 | 34.3474 | 34.3384 | 33.9898 | 34.3588 | 35.8694 | 35.189 | 36.2486 | 36.2093 | 33.5719 | 94.8037 | 95.1311 | 94.2713
2022-09-08 03:12 | 5:22 | 17.8756 | 18.3387 | 21.0429 | 34.7956 | 34.3996 | 33.8576 | 34.6675 | 35.4405 | 36.5639 | 37.3143 | 36.844 | 37.9168 | 34.3169 | 34.2963 | 34.2115 | 35.0852 | 35.2055 | 35.603 | 36.3313 | 36.6561 | 21.0435 | 17.5387 | 94.1893 | 33.3553 | 33.1185 | 35.0646 | 33.4169 | 33.0794 | 33.4736 | 34.8245 | 34.3334 | 34.1152 | 37.2362 | 36.2666 | 33.4659 | 34.393 | 36.2887 | 36.5496 | 37.4432 | 36.2863 | 33.4148 | 32.6752 | 34.4745 | 35.0525 | 33.0914 | 34.2698 | 34.4414 | 34.4706 | 34.3375 | 34.3434 | 34.3388 | 33.9721 | 34.3765 | 35.868 | 35.2075 | 36.2369 | 36.2227 | 33.5826 | 94.841 | 95.273 | 94.3379
2022-09-08 03:13 | 5:22 | 17.8508 | 18.3117 | 20.8923 | 34.7953 | 34.3892 | 33.8439 | 34.6638 | 35.4168 | 36.5692 | 37.299 | 36.8454 | 37.8952 | 34.2931 | 34.2767 | 34.2043 | 35.0819 | 35.1972 | 35.6229 | 36.3406 | 36.6633 | 21.0503 | 17.5249 | 94.2385 | 33.4529 | 33.1153 | 35.078 | 33.4081 | 33.0952 | 33.4798 | 34.8323 | 34.3556 | 34.1067 | 37.2167 | 36.2861 | 33.4777 | 34.3807 | 36.272 | 36.5573 | 37.4422 | 36.2859 | 33.3867 | 32.6659 | 34.4826 | 35.0493 | 33.0894 | 34.2889 | 34.4258 | 34.4778 | 34.3617 | 34.3519 | 34.3219 | 33.9809 | 34.3375 | 35.8491 | 35.226 | 36.2383 | 36.2226 | 33.5673 | 95.0233 | 95.4178 | 94.3877
2022-09-08 03:13 | 5:23 | 17.8735 | 18.2506 | 20.9253 | 34.7261 | 34.4122 | 33.8624 | 34.656 | 35.4269 | 36.558 | 37.3218 | 36.8522 | 37.9274 | 34.3144 | 34.2881 | 34.1983 | 35.0937 | 35.2127 | 35.6166 | 36.3175 | 36.6659 | 21.0034 | 17.4875 | 94.2911 | 33.4327 | 33.1087 | 35.0749 | 33.4206 | 33.085 | 33.4786 | 34.827 | 34.3511 | 34.1202 | 37.242 | 36.2703 | 33.4682 | 34.4029 | 36.2666 | 36.538 | 37.4359 | 36.2641 | 33.3895 | 32.6608 | 34.4757 | 35.0263 | 33.0732 | 34.2827 | 34.4204 | 34.453 | 34.362 | 34.3529 | 34.3218 | 33.9676 | 34.3617 | 35.8669 | 35.2009 | 36.2324 | 36.2312 | 33.5546 | 95.0642 | 95.5175 | 94.3099
2022-09-08 03:13 | 5:23 | 17.8072 | 18.1963 | 20.8825 | 34.784 | 34.3923 | 33.8645 | 34.6622 | 35.4153 | 36.57 | 37.3013 | 36.8511 | 37.9165 | 34.304 | 34.2839 | 34.2028 | 35.0915 | 35.1956 | 35.5916 | 36.2967 | 36.652 | 21.0186 | 17.4694 | 94.3561 | 33.3373 | 33.123 | 35.0672 | 33.4111 | 33.0924 | 33.4739 | 34.8205 | 34.3209 | 34.1081 | 37.2263 | 36.277 | 33.4549 | 34.3882 | 36.2861 | 36.5424 | 37.4389 | 36.2887 | 33.4057 | 32.6482 | 34.479 | 35.0237 | 33.0825 | 34.2647 | 34.4527 | 34.4804 | 34.3398 | 34.3565 | 34.3323 | 33.9795 | 34.362 | 35.8406 | 35.205 | 36.2349 | 36.222 | 33.5615 | 95.1681 | 95.6004 | 94.4908
2022-09-08 03:13 | 5:23 | 17.7911 | 18.2081 | 20.8546 | 34.7314 | 34.401 | 33.8637 | 34.6485 | 35.4205 | 36.5605 | 37.2988 | 36.851 | 37.9259 | 34.3186 | 34.2905 | 34.2191 | 35.0845 | 35.1882 | 35.5898 | 36.3036 | 36.6552 | 20.9991 | 17.4346 | 94.402 | 33.3554 | 33.1198 | 35.0811 | 33.4148 | 33.0891 | 33.4659 | 34.8249 | 34.3359 | 34.1136 | 37.2442 | 36.2682 | 33.4568 | 34.3903 | 36.2703 | 36.5567 | 37.4328 | 36.272 | 33.3989 | 32.6565 | 34.4731 | 35.0245 | 33.0703 | 34.2681 | 34.4404 | 34.4565 | 34.3747 | 34.3655 | 34.345 | 33.9624 | 34.3398 | 35.8573 | 35.2086 | 36.2344 | 36.21 | 33.5648 | 95.2718 | 95.6874 | 94.5534
2022-09-08 03:13 | 5:23 | 17.736 | 18.1091 | 20.8062 | 34.7203 | 34.3783 | 33.8689 | 34.642 | 35.4245 | 36.5592 | 37.311 | 36.8486 | 37.9119 | 34.3119 | 34.2812 | 34.197 | 35.0996 | 35.1823 | 35.5948 | 36.3282 | 36.6246 | 20.9857 | 17.4249 | 94.486 | 33.3847 | 33.1065 | 35.0714 | 33.3867 | 33.1061 | 33.4777 | 34.8267 | 34.3356 | 34.112 | 37.2097 | 36.2732 | 33.4581 | 34.3912 | 36.277 | 36.5477 | 37.4279 | 36.2666 | 33.4082 | 32.6503 | 34.4643 | 35.0092 | 33.0658 | 34.283 | 34.4387 | 34.4695 | 34.3511 | 34.347 | 34.3195 | 33.97 | 34.3747 | 35.8475 | 35.1984 | 36.2422 | 36.2246 | 33.5589 | 95.3396 | 95.6921 | 94.585
2022-09-08 03:13 | 5:23 | 17.7206 | 18.1103 | 20.7092 | 34.7357 | 34.3928 | 33.8597 | 34.6456 | 35.4197 | 36.5606 | 37.2928 | 36.8645 | 37.9126 | 34.3025 | 34.2769 | 34.1989 | 35.0807 | 35.1952 | 35.5944 | 36.2887 | 36.6473 | 20.9843 | 17.4007 | 94.4133 | 33.4895 | 33.1122 | 35.0767 | 33.3895 | 33.0821 | 33.4682 | 34.8245 | 34.3257 | 34.1174 | 37.224 | 36.2669 | 33.4496 | 34.3889 | 36.2682 | 36.5428 | 37.4408 | 36.2861 | 33.4073 | 32.6373 | 34.4593 | 35.0175 | 33.0461 | 34.2721 | 34.4295 | 34.4558 | 34.3657 | 34.3498 | 34.3116 | 33.9817 | 34.3511 | 35.839 | 35.187 | 36.2506 | 36.2043 | 33.551 | 95.1503 | 95.5307 | 94.4015
2022-09-08 03:14 | 5:24 | 17.6532 | 18.0781 | 20.7383 | 34.6571 | 34.3933 | 33.8431 | 34.6629 | 35.407 | 36.5695 | 37.2897 | 36.8599 | 37.9229 | 34.3256 | 34.2715 | 34.1947 | 35.0768 | 35.1801 | 35.594 | 36.3133 | 36.6523 | 21.0168 | 17.3374 | 94.2023 | 33.2324 | 33.0898 | 35.0572 | 33.4057 | 33.1006 | 33.4549 | 34.8189 | 34.3259 | 34.1239 | 37.2244 | 36.2617 | 33.4573 | 34.374 | 36.2732 | 36.5321 | 37.4105 | 36.2703 | 33.3987 | 32.6382 | 34.4496 | 35.0012 | 33.0481 | 34.2586 | 34.4209 | 34.4459 | 34.3894 | 34.3728 | 34.3142 | 33.9823 | 34.3657 | 35.831 | 35.2046 | 36.2561 | 36.2148 | 33.5329 | 94.8722 | 95.3027 | 94.1962
2022-09-08 03:14 | 5:24 | 17.6346 | 18.0441 | 20.7032 | 34.5698 | 34.3804 | 33.8522 | 34.6385 | 35.4077 | 36.5583 | 37.2911 | 36.8559 | 37.914 | 34.308 | 34.2877 | 34.1922 | 35.0851 | 35.172 | 35.5884 | 36.3065 | 36.6437 | 20.9952 | 17.3382 | 94.1015 | 33.2779 | 33.0966 | 35.0771 | 33.3989 | 33.0847 | 33.4568 | 34.8146 | 34.3313 | 34.103 | 37.1985 | 36.2756 | 33.4456 | 34.3896 | 36.2669 | 36.5245 | 37.4304 | 36.277 | 33.3973 | 32.6268 | 34.4353 | 34.9976 | 33.0461 | 34.2583 | 34.4295 | 34.4397 | 34.3594 | 34.3644 | 34.3204 | 33.9631 | 34.3894 | 35.8229 | 35.2101 | 36.2343 | 36.2063 | 33.5348 | 94.6555 | 95.0345 | 94.1054
2022-09-08 03:14 | 5:24 | 17.6063 | 18.0384 | 20.6778 | 34.6848 | 34.4116 | 33.8452 | 34.6481 | 35.4139 | 36.5573 | 37.2745 | 36.8407 | 37.9102 | 34.3271 | 34.2848 | 34.198 | 35.0753 | 35.2117 | 35.5873 | 36.3106 | 36.6339 | 21.0149 | 17.2749 | 93.9727 | 33.2822 | 33.076 | 35.0683 | 33.4082 | 33.0893 | 33.4581 | 34.809 | 34.35 | 34.0948 | 37.2181 | 36.2688 | 33.4608 | 34.3856 | 36.2617 | 36.5343 | 37.3817 | 36.2682 | 33.4056 | 32.6105 | 34.4263 | 34.9862 | 33.0255 | 34.2704 | 34.4387 | 34.4423 | 34.3858 | 34.3415 | 34.3077 | 33.9467 | 34.3594 | 35.8184 | 35.2026 | 36.2489 | 36.1987 | 33.528 | 94.4676 | 94.8311 | 93.939
2022-09-08 03:14 | 5:24 | 17.6318 | 18.0086 | 20.6113 | 34.8244 | 34.3854 | 33.846 | 34.6489 | 35.4083 | 36.5408 | 37.3017 | 36.8547 | 37.9081 | 34.3227 | 34.2906 | 34.195 | 35.083 | 35.1952 | 35.5866 | 36.2928 | 36.6116 | 21.0455 | 17.2569 | 93.9002 | 33.3392 | 33.0811 | 35.0646 | 33.4073 | 33.0845 | 33.4496 | 34.7974 | 34.3107 | 34.1009 | 37.2206 | 36.2774 | 33.447 | 34.3901 | 36.2756 | 36.5309 | 37.4267 | 36.2732 | 33.3885 | 32.6137 | 34.4356 | 34.9763 | 33.0354 | 34.2681 | 34.4251 | 34.443 | 34.3832 | 34.3632 | 34.314 | 33.9428 | 34.3858 | 35.838 | 35.1996 | 36.2221 | 36.2037 | 33.522 | 94.3071 | 94.6867 | 93.8706
2022-09-08 03:14 | 5:24 | 17.6031 | 18.0054 | 20.5487 | 34.7275 | 34.4085 | 33.8524 | 34.6497 | 35.4225 | 36.5406 | 37.2925 | 36.8635 | 37.8941 | 34.3273 | 34.2847 | 34.1938 | 35.0943 | 35.1843 | 35.5769 | 36.2964 | 36.6221 | 21.0678 | 17.222 | 93.8281 | 33.3962 | 33.1061 | 35.0778 | 33.3987 | 33.09 | 33.4573 | 34.8017 | 34.3388 | 34.1166 | 37.2151 | 36.2735 | 33.4487 | 34.3825 | 36.2688 | 36.5347 | 37.3941 | 36.2669 | 33.3913 | 32.6117 | 34.4375 | 34.9634 | 33.0187 | 34.2561 | 34.4089 | 34.4518 | 34.4034 | 34.3614 | 34.3132 | 33.9532 | 34.3832 | 35.8122 | 35.1667 | 36.2244 | 36.1995 | 33.5389 | 94.1966 | 94.5581 | 93.7851
2022-09-08 03:14 | 5:24 | 17.5342 | 17.9155 | 20.5288 | 34.5918 | 34.3962 | 33.8369 | 34.6466 | 35.4141 | 36.5422 | 37.2717 | 36.8564 | 37.9069 | 34.3233 | 34.2827 | 34.1843 | 35.0778 | 35.1618 | 35.5826 | 36.2963 | 36.6287 | 21.1059 | 17.2419 | 93.807 | 33.2194 | 33.0812 | 35.075 | 33.3973 | 33.0847 | 33.4456 | 34.7907 | 34.3327 | 34.1032 | 37.1921 | 36.2821 | 33.4606 | 34.3954 | 36.2774 | 36.5255 | 37.4113 | 36.2617 | 33.3832 | 32.5977 | 34.4232 | 34.9523 | 33.0214 | 34.2619 | 34.423 | 34.437 | 34.3836 | 34.3662 | 34.2918 | 33.9494 | 34.4034 | 35.8116 | 35.1906 | 36.2413 | 36.2217 | 33.5005 | 94.1405 | 94.4686 | 93.7968
2022-09-08 03:15 | 5:24 | 17.5656 | 17.8537 | 20.5574 | 34.6341 | 34.3828 | 33.8433 | 34.6427 | 35.4084 | 36.5376 | 37.2885 | 36.8608 | 37.9231 | 34.3017 | 34.2799 | 34.1609 | 35.0714 | 35.1797 | 35.5846 | 36.297 | 36.6285 | 21.0998 | 17.2534 | 93.8253 | 33.3919 | 33.0822 | 35.0634 | 33.4056 | 33.0759 | 33.4608 | 34.7969 | 34.3407 | 34.1031 | 37.2201 | 36.2811 | 33.4548 | 34.3843 | 36.2735 | 36.5469 | 37.3868 | 36.2756 | 33.4 | 32.599 | 34.4198 | 34.9562 | 33.026 | 34.2527 | 34.4268 | 34.4467 | 34.392 | 34.3685 | 34.2875 | 33.9534 | 34.3836 | 35.808 | 35.1987 | 36.2446 | 36.2024 | 33.5147 | 94.1101 | 94.3705 | 93.8307
2022-09-08 03:15 | 5:25 | 17.534 | 17.9313 | 20.5628 | 34.5252 | 34.371 | 33.8519 | 34.641 | 35.4072 | 36.5409 | 37.2801 | 36.8649 | 37.9145 | 34.3313 | 34.2827 | 34.1754 | 35.0679 | 35.1575 | 35.5746 | 36.2914 | 36.6095 | 21.1318 | 17.2154 | 93.7749 | 33.3877 | 33.0699 | 35.0656 | 33.3885 | 33.0733 | 33.447 | 34.7945 | 34.3453 | 34.1012 | 37.2218 | 36.2795 | 33.4415 | 34.3993 | 36.2821 | 36.5457 | 37.3996 | 36.2688 | 33.3999 | 32.5818 | 34.4052 | 34.964 | 33.0156 | 34.2639 | 34.4294 | 34.429 | 34.3863 | 34.3496 | 34.292 | 33.938 | 34.392 | 35.8103 | 35.2136 | 36.2331 | 36.1829 | 33.5068 | 94.0044 | 94.2663 | 93.7432
2022-09-08 03:15 | 5:25 | 17.5216 | 17.8944 | 20.5293 | 34.575 | 34.3776 | 33.8524 | 34.6321 | 35.4068 | 36.5495 | 37.2693 | 36.8487 | 37.9265 | 34.3329 | 34.2812 | 34.1828 | 35.0806 | 35.1733 | 35.563 | 36.2642 | 36.6209 | 21.1269 | 17.1726 | 93.7566 | 33.3556 | 33.0704 | 35.0488 | 33.3913 | 33.0663 | 33.4487 | 34.7911 | 34.3272 | 34.1016 | 37.2173 | 36.2684 | 33.4559 | 34.3841 | 36.2811 | 36.5284 | 37.3961 | 36.2774 | 33.3946 | 32.6038 | 34.4021 | 34.9429 | 33.0017 | 34.2508 | 34.4154 | 34.4404 | 34.3792 | 34.3672 | 34.2984 | 33.9434 | 34.3863 | 35.8133 | 35.1821 | 36.2379 | 36.2049 | 33.5292 | 93.9413 | 94.1858 | 93.7063
2022-09-08 03:15 | 5:25 | 17.4855 | 17.8337 | 20.4583 | 34.6091 | 34.3658 | 33.8493 | 34.6447 | 35.4101 | 36.5465 | 37.2811 | 36.8552 | 37.9258 | 34.3225 | 34.2935 | 34.1758 | 35.0698 | 35.1797 | 35.5676 | 36.2894 | 36.5932 | 21.1626 | 17.2025 | 93.6692 | 33.2097 | 33.0693 | 35.0595 | 33.3832 | 33.0611 | 33.4606 | 34.7989 | 34.3519 | 34.1009 | 37.2214 | 36.2859 | 33.4354 | 34.3876 | 36.2795 | 36.5453 | 37.3926 | 36.2735 | 33.3976 | 32.5876 | 34.4123 | 34.9611 | 33.0102 | 34.2626 | 34.4115 | 34.4295 | 34.3816 | 34.3824 | 34.3025 | 33.9271 | 34.3792 | 35.8004 | 35.2078 | 36.2389 | 36.2003 | 33.4837 | 93.8977 | 94.1333 | 93.6111
2022-09-08 03:15 | 5:25 | 17.4068 | 17.789 | 20.4704 | 34.5096 | 34.3654 | 33.8601 | 34.6414 | 35.3994 | 36.54 | 37.267 | 36.8454 | 37.9367 | 34.313 | 34.3064 | 34.1638 | 35.0839 | 35.1671 | 35.5872 | 36.2614 | 36.6213 | 21.1352 | 17.1741 | 93.7177 | 33.3084 | 33.08 | 35.0734 | 33.4 | 33.0656 | 33.4548 | 34.7987 | 34.3383 | 34.1216 | 37.2111 | 36.2701 | 33.4507 | 34.398 | 36.2684 | 36.5269 | 37.3867 | 36.2821 | 33.3848 | 32.5708 | 34.3902 | 34.9327 | 32.9931 | 34.2634 | 34.4068 | 34.4351 | 34.4022 | 34.3666 | 34.2946 | 33.9417 | 34.3816 | 35.816 | 35.1943 | 36.2508 | 36.2019 | 33.4959 | 93.8663 | 94.1089 | 93.698
2022-09-08 03:15 | 5:25 | 17.4233 | 17.8031 | 20.416 | 34.4874 | 34.3778 | 33.8644 | 34.6434 | 35.4201 | 36.5422 | 37.2812 | 36.8611 | 37.9206 | 34.3182 | 34.2832 | 34.1738 | 35.0785 | 35.1844 | 35.5709 | 36.2666 | 36.6107 | 21.1137 | 17.1144 | 93.7602 | 33.2373 | 33.0681 | 35.0866 | 33.3999 | 33.0733 | 33.4415 | 34.7809 | 34.3495 | 34.1134 | 37.2207 | 36.25 | 33.4594 | 34.396 | 36.2859 | 36.5253 | 37.3897 | 36.2811 | 33.3892 | 32.5656 | 34.3993 | 34.9347 | 32.996 | 34.2439 | 34.425 | 34.4223 | 34.418 | 34.366 | 34.2906 | 33.9205 | 34.4022 | 35.8072 | 35.1869 | 36.2412 | 36.1754 | 33.5062 | 93.8357 | 94.0553 | 93.6911
2022-09-08 03:16 | 5:26 | 17.3932 | 17.7625 | 20.3029 | 34.5216 | 34.3642 | 33.8495 | 34.6423 | 35.4193 | 36.5293 | 37.2607 | 36.8633 | 37.9343 | 34.338 | 34.3067 | 34.1654 | 35.0807 | 35.1603 | 35.5688 | 36.2763 | 36.6032 | 21.1132 | 17.1133 | 93.6583 | 33.3186 | 33.0568 | 35.0707 | 33.3946 | 33.0767 | 33.4559 | 34.7987 | 34.3507 | 34.1062 | 37.2161 | 36.2893 | 33.4466 | 34.4049 | 36.2701 | 36.5315 | 37.3915 | 36.2795 | 33.3768 | 32.5734 | 34.3971 | 34.946 | 33.0119 | 34.2523 | 34.4166 | 34.4075 | 34.3974 | 34.355 | 34.2902 | 33.915 | 34.418 | 35.8139 | 35.1905 | 36.2505 | 36.188 | 33.4941 | 93.7745 | 94.0139 | 93.5784
2022-09-08 03:16 | 5:26 | 17.4046 | 17.7376 | 20.2027 | 34.5267 | 34.359 | 33.8561 | 34.6525 | 35.4156 | 36.5437 | 37.2678 | 36.8773 | 37.9329 | 34.3344 | 34.304 | 34.1812 | 35.0681 | 35.1919 | 35.5707 | 36.2698 | 36.613 | 21.1133 | 17.1035 | 93.5488 | 33.1431 | 33.0488 | 35.0497 | 33.3976 | 33.0681 | 33.4354 | 34.7921 | 34.3602 | 34.1256 | 37.2043 | 36.2811 | 33.4517 | 34.4001 | 36.25 | 36.538 | 37.3864 | 36.2684 | 33.3815 | 32.5624 | 34.3857 | 34.9457 | 33.0011 | 34.2518 | 34.4046 | 34.4201 | 34.3967 | 34.3646 | 34.2858 | 33.9168 | 34.3974 | 35.8078 | 35.1915 | 36.2505 | 36.2048 | 33.5022 | 93.7056 | 93.9532 | 93.5003
2022-09-08 03:16 | 5:26 | 17.3749 | 17.7161 | 20.1943 | 34.5158 | 34.3712 | 33.8528 | 34.6424 | 35.4132 | 36.5498 | 37.2769 | 36.8708 | 37.9051 | 34.3374 | 34.3165 | 34.1669 | 35.0752 | 35.1702 | 35.5747 | 36.2549 | 36.6089 | 21.1238 | 17.0912 | 93.4976 | 33.1667 | 33.0819 | 35.0568 | 33.3848 | 33.0784 | 33.4507 | 34.7949 | 34.3557 | 34.1081 | 37.2091 | 36.2607 | 33.4463 | 34.4061 | 36.2893 | 36.5423 | 37.3822 | 36.2859 | 33.4007 | 32.5602 | 34.3793 | 34.9256 | 32.9944 | 34.2437 | 34.3969 | 34.4168 | 34.3908 | 34.3808 | 34.286 | 33.9333 | 34.3967 | 35.8048 | 35.2107 | 36.2732 | 36.2015 | 33.4986 | 93.6181 | 93.877 | 93.4425
2022-09-08 03:16 | 5:26 | 17.4488 | 17.7768 | 20.2395 | 34.565 | 34.3432 | 33.8439 | 34.6321 | 35.4111 | 36.5495 | 37.2854 | 36.8621 | 37.9307 | 34.3303 | 34.296 | 34.1747 | 35.0783 | 35.1699 | 35.5836 | 36.2821 | 36.5948 | 21.0985 | 17.1283 | 93.4103 | 33.1275 | 33.0649 | 35.0695 | 33.3892 | 33.0909 | 33.4594 | 34.7899 | 34.345 | 34.1176 | 37.2066 | 36.2601 | 33.4529 | 34.4004 | 36.2811 | 36.5268 | 37.3785 | 36.2701 | 33.3954 | 32.5596 | 34.3758 | 34.9351 | 32.983 | 34.2599 | 34.3927 | 34.4184 | 34.4089 | 34.3791 | 34.2851 | 33.9105 | 34.3908 | 35.7975 | 35.218 | 36.2463 | 36.2053 | 33.507 | 93.5724 | 93.8002 | 93.4094
2022-09-08 03:16 | 5:26 | 17.3923 | 17.7351 | 20.3157 | 34.5178 | 34.3388 | 33.8651 | 34.6482 | 35.4202 | 36.5444 | 37.2808 | 36.8723 | 37.9188 | 34.3228 | 34.2982 | 34.166 | 35.0968 | 35.1725 | 35.5662 | 36.2697 | 36.6006 | 21.0973 | 17.1114 | 93.4728 | 33.1615 | 33.0597 | 35.0778 | 33.3768 | 33.0826 | 33.4466 | 34.7782 | 34.3503 | 34.1298 | 37.2124 | 36.2574 | 33.4461 | 34.4035 | 36.2607 | 36.5279 | 37.3918 | 36.25 | 33.3893 | 32.5508 | 34.3585 | 34.9473 | 32.9819 | 34.2711 | 34.3927 | 34.4179 | 34.4226 | 34.3903 | 34.2716 | 33.9378 | 34.4089 | 35.8123 | 35.1979 | 36.2572 | 36.2113 | 33.5093 | 93.5203 | 93.7024 | 93.3951
2022-09-08 03:16 | 5:26 | 17.2863 | 17.6601 | 20.2937 | 34.5078 | 34.3559 | 33.8415 | 34.6322 | 35.4139 | 36.5465 | 37.2726 | 36.8971 | 37.9361 | 34.3372 | 34.3148 | 34.1662 | 35.0785 | 35.1538 | 35.576 | 36.2596 | 36.6146 | 21.0848 | 17.0693 | 93.4103 | 33.1911 | 33.0598 | 35.0817 | 33.3815 | 33.0785 | 33.4517 | 34.7852 | 34.3422 | 34.1047 | 37.2208 | 36.2742 | 33.4437 | 34.4062 | 36.2601 | 36.5482 | 37.3809 | 36.2893 | 33.3947 | 32.57 | 34.3691 | 34.9211 | 32.9838 | 34.2577 | 34.3944 | 34.3846 | 34.4184 | 34.3563 | 34.2707 | 33.9219 | 34.4226 | 35.8023 | 35.1968 | 36.2362 | 36.2015 | 33.4905 | 93.4187 | 93.6261 | 93.3026
2022-09-08 03:17 | 5:26 | 17.2908 | 17.6815 | 20.2241 | 34.6139 | 34.3475 | 33.8478 | 34.641 | 35.4175 | 36.5414 | 37.2672 | 36.8873 | 37.9296 | 34.3556 | 34.2949 | 34.1805 | 35.0761 | 35.1556 | 35.5753 | 36.2568 | 36.5955 | 21.0669 | 16.9918 | 93.3452 | 33.1137 | 33.0606 | 35.0807 | 33.4007 | 33.0737 | 33.4463 | 34.7876 | 34.3406 | 34.1218 | 37.2248 | 36.2623 | 33.4434 | 34.4073 | 36.2574 | 36.5515 | 37.3781 | 36.2811 | 33.3823 | 32.5517 | 34.3528 | 34.9335 | 32.953 | 34.2525 | 34.4015 | 34.3978 | 34.4196 | 34.3596 | 34.2963 | 33.9273 | 34.4184 | 35.8207 | 35.2009 | 36.2528 | 36.209 | 33.4928 | 93.3334 | 93.5129 | 93.2641
2022-09-08 03:17 | 5:27 | 17.2757 | 17.6252 | 20.2043 | 34.4445 | 34.3447 | 33.8608 | 34.6371 | 35.4162 | 36.5459 | 37.2377 | 36.8718 | 37.9408 | 34.3421 | 34.3084 | 34.1742 | 35.0691 | 35.179 | 35.5549 | 36.2701 | 36.5969 | 21.0526 | 17.0244 | 93.2014 | 33.1629 | 33.0598 | 35.0627 | 33.3954 | 33.0761 | 33.4529 | 34.7825 | 34.3596 | 34.1101 | 37.2115 | 36.2757 | 33.4403 | 34.4102 | 36.2742 | 36.5543 | 37.3837 | 36.2607 | 33.376 | 32.5521 | 34.3652 | 34.9236 | 32.9721 | 34.2627 | 34.3947 | 34.3915 | 34.4232 | 34.3643 | 34.2767 | 33.9203 | 34.4196 | 35.8182 | 35.1952 | 36.2586 | 36.1937 | 33.4801 | 93.1875 | 93.3701 | 93.0629
2022-09-08 03:17 | 5:27 | 17.235 | 17.6018 | 20.1924 | 34.5767 | 34.3582 | 33.8666 | 34.6209 | 35.4045 | 36.5365 | 37.2681 | 36.8906 | 37.9537 | 34.3439 | 34.2919 | 34.1707 | 35.0673 | 35.1627 | 35.5563 | 36.267 | 36.6059 | 21.0315 | 17.0167 | 93.1235 | 33.2113 | 33.0371 | 35.0701 | 33.3893 | 33.0827 | 33.4461 | 34.7876 | 34.3466 | 34.0949 | 37.2163 | 36.2591 | 33.4609 | 34.4219 | 36.2623 | 36.5305 | 37.3747 | 36.2601 | 33.3787 | 32.5289 | 34.3494 | 34.9449 | 32.9698 | 34.2715 | 34.4125 | 34.4027 | 34.4102 | 34.3538 | 34.2881 | 33.9332 | 34.4232 | 35.8355 | 35.1948 | 36.2622 | 36.1949 | 33.4885 | 93.0585 | 93.269 | 93.0262
2022-09-08 03:17 | 5:27 | 17.2495 | 17.613 | 20.1439 | 34.5461 | 34.3384 | 33.8716 | 34.6248 | 35.4181 | 36.5249 | 37.2805 | 36.8917 | 37.9509 | 34.3364 | 34.3071 | 34.163 | 35.0905 | 35.1655 | 35.5765 | 36.2655 | 36.5973 | 21.0187 | 16.9859 | 93.0728 | 33.1398 | 33.0678 | 35.0685 | 33.3947 | 33.0885 | 33.4437 | 34.7851 | 34.3653 | 34.1142 | 37.2216 | 36.2654 | 33.4401 | 34.4123 | 36.2757 | 36.5564 | 37.371 | 36.2574 | 33.3815 | 32.554 | 34.3828 | 34.9299 | 32.9475 | 34.2733 | 34.4137 | 34.404 | 34.4409 | 34.3796 | 34.2839 | 33.9211 | 34.4102 | 35.8356 | 35.2041 | 36.2591 | 36.2014 | 33.4951 | 92.9616 | 93.1606 | 93.0055
2022-09-08 03:17 | 5:27 | 17.3023 | 17.6108 | 20.1792 | 34.4964 | 34.3388 | 33.8456 | 34.6288 | 35.4174 | 36.5328 | 37.2886 | 36.8751 | 37.9333 | 34.3341 | 34.3096 | 34.161 | 35.0774 | 35.1701 | 35.5816 | 36.2653 | 36.6158 | 21.0127 | 17.0185 | 92.9844 | 33.1637 | 33.0537 | 35.0621 | 33.3823 | 33.0638 | 33.4434 | 34.7852 | 34.3397 | 34.1181 | 37.2197 | 36.2575 | 33.4507 | 34.4138 | 36.2591 | 36.5406 | 37.3788 | 36.2742 | 33.3801 | 32.5302 | 34.3471 | 34.9353 | 32.9272 | 34.2696 | 34.3845 | 34.394 | 34.4239 | 34.3631 | 34.2905 | 33.8986 | 34.4409 | 35.836 | 35.2046 | 36.244 | 36.2059 | 33.5046 | 92.8271 | 93.0763 | 92.8723
2022-09-08 03:17 | 5:27 | 17.225 | 17.4922 | 20.143 | 34.394 | 34.3219 | 33.8692 | 34.6325 | 35.403 | 36.5437 | 37.2692 | 36.8724 | 37.9561 | 34.3359 | 34.3162 | 34.165 | 35.0975 | 35.1635 | 35.5885 | 36.2638 | 36.6371 | 20.9998 | 16.9718 | 92.9227 | 33.078 | 33.0594 | 35.078 | 33.376 | 33.0737 | 33.4403 | 34.7622 | 34.3508 | 34.1254 | 37.2137 | 36.2629 | 33.448 | 34.3802 | 36.2654 | 36.5431 | 37.3795 | 36.2623 | 33.3721 | 32.5383 | 34.3496 | 34.9414 | 32.9409 | 34.2707 | 34.4024 | 34.3853 | 34.4106 | 34.3827 | 34.2812 | 33.9108 | 34.4239 | 35.8207 | 35.1867 | 36.2656 | 36.2015 | 33.5026 | 92.7648 | 92.935 | 92.8147
2022-09-08 03:18 | 5:28 | 17.154 | 17.4876 | 20.1321 | 34.4426 | 34.3218 | 33.865 | 34.6268 | 35.423 | 36.5462 | 37.2776 | 36.9101 | 37.9495 | 34.3354 | 34.321 | 34.1752 | 35.0826 | 35.1672 | 35.5627 | 36.2725 | 36.6033 | 20.9722 | 16.889 | 92.8096 | 33.1198 | 33.0382 | 35.0645 | 33.3787 | 33.0709 | 33.4609 | 34.7824 | 34.3524 | 34.1173 | 37.215 | 36.2605 | 33.4546 | 34.428 | 36.2575 | 36.5558 | 37.383 | 36.2757 | 33.3685 | 32.5195 | 34.3372 | 34.9351 | 32.914 | 34.2944 | 34.391 | 34.4028 | 34.4389 | 34.3615 | 34.2769 | 33.9368 | 34.4106 | 35.8334 | 35.1953 | 36.2622 | 36.2097 | 33.498 | 92.6846 | 92.8567 | 92.8113
2022-09-08 03:18 | 5:28 | 17.2115 | 17.4613 | 20.1062 | 34.3572 | 34.3323 | 33.8855 | 34.6494 | 35.4125 | 36.549 | 37.2629 | 36.897 | 37.9474 | 34.3367 | 34.3144 | 34.1779 | 35.087 | 35.1531 | 35.5533 | 36.2601 | 36.6078 | 20.9712 | 16.9359 | 92.7445 | 33.1596 | 33.0437 | 35.0707 | 33.3815 | 33.0819 | 33.4401 | 34.7757 | 34.3732 | 34.1131 | 37.2194 | 36.2549 | 33.4239 | 34.417 | 36.2629 | 36.5384 | 37.3798 | 36.2591 | 33.3769 | 32.5131 | 34.3462 | 34.939 | 32.9394 | 34.2814 | 34.3988 | 34.3963 | 34.4553 | 34.3912 | 34.2715 | 33.9179 | 34.4389 | 35.8466 | 35.1992 | 36.2421 | 36.2238 | 33.4941 | 92.6005 | 92.7193 | 92.6393
2022-09-08 03:18 | 5:28 | 17.1499 | 17.4804 | 20.0745 | 34.4208 | 34.345 | 33.8589 | 34.6342 | 35.4157 | 36.5328 | 37.2743 | 36.8926 | 37.956 | 34.3326 | 34.318 | 34.1526 | 35.0785 | 35.1564 | 35.5704 | 36.2734 | 36.6273 | 20.9624 | 16.8907 | 92.6833 | 33.1335 | 33.0391 | 35.0702 | 33.3801 | 33.0603 | 33.4507 | 34.7856 | 34.3802 | 34.1118 | 37.2303 | 36.2563 | 33.4311 | 34.4171 | 36.2605 | 36.557 | 37.3789 | 36.2654 | 33.3677 | 32.5236 | 34.3713 | 34.9065 | 32.934 | 34.296 | 34.4069 | 34.3786 | 34.423 | 34.3688 | 34.2877 | 33.9251 | 34.4553 | 35.8441 | 35.193 | 36.2713 | 36.2079 | 33.5048 | 92.5127 | 92.5952 | 92.623
2022-09-08 03:18 | 5:28 | 17.0888 | 17.4667 | 20.082 | 34.4076 | 34.3195 | 33.8698 | 34.6414 | 35.418 | 36.5419 | 37.27 | 36.893 | 37.955 | 34.3327 | 34.3345 | 34.1535 | 35.0733 | 35.1553 | 35.5734 | 36.2605 | 36.6072 | 20.9324 | 16.8492 | 92.5986 | 33.1092 | 33.0226 | 35.0606 | 33.3721 | 33.0583 | 33.448 | 34.7794 | 34.3579 | 34.1203 | 37.2289 | 36.2432 | 33.4359 | 34.4051 | 36.2549 | 36.5568 | 37.3803 | 36.2575 | 33.3526 | 32.521 | 34.348 | 34.9265 | 32.9415 | 34.2778 | 34.3873 | 34.3816 | 34.4346 | 34.3942 | 34.2848 | 33.9059 | 34.423 | 35.8316 | 35.2069 | 36.272 | 36.2123 | 33.4963 | 92.4178 | 92.4689 | 92.6034
2022-09-08 03:18 | 5:28 | 17.0011 | 17.3065 | 20.0257 | 34.357 | 34.3116 | 33.8759 | 34.6298 | 35.4253 | 36.5264 | 37.2686 | 36.8932 | 37.9538 | 34.3509 | 34.3127 | 34.1587 | 35.0849 | 35.1549 | 35.5704 | 36.256 | 36.5977 | 20.9259 | 16.7993 | 92.608 | 33.0162 | 33.0482 | 35.061 | 33.3685 | 33.0551 | 33.4546 | 34.7795 | 34.3477 | 34.1325 | 37.2274 | 36.229 | 33.433 | 34.43 | 36.2563 | 36.5638 | 37.3962 | 36.2629 | 33.3703 | 32.5171 | 34.345 | 34.9308 | 32.9116 | 34.2818 | 34.3816 | 34.3742 | 34.4469 | 34.4051 | 34.2906 | 33.9087 | 34.4346 | 35.8212 | 35.2019 | 36.238 | 36.2146 | 33.5293 | 92.2773 | 92.3849 | 92.4027
2022-09-08 03:18 | 5:28 | 16.9966 | 17.297 | 20.0139 | 34.3052 | 34.3142 | 33.8567 | 34.6327 | 35.4235 | 36.5221 | 37.264 | 36.8701 | 37.9444 | 34.3416 | 34.3299 | 34.1548 | 35.0962 | 35.1609 | 35.5588 | 36.2583 | 36.6166 | 20.9031 | 16.8 | 92.4541 | 33.0938 | 33.0541 | 35.0493 | 33.3769 | 33.0591 | 33.4239 | 34.774 | 34.353 | 34.1305 | 37.2332 | 36.2371 | 33.4472 | 34.4116 | 36.2432 | 36.5458 | 37.3788 | 36.2605 | 33.3599 | 32.5272 | 34.3488 | 34.9266 | 32.8998 | 34.2649 | 34.398 | 34.369 | 34.4279 | 34.3891 | 34.2847 | 33.9129 | 34.4469 | 35.8599 | 35.1915 | 36.2635 | 36.2302 | 33.5035 | 92.1457 | 92.2621 | 92.4031
2022-09-08 03:19 | 5:28 | 17.0115 | 17.3324 | 19.9488 | 34.3623 | 34.3204 | 33.874 | 34.6302 | 35.4229 | 36.5406 | 37.2865 | 36.8822 | 37.948 | 34.3402 | 34.3448 | 34.1589 | 35.0923 | 35.1674 | 35.5682 | 36.2413 | 36.6179 | 20.878 | 16.8083 | 92.4786 | 33.1329 | 33.0388 | 35.0489 | 33.3677 | 33.0682 | 33.4311 | 34.789 | 34.365 | 34.1204 | 37.2341 | 36.2316 | 33.4251 | 34.4223 | 36.229 | 36.523 | 37.3817 | 36.2549 | 33.3648 | 32.4846 | 34.36 | 34.9284 | 32.8999 | 34.2739 | 34.3923 | 34.3625 | 34.4279 | 34.3939 | 34.2827 | 33.9228 | 34.4279 | 35.8407 | 35.2048 | 36.2588 | 36.2251 | 33.5119 | 92.164 | 92.287 | 92.4354
2022-09-08 03:19 | 5:29 | 16.9929 | 17.3284 | 19.9505 | 34.3601 | 34.3077 | 33.8573 | 34.6332 | 35.4127 | 36.5326 | 37.279 | 36.895 | 37.9586 | 34.3494 | 34.3212 | 34.1628 | 35.0817 | 35.1629 | 35.582 | 36.2708 | 36.6352 | 20.8805 | 16.7962 | 92.5376 | 33.0894 | 33.0359 | 35.0561 | 33.3526 | 33.0649 | 33.4359 | 34.7829 | 34.3541 | 34.123 | 37.2217 | 36.2563 | 33.435 | 34.4248 | 36.2371 | 36.5346 | 37.3877 | 36.2563 | 33.352 | 32.5 | 34.3283 | 34.9216 | 32.8919 | 34.2853 | 34.3978 | 34.3686 | 34.4199 | 34.4034 | 34.2799 | 33.9172 | 34.4279 | 35.8401 | 35.1817 | 36.2728 | 36.2125 | 33.4956 | 92.2912 | 92.3761 | 92.4762
2022-09-08 03:19 | 5:29 | 17.0461 | 17.3095 | 19.8913 | 34.4227 | 34.314 | 33.8624 | 34.6345 | 35.4271 | 36.562 | 37.2653 | 36.8808 | 37.9655 | 34.3382 | 34.3263 | 34.172 | 35.086 | 35.1654 | 35.5773 | 36.2575 | 36.6201 | 20.8514 | 16.7464 | 92.602 | 33.1867 | 33.0262 | 35.0484 | 33.3703 | 33.0557 | 33.433 | 34.7956 | 34.3711 | 34.1218 | 37.2462 | 36.245 | 33.4328 | 34.4215 | 36.2316 | 36.5619 | 37.3734 | 36.2432 | 33.3415 | 32.5202 | 34.3236 | 34.9203 | 32.9025 | 34.2891 | 34.3691 | 34.3632 | 34.4316 | 34.3994 | 34.2827 | 33.9101 | 34.4199 | 35.8515 | 35.1949 | 36.2698 | 36.2216 | 33.5153 | 92.3418 | 92.4523 | 92.607
2022-09-08 03:19 | 5:29 | 16.9939 | 17.3486 | 19.8888 | 34.3174 | 34.3132 | 33.8629 | 34.6223 | 35.428 | 36.5462 | 37.2825 | 36.8958 | 37.967 | 34.3397 | 34.3437 | 34.1779 | 35.0848 | 35.1584 | 35.568 | 36.2617 | 36.6216 | 20.8376 | 16.7939 | 92.6826 | 32.9774 | 33.033 | 35.0724 | 33.3599 | 33.05 | 33.4472 | 34.7619 | 34.362 | 34.1031 | 37.2128 | 36.2474 | 33.4291 | 34.4224 | 36.2563 | 36.5434 | 37.3791 | 36.229 | 33.3542 | 32.4901 | 34.3239 | 34.9183 | 32.8715 | 34.2936 | 34.3905 | 34.3732 | 34.4469 | 34.3919 | 34.2812 | 33.8925 | 34.4316 | 35.8424 | 35.1965 | 36.2626 | 36.2187 | 33.5009 | 92.4076 | 92.5599 | 92.6599
2022-09-08 03:19 | 5:29 | 17.0848 | 17.3384 | 19.8912 | 34.4057 | 34.2918 | 33.8664 | 34.6361 | 35.4251 | 36.5359 | 37.2786 | 36.8767 | 37.9593 | 34.3627 | 34.331 | 34.1685 | 35.0773 | 35.1523 | 35.5751 | 36.2549 | 36.6054 | 20.8187 | 16.7995 | 92.7269 | 33.0832 | 33.0319 | 35.052 | 33.3648 | 33.0589 | 33.4251 | 34.7907 | 34.3613 | 34.1065 | 37.2158 | 36.2226 | 33.4218 | 34.4181 | 36.245 | 36.5479 | 37.3768 | 36.2371 | 33.3199 | 32.4751 | 34.3199 | 34.934 | 32.8499 | 34.2927 | 34.3845 | 34.3588 | 34.4431 | 34.3947 | 34.2935 | 33.9007 | 34.4469 | 35.8269 | 35.1737 | 36.2603 | 36.2091 | 33.5103 | 92.5023 | 92.6839 | 92.6701
2022-09-08 03:19 | 5:29 | 16.9622 | 17.2843 | 19.7708 | 34.386 | 34.2875 | 33.8662 | 34.6263 | 35.4102 | 36.5275 | 37.2768 | 36.8874 | 37.9492 | 34.3474 | 34.3357 | 34.1668 | 35.0836 | 35.1529 | 35.5641 | 36.2451 | 36.6369 | 20.8002 | 16.7812 | 92.6991 | 33.0567 | 33.0266 | 35.027 | 33.352 | 33.041 | 33.435 | 34.7795 | 34.3674 | 34.1013 | 37.2229 | 36.2277 | 33.4267 | 34.4007 | 36.2474 | 36.5573 | 37.3897 | 36.2316 | 33.3146 | 32.4995 | 34.32 | 34.9281 | 32.8429 | 34.2907 | 34.3658 | 34.3777 | 34.4472 | 34.4015 | 34.3064 | 33.9179 | 34.4431 | 35.8417 | 35.184 | 36.2683 | 36.2323 | 33.5046 | 92.5646 | 92.7675 | 92.7379
2022-09-08 03:20 | 5:29 | 16.9245 | 17.1767 | 19.7765 | 34.4138 | 34.292 | 33.875 | 34.6202 | 35.4138 | 36.5395 | 37.291 | 36.8864 | 37.9467 | 34.3434 | 34.3207 | 34.1526 | 35.0631 | 35.1556 | 35.5894 | 36.2621 | 36.616 | 20.7533 | 16.6867 | 92.8216 | 33.0644 | 33.007 | 35.0241 | 33.3415 | 33.0623 | 33.4328 | 34.776 | 34.3618 | 34.0982 | 37.2291 | 36.228 | 33.4172 | 34.4046 | 36.2226 | 36.5531 | 37.3722 | 36.2563 | 33.3357 | 32.487 | 34.3396 | 34.9022 | 32.8473 | 34.2996 | 34.3918 | 34.3644 | 34.4273 | 34.3819 | 34.2832 | 33.9069 | 34.4472 | 35.8359 | 35.1899 | 36.2767 | 36.2061 | 33.5122 | 92.7251 | 92.8417 | 92.864
2022-09-08 03:20 | 5:30 | 16.8409 | 17.1496 | 19.7947 | 34.2122 | 34.2984 | 33.859 | 34.6257 | 35.4298 | 36.5287 | 37.2655 | 36.8843 | 37.9447 | 34.3519 | 34.3302 | 34.1683 | 35.0689 | 35.1405 | 35.5708 | 36.2435 | 36.604 | 20.7364 | 16.6544 | 92.9134 | 32.993 | 33.0257 | 35.0125 | 33.3542 | 33.0543 | 33.4291 | 34.766 | 34.3648 | 34.0867 | 37.2201 | 36.2164 | 33.4288 | 34.3986 | 36.2277 | 36.5551 | 37.3645 | 36.245 | 33.3245 | 32.4735 | 34.3192 | 34.8934 | 32.8589 | 34.3058 | 34.3617 | 34.3685 | 34.4391 | 34.3962 | 34.3067 | 33.914 | 34.4273 | 35.8287 | 35.1767 | 36.2753 | 36.2268 | 33.5102 | 92.8339 | 92.9624 | 92.9329
2022-09-08 03:20 | 5:30 | 16.8526 | 17.1389 | 19.7943 | 34.2757 | 34.3025 | 33.8428 | 34.6097 | 35.4103 | 36.5299 | 37.2807 | 36.8766 | 37.9471 | 34.3529 | 34.3411 | 34.1749 | 35.0787 | 35.1375 | 35.5574 | 36.2476 | 36.6127 | 20.6933 | 16.6518 | 92.9839 | 33.1218 | 33.0278 | 35.0185 | 33.3199 | 33.0333 | 33.4218 | 34.7743 | 34.3436 | 34.1057 | 37.2091 | 36.2156 | 33.4194 | 34.4027 | 36.228 | 36.5338 | 37.3745 | 36.2474 | 33.3066 | 32.4643 | 34.3036 | 34.9178 | 32.8546 | 34.2985 | 34.3536 | 34.3754 | 34.4219 | 34.4025 | 34.304 | 33.8991 | 34.4391 | 35.8362 | 35.1755 | 36.2636 | 36.2181 | 33.4935 | 92.8935 | 93.0556 | 92.9368
2022-09-08 03:20 | 5:30 | 16.821 | 17.1097 | 19.7437 | 34.2829 | 34.2946 | 33.8496 | 34.6227 | 35.4136 | 36.5471 | 37.2804 | 36.8783 | 37.9643 | 34.3565 | 34.3387 | 34.1484 | 35.0719 | 35.1395 | 35.5682 | 36.2369 | 36.6077 | 20.6648 | 16.6321 | 93.0413 | 33.1157 | 33.0297 | 35.0172 | 33.3146 | 33.0312 | 33.4267 | 34.7964 | 34.3271 | 34.1062 | 37.2099 | 36.2048 | 33.4132 | 34.3958 | 36.2164 | 36.528 | 37.3742 | 36.2226 | 33.3067 | 32.4754 | 34.3036 | 34.9162 | 32.8342 | 34.3169 | 34.3628 | 34.3604 | 34.4269 | 34.4213 | 34.3165 | 33.8796 | 34.4219 | 35.8543 | 35.1805 | 36.258 | 36.2299 | 33.4995 | 92.9626 | 93.243 | 93.0587
2022-09-08 03:20 | 5:30 | 16.8608 | 17.1423 | 19.7369 | 34.2039 | 34.2906 | 33.856 | 34.6137 | 35.4114 | 36.5337 | 37.2776 | 36.892 | 37.9368 | 34.3655 | 34.3405 | 34.1682 | 35.0643 | 35.1401 | 35.5566 | 36.2306 | 36.6126 | 20.6487 | 16.6235 | 93.0373 | 33.1214 | 33.0213 | 35.0251 | 33.3357 | 33.0347 | 33.4172 | 34.7792 | 34.3524 | 34.0898 | 37.2065 | 36.221 | 33.4149 | 34.3946 | 36.2156 | 36.5472 | 37.3781 | 36.2277 | 33.3185 | 32.4572 | 34.308 | 34.8914 | 32.8173 | 34.2959 | 34.3686 | 34.3679 | 34.4476 | 34.4119 | 34.296 | 33.8828 | 34.4269 | 35.8332 | 35.1748 | 36.2529 | 36.1839 | 33.5049 | 93.0519 | 93.3015 | 92.9999
2022-09-08 03:20 | 5:30 | 16.8615 | 17.1437 | 19.7821 | 34.3743 | 34.2902 | 33.8332 | 34.608 | 35.4177 | 36.5395 | 37.2747 | 36.8812 | 37.9348 | 34.347 | 34.3314 | 34.1593 | 35.0654 | 35.1469 | 35.5446 | 36.2304 | 36.6238 | 20.6281 | 16.628 | 93.1336 | 32.9924 | 33.0142 | 35.0155 | 33.3245 | 33.0397 | 33.4288 | 34.7741 | 34.3402 | 34.0877 | 37.205 | 36.2122 | 33.4151 | 34.3926 | 36.2048 | 36.5364 | 37.3782 | 36.228 | 33.318 | 32.4554 | 34.2848 | 34.8732 | 32.8115 | 34.2938 | 34.3774 | 34.3635 | 34.449 | 34.4074 | 34.2982 | 33.9024 | 34.4476 | 35.8268 | 35.1678 | 36.2719 | 36.2106 | 33.4905 | 93.2078 | 93.4241 | 93.1355
2022-09-08 03:21 | 5:31 | 16.7767 | 17.1122 | 19.6948 | 34.2825 | 34.2858 | 33.8557 | 34.6071 | 35.4066 | 36.5187 | 37.2711 | 36.8817 | 37.9429 | 34.3498 | 34.3627 | 34.1538 | 35.0658 | 35.1392 | 35.5459 | 36.2365 | 36.6191 | 20.6242 | 16.6163 | 93.1552 | 32.9527 | 33.0142 | 35.0022 | 33.3066 | 33.0379 | 33.4194 | 34.7637 | 34.3559 | 34.1118 | 37.2084 | 36.2158 | 33.4262 | 34.4068 | 36.221 | 36.5359 | 37.37 | 36.2164 | 33.3144 | 32.4526 | 34.2914 | 34.8922 | 32.8077 | 34.3121 | 34.3532 | 34.3662 | 34.4414 | 34.4132 | 34.3148 | 33.8865 | 34.449 | 35.8405 | 35.1572 | 36.2689 | 36.2048 | 33.4844 | 93.2245 | 93.4877 | 93.1653
2022-09-08 03:21 | 5:31 | 16.8048 | 17.1024 | 19.6652 | 34.2085 | 34.286 | 33.8374 | 34.5999 | 35.4134 | 36.536 | 37.2721 | 36.8615 | 37.9517 | 34.3728 | 34.3524 | 34.1409 | 35.0643 | 35.1305 | 35.556 | 36.2385 | 36.6232 | 20.5977 | 16.6162 | 93.1969 | 32.9358 | 33.0218 | 35.0003 | 33.3067 | 33.0356 | 33.4132 | 34.7702 | 34.3355 | 34.0925 | 37.209 | 36.2173 | 33.4221 | 34.3938 | 36.2122 | 36.5309 | 37.3751 | 36.2156 | 33.3112 | 32.4289 | 34.3051 | 34.8906 | 32.8079 | 34.3078 | 34.3604 | 34.3678 | 34.4258 | 34.4166 | 34.2949 | 33.8827 | 34.4414 | 35.8443 | 35.1794 | 36.2709 | 36.2105 | 33.4806 | 93.3151 | 93.6014 | 93.2325
2022-09-08 03:21 | 5:31 | 16.7781 | 17.0665 | 19.6455 | 34.2727 | 34.2851 | 33.8452 | 34.5989 | 35.4076 | 36.5337 | 37.2688 | 36.867 | 37.9349 | 34.3644 | 34.339 | 34.1511 | 35.0372 | 35.1241 | 35.5494 | 36.2295 | 36.6022 | 20.5865 | 16.597 | 93.2615 | 32.9935 | 33.012 | 35.0217 | 33.3185 | 33.0334 | 33.4149 | 34.771 | 34.3411 | 34.085 | 37.1817 | 36.1959 | 33.4214 | 34.4148 | 36.2158 | 36.5265 | 37.361 | 36.2048 | 33.3157 | 32.4455 | 34.2777 | 34.8638 | 32.7959 | 34.3231 | 34.3499 | 34.3684 | 34.4204 | 34.4133 | 34.3084 | 33.8663 | 34.4258 | 35.8311 | 35.155 | 36.2695 | 36.2098 | 33.4763 | 93.3949 | 93.6864 | 93.3331
2022-09-08 03:21 | 5:31 | 16.7946 | 17.0294 | 19.6823 | 34.2091 | 34.2716 | 33.8265 | 34.5951 | 35.3891 | 36.5202 | 37.2862 | 36.8845 | 37.9308 | 34.3415 | 34.3447 | 34.1495 | 35.0572 | 35.1236 | 35.5481 | 36.222 | 36.627 | 20.5432 | 16.5663 | 93.2994 | 32.9656 | 33.0215 | 35.016 | 33.318 | 33.0187 | 33.4151 | 34.7741 | 34.3366 | 34.0916 | 37.2138 | 36.1989 | 33.4139 | 34.39 | 36.2173 | 36.554 | 37.3645 | 36.221 | 33.2913 | 32.4316 | 34.2703 | 34.8748 | 32.7981 | 34.3181 | 34.3373 | 34.3735 | 34.4527 | 34.421 | 34.2919 | 33.8816 | 34.4204 | 35.8233 | 35.1688 | 36.2619 | 36.2091 | 33.4774 | 93.5437 | 93.7561 | 93.4534
2022-09-08 03:21 | 5:31 | 16.7325 | 17.0313 | 19.6047 | 34.2658 | 34.2707 | 33.8139 | 34.5927 | 35.4173 | 36.5471 | 37.263 | 36.8609 | 37.9436 | 34.3632 | 34.3445 | 34.1417 | 35.0372 | 35.1254 | 35.5552 | 36.2445 | 36.6133 | 20.5348 | 16.6073 | 93.411 | 32.8901 | 33.0096 | 35.0073 | 33.3144 | 33.0408 | 33.4262 | 34.7852 | 34.3277 | 34.0889 | 37.21 | 36.2032 | 33.4311 | 34.3765 | 36.1959 | 36.5328 | 37.3783 | 36.2122 | 33.3136 | 32.4284 | 34.2596 | 34.855 | 32.7912 | 34.3252 | 34.3479 | 34.3545 | 34.4404 | 34.4104 | 34.3071 | 33.8728 | 34.4527 | 35.8388 | 35.1585 | 36.2576 | 36.219 | 33.4732 | 93.7205 | 93.7904 | 93.5197
2022-09-08 03:21 | 5:31 | 16.8036 | 17.0599 | 19.6024 | 34.217 | 34.2963 | 33.8427 | 34.6065 | 35.4123 | 36.5241 | 37.2811 | 36.8638 | 37.9364 | 34.3614 | 34.3313 | 34.1523 | 35.0591 | 35.1206 | 35.5588 | 36.2131 | 36.6158 | 20.5271 | 16.5999 | 93.5129 | 32.9966 | 33.0013 | 35.0082 | 33.3112 | 33.0215 | 33.4221 | 34.7799 | 34.3353 | 34.099 | 37.1988 | 36.2078 | 33.4049 | 34.4009 | 36.1989 | 36.5255 | 37.369 | 36.2158 | 33.3029 | 32.4197 | 34.2709 | 34.862 | 32.7962 | 34.3314 | 34.3418 | 34.3578 | 34.4387 | 34.4134 | 34.3096 | 33.8784 | 34.4404 | 35.8186 | 35.1526 | 36.2734 | 36.2058 | 33.4785 | 93.8334 | 93.827 | 93.6494
2022-09-08 03:22 | 5:31 | 16.7569 | 17.045 | 19.5772 | 34.2771 | 34.2767 | 33.8182 | 34.6021 | 35.3974 | 36.5353 | 37.2816 | 36.8722 | 37.947 | 34.3662 | 34.3636 | 34.1514 | 35.0588 | 35.114 | 35.5251 | 36.2282 | 36.6335 | 20.4966 | 16.5533 | 93.5489 | 33.0188 | 33.0127 | 35.0075 | 33.3157 | 33.0188 | 33.4214 | 34.7763 | 34.3386 | 34.0866 | 37.2055 | 36.1947 | 33.4021 | 34.386 | 36.2032 | 36.5407 | 37.3595 | 36.2173 | 33.2942 | 32.4302 | 34.2609 | 34.8691 | 32.7719 | 34.2991 | 34.3498 | 34.3728 | 34.4295 | 34.4025 | 34.3162 | 33.8731 | 34.4387 | 35.8501 | 35.1614 | 36.2493 | 36.2096 | 33.4665 | 93.9801 | 93.8783 | 93.7268
2022-09-08 03:22 | 5:32 | 16.7301 | 16.9951 | 19.678 | 34.1895 | 34.2881 | 33.8275 | 34.593 | 35.4064 | 36.5279 | 37.2786 | 36.8593 | 37.9385 | 34.3685 | 34.3523 | 34.1463 | 35.0434 | 35.1055 | 35.5666 | 36.2211 | 36.6071 | 20.4937 | 16.533 | 93.6458 | 32.9615 | 33.009 | 35.0125 | 33.2913 | 33.0384 | 33.4139 | 34.7831 | 34.3246 | 34.0908 | 37.2032 | 36.2073 | 33.4094 | 34.3931 | 36.2078 | 36.5457 | 37.3728 | 36.1959 | 33.3041 | 32.411 | 34.2637 | 34.8695 | 32.7694 | 34.3191 | 34.3176 | 34.3603 | 34.4209 | 34.4135 | 34.321 | 33.8672 | 34.4295 | 35.831 | 35.1651 | 36.2622 | 36.2212 | 33.46 | 94.1138 | 93.9597 | 93.7814
2022-09-08 03:22 | 5:32 | 16.7338 | 17.0049 | 19.6613 | 34.2388 | 34.2839 | 33.8309 | 34.6016 | 35.4069 | 36.524 | 37.2803 | 36.8763 | 37.9241 | 34.3496 | 34.3511 | 34.1466 | 35.0438 | 35.1071 | 35.5526 | 36.2328 | 36.6191 | 20.4622 | 16.5215 | 93.7428 | 32.7856 | 32.998 | 35.0032 | 33.3136 | 33.0383 | 33.4311 | 34.7649 | 34.3293 | 34.0813 | 37.1949 | 36.2148 | 33.4008 | 34.3956 | 36.1947 | 36.5286 | 37.3728 | 36.1989 | 33.3027 | 32.4116 | 34.2591 | 34.8469 | 32.7642 | 34.3173 | 34.3354 | 34.3712 | 34.4295 | 34.4239 | 34.3144 | 33.8791 | 34.4209 | 35.8438 | 35.1775 | 36.262 | 36.2137 | 33.4779 | 94.243 | 94.0922 | 93.8868
2022-09-08 03:22 | 5:32 | 16.7215 | 17.0196 | 19.5404 | 34.2211 | 34.2905 | 33.8235 | 34.5999 | 35.4135 | 36.5277 | 37.2783 | 36.8855 | 37.933 | 34.3672 | 34.3342 | 34.1333 | 35.0428 | 35.1002 | 35.5603 | 36.2147 | 36.6261 | 20.4851 | 16.5075 | 93.7878 | 32.9076 | 33.0094 | 35.0012 | 33.3029 | 33.03 | 33.4049 | 34.7714 | 34.3247 | 34.0839 | 37.2057 | 36.1915 | 33.4137 | 34.3925 | 36.2073 | 36.5488 | 37.3666 | 36.2032 | 33.2757 | 32.3971 | 34.2442 | 34.8545 | 32.7654 | 34.3165 | 34.3349 | 34.3591 | 34.4387 | 34.4111 | 34.318 | 33.8713 | 34.4295 | 35.8481 | 35.1541 | 36.2689 | 36.2147 | 33.4614 | 94.3749 | 94.2687 | 93.9759
2022-09-08 03:22 | 5:32 | 16.7119 | 17.0334 | 19.6014 | 34.1126 | 34.2812 | 33.8435 | 34.6055 | 35.3928 | 36.5387 | 37.2756 | 36.8565 | 37.9486 | 34.3824 | 34.3608 | 34.1356 | 35.0399 | 35.0924 | 35.5472 | 36.2206 | 36.6144 | 20.4637 | 16.495 | 93.8871 | 33.0148 | 32.9883 | 35.0044 | 33.2942 | 33.0262 | 33.4021 | 34.7596 | 34.3189 | 34.0887 | 37.2077 | 36.1994 | 33.3978 | 34.373 | 36.2148 | 36.5274 | 37.3627 | 36.2078 | 33.3058 | 32.4036 | 34.2328 | 34.8543 | 32.744 | 34.3 | 34.3052 | 34.3628 | 34.4251 | 34.4036 | 34.3345 | 33.8541 | 34.4387 | 35.8363 | 35.157 | 36.271 | 36.2142 | 33.4642 | 94.4765 | 94.4957 | 94.0976
2022-09-08 03:22 | 5:32 | 16.7428 | 17.0306 | 19.5711 | 34.1422 | 34.2769 | 33.8139 | 34.6098 | 35.3995 | 36.5251 | 37.2935 | 36.8913 | 37.9514 | 34.3666 | 34.3525 | 34.1266 | 35.0441 | 35.1114 | 35.5585 | 36.2391 | 36.598 | 20.4484 | 16.5105 | 93.9695 | 32.9621 | 32.9963 | 34.9903 | 33.3041 | 33.0229 | 33.4094 | 34.778 | 34.324 | 34.0872 | 37.1884 | 36.1811 | 33.3907 | 34.3857 | 36.1915 | 36.5227 | 37.3543 | 36.1947 | 33.2855 | 32.39 | 34.2427 | 34.8436 | 32.7436 | 34.325 | 34.3244 | 34.3625 | 34.4089 | 34.4305 | 34.3127 | 33.8745 | 34.4251 | 35.8581 | 35.1682 | 36.261 | 36.2217 | 33.4648 | 94.5994 | 94.619 | 94.1244
2022-09-08 03:23 | 5:33 | 16.7184 | 17.0341 | 19.5718 | 34.2916 | 34.2715 | 33.8025 | 34.5955 | 35.4058 | 36.5124 | 37.2655 | 36.8685 | 37.9349 | 34.366 | 34.3616 | 34.1448 | 35.0511 | 35.112 | 35.5126 | 36.2257 | 36.6094 | 20.4805 | 16.5712 | 93.945 | 32.9254 | 32.9708 | 34.9799 | 33.3027 | 33.0014 | 33.4008 | 34.7796 | 34.3391 | 34.0908 | 37.1836 | 36.1916 | 33.4129 | 34.3818 | 36.1994 | 36.5202 | 37.361 | 36.2073 | 33.2811 | 32.3886 | 34.2328 | 34.8178 | 32.7493 | 34.3387 | 34.3082 | 34.3835 | 34.423 | 34.4159 | 34.3299 | 33.8631 | 34.4089 | 35.8415 | 35.1615 | 36.2656 | 36.2074 | 33.4591 | 94.6996 | 94.7835 | 94.1908
2022-09-08 03:23 | 5:33 | 16.7517 | 17.0374 | 19.6392 | 34.1707 | 34.2877 | 33.8157 | 34.5958 | 35.4055 | 36.5265 | 37.2802 | 36.8689 | 37.9391 | 34.355 | 34.3556 | 34.1305 | 35.0496 | 35.1069 | 35.5435 | 36.2165 | 36.5811 | 20.4756 | 16.5339 | 94.0542 | 32.9477 | 32.9835 | 34.9901 | 33.2757 | 33.0135 | 33.4137 | 34.7558 | 34.3244 | 34.0808 | 37.1837 | 36.1898 | 33.3946 | 34.3713 | 36.1811 | 36.5309 | 37.3557 | 36.2148 | 33.2553 | 32.417 | 34.2373 | 34.8233 | 32.7527 | 34.3204 | 34.3131 | 34.3499 | 34.4268 | 34.4245 | 34.3448 | 33.8477 | 34.423 | 35.8539 | 35.1676 | 36.275 | 36.2252 | 33.4423 | 94.8327 | 94.8979 | 94.2981
2022-09-08 03:23 | 5:33 | 16.6688 | 16.9416 | 19.5494 | 34.1122 | 34.2848 | 33.8091 | 34.5958 | 35.4137 | 36.5229 | 37.2633 | 36.8662 | 37.9383 | 34.3646 | 34.3518 | 34.1236 | 35.0284 | 35.0973 | 35.5474 | 36.2156 | 36.6023 | 20.4572 | 16.4939 | 94.2791 | 32.7439 | 32.9882 | 34.9739 | 33.3058 | 33.0266 | 33.3978 | 34.757 | 34.3259 | 34.0838 | 37.179 | 36.2033 | 33.3827 | 34.3857 | 36.1916 | 36.5135 | 37.3392 | 36.1915 | 33.2705 | 32.3837 | 34.2256 | 34.8291 | 32.7172 | 34.3322 | 34.2898 | 34.3518 | 34.4294 | 34.4136 | 34.3212 | 33.865 | 34.4268 | 35.8349 | 35.162 | 36.2575 | 36.2162 | 33.4561 | 95.0157 | 95.0494 | 94.3945
2022-09-08 03:23 | 5:33 | 16.649 | 16.9751 | 19.5355 | 34.1396 | 34.2906 | 33.8139 | 34.5774 | 35.4007 | 36.504 | 37.2646 | 36.871 | 37.931 | 34.3808 | 34.3473 | 34.1395 | 35.0381 | 35.0924 | 35.5286 | 36.2147 | 36.5954 | 20.4407 | 16.4821 | 94.1483 | 32.8866 | 32.9857 | 34.9718 | 33.2855 | 33.0032 | 33.3907 | 34.7708 | 34.3066 | 34.0781 | 37.2017 | 36.1626 | 33.3988 | 34.3897 | 36.1898 | 36.5128 | 37.3269 | 36.1994 | 33.276 | 32.389 | 34.2482 | 34.8454 | 32.7339 | 34.3381 | 34.3036 | 34.3533 | 34.4154 | 34.4269 | 34.3263 | 33.8543 | 34.4294 | 35.8382 | 35.1746 | 36.2732 | 36.1936 | 33.4363 | 95.1343 | 95.1084 | 94.4482
2022-09-08 03:23 | 5:33 | 16.6617 | 16.9608 | 19.4955 | 34.1999 | 34.2847 | 33.8242 | 34.5886 | 35.418 | 36.5048 | 37.2522 | 36.8615 | 37.9427 | 34.3791 | 34.3631 | 34.1424 | 35.0423 | 35.0901 | 35.5388 | 36.2045 | 36.5918 | 20.4178 | 16.4725 | 94.0986 | 32.9448 | 32.9639 | 34.9863 | 33.2811 | 33.0163 | 33.4129 | 34.7714 | 34.3263 | 34.0836 | 37.1759 | 36.1839 | 33.4093 | 34.3713 | 36.2033 | 36.518 | 37.3453 | 36.1811 | 33.2699 | 32.3511 | 34.215 | 34.8047 | 32.7113 | 34.3467 | 34.3063 | 34.3676 | 34.4115 | 34.4188 | 34.3437 | 33.8487 | 34.4154 | 35.8247 | 35.1415 | 36.257 | 36.2048 | 33.4221 | 95.1529 | 95.2106 | 94.4166
2022-09-08 03:23 | 5:33 | 16.7065 | 17.0158 | 19.4055 | 34.148 | 34.2827 | 33.8322 | 34.5858 | 35.3952 | 36.508 | 37.2616 | 36.8684 | 37.9204 | 34.3903 | 34.3588 | 34.1176 | 35.0328 | 35.1046 | 35.5393 | 36.1979 | 36.5852 | 20.4016 | 16.4809 | 94.2105 | 32.8876 | 32.9763 | 34.9594 | 33.2553 | 33.0017 | 33.3946 | 34.7651 | 34.3218 | 34.0744 | 37.1767 | 36.1828 | 33.3909 | 34.3712 | 36.1626 | 36.5129 | 37.3334 | 36.1916 | 33.274 | 32.3706 | 34.2178 | 34.824 | 32.7042 | 34.3486 | 34.3027 | 34.3614 | 34.4068 | 34.4209 | 34.331 | 33.8619 | 34.4115 | 35.8058 | 35.1527 | 36.2513 | 36.2143 | 33.431 | 95.1488 | 95.1402 | 94.4544
2022-09-08 03:24 | 5:33 | 16.7035 | 17.0181 | 19.4399 | 34.1376 | 34.2799 | 33.8086 | 34.5819 | 35.3835 | 36.4992 | 37.2633 | 36.8644 | 37.918 | 34.3563 | 34.3765 | 34.1067 | 35.0321 | 35.0728 | 35.5365 | 36.219 | 36.5994 | 20.4094 | 16.4602 | 94.1914 | 32.98 | 32.9536 | 34.9767 | 33.2705 | 32.9916 | 33.3827 | 34.7589 | 34.3263 | 34.0717 | 37.1837 | 36.1814 | 33.387 | 34.3921 | 36.1839 | 36.5163 | 37.3238 | 36.1898 | 33.2645 | 32.3593 | 34.2052 | 34.793 | 32.713 | 34.3317 | 34.2816 | 34.3413 | 34.425 | 34.4249 | 34.3357 | 33.8408 | 34.4068 | 35.8323 | 35.1528 | 36.2519 | 36.1987 | 33.4357 | 94.9656 | 95.0439 | 94.3127
2022-09-08 03:24 | 5:34 | 16.7041 | 17.0205 | 19.4085 | 34.1372 | 34.2827 | 33.8334 | 34.5767 | 35.4037 | 36.4976 | 37.2404 | 36.8539 | 37.9213 | 34.3596 | 34.3375 | 34.1259 | 35.0414 | 35.0705 | 35.5352 | 36.1736 | 36.5785 | 20.4027 | 16.4753 | 93.9983 | 32.9265 | 32.967 | 34.9777 | 33.276 | 33.0033 | 33.3988 | 34.7687 | 34.3191 | 34.0644 | 37.1767 | 36.1849 | 33.3805 | 34.3867 | 36.1828 | 36.5293 | 37.3332 | 36.2033 | 33.259 | 32.3513 | 34.1998 | 34.8001 | 32.6904 | 34.3325 | 34.2981 | 34.3613 | 34.4166 | 34.4249 | 34.3207 | 33.8354 | 34.425 | 35.8161 | 35.1453 | 36.2633 | 36.1962 | 33.4162 | 94.7251 | 94.8539 | 94.1256
2022-09-08 03:24 | 5:34 | 16.6595 | 16.9751 | 19.4155 | 34.0937 | 34.2812 | 33.8019 | 34.578 | 35.3919 | 36.5066 | 37.2378 | 36.8578 | 37.9281 | 34.3643 | 34.3617 | 34.0989 | 35.0246 | 35.0683 | 35.5135 | 36.2009 | 36.5627 | 20.4318 | 16.435 | 93.9162 | 32.8188 | 32.9508 | 34.9691 | 33.2699 | 33.0054 | 33.4093 | 34.7603 | 34.3313 | 34.0535 | 37.1622 | 36.1726 | 33.387 | 34.375 | 36.1814 | 36.5036 | 37.3108 | 36.1626 | 33.278 | 32.3299 | 34.1863 | 34.7888 | 32.6979 | 34.3365 | 34.2981 | 34.3661 | 34.4046 | 34.4237 | 34.3302 | 33.8424 | 34.4166 | 35.8194 | 35.1535 | 36.2672 | 36.1905 | 33.4085 | 94.4835 | 94.5822 | 94.039
2022-09-08 03:24 | 5:34 | 16.6913 | 17.0283 | 19.4453 | 34.2154 | 34.2935 | 33.8107 | 34.5687 | 35.3923 | 36.4841 | 37.2449 | 36.8757 | 37.9328 | 34.3538 | 34.362 | 34.0943 | 35.0313 | 35.0811 | 35.5111 | 36.1796 | 36.5663 | 20.4683 | 16.5078 | 93.8492 | 32.7882 | 32.953 | 34.9808 | 33.274 | 32.9928 | 33.3909 | 34.7511 | 34.3364 | 34.0367 | 37.1636 | 36.1819 | 33.3775 | 34.371 | 36.1849 | 36.5046 | 37.3392 | 36.1839 | 33.262 | 32.3468 | 34.1757 | 34.7813 | 32.687 | 34.3537 | 34.2827 | 34.3659 | 34.3969 | 34.412 | 34.3411 | 33.8428 | 34.4046 | 35.7987 | 35.1615 | 36.2695 | 36.1807 | 33.4046 | 94.3072 | 94.3815 | 93.947
2022-09-08 03:24 | 5:34 | 15.5299 | 16.6546 | 19.1791 | 34.0765 | 34.3064 | 33.8145 | 34.5695 | 35.3891 | 36.5082 | 37.2341 | 36.8686 | 37.9316 | 34.3796 | 34.3398 | 34.1043 | 35.0112 | 35.0563 | 35.5066 | 36.1761 | 36.562 | 20.4713 | 16.7575 | 93.7469 | 32.8645 | 32.9576 | 34.97 | 33.2645 | 33.0015 | 33.387 | 34.7551 | 34.3221 | 34.0552 | 37.1518 | 36.196 | 33.3816 | 34.3647 | 36.1726 | 36.5053 | 37.3242 | 36.1828 | 33.2614 | 32.346 | 34.186 | 34.7767 | 32.7142 | 34.3381 | 34.2957 | 34.361 | 34.3927 | 34.4337 | 34.3387 | 33.8319 | 34.3969 | 35.808 | 35.1524 | 36.2667 | 36.1938 | 33.4022 | 94.1502 | 94.1906 | 93.8804
2022-09-08 03:24 | 5:34 | 15.2388 | 16.3933 | 18.9055 | 33.9276 | 34.2832 | 33.805 | 34.5885 | 35.3739 | 36.4973 | 37.2446 | 36.8572 | 37.935 | 34.3631 | 34.3747 | 34.0938 | 35.0104 | 35.0549 | 35.5271 | 36.186 | 36.5463 | 20.8335 | 17.5144 | 93.711 | 32.8838 | 32.9626 | 34.9716 | 33.259 | 32.993 | 33.3805 | 34.7359 | 34.3162 | 34.0571 | 37.1796 | 36.1974 | 33.3808 | 34.3691 | 36.1819 | 36.5057 | 37.3012 | 36.1814 | 33.2638 | 32.3197 | 34.1715 | 34.7497 | 32.6799 | 34.3456 | 34.2769 | 34.3587 | 34.3927 | 34.4367 | 34.3405 | 33.8238 | 34.3927 | 35.7775 | 35.1457 | 36.2399 | 36.1825 | 33.3975 | 94.0249 | 94.1531 | 93.8469
2022-09-08 03:25 | 5:35 | 14.9707 | 16.1865 | 18.6455 | 34.0327 | 34.3067 | 33.8075 | 34.5688 | 35.3821 | 36.4883 | 37.234 | 36.8597 | 37.9174 | 34.3827 | 34.3511 | 34.0947 | 35.0222 | 35.062 | 35.5107 | 36.1861 | 36.553 | 21.4391 | 18.5495 | 93.6156 | 33.0431 | 32.9409 | 34.9854 | 33.278 | 32.9939 | 33.387 | 34.7603 | 34.3205 | 34.0598 | 37.1572 | 36.1737 | 33.4011 | 34.3819 | 36.196 | 36.507 | 37.3081 | 36.1849 | 33.2568 | 32.3299 | 34.176 | 34.7569 | 32.6927 | 34.351 | 34.2938 | 34.3718 | 34.3944 | 34.4328 | 34.3314 | 33.8105 | 34.3927 | 35.7903 | 35.1624 | 36.2556 | 36.1799 | 33.3815 | 93.9343 | 94.0757 | 93.7956
2022-09-08 03:25 | 5:35 | 14.6744 | 15.9121 | 18.4534 | 33.9505 | 34.304 | 33.7938 | 34.562 | 35.3811 | 36.4733 | 37.2294 | 36.8462 | 37.921 | 34.3615 | 34.3657 | 34.0747 | 34.9957 | 35.0569 | 35.5068 | 36.1917 | 36.5408 | 22.1781 | 19.7446 | 93.5117 | 33.0138 | 32.9499 | 34.9805 | 33.262 | 32.9936 | 33.3775 | 34.7361 | 34.3226 | 34.0778 | 37.1716 | 36.1947 | 33.3726 | 34.3757 | 36.1974 | 36.5213 | 37.3055 | 36.1726 | 33.2615 | 32.3266 | 34.1846 | 34.7779 | 32.6929 | 34.3601 | 34.2731 | 34.3258 | 34.4015 | 34.4064 | 34.3627 | 33.8321 | 34.3944 | 35.7917 | 35.1401 | 36.2627 | 36.1987 | 33.3793 | 93.8672 | 94.0541 | 93.8276
2022-09-08 03:25 | 5:35 | 14.5176 | 15.8007 | 18.2259 | 33.9566 | 34.3165 | 33.8 | 34.5642 | 35.3653 | 36.4846 | 37.2407 | 36.8705 | 37.9347 | 34.3912 | 34.3894 | 34.0842 | 35.0361 | 35.0624 | 35.5083 | 36.1927 | 36.5571 | 22.9763 | 20.9431 | 93.6075 | 33.1853 | 32.9595 | 34.9781 | 33.2614 | 32.9978 | 33.3816 | 34.7325 | 34.3199 | 34.0563 | 37.1555 | 36.1751 | 33.3794 | 34.3628 | 36.1737 | 36.5154 | 37.32 | 36.1819 | 33.2684 | 32.3144 | 34.1745 | 34.7672 | 32.682 | 34.3682 | 34.2923 | 34.368 | 34.3947 | 34.4295 | 34.3524 | 33.8215 | 34.4015 | 35.795 | 35.1516 | 36.2759 | 36.1873 | 33.3784 | 93.8334 | 94.0579 | 93.8008
2022-09-08 03:25 | 5:35 | 14.2625 | 15.6104 | 18.135 | 33.8525 | 34.296 | 33.8123 | 34.5548 | 35.3558 | 36.4837 | 37.2347 | 36.8718 | 37.937 | 34.3688 | 34.3594 | 34.0884 | 35.025 | 35.0344 | 35.4976 | 36.1817 | 36.5522 | 23.7965 | 22.1174 | 93.6385 | 33.209 | 32.9503 | 34.979 | 33.2638 | 32.9911 | 33.3808 | 34.7291 | 34.3344 | 34.0395 | 37.1729 | 36.1912 | 33.376 | 34.3595 | 36.1947 | 36.5008 | 37.3049 | 36.196 | 33.2481 | 32.3344 | 34.1698 | 34.7736 | 32.6756 | 34.3592 | 34.2772 | 34.3634 | 34.4125 | 34.4129 | 34.339 | 33.8204 | 34.3947 | 35.7836 | 35.1227 | 36.272 | 36.1972 | 33.3896 | 93.7952 | 93.9006 | 93.7414
2022-09-08 03:25 | 5:35 | 14.1152 | 15.458 | 17.9938 | 33.9333 | 34.2982 | 33.8027 | 34.5611 | 35.3854 | 36.4808 | 37.2116 | 36.8666 | 37.9301 | 34.3942 | 34.3858 | 34.0782 | 35.0221 | 35.0358 | 35.5029 | 36.1933 | 36.5424 | 24.5536 | 23.1622 | 93.4725 | 33.4581 | 32.9291 | 34.9615 | 33.2568 | 33.003 | 33.4011 | 34.7272 | 34.3225 | 34.0726 | 37.1716 | 36.1919 | 33.3755 | 34.386 | 36.1751 | 36.5344 | 37.2974 | 36.1974 | 33.2743 | 32.3209 | 34.1657 | 34.7384 | 32.6971 | 34.3334 | 34.2701 | 34.3498 | 34.4137 | 34.4178 | 34.3447 | 33.8086 | 34.4125 | 35.8126 | 35.1396 | 36.2604 | 36.1765 | 33.3883 | 93.7645 | 93.8307 | 93.6594
2022-09-08 03:25 | 5:35 | 13.9328 | 15.2896 | 17.8937 | 33.9318 | 34.3148 | 33.8082 | 34.5543 | 35.3741 | 36.4806 | 37.2297 | 36.8946 | 37.9357 | 34.4051 | 34.3832 | 34.0794 | 35.0236 | 35.0468 | 35.5088 | 36.1817 | 36.5418 | 25.2767 | 24.1101 | 93.48 | 33.3655 | 32.9478 | 34.9646 | 33.2615 | 33.0243 | 33.3726 | 34.7425 | 34.3317 | 34.0565 | 37.1588 | 36.1622 | 33.3816 | 34.3827 | 36.1912 | 36.5338 | 37.3204 | 36.1737 | 33.2638 | 32.3258 | 34.1672 | 34.7671 | 32.7022 | 34.3646 | 34.2775 | 34.3538 | 34.3845 | 34.4223 | 34.3445 | 33.8089 | 34.4137 | 35.8041 | 35.1547 | 36.2531 | 36.2017 | 33.3838 | 93.624 | 93.6955 | 93.564
2022-09-08 03:26 | 5:35 | 13.7671 | 15.1679 | 17.689 | 33.7784 | 34.2949 | 33.8091 | 34.5391 | 35.3742 | 36.4825 | 37.2278 | 36.8715 | 37.9495 | 34.3891 | 34.4034 | 34.0846 | 35.0189 | 35.0354 | 35.5107 | 36.197 | 36.5587 | 25.9251 | 24.9455 | 93.3918 | 33.4652 | 32.9513 | 34.9965 | 33.2684 | 33.0324 | 33.3794 | 34.7366 | 34.3404 | 34.0831 | 37.1597 | 36.1892 | 33.3695 | 34.3973 | 36.1919 | 36.4973 | 37.2831 | 36.1947 | 33.2506 | 32.308 | 34.176 | 34.7574 | 32.6999 | 34.3543 | 34.2698 | 34.3479 | 34.4024 | 34.4268 | 34.3313 | 33.8282 | 34.3845 | 35.8081 | 35.1486 | 36.2645 | 36.1946 | 33.3805 | 93.5454 | 93.6365 | 93.523
2022-09-08 03:26 | 5:36 | 13.6657 | 15.046 | 17.6193 | 33.8264 | 34.3084 | 33.8023 | 34.5416 | 35.3773 | 36.4601 | 37.2297 | 36.8661 | 37.9467 | 34.3939 | 34.3836 | 34.0783 | 35.0202 | 35.042 | 35.5002 | 36.1759 | 36.5464 | 26.5181 | 25.6603 | 93.3555 | 33.5029 | 32.9511 | 34.9899 | 33.2481 | 33.0384 | 33.376 | 34.7481 | 34.3466 | 34.0463 | 37.1845 | 36.1764 | 33.3828 | 34.3709 | 36.1622 | 36.5121 | 37.3093 | 36.1751 | 33.2469 | 32.3332 | 34.1773 | 34.7506 | 32.705 | 34.3653 | 34.2889 | 34.3627 | 34.391 | 34.4336 | 34.3636 | 33.8085 | 34.4024 | 35.8199 | 35.1547 | 36.2631 | 36.1955 | 33.3795 | 93.453 | 93.6571 | 93.4796
2022-09-08 03:26 | 5:36 | 13.5389 | 14.905 | 17.4755 | 33.7122 | 34.2919 | 33.7837 | 34.5321 | 35.388 | 36.4685 | 37.218 | 36.8714 | 37.9351 | 34.4034 | 34.392 | 34.0836 | 35.0071 | 35.0266 | 35.5054 | 36.193 | 36.5585 | 27.051 | 26.2973 | 93.1434 | 33.5546 | 32.9541 | 34.9589 | 33.2743 | 33.032 | 33.3755 | 34.7414 | 34.3277 | 34.067 | 37.1642 | 36.1723 | 33.378 | 34.3886 | 36.1892 | 36.5162 | 37.312 | 36.1912 | 33.2416 | 32.3346 | 34.1725 | 34.7488 | 32.701 | 34.3484 | 34.2827 | 34.3617 | 34.3988 | 34.4344 | 34.3523 | 33.8101 | 34.391 | 35.8058 | 35.1633 | 36.265 | 36.2128 | 33.3882 | 93.3747 | 93.5596 | 93.4524
2022-09-08 03:26 | 5:36 | 13.4492 | 14.7445 | 17.4257 | 33.6987 | 34.3071 | 33.7769 | 34.5482 | 35.3753 | 36.4656 | 37.2216 | 36.8825 | 37.9436 | 34.3994 | 34.3863 | 34.0993 | 35.0259 | 35.0363 | 35.5191 | 36.1864 | 36.5553 | 27.5037 | 26.8284 | 93.1909 | 33.4682 | 32.9536 | 34.9606 | 33.2638 | 33.0464 | 33.3816 | 34.742 | 34.3346 | 34.0592 | 37.185 | 36.1759 | 33.3902 | 34.3703 | 36.1764 | 36.5183 | 37.3141 | 36.1919 | 33.2417 | 32.3248 | 34.1887 | 34.7441 | 32.7097 | 34.3619 | 34.2647 | 34.3503 | 34.4069 | 34.4054 | 34.3511 | 33.8107 | 34.3988 | 35.8146 | 35.1232 | 36.2841 | 36.2025 | 33.3848 | 93.3066 | 93.4473 | 93.3643
2022-09-08 03:26 | 5:36 | 13.2996 | 14.6296 | 17.2943 | 33.748 | 34.3096 | 33.8159 | 34.5541 | 35.348 | 36.4773 | 37.2367 | 36.883 | 37.9515 | 34.3919 | 34.3792 | 34.0869 | 35.0172 | 35.0393 | 35.481 | 36.1911 | 36.5608 | 27.8934 | 27.2778 | 93.1417 | 33.6468 | 32.9528 | 34.9767 | 33.2506 | 33.0422 | 33.3695 | 34.7323 | 34.3387 | 34.0708 | 37.1778 | 36.1954 | 33.3794 | 34.3824 | 36.1723 | 36.5073 | 37.2912 | 36.1622 | 33.2447 | 32.3181 | 34.1925 | 34.7598 | 32.7111 | 34.3503 | 34.2681 | 34.3367 | 34.3873 | 34.42 | 34.3342 | 33.8234 | 34.4069 | 35.815 | 35.1687 | 36.2791 | 36.1938 | 33.4072 | 93.234 | 93.3471 | 93.3002
2022-09-08 03:26 | 5:36 | 13.1783 | 14.5041 | 17.1235 | 33.7523 | 34.3162 | 33.8052 | 34.5414 | 35.3654 | 36.4905 | 37.2105 | 36.8751 | 37.9354 | 34.3947 | 34.3816 | 34.0812 | 35.0245 | 35.0469 | 35.4848 | 36.1919 | 36.5458 | 28.2581 | 27.6715 | 93.0553 | 33.692 | 32.9631 | 34.9884 | 33.2469 | 33.0438 | 33.3828 | 34.7464 | 34.3519 | 34.0612 | 37.1682 | 36.1903 | 33.3565 | 34.3777 | 36.1759 | 36.4965 | 37.3036 | 36.1892 | 33.2707 | 32.3216 | 34.1771 | 34.754 | 32.7292 | 34.3664 | 34.283 | 34.3436 | 34.3816 | 34.4248 | 34.3608 | 33.8118 | 34.3873 | 35.8045 | 35.1631 | 36.2601 | 36.2022 | 33.3983 | 93.1573 | 93.2274 | 93.2317
2022-09-08 03:27 | 5:37 | 13.0098 | 14.3626 | 16.945 | 33.676 | 34.321 | 33.8036 | 34.5209 | 35.3728 | 36.4781 | 37.2242 | 36.8841 | 37.9438 | 34.4015 | 34.4022 | 34.0838 | 35.012 | 35.034 | 35.4878 | 36.1821 | 36.5397 | 28.5581 | 27.9878 | 93.125 | 33.7818 | 32.9607 | 34.9881 | 33.2416 | 33.0579 | 33.378 | 34.7411 | 34.3356 | 34.0721 | 37.1811 | 36.1697 | 33.3847 | 34.3691 | 36.1954 | 36.5202 | 37.3106 | 36.1764 | 33.2622 | 32.3436 | 34.1991 | 34.7606 | 32.7373 | 34.3669 | 34.2721 | 34.3611 | 34.398 | 34.4016 | 34.3525 | 33.8121 | 34.3816 | 35.8224 | 35.1536 | 36.2673 | 36.2075 | 33.3826 | 93.1445 | 93.1122 | 93.2737
2022-09-08 03:27 | 5:37 | 12.9035 | 14.2523 | 16.8289 | 33.7447 | 34.3144 | 33.7866 | 34.5268 | 35.3697 | 36.4786 | 37.2034 | 36.8865 | 37.9489 | 34.3819 | 34.418 | 34.0838 | 35.0295 | 35.043 | 35.4838 | 36.1878 | 36.5501 | 28.836 | 28.3019 | 92.985 | 33.7308 | 32.9651 | 34.9795 | 33.2417 | 33.0355 | 33.3902 | 34.7404 | 34.339 | 34.0474 | 37.1723 | 36.1834 | 33.3668 | 34.37 | 36.1903 | 36.5185 | 37.3134 | 36.1723 | 33.2376 | 32.3259 | 34.2067 | 34.7649 | 32.7355 | 34.3692 | 34.2586 | 34.364 | 34.3923 | 34.4262 | 34.3616 | 33.7983 | 34.398 | 35.8125 | 35.1449 | 36.2684 | 36.199 | 33.4104 | 93.0819 | 93.0533 | 93.1805
2022-09-08 03:27 | 5:37 | 12.7593 | 14.1063 | 16.7968 | 33.6069 | 34.318 | 33.7713 | 34.5366 | 35.369 | 36.4972 | 37.2188 | 36.8813 | 37.9629 | 34.3962 | 34.3974 | 34.081 | 35.0283 | 35.0258 | 35.4879 | 36.1855 | 36.5504 | 29.0815 | 28.5424 | 92.9053 | 33.8692 | 32.9644 | 34.9636 | 33.2447 | 33.0543 | 33.3794 | 34.7335 | 34.3265 | 34.0691 | 37.1738 | 36.1874 | 33.367 | 34.3896 | 36.1697 | 36.5176 | 37.3015 | 36.1759 | 33.2488 | 32.344 | 34.2223 | 34.7719 | 32.7316 | 34.3773 | 34.2583 | 34.3409 | 34.3978 | 34.4062 | 34.3556 | 33.8345 | 34.3923 | 35.8093 | 35.1564 | 36.2774 | 36.1955 | 33.3924 | 92.9308 | 92.8966 | 93.0997
2022-09-08 03:27 | 5:37 | 12.683 | 14.0068 | 16.7236 | 33.6675 | 34.3345 | 33.7855 | 34.5208 | 35.3754 | 36.472 | 37.2275 | 36.8853 | 37.9549 | 34.4025 | 34.3967 | 34.0694 | 35.0278 | 35.0425 | 35.4925 | 36.1883 | 36.5425 | 29.2875 | 28.764 | 92.6549 | 33.8359 | 32.9684 | 34.9898 | 33.2707 | 33.0476 | 33.3565 | 34.7481 | 34.3371 | 34.0554 | 37.1645 | 36.1889 | 33.3826 | 34.3718 | 36.1834 | 36.5066 | 37.3083 | 36.1954 | 33.2373 | 32.3398 | 34.2133 | 34.7826 | 32.7258 | 34.3742 | 34.2704 | 34.3465 | 34.3691 | 34.4174 | 34.3518 | 33.8079 | 34.3978 | 35.8111 | 35.1796 | 36.2735 | 36.203 | 33.3916 | 92.8452 | 92.7564 | 93.0413
2022-09-08 03:27 | 5:37 | 12.5542 | 13.8603 | 16.5667 | 33.6197 | 34.3127 | 33.7907 | 34.5299 | 35.3419 | 36.4712 | 37.2263 | 36.8919 | 37.9438 | 34.4213 | 34.3908 | 34.0845 | 35.0203 | 35.0479 | 35.5016 | 36.1806 | 36.5546 | 29.473 | 28.9672 | 92.7842 | 33.9579 | 32.9424 | 34.9602 | 33.2622 | 33.0555 | 33.3847 | 34.7391 | 34.3331 | 34.0645 | 37.1906 | 36.1754 | 33.3718 | 34.3703 | 36.1874 | 36.5304 | 37.3043 | 36.1903 | 33.2456 | 32.3282 | 34.2174 | 34.7735 | 32.7286 | 34.3805 | 34.2681 | 34.3507 | 34.3905 | 34.4225 | 34.3473 | 33.7916 | 34.3691 | 35.8283 | 35.1492 | 36.2764 | 36.2158 | 33.4004 | 92.7349 | 92.6585 | 92.9885
2022-09-08 03:27 | 5:37 | 12.4558 | 13.7216 | 16.3632 | 33.5756 | 34.3299 | 33.7992 | 34.5134 | 35.3728 | 36.486 | 37.2255 | 36.8785 | 37.9468 | 34.4119 | 34.4089 | 34.0849 | 35.0204 | 35.0294 | 35.4825 | 36.1902 | 36.548 | 29.6011 | 29.125 | 92.632 | 33.9313 | 32.9683 | 34.978 | 33.2376 | 33.0528 | 33.3668 | 34.7377 | 34.3369 | 34.0762 | 37.1722 | 36.1834 | 33.3754 | 34.3643 | 36.1889 | 36.5087 | 37.3093 | 36.1697 | 33.2244 | 32.3456 | 34.2006 | 34.7796 | 32.7352 | 34.3716 | 34.2561 | 34.3516 | 34.3845 | 34.3985 | 34.3631 | 33.8113 | 34.3905 | 35.8102 | 35.1482 | 36.2702 | 36.2091 | 33.409 | 92.5152 | 92.5222 | 92.8598
2022-09-08 03:28 | 5:38 | 12.3218 | 13.6554 | 16.2545 | 33.7032 | 34.3448 | 33.7863 | 34.5058 | 35.3635 | 36.4724 | 37.2411 | 36.8948 | 37.9656 | 34.4074 | 34.4226 | 34.0819 | 35.0154 | 35.0018 | 35.4857 | 36.1824 | 36.5297 | 29.7735 | 29.3072 | 92.5087 | 33.9059 | 32.9488 | 34.9818 | 33.2488 | 33.0585 | 33.367 | 34.7527 | 34.3288 | 34.0681 | 37.1674 | 36.1703 | 33.3855 | 34.3755 | 36.1754 | 36.52 | 37.3041 | 36.1834 | 33.2385 | 32.3477 | 34.2338 | 34.8022 | 32.7523 | 34.3826 | 34.2619 | 34.335 | 34.3658 | 34.4203 | 34.3588 | 33.829 | 34.3845 | 35.8302 | 35.1546 | 36.2588 | 36.2122 | 33.4149 | 92.4136 | 92.448 | 92.7929
2022-09-08 03:28 | 5:38 | 12.3907 | 13.5429 | 16.2371 | 33.5867 | 34.3212 | 33.7828 | 34.5144 | 35.3588 | 36.4827 | 37.2254 | 36.8912 | 37.9697 | 34.4132 | 34.4184 | 34.0678 | 35.0228 | 35.0214 | 35.495 | 36.1802 | 36.5566 | 29.9023 | 29.4338 | 92.3471 | 33.8914 | 32.9485 | 34.9663 | 33.2373 | 33.0491 | 33.3826 | 34.7433 | 34.3286 | 34.068 | 37.1783 | 36.1626 | 33.3688 | 34.3559 | 36.1834 | 36.5188 | 37.2906 | 36.1874 | 33.2423 | 32.3393 | 34.2291 | 34.7968 | 32.7527 | 34.3757 | 34.2527 | 34.3701 | 34.3918 | 34.409 | 34.3765 | 33.818 | 34.3658 | 35.8261 | 35.1548 | 36.2719 | 36.202 | 33.3961 | 92.2398 | 92.2191 | 92.637
2022-09-08 03:28 | 5:38 | 12.3069 | 13.4406 | 16.185 | 33.6138 | 34.3263 | 33.8023 | 34.5145 | 35.3673 | 36.4806 | 37.2311 | 36.8907 | 37.9593 | 34.4166 | 34.4196 | 34.0641 | 35.022 | 35.0151 | 35.4821 | 36.1833 | 36.5522 | 30.0172 | 29.5431 | 92.3364 | 34.0444 | 32.9682 | 34.9906 | 33.2456 | 33.0689 | 33.3718 | 34.7225 | 34.3193 | 34.0703 | 37.1819 | 36.1603 | 33.366 | 34.3475 | 36.1703 | 36.5148 | 37.3056 | 36.1889 | 33.2341 | 32.3411 | 34.2555 | 34.7987 | 32.7507 | 34.3972 | 34.2639 | 34.3582 | 34.3617 | 34.4133 | 34.3375 | 33.7962 | 34.3918 | 35.8295 | 35.1558 | 36.2583 | 36.208 | 33.4038 | 92.1443 | 92.113 | 92.582
2022-09-08 03:28 | 5:38 | 12.1202 | 13.2989 | 16.1081 | 33.5502 | 34.3437 | 33.7681 | 34.4869 | 35.3584 | 36.4834 | 37.2304 | 36.8804 | 37.9597 | 34.4133 | 34.4232 | 34.0613 | 35.0093 | 35.0109 | 35.4924 | 36.1927 | 36.5459 | 30.1332 | 29.685 | 92.2198 | 33.9537 | 32.9556 | 34.9556 | 33.2244 | 33.0355 | 33.3754 | 34.7486 | 34.3441 | 34.0738 | 37.1777 | 36.174 | 33.3666 | 34.3733 | 36.1626 | 36.5105 | 37.291 | 36.1754 | 33.2379 | 32.3582 | 34.2396 | 34.7997 | 32.7608 | 34.4101 | 34.2508 | 34.3366 | 34.3536 | 34.4091 | 34.3617 | 33.811 | 34.3617 | 35.8276 | 35.1406 | 36.2673 | 36.2287 | 33.4097 | 92.0119 | 91.9922 | 92.4545
2022-09-08 03:28 | 5:38 | 11.8098 | 13.0045 | 15.8505 | 33.5172 | 34.331 | 33.7815 | 34.4956 | 35.3786 | 36.4681 | 37.2382 | 36.9012 | 37.9542 | 34.421 | 34.4102 | 34.0831 | 35.0276 | 35.0282 | 35.4959 | 36.2011 | 36.5677 | 30.2217 | 29.7813 | 92.1628 | 34.026 | 32.967 | 34.9727 | 33.2385 | 33.0517 | 33.3855 | 34.745 | 34.3342 | 34.0651 | 37.1874 | 36.1816 | 33.3919 | 34.3704 | 36.1603 | 36.532 | 37.2869 | 36.1834 | 33.2301 | 32.34 | 34.2516 | 34.8007 | 32.7663 | 34.3942 | 34.2626 | 34.3695 | 34.3628 | 34.4104 | 34.362 | 33.8085 | 34.3536 | 35.8286 | 35.1579 | 36.2794 | 36.2225 | 33.4045 | 91.8396 | 91.8959 | 92.367
2022-09-08 03:28 | 5:38 | 11.8077 | 11.2267 | 15.2898 | 33.5102 | 34.3357 | 33.7722 | 34.4918 | 35.3522 | 36.4773 | 37.2318 | 36.8993 | 37.9613 | 34.4104 | 34.4409 | 34.0691 | 35.0096 | 35.0099 | 35.5028 | 36.1863 | 36.5464 | 30.2266 | 29.8351 | 92.059 | 34.009 | 32.9659 | 34.971 | 33.2423 | 33.0625 | 33.3688 | 34.7463 | 34.3417 | 34.0605 | 37.1581 | 36.1562 | 33.3692 | 34.358 | 36.174 | 36.5212 | 37.3106 | 36.1703 | 33.2295 | 32.366 | 34.2467 | 34.8202 | 32.7742 | 34.3994 | 34.2634 | 34.3447 | 34.3686 | 34.409 | 34.3398 | 33.8202 | 34.3628 | 35.8517 | 35.1469 | 36.2836 | 36.2183 | 33.4006 | 91.7979 | 91.8338 | 92.3182
2022-09-08 03:29 | 5:38 | 14.2159 | 11.8846 | 16.9326 | 33.5228 | 34.3207 | 33.7846 | 34.4933 | 35.3379 | 36.4634 | 37.2424 | 36.8946 | 37.9691 | 34.4134 | 34.4239 | 34.0767 | 35.0122 | 35.0057 | 35.5092 | 36.1763 | 36.5432 | 30.3102 | 29.9107 | 92.1028 | 34.1001 | 32.9624 | 34.9636 | 33.2341 | 33.0618 | 33.366 | 34.738 | 34.337 | 34.0697 | 37.1869 | 36.1673 | 33.3757 | 34.3672 | 36.1816 | 36.5155 | 37.3016 | 36.1626 | 33.2167 | 32.3642 | 34.2387 | 34.7909 | 32.7925 | 34.4098 | 34.2439 | 34.3517 | 34.3774 | 34.4054 | 34.3747 | 33.8287 | 34.3686 | 35.8314 | 35.1563 | 36.2746 | 36.227 | 33.4317 | 91.8231 | 91.8599 | 92.3199
2022-09-08 03:29 | 5:39 | 16.5531 | 13.2154 | 18.7916 | 33.5938 | 34.3302 | 33.7736 | 34.4754 | 35.3509 | 36.464 | 37.2288 | 36.9001 | 37.9512 | 34.4025 | 34.4106 | 34.0577 | 35.0077 | 35.0003 | 35.4914 | 36.1797 | 36.5712 | 30.3817 | 29.974 | 92.0935 | 34.1412 | 32.9489 | 34.9755 | 33.2379 | 33.0613 | 33.3666 | 34.7532 | 34.3405 | 34.0752 | 37.1643 | 36.1632 | 33.3825 | 34.368 | 36.1562 | 36.5347 | 37.3078 | 36.1603 | 33.2204 | 32.362 | 34.2754 | 34.803 | 32.7833 | 34.3983 | 34.2523 | 34.3428 | 34.3532 | 34.3984 | 34.3511 | 33.81 | 34.3774 | 35.8443 | 35.1456 | 36.2831 | 36.2236 | 33.4115 | 91.85 | 91.9078 | 92.4292
2022-09-08 03:29 | 5:39 | 18.1014 | 14.7863 | 20.5057 | 33.8577 | 34.3411 | 33.7834 | 34.4532 | 35.3546 | 36.4512 | 37.2269 | 36.9016 | 37.953 | 34.4135 | 34.4389 | 34.0615 | 35.0159 | 35.0095 | 35.5082 | 36.1699 | 36.5395 | 30.4459 | 30.059 | 92.2469 | 34.158 | 32.9616 | 34.9568 | 33.2301 | 33.0646 | 33.3919 | 34.7539 | 34.3461 | 34.0639 | 37.1672 | 36.1555 | 33.3682 | 34.3762 | 36.1673 | 36.523 | 37.2999 | 36.174 | 33.2335 | 32.3683 | 34.2407 | 34.8097 | 32.7773 | 34.4123 | 34.2518 | 34.3549 | 34.3604 | 34.4037 | 34.3657 | 33.8215 | 34.3532 | 35.8294 | 35.1456 | 36.2841 | 36.2347 | 33.3959 | 91.9298 | 91.9733 | 92.5165
2022-09-08 03:29 | 5:39 | 19.197 | 16.4908 | 21.9645 | 33.8884 | 34.3387 | 33.7707 | 34.492 | 35.3537 | 36.4722 | 37.2291 | 36.8888 | 37.9528 | 34.4239 | 34.4553 | 34.0843 | 35.0116 | 35.0008 | 35.4931 | 36.1939 | 36.5355 | 30.5164 | 30.1475 | 92.2698 | 34.169 | 32.956 | 34.9581 | 33.2295 | 33.0662 | 33.3692 | 34.7637 | 34.33 | 34.0599 | 37.1868 | 36.1626 | 33.3631 | 34.3517 | 36.1632 | 36.5258 | 37.3092 | 36.1816 | 33.2358 | 32.3875 | 34.2734 | 34.8235 | 32.7857 | 34.4114 | 34.2437 | 34.3454 | 34.3499 | 34.4099 | 34.3894 | 33.8215 | 34.3604 | 35.8521 | 35.1561 | 36.2737 | 36.2094 | 33.4227 | 92.0794 | 92.101 | 92.5816
2022-09-08 03:29 | 5:39 | 20.136 | 18.0409 | 23.2419 | 34.0934 | 34.3405 | 33.7578 | 34.4782 | 35.3548 | 36.4614 | 37.2519 | 36.8818 | 37.9557 | 34.4111 | 34.423 | 34.0679 | 35.0146 | 34.9992 | 35.4909 | 36.1829 | 36.5515 | 30.5766 | 30.1915 | 92.3047 | 34.2515 | 32.9605 | 34.9489 | 33.2167 | 33.0758 | 33.3757 | 34.7436 | 34.3398 | 34.0706 | 37.1682 | 36.174 | 33.3691 | 34.3413 | 36.1555 | 36.5197 | 37.3105 | 36.1562 | 33.2301 | 32.3768 | 34.2577 | 34.8191 | 32.7894 | 34.4269 | 34.2599 | 34.3573 | 34.3373 | 34.4007 | 34.3594 | 33.8292 | 34.3499 | 35.8495 | 35.1246 | 36.3047 | 36.2178 | 33.3968 | 92.1941 | 92.1687 | 92.6195
2022-09-08 03:29 | 5:39 | 21.0876 | 19.5419 | 24.2173 | 34.2137 | 34.3314 | 33.7565 | 34.4783 | 35.3628 | 36.4677 | 37.2219 | 36.8974 | 37.9655 | 34.4036 | 34.4346 | 34.0804 | 35.0142 | 34.9867 | 35.4895 | 36.1964 | 36.5595 | 30.6508 | 30.2586 | 92.2227 | 34.2483 | 32.9672 | 34.9505 | 33.2204 | 33.0589 | 33.3825 | 34.7569 | 34.3364 | 34.0589 | 37.1816 | 36.1508 | 33.3716 | 34.348 | 36.1626 | 36.5196 | 37.2946 | 36.1673 | 33.2198 | 32.3823 | 34.2726 | 34.8134 | 32.8044 | 34.4099 | 34.2711 | 34.3704 | 34.3479 | 34.3993 | 34.3858 | 33.8222 | 34.3373 | 35.83 | 35.1321 | 36.2894 | 36.2216 | 33.4083 | 92.2868 | 92.2731 | 92.6165
2022-09-08 03:30 | 5:40 | 21.9435 | 20.9483 | 25.1046 | 34.2742 | 34.3627 | 33.7599 | 34.4629 | 35.3431 | 36.469 | 37.2253 | 36.887 | 37.9666 | 34.4305 | 34.4469 | 34.0629 | 35.0069 | 34.9766 | 35.5173 | 36.1868 | 36.5384 | 30.713 | 30.3276 | 92.3281 | 34.2981 | 32.9507 | 34.9534 | 33.2335 | 33.0751 | 33.3682 | 34.7542 | 34.3218 | 34.0463 | 37.1719 | 36.1398 | 33.3493 | 34.3513 | 36.174 | 36.5255 | 37.3051 | 36.1632 | 33.2174 | 32.4015 | 34.2861 | 34.8199 | 32.7988 | 34.4132 | 34.2577 | 34.3557 | 34.3418 | 34.4127 | 34.3832 | 33.8132 | 34.3479 | 35.8361 | 35.1507 | 36.2817 | 36.218 | 33.4238 | 92.4047 | 92.3571 | 92.6978
2022-09-08 03:30 | 5:40 | 22.7282 | 22.187 | 25.8713 | 34.3081 | 34.3524 | 33.7725 | 34.4757 | 35.3578 | 36.4503 | 37.2351 | 36.8773 | 37.9507 | 34.4159 | 34.4279 | 34.0535 | 35.0103 | 35.0129 | 35.4916 | 36.1753 | 36.5283 | 30.7983 | 30.3766 | 92.3974 | 34.3125 | 32.9528 | 34.9389 | 33.2358 | 33.0418 | 33.3631 | 34.7371 | 34.3343 | 34.0678 | 37.1617 | 36.1339 | 33.3639 | 34.3553 | 36.1508 | 36.5264 | 37.2872 | 36.1555 | 33.1923 | 32.4036 | 34.2518 | 34.8094 | 32.7919 | 34.4238 | 34.2525 | 34.349 | 34.3498 | 34.3996 | 34.4034 | 33.8365 | 34.3418 | 35.8384 | 35.1268 | 36.2855 | 36.2494 | 33.4128 | 92.4844 | 92.5007 | 92.7724
2022-09-08 03:30 | 5:40 | 23.4194 | 23.2816 | 26.7285 | 34.5157 | 34.339 | 33.78 | 34.4785 | 35.3537 | 36.4684 | 37.2354 | 36.8788 | 37.9499 | 34.4245 | 34.4279 | 34.0507 | 34.9941 | 34.9667 | 35.4817 | 36.1803 | 36.556 | 30.8293 | 30.4253 | 92.6279 | 34.3692 | 32.9683 | 34.9402 | 33.2301 | 33.0576 | 33.3691 | 34.721 | 34.3149 | 34.0297 | 37.1783 | 36.1431 | 33.3737 | 34.3628 | 36.1398 | 36.5168 | 37.309 | 36.1626 | 33.2024 | 32.3945 | 34.2957 | 34.8176 | 32.8118 | 34.4121 | 34.2627 | 34.3421 | 34.3176 | 34.3892 | 34.3836 | 33.8412 | 34.3498 | 35.8482 | 35.1326 | 36.2804 | 36.2091 | 33.4212 | 92.5931 | 92.6304 | 92.8858
2022-09-08 03:30 | 5:40 | 24.8012 | 21.0036 | 26.9674 | 34.4449 | 34.3447 | 33.7798 | 34.4792 | 35.3447 | 36.4658 | 37.2458 | 36.8835 | 37.9486 | 34.4136 | 34.4199 | 34.0627 | 35.0157 | 34.9879 | 35.4981 | 36.208 | 36.5548 | 30.7095 | 24.9726 | 92.715 | 34.3719 | 32.9555 | 34.9587 | 33.2198 | 33.0607 | 33.3716 | 34.7447 | 34.3304 | 34.0665 | 37.1789 | 36.1312 | 33.3548 | 34.353 | 36.1339 | 36.5281 | 37.2887 | 36.174 | 33.2067 | 32.3712 | 34.2895 | 34.8141 | 32.8102 | 34.4179 | 34.2715 | 34.34 | 34.3354 | 34.4122 | 34.392 | 33.835 | 34.3176 | 35.8447 | 35.1336 | 36.2797 | 36.2202 | 33.4006 | 92.7434 | 92.7593 | 92.9578
2022-09-08 03:30 | 5:40 | 27.0731 | 27.158 | 27.4377 | 34.6164 | 34.3445 | 33.7597 | 34.4756 | 35.3511 | 36.4555 | 37.2419 | 36.8667 | 37.9557 | 34.4269 | 34.4316 | 34.0573 | 35.015 | 34.9759 | 35.4948 | 36.1967 | 36.5648 | 30.6179 | 26.2769 | 92.6107 | 34.3619 | 32.9475 | 34.9385 | 33.2174 | 33.0414 | 33.3493 | 34.7354 | 34.3059 | 34.0474 | 37.1567 | 36.15 | 33.3718 | 34.3546 | 36.1431 | 36.5134 | 37.287 | 36.1508 | 33.1947 | 32.391 | 34.3081 | 34.8107 | 32.8276 | 34.4172 | 34.2733 | 34.3432 | 34.3349 | 34.3923 | 34.3863 | 33.8385 | 34.3354 | 35.8394 | 35.1206 | 36.2903 | 36.2512 | 33.4124 | 92.798 | 92.8618 | 92.9704
2022-09-08 03:30 | 5:40 | 29.5504 | 29.3037 | 28.1926 | 34.6065 | 34.3313 | 33.7838 | 34.5018 | 35.3504 | 36.4442 | 37.2392 | 36.8682 | 37.9409 | 34.4188 | 34.4469 | 34.0775 | 35.0211 | 34.9826 | 35.505 | 36.2049 | 36.5551 | 30.965 | 28.2934 | 92.6921 | 34.3112 | 32.9681 | 34.9482 | 33.1923 | 33.0568 | 33.3639 | 34.7394 | 34.3239 | 34.0401 | 37.1533 | 36.154 | 33.3513 | 34.3667 | 36.1312 | 36.4876 | 37.2903 | 36.1398 | 33.2054 | 32.4067 | 34.2919 | 34.8003 | 32.8133 | 34.4247 | 34.2696 | 34.3653 | 34.3052 | 34.401 | 34.3792 | 33.8288 | 34.3349 | 35.8376 | 35.148 | 36.2897 | 36.2077 | 33.4091 | 92.8637 | 92.9677 | 92.9952
2022-09-08 03:31 | 5:40 | 30.8221 | 29.9491 | 29.026 | 34.7581 | 34.3636 | 33.7629 | 34.5204 | 35.344 | 36.4471 | 37.2402 | 36.8766 | 37.9484 | 34.4209 | 34.4431 | 34.0636 | 34.9987 | 34.9521 | 35.5056 | 36.2296 | 36.528 | 31.8074 | 29.3181 | 92.8233 | 34.3927 | 32.9507 | 34.9299 | 33.2024 | 33.0462 | 33.3737 | 34.7314 | 34.3051 | 34.0542 | 37.1595 | 36.1408 | 33.3764 | 34.3578 | 36.15 | 36.513 | 37.2789 | 36.1339 | 33.1975 | 32.3818 | 34.2986 | 34.8103 | 32.837 | 34.426 | 34.2707 | 34.3685 | 34.3244 | 34.3783 | 34.3816 | 33.8433 | 34.3052 | 35.8385 | 35.1335 | 36.2677 | 36.2346 | 33.432 | 92.9261 | 93.1237 | 93.0588
2022-09-08 03:31 | 5:41 | 31.3896 | 30.2449 | 29.4709 | 34.9134 | 34.3523 | 33.7664 | 34.5184 | 35.3521 | 36.4451 | 37.2573 | 36.8774 | 37.945 | 34.4249 | 34.4472 | 34.0853 | 34.995 | 34.962 | 35.4905 | 36.2197 | 36.5534 | 32.5856 | 29.8447 | 92.8379 | 34.3573 | 32.9529 | 34.9272 | 33.2067 | 33.0492 | 33.3548 | 34.7493 | 34.3379 | 34.0345 | 37.1722 | 36.1351 | 33.365 | 34.3622 | 36.154 | 36.4913 | 37.3018 | 36.1431 | 33.206 | 32.3862 | 34.2902 | 34.8041 | 32.8193 | 34.4326 | 34.2944 | 34.3612 | 34.3082 | 34.3928 | 34.4022 | 33.8433 | 34.3244 | 35.831 | 35.1193 | 36.2898 | 36.2242 | 33.4048 | 92.9801 | 93.1695 | 93.0933
2022-09-08 03:31 | 5:41 | 31.9296 | 30.4201 | 29.8293 | 34.8748 | 34.3511 | 33.7965 | 34.5292 | 35.3382 | 36.4706 | 37.2497 | 36.8799 | 37.9354 | 34.4249 | 34.4273 | 34.058 | 34.989 | 34.959 | 35.5051 | 36.2304 | 36.5489 | 33.2819 | 30.1423 | 92.7124 | 34.421 | 32.9712 | 34.9211 | 33.1947 | 33.0572 | 33.3718 | 34.7501 | 34.3194 | 34.042 | 37.1525 | 36.1408 | 33.3791 | 34.3646 | 36.1408 | 36.5002 | 37.2973 | 36.1312 | 33.1966 | 32.4063 | 34.3051 | 34.7988 | 32.8418 | 34.4374 | 34.2814 | 34.3607 | 34.3131 | 34.3933 | 34.418 | 33.8306 | 34.3082 | 35.8549 | 35.1373 | 36.2955 | 36.2341 | 33.4049 | 93.1396 | 93.2389 | 93.1454
2022-09-08 03:31 | 5:41 | 32.3015 | 30.5516 | 30.2964 | 34.9984 | 34.3342 | 33.7754 | 34.517 | 35.3621 | 36.4785 | 37.2468 | 36.8735 | 37.9506 | 34.4237 | 34.4391 | 34.0584 | 34.9976 | 34.9634 | 35.5293 | 36.2492 | 36.5449 | 33.7962 | 30.4698 | 92.8144 | 34.4588 | 32.9597 | 34.9257 | 33.2054 | 33.0569 | 33.3513 | 34.7535 | 34.3256 | 34.037 | 37.1411 | 36.1546 | 33.3749 | 34.3536 | 36.1351 | 36.4996 | 37.3059 | 36.15 | 33.2121 | 32.4026 | 34.2985 | 34.8147 | 32.8324 | 34.443 | 34.296 | 34.3558 | 34.2898 | 34.3804 | 34.3974 | 33.8439 | 34.3131 | 35.8583 | 35.1265 | 36.2779 | 36.2269 | 33.3838 | 93.31 | 93.3597 | 93.2568
2022-09-08 03:31 | 5:41 | 32.6494 | 30.6649 | 30.4614 | 34.9995 | 34.3608 | 33.8023 | 34.5396 | 35.3598 | 36.4573 | 37.2661 | 36.8808 | 37.9535 | 34.412 | 34.4219 | 34.0629 | 35.0037 | 34.9537 | 35.5098 | 36.2474 | 36.5505 | 34.124 | 30.7514 | 92.883 | 34.5651 | 32.9455 | 34.9117 | 33.1975 | 33.0641 | 33.3764 | 34.7405 | 34.3224 | 34.0378 | 37.1495 | 36.1581 | 33.3792 | 34.3614 | 36.1408 | 36.5166 | 37.3179 | 36.154 | 33.192 | 32.4058 | 34.3107 | 34.8213 | 32.8496 | 34.4445 | 34.2778 | 34.3766 | 34.3036 | 34.4116 | 34.3967 | 33.8272 | 34.2898 | 35.8579 | 35.124 | 36.2815 | 36.2156 | 33.4208 | 93.4446 | 93.4899 | 93.3618
2022-09-08 03:31 | 5:41 | 32.9601 | 30.742 | 30.7477 | 35.0535 | 34.3525 | 33.7921 | 34.527 | 35.3466 | 36.4686 | 37.2707 | 36.869 | 37.957 | 34.4337 | 34.4269 | 34.0759 | 34.9886 | 34.9557 | 35.5171 | 36.2514 | 36.5464 | 34.2603 | 30.9263 | 93.0259 | 34.5192 | 32.9362 | 34.9314 | 33.206 | 33.0807 | 33.365 | 34.7434 | 34.3067 | 34.0324 | 37.1589 | 36.1519 | 33.3604 | 34.3617 | 36.1546 | 36.5026 | 37.3129 | 36.1408 | 33.2057 | 32.4181 | 34.2947 | 34.8289 | 32.8679 | 34.4303 | 34.2818 | 34.3529 | 34.3063 | 34.3854 | 34.3908 | 33.8298 | 34.3036 | 35.8298 | 35.1099 | 36.283 | 36.2244 | 33.4091 | 93.5453 | 93.6112 | 93.4415
2022-09-08 03:32 | 5:42 | 33.1707 | 30.8207 | 30.9687 | 35.1349 | 34.3616 | 33.7734 | 34.5351 | 35.3666 | 36.4626 | 37.2826 | 36.8767 | 37.9337 | 34.4367 | 34.4476 | 34.0714 | 35.0004 | 34.9475 | 35.5387 | 36.2549 | 36.5631 | 34.3061 | 31.0414 | 93.1187 | 34.5694 | 32.9708 | 34.9361 | 33.1966 | 33.0675 | 33.3791 | 34.7487 | 34.3083 | 34.0342 | 37.1438 | 36.1354 | 33.3629 | 34.3644 | 36.1581 | 36.5162 | 37.3103 | 36.1351 | 33.2149 | 32.4114 | 34.3247 | 34.8094 | 32.8499 | 34.4451 | 34.2649 | 34.3656 | 34.3027 | 34.4085 | 34.4089 | 33.8343 | 34.3063 | 35.85 | 35.131 | 36.2872 | 36.2489 | 33.4161 | 93.7108 | 93.7678 | 93.5349
2022-09-08 03:32 | 5:42 | 33.2289 | 30.9013 | 31.0443 | 35.1859 | 34.3556 | 33.7922 | 34.5394 | 35.3663 | 36.4468 | 37.2686 | 36.8822 | 37.9297 | 34.4328 | 34.449 | 34.0617 | 35.0022 | 34.9488 | 35.5347 | 36.2719 | 36.5423 | 34.2779 | 31.1279 | 93.0914 | 34.6531 | 32.9729 | 34.9263 | 33.2121 | 33.0877 | 33.3749 | 34.7529 | 34.3165 | 34.0424 | 37.1686 | 36.1466 | 33.3713 | 34.3638 | 36.1519 | 36.4863 | 37.3132 | 36.1408 | 33.188 | 32.4149 | 34.3326 | 34.8445 | 32.8774 | 34.4376 | 34.2739 | 34.3706 | 34.2816 | 34.3962 | 34.4226 | 33.8262 | 34.3027 | 35.85 | 35.1263 | 36.2839 | 36.2308 | 33.412 | 93.8633 | 93.924 | 93.5623
2022-09-08 03:32 | 5:42 | 33.3573 | 30.9591 | 31.1941 | 35.3141 | 34.3518 | 33.7999 | 34.5463 | 35.3685 | 36.4662 | 37.2688 | 36.8683 | 37.9581 | 34.4064 | 34.4414 | 34.0604 | 34.9968 | 34.9454 | 35.5474 | 36.277 | 36.5479 | 34.2798 | 31.1807 | 93.3089 | 34.6772 | 32.9676 | 34.9263 | 33.192 | 33.0657 | 33.3792 | 34.7683 | 34.3196 | 34.0578 | 37.1491 | 36.1478 | 33.3638 | 34.38 | 36.1354 | 36.4896 | 37.3202 | 36.1546 | 33.2199 | 32.4145 | 34.3199 | 34.8332 | 32.8712 | 34.4296 | 34.2853 | 34.3792 | 34.2981 | 34.3828 | 34.4184 | 33.8294 | 34.2816 | 35.8557 | 35.1274 | 36.2736 | 36.2298 | 33.4297 | 93.9773 | 94.1239 | 93.4972
2022-09-08 03:32 | 5:42 | 33.4851 | 31.0565 | 31.3635 | 35.2897 | 34.3473 | 33.7882 | 34.5355 | 35.3749 | 36.4689 | 37.2654 | 36.8679 | 37.9369 | 34.4295 | 34.4258 | 34.0677 | 35.012 | 34.9496 | 35.525 | 36.2657 | 36.56 | 34.2546 | 31.2157 | 93.3841 | 34.6442 | 32.9542 | 34.922 | 33.2057 | 33.0664 | 33.3604 | 34.7529 | 34.3234 | 34.041 | 37.1477 | 36.152 | 33.3774 | 34.3677 | 36.1466 | 36.4958 | 37.306 | 36.1581 | 33.19 | 32.4312 | 34.3413 | 34.8492 | 32.883 | 34.4382 | 34.2891 | 34.3865 | 34.2981 | 34.371 | 34.4196 | 33.8443 | 34.2981 | 35.8655 | 35.1215 | 36.2744 | 36.2256 | 33.4265 | 94.16 | 94.2712 | 93.7039
2022-09-08 03:32 | 5:42 | 33.522 | 31.1169 | 31.4899 | 35.2476 | 34.3631 | 33.7932 | 34.5415 | 35.3516 | 36.4495 | 37.2727 | 36.8826 | 37.9506 | 34.4129 | 34.4204 | 34.0709 | 34.9976 | 34.9346 | 35.533 | 36.2873 | 36.5386 | 34.2168 | 31.2444 | 93.4863 | 34.6593 | 32.9854 | 34.9356 | 33.2149 | 33.0719 | 33.3629 | 34.7622 | 34.3199 | 34.0203 | 37.1509 | 36.1392 | 33.3438 | 34.364 | 36.1478 | 36.5114 | 37.3247 | 36.1519 | 33.1959 | 32.4361 | 34.3445 | 34.8398 | 32.8817 | 34.4312 | 34.2936 | 34.3806 | 34.2827 | 34.3776 | 34.4232 | 33.8337 | 34.2981 | 35.8491 | 35.1326 | 36.2706 | 36.2297 | 33.4018 | 94.1753 | 94.4277 | 93.7418
2022-09-08 03:32 | 5:42 | 33.5718 | 31.1705 | 31.6017 | 35.3329 | 34.3588 | 33.7878 | 34.5698 | 35.3701 | 36.4586 | 37.3032 | 36.8916 | 37.9505 | 34.4178 | 34.4527 | 34.1009 | 35.0119 | 34.9303 | 35.529 | 36.285 | 36.5539 | 34.1273 | 31.2824 | 93.5883 | 34.7252 | 32.9576 | 34.926 | 33.188 | 33.0584 | 33.3713 | 34.759 | 34.3091 | 34.0356 | 37.1465 | 36.1485 | 33.3686 | 34.3652 | 36.152 | 36.5004 | 37.3319 | 36.1354 | 33.1944 | 32.4357 | 34.3267 | 34.8393 | 32.8925 | 34.4579 | 34.2927 | 34.3863 | 34.2957 | 34.3658 | 34.4102 | 33.8502 | 34.2827 | 35.8501 | 35.114 | 36.2821 | 36.237 | 33.4034 | 94.3651 | 94.5961 | 93.9456
2022-09-08 03:33 | 5:42 | 33.5891 | 31.2076 | 31.6712 | 35.5077 | 34.3765 | 33.8055 | 34.5416 | 35.3711 | 36.444 | 37.2783 | 36.8808 | 37.9426 | 34.4223 | 34.4404 | 34.0706 | 35.014 | 34.9312 | 35.5492 | 36.2858 | 36.5555 | 33.9713 | 31.3076 | 93.8142 | 34.7218 | 32.967 | 34.9136 | 33.2199 | 33.0785 | 33.3638 | 34.7502 | 34.3239 | 34.0207 | 37.1466 | 36.1467 | 33.3682 | 34.3607 | 36.1392 | 36.4914 | 37.3211 | 36.1466 | 33.1792 | 32.4249 | 34.3374 | 34.8397 | 32.8994 | 34.4456 | 34.2907 | 34.392 | 34.2769 | 34.3654 | 34.4409 | 33.8339 | 34.2957 | 35.849 | 35.1179 | 36.2886 | 36.2283 | 33.3921 | 94.4754 | 94.7056 | 93.9627
2022-09-08 03:33 | 5:43 | 33.6312 | 31.2566 | 31.7878 | 35.4047 | 34.3375 | 33.8068 | 34.5462 | 35.3556 | 36.4581 | 37.2817 | 36.8739 | 37.9273 | 34.4268 | 34.4387 | 34.0588 | 35.0156 | 34.9476 | 35.5303 | 36.2959 | 36.5374 | 33.8774 | 31.3478 | 93.8428 | 34.764 | 32.9677 | 34.921 | 33.19 | 33.0807 | 33.3774 | 34.7545 | 34.3161 | 34.0291 | 37.1518 | 36.1399 | 33.3559 | 34.3869 | 36.1485 | 36.5053 | 37.3179 | 36.1478 | 33.1886 | 32.4326 | 34.3567 | 34.843 | 32.9126 | 34.4412 | 34.2996 | 34.3833 | 34.2938 | 34.3778 | 34.4239 | 33.8315 | 34.2769 | 35.8462 | 35.115 | 36.3017 | 36.2456 | 33.4093 | 94.6263 | 94.8155 | 94.059
2022-09-08 03:33 | 5:43 | 33.7369 | 31.3113 | 31.8849 | 35.5577 | 34.3617 | 33.7963 | 34.5566 | 35.3627 | 36.4571 | 37.2951 | 36.8754 | 37.9391 | 34.4336 | 34.4295 | 34.0626 | 35.0123 | 34.9274 | 35.5448 | 36.2953 | 36.5363 | 33.8126 | 31.3361 | 93.8631 | 34.8291 | 32.9588 | 34.9109 | 33.1959 | 33.0728 | 33.3438 | 34.7419 | 34.3117 | 34.0194 | 37.1497 | 36.149 | 33.3503 | 34.357 | 36.1467 | 36.479 | 37.2921 | 36.152 | 33.1952 | 32.4491 | 34.3607 | 34.8437 | 32.9013 | 34.4437 | 34.3058 | 34.3823 | 34.2731 | 34.3642 | 34.4106 | 33.834 | 34.2938 | 35.8483 | 35.1202 | 36.2769 | 36.2446 | 33.4172 | 94.7586 | 94.864 | 94.1795
2022-09-08 03:33 | 5:43 | 33.8369 | 31.3353 | 31.9755 | 35.6503 | 34.362 | 33.8032 | 34.5618 | 35.3715 | 36.4491 | 37.2785 | 36.87 | 37.9377 | 34.4344 | 34.4209 | 34.0543 | 35.0005 | 34.9259 | 35.534 | 36.3133 | 36.5497 | 33.7591 | 31.3551 | 93.887 | 34.79 | 32.9529 | 34.9072 | 33.1944 | 33.0406 | 33.3686 | 34.7562 | 34.3205 | 34.02 | 37.1311 | 36.1434 | 33.3464 | 34.3683 | 36.1399 | 36.4939 | 37.3053 | 36.1392 | 33.1847 | 32.4447 | 34.3486 | 34.8336 | 32.9301 | 34.4477 | 34.2985 | 34.4017 | 34.2923 | 34.359 | 34.4389 | 33.8541 | 34.2731 | 35.8506 | 35.12 | 36.2715 | 36.2337 | 33.3949 | 94.8415 | 94.9542 | 94.1776
2022-09-08 03:33 | 5:43 | 33.918 | 31.3633 | 32.0532 | 35.6594 | 34.3398 | 33.7926 | 34.5523 | 35.3623 | 36.4448 | 37.2788 | 36.8575 | 37.9494 | 34.4054 | 34.4295 | 34.0543 | 34.9922 | 34.9311 | 35.5257 | 36.2987 | 36.5406 | 33.7195 | 31.3602 | 93.9715 | 34.7291 | 32.9793 | 34.9083 | 33.1792 | 33.0819 | 33.3682 | 34.7396 | 34.3081 | 34.0224 | 37.1285 | 36.1412 | 33.3428 | 34.3676 | 36.149 | 36.4923 | 37.3176 | 36.1485 | 33.195 | 32.4279 | 34.3471 | 34.8549 | 32.9239 | 34.4351 | 34.3169 | 34.3862 | 34.2772 | 34.3712 | 34.4553 | 33.8171 | 34.2923 | 35.8562 | 35.1154 | 36.2822 | 36.2317 | 33.4081 | 94.842 | 94.994 | 94.2211
2022-09-08 03:33 | 5:43 | 33.9617 | 31.4008 | 32.1188 | 35.6982 | 34.3747 | 33.7805 | 34.5748 | 35.374 | 36.4412 | 37.2718 | 36.8525 | 37.9381 | 34.42 | 34.4387 | 34.0673 | 34.9922 | 34.9228 | 35.514 | 36.3058 | 36.5374 | 33.7371 | 31.3702 | 93.9522 | 34.7807 | 32.9667 | 34.9005 | 33.1886 | 33.0814 | 33.3559 | 34.7601 | 34.3166 | 34.0052 | 37.1487 | 36.1663 | 33.3489 | 34.3699 | 36.1434 | 36.5032 | 37.2992 | 36.1467 | 33.1949 | 32.4359 | 34.3448 | 34.8462 | 32.9204 | 34.4478 | 34.2959 | 34.3773 | 34.2701 | 34.3432 | 34.423 | 33.8345 | 34.2772 | 35.8181 | 35.1229 | 36.2795 | 36.2297 | 33.3996 | 94.7417 | 94.9153 | 94.1476
2022-09-08 03:34 | 5:44 | 33.9985 | 31.435 | 32.181 | 35.6818 | 34.3511 | 33.7793 | 34.5551 | 35.3662 | 36.4385 | 37.2782 | 36.8527 | 37.9352 | 34.4248 | 34.4251 | 34.0499 | 35.0144 | 34.9113 | 35.5326 | 36.2929 | 36.5243 | 33.7643 | 31.4045 | 93.8048 | 34.8337 | 32.9656 | 34.8935 | 33.1952 | 33.0684 | 33.3503 | 34.7569 | 34.2922 | 34.0051 | 37.1538 | 36.1682 | 33.3627 | 34.3541 | 36.1412 | 36.497 | 37.3007 | 36.1399 | 33.1957 | 32.4442 | 34.3622 | 34.837 | 32.9316 | 34.4459 | 34.2938 | 34.4033 | 34.2775 | 34.3388 | 34.4346 | 33.8476 | 34.2701 | 35.8358 | 35.1101 | 36.2761 | 36.2314 | 33.4069 | 94.5264 | 94.7192 | 93.9879
2022-09-08 03:34 | 5:44 | 34.0641 | 31.4579 | 32.2393 | 35.7206 | 34.3657 | 33.8112 | 34.5381 | 35.3697 | 36.4302 | 37.2716 | 36.872 | 37.9433 | 34.4016 | 34.4089 | 34.0502 | 35.0057 | 34.9245 | 35.5384 | 36.3002 | 36.5202 | 33.7699 | 31.3868 | 93.7025 | 34.8474 | 32.9609 | 34.9104 | 33.1847 | 33.0727 | 33.3464 | 34.7471 | 34.2815 | 34.0057 | 37.1461 | 36.1265 | 33.3526 | 34.378 | 36.1663 | 36.4962 | 37.2851 | 36.149 | 33.1992 | 32.4523 | 34.3708 | 34.8479 | 32.9496 | 34.4329 | 34.3121 | 34.4073 | 34.2698 | 34.3559 | 34.4469 | 33.8386 | 34.2775 | 35.8558 | 35.1146 | 36.3013 | 36.2255 | 33.3841 | 94.2863 | 94.4992 | 93.8567
2022-09-08 03:34 | 5:44 | 34.1503 | 31.4802 | 32.3247 | 35.844 | 34.3894 | 33.8165 | 34.563 | 35.3551 | 36.4312 | 37.2708 | 36.8574 | 37.9497 | 34.4262 | 34.423 | 34.0428 | 34.9901 | 34.9384 | 35.5123 | 36.302 | 36.5188 | 33.8829 | 31.408 | 93.5057 | 34.8897 | 32.9613 | 34.9299 | 33.195 | 33.0883 | 33.3428 | 34.7405 | 34.3103 | 34.0234 | 37.124 | 36.1634 | 33.3535 | 34.3797 | 36.1682 | 36.4846 | 37.2929 | 36.1434 | 33.1833 | 32.4613 | 34.3873 | 34.8298 | 32.9269 | 34.4528 | 34.3078 | 34.4149 | 34.2889 | 34.3475 | 34.4279 | 33.8242 | 34.2698 | 35.8472 | 35.1079 | 36.2697 | 36.244 | 33.3808 | 94.0679 | 94.2912 | 93.6896
2022-09-08 03:34 | 5:44 | 34.279 | 31.4954 | 32.4089 | 35.7591 | 34.3594 | 33.7843 | 34.5604 | 35.3665 | 36.4315 | 37.2868 | 36.8636 | 37.9334 | 34.4062 | 34.4268 | 34.0454 | 34.9937 | 34.9116 | 35.5282 | 36.2951 | 36.5244 | 33.9789 | 31.4256 | 93.3863 | 34.8522 | 32.962 | 34.9305 | 33.1949 | 33.0741 | 33.3489 | 34.7375 | 34.297 | 34.0213 | 37.1433 | 36.1716 | 33.372 | 34.3701 | 36.1265 | 36.4905 | 37.3151 | 36.1412 | 33.1861 | 32.4686 | 34.367 | 34.8535 | 32.9609 | 34.4457 | 34.3231 | 34.408 | 34.2827 | 34.3447 | 34.4279 | 33.8479 | 34.2889 | 35.8362 | 35.1118 | 36.271 | 36.2375 | 33.3927 | 93.9358 | 94.0869 | 93.6296
2022-09-08 03:34 | 5:44 | 34.4631 | 31.5197 | 32.4977 | 35.8399 | 34.3858 | 33.8141 | 34.558 | 35.3822 | 36.4239 | 37.2854 | 36.8533 | 37.9333 | 34.4174 | 34.4294 | 34.0656 | 34.986 | 34.9244 | 35.5223 | 36.3154 | 36.5339 | 34.0237 | 31.4494 | 93.4128 | 34.916 | 32.9594 | 34.9273 | 33.1957 | 33.077 | 33.3627 | 34.7382 | 34.3113 | 34.0186 | 37.133 | 36.1649 | 33.3631 | 34.3647 | 36.1634 | 36.4885 | 37.3071 | 36.1663 | 33.2039 | 32.4683 | 34.3659 | 34.8388 | 32.9606 | 34.4386 | 34.3181 | 34.4058 | 34.2647 | 34.3582 | 34.4199 | 33.8624 | 34.2827 | 35.8509 | 35.1146 | 36.2892 | 36.2192 | 33.3823 | 93.8218 | 93.9633 | 93.5722
2022-09-08 03:34 | 5:44 | 34.5692 | 31.5509 | 32.5939 | 35.8981 | 34.3832 | 33.7904 | 34.5613 | 35.3808 | 36.4282 | 37.2852 | 36.8686 | 37.9419 | 34.4225 | 34.4154 | 34.0658 | 35.0149 | 34.9158 | 35.5316 | 36.3065 | 36.542 | 34.1805 | 31.4381 | 93.2283 | 34.9238 | 32.9616 | 34.9125 | 33.1992 | 33.0665 | 33.3526 | 34.7591 | 34.3027 | 34.0089 | 37.1474 | 36.1487 | 33.3638 | 34.3608 | 36.1716 | 36.5099 | 37.3012 | 36.1682 | 33.1982 | 32.4701 | 34.3627 | 34.8434 | 32.962 | 34.455 | 34.3252 | 34.4159 | 34.2681 | 34.3384 | 34.4316 | 33.8578 | 34.2647 | 35.8483 | 35.12 | 36.2993 | 36.2361 | 33.3985 | 93.6996 | 93.8272 | 93.4553
2022-09-08 03:35 | 5:44 | 32.6172 | 31.3958 | 32.4805 | 35.9046 | 34.4034 | 33.8044 | 34.5756 | 35.3682 | 36.4179 | 37.2701 | 36.8661 | 37.9341 | 34.3985 | 34.4115 | 34.0633 | 35.01 | 34.9246 | 35.5383 | 36.3101 | 36.5393 | 32.1627 | 31.3638 | 93.2562 | 34.9973 | 32.9544 | 34.8997 | 33.1833 | 33.0627 | 33.3535 | 34.7493 | 34.2981 | 34.0179 | 37.1388 | 36.1629 | 33.3488 | 34.3751 | 36.1649 | 36.4995 | 37.2842 | 36.1265 | 33.2012 | 32.4727 | 34.3803 | 34.841 | 32.9705 | 34.4164 | 34.3314 | 34.4064 | 34.283 | 34.3388 | 34.4469 | 33.836 | 34.2681 | 35.8424 | 35.1367 | 36.2868 | 36.2427 | 33.3919 | 93.6271 | 93.7543 | 93.4356
2022-09-08 03:35 | 5:45 | 29.7144 | 30.1637 | 31.7999 | 35.8756 | 34.3836 | 33.8028 | 34.5766 | 35.3875 | 36.4202 | 37.2851 | 36.854 | 37.9579 | 34.4203 | 34.4068 | 34.0621 | 34.9976 | 34.9258 | 35.5457 | 36.3219 | 36.5261 | 28.0538 | 30.857 | 93.1127 | 34.8851 | 32.987 | 34.9352 | 33.1861 | 33.0684 | 33.372 | 34.758 | 34.2805 | 34.0056 | 37.1468 | 36.1681 | 33.3559 | 34.3691 | 36.1487 | 36.4778 | 37.3093 | 36.1634 | 33.2006 | 32.4749 | 34.3924 | 34.8665 | 33.0129 | 34.4336 | 34.2991 | 34.4028 | 34.2721 | 34.3219 | 34.4431 | 33.8306 | 34.283 | 35.8374 | 35.1243 | 36.2938 | 36.2242 | 33.371 | 93.5774 | 93.6701 | 93.3831
2022-09-08 03:35 | 5:45 | 30.9409 | 20.6071 | 31.7141 | 35.8424 | 34.392 | 33.7968 | 34.5652 | 35.3623 | 36.435 | 37.2866 | 36.8894 | 37.927 | 34.409 | 34.425 | 34.0395 | 35.0121 | 34.9329 | 35.5314 | 36.3158 | 36.5309 | 27.3877 | 30.8398 | 93.0729 | 34.8908 | 32.9619 | 34.9154 | 33.2039 | 33.0739 | 33.3631 | 34.7482 | 34.3229 | 34.0122 | 37.1336 | 36.1543 | 33.3651 | 34.3847 | 36.1629 | 36.495 | 37.3125 | 36.1716 | 33.2055 | 32.498 | 34.3595 | 34.8231 | 33.0057 | 34.4273 | 34.3191 | 34.4004 | 34.2586 | 34.3218 | 34.4472 | 33.8535 | 34.2721 | 35.8 | 35.1041 | 36.2891 | 36.2471 | 33.3863 | 93.4927 | 93.6062 | 93.3318
2022-09-08 03:35 | 5:45 | 31.5246 | 23.4139 | 31.9135 | 35.907 | 34.3863 | 33.812 | 34.5677 | 35.3701 | 36.4413 | 37.2801 | 36.8762 | 37.9566 | 34.4133 | 34.4166 | 34.033 | 34.9879 | 34.9135 | 35.5333 | 36.3206 | 36.5239 | 28.1096 | 30.839 | 93.0678 | 34.888 | 32.984 | 34.9171 | 33.1982 | 33.0832 | 33.3638 | 34.7502 | 34.3258 | 34.022 | 37.1417 | 36.1723 | 33.3618 | 34.3633 | 36.1681 | 36.4896 | 37.3353 | 36.1649 | 33.2011 | 32.4975 | 34.3883 | 34.8645 | 32.9924 | 34.4329 | 34.3173 | 34.3999 | 34.2583 | 34.3323 | 34.4273 | 33.8565 | 34.2586 | 35.8242 | 35.1176 | 36.2949 | 36.233 | 33.378 | 93.4713 | 93.5816 | 93.3318
2022-09-08 03:35 | 5:45 | 31.7436 | 26.0836 | 32.0445 | 35.9111 | 34.3792 | 33.8015 | 34.5763 | 35.381 | 36.4518 | 37.2996 | 36.8831 | 37.9468 | 34.4091 | 34.4046 | 34.0497 | 35.0038 | 34.9168 | 35.5655 | 36.317 | 36.5208 | 28.8277 | 30.8696 | 93.0111 | 35.0002 | 32.9882 | 34.9206 | 33.2012 | 33.0783 | 33.3488 | 34.7349 | 34.3047 | 34.0326 | 37.1377 | 36.1793 | 33.3636 | 34.3488 | 36.1543 | 36.4912 | 37.3279 | 36.1487 | 33.2037 | 32.4952 | 34.3849 | 34.8789 | 32.9846 | 34.4172 | 34.3165 | 34.4069 | 34.2704 | 34.345 | 34.4391 | 33.8555 | 34.2583 | 35.8399 | 35.1153 | 36.2699 | 36.2066 | 33.3869 | 93.3934 | 93.5477 | 93.284
2022-09-08 03:35 | 5:45 | 31.8544 | 27.8561 | 32.1225 | 35.9417 | 34.3816 | 33.8001 | 34.5698 | 35.3708 | 36.4243 | 37.3077 | 36.8753 | 37.9584 | 34.4104 | 34.3969 | 34.0271 | 34.9985 | 34.9194 | 35.5379 | 36.3279 | 36.5304 | 29.4643 | 30.9262 | 93.0312 | 35.0037 | 32.9713 | 34.9366 | 33.2006 | 33.0731 | 33.3559 | 34.7511 | 34.3071 | 34.0159 | 37.1272 | 36.177 | 33.3749 | 34.3704 | 36.1723 | 36.4918 | 37.3075 | 36.1629 | 33.197 | 32.4997 | 34.3845 | 34.8589 | 33.0175 | 34.4199 | 34.3 | 34.4079 | 34.2681 | 34.3195 | 34.4219 | 33.8608 | 34.2704 | 35.8377 | 35.1083 | 36.2737 | 36.2524 | 33.3942 | 93.354 | 93.4603 | 93.2716
2022-09-08 03:36 | 5:46 | 31.9722 | 29.0046 | 32.2086 | 35.8948 | 34.4022 | 33.8164 | 34.5735 | 35.3814 | 36.4308 | 37.301 | 36.8887 | 37.9452 | 34.409 | 34.3927 | 34.0579 | 34.9969 | 34.9205 | 35.5498 | 36.3106 | 36.5202 | 30.0072 | 30.982 | 93.0895 | 34.9968 | 32.9821 | 34.9182 | 33.2055 | 33.0784 | 33.3651 | 34.7475 | 34.3178 | 34.0077 | 37.1412 | 36.1758 | 33.3487 | 34.3722 | 36.1793 | 36.4922 | 37.3084 | 36.1681 | 33.206 | 32.4986 | 34.4214 | 34.8763 | 33.0203 | 34.4001 | 34.325 | 34.414 | 34.2561 | 34.3116 | 34.4269 | 33.8586 | 34.2681 | 35.862 | 35.1233 | 36.2716 | 36.2312 | 33.3753 | 93.2998 | 93.412 | 93.2533
2022-09-08 03:36 | 5:46 | 32.0255 | 29.702 | 32.2573 | 35.9068 | 34.418 | 33.802 | 34.5681 | 35.3634 | 36.4222 | 37.2834 | 36.882 | 37.947 | 34.4054 | 34.3927 | 34.0524 | 35.0234 | 34.9423 | 35.5508 | 36.3297 | 36.5412 | 30.4317 | 31.0326 | 92.9966 | 34.9584 | 32.9705 | 34.91 | 33.2011 | 33.0737 | 33.3618 | 34.7188 | 34.3003 | 34.0354 | 37.1422 | 36.1561 | 33.3554 | 34.3755 | 36.177 | 36.4956 | 37.311 | 36.1543 | 33.2034 | 32.5182 | 34.4031 | 34.8758 | 33.03 | 34.4151 | 34.3387 | 34.4321 | 34.2619 | 34.3142 | 34.4476 | 33.862 | 34.2561 | 35.8513 | 35.1253 | 36.2708 | 36.2411 | 33.3801 | 93.18 | 93.3087 | 93.1829
2022-09-08 03:36 | 5:46 | 32.0996 | 30.1752 | 32.3288 | 35.9503 | 34.3974 | 33.8155 | 34.5783 | 35.3788 | 36.4613 | 37.3165 | 36.8735 | 37.9551 | 34.3984 | 34.3944 | 34.0549 | 35.0097 | 34.9465 | 35.5478 | 36.3345 | 36.5107 | 30.7747 | 31.1044 | 92.873 | 35.1174 | 32.9541 | 34.9251 | 33.2037 | 33.068 | 33.3636 | 34.7559 | 34.3173 | 34.0137 | 37.162 | 36.1655 | 33.3806 | 34.3859 | 36.1758 | 36.4848 | 37.3099 | 36.1723 | 33.2295 | 32.5183 | 34.4035 | 34.8791 | 33.018 | 34.4106 | 34.3204 | 34.4082 | 34.2527 | 34.3204 | 34.449 | 33.8587 | 34.2619 | 35.8724 | 35.1143 | 36.2884 | 36.2217 | 33.3936 | 93.139 | 93.2388 | 93.1392
2022-09-08 03:36 | 5:46 | 32.16 | 30.5012 | 32.3691 | 36.0157 | 34.3967 | 33.8232 | 34.5607 | 35.3818 | 36.4258 | 37.2862 | 36.8789 | 37.9702 | 34.4037 | 34.4015 | 34.0613 | 35.0013 | 34.9223 | 35.5599 | 36.3339 | 36.5459 | 31.0158 | 31.1393 | 92.8079 | 35.0408 | 32.9666 | 34.9328 | 33.197 | 33.0932 | 33.3749 | 34.7506 | 34.3168 | 34.0381 | 37.1407 | 36.1791 | 33.3626 | 34.3797 | 36.1561 | 36.5048 | 37.3196 | 36.1793 | 33.2036 | 32.5305 | 34.3956 | 34.8949 | 33.0452 | 34.4168 | 34.3322 | 34.4182 | 34.2639 | 34.3077 | 34.4414 | 33.8499 | 34.2527 | 35.8473 | 35.1115 | 36.2726 | 36.2261 | 33.395 | 93.032 | 93.137 | 93.0356
2022-09-08 03:36 | 5:46 | 32.2382 | 30.7137 | 32.4037 | 36.0498 | 34.3908 | 33.8188 | 34.584 | 35.3763 | 36.452 | 37.3027 | 36.8811 | 37.9643 | 34.4099 | 34.3947 | 34.0662 | 35.0166 | 34.9414 | 35.5615 | 36.3296 | 36.5466 | 31.276 | 31.1768 | 92.8272 | 35.005 | 32.9603 | 34.9312 | 33.206 | 33.0779 | 33.3487 | 34.7356 | 34.3226 | 34.0134 | 37.153 | 36.185 | 33.3665 | 34.376 | 36.1655 | 36.5093 | 37.3296 | 36.177 | 33.2084 | 32.537 | 34.4366 | 34.9049 | 33.0489 | 34.4091 | 34.3381 | 34.4147 | 34.2508 | 34.314 | 34.4258 | 33.8654 | 34.2639 | 35.8501 | 35.111 | 36.3045 | 36.2506 | 33.3823 | 92.9805 | 93.0695 | 92.9854
2022-09-08 03:36 | 5:46 | 32.2918 | 30.8883 | 32.4397 | 36.0857 | 34.4089 | 33.8207 | 34.5861 | 35.3648 | 36.4327 | 37.3134 | 36.8777 | 37.9509 | 34.4007 | 34.4125 | 34.0505 | 35.0162 | 34.9369 | 35.5364 | 36.3335 | 36.5394 | 31.4617 | 31.2095 | 92.7625 | 35.0643 | 32.978 | 34.9434 | 33.2034 | 33.0745 | 33.3554 | 34.7501 | 34.3111 | 34.0256 | 37.1508 | 36.1844 | 33.3629 | 34.3673 | 36.1791 | 36.4891 | 37.3313 | 36.1758 | 33.208 | 32.5508 | 34.4224 | 34.8782 | 33.0508 | 34.4137 | 34.3467 | 34.4103 | 34.2626 | 34.3132 | 34.4204 | 33.8711 | 34.2508 | 35.8463 | 35.1157 | 36.2746 | 36.2414 | 33.4087 | 92.894 | 92.9698 | 92.9179
2022-09-08 03:37 | 5:46 | 32.3421 | 31.0123 | 32.4946 | 36.0798 | 34.4226 | 33.7996 | 34.6003 | 35.3725 | 36.4582 | 37.3102 | 36.8832 | 37.9394 | 34.3993 | 34.4137 | 34.0656 | 35.0087 | 34.9385 | 35.5632 | 36.3432 | 36.5264 | 31.5983 | 31.23 | 92.6823 | 35.0297 | 32.9815 | 34.9414 | 33.2295 | 33.0736 | 33.3806 | 34.7498 | 34.3267 | 34.0188 | 37.1542 | 36.186 | 33.356 | 34.377 | 36.185 | 36.4987 | 37.3339 | 36.1561 | 33.2189 | 32.5292 | 34.4372 | 34.9158 | 33.0574 | 34.3952 | 34.3486 | 34.4113 | 34.2634 | 34.2918 | 34.4527 | 33.8701 | 34.2626 | 35.8607 | 35.1116 | 36.2852 | 36.2524 | 33.3968 | 92.7972 | 92.9045 | 92.8727
2022-09-08 03:37 | 5:47 | 32.4006 | 31.1022 | 32.4989 | 35.9694 | 34.4184 | 33.8025 | 34.5782 | 35.3806 | 36.4568 | 37.3175 | 36.8663 | 37.9662 | 34.4127 | 34.3845 | 34.0663 | 35.0182 | 34.9324 | 35.5593 | 36.3592 | 36.5611 | 31.7251 | 31.2786 | 92.4948 | 35.0906 | 32.9744 | 34.9273 | 33.2036 | 33.0894 | 33.3626 | 34.7506 | 34.3183 | 34.0206 | 37.1411 | 36.194 | 33.3589 | 34.3724 | 36.1844 | 36.4854 | 37.3416 | 36.1655 | 33.2187 | 32.5512 | 34.4265 | 34.9126 | 33.0652 | 34.3969 | 34.3317 | 34.4163 | 34.2439 | 34.2875 | 34.4404 | 33.8749 | 34.2634 | 35.8702 | 35.1203 | 36.2916 | 36.2492 | 33.4044 | 92.7201 | 92.7745 | 92.7816
2022-09-08 03:37 | 5:47 | 32.4471 | 31.1686 | 32.5523 | 36.1057 | 34.4196 | 33.821 | 34.5913 | 35.3818 | 36.434 | 37.3049 | 36.8891 | 37.9675 | 34.3996 | 34.4024 | 34.0538 | 35.0141 | 34.9464 | 35.555 | 36.3569 | 36.5441 | 31.8316 | 31.2844 | 92.4034 | 35.0612 | 32.9653 | 34.9406 | 33.2084 | 33.0644 | 33.3665 | 34.7489 | 34.3164 | 34.0373 | 37.1553 | 36.1776 | 33.364 | 34.3838 | 36.186 | 36.5026 | 37.3344 | 36.1791 | 33.2246 | 32.5622 | 34.4418 | 34.9047 | 33.0784 | 34.3822 | 34.3325 | 34.4302 | 34.2523 | 34.292 | 34.4387 | 33.8777 | 34.2439 | 35.864 | 35.1099 | 36.2918 | 36.2591 | 33.3998 | 92.5124 | 92.6418 | 92.6418
2022-09-08 03:37 | 5:47 | 32.4611 | 31.2296 | 32.5837 | 36.1135 | 34.4232 | 33.8201 | 34.603 | 35.3946 | 36.4526 | 37.3093 | 36.882 | 37.9462 | 34.3892 | 34.391 | 34.062 | 35.0044 | 34.9526 | 35.5624 | 36.3578 | 36.5327 | 31.9255 | 31.3199 | 92.5137 | 35.1341 | 32.9664 | 34.9289 | 33.208 | 33.0667 | 33.3629 | 34.76 | 34.322 | 34.0177 | 37.1562 | 36.1866 | 33.3598 | 34.3763 | 36.194 | 36.5329 | 37.3229 | 36.185 | 33.2306 | 32.5545 | 34.4707 | 34.9453 | 33.0895 | 34.3891 | 34.3365 | 34.4363 | 34.2518 | 34.2984 | 34.4295 | 33.8672 | 34.2523 | 35.8645 | 35.1013 | 36.2947 | 36.2478 | 33.4198 | 92.4573 | 92.5341 | 92.7038
2022-09-08 03:37 | 5:47 | 32.4876 | 31.2882 | 32.6014 | 36.1832 | 34.4102 | 33.8263 | 34.5894 | 35.3794 | 36.4484 | 37.3193 | 36.9076 | 37.9775 | 34.4122 | 34.3988 | 34.0821 | 35.0084 | 34.9372 | 35.5637 | 36.3417 | 36.5532 | 32.005 | 31.3355 | 92.2575 | 35.1161 | 32.9878 | 34.9564 | 33.2189 | 33.0849 | 33.356 | 34.7497 | 34.314 | 34.0224 | 37.156 | 36.1901 | 33.3758 | 34.3947 | 36.1776 | 36.4936 | 37.3493 | 36.1844 | 33.2026 | 32.557 | 34.4716 | 34.9255 | 33.104 | 34.3849 | 34.3537 | 34.4237 | 34.2437 | 34.3025 | 34.4209 | 33.8819 | 34.2518 | 35.8731 | 35.1112 | 36.2873 | 36.2638 | 33.4187 | 92.3556 | 92.4255 | 92.6256
2022-09-08 03:37 | 5:47 | 32.5468 | 31.3213 | 32.6355 | 36.2182 | 34.4409 | 33.831 | 34.6024 | 35.3837 | 36.4586 | 37.323 | 36.8875 | 37.9657 | 34.3923 | 34.4069 | 34.0758 | 35.0113 | 34.9376 | 35.578 | 36.3536 | 36.5404 | 32.0533 | 31.3714 | 92.236 | 35.0981 | 32.9887 | 34.9336 | 33.2187 | 33.0814 | 33.3589 | 34.7352 | 34.3161 | 34.0222 | 37.174 | 36.1807 | 33.3505 | 34.3847 | 36.1866 | 36.5031 | 37.3315 | 36.186 | 33.223 | 32.5668 | 34.4735 | 34.9376 | 33.0927 | 34.3789 | 34.3381 | 34.4293 | 34.2599 | 34.2946 | 34.4295 | 33.8824 | 34.2437 | 35.8698 | 35.1123 | 36.284 | 36.2384 | 33.4172 | 92.3119 | 92.281 | 92.484
2022-09-08 03:38 | 5:47 | 32.6158 | 31.3859 | 32.6774 | 36.1903 | 34.4239 | 33.821 | 34.5894 | 35.4031 | 36.4453 | 37.3134 | 36.8931 | 37.9666 | 34.401 | 34.3873 | 34.077 | 35.0076 | 34.9458 | 35.5833 | 36.3638 | 36.5418 | 32.2505 | 31.3835 | 92.1347 | 35.1368 | 32.9721 | 34.9505 | 33.2246 | 33.0916 | 33.364 | 34.7477 | 34.3187 | 34.0067 | 37.1689 | 36.1807 | 33.3719 | 34.3872 | 36.1901 | 36.5108 | 37.3434 | 36.194 | 33.2205 | 32.5635 | 34.483 | 34.9433 | 33.1036 | 34.3824 | 34.3456 | 34.4425 | 34.2711 | 34.2906 | 34.4387 | 33.8947 | 34.2599 | 35.8694 | 35.1309 | 36.2985 | 36.2642 | 33.4216 | 92.1952 | 92.0809 | 92.4014
2022-09-08 03:38 | 5:48 | 32.6633 | 31.424 | 32.6959 | 36.1982 | 34.4106 | 33.828 | 34.5846 | 35.3948 | 36.4618 | 37.3284 | 36.9034 | 37.9557 | 34.3783 | 34.3816 | 34.0583 | 35.0212 | 34.9505 | 35.579 | 36.3803 | 36.5517 | 32.3797 | 31.4086 | 91.9749 | 35.1264 | 32.9911 | 34.9456 | 33.2306 | 33.103 | 33.3598 | 34.748 | 34.3362 | 34.0206 | 37.1719 | 36.1997 | 33.3641 | 34.3799 | 36.1807 | 36.5122 | 37.341 | 36.1776 | 33.2206 | 32.5766 | 34.4885 | 34.9449 | 33.1106 | 34.3919 | 34.351 | 34.4411 | 34.2577 | 34.2902 | 34.4251 | 33.8961 | 34.2711 | 35.8807 | 35.1204 | 36.3054 | 36.2513 | 33.4454 | 91.9665 | 91.9506 | 92.2284
2022-09-08 03:38 | 5:48 | 32.7077 | 31.7394 | 32.7251 | 36.2258 | 34.4389 | 33.8123 | 34.5752 | 35.4026 | 36.457 | 37.324 | 36.8894 | 37.9741 | 34.3928 | 34.398 | 34.0817 | 35.026 | 34.948 | 35.5741 | 36.371 | 36.5431 | 32.8262 | 31.9585 | 91.9614 | 35.2767 | 32.9895 | 34.9336 | 33.2026 | 33.092 | 33.3758 | 34.761 | 34.2935 | 34.0269 | 37.1499 | 36.2048 | 33.372 | 34.3831 | 36.1807 | 36.5162 | 37.3338 | 36.1866 | 33.2172 | 32.5843 | 34.5012 | 34.9587 | 33.1048 | 34.385 | 34.3601 | 34.424 | 34.2525 | 34.2858 | 34.4089 | 33.8977 | 34.2577 | 35.8934 | 35.1159 | 36.2999 | 36.2556 | 33.4164 | 91.8089 | 91.8635 | 92.2604
2022-09-08 03:38 | 5:48 | 33.2102 | 31.7426 | 32.991 | 36.1899 | 34.4553 | 33.8306 | 34.5872 | 35.3987 | 36.4509 | 37.3291 | 36.8921 | 37.9809 | 34.3933 | 34.3923 | 34.0937 | 35.0131 | 34.9522 | 35.5789 | 36.3599 | 36.556 | 33.3902 | 32.2215 | 91.7755 | 35.1679 | 32.9879 | 34.932 | 33.223 | 33.0791 | 33.3505 | 34.7596 | 34.3075 | 34.0461 | 37.1561 | 36.1958 | 33.3684 | 34.3863 | 36.1997 | 36.4972 | 37.3408 | 36.1901 | 33.223 | 32.6005 | 34.4943 | 34.9618 | 33.1172 | 34.3715 | 34.3682 | 34.44 | 34.2627 | 34.286 | 34.423 | 33.8996 | 34.2525 | 35.8807 | 35.1017 | 36.2866 | 36.2674 | 33.4384 | 91.6522 | 91.7494 | 92.151
2022-09-08 03:38 | 5:48 | 34.1141 | 31.7063 | 33.2323 | 36.1615 | 34.423 | 33.8236 | 34.5893 | 35.4019 | 36.461 | 37.333 | 36.8784 | 37.9861 | 34.3804 | 34.3978 | 34.0823 | 35.0322 | 34.9598 | 35.5795 | 36.3761 | 36.5523 | 34.0383 | 32.3312 | 91.6609 | 35.2767 | 32.9999 | 34.9714 | 33.2205 | 33.1001 | 33.3719 | 34.7576 | 34.319 | 34.0375 | 37.1769 | 36.1893 | 33.3767 | 34.4115 | 36.2048 | 36.5175 | 37.3606 | 36.1807 | 33.2202 | 32.615 | 34.51 | 34.9694 | 33.1242 | 34.3791 | 34.3592 | 34.4454 | 34.2715 | 34.2851 | 34.4268 | 33.891 | 34.2627 | 35.8938 | 35.1107 | 36.3027 | 36.2684 | 33.433 | 91.6296 | 91.7066 | 92.155
2022-09-08 03:38 | 5:48 | 34.7859 | 31.6937 | 33.4526 | 36.2193 | 34.4346 | 33.8224 | 34.5963 | 35.4047 | 36.4561 | 37.333 | 36.8869 | 37.9641 | 34.4116 | 34.3691 | 34.0955 | 35.023 | 34.9404 | 35.5611 | 36.3856 | 36.5691 | 34.5787 | 32.2533 | 91.8124 | 35.2645 | 33.0169 | 34.9354 | 33.2206 | 33.105 | 33.3641 | 34.7665 | 34.3095 | 34.0306 | 37.1622 | 36.1857 | 33.3652 | 34.3948 | 36.1958 | 36.526 | 37.3453 | 36.1807 | 33.2278 | 32.6074 | 34.5108 | 34.9615 | 33.1343 | 34.3557 | 34.3334 | 34.4384 | 34.2733 | 34.2716 | 34.4294 | 33.9077 | 34.2715 | 35.8859 | 35.1047 | 36.3106 | 36.2565 | 33.4475 | 91.6277 | 91.7138 | 92.1458
2022-09-08 03:39 | 5:49 | 35.0398 | 31.6947 | 33.5932 | 36.2151 | 34.4469 | 33.8295 | 34.61 | 35.4108 | 36.4625 | 37.3541 | 36.8926 | 37.9693 | 34.3854 | 34.3905 | 34.0904 | 35.0115 | 34.9601 | 35.5729 | 36.3868 | 36.5605 | 34.7587 | 32.0615 | 91.8255 | 35.352 | 32.99 | 34.9645 | 33.2172 | 33.0928 | 33.372 | 34.7587 | 34.3201 | 34.0219 | 37.1691 | 36.1896 | 33.3823 | 34.3792 | 36.1893 | 36.5246 | 37.3556 | 36.1997 | 33.2099 | 32.5954 | 34.5013 | 34.9782 | 33.13 | 34.3709 | 34.3646 | 34.4509 | 34.2696 | 34.2707 | 34.4154 | 33.9126 | 34.2733 | 35.8892 | 35.1111 | 36.2818 | 36.2649 | 33.4523 | 91.729 | 91.845 | 92.1355
2022-09-08 03:39 | 5:49 | 35.124 | 31.7122 | 33.596 | 36.3187 | 34.4279 | 33.8221 | 34.5953 | 35.4078 | 36.4571 | 37.3411 | 36.8814 | 37.9813 | 34.4085 | 34.3845 | 34.0958 | 35.0288 | 34.9589 | 35.5781 | 36.3713 | 36.5494 | 34.8706 | 31.9793 | 91.8736 | 35.3293 | 33.0021 | 34.9398 | 33.223 | 33.0938 | 33.3684 | 34.7544 | 34.3361 | 34.0276 | 37.1758 | 36.1911 | 33.3637 | 34.393 | 36.1857 | 36.5112 | 37.3543 | 36.2048 | 33.2195 | 32.6215 | 34.5068 | 34.9549 | 33.1354 | 34.3693 | 34.3543 | 34.4368 | 34.2707 | 34.2963 | 34.4115 | 33.9183 | 34.2696 | 35.8943 | 35.1064 | 36.298 | 36.2676 | 33.4457 | 91.8212 | 91.9276 | 92.2381
2022-09-08 03:39 | 5:49 | 35.1708 | 31.7356 | 33.6614 | 36.3618 | 34.4279 | 33.8421 | 34.6085 | 35.3999 | 36.4559 | 37.3468 | 36.8929 | 37.9562 | 34.3962 | 34.3658 | 34.0812 | 35.0021 | 34.9501 | 35.567 | 36.3859 | 36.5523 | 34.9794 | 31.9817 | 91.9163 | 35.3373 | 33.0088 | 34.9492 | 33.2202 | 33.0975 | 33.3767 | 34.7611 | 34.3266 | 34.0339 | 37.1487 | 36.1887 | 33.3661 | 34.4001 | 36.1896 | 36.515 | 37.3758 | 36.1958 | 33.2047 | 32.6263 | 34.5344 | 34.9646 | 33.142 | 34.371 | 34.3653 | 34.4566 | 34.2944 | 34.2767 | 34.4068 | 33.9025 | 34.2707 | 35.9083 | 35.0942 | 36.3013 | 36.2781 | 33.4414 | 91.8786 | 92.0147 | 92.3002
2022-09-08 03:39 | 5:49 | 35.1711 | 31.734 | 33.6931 | 36.4352 | 34.4199 | 33.8259 | 34.5947 | 35.4058 | 36.4731 | 37.3211 | 36.8816 | 37.9665 | 34.3828 | 34.3918 | 34.0937 | 35.0165 | 34.9659 | 35.5831 | 36.3899 | 36.5585 | 34.9671 | 31.9013 | 92.0637 | 35.3323 | 33.0005 | 34.9537 | 33.2278 | 33.1026 | 33.3652 | 34.7848 | 34.3008 | 34.0328 | 37.1487 | 36.1762 | 33.3892 | 34.3887 | 36.1911 | 36.5163 | 37.3416 | 36.1893 | 33.2337 | 32.6177 | 34.5306 | 34.998 | 33.1425 | 34.3707 | 34.3484 | 34.4528 | 34.2814 | 34.2881 | 34.425 | 33.9195 | 34.2944 | 35.911 | 35.1147 | 36.292 | 36.28 | 33.4601 | 91.9573 | 92.1471 | 92.2791
2022-09-08 03:39 | 5:49 | 35.0269 | 31.7528 | 33.5917 | 36.3657 | 34.4316 | 33.8144 | 34.6023 | 35.3957 | 36.4698 | 37.349 | 36.8907 | 37.9595 | 34.371 | 34.3617 | 34.0796 | 35.0172 | 34.9421 | 35.5774 | 36.3863 | 36.5679 | 34.9096 | 31.8738 | 91.9967 | 35.3387 | 33.0016 | 34.9443 | 33.2099 | 33.0996 | 33.3823 | 34.7564 | 34.3253 | 34.0083 | 37.1594 | 36.1968 | 33.3714 | 34.3925 | 36.1887 | 36.5109 | 37.3608 | 36.1857 | 33.2036 | 32.6327 | 34.5262 | 35.0119 | 33.1792 | 34.3559 | 34.3619 | 34.4496 | 34.296 | 34.2839 | 34.4166 | 33.9167 | 34.2814 | 35.9027 | 35.1143 | 36.2925 | 36.279 | 33.4778 | 92.0647 | 92.2122 | 92.4066
2022-09-08 03:39 | 5:49 | 35.0159 | 31.7613 | 33.4737 | 36.3299 | 34.4469 | 33.8065 | 34.6069 | 35.4046 | 36.4588 | 37.3427 | 36.8907 | 37.9694 | 34.3776 | 34.3536 | 34.0894 | 35.0116 | 34.9636 | 35.5798 | 36.3695 | 36.5847 | 34.9075 | 31.8542 | 92.0439 | 35.3643 | 33.0061 | 34.9412 | 33.2195 | 33.1064 | 33.3637 | 34.7672 | 34.3007 | 34.0254 | 37.1835 | 36.1818 | 33.3795 | 34.3881 | 36.1762 | 36.5057 | 37.3638 | 36.1896 | 33.2046 | 32.6335 | 34.5428 | 34.9927 | 33.1722 | 34.3669 | 34.3503 | 34.4403 | 34.2778 | 34.2905 | 34.4046 | 33.9371 | 34.296 | 35.9075 | 35.1013 | 36.3086 | 36.2894 | 33.4724 | 92.1667 | 92.3371 | 92.4635
2022-09-08 03:40 | 5:49 | 34.9671 | 31.7789 | 33.4238 | 36.304 | 34.4431 | 33.8096 | 34.5785 | 35.3967 | 36.4616 | 37.3387 | 36.8757 | 37.9546 | 34.3658 | 34.3628 | 34.1059 | 34.9998 | 34.9478 | 35.5859 | 36.3785 | 36.5532 | 34.9245 | 31.8512 | 92.0138 | 35.3864 | 33.0146 | 34.949 | 33.2047 | 33.0994 | 33.3661 | 34.7749 | 34.3139 | 34.0163 | 37.1584 | 36.1865 | 33.3649 | 34.3882 | 36.1968 | 36.5024 | 37.3672 | 36.1911 | 33.2346 | 32.6344 | 34.5275 | 34.997 | 33.1868 | 34.3586 | 34.3664 | 34.4414 | 34.2818 | 34.2812 | 34.3969 | 33.9065 | 34.2778 | 35.8858 | 35.0961 | 36.2929 | 36.266 | 33.4613 | 92.3154 | 92.4387 | 92.473
2022-09-08 03:40 | 5:50 | 34.822 | 31.7731 | 33.4058 | 36.3826 | 34.4472 | 33.8133 | 34.6176 | 35.3846 | 36.4667 | 37.3531 | 36.8681 | 37.9544 | 34.3654 | 34.3686 | 34.0937 | 35.0157 | 34.9452 | 35.5676 | 36.4002 | 36.5644 | 34.9014 | 31.8348 | 92.1645 | 35.383 | 33.0139 | 34.9342 | 33.2337 | 33.0963 | 33.3892 | 34.7713 | 34.294 | 34.0205 | 37.151 | 36.1839 | 33.3803 | 34.3893 | 36.1818 | 36.5157 | 37.3622 | 36.1887 | 33.2228 | 32.6383 | 34.5558 | 34.998 | 33.1899 | 34.3725 | 34.3669 | 34.4326 | 34.2649 | 34.2769 | 34.3927 | 33.9246 | 34.2818 | 35.9005 | 35.1037 | 36.295 | 36.2832 | 33.4649 | 92.4261 | 92.6082 | 92.3898
2022-09-08 03:40 | 5:50 | 34.6335 | 31.7847 | 33.3875 | 36.4635 | 34.4273 | 33.817 | 34.589 | 35.4025 | 36.4717 | 37.3499 | 36.8863 | 37.9637 | 34.3778 | 34.3774 | 34.0879 | 35.0256 | 34.951 | 35.5831 | 36.3813 | 36.5808 | 34.9389 | 31.8371 | 92.2818 | 35.4557 | 33.0228 | 34.9346 | 33.2036 | 33.0857 | 33.3714 | 34.7675 | 34.314 | 34.0119 | 37.1744 | 36.1962 | 33.3826 | 34.3898 | 36.1865 | 36.5007 | 37.3769 | 36.1762 | 33.2096 | 32.6476 | 34.55 | 35.0018 | 33.1742 | 34.3397 | 34.3692 | 34.458 | 34.2739 | 34.2715 | 34.3927 | 33.9102 | 34.2649 | 35.8925 | 35.0958 | 36.3017 | 36.2742 | 33.4516 | 92.5446 | 92.6799 | 92.5851
2022-09-08 03:40 | 5:50 | 34.7265 | 31.7812 | 33.4151 | 36.5225 | 34.4391 | 33.8134 | 34.5833 | 35.4093 | 36.4505 | 37.3379 | 36.879 | 37.9604 | 34.3642 | 34.3532 | 34.0845 | 35.0134 | 34.9555 | 35.5812 | 36.3826 | 36.5899 | 35.0065 | 31.8514 | 92.2903 | 35.3771 | 33.0175 | 34.9443 | 33.2046 | 33.0966 | 33.3795 | 34.7667 | 34.3114 | 34.0249 | 37.1706 | 36.1798 | 33.3927 | 34.386 | 36.1839 | 36.4968 | 37.3731 | 36.1968 | 33.2092 | 32.6588 | 34.5617 | 35.0048 | 33.1886 | 34.3448 | 34.3773 | 34.4617 | 34.2853 | 34.2877 | 34.3944 | 33.9302 | 34.2739 | 35.913 | 35.0985 | 36.3118 | 36.2803 | 33.4743 | 92.6413 | 92.769 | 92.6609
2022-09-08 03:40 | 5:50 | 35.0361 | 31.793 | 33.4976 | 36.3927 | 34.4219 | 33.8119 | 34.5901 | 35.3914 | 36.4728 | 37.336 | 36.8814 | 37.9682 | 34.359 | 34.3604 | 34.1091 | 35.022 | 34.9382 | 35.5641 | 36.3946 | 36.5741 | 35.0806 | 31.8629 | 92.4476 | 35.391 | 33.0301 | 34.9512 | 33.2346 | 33.0852 | 33.3649 | 34.7819 | 34.2933 | 34.0253 | 37.163 | 36.1844 | 33.3801 | 34.3754 | 36.1962 | 36.5083 | 37.3792 | 36.1818 | 33.2185 | 32.6558 | 34.5464 | 35.0084 | 33.1896 | 34.3559 | 34.3742 | 34.4287 | 34.2891 | 34.2848 | 34.4015 | 33.9485 | 34.2853 | 35.9006 | 35.107 | 36.2898 | 36.2704 | 33.4703 | 92.738 | 92.8755 | 92.7608
2022-09-08 03:40 | 5:50 | 35.1041 | 31.8104 | 33.5128 | 36.4325 | 34.4269 | 33.8299 | 34.5859 | 35.3907 | 36.4714 | 37.3749 | 36.8807 | 37.9449 | 34.3712 | 34.3499 | 34.1001 | 35.0078 | 34.95 | 35.5504 | 36.3942 | 36.5746 | 35.1215 | 31.8803 | 92.5444 | 35.4679 | 33.0249 | 34.9477 | 33.2228 | 33.0869 | 33.3803 | 34.7785 | 34.2944 | 34.0198 | 37.1563 | 36.1877 | 33.393 | 34.3851 | 36.1798 | 36.509 | 37.3682 | 36.1865 | 33.2068 | 32.6509 | 34.5631 | 35.0112 | 33.2143 | 34.3519 | 34.3805 | 34.4475 | 34.2936 | 34.2906 | 34.3947 | 33.9278 | 34.2891 | 35.9021 | 35.0992 | 36.2997 | 36.2668 | 33.4758 | 92.8752 | 92.9571 | 92.7654
2022-09-08 03:41 | 5:51 | 35.2136 | 31.8181 | 33.557 | 36.4429 | 34.4476 | 33.8069 | 34.6066 | 35.3868 | 36.489 | 37.3616 | 36.8757 | 37.9679 | 34.3432 | 34.3373 | 34.1122 | 35.0079 | 34.9609 | 35.5806 | 36.3899 | 36.5869 | 35.1737 | 31.882 | 92.5494 | 35.475 | 33.0231 | 34.9575 | 33.2096 | 33.0949 | 33.3826 | 34.7742 | 34.289 | 34.0195 | 37.1734 | 36.2161 | 33.3886 | 34.3795 | 36.1844 | 36.5054 | 37.3951 | 36.1839 | 33.2214 | 32.6527 | 34.5712 | 35.0075 | 33.2023 | 34.3565 | 34.3716 | 34.4374 | 34.2927 | 34.2847 | 34.4125 | 33.9235 | 34.2936 | 35.9187 | 35.0977 | 36.302 | 36.2807 | 33.4744 | 92.9825 | 93.14 | 92.8898
2022-09-08 03:41 | 5:51 | 35.2829 | 31.8437 | 33.6331 | 36.4591 | 34.449 | 33.8348 | 34.5973 | 35.4084 | 36.4762 | 37.3601 | 36.8783 | 37.9652 | 34.3388 | 34.3479 | 34.1078 | 35.0181 | 34.9612 | 35.5865 | 36.4146 | 36.5784 | 35.1798 | 31.896 | 92.7236 | 35.4776 | 33.0329 | 34.9584 | 33.2092 | 33.0988 | 33.3927 | 34.7818 | 34.2777 | 34.0091 | 37.1628 | 36.1885 | 33.3792 | 34.3735 | 36.1877 | 36.5021 | 37.3962 | 36.1962 | 33.2336 | 32.6654 | 34.5675 | 35.0257 | 33.2184 | 34.338 | 34.3826 | 34.4538 | 34.2907 | 34.2827 | 34.4137 | 33.9255 | 34.2927 | 35.9133 | 35.0949 | 36.2971 | 36.2963 | 33.4675 | 93.143 | 93.2505 | 93.0046
2022-09-08 03:41 | 5:51 | 35.3829 | 31.865 | 33.7342 | 36.5685 | 34.4414 | 33.824 | 34.5988 | 35.4058 | 36.4771 | 37.3809 | 36.8514 | 37.9603 | 34.3559 | 34.3418 | 34.1208 | 35.0033 | 34.9527 | 35.5718 | 36.4143 | 36.5984 | 35.201 | 31.9205 | 92.7116 | 35.4735 | 33.0395 | 34.9449 | 33.2185 | 33.1111 | 33.3801 | 34.7842 | 34.2992 | 34.0128 | 37.16 | 36.1982 | 33.3824 | 34.3666 | 36.2161 | 36.502 | 37.401 | 36.1798 | 33.2259 | 32.6728 | 34.5791 | 35.0266 | 33.2311 | 34.3476 | 34.3757 | 34.4558 | 34.2996 | 34.2799 | 34.3845 | 33.9397 | 34.2907 | 35.9076 | 35.1045 | 36.2874 | 36.2932 | 33.4864 | 93.2705 | 93.3796 | 93.1111
2022-09-08 03:41 | 5:51 | 35.4492 | 31.9045 | 33.814 | 36.5922 | 34.4258 | 33.8142 | 34.5968 | 35.4037 | 36.4927 | 37.3528 | 36.866 | 37.9616 | 34.3475 | 34.3498 | 34.1147 | 35.0016 | 34.9705 | 35.5726 | 36.405 | 36.5878 | 35.1924 | 31.9156 | 92.8448 | 35.5724 | 33.0379 | 34.9613 | 33.2068 | 33.1047 | 33.393 | 34.7823 | 34.2969 | 33.9978 | 37.1658 | 36.1981 | 33.3848 | 34.3782 | 36.1885 | 36.5048 | 37.4059 | 36.1844 | 33.2184 | 32.6852 | 34.593 | 35.0151 | 33.2262 | 34.3403 | 34.3972 | 34.4425 | 34.3058 | 34.2827 | 34.4024 | 33.9319 | 34.2996 | 35.9133 | 35.1096 | 36.3006 | 36.2938 | 33.4856 | 93.4095 | 93.5014 | 93.1699
2022-09-08 03:41 | 5:51 | 35.4894 | 31.9168 | 33.9168 | 36.5362 | 34.4204 | 33.8204 | 34.5861 | 35.401 | 36.4949 | 37.3759 | 36.8744 | 37.9449 | 34.3447 | 34.3176 | 34.1129 | 35.0085 | 34.9703 | 35.5826 | 36.407 | 36.5888 | 35.2281 | 31.9471 | 93.0045 | 35.5342 | 33.0422 | 34.9465 | 33.2214 | 33.0977 | 33.3886 | 34.7829 | 34.2948 | 34.009 | 37.1649 | 36.177 | 33.3899 | 34.3696 | 36.1982 | 36.5123 | 37.3963 | 36.1877 | 33.2124 | 32.683 | 34.5865 | 35.0196 | 33.2435 | 34.3401 | 34.4101 | 34.4436 | 34.2985 | 34.2812 | 34.391 | 33.9404 | 34.3058 | 35.9301 | 35.1135 | 36.2959 | 36.3014 | 33.4938 | 93.6037 | 93.7158 | 93.3098
2022-09-08 03:41 | 5:51 | 35.5579 | 31.9366 | 34.0587 | 36.6061 | 34.4527 | 33.8101 | 34.61 | 35.4111 | 36.4879 | 37.3888 | 36.8641 | 37.9745 | 34.3582 | 34.3354 | 34.1196 | 35.0235 | 34.9559 | 35.5777 | 36.4139 | 36.5944 | 35.25 | 31.9425 | 93.1435 | 35.5848 | 33.0492 | 34.9648 | 33.2336 | 33.1022 | 33.3792 | 34.7644 | 34.2888 | 34.0102 | 37.1595 | 36.2118 | 33.4067 | 34.3655 | 36.1981 | 36.5106 | 37.4016 | 36.2161 | 33.2277 | 32.6807 | 34.6127 | 35.0425 | 33.2569 | 34.3429 | 34.3942 | 34.435 | 34.3169 | 34.2935 | 34.3988 | 33.955 | 34.2985 | 35.9062 | 35.1088 | 36.2906 | 36.2913 | 33.4939 | 93.7725 | 93.8693 | 93.4075
2022-09-08 03:42 | 5:51 | 35.5996 | 31.9383 | 34.117 | 36.5833 | 34.4404 | 33.8223 | 34.5946 | 35.3777 | 36.4824 | 37.3882 | 36.8656 | 37.9691 | 34.3384 | 34.3349 | 34.1135 | 35.008 | 34.9739 | 35.5823 | 36.4101 | 36.6041 | 35.2909 | 31.944 | 93.1747 | 35.5493 | 33.0279 | 34.9674 | 33.2259 | 33.0993 | 33.3824 | 34.7971 | 34.2835 | 34.0149 | 37.1658 | 36.1899 | 33.3661 | 34.3792 | 36.177 | 36.4992 | 37.3907 | 36.1885 | 33.2256 | 32.6905 | 34.5915 | 35.0381 | 33.2548 | 34.3268 | 34.3994 | 34.4296 | 34.2959 | 34.3064 | 34.4069 | 33.9446 | 34.3169 | 35.9102 | 35.0914 | 36.3022 | 36.2996 | 33.5012 | 93.951 | 93.9965 | 93.4546
2022-09-08 03:42 | 5:52 | 35.6521 | 31.9528 | 34.1522 | 36.5277 | 34.4387 | 33.8118 | 34.6167 | 35.3955 | 36.4938 | 37.3875 | 36.8829 | 37.9679 | 34.3388 | 34.3052 | 34.1303 | 34.9983 | 34.9745 | 35.5785 | 36.409 | 36.5887 | 35.3166 | 31.9562 | 93.2275 | 35.5264 | 33.0257 | 34.9635 | 33.2184 | 33.098 | 33.3848 | 34.7877 | 34.2865 | 34.0048 | 37.1698 | 36.2039 | 33.3788 | 34.3894 | 36.2118 | 36.5238 | 37.4058 | 36.1982 | 33.2284 | 32.6972 | 34.6077 | 35.0276 | 33.2666 | 34.308 | 34.4098 | 34.456 | 34.2938 | 34.2832 | 34.3873 | 33.9622 | 34.2959 | 35.9282 | 35.1077 | 36.2905 | 36.2976 | 33.4945 | 94.1166 | 94.2085 | 93.5282
2022-09-08 03:42 | 5:52 | 35.6692 | 31.9852 | 34.2043 | 36.6489 | 34.4295 | 33.8196 | 34.5876 | 35.4102 | 36.4676 | 37.3958 | 36.877 | 37.9694 | 34.3219 | 34.3244 | 34.1099 | 35.0081 | 34.9601 | 35.5844 | 36.4054 | 36.5893 | 35.3046 | 31.9785 | 93.1758 | 35.6029 | 33.0519 | 34.9553 | 33.2124 | 33.1072 | 33.3899 | 34.7923 | 34.2823 | 34.0191 | 37.1762 | 36.2147 | 33.391 | 34.3571 | 36.1899 | 36.5125 | 37.4023 | 36.1981 | 33.2261 | 32.7004 | 34.607 | 35.047 | 33.2674 | 34.3268 | 34.3983 | 34.4484 | 34.3121 | 34.3067 | 34.3816 | 33.951 | 34.2938 | 35.9233 | 35.0883 | 36.3044 | 36.3027 | 33.5049 | 94.239 | 94.328 | 93.6004
2022-09-08 03:42 | 5:52 | 32.497 | 31.7873 | 33.6805 | 36.6385 | 34.4209 | 33.8198 | 34.5885 | 35.4167 | 36.484 | 37.3762 | 36.8484 | 37.9758 | 34.3218 | 34.3082 | 34.1165 | 35.0151 | 34.962 | 35.5629 | 36.4059 | 36.6099 | 31.9062 | 31.6325 | 93.5228 | 35.5492 | 33.0258 | 34.9614 | 33.2277 | 33.1146 | 33.4067 | 34.7884 | 34.2864 | 34.0012 | 37.1585 | 36.1975 | 33.3869 | 34.3707 | 36.2039 | 36.5046 | 37.4313 | 36.177 | 33.2089 | 32.704 | 34.6367 | 35.0429 | 33.2975 | 34.3219 | 34.4123 | 34.4498 | 34.3078 | 34.304 | 34.398 | 33.9692 | 34.3121 | 35.9389 | 35.1063 | 36.2746 | 36.2923 | 33.4878 | 94.4445 | 94.467 | 93.7264
2022-09-08 03:42 | 5:52 | 30.1621 | 30.2276 | 32.2745 | 36.6351 | 34.4295 | 33.8311 | 34.6052 | 35.3954 | 36.4962 | 37.3721 | 36.8692 | 37.9512 | 34.3323 | 34.3131 | 34.128 | 35.0301 | 34.9976 | 35.5863 | 36.4099 | 36.5866 | 28.6827 | 29.7152 | 93.4885 | 35.4703 | 33.0338 | 34.9474 | 33.2256 | 33.1118 | 33.3661 | 34.7706 | 34.2486 | 33.9974 | 37.1732 | 36.2204 | 33.3946 | 34.3562 | 36.2147 | 36.5054 | 37.4042 | 36.2118 | 33.2268 | 32.7088 | 34.6145 | 35.0482 | 33.3045 | 34.3088 | 34.4114 | 34.4566 | 34.3231 | 34.3165 | 34.3923 | 33.944 | 34.3078 | 35.9041 | 35.0777 | 36.3246 | 36.283 | 33.484 | 94.4308 | 94.59 | 93.6774
2022-09-08 03:42 | 5:52 | 31.1333 | 29.3046 | 31.8512 | 36.553 | 34.4387 | 33.8013 | 34.6114 | 35.4173 | 36.4788 | 37.3818 | 36.8709 | 37.9625 | 34.345 | 34.2898 | 34.1122 | 35.0009 | 34.9604 | 35.5627 | 36.4063 | 36.5838 | 28.8831 | 28.4919 | 93.5544 | 35.4397 | 33.0382 | 34.9663 | 33.2284 | 33.0844 | 33.3788 | 34.7889 | 34.2598 | 34.0176 | 37.1772 | 36.2249 | 33.3811 | 34.3732 | 36.1975 | 36.5201 | 37.4134 | 36.1899 | 33.2377 | 32.694 | 34.6107 | 35.0438 | 33.3056 | 34.3074 | 34.4269 | 34.4573 | 34.3181 | 34.296 | 34.3978 | 33.9426 | 34.3231 | 35.939 | 35.098 | 36.3147 | 36.2849 | 33.4751 | 94.5468 | 94.7109 | 93.8912
2022-09-08 03:43 | 5:53 | 31.4716 | 28.8148 | 31.9102 | 36.4587 | 34.4251 | 33.816 | 34.6078 | 35.4182 | 36.485 | 37.3918 | 36.8816 | 37.9588 | 34.3195 | 34.3036 | 34.1311 | 34.9925 | 34.9661 | 35.5641 | 36.4118 | 36.5857 | 29.0381 | 27.9645 | 93.7661 | 35.3635 | 33.0365 | 34.9651 | 33.2261 | 33.108 | 33.391 | 34.7788 | 34.2749 | 34.0158 | 37.1671 | 36.2211 | 33.3739 | 34.3728 | 36.2204 | 36.505 | 37.4069 | 36.2039 | 33.2171 | 32.6962 | 34.6426 | 35.0791 | 33.3025 | 34.3091 | 34.4099 | 34.4673 | 34.3252 | 34.2982 | 34.3691 | 33.9741 | 34.3181 | 35.9299 | 35.1041 | 36.3043 | 36.2994 | 33.4982 | 94.7557 | 94.7824 | 93.9948
2022-09-08 03:43 | 5:53 | 31.5569 | 28.3278 | 31.8121 | 36.5867 | 34.4089 | 33.8233 | 34.627 | 35.399 | 36.5041 | 37.3828 | 36.8663 | 37.9669 | 34.3116 | 34.3063 | 34.1277 | 35.0125 | 34.9843 | 35.5752 | 36.4021 | 36.5889 | 29.4087 | 27.3544 | 93.721 | 35.3007 | 33.0431 | 34.9636 | 33.2089 | 33.0974 | 33.3869 | 34.7853 | 34.2872 | 34.0078 | 37.1718 | 36.2271 | 33.3791 | 34.3688 | 36.2249 | 36.4998 | 37.425 | 36.2147 | 33.2373 | 32.7359 | 34.6293 | 35.0642 | 33.2976 | 34.2994 | 34.4132 | 34.4607 | 34.3314 | 34.3148 | 34.3905 | 33.9532 | 34.3252 | 35.9077 | 35.1129 | 36.2958 | 36.3124 | 33.5024 | 94.7825 | 94.9088 | 94.0287
2022-09-08 03:43 | 5:53 | 31.5224 | 28.0613 | 31.5716 | 36.6039 | 34.423 | 33.8189 | 34.6441 | 35.4221 | 36.4986 | 37.3785 | 36.8634 | 37.9713 | 34.3142 | 34.3027 | 34.141 | 35.0047 | 34.9607 | 35.5711 | 36.4086 | 36.5895 | 29.7601 | 26.5533 | 93.8492 | 35.2272 | 33.0436 | 34.9665 | 33.2268 | 33.113 | 33.3946 | 34.7558 | 34.2877 | 34.016 | 37.1658 | 36.2279 | 33.3823 | 34.3636 | 36.2211 | 36.5076 | 37.4012 | 36.1975 | 33.2314 | 32.699 | 34.642 | 35.0626 | 33.2946 | 34.3144 | 34.4238 | 34.4703 | 34.2991 | 34.2949 | 34.3845 | 33.9536 | 34.3314 | 35.9067 | 35.1039 | 36.2917 | 36.3019 | 33.482 | 94.8621 | 94.9514 | 94.1204
2022-09-08 03:43 | 5:53 | 31.4623 | 27.9312 | 31.5459 | 36.535 | 34.4268 | 33.7972 | 34.6327 | 35.4208 | 36.4874 | 37.3665 | 36.8701 | 37.9508 | 34.3204 | 34.2816 | 34.1307 | 35.0101 | 34.9864 | 35.5696 | 36.3952 | 36.5874 | 29.953 | 26.255 | 93.8526 | 35.2875 | 33.0346 | 34.9374 | 33.2377 | 33.114 | 33.3811 | 34.7729 | 34.2813 | 33.9986 | 37.1487 | 36.2323 | 33.3833 | 34.3645 | 36.2271 | 36.4846 | 37.4167 | 36.2204 | 33.221 | 32.729 | 34.6212 | 35.0691 | 33.2838 | 34.299 | 34.4121 | 34.4463 | 34.3191 | 34.3084 | 34.3658 | 33.9613 | 34.2991 | 35.908 | 35.1111 | 36.2886 | 36.3023 | 33.466 | 94.7669 | 94.929 | 94.0185
2022-09-08 03:43 | 5:53 | 31.3806 | 27.8616 | 31.3685 | 36.6067 | 34.4294 | 33.8065 | 34.6632 | 35.4068 | 36.4923 | 37.3675 | 36.8482 | 37.9631 | 34.3077 | 34.2981 | 34.1148 | 35.0124 | 34.9734 | 35.578 | 36.4123 | 36.59 | 29.9709 | 26.0817 | 93.5717 | 35.2698 | 33.0229 | 34.947 | 33.2171 | 33.1098 | 33.3739 | 34.7837 | 34.2805 | 33.9941 | 37.1759 | 36.2067 | 33.3961 | 34.3552 | 36.2279 | 36.4992 | 37.4019 | 36.2249 | 33.2492 | 32.7255 | 34.6149 | 35.0644 | 33.288 | 34.2968 | 34.4179 | 34.4606 | 34.3173 | 34.2919 | 34.3918 | 33.9931 | 34.3191 | 35.9193 | 35.1113 | 36.2965 | 36.2773 | 33.4578 | 94.5876 | 94.739 | 93.8214
2022-09-08 03:43 | 5:53 | 31.2919 | 27.8824 | 31.2217 | 36.5501 | 34.4154 | 33.7963 | 34.6555 | 35.4129 | 36.4789 | 37.3673 | 36.8487 | 37.9712 | 34.314 | 34.2981 | 34.1183 | 35.0003 | 34.9588 | 35.5515 | 36.403 | 36.5672 | 29.8451 | 25.9516 | 93.4936 | 35.2399 | 33.0341 | 34.9731 | 33.2373 | 33.1228 | 33.3791 | 34.7571 | 34.2753 | 34.0257 | 37.163 | 36.2192 | 33.3854 | 34.3737 | 36.2323 | 36.5031 | 37.4031 | 36.2211 | 33.2333 | 32.7161 | 34.6292 | 35.0739 | 33.2998 | 34.3193 | 34.4172 | 34.4605 | 34.3165 | 34.3071 | 34.3617 | 33.9751 | 34.3173 | 35.9008 | 35.1038 | 36.2829 | 36.2963 | 33.47 | 94.3099 | 94.4795 | 93.6076
2022-09-08 03:44 | 5:53 | 31.1757 | 27.8751 | 31.0803 | 36.4898 | 34.4115 | 33.8111 | 34.6674 | 35.3956 | 36.4803 | 37.3576 | 36.8589 | 37.9534 | 34.3132 | 34.2827 | 34.1194 | 35.007 | 34.9844 | 35.5818 | 36.3964 | 36.5733 | 29.6869 | 25.7715 | 93.4299 | 35.1611 | 33.0269 | 34.9588 | 33.2314 | 33.0899 | 33.3823 | 34.7671 | 34.2764 | 33.9959 | 37.1737 | 36.2199 | 33.3768 | 34.3668 | 36.2067 | 36.483 | 37.4254 | 36.2271 | 33.2425 | 32.7399 | 34.6106 | 35.0565 | 33.2876 | 34.2921 | 34.4247 | 34.4524 | 34.3 | 34.3096 | 34.3536 | 33.9617 | 34.3165 | 35.89 | 35.0922 | 36.3012 | 36.2888 | 33.4693 | 94.1429 | 94.2476 | 93.6045
2022-09-08 03:44 | 5:54 | 30.9937 | 27.8744 | 31.147 | 36.5426 | 34.4068 | 33.8049 | 34.6821 | 35.4248 | 36.4848 | 37.3704 | 36.8445 | 37.9504 | 34.2918 | 34.2957 | 34.1377 | 35.0106 | 34.9839 | 35.5633 | 36.3708 | 36.573 | 29.5504 | 25.669 | 93.2991 | 35.147 | 33.0383 | 34.9612 | 33.221 | 33.1001 | 33.3833 | 34.7815 | 34.2601 | 33.9989 | 37.1694 | 36.2569 | 33.3879 | 34.3646 | 36.2192 | 36.4929 | 37.3998 | 36.2279 | 33.2382 | 32.7284 | 34.6147 | 35.0387 | 33.3308 | 34.2805 | 34.426 | 34.4588 | 34.325 | 34.3162 | 34.3628 | 33.9669 | 34.3 | 35.9211 | 35.1001 | 36.2765 | 36.2796 | 33.4713 | 93.936 | 94.0959 | 93.4976
2022-09-08 03:44 | 5:54 | 30.9394 | 27.8621 | 30.9347 | 36.6581 | 34.425 | 33.8129 | 34.6764 | 35.4152 | 36.4932 | 37.3773 | 36.8635 | 37.9577 | 34.2875 | 34.2769 | 34.1105 | 35.0065 | 34.9828 | 35.5763 | 36.3841 | 36.5652 | 29.3569 | 25.5469 | 93.171 | 35.1534 | 33.0443 | 34.9716 | 33.2492 | 33.1011 | 33.3961 | 34.774 | 34.2787 | 34.009 | 37.1774 | 36.2508 | 33.3882 | 34.3908 | 36.2199 | 36.4812 | 37.4289 | 36.2323 | 33.2325 | 32.739 | 34.6362 | 35.0448 | 33.2953 | 34.2961 | 34.4326 | 34.4566 | 34.3387 | 34.321 | 34.3686 | 33.9683 | 34.325 | 35.8947 | 35.1031 | 36.2956 | 36.2984 | 33.4777 | 93.7993 | 94.005 | 93.4106
2022-09-08 03:44 | 5:54 | 30.5778 | 27.7978 | 30.6474 | 36.4758 | 34.4166 | 33.8086 | 34.6901 | 35.3996 | 36.4835 | 37.3677 | 36.8511 | 37.9621 | 34.292 | 34.2938 | 34.1207 | 35.0074 | 34.9786 | 35.5485 | 36.3769 | 36.5735 | 29.2078 | 25.4165 | 93.1444 | 35.1193 | 33.0335 | 34.948 | 33.2333 | 33.1027 | 33.3854 | 34.7663 | 34.2674 | 33.9926 | 37.1741 | 36.2375 | 33.374 | 34.3583 | 36.2569 | 36.4962 | 37.4263 | 36.2067 | 33.249 | 32.7365 | 34.6073 | 35.0685 | 33.321 | 34.2845 | 34.4374 | 34.4531 | 34.3204 | 34.3144 | 34.3774 | 33.9741 | 34.3387 | 35.9108 | 35.1099 | 36.2951 | 36.3122 | 33.4638 | 93.7248 | 93.8936 | 93.3786
2022-09-08 03:44 | 5:54 | 27.9551 | 27.7699 | 30.0493 | 36.4399 | 34.4046 | 33.8117 | 34.6902 | 35.4193 | 36.4873 | 37.365 | 36.875 | 37.953 | 34.2984 | 34.2731 | 34.12 | 35.0104 | 34.9834 | 35.5618 | 36.3831 | 36.5822 | 29.0566 | 25.4064 | 93.1753 | 35.1346 | 33.0426 | 34.9602 | 33.2425 | 33.1003 | 33.3768 | 34.7657 | 34.2757 | 34.0177 | 37.174 | 36.2311 | 33.3754 | 34.3665 | 36.2508 | 36.4915 | 37.3903 | 36.2192 | 33.2621 | 32.7269 | 34.5968 | 35.056 | 33.3182 | 34.2917 | 34.443 | 34.4613 | 34.3322 | 34.318 | 34.3532 | 33.9585 | 34.3204 | 35.9144 | 35.0873 | 36.2844 | 36.2963 | 33.4766 | 93.5791 | 93.8788 | 93.3303
2022-09-08 03:44 | 5:54 | 26.3508 | 27.455 | 29.5738 | 36.5498 | 34.3969 | 33.8218 | 34.6928 | 35.4264 | 36.4931 | 37.3611 | 36.8663 | 37.9555 | 34.3025 | 34.2923 | 34.1138 | 35.0125 | 34.9948 | 35.5556 | 36.3945 | 36.568 | 28.9007 | 25.1609 | 93.1535 | 35.0154 | 33.0161 | 34.9746 | 33.2382 | 33.0988 | 33.3879 | 34.7668 | 34.2743 | 34.0264 | 37.1817 | 36.2578 | 33.3978 | 34.3772 | 36.2375 | 36.5078 | 37.3854 | 36.2199 | 33.2449 | 32.7502 | 34.6223 | 35.0318 | 33.3023 | 34.275 | 34.4445 | 34.4599 | 34.3381 | 34.3345 | 34.3604 | 33.9558 | 34.3322 | 35.9235 | 35.09 | 36.3068 | 36.2852 | 33.4581 | 93.5347 | 93.8163 | 93.4071
2022-09-08 03:45 | 5:55 | 25.9985 | 27.249 | 29.1656 | 36.3867 | 34.3927 | 33.8122 | 34.718 | 35.4316 | 36.5031 | 37.3521 | 36.8542 | 37.9539 | 34.2946 | 34.2772 | 34.1126 | 34.9922 | 34.9837 | 35.5589 | 36.3749 | 36.5699 | 28.7504 | 25.016 | 93.1104 | 35.0756 | 33.048 | 34.9789 | 33.2325 | 33.0919 | 33.3882 | 34.7633 | 34.2811 | 34.0167 | 37.1742 | 36.251 | 33.388 | 34.3565 | 36.2311 | 36.5117 | 37.4123 | 36.2569 | 33.2484 | 32.7421 | 34.6164 | 35.0579 | 33.3081 | 34.2658 | 34.4303 | 34.4566 | 34.3467 | 34.3127 | 34.3499 | 33.9818 | 34.3381 | 35.8918 | 35.0887 | 36.3041 | 36.2937 | 33.4555 | 93.5102 | 93.6816 | 93.2919
2022-09-08 03:45 | 5:55 | 25.679 | 26.9611 | 28.8823 | 36.4046 | 34.3927 | 33.814 | 34.708 | 35.4232 | 36.4993 | 37.3426 | 36.8684 | 37.9483 | 34.2906 | 34.2701 | 34.1095 | 35.0194 | 34.9865 | 35.5624 | 36.356 | 36.5562 | 28.544 | 24.8967 | 93.1215 | 35.0689 | 33.0433 | 34.9835 | 33.249 | 33.0852 | 33.374 | 34.7771 | 34.2868 | 34.0111 | 37.1512 | 36.2576 | 33.3836 | 34.3635 | 36.2578 | 36.4872 | 37.4044 | 36.2508 | 33.2436 | 32.746 | 34.6328 | 35.0511 | 33.313 | 34.2686 | 34.4451 | 34.4399 | 34.3486 | 34.3299 | 34.3373 | 33.9527 | 34.3467 | 35.8992 | 35.0967 | 36.3072 | 36.2841 | 33.4714 | 93.4572 | 93.6106 | 93.2799
2022-09-08 03:45 | 5:55 | 25.4571 | 26.7057 | 28.6887 | 36.4303 | 34.3944 | 33.8139 | 34.7027 | 35.4346 | 36.4872 | 37.3581 | 36.8475 | 37.9549 | 34.2902 | 34.2775 | 34.1118 | 35.0248 | 35.0193 | 35.5583 | 36.3723 | 36.5658 | 28.3952 | 24.7564 | 92.9586 | 35.0359 | 33.0387 | 34.9842 | 33.2621 | 33.1108 | 33.3754 | 34.7666 | 34.2759 | 34.0213 | 37.1751 | 36.2522 | 33.3996 | 34.3689 | 36.251 | 36.5029 | 37.4103 | 36.2375 | 33.2671 | 32.7461 | 34.5935 | 35.0517 | 33.3268 | 34.2785 | 34.4376 | 34.4585 | 34.3317 | 34.3448 | 34.3479 | 33.9929 | 34.3486 | 35.8908 | 35.0965 | 36.3053 | 36.2938 | 33.4688 | 93.3529 | 93.5363 | 93.1997
2022-09-08 03:45 | 5:55 | 25.1289 | 26.4009 | 28.387 | 36.3795 | 34.4015 | 33.8207 | 34.7019 | 35.4179 | 36.4929 | 37.3719 | 36.8721 | 37.9679 | 34.2858 | 34.2698 | 34.1302 | 35.0237 | 34.9907 | 35.5471 | 36.3559 | 36.5595 | 28.1983 | 24.5989 | 93.0458 | 34.9674 | 33.0207 | 34.9787 | 33.2449 | 33.1109 | 33.3978 | 34.7785 | 34.2803 | 34.0038 | 37.1804 | 36.278 | 33.3871 | 34.375 | 36.2576 | 36.4988 | 37.4152 | 36.2311 | 33.2491 | 32.7513 | 34.6249 | 35.0587 | 33.3175 | 34.2701 | 34.4296 | 34.4658 | 34.3325 | 34.3212 | 34.3418 | 33.973 | 34.3317 | 35.8916 | 35.1018 | 36.2979 | 36.2917 | 33.4574 | 93.3054 | 93.5326 | 93.2047
2022-09-08 03:45 | 5:55 | 24.995 | 26.1418 | 28.2124 | 36.2513 | 34.3947 | 33.8106 | 34.6916 | 35.4223 | 36.4925 | 37.349 | 36.8751 | 37.958 | 34.286 | 34.2889 | 34.123 | 35.0129 | 35.0052 | 35.5514 | 36.372 | 36.5664 | 27.9604 | 24.4469 | 92.9122 | 34.9821 | 33.0341 | 34.9854 | 33.2484 | 33.1148 | 33.388 | 34.7594 | 34.2939 | 34.0226 | 37.1858 | 36.238 | 33.3986 | 34.3615 | 36.2522 | 36.4935 | 37.3909 | 36.2578 | 33.2722 | 32.7489 | 34.6136 | 35.056 | 33.316 | 34.2543 | 34.4382 | 34.4669 | 34.3365 | 34.3263 | 34.3498 | 33.9758 | 34.3325 | 35.9146 | 35.1152 | 36.3126 | 36.2705 | 33.4648 | 93.1924 | 93.4263 | 93.0851
2022-09-08 03:45 | 5:55 | 24.7203 | 25.9282 | 27.9484 | 36.3428 | 34.4125 | 33.8262 | 34.6925 | 35.4374 | 36.507 | 37.3454 | 36.8664 | 37.9665 | 34.2851 | 34.2827 | 34.1256 | 35.0186 | 34.9918 | 35.5381 | 36.3648 | 36.5881 | 27.7228 | 24.256 | 92.9925 | 35.0113 | 33.0519 | 34.9854 | 33.2436 | 33.1222 | 33.3836 | 34.7693 | 34.2609 | 34.0267 | 37.184 | 36.2512 | 33.3982 | 34.3829 | 36.278 | 36.5039 | 37.4008 | 36.251 | 33.2598 | 32.7459 | 34.608 | 35.0557 | 33.3287 | 34.2664 | 34.4312 | 34.4386 | 34.3537 | 34.3437 | 34.3176 | 33.9657 | 34.3365 | 35.9201 | 35.1057 | 36.3097 | 36.2923 | 33.4742 | 93.1879 | 93.3371 | 93.0598
2022-09-08 03:46 | 5:56 | 24.5853 | 25.7208 | 27.8338 | 36.3865 | 34.4137 | 33.8135 | 34.6865 | 35.4091 | 36.497 | 37.3466 | 36.857 | 37.9655 | 34.2716 | 34.2647 | 34.1137 | 35.0289 | 35.0191 | 35.5362 | 36.3498 | 36.5726 | 27.4925 | 24.1102 | 92.9427 | 34.9279 | 33.0438 | 35.0012 | 33.2671 | 33.1219 | 33.3996 | 34.7492 | 34.2822 | 34.0232 | 37.1774 | 36.2556 | 33.4078 | 34.3665 | 36.238 | 36.5161 | 37.426 | 36.2576 | 33.2499 | 32.744 | 34.6275 | 35.0569 | 33.3211 | 34.2804 | 34.4579 | 34.4348 | 34.3381 | 34.331 | 34.3354 | 33.9934 | 34.3537 | 35.9159 | 35.1003 | 36.3205 | 36.2904 | 33.4704 | 93.1383 | 93.3143 | 93.0552
2022-09-08 03:46 | 5:56 | 24.3593 | 25.4765 | 27.5487 | 36.3472 | 34.3845 | 33.804 | 34.7091 | 35.4285 | 36.5037 | 37.3708 | 36.8824 | 37.9671 | 34.2707 | 34.2681 | 34.1176 | 35.0054 | 35.0006 | 35.5507 | 36.3543 | 36.5669 | 27.2659 | 23.9513 | 92.9408 | 34.9736 | 33.0349 | 34.9863 | 33.2491 | 33.1294 | 33.3871 | 34.76 | 34.2775 | 34.0232 | 37.1833 | 36.2606 | 33.4012 | 34.37 | 36.2512 | 36.5035 | 37.4146 | 36.2522 | 33.2545 | 32.7676 | 34.627 | 35.0347 | 33.3214 | 34.2507 | 34.4456 | 34.4526 | 34.3456 | 34.3357 | 34.3349 | 33.9776 | 34.3381 | 35.9277 | 35.1286 | 36.3114 | 36.3289 | 33.471 | 93.1301 | 93.3212 | 93.0429
2022-09-08 03:46 | 5:56 | 24.1214 | 25.2475 | 27.4785 | 36.1458 | 34.4024 | 33.8168 | 34.6977 | 35.4235 | 36.497 | 37.3584 | 36.8961 | 37.9702 | 34.2963 | 34.283 | 34.1273 | 35.0292 | 35.0122 | 35.5528 | 36.3516 | 36.5736 | 27.1026 | 23.7607 | 92.9332 | 34.9102 | 33.0391 | 34.9866 | 33.2722 | 33.1207 | 33.3986 | 34.7689 | 34.2918 | 34.026 | 37.1743 | 36.2785 | 33.3963 | 34.3764 | 36.2556 | 36.5116 | 37.4239 | 36.278 | 33.279 | 32.7686 | 34.6044 | 35.0614 | 33.3238 | 34.2644 | 34.4412 | 34.4639 | 34.351 | 34.3207 | 34.3052 | 33.98 | 34.3456 | 35.9109 | 35.1141 | 36.3201 | 36.305 | 33.4578 | 93.1075 | 93.2784 | 92.9788
2022-09-08 03:46 | 5:56 | 23.9506 | 25.0255 | 27.2596 | 36.195 | 34.391 | 33.8077 | 34.6803 | 35.4251 | 36.5059 | 37.3542 | 36.8892 | 37.9659 | 34.2767 | 34.2721 | 34.1285 | 35.0175 | 35.0194 | 35.5503 | 36.3748 | 36.5686 | 26.9413 | 23.5813 | 92.8902 | 34.8292 | 33.0322 | 34.9865 | 33.2598 | 33.115 | 33.3982 | 34.7676 | 34.2796 | 34.0045 | 37.1736 | 36.2818 | 33.4091 | 34.3969 | 36.2606 | 36.4974 | 37.4269 | 36.238 | 33.2719 | 32.7323 | 34.6089 | 35.0672 | 33.32 | 34.2642 | 34.4437 | 34.4518 | 34.3601 | 34.3302 | 34.3244 | 34.0033 | 34.351 | 35.9127 | 35.1229 | 36.295 | 36.3023 | 33.4766 | 93.0534 | 93.2322 | 92.9113
2022-09-08 03:46 | 5:56 | 23.8115 | 24.8258 | 27.1553 | 36.144 | 34.3988 | 33.8183 | 34.6841 | 35.4181 | 36.4882 | 37.3534 | 36.8759 | 37.9769 | 34.2881 | 34.2586 | 34.1296 | 35.0247 | 35.0141 | 35.5451 | 36.3629 | 36.5667 | 26.7204 | 23.4423 | 92.8307 | 34.7337 | 33.031 | 34.9864 | 33.2499 | 33.1002 | 33.4078 | 34.7438 | 34.2815 | 34.0378 | 37.1861 | 36.2816 | 33.3894 | 34.3701 | 36.2785 | 36.5248 | 37.427 | 36.2512 | 33.2565 | 32.7735 | 34.6235 | 35.0687 | 33.2995 | 34.2582 | 34.4477 | 34.4512 | 34.3682 | 34.3411 | 34.3082 | 33.984 | 34.3601 | 35.9089 | 35.1107 | 36.3226 | 36.3042 | 33.4839 | 92.9878 | 93.1377 | 92.8478
2022-09-08 03:46 | 5:56 | 23.7064 | 24.662 | 26.9634 | 36.0652 | 34.4069 | 33.8262 | 34.6896 | 35.4321 | 36.5107 | 37.3558 | 36.8793 | 37.968 | 34.2839 | 34.2583 | 34.1251 | 35.0326 | 35.0334 | 35.5499 | 36.3498 | 36.564 | 26.4904 | 23.2762 | 92.8659 | 34.8072 | 33.0437 | 34.9955 | 33.2545 | 33.1047 | 33.4012 | 34.7602 | 34.2856 | 34.0333 | 37.1765 | 36.2683 | 33.3941 | 34.3745 | 36.2818 | 36.5 | 37.4332 | 36.2556 | 33.2691 | 32.7531 | 34.6226 | 35.0836 | 33.3188 | 34.254 | 34.4351 | 34.4588 | 34.3592 | 34.3387 | 34.3131 | 34.0131 | 34.3682 | 35.9244 | 35.1283 | 36.3104 | 36.3054 | 33.4794 | 92.8959 | 93.0513 | 92.8062
2022-09-08 03:47 | 5:56 | 23.5075 | 24.4602 | 26.8174 | 36.2014 | 34.3873 | 33.821 | 34.6881 | 35.4318 | 36.5149 | 37.3404 | 36.8694 | 37.9701 | 34.2905 | 34.2704 | 34.1251 | 35.037 | 35.0329 | 35.545 | 36.3556 | 36.5695 | 26.2022 | 23.1119 | 92.7787 | 34.7502 | 33.0357 | 35.0102 | 33.279 | 33.1118 | 33.3963 | 34.7589 | 34.2795 | 34.0202 | 37.1983 | 36.2784 | 33.3969 | 34.377 | 36.2816 | 36.4954 | 37.4111 | 36.2606 | 33.2849 | 32.7699 | 34.6126 | 35.0656 | 33.2997 | 34.2614 | 34.4478 | 34.4357 | 34.3334 | 34.3405 | 34.2898 | 33.9963 | 34.3592 | 35.9103 | 35.1092 | 36.3259 | 36.3034 | 33.4736 | 92.8253 | 93.008 | 92.6702
2022-09-08 03:47 | 5:57 | 23.2269 | 24.2513 | 26.673 | 36.136 | 34.3816 | 33.8195 | 34.6885 | 35.4371 | 36.5232 | 37.3448 | 36.881 | 37.9721 | 34.2812 | 34.2681 | 34.1318 | 35.0209 | 35.0199 | 35.5446 | 36.361 | 36.567 | 25.9073 | 22.8983 | 92.6906 | 34.6904 | 33.0366 | 35.0271 | 33.2719 | 33.1011 | 33.4091 | 34.7448 | 34.2831 | 34.0531 | 37.1999 | 36.2731 | 33.3872 | 34.3768 | 36.2683 | 36.5016 | 37.4244 | 36.2785 | 33.2718 | 32.751 | 34.6159 | 35.0734 | 33.3008 | 34.2462 | 34.4459 | 34.4351 | 34.3646 | 34.3314 | 34.3036 | 33.9807 | 34.3334 | 35.9333 | 35.1047 | 36.3317 | 36.3013 | 33.477 | 92.7196 | 92.8913 | 92.6
2022-09-08 03:47 | 5:57 | 23.1407 | 24.0408 | 26.5339 | 36.1182 | 34.398 | 33.8203 | 34.6951 | 35.4442 | 36.5138 | 37.3628 | 36.8852 | 37.9631 | 34.2769 | 34.2561 | 34.1268 | 35.0043 | 35.0193 | 35.5487 | 36.3609 | 36.5701 | 25.5802 | 22.7086 | 92.6464 | 34.5805 | 33.0356 | 35.0224 | 33.2565 | 33.1052 | 33.3894 | 34.7473 | 34.2871 | 34.0239 | 37.1996 | 36.2637 | 33.3885 | 34.3736 | 36.2784 | 36.5036 | 37.4274 | 36.2818 | 33.2724 | 32.7737 | 34.6137 | 35.0832 | 33.3228 | 34.2474 | 34.4329 | 34.4514 | 34.3543 | 34.3627 | 34.3063 | 34.0045 | 34.3646 | 35.9403 | 35.098 | 36.3101 | 36.2922 | 33.4873 | 92.5455 | 92.7679 | 92.5698
2022-09-08 03:47 | 5:57 | 22.9177 | 23.8192 | 26.2978 | 36.04 | 34.3923 | 33.8262 | 34.7004 | 35.418 | 36.5134 | 37.349 | 36.9001 | 37.9673 | 34.2715 | 34.2619 | 34.142 | 35.0352 | 35.0305 | 35.5498 | 36.3427 | 36.5777 | 25.2937 | 22.5347 | 92.59 | 34.6327 | 33.0279 | 35.016 | 33.2691 | 33.0991 | 33.3941 | 34.7723 | 34.2912 | 34.0396 | 37.1909 | 36.2911 | 33.3958 | 34.3729 | 36.2731 | 36.5147 | 37.4303 | 36.2816 | 33.2835 | 32.7832 | 34.624 | 35.0645 | 33.3133 | 34.2508 | 34.4528 | 34.4522 | 34.3653 | 34.3524 | 34.3027 | 33.9942 | 34.3543 | 35.937 | 35.1207 | 36.3125 | 36.3082 | 33.4911 | 92.5041 | 92.6946 | 92.5387
2022-09-08 03:47 | 5:57 | 22.7821 | 23.6978 | 26.161 | 35.922 | 34.3978 | 33.8299 | 34.6965 | 35.4266 | 36.5264 | 37.3449 | 36.8796 | 37.9732 | 34.2877 | 34.2527 | 34.1511 | 35.036 | 35.0442 | 35.5532 | 36.3473 | 36.5872 | 24.9968 | 22.3214 | 92.5011 | 34.6643 | 33.0207 | 35.0132 | 33.2849 | 33.0961 | 33.3969 | 34.7533 | 34.2925 | 34.0454 | 37.194 | 36.2894 | 33.4079 | 34.3699 | 36.2637 | 36.515 | 37.4416 | 36.2683 | 33.2907 | 32.7782 | 34.6148 | 35.0645 | 33.3008 | 34.2349 | 34.4457 | 34.4491 | 34.3484 | 34.339 | 34.2816 | 34.0008 | 34.3653 | 35.9333 | 35.1025 | 36.2984 | 36.3056 | 33.4883 | 92.3926 | 92.5536 | 92.4071
2022-09-08 03:47 | 5:57 | 22.5499 | 23.4341 | 25.9587 | 35.9562 | 34.3691 | 33.8215 | 34.7127 | 35.4286 | 36.528 | 37.3686 | 36.8802 | 37.9877 | 34.2848 | 34.2639 | 34.1445 | 35.031 | 35.0498 | 35.5417 | 36.3476 | 36.5735 | 24.7574 | 22.1368 | 92.4351 | 34.6912 | 33.05 | 35.0084 | 33.2718 | 33.1011 | 33.3872 | 34.752 | 34.2926 | 34.0236 | 37.1848 | 36.2868 | 33.3815 | 34.388 | 36.2911 | 36.5252 | 37.438 | 36.2784 | 33.2816 | 32.7774 | 34.617 | 35.0822 | 33.287 | 34.2412 | 34.4386 | 34.4293 | 34.3619 | 34.3447 | 34.2981 | 33.9945 | 34.3484 | 35.9395 | 35.113 | 36.2997 | 36.3119 | 33.5027 | 92.2733 | 92.4345 | 92.42
2022-09-08 03:48 | 5:58 | 22.4267 | 23.2959 | 25.7951 | 35.9137 | 34.3905 | 33.8287 | 34.6929 | 35.4278 | 36.5228 | 37.3491 | 36.8918 | 37.9772 | 34.2906 | 34.2508 | 34.1396 | 35.0445 | 35.0429 | 35.5476 | 36.3369 | 36.578 | 24.5108 | 21.9693 | 92.3274 | 34.5395 | 33.0288 | 35.0074 | 33.2724 | 33.0915 | 33.3885 | 34.7513 | 34.3048 | 34.0269 | 37.1975 | 36.2942 | 33.3887 | 34.3968 | 36.2894 | 36.5196 | 37.4333 | 36.2731 | 33.277 | 32.7676 | 34.6085 | 35.0809 | 33.2954 | 34.2477 | 34.455 | 34.4311 | 34.3503 | 34.3445 | 34.2981 | 33.9933 | 34.3619 | 35.9413 | 35.1046 | 36.3059 | 36.3078 | 33.5009 | 92.1982 | 92.3605 | 92.2938
2022-09-08 03:48 | 5:58 | 22.1906 | 23.082 | 25.6409 | 35.8598 | 34.3845 | 33.8328 | 34.6865 | 35.4291 | 36.5217 | 37.3649 | 36.8817 | 37.9705 | 34.2847 | 34.2626 | 34.1536 | 35.0175 | 35.05 | 35.5518 | 36.3526 | 36.581 | 24.277 | 21.7593 | 92.3108 | 34.4863 | 33.0338 | 35.0135 | 33.2835 | 33.1057 | 33.3958 | 34.7612 | 34.296 | 34.0383 | 37.2211 | 36.2878 | 33.4042 | 34.399 | 36.2868 | 36.5196 | 37.431 | 36.2637 | 33.2709 | 32.7656 | 34.6139 | 35.0926 | 33.2891 | 34.249 | 34.4164 | 34.4192 | 34.3664 | 34.3313 | 34.2827 | 34.0095 | 34.3503 | 35.9397 | 35.116 | 36.3233 | 36.317 | 33.5014 | 92.122 | 92.2279 | 92.3053
2022-09-08 03:48 | 5:58 | 22.0508 | 22.9686 | 25.4238 | 35.8102 | 34.3658 | 33.82 | 34.6784 | 35.4319 | 36.5236 | 37.3676 | 36.88 | 37.9967 | 34.2827 | 34.2634 | 34.1458 | 35.0445 | 35.048 | 35.5491 | 36.3257 | 36.606 | 24.0962 | 21.576 | 92.2867 | 34.5321 | 33.0073 | 35.0235 | 33.2907 | 33.106 | 33.4079 | 34.7559 | 34.2674 | 34.0604 | 37.2035 | 36.2825 | 33.4076 | 34.3708 | 36.2942 | 36.5109 | 37.4187 | 36.2911 | 33.2877 | 32.7397 | 34.6065 | 35.0961 | 33.2867 | 34.252 | 34.4336 | 34.4235 | 34.3669 | 34.3636 | 34.2957 | 34.013 | 34.3664 | 35.9526 | 35.1146 | 36.3129 | 36.3036 | 33.495 | 92.0724 | 92.2028 | 92.2765
2022-09-08 03:48 | 5:58 | 21.8599 | 22.7147 | 25.3332 | 35.8868 | 34.3918 | 33.8233 | 34.6976 | 35.4388 | 36.5487 | 37.3665 | 36.8854 | 37.9924 | 34.2799 | 34.2439 | 34.1599 | 35.0389 | 35.0351 | 35.5554 | 36.3394 | 36.5778 | 23.9157 | 21.3928 | 92.335 | 34.3844 | 33.0493 | 35.0081 | 33.2816 | 33.077 | 33.3815 | 34.7469 | 34.2945 | 34.04 | 37.2054 | 36.2739 | 33.4034 | 34.3743 | 36.2878 | 36.5191 | 37.4487 | 36.2894 | 33.2988 | 32.7724 | 34.6036 | 35.0866 | 33.2809 | 34.2547 | 34.4273 | 34.4295 | 34.3692 | 34.3523 | 34.2769 | 34.0255 | 34.3669 | 35.9491 | 35.113 | 36.3063 | 36.3171 | 33.493 | 92.1653 | 92.2074 | 92.3422
2022-09-08 03:48 | 5:58 | 21.722 | 22.5954 | 25.1482 | 35.8454 | 34.3617 | 33.841 | 34.6978 | 35.4442 | 36.5394 | 37.3502 | 36.9106 | 37.99 | 34.2827 | 34.2523 | 34.1638 | 35.0333 | 35.0585 | 35.5408 | 36.3437 | 36.5899 | 23.6772 | 21.2428 | 92.3534 | 34.4566 | 33.047 | 35.0069 | 33.277 | 33.1022 | 33.3887 | 34.7649 | 34.2946 | 34.0446 | 37.21 | 36.2938 | 33.4056 | 34.3759 | 36.2825 | 36.5199 | 37.4344 | 36.2868 | 33.2859 | 32.7534 | 34.5922 | 35.0618 | 33.2736 | 34.252 | 34.4329 | 34.4147 | 34.3773 | 34.3511 | 34.2938 | 34.011 | 34.3692 | 35.9427 | 35.1031 | 36.3248 | 36.3291 | 33.5113 | 92.1752 | 92.2798 | 92.3402
2022-09-08 03:48 | 5:58 | 21.5936 | 22.4283 | 25.0195 | 35.7669 | 34.3536 | 33.8215 | 34.687 | 35.4407 | 36.5321 | 37.3657 | 36.8946 | 37.9954 | 34.2812 | 34.2518 | 34.1563 | 35.0506 | 35.0527 | 35.5386 | 36.3397 | 36.5983 | 23.4684 | 21.0697 | 92.4051 | 34.4351 | 33.0399 | 35.0046 | 33.2709 | 33.1027 | 33.4042 | 34.7618 | 34.3045 | 34.0455 | 37.2133 | 36.264 | 33.3839 | 34.3631 | 36.2739 | 36.5143 | 37.4424 | 36.2942 | 33.2958 | 32.7534 | 34.6141 | 35.075 | 33.2796 | 34.2461 | 34.4172 | 34.4111 | 34.3742 | 34.3342 | 34.2731 | 34.0135 | 34.3773 | 35.9516 | 35.1114 | 36.3206 | 36.3155 | 33.4969 | 92.2355 | 92.355 | 92.3506
2022-09-08 03:49 | 5:58 | 21.426 | 22.2685 | 24.8959 | 35.8078 | 34.3628 | 33.8283 | 34.6748 | 35.4315 | 36.5305 | 37.3664 | 36.8806 | 37.9958 | 34.2935 | 34.2437 | 34.1701 | 35.0576 | 35.0633 | 35.5562 | 36.3471 | 36.597 | 23.2671 | 20.9495 | 92.4246 | 34.267 | 33.0511 | 35.017 | 33.2877 | 33.0782 | 33.4076 | 34.7465 | 34.2866 | 34.0404 | 37.2139 | 36.2628 | 33.3862 | 34.3802 | 36.2938 | 36.5262 | 37.4425 | 36.2878 | 33.27 | 32.7537 | 34.6062 | 35.087 | 33.2584 | 34.2366 | 34.4199 | 34.4196 | 34.3805 | 34.3608 | 34.2923 | 34.0159 | 34.3742 | 35.9677 | 35.104 | 36.3171 | 36.3052 | 33.5056 | 92.2882 | 92.4393 | 92.3498
2022-09-08 03:49 | 5:59 | 21.2685 | 22.1228 | 24.7823 | 35.7452 | 34.3686 | 33.8183 | 34.6731 | 35.4399 | 36.5376 | 37.3519 | 36.8887 | 37.995 | 34.3064 | 34.2599 | 34.1492 | 35.0334 | 35.0433 | 35.5536 | 36.3106 | 36.607 | 23.078 | 20.7451 | 92.4859 | 34.3267 | 33.0438 | 35.0191 | 33.2988 | 33.0856 | 33.4034 | 34.7743 | 34.2745 | 34.0322 | 37.2027 | 36.2829 | 33.3854 | 34.3791 | 36.264 | 36.5012 | 37.4312 | 36.2825 | 33.2719 | 32.7619 | 34.592 | 35.0861 | 33.2462 | 34.2515 | 34.4001 | 34.4169 | 34.3716 | 34.3525 | 34.2772 | 34.0165 | 34.3805 | 35.9497 | 35.1232 | 36.3262 | 36.3173 | 33.4881 | 92.3746 | 92.5506 | 92.4634
2022-09-08 03:49 | 5:59 | 21.1576 | 22.0132 | 24.6249 | 35.6238 | 34.3774 | 33.8414 | 34.6802 | 35.4331 | 36.5377 | 37.3707 | 36.8903 | 37.9857 | 34.2832 | 34.2711 | 34.1694 | 35.0368 | 35.0635 | 35.5326 | 36.3188 | 36.5854 | 22.9244 | 20.6032 | 92.5519 | 34.2776 | 33.0558 | 35.0234 | 33.2859 | 33.0974 | 33.4056 | 34.7578 | 34.2808 | 34.0276 | 37.2023 | 36.2497 | 33.3855 | 34.3772 | 36.2628 | 36.5197 | 37.4342 | 36.2739 | 33.2907 | 32.7428 | 34.5749 | 35.0654 | 33.2222 | 34.2602 | 34.4151 | 34.4227 | 34.3826 | 34.3616 | 34.2701 | 34.0145 | 34.3716 | 35.9622 | 35.0804 | 36.3245 | 36.3242 | 33.5155 | 92.4448 | 92.6848 | 92.5314
2022-09-08 03:49 | 5:59 | 21.1137 | 21.8135 | 24.4605 | 35.6851 | 34.3532 | 33.8229 | 34.6792 | 35.4231 | 36.5376 | 37.352 | 36.8751 | 37.9734 | 34.3067 | 34.2577 | 34.1623 | 35.0314 | 35.0633 | 35.5232 | 36.3106 | 36.5792 | 22.7844 | 20.4413 | 92.6248 | 34.2385 | 33.0481 | 35.0041 | 33.2958 | 33.0858 | 33.3839 | 34.7503 | 34.2676 | 34.0391 | 37.2 | 36.2736 | 33.3799 | 34.3655 | 36.2829 | 36.5013 | 37.456 | 36.2938 | 33.2728 | 32.7352 | 34.5766 | 35.0793 | 33.2241 | 34.2486 | 34.4106 | 34.4045 | 34.3757 | 34.3556 | 34.2775 | 34.0343 | 34.3826 | 35.9273 | 35.1003 | 36.3256 | 36.3084 | 33.5143 | 92.5619 | 92.8307 | 92.6345
2022-09-08 03:49 | 5:59 | 21.0516 | 21.6698 | 24.2982 | 35.5941 | 34.3604 | 33.8211 | 34.6652 | 35.4269 | 36.537 | 37.3393 | 36.8767 | 37.9781 | 34.304 | 34.2525 | 34.1651 | 35.0145 | 35.042 | 35.5312 | 36.313 | 36.5839 | 22.6478 | 20.3409 | 92.6501 | 34.1928 | 33.0347 | 35.0129 | 33.27 | 33.078 | 33.3862 | 34.7485 | 34.2795 | 34.032 | 37.2094 | 36.2759 | 33.3922 | 34.3716 | 36.2497 | 36.4954 | 37.4329 | 36.264 | 33.289 | 32.7625 | 34.5696 | 35.0531 | 33.2305 | 34.2589 | 34.4168 | 34.4023 | 34.3972 | 34.3518 | 34.2698 | 34.0185 | 34.3757 | 35.9596 | 35.1151 | 36.316 | 36.3293 | 33.5081 | 92.7396 | 92.9657 | 92.7849
2022-09-08 03:49 | 5:59 | 20.6805 | 21.4633 | 24.1477 | 35.6128 | 34.3499 | 33.8175 | 34.6579 | 35.4204 | 36.5358 | 37.3557 | 36.8727 | 37.9917 | 34.3165 | 34.2627 | 34.1624 | 35.0421 | 35.0573 | 35.5222 | 36.3265 | 36.5917 | 22.5431 | 20.1224 | 92.8053 | 34.304 | 33.0347 | 35.0077 | 33.2719 | 33.0778 | 33.3854 | 34.7351 | 34.2624 | 34.0283 | 37.21 | 36.2767 | 33.3795 | 34.3807 | 36.2736 | 36.5159 | 37.4282 | 36.2628 | 33.2744 | 32.7276 | 34.574 | 35.0705 | 33.2296 | 34.2389 | 34.4091 | 34.4059 | 34.4101 | 34.3473 | 34.2889 | 34.0065 | 34.3972 | 35.9549 | 35.1002 | 36.3277 | 36.3133 | 33.4948 | 92.9445 | 93.0949 | 92.8929
2022-09-08 03:50 | 6:00 | 20.5838 | 21.3789 | 24.0591 | 35.5944 | 34.3373 | 33.8186 | 34.6714 | 35.4349 | 36.5594 | 37.3458 | 36.868 | 37.9803 | 34.296 | 34.2715 | 34.1538 | 35.0289 | 35.0593 | 35.5289 | 36.3014 | 36.5908 | 22.4066 | 20.0005 | 92.852 | 34.025 | 33.0326 | 35.0025 | 33.2907 | 33.0612 | 33.3855 | 34.7544 | 34.2795 | 34.037 | 37.1929 | 36.2873 | 33.3946 | 34.3696 | 36.2759 | 36.5055 | 37.4139 | 36.2829 | 33.2723 | 32.7377 | 34.569 | 35.0591 | 33.2267 | 34.229 | 34.4137 | 34.3945 | 34.3942 | 34.3631 | 34.2827 | 34.0189 | 34.4101 | 35.9569 | 35.0929 | 36.3302 | 36.3237 | 33.4966 | 93.0614 | 93.1519 | 92.9911
2022-09-08 03:50 | 6:00 | 20.5062 | 21.2536 | 23.941 | 35.6098 | 34.3479 | 33.8139 | 34.6577 | 35.4367 | 36.5369 | 37.3407 | 36.8896 | 37.9707 | 34.2982 | 34.2733 | 34.1553 | 35.0327 | 35.059 | 35.5304 | 36.3104 | 36.5729 | 22.3382 | 19.907 | 92.9342 | 34.0477 | 33.0209 | 35.0087 | 33.2728 | 33.0596 | 33.3799 | 34.7398 | 34.2782 | 34.018 | 37.2014 | 36.2756 | 33.4004 | 34.3694 | 36.2767 | 36.5026 | 37.4166 | 36.2497 | 33.2812 | 32.7239 | 34.5476 | 35.046 | 33.215 | 34.2635 | 34.3952 | 34.3932 | 34.3994 | 34.3588 | 34.2647 | 34.0178 | 34.3942 | 35.9347 | 35.0891 | 36.3449 | 36.3161 | 33.4844 | 93.0984 | 93.3076 | 92.9366
2022-09-08 03:50 | 6:00 | 20.3022 | 21.0788 | 23.8062 | 35.5124 | 34.3418 | 33.8198 | 34.6632 | 35.4452 | 36.5361 | 37.3523 | 36.8883 | 37.9844 | 34.3148 | 34.2696 | 34.1627 | 35.0408 | 35.0504 | 35.5192 | 36.3036 | 36.5851 | 22.3053 | 19.7711 | 93.0283 | 34.1586 | 33.0197 | 35.0159 | 33.289 | 33.0415 | 33.3922 | 34.7506 | 34.2829 | 34.0352 | 37.2042 | 36.2452 | 33.3928 | 34.3811 | 36.2873 | 36.4964 | 37.4419 | 36.2736 | 33.276 | 32.7195 | 34.5506 | 35.0474 | 33.1983 | 34.2428 | 34.3969 | 34.3857 | 34.4098 | 34.3765 | 34.2681 | 34.0188 | 34.3994 | 35.9689 | 35.101 | 36.3204 | 36.3178 | 33.5008 | 93.2367 | 93.4433 | 93.0981
2022-09-08 03:50 | 6:00 | 20.1906 | 20.9513 | 23.6464 | 35.5465 | 34.3498 | 33.8269 | 34.6435 | 35.4087 | 36.5443 | 37.3368 | 36.8773 | 37.9851 | 34.2949 | 34.2707 | 34.1589 | 35.0228 | 35.0524 | 35.5189 | 36.3127 | 36.5852 | 22.2347 | 19.6053 | 93.0483 | 33.98 | 33.0387 | 35.0001 | 33.2744 | 33.0386 | 33.3795 | 34.7612 | 34.2584 | 34.0377 | 37.1955 | 36.2464 | 33.3841 | 34.3642 | 36.2756 | 36.5022 | 37.439 | 36.2759 | 33.2692 | 32.7265 | 34.5497 | 35.0438 | 33.2077 | 34.2258 | 34.3822 | 34.3916 | 34.3983 | 34.3375 | 34.283 | 34.015 | 34.4098 | 35.9541 | 35.1155 | 36.3238 | 36.3213 | 33.5012 | 93.3379 | 93.6024 | 93.0617
2022-09-08 03:50 | 6:00 | 20.0935 | 20.8382 | 23.5461 | 35.5196 | 34.3176 | 33.8185 | 34.6678 | 35.4489 | 36.5363 | 37.3546 | 36.8502 | 37.9586 | 34.3084 | 34.2944 | 34.1633 | 35.042 | 35.0528 | 35.5311 | 36.2922 | 36.5745 | 22.1772 | 19.5287 | 93.1931 | 34.0519 | 33.0377 | 35.0057 | 33.2723 | 33.033 | 33.3946 | 34.7371 | 34.2638 | 34.0303 | 37.2168 | 36.2728 | 33.3908 | 34.3593 | 36.2452 | 36.5091 | 37.4309 | 36.2767 | 33.2806 | 32.7194 | 34.5213 | 35.036 | 33.1946 | 34.2403 | 34.3891 | 34.3824 | 34.4123 | 34.3617 | 34.2721 | 34.0097 | 34.3983 | 35.9604 | 35.0973 | 36.3319 | 36.3022 | 33.4929 | 93.5126 | 93.7939 | 93.2472
2022-09-08 03:50 | 6:00 | 20.0361 | 20.7857 | 23.4626 | 35.3697 | 34.3354 | 33.8231 | 34.6638 | 35.425 | 36.5339 | 37.3567 | 36.8713 | 37.9622 | 34.2919 | 34.2814 | 34.1516 | 35.0271 | 35.0563 | 35.5277 | 36.2844 | 36.5984 | 22.1329 | 19.4563 | 93.3507 | 33.9823 | 33.0211 | 34.9968 | 33.2812 | 33.0489 | 33.4004 | 34.74 | 34.2603 | 34.0225 | 37.199 | 36.265 | 33.3868 | 34.3868 | 36.2464 | 36.4924 | 37.4564 | 36.2873 | 33.2747 | 32.7207 | 34.5322 | 35.0121 | 33.1885 | 34.2407 | 34.3849 | 34.4062 | 34.4114 | 34.362 | 34.2586 | 34.0131 | 34.4123 | 35.966 | 35.0953 | 36.3327 | 36.3162 | 33.4965 | 93.6632 | 93.9939 | 93.3664
2022-09-08 03:51 | 6:00 | 19.9749 | 20.6434 | 23.3094 | 35.5253 | 34.3349 | 33.8292 | 34.6517 | 35.4273 | 36.5431 | 37.3496 | 36.8666 | 37.9685 | 34.3071 | 34.296 | 34.1641 | 35.0365 | 35.0416 | 35.5286 | 36.3045 | 36.5913 | 22.106 | 19.3257 | 93.436 | 34.0335 | 33.0275 | 34.9942 | 33.276 | 33.0416 | 33.3928 | 34.7545 | 34.2685 | 34.0186 | 37.1913 | 36.2643 | 33.3796 | 34.3702 | 36.2728 | 36.5075 | 37.4255 | 36.2756 | 33.2872 | 32.6994 | 34.5373 | 35.0346 | 33.1773 | 34.2518 | 34.3789 | 34.3742 | 34.4269 | 34.3398 | 34.2583 | 33.9976 | 34.4114 | 35.9564 | 35.0966 | 36.3349 | 36.317 | 33.5149 | 93.7999 | 94.1762 | 93.4239
2022-09-08 03:51 | 6:01 | 19.7944 | 20.5108 | 23.1478 | 35.4629 | 34.3052 | 33.8196 | 34.6609 | 35.4136 | 36.5496 | 37.3501 | 36.8622 | 37.9749 | 34.3096 | 34.2778 | 34.1508 | 35.0212 | 35.0573 | 35.5135 | 36.2856 | 36.5948 | 22.0621 | 19.2456 | 93.5247 | 34.0002 | 33.0238 | 34.9939 | 33.2692 | 33.019 | 33.3841 | 34.7548 | 34.2555 | 34.0129 | 37.199 | 36.2561 | 33.3875 | 34.3556 | 36.265 | 36.5081 | 37.4408 | 36.2452 | 33.2687 | 32.7085 | 34.5152 | 35.0281 | 33.1611 | 34.2593 | 34.3824 | 34.372 | 34.4099 | 34.3747 | 34.2704 | 34.0018 | 34.4269 | 35.9622 | 35.0983 | 36.3274 | 36.3168 | 33.4871 | 93.9468 | 94.3332 | 93.6084
2022-09-08 03:51 | 6:01 | 19.8097 | 20.3955 | 23.0611 | 35.4333 | 34.3244 | 33.8262 | 34.6397 | 35.426 | 36.5346 | 37.3386 | 36.891 | 37.9864 | 34.3162 | 34.2818 | 34.1706 | 35.024 | 35.062 | 35.5183 | 36.2892 | 36.596 | 22.0188 | 19.1833 | 93.6396 | 33.9596 | 33.0293 | 35.0089 | 33.2806 | 33.0275 | 33.3908 | 34.7404 | 34.2943 | 34.0316 | 37.1884 | 36.2655 | 33.388 | 34.3586 | 36.2643 | 36.5228 | 37.4389 | 36.2464 | 33.2706 | 32.6995 | 34.5152 | 35.0399 | 33.1573 | 34.2651 | 34.3919 | 34.3765 | 34.4132 | 34.3511 | 34.2681 | 34.0291 | 34.4099 | 35.954 | 35.1025 | 36.3258 | 36.3136 | 33.4967 | 94.1665 | 94.5181 | 93.7448
2022-09-08 03:51 | 6:01 | 19.6231 | 20.2951 | 22.9433 | 35.3555 | 34.3082 | 33.8309 | 34.6585 | 35.4306 | 36.5424 | 37.3581 | 36.8794 | 37.9801 | 34.321 | 34.2649 | 34.1599 | 35.0256 | 35.0525 | 35.5256 | 36.2797 | 36.5909 | 21.9892 | 19.0921 | 93.821 | 33.8465 | 33.025 | 35.0174 | 33.2747 | 33.0282 | 33.3868 | 34.7341 | 34.2582 | 34.028 | 37.2039 | 36.2799 | 33.3846 | 34.3791 | 36.2561 | 36.5126 | 37.4486 | 36.2728 | 33.261 | 32.6909 | 34.5204 | 35.01 | 33.1639 | 34.2621 | 34.385 | 34.3802 | 34.4238 | 34.3657 | 34.2561 | 33.9976 | 34.4132 | 35.9464 | 35.1085 | 36.3237 | 36.3151 | 33.4969 | 94.3215 | 94.7225 | 93.8428
2022-09-08 03:51 | 6:01 | 19.4947 | 20.1786 | 22.9154 | 35.3105 | 34.3131 | 33.8195 | 34.6377 | 35.4216 | 36.5464 | 37.3261 | 36.8727 | 37.9709 | 34.3144 | 34.2739 | 34.1611 | 35.014 | 35.0441 | 35.5222 | 36.2867 | 36.5791 | 21.9308 | 18.988 | 93.9067 | 33.9402 | 33.0292 | 35.0013 | 33.2872 | 33.0418 | 33.3796 | 34.7392 | 34.263 | 34.0271 | 37.191 | 36.2739 | 33.3821 | 34.3679 | 36.2655 | 36.4993 | 37.4188 | 36.265 | 33.2762 | 32.6728 | 34.5129 | 35.0205 | 33.1428 | 34.27 | 34.3715 | 34.3848 | 34.4121 | 34.3894 | 34.2619 | 33.992 | 34.4238 | 35.9456 | 35.0996 | 36.3399 | 36.309 | 33.5078 | 94.4754 | 94.9481 | 93.9907
2022-09-08 03:51 | 6:01 | 19.5076 | 20.1241 | 22.7715 | 35.3539 | 34.2898 | 33.8099 | 34.6472 | 35.422 | 36.5412 | 37.3343 | 36.8907 | 37.9751 | 34.318 | 34.2853 | 34.1507 | 35.0183 | 35.0573 | 35.5112 | 36.2807 | 36.584 | 21.9007 | 18.9948 | 93.9661 | 33.9081 | 33.0172 | 35.0057 | 33.2687 | 33.0284 | 33.3875 | 34.7435 | 34.2582 | 34.0354 | 37.2017 | 36.2694 | 33.3747 | 34.3624 | 36.2799 | 36.4871 | 37.4142 | 36.2643 | 33.2582 | 32.668 | 34.5057 | 35.0188 | 33.1497 | 34.2677 | 34.3791 | 34.3537 | 34.4179 | 34.3594 | 34.2527 | 34.0006 | 34.4121 | 35.9614 | 35.086 | 36.3268 | 36.3122 | 33.4988 | 94.5624 | 95.1179 | 94.1139
2022-09-08 03:52 | 6:02 | 19.3746 | 20.0418 | 22.7143 | 35.2413 | 34.3036 | 33.8077 | 34.6449 | 35.4163 | 36.5468 | 37.3589 | 36.882 | 37.9812 | 34.3345 | 34.2891 | 34.1609 | 35.0367 | 35.0339 | 35.5012 | 36.2898 | 36.5819 | 21.8369 | 18.8557 | 94.1 | 33.9688 | 33.0331 | 35.0033 | 33.2706 | 33.0042 | 33.388 | 34.7202 | 34.2668 | 34.0195 | 37.1907 | 36.2809 | 33.3713 | 34.3689 | 36.2739 | 36.4863 | 37.4294 | 36.2561 | 33.2861 | 32.674 | 34.513 | 35.0028 | 33.1353 | 34.2653 | 34.3557 | 34.3558 | 34.4172 | 34.3858 | 34.2639 | 33.9864 | 34.4179 | 35.9508 | 35.1006 | 36.3122 | 36.3156 | 33.486 | 94.6681 | 95.2641 | 94.2175
2022-09-08 03:52 | 6:02 | 19.3312 | 19.9926 | 22.6894 | 35.2733 | 34.3063 | 33.8295 | 34.6263 | 35.4396 | 36.5286 | 37.3455 | 36.865 | 37.979 | 34.3127 | 34.2936 | 34.1588 | 35.0341 | 35.0535 | 35.4954 | 36.2789 | 36.598 | 21.8079 | 18.7912 | 94.176 | 33.87 | 33.0199 | 35.0153 | 33.261 | 33.0154 | 33.3846 | 34.7513 | 34.2557 | 34.0241 | 37.2045 | 36.2549 | 33.3834 | 34.3571 | 36.2694 | 36.4971 | 37.4194 | 36.2655 | 33.2636 | 32.6705 | 34.4979 | 34.9921 | 33.157 | 34.2663 | 34.3709 | 34.3596 | 34.4247 | 34.3832 | 34.2508 | 33.9872 | 34.4172 | 35.9352 | 35.084 | 36.328 | 36.3249 | 33.4919 | 94.8477 | 95.4015 | 94.345
2022-09-08 03:52 | 6:02 | 19.2554 | 19.9128 | 22.5911 | 35.3018 | 34.3027 | 33.8021 | 34.6322 | 35.4415 | 36.5412 | 37.3455 | 36.8695 | 37.9753 | 34.3299 | 34.2927 | 34.152 | 35.0085 | 35.0526 | 35.5137 | 36.2748 | 36.5701 | 21.7792 | 18.7652 | 94.2407 | 33.8949 | 33.0149 | 34.9999 | 33.2762 | 33.0298 | 33.3821 | 34.7297 | 34.2562 | 34.0352 | 37.2091 | 36.284 | 33.3847 | 34.3674 | 36.2809 | 36.4949 | 37.4168 | 36.2799 | 33.2643 | 32.6672 | 34.4851 | 34.9893 | 33.1332 | 34.2742 | 34.3693 | 34.3644 | 34.426 | 34.4034 | 34.2626 | 33.9894 | 34.4247 | 35.9445 | 35.0993 | 36.3191 | 36.3162 | 33.4815 | 94.9499 | 95.5261 | 94.3384
2022-09-08 03:52 | 6:02 | 19.1827 | 19.8387 | 22.5089 | 35.1818 | 34.2816 | 33.8181 | 34.6316 | 35.408 | 36.5187 | 37.3357 | 36.8619 | 37.9718 | 34.3448 | 34.2907 | 34.1582 | 35.0335 | 35.0516 | 35.5236 | 36.2806 | 36.5701 | 21.7495 | 18.6543 | 94.3113 | 33.7578 | 33.0204 | 34.9939 | 33.2582 | 33.0134 | 33.3747 | 34.7209 | 34.2472 | 34.031 | 37.1878 | 36.2564 | 33.3763 | 34.3522 | 36.2549 | 36.4978 | 37.4191 | 36.2739 | 33.273 | 32.6625 | 34.4825 | 34.9798 | 33.1001 | 34.2957 | 34.371 | 34.3478 | 34.4326 | 34.3836 | 34.2634 | 33.9862 | 34.426 | 35.9672 | 35.0904 | 36.3393 | 36.3128 | 33.4818 | 95.1231 | 95.6375 | 94.4155
2022-09-08 03:52 | 6:02 | 19.1025 | 19.7134 | 22.4747 | 35.271 | 34.2981 | 33.8127 | 34.6355 | 35.4308 | 36.5427 | 37.3406 | 36.8691 | 37.9588 | 34.3212 | 34.2996 | 34.1533 | 35.025 | 35.0416 | 35.4991 | 36.2633 | 36.5788 | 21.7364 | 18.6138 | 94.3625 | 33.7857 | 33.0314 | 34.9951 | 33.2861 | 33.028 | 33.3713 | 34.7343 | 34.2672 | 34.0134 | 37.2054 | 36.2723 | 33.3677 | 34.3578 | 36.284 | 36.4926 | 37.416 | 36.2694 | 33.2722 | 32.6666 | 34.4684 | 34.9731 | 33.1256 | 34.2737 | 34.3707 | 34.3682 | 34.4374 | 34.392 | 34.2439 | 33.9858 | 34.4326 | 35.932 | 35.0925 | 36.3244 | 36.3017 | 33.4764 | 95.1162 | 95.6613 | 94.3771
2022-09-08 03:52 | 6:02 | 18.9687 | 19.6003 | 22.3361 | 35.2036 | 34.2981 | 33.821 | 34.6226 | 35.4396 | 36.5362 | 37.3282 | 36.8637 | 37.9592 | 34.3263 | 34.3058 | 34.1393 | 35.0316 | 35.0539 | 35.4879 | 36.2567 | 36.5653 | 21.6961 | 18.4765 | 94.4043 | 33.8388 | 33.0175 | 34.9968 | 33.2636 | 33.0331 | 33.3834 | 34.7209 | 34.2631 | 34.0314 | 37.2079 | 36.2546 | 33.3816 | 34.3575 | 36.2564 | 36.4909 | 37.4056 | 36.2809 | 33.2558 | 32.6632 | 34.4818 | 34.9625 | 33.0958 | 34.2621 | 34.3559 | 34.3529 | 34.443 | 34.3863 | 34.2523 | 33.9931 | 34.4374 | 35.9429 | 35.0902 | 36.3384 | 36.3043 | 33.4619 | 95.2083 | 95.7177 | 94.4916
2022-09-08 03:53 | 6:02 | 18.9306 | 19.5249 | 22.2794 | 35.1378 | 34.2827 | 33.8256 | 34.6384 | 35.4179 | 36.5371 | 37.3303 | 36.8931 | 37.9781 | 34.3437 | 34.2985 | 34.1364 | 35.0332 | 35.0664 | 35.4805 | 36.2581 | 36.5779 | 21.6927 | 18.454 | 94.3547 | 33.7139 | 33.0227 | 35.0173 | 33.2643 | 33.0111 | 33.3847 | 34.7096 | 34.2438 | 34.0161 | 37.1895 | 36.2508 | 33.3794 | 34.3558 | 36.2723 | 36.5049 | 37.3974 | 36.2549 | 33.2737 | 32.6522 | 34.4818 | 34.9672 | 33.1128 | 34.2724 | 34.3669 | 34.3551 | 34.4445 | 34.3792 | 34.2518 | 33.9944 | 34.443 | 35.9414 | 35.099 | 36.3308 | 36.304 | 33.4674 | 95.1662 | 95.6006 | 94.4272
2022-09-08 03:53 | 6:03 | 18.9244 | 19.4816 | 22.2087 | 35.2107 | 34.2957 | 33.8122 | 34.6346 | 35.423 | 36.544 | 37.3115 | 36.8831 | 37.9574 | 34.331 | 34.3169 | 34.1554 | 35.0251 | 35.0427 | 35.47 | 36.2689 | 36.5563 | 21.6664 | 18.3946 | 94.1684 | 33.736 | 33.0196 | 35.0109 | 33.273 | 33.0084 | 33.3763 | 34.7194 | 34.2514 | 34.0177 | 37.1936 | 36.246 | 33.3617 | 34.3696 | 36.2546 | 36.4933 | 37.4008 | 36.284 | 33.2672 | 32.6547 | 34.4533 | 34.9609 | 33.1021 | 34.27 | 34.3586 | 34.3425 | 34.4303 | 34.3816 | 34.2437 | 33.9748 | 34.4445 | 35.9266 | 35.0933 | 36.321 | 36.3032 | 33.4411 | 94.9221 | 95.3124 | 94.2206
2022-09-08 03:53 | 6:03 | 18.7706 | 19.3734 | 22.1227 | 35.0946 | 34.2769 | 33.8202 | 34.6254 | 35.4238 | 36.5216 | 37.3125 | 36.8944 | 37.9697 | 34.3357 | 34.2959 | 34.1516 | 35.0259 | 35.0564 | 35.4906 | 36.2385 | 36.5537 | 21.6579 | 18.3613 | 94.0707 | 33.709 | 33.0027 | 35.0085 | 33.2722 | 33.0154 | 33.3677 | 34.7197 | 34.2571 | 34.0222 | 37.1916 | 36.2696 | 33.3787 | 34.3697 | 36.2508 | 36.4851 | 37.4149 | 36.2564 | 33.2608 | 32.6411 | 34.459 | 34.9719 | 33.1204 | 34.2821 | 34.3725 | 34.3567 | 34.4451 | 34.4022 | 34.2599 | 33.954 | 34.4303 | 35.9366 | 35.1103 | 36.326 | 36.3008 | 33.455 | 94.6675 | 95.0383 | 94.0497
2022-09-08 03:53 | 6:03 | 18.7531 | 19.3491 | 22.1045 | 35.1769 | 34.2938 | 33.8015 | 34.6163 | 35.425 | 36.5344 | 37.3108 | 36.8772 | 37.9573 | 34.3207 | 34.2938 | 34.1694 | 35.0276 | 35.0381 | 35.4929 | 36.2499 | 36.57 | 21.6204 | 18.2678 | 93.9758 | 33.6708 | 33.0058 | 35.0057 | 33.2558 | 33.0129 | 33.3816 | 34.7046 | 34.2649 | 34.0189 | 37.1751 | 36.2795 | 33.3936 | 34.3631 | 36.246 | 36.4899 | 37.3969 | 36.2723 | 33.2691 | 32.6244 | 34.4348 | 34.9645 | 33.0778 | 34.2861 | 34.3397 | 34.3457 | 34.4376 | 34.418 | 34.2711 | 33.9568 | 34.4451 | 35.9125 | 35.1117 | 36.3239 | 36.3196 | 33.4748 | 94.4634 | 94.866 | 94.0439
2022-09-08 03:53 | 6:03 | 18.7129 | 19.255 | 21.9976 | 35.0216 | 34.2731 | 33.8041 | 34.6128 | 35.4134 | 36.5312 | 37.3327 | 36.8807 | 37.9789 | 34.3302 | 34.3121 | 34.1366 | 35.0088 | 35.0324 | 35.4715 | 36.2471 | 36.5362 | 21.6178 | 18.2208 | 93.9144 | 33.5919 | 32.99 | 35.004 | 33.2737 | 32.9944 | 33.3794 | 34.721 | 34.2503 | 34.0349 | 37.1932 | 36.2522 | 33.3723 | 34.3533 | 36.2696 | 36.4845 | 37.3945 | 36.2546 | 33.269 | 32.6046 | 34.4382 | 34.9463 | 33.0817 | 34.2656 | 34.3448 | 34.3453 | 34.4296 | 34.3974 | 34.2577 | 33.9881 | 34.4376 | 35.9187 | 35.1155 | 36.3221 | 36.3068 | 33.4321 | 94.3652 | 94.7042 | 93.8703
2022-09-08 03:53 | 6:03 | 18.6112 | 19.1926 | 21.8803 | 35.0081 | 34.2923 | 33.8142 | 34.615 | 35.4194 | 36.5269 | 37.3126 | 36.8665 | 37.9592 | 34.3411 | 34.3078 | 34.1134 | 35.0212 | 35.0353 | 35.4738 | 36.2282 | 36.5284 | 21.6165 | 18.1431 | 93.8146 | 33.6942 | 33.0004 | 35.0061 | 33.2672 | 32.9926 | 33.3617 | 34.6988 | 34.2619 | 34.0108 | 37.1826 | 36.2499 | 33.3725 | 34.3728 | 36.2795 | 36.4807 | 37.3932 | 36.2508 | 33.2634 | 32.6236 | 34.4355 | 34.926 | 33.074 | 34.2876 | 34.3559 | 34.3452 | 34.4382 | 34.3967 | 34.2525 | 33.9791 | 34.4296 | 35.9153 | 35.1025 | 36.3303 | 36.2936 | 33.443 | 94.2653 | 94.6399 | 93.7963
2022-09-08 03:54 | 6:04 | 18.6195 | 19.1924 | 21.8811 | 35.0453 | 34.2772 | 33.8134 | 34.6126 | 35.4215 | 36.5212 | 37.3242 | 36.8736 | 37.9684 | 34.3387 | 34.3231 | 34.1438 | 35.021 | 35.0444 | 35.4795 | 36.242 | 36.5528 | 21.6363 | 18.157 | 93.7636 | 33.6333 | 32.9847 | 34.9971 | 33.2608 | 33.001 | 33.3787 | 34.7233 | 34.2397 | 34.0249 | 37.1906 | 36.2499 | 33.3597 | 34.3676 | 36.2522 | 36.4786 | 37.3935 | 36.246 | 33.2664 | 32.6049 | 34.4373 | 34.9299 | 33.0619 | 34.2844 | 34.3519 | 34.3377 | 34.4312 | 34.3908 | 34.2627 | 33.9794 | 34.4382 | 35.9036 | 35.0862 | 36.3372 | 36.293 | 33.4434 | 94.1406 | 94.5521 | 93.8266
2022-09-08 03:54 | 6:04 | 18.5765 | 19.1127 | 21.8445 | 35.0468 | 34.2701 | 33.793 | 34.6311 | 35.4048 | 36.5273 | 37.3257 | 36.8892 | 37.9845 | 34.3405 | 34.3181 | 34.1193 | 35.0143 | 35.0538 | 35.4549 | 36.2296 | 36.5527 | 21.6539 | 18.1656 | 93.711 | 33.7246 | 32.9767 | 35.0036 | 33.2691 | 33.026 | 33.3936 | 34.6976 | 34.2575 | 34.0198 | 37.1906 | 36.2488 | 33.3745 | 34.3416 | 36.2499 | 36.4837 | 37.3617 | 36.2696 | 33.2781 | 32.6239 | 34.4175 | 34.9397 | 33.0621 | 34.2697 | 34.3565 | 34.3544 | 34.4579 | 34.4089 | 34.2715 | 33.9611 | 34.4312 | 35.925 | 35.1032 | 36.3285 | 36.2825 | 33.4338 | 94.0868 | 94.4165 | 93.6965
2022-09-08 03:54 | 6:04 | 18.4657 | 18.9941 | 21.8366 | 34.977 | 34.2775 | 33.8151 | 34.6178 | 35.4098 | 36.5294 | 37.3253 | 36.8816 | 37.9781 | 34.3314 | 34.3252 | 34.1414 | 35.0399 | 35.0349 | 35.4627 | 36.2269 | 36.5424 | 21.6625 | 18.0866 | 93.5601 | 33.5651 | 32.9991 | 35.0014 | 33.269 | 32.9866 | 33.3723 | 34.7161 | 34.2673 | 34.0237 | 37.1775 | 36.2632 | 33.365 | 34.3604 | 36.2499 | 36.4997 | 37.3856 | 36.2795 | 33.2619 | 32.5909 | 34.4227 | 34.9131 | 33.0603 | 34.2787 | 34.338 | 34.3551 | 34.4456 | 34.4226 | 34.2733 | 33.9647 | 34.4579 | 35.9085 | 35.1066 | 36.3409 | 36.297 | 33.4382 | 93.9699 | 94.2638 | 93.6294
2022-09-08 03:54 | 6:04 | 18.4345 | 18.9481 | 21.757 | 34.9411 | 34.2698 | 33.8359 | 34.6187 | 35.4024 | 36.5259 | 37.2907 | 36.8745 | 37.9715 | 34.3627 | 34.3314 | 34.1447 | 35.0311 | 35.045 | 35.4854 | 36.2138 | 36.5406 | 21.6355 | 18.0181 | 93.6067 | 33.5891 | 32.9895 | 35.0107 | 33.2634 | 32.998 | 33.3725 | 34.6996 | 34.2507 | 34.0207 | 37.185 | 36.2742 | 33.3719 | 34.3657 | 36.2488 | 36.4922 | 37.4027 | 36.2522 | 33.2639 | 32.5937 | 34.3982 | 34.932 | 33.0627 | 34.2784 | 34.3476 | 34.3407 | 34.4412 | 34.4184 | 34.2696 | 33.9616 | 34.4456 | 35.9179 | 35.1214 | 36.3353 | 36.2853 | 33.4393 | 93.8837 | 94.1956 | 93.628
2022-09-08 03:54 | 6:04 | 18.485 | 18.9758 | 21.7603 | 34.9196 | 34.2889 | 33.8174 | 34.595 | 35.4061 | 36.5107 | 37.2976 | 36.8856 | 37.9767 | 34.3524 | 34.2991 | 34.1176 | 35.0315 | 35.0418 | 35.4797 | 36.2155 | 36.5377 | 21.6345 | 18.0436 | 93.5964 | 33.5679 | 32.9885 | 35.0095 | 33.2664 | 33.0098 | 33.3597 | 34.6977 | 34.2669 | 34.0241 | 37.1913 | 36.2655 | 33.3756 | 34.3587 | 36.2632 | 36.486 | 37.39 | 36.2499 | 33.2576 | 32.6202 | 34.4113 | 34.8988 | 33.0491 | 34.2751 | 34.3403 | 34.3234 | 34.4437 | 34.4196 | 34.2707 | 33.9794 | 34.4412 | 35.9079 | 35.1011 | 36.3221 | 36.2945 | 33.4332 | 93.8073 | 94.1587 | 93.575
2022-09-08 03:54 | 6:04 | 18.3647 | 18.8786 | 21.6243 | 34.8693 | 34.2827 | 33.8329 | 34.6243 | 35.4236 | 36.5179 | 37.2858 | 36.885 | 37.974 | 34.339 | 34.3191 | 34.1366 | 35.0307 | 35.0399 | 35.4734 | 36.2253 | 36.5397 | 21.6149 | 17.9252 | 93.6967 | 33.5809 | 32.9964 | 34.9992 | 33.2781 | 33.0089 | 33.3745 | 34.6882 | 34.2617 | 34.0342 | 37.1916 | 36.2543 | 33.3643 | 34.3537 | 36.2742 | 36.4942 | 37.3738 | 36.2499 | 33.2888 | 32.5825 | 34.4131 | 34.9095 | 33.0465 | 34.2755 | 34.3401 | 34.3609 | 34.4477 | 34.4232 | 34.2944 | 33.9713 | 34.4437 | 35.9109 | 35.1107 | 36.3314 | 36.3109 | 33.4305 | 93.8374 | 94.104 | 93.622
2022-09-08 03:55 | 6:04 | 18.379 | 18.8662 | 21.5428 | 34.8879 | 34.2647 | 33.8275 | 34.6079 | 35.4256 | 36.5161 | 37.306 | 36.8953 | 37.9741 | 34.3447 | 34.3173 | 34.1219 | 35.0302 | 35.0406 | 35.4788 | 36.2049 | 36.5287 | 21.6212 | 17.9547 | 93.6073 | 33.5915 | 32.9879 | 35.0153 | 33.2619 | 32.9871 | 33.365 | 34.6907 | 34.2586 | 34.0273 | 37.1861 | 36.2404 | 33.3635 | 34.3535 | 36.2655 | 36.4734 | 37.3957 | 36.2488 | 33.2738 | 32.5953 | 34.3942 | 34.8957 | 33.0398 | 34.2747 | 34.3429 | 34.3622 | 34.4351 | 34.4102 | 34.2814 | 33.9606 | 34.4477 | 35.9236 | 35.1053 | 36.3446 | 36.29 | 33.4306 | 93.8008 | 94.0389 | 93.5053
2022-09-08 03:55 | 6:05 | 18.4031 | 18.8479 | 21.5674 | 34.8838 | 34.2681 | 33.8401 | 34.6009 | 35.4265 | 36.5384 | 37.2949 | 36.8762 | 37.9787 | 34.3445 | 34.3165 | 34.1296 | 35.0278 | 35.038 | 35.4708 | 36.2009 | 36.5431 | 21.595 | 17.9746 | 93.6245 | 33.5776 | 32.983 | 35.0003 | 33.2639 | 32.9966 | 33.3719 | 34.7131 | 34.2573 | 34.0207 | 37.1746 | 36.2718 | 33.378 | 34.3538 | 36.2543 | 36.4745 | 37.3771 | 36.2632 | 33.274 | 32.5759 | 34.3894 | 34.9037 | 33.0408 | 34.277 | 34.3268 | 34.3494 | 34.4478 | 34.4409 | 34.296 | 33.9519 | 34.4351 | 35.9163 | 35.1025 | 36.3358 | 36.3139 | 33.4268 | 93.8088 | 94.041 | 93.6108
2022-09-08 03:55 | 6:05 | 18.2492 | 18.7196 | 21.4487 | 34.8621 | 34.283 | 33.8265 | 34.5956 | 35.414 | 36.5474 | 37.2999 | 36.8902 | 37.9819 | 34.3313 | 34.3 | 34.1341 | 35.0266 | 35.0408 | 35.4546 | 36.208 | 36.5331 | 21.5867 | 17.9285 | 93.5587 | 33.626 | 33.0083 | 35.0169 | 33.2576 | 32.9897 | 33.3756 | 34.6886 | 34.2667 | 34.0366 | 37.1869 | 36.2935 | 33.3806 | 34.3843 | 36.2404 | 36.4987 | 37.388 | 36.2742 | 33.2712 | 32.5957 | 34.4076 | 34.9013 | 33.0266 | 34.2969 | 34.308 | 34.363 | 34.4459 | 34.4239 | 34.2778 | 33.9565 | 34.4478 | 35.8956 | 35.1044 | 36.3321 | 36.3156 | 33.4387 | 93.683 | 93.9224 | 93.4358
2022-09-08 03:55 | 6:05 | 18.3169 | 18.7154 | 21.4143 | 34.8948 | 34.2721 | 33.8411 | 34.6055 | 35.4149 | 36.523 | 37.2939 | 36.8976 | 37.9858 | 34.3636 | 34.325 | 34.1336 | 35.0293 | 35.0491 | 35.4698 | 36.2184 | 36.5348 | 21.5525 | 17.8737 | 93.4208 | 33.4823 | 32.9887 | 35.0076 | 33.2888 | 33.0119 | 33.3643 | 34.6842 | 34.2516 | 34.0402 | 37.1887 | 36.2495 | 33.3636 | 34.3764 | 36.2718 | 36.4949 | 37.3781 | 36.2655 | 33.2598 | 32.5877 | 34.3881 | 34.9104 | 33.0147 | 34.2686 | 34.3268 | 34.3474 | 34.4329 | 34.4106 | 34.2818 | 33.9569 | 34.4459 | 35.9321 | 35.0843 | 36.3277 | 36.3088 | 33.4384 | 93.5863 | 93.8319 | 93.3947
2022-09-08 03:55 | 6:05 | 18.2121 | 18.6422 | 21.3973 | 34.8878 | 34.2586 | 33.8253 | 34.6097 | 35.4238 | 36.5222 | 37.3149 | 36.9005 | 37.9981 | 34.3523 | 34.3387 | 34.1228 | 35.0339 | 35.0478 | 35.4556 | 36.2246 | 36.5328 | 21.5648 | 17.8676 | 93.3929 | 33.5261 | 32.9858 | 35.0132 | 33.2738 | 32.9906 | 33.3635 | 34.6958 | 34.2612 | 34.0213 | 37.1737 | 36.2634 | 33.3789 | 34.3794 | 36.2935 | 36.4937 | 37.3721 | 36.2543 | 33.2735 | 32.5892 | 34.4059 | 34.8912 | 33.0197 | 34.2753 | 34.3219 | 34.3508 | 34.4528 | 34.4389 | 34.2649 | 33.9507 | 34.4329 | 35.9262 | 35.1006 | 36.3419 | 36.2987 | 33.4363 | 93.5205 | 93.7555 | 93.3242
2022-09-08 03:55 | 6:05 | 18.0976 | 18.5575 | 21.3764 | 34.825 | 34.2583 | 33.84 | 34.6229 | 35.4234 | 36.5386 | 37.3249 | 36.8968 | 37.9891 | 34.3511 | 34.3204 | 34.1194 | 35.0379 | 35.0431 | 35.4674 | 36.1969 | 36.5276 | 21.5247 | 17.7741 | 93.3146 | 33.5081 | 32.9954 | 35.0195 | 33.274 | 32.9958 | 33.378 | 34.703 | 34.2567 | 34.0369 | 37.1879 | 36.2552 | 33.3695 | 34.3913 | 36.2495 | 36.4869 | 37.3626 | 36.2404 | 33.2606 | 32.5592 | 34.3904 | 34.9047 | 33.0089 | 34.3039 | 34.3088 | 34.3715 | 34.4457 | 34.4553 | 34.2739 | 33.9539 | 34.4528 | 35.9098 | 35.1211 | 36.3411 | 36.3092 | 33.4288 | 93.4379 | 93.6665 | 93.2601
2022-09-08 03:56 | 6:05 | 18.0527 | 18.4998 | 21.2857 | 34.8771 | 34.2704 | 33.8304 | 34.6203 | 35.4286 | 36.5286 | 37.3019 | 36.8982 | 37.9668 | 34.3342 | 34.3322 | 34.1255 | 35.0308 | 35.0424 | 35.4617 | 36.209 | 36.5604 | 21.4935 | 17.7361 | 93.279 | 33.514 | 32.9912 | 35.0255 | 33.2712 | 32.9954 | 33.3806 | 34.6845 | 34.2733 | 34.0567 | 37.1933 | 36.2702 | 33.3782 | 34.3809 | 36.2634 | 36.4928 | 37.3653 | 36.2718 | 33.2718 | 32.5719 | 34.3819 | 34.8869 | 33.0275 | 34.3025 | 34.3074 | 34.3569 | 34.4386 | 34.423 | 34.2853 | 33.9628 | 34.4457 | 35.9311 | 35.0962 | 36.3268 | 36.318 | 33.4096 | 93.3414 | 93.5802 | 93.201
2022-09-08 03:56 | 6:06 | 18.1009 | 18.4928 | 21.1717 | 34.7938 | 34.2681 | 33.8227 | 34.6062 | 35.417 | 36.522 | 37.2941 | 36.8939 | 37.9948 | 34.3608 | 34.3381 | 34.1435 | 35.0361 | 35.0414 | 35.4589 | 36.1999 | 36.56 | 21.4771 | 17.7457 | 93.3312 | 33.3811 | 32.9753 | 35.0143 | 33.2598 | 32.9987 | 33.3636 | 34.6755 | 34.2639 | 34.0246 | 37.2012 | 36.2636 | 33.3796 | 34.3835 | 36.2552 | 36.4975 | 37.3527 | 36.2935 | 33.2822 | 32.5571 | 34.3661 | 34.8878 | 33.0079 | 34.2992 | 34.3091 | 34.3462 | 34.455 | 34.4346 | 34.2891 | 33.9346 | 34.4386 | 35.9117 | 35.1038 | 36.3485 | 36.2936 | 33.4349 | 93.3494 | 93.5268 | 93.2628
2022-09-08 03:56 | 6:06 | 18.0183 | 18.4562 | 21.1783 | 34.8553 | 34.2561 | 33.8322 | 34.611 | 35.4174 | 36.5139 | 37.291 | 36.9072 | 37.9881 | 34.3525 | 34.3467 | 34.1226 | 35.033 | 35.0714 | 35.4641 | 36.2103 | 36.5325 | 21.4595 | 17.7181 | 93.2851 | 33.4131 | 32.977 | 35.0125 | 33.2735 | 33.0081 | 33.3789 | 34.6861 | 34.261 | 34.0375 | 37.1943 | 36.2698 | 33.371 | 34.3611 | 36.2702 | 36.4983 | 37.3757 | 36.2495 | 33.2735 | 32.5744 | 34.3776 | 34.8935 | 33.0054 | 34.2896 | 34.2994 | 34.3559 | 34.4164 | 34.4469 | 34.2936 | 33.9522 | 34.455 | 35.916 | 35.1062 | 36.3294 | 36.3085 | 33.432 | 93.2576 | 93.4475 | 93.161
2022-09-08 03:56 | 6:06 | 18.0269 | 18.472 | 21.1701 | 34.8703 | 34.2619 | 33.8506 | 34.601 | 35.4143 | 36.5441 | 37.3053 | 36.8867 | 37.9785 | 34.3616 | 34.3486 | 34.115 | 35.0453 | 35.0521 | 35.4635 | 36.2034 | 36.5429 | 21.4539 | 17.6805 | 93.2979 | 33.3505 | 32.9868 | 35.0109 | 33.2606 | 33.0028 | 33.3695 | 34.6904 | 34.2683 | 34.0523 | 37.1793 | 36.268 | 33.3837 | 34.378 | 36.2636 | 36.5033 | 37.365 | 36.2634 | 33.2663 | 32.5422 | 34.3739 | 34.8997 | 33.0135 | 34.3013 | 34.3144 | 34.3773 | 34.4336 | 34.4279 | 34.2927 | 33.9409 | 34.4164 | 35.9202 | 35.0895 | 36.3449 | 36.3171 | 33.4354 | 93.2188 | 93.3081 | 93.2131
2022-09-08 03:56 | 6:06 | 17.8929 | 18.3368 | 21.1008 | 34.8061 | 34.2527 | 33.8485 | 34.61 | 35.3878 | 36.52 | 37.3068 | 36.8938 | 38.0094 | 34.3556 | 34.3317 | 34.1229 | 35.047 | 35.0631 | 35.4564 | 36.2028 | 36.5368 | 21.4428 | 17.6514 | 93.1929 | 33.4826 | 32.9935 | 35.0169 | 33.2718 | 32.9987 | 33.3782 | 34.6878 | 34.2765 | 34.0376 | 37.1996 | 36.2514 | 33.3765 | 34.371 | 36.2698 | 36.5049 | 37.3714 | 36.2552 | 33.2656 | 32.5717 | 34.3545 | 34.8907 | 32.9996 | 34.2854 | 34.299 | 34.3603 | 34.4273 | 34.4279 | 34.2907 | 33.9498 | 34.4336 | 35.9261 | 35.1102 | 36.327 | 36.2998 | 33.4295 | 93.0968 | 93.2055 | 93.0698
2022-09-08 03:56 | 6:06 | 17.8739 | 18.2923 | 21.0477 | 34.852 | 34.2639 | 33.8402 | 34.5816 | 35.414 | 36.5291 | 37.3068 | 36.904 | 38.0083 | 34.3518 | 34.3325 | 34.1267 | 35.0268 | 35.0463 | 35.4711 | 36.2185 | 36.5466 | 21.4183 | 17.5662 | 92.9928 | 33.3368 | 32.9754 | 35.0168 | 33.2822 | 32.9985 | 33.3796 | 34.6862 | 34.2742 | 34.0473 | 37.2014 | 36.2773 | 33.3573 | 34.3971 | 36.268 | 36.4938 | 37.368 | 36.2702 | 33.2852 | 32.561 | 34.3807 | 34.8805 | 33.0017 | 34.2937 | 34.2968 | 34.3519 | 34.4329 | 34.4199 | 34.2996 | 33.9542 | 34.4273 | 35.9399 | 35.111 | 36.3384 | 36.309 | 33.4256 | 92.9222 | 93.0551 | 92.8857
2022-09-08 03:57 | 6:07 | 17.9691 | 18.3194 | 21.0489 | 34.6932 | 34.2508 | 33.8401 | 34.6111 | 35.4115 | 36.5265 | 37.314 | 36.901 | 37.9903 | 34.3473 | 34.3365 | 34.1393 | 35.0511 | 35.0539 | 35.4628 | 36.1907 | 36.5388 | 21.4046 | 17.5766 | 92.9849 | 33.321 | 32.9795 | 35.003 | 33.2735 | 32.9922 | 33.371 | 34.6909 | 34.2812 | 34.0537 | 37.1994 | 36.2655 | 33.3549 | 34.3752 | 36.2514 | 36.4956 | 37.3539 | 36.2636 | 33.2616 | 32.5412 | 34.3736 | 34.8971 | 32.9907 | 34.3034 | 34.3193 | 34.3494 | 34.4172 | 34.4316 | 34.3058 | 33.942 | 34.4329 | 35.9239 | 35.1086 | 36.3386 | 36.3079 | 33.4279 | 92.8556 | 92.9808 | 92.8863
2022-09-08 03:57 | 6:07 | 17.7805 | 18.2414 | 21.0169 | 34.8951 | 34.2626 | 33.8342 | 34.6183 | 35.4368 | 36.5216 | 37.298 | 36.9263 | 37.9924 | 34.3631 | 34.3537 | 34.1345 | 35.0337 | 35.0473 | 35.4459 | 36.1906 | 36.5499 | 21.3886 | 17.551 | 92.9124 | 33.3814 | 32.9757 | 35.022 | 33.2663 | 33.0003 | 33.3837 | 34.6958 | 34.2684 | 34.0581 | 37.1907 | 36.259 | 33.3943 | 34.3778 | 36.2773 | 36.5055 | 37.3663 | 36.2698 | 33.2561 | 32.5417 | 34.351 | 34.8891 | 32.9681 | 34.3116 | 34.2921 | 34.3616 | 34.4199 | 34.4469 | 34.2985 | 33.9615 | 34.4172 | 35.9197 | 35.1129 | 36.3364 | 36.3075 | 33.4406 | 92.7157 | 92.8583 | 92.7593
2022-09-08 03:57 | 6:07 | 17.7416 | 18.1608 | 20.9349 | 34.7838 | 34.2634 | 33.86 | 34.6159 | 35.4227 | 36.5128 | 37.3075 | 36.9057 | 38.0228 | 34.3588 | 34.3381 | 34.1223 | 35.0398 | 35.0534 | 35.4751 | 36.2135 | 36.543 | 21.36 | 17.4808 | 92.8222 | 33.3942 | 32.9837 | 35.0074 | 33.2656 | 32.9796 | 33.3765 | 34.6838 | 34.2848 | 34.044 | 37.1962 | 36.2613 | 33.3791 | 34.3766 | 36.2655 | 36.5076 | 37.3665 | 36.268 | 33.2512 | 32.5387 | 34.3555 | 34.9026 | 32.9479 | 34.3085 | 34.2805 | 34.3484 | 34.4001 | 34.4431 | 34.3169 | 33.9565 | 34.4199 | 35.9353 | 35.1171 | 36.3552 | 36.3076 | 33.4461 | 92.6374 | 92.77 | 92.8064
2022-09-08 03:57 | 6:07 | 17.7605 | 18.1667 | 20.9397 | 34.7651 | 34.2439 | 33.8588 | 34.6192 | 35.4178 | 36.5315 | 37.3139 | 36.9119 | 37.999 | 34.3765 | 34.3456 | 34.1259 | 35.0363 | 35.0573 | 35.4545 | 36.2012 | 36.5313 | 21.3395 | 17.421 | 92.7232 | 33.4577 | 32.9761 | 35.0173 | 33.2852 | 32.9853 | 33.3573 | 34.696 | 34.2794 | 34.0588 | 37.2 | 36.2593 | 33.3719 | 34.3863 | 36.259 | 36.5155 | 37.3528 | 36.2514 | 33.2601 | 32.5447 | 34.3516 | 34.8929 | 32.9869 | 34.3157 | 34.2961 | 34.3568 | 34.4151 | 34.4472 | 34.2959 | 33.9403 | 34.4001 | 35.9345 | 35.098 | 36.3514 | 36.3214 | 33.431 | 92.5329 | 92.6968 | 92.6557
2022-09-08 03:57 | 6:07 | 17.7302 | 18.095 | 20.8999 | 34.6581 | 34.2523 | 33.8364 | 34.6131 | 35.4148 | 36.5265 | 37.3013 | 36.9181 | 37.9828 | 34.3375 | 34.351 | 34.1363 | 35.0346 | 35.0322 | 35.464 | 36.1858 | 36.5382 | 21.3101 | 17.4267 | 92.6491 | 33.3134 | 32.9751 | 35.013 | 33.2616 | 32.9822 | 33.3549 | 34.6933 | 34.2834 | 34.0604 | 37.2026 | 36.2638 | 33.3754 | 34.3919 | 36.2613 | 36.4912 | 37.366 | 36.2773 | 33.2636 | 32.5421 | 34.337 | 34.8863 | 32.9544 | 34.3132 | 34.2845 | 34.3324 | 34.4106 | 34.4273 | 34.2938 | 33.9549 | 34.4151 | 35.9233 | 35.1033 | 36.3494 | 36.3221 | 33.4313 | 92.4273 | 92.5382 | 92.5763
2022-09-08 03:57 | 6:07 | 17.6562 | 18.0676 | 20.8722 | 34.6966 | 34.2518 | 33.8334 | 34.5928 | 35.4197 | 36.5407 | 37.2759 | 36.9311 | 38.0018 | 34.3617 | 34.3601 | 34.1245 | 35.0307 | 35.0411 | 35.4657 | 36.209 | 36.5352 | 21.3099 | 17.4261 | 92.5995 | 33.4294 | 32.9846 | 35.0156 | 33.2561 | 32.9976 | 33.3943 | 34.6968 | 34.3043 | 34.0678 | 37.2114 | 36.2555 | 33.3773 | 34.3746 | 36.2593 | 36.5029 | 37.3739 | 36.2655 | 33.2587 | 32.5266 | 34.3512 | 34.8722 | 32.9426 | 34.311 | 34.2917 | 34.3554 | 34.4168 | 34.4391 | 34.3121 | 33.9475 | 34.4106 | 35.9463 | 35.1172 | 36.3299 | 36.324 | 33.4367 | 92.3264 | 92.408 | 92.507
2022-09-08 03:58 | 6:07 | 17.6093 | 18.0064 | 20.8179 | 34.6623 | 34.2437 | 33.8452 | 34.6063 | 35.4247 | 36.543 | 37.2982 | 36.9057 | 38.0228 | 34.362 | 34.3682 | 34.1246 | 35.0563 | 35.0594 | 35.4808 | 36.2065 | 36.5488 | 21.2857 | 17.3749 | 92.4823 | 33.2606 | 32.9666 | 35.0219 | 33.2512 | 32.9926 | 33.3791 | 34.7002 | 34.285 | 34.0532 | 37.1978 | 36.239 | 33.3709 | 34.3911 | 36.2638 | 36.5064 | 37.3692 | 36.259 | 33.2328 | 32.5275 | 34.3427 | 34.8789 | 32.9446 | 34.3103 | 34.275 | 34.3674 | 34.4091 | 34.4219 | 34.3078 | 33.9463 | 34.4168 | 35.9437 | 35.1236 | 36.347 | 36.3151 | 33.444 | 92.1597 | 92.293 | 92.3124
2022-09-08 03:58 | 6:08 | 17.6442 | 18.0115 | 20.7651 | 34.7825 | 34.2599 | 33.851 | 34.6073 | 35.4218 | 36.5431 | 37.3077 | 36.908 | 38.0139 | 34.3398 | 34.3592 | 34.1281 | 35.0474 | 35.0539 | 35.4729 | 36.1917 | 36.558 | 21.2845 | 17.4166 | 92.4295 | 33.3685 | 32.9915 | 35.0144 | 33.2601 | 32.9952 | 33.3719 | 34.6967 | 34.2966 | 34.0536 | 37.2063 | 36.2409 | 33.3703 | 34.3985 | 36.2555 | 36.497 | 37.3698 | 36.2613 | 33.2473 | 32.5239 | 34.3466 | 34.88 | 32.9317 | 34.3166 | 34.2658 | 34.3575 | 34.4137 | 34.4269 | 34.3231 | 33.946 | 34.4091 | 35.9311 | 35.0997 | 36.3402 | 36.3228 | 33.4559 | 92.1172 | 92.2621 | 92.3611
2022-09-08 03:58 | 6:08 | 17.5627 | 17.949 | 20.6994 | 34.6739 | 34.2711 | 33.849 | 34.5947 | 35.4513 | 36.5261 | 37.2885 | 36.9019 | 38.023 | 34.3747 | 34.3334 | 34.1335 | 35.0425 | 35.0625 | 35.4662 | 36.1856 | 36.5614 | 21.2697 | 17.3311 | 92.6092 | 33.3897 | 32.9705 | 35.0202 | 33.2636 | 32.9888 | 33.3754 | 34.6935 | 34.2697 | 34.0558 | 37.1924 | 36.2534 | 33.3694 | 34.3804 | 36.239 | 36.5189 | 37.3843 | 36.2593 | 33.2448 | 32.5277 | 34.3326 | 34.8841 | 32.9209 | 34.3028 | 34.2686 | 34.353 | 34.3952 | 34.4476 | 34.3181 | 33.9369 | 34.4137 | 35.9482 | 35.118 | 36.3497 | 36.3075 | 33.4638 | 92.2856 | 92.3432 | 92.5796
2022-09-08 03:58 | 6:08 | 17.5103 | 17.9034 | 20.6611 | 34.6502 | 34.2577 | 33.8365 | 34.6046 | 35.4458 | 36.5298 | 37.316 | 36.9324 | 38.0048 | 34.3511 | 34.3646 | 34.1209 | 35.0509 | 35.0583 | 35.4604 | 36.1886 | 36.5461 | 21.2496 | 17.2772 | 92.6269 | 33.1606 | 32.9611 | 35.0134 | 33.2587 | 32.9946 | 33.3773 | 34.6864 | 34.2695 | 34.0499 | 37.1993 | 36.23 | 33.3661 | 34.384 | 36.2409 | 36.5132 | 37.353 | 36.2638 | 33.2394 | 32.5169 | 34.3385 | 34.8959 | 32.9193 | 34.3171 | 34.2785 | 34.3742 | 34.3969 | 34.449 | 34.3252 | 33.9375 | 34.3952 | 35.9457 | 35.12 | 36.3389 | 36.3032 | 33.4394 | 92.3652 | 92.4275 | 92.6457
2022-09-08 03:58 | 6:08 | 17.5126 | 17.9303 | 20.6365 | 34.6754 | 34.2525 | 33.8622 | 34.6125 | 35.4329 | 36.5355 | 37.2935 | 36.905 | 38.0054 | 34.3657 | 34.3543 | 34.1278 | 35.049 | 35.0492 | 35.4769 | 36.1871 | 36.5322 | 21.23 | 17.2709 | 92.6569 | 33.3712 | 32.9707 | 34.9928 | 33.2328 | 32.9868 | 33.3709 | 34.7114 | 34.2815 | 34.0467 | 37.1916 | 36.223 | 33.3634 | 34.398 | 36.2534 | 36.5081 | 37.3662 | 36.2555 | 33.2496 | 32.5196 | 34.3265 | 34.8678 | 32.9166 | 34.3077 | 34.2701 | 34.3594 | 34.3822 | 34.4414 | 34.3314 | 33.9579 | 34.3969 | 35.9254 | 35.1214 | 36.3517 | 36.3259 | 33.4291 | 92.4022 | 92.5011 | 92.553
2022-09-08 03:58 | 6:08 | 17.4842 | 17.8606 | 20.5963 | 34.5714 | 34.2627 | 33.8485 | 34.6007 | 35.4287 | 36.5261 | 37.3058 | 36.9143 | 38.004 | 34.3894 | 34.3653 | 34.1284 | 35.0296 | 35.0533 | 35.4503 | 36.1865 | 36.5536 | 21.1918 | 17.2455 | 92.6159 | 33.3017 | 32.9679 | 35.0094 | 33.2473 | 32.9714 | 33.3703 | 34.6787 | 34.2669 | 34.046 | 37.1984 | 36.2274 | 33.3429 | 34.3951 | 36.23 | 36.4971 | 37.3443 | 36.239 | 33.2276 | 32.486 | 34.328 | 34.8635 | 32.8937 | 34.3141 | 34.2543 | 34.3448 | 34.3891 | 34.4258 | 34.2991 | 33.9368 | 34.3822 | 35.9517 | 35.1025 | 36.3567 | 36.3124 | 33.4458 | 92.4081 | 92.5719 | 92.6022
2022-09-08 03:59 | 6:09 | 17.4326 | 17.8249 | 20.4942 | 34.6181 | 34.2715 | 33.8433 | 34.5923 | 35.4242 | 36.5383 | 37.2947 | 36.9157 | 37.9986 | 34.3594 | 34.3484 | 34.1102 | 35.0339 | 35.0585 | 35.476 | 36.1902 | 36.5478 | 21.1708 | 17.2138 | 92.7454 | 33.3741 | 32.9546 | 34.9881 | 33.2448 | 32.9726 | 33.3694 | 34.6718 | 34.2756 | 34.053 | 37.2028 | 36.2267 | 33.3721 | 34.3869 | 36.223 | 36.5016 | 37.3484 | 36.2409 | 33.2186 | 32.5262 | 34.3301 | 34.8457 | 32.8857 | 34.308 | 34.2664 | 34.3777 | 34.3849 | 34.4204 | 34.3191 | 33.9338 | 34.3891 | 35.9463 | 35.0939 | 36.3509 | 36.3018 | 33.4564 | 92.4906 | 92.6506 | 92.6806
2022-09-08 03:59 | 6:09 | 17.4917 | 17.8328 | 20.5019 | 34.6457 | 34.2733 | 33.8518 | 34.6 | 35.431 | 36.5278 | 37.3031 | 36.9093 | 38.0062 | 34.3858 | 34.3619 | 34.1306 | 35.0152 | 35.0387 | 35.4662 | 36.1962 | 36.5552 | 21.153 | 17.2426 | 92.7627 | 33.3282 | 32.9559 | 34.9898 | 33.2394 | 32.9873 | 33.3661 | 34.6813 | 34.275 | 34.0506 | 37.1947 | 36.2281 | 33.354 | 34.3652 | 36.2274 | 36.5087 | 37.344 | 36.2534 | 33.2275 | 32.4973 | 34.3256 | 34.8433 | 32.8836 | 34.3024 | 34.2804 | 34.367 | 34.3789 | 34.4527 | 34.3173 | 33.9356 | 34.3849 | 35.9318 | 35.103 | 36.3655 | 36.3251 | 33.4344 | 92.6018 | 92.7799 | 92.7031
2022-09-08 03:59 | 6:09 | 17.4048 | 17.8106 | 20.4837 | 34.5719 | 34.2696 | 33.8583 | 34.5816 | 35.4291 | 36.5436 | 37.3076 | 36.9012 | 38.0105 | 34.3832 | 34.3503 | 34.1319 | 35.0355 | 35.0438 | 35.4544 | 36.1858 | 36.5427 | 21.1314 | 17.2303 | 92.8501 | 33.2575 | 32.9557 | 34.9943 | 33.2496 | 32.9725 | 33.3634 | 34.664 | 34.2846 | 34.0531 | 37.196 | 36.2318 | 33.3629 | 34.3812 | 36.2267 | 36.4949 | 37.3411 | 36.23 | 33.2402 | 32.4849 | 34.316 | 34.8426 | 32.8609 | 34.3274 | 34.2507 | 34.3611 | 34.3824 | 34.4404 | 34.3165 | 33.9262 | 34.3789 | 35.9417 | 35.0951 | 36.3647 | 36.3243 | 33.426 | 92.7159 | 92.8731 | 92.7948
2022-09-08 03:59 | 6:09 | 17.3318 | 17.7056 | 20.379 | 34.37 | 34.2707 | 33.831 | 34.5868 | 35.4192 | 36.5397 | 37.2833 | 36.902 | 38.0073 | 34.4034 | 34.3664 | 34.119 | 35.0311 | 35.0445 | 35.4674 | 36.177 | 36.5499 | 21.0659 | 17.1393 | 92.8382 | 33.1239 | 32.9561 | 35.0077 | 33.2276 | 32.9558 | 33.3429 | 34.6753 | 34.2561 | 34.0421 | 37.1916 | 36.2086 | 33.3675 | 34.3537 | 36.2281 | 36.5093 | 37.3653 | 36.223 | 33.2243 | 32.4907 | 34.313 | 34.8484 | 32.8771 | 34.3311 | 34.2644 | 34.3637 | 34.3919 | 34.4387 | 34.3 | 33.9323 | 34.3824 | 35.929 | 35.1174 | 36.3471 | 36.2951 | 33.4395 | 92.7814 | 93.0017 | 92.7974
2022-09-08 03:59 | 6:09 | 17.3375 | 17.709 | 20.4309 | 34.4515 | 34.2944 | 33.8472 | 34.5748 | 35.4201 | 36.5295 | 37.2923 | 36.8854 | 37.9902 | 34.3836 | 34.3669 | 34.1237 | 35.0548 | 35.0279 | 35.4515 | 36.1696 | 36.5432 | 21.0547 | 17.1291 | 92.8778 | 33.0718 | 32.9423 | 34.9706 | 33.2186 | 32.9654 | 33.3721 | 34.6841 | 34.2608 | 34.0546 | 37.1865 | 36.2238 | 33.359 | 34.3603 | 36.2318 | 36.5087 | 37.3645 | 36.2274 | 33.2322 | 32.492 | 34.3262 | 34.8424 | 32.8673 | 34.3401 | 34.2642 | 34.3526 | 34.385 | 34.4295 | 34.325 | 33.9327 | 34.3919 | 35.9495 | 35.0881 | 36.3592 | 36.3235 | 33.4434 | 92.9178 | 93.1158 | 92.9411
2022-09-08 03:59 | 6:09 | 17.3466 | 17.7276 | 20.4268 | 34.5116 | 34.2814 | 33.8268 | 34.5778 | 35.4119 | 36.5244 | 37.2966 | 36.9101 | 37.9955 | 34.392 | 34.3692 | 34.1101 | 35.0364 | 35.0435 | 35.4516 | 36.1674 | 36.5381 | 21.0184 | 17.1228 | 92.9368 | 33.2025 | 32.9461 | 34.9932 | 33.2275 | 32.961 | 33.354 | 34.6893 | 34.2557 | 34.046 | 37.2087 | 36.2154 | 33.368 | 34.3856 | 36.2086 | 36.5196 | 37.347 | 36.2267 | 33.2177 | 32.4518 | 34.2996 | 34.8179 | 32.8591 | 34.3395 | 34.2582 | 34.3495 | 34.3715 | 34.4209 | 34.3387 | 33.9418 | 34.385 | 35.9305 | 35.1107 | 36.3647 | 36.3182 | 33.4344 | 92.9785 | 93.2351 | 92.9182
2022-09-08 04:00 | 6:09 | 17.3512 | 17.7082 | 20.4201 | 34.6257 | 34.296 | 33.8472 | 34.5816 | 35.4217 | 36.5322 | 37.309 | 36.9039 | 38.0099 | 34.3863 | 34.3773 | 34.1247 | 35.0172 | 35.0237 | 35.4453 | 36.1719 | 36.5315 | 21.0002 | 17.1242 | 93.0337 | 33.0582 | 32.9506 | 34.967 | 33.2402 | 32.9555 | 33.3629 | 34.6776 | 34.2597 | 34.0436 | 37.195 | 36.2042 | 33.3552 | 34.3707 | 36.2238 | 36.5021 | 37.3558 | 36.2281 | 33.219 | 32.4892 | 34.2912 | 34.8209 | 32.8479 | 34.3134 | 34.254 | 34.3526 | 34.3791 | 34.4295 | 34.3204 | 33.9172 | 34.3715 | 35.9251 | 35.0891 | 36.3488 | 36.3102 | 33.4316 | 93.1258 | 93.3491 | 93.0614
2022-09-08 04:00 | 6:10 | 17.3532 | 17.6893 | 20.3281 | 34.47 | 34.2778 | 33.8367 | 34.5934 | 35.4073 | 36.5332 | 37.2965 | 36.891 | 37.9877 | 34.3792 | 34.3742 | 34.1289 | 35.0115 | 35.0254 | 35.4326 | 36.1735 | 36.5456 | 20.9763 | 17.076 | 93.0538 | 33.226 | 32.9384 | 34.9977 | 33.2243 | 32.9526 | 33.3675 | 34.6705 | 34.271 | 34.032 | 37.1941 | 36.2179 | 33.3692 | 34.3623 | 36.2154 | 36.4967 | 37.34 | 36.2318 | 33.214 | 32.4452 | 34.2997 | 34.8136 | 32.838 | 34.3389 | 34.2614 | 34.3604 | 34.3557 | 34.4387 | 34.3322 | 33.9211 | 34.3791 | 35.9034 | 35.0844 | 36.3548 | 36.32 | 33.4247 | 93.2062 | 93.4487 | 93.0847
2022-09-08 04:00 | 6:10 | 17.2398 | 17.5528 | 20.3196 | 34.3748 | 34.2818 | 33.8357 | 34.5866 | 35.4111 | 36.5155 | 37.3028 | 36.9001 | 38.0086 | 34.3816 | 34.3805 | 34.1088 | 35.0191 | 35.0372 | 35.4357 | 36.1572 | 36.5389 | 20.9495 | 17.0508 | 93.1453 | 33.1748 | 32.9555 | 34.9615 | 33.2322 | 32.9809 | 33.359 | 34.6819 | 34.2724 | 34.0445 | 37.1811 | 36.2256 | 33.3464 | 34.3619 | 36.2042 | 36.5121 | 37.3569 | 36.2086 | 33.2127 | 32.4685 | 34.2763 | 34.8366 | 32.8357 | 34.3305 | 34.2462 | 34.3449 | 34.3709 | 34.4251 | 34.3381 | 33.9248 | 34.3557 | 35.9253 | 35.0903 | 36.3564 | 36.3196 | 33.4307 | 93.3238 | 93.5746 | 93.1727
2022-09-08 04:00 | 6:10 | 17.2053 | 17.5551 | 20.2448 | 34.4647 | 34.2649 | 33.8451 | 34.5809 | 35.4198 | 36.5145 | 37.2947 | 36.888 | 37.978 | 34.4022 | 34.3716 | 34.101 | 35.0334 | 35.0273 | 35.4376 | 36.1653 | 36.5401 | 20.9204 | 17.0167 | 93.3123 | 33.1136 | 32.9443 | 34.9581 | 33.2177 | 32.9608 | 33.368 | 34.6849 | 34.266 | 34.0333 | 37.1748 | 36.2216 | 33.3602 | 34.3788 | 36.2179 | 36.5033 | 37.3629 | 36.2238 | 33.2149 | 32.4502 | 34.2662 | 34.8095 | 32.8468 | 34.3484 | 34.2474 | 34.3454 | 34.3693 | 34.4089 | 34.3467 | 33.9176 | 34.3709 | 35.9403 | 35.0831 | 36.3493 | 36.3203 | 33.4371 | 93.4581 | 93.7299 | 93.3634
2022-09-08 04:00 | 6:10 | 17.2189 | 17.5175 | 20.2932 | 34.4877 | 34.2739 | 33.8351 | 34.5811 | 35.4165 | 36.5115 | 37.3075 | 36.8827 | 37.979 | 34.418 | 34.3826 | 34.1088 | 35.0212 | 35.0351 | 35.4457 | 36.178 | 36.5612 | 20.892 | 17.0075 | 93.3565 | 33.1255 | 32.9606 | 34.9596 | 33.219 | 32.9526 | 33.3552 | 34.6872 | 34.2677 | 34.0333 | 37.1924 | 36.1946 | 33.3642 | 34.3704 | 36.2256 | 36.5173 | 37.3593 | 36.2154 | 33.2059 | 32.45 | 34.2807 | 34.8194 | 32.8223 | 34.3515 | 34.2508 | 34.3481 | 34.371 | 34.423 | 34.3486 | 33.9105 | 34.3693 | 35.9343 | 35.0869 | 36.3374 | 36.3046 | 33.4176 | 93.5649 | 93.8675 | 93.3795
2022-09-08 04:00 | 6:10 | 17.2251 | 17.5314 | 20.2395 | 34.4068 | 34.2853 | 33.8362 | 34.5746 | 35.4118 | 36.5127 | 37.3064 | 36.9102 | 37.9922 | 34.3974 | 34.3757 | 34.0841 | 35.0091 | 35.0181 | 35.4455 | 36.1609 | 36.5371 | 20.8798 | 17.0036 | 93.4381 | 33.1587 | 32.9582 | 34.9716 | 33.214 | 32.9614 | 33.3692 | 34.6835 | 34.2436 | 34.036 | 37.1706 | 36.2269 | 33.3363 | 34.3592 | 36.2216 | 36.5005 | 37.3559 | 36.2042 | 33.2052 | 32.4485 | 34.2698 | 34.8194 | 32.8167 | 34.3491 | 34.2349 | 34.37 | 34.3707 | 34.4268 | 34.3317 | 33.8977 | 34.371 | 35.9223 | 35.0918 | 36.3405 | 36.3059 | 33.4307 | 93.7319 | 94.0431 | 93.5087
2022-09-08 04:01 | 6:11 | 17.1816 | 17.5362 | 20.2303 | 34.3894 | 34.2891 | 33.8344 | 34.5827 | 35.4131 | 36.5269 | 37.2932 | 36.9045 | 37.9935 | 34.3967 | 34.3972 | 34.0933 | 35.004 | 35.001 | 35.4257 | 36.1658 | 36.5418 | 20.8462 | 16.9938 | 93.5165 | 33.163 | 32.9351 | 34.9849 | 33.2127 | 32.9625 | 33.3464 | 34.6794 | 34.2836 | 34.0335 | 37.1951 | 36.2266 | 33.3374 | 34.3593 | 36.1946 | 36.5051 | 37.3574 | 36.2179 | 33.2037 | 32.4452 | 34.2719 | 34.7903 | 32.8107 | 34.3442 | 34.2412 | 34.3598 | 34.3559 | 34.4294 | 34.3325 | 33.9149 | 34.3707 | 35.922 | 35.0921 | 36.3568 | 36.3019 | 33.4257 | 93.8916 | 94.1843 | 93.5868
2022-09-08 04:01 | 6:11 | 17.1876 | 17.5295 | 20.2467 | 34.4774 | 34.2936 | 33.849 | 34.5742 | 35.4362 | 36.5215 | 37.2937 | 36.9029 | 37.9786 | 34.3908 | 34.4101 | 34.0966 | 35.0227 | 35.0121 | 35.4437 | 36.176 | 36.5387 | 20.8492 | 16.9875 | 93.6545 | 33.1602 | 32.9388 | 34.954 | 33.2149 | 32.9569 | 33.3602 | 34.6669 | 34.2614 | 34.04 | 37.1872 | 36.2095 | 33.3355 | 34.3662 | 36.2269 | 36.4907 | 37.3324 | 36.2256 | 33.1863 | 32.4451 | 34.253 | 34.7881 | 32.8056 | 34.3612 | 34.2477 | 34.3728 | 34.3669 | 34.4154 | 34.3365 | 33.9074 | 34.3559 | 35.9149 | 35.0887 | 36.3671 | 36.3326 | 33.4134 | 94.0446 | 94.3507 | 93.7187
2022-09-08 04:01 | 6:11 | 17.1965 | 17.5026 | 20.2098 | 34.3911 | 34.2927 | 33.8614 | 34.5781 | 35.4097 | 36.5356 | 37.2885 | 36.8925 | 37.9924 | 34.4089 | 34.3942 | 34.1113 | 35.0113 | 35.0109 | 35.454 | 36.1668 | 36.5373 | 20.8266 | 16.987 | 93.7083 | 33.1432 | 32.9377 | 34.9658 | 33.2059 | 32.9527 | 33.3642 | 34.6731 | 34.2631 | 34.0337 | 37.1837 | 36.2028 | 33.3689 | 34.3853 | 36.2266 | 36.5027 | 37.3308 | 36.2216 | 33.2107 | 32.4354 | 34.2551 | 34.787 | 32.8084 | 34.356 | 34.249 | 34.3541 | 34.3586 | 34.4115 | 34.3537 | 33.9055 | 34.3669 | 35.9531 | 35.0832 | 36.3314 | 36.3299 | 33.4264 | 94.2016 | 94.4852 | 93.8132
2022-09-08 04:01 | 6:11 | 17.1353 | 17.4703 | 20.2141 | 34.3606 | 34.2907 | 33.8269 | 34.5771 | 35.4164 | 36.5275 | 37.3126 | 36.8858 | 37.9767 | 34.4226 | 34.3994 | 34.1122 | 35.0077 | 35.0134 | 35.4297 | 36.161 | 36.5362 | 20.8253 | 16.9515 | 93.7728 | 33.1383 | 32.9425 | 34.9612 | 33.2052 | 32.9519 | 33.3363 | 34.686 | 34.2599 | 34.031 | 37.1611 | 36.1938 | 33.3462 | 34.365 | 36.2095 | 36.4981 | 37.3467 | 36.1946 | 33.1942 | 32.4366 | 34.2634 | 34.8005 | 32.7995 | 34.3552 | 34.252 | 34.3684 | 34.3725 | 34.4068 | 34.3381 | 33.8991 | 34.3586 | 35.9432 | 35.0874 | 36.3607 | 36.3186 | 33.4005 | 94.377 | 94.6318 | 93.8329
2022-09-08 04:01 | 6:11 | 17.1335 | 17.4502 | 20.1512 | 34.4169 | 34.2996 | 33.8376 | 34.5755 | 35.4272 | 36.5142 | 37.301 | 36.8928 | 37.9848 | 34.4184 | 34.4098 | 34.1058 | 35.0016 | 35.0106 | 35.4284 | 36.1523 | 36.5441 | 20.8054 | 16.944 | 93.9654 | 33.1344 | 32.935 | 34.9624 | 33.2037 | 32.9555 | 33.3374 | 34.6773 | 34.237 | 34.0342 | 37.1974 | 36.2015 | 33.3297 | 34.3782 | 36.2028 | 36.5067 | 37.3409 | 36.2269 | 33.2019 | 32.4216 | 34.241 | 34.777 | 32.7789 | 34.3595 | 34.2547 | 34.3537 | 34.3397 | 34.425 | 34.3456 | 33.9127 | 34.3725 | 35.9336 | 35.0824 | 36.3712 | 36.2864 | 33.3973 | 94.4833 | 94.8381 | 94.0905
2022-09-08 04:01 | 6:11 | 17.0395 | 17.3959 | 20.1174 | 34.3538 | 34.3058 | 33.8202 | 34.5589 | 35.4243 | 36.533 | 37.2846 | 36.8839 | 37.9915 | 34.4196 | 34.3983 | 34.1187 | 35.0099 | 35.011 | 35.4385 | 36.1563 | 36.5566 | 20.7847 | 16.9312 | 94.0523 | 33.0754 | 32.919 | 34.951 | 33.1863 | 32.96 | 33.3355 | 34.687 | 34.2384 | 34.0053 | 37.1628 | 36.2081 | 33.3386 | 34.3542 | 36.1938 | 36.491 | 37.3627 | 36.2266 | 33.1934 | 32.4196 | 34.2159 | 34.7777 | 32.7902 | 34.3552 | 34.252 | 34.3535 | 34.3448 | 34.4166 | 34.351 | 33.9078 | 34.3397 | 35.9241 | 35.0844 | 36.34 | 36.3004 | 33.3899 | 94.6768 | 95.0311 | 94.2011
2022-09-08 04:02 | 6:11 | 17.0818 | 17.4386 | 20.0572 | 34.4672 | 34.2985 | 33.8159 | 34.5637 | 35.4162 | 36.5217 | 37.3011 | 36.8913 | 37.9997 | 34.4232 | 34.4123 | 34.1125 | 35.0121 | 35.0153 | 35.4285 | 36.1446 | 36.5328 | 20.7668 | 16.9127 | 94.1731 | 33.0301 | 32.9478 | 34.9573 | 33.2107 | 32.9362 | 33.3689 | 34.6754 | 34.2475 | 34.0288 | 37.1794 | 36.201 | 33.3366 | 34.3635 | 36.2015 | 36.4946 | 37.3359 | 36.2095 | 33.1989 | 32.4037 | 34.242 | 34.7882 | 32.7831 | 34.3697 | 34.2461 | 34.3607 | 34.3559 | 34.4046 | 34.3601 | 33.9093 | 34.3448 | 35.9254 | 35.0828 | 36.3555 | 36.3091 | 33.3898 | 94.8114 | 95.1949 | 94.3364
2022-09-08 04:02 | 6:12 | 17.0556 | 17.4066 | 20.0769 | 34.297 | 34.3169 | 33.8157 | 34.5592 | 35.4203 | 36.5099 | 37.2943 | 36.9073 | 37.998 | 34.4102 | 34.4114 | 34.1028 | 35.0054 | 35.0002 | 35.4323 | 36.1563 | 36.5262 | 20.7627 | 16.8995 | 94.2528 | 32.9911 | 32.9213 | 34.9582 | 33.1942 | 32.9512 | 33.3462 | 34.6628 | 34.2495 | 34.0254 | 37.1641 | 36.2 | 33.3483 | 34.37 | 36.2081 | 36.4873 | 37.3328 | 36.2028 | 33.1968 | 32.3932 | 34.2407 | 34.7543 | 32.7556 | 34.3657 | 34.2366 | 34.36 | 34.3519 | 34.3969 | 34.3682 | 33.9014 | 34.3559 | 35.9272 | 35.0856 | 36.3674 | 36.2995 | 33.3941 | 94.9607 | 95.3523 | 94.3954
2022-09-08 04:02 | 6:12 | 17.014 | 17.3654 | 20.0441 | 34.3323 | 34.2959 | 33.8236 | 34.5612 | 35.4241 | 36.5296 | 37.3049 | 36.8958 | 37.9917 | 34.4409 | 34.4269 | 34.0945 | 35.0014 | 35.0023 | 35.4308 | 36.1524 | 36.5277 | 20.7382 | 16.8362 | 94.302 | 33.0945 | 32.9378 | 34.943 | 33.2019 | 32.9512 | 33.3297 | 34.6786 | 34.2331 | 34.0265 | 37.1698 | 36.2209 | 33.3327 | 34.3723 | 36.201 | 36.4876 | 37.3234 | 36.1938 | 33.1946 | 32.4016 | 34.2358 | 34.7474 | 32.7613 | 34.3775 | 34.2515 | 34.3436 | 34.3565 | 34.3927 | 34.3592 | 33.8837 | 34.3519 | 35.9139 | 35.0745 | 36.3573 | 36.3055 | 33.3977 | 95.0045 | 95.4941 | 94.3994
2022-09-08 04:02 | 6:12 | 17.0263 | 17.3862 | 20.0111 | 34.3616 | 34.2938 | 33.8233 | 34.5687 | 35.4143 | 36.5251 | 37.2791 | 36.9023 | 37.9936 | 34.4239 | 34.4099 | 34.1061 | 35.0051 | 34.997 | 35.4224 | 36.1298 | 36.536 | 20.7144 | 16.9078 | 94.4215 | 32.924 | 32.9181 | 34.9598 | 33.1934 | 32.9416 | 33.3386 | 34.6735 | 34.2468 | 34.0192 | 37.1684 | 36.2129 | 33.3411 | 34.3551 | 36.2 | 36.5104 | 37.3201 | 36.2015 | 33.1913 | 32.4081 | 34.2083 | 34.7546 | 32.7641 | 34.3693 | 34.2602 | 34.3616 | 34.338 | 34.3927 | 34.3334 | 33.8727 | 34.3565 | 35.9303 | 35.0897 | 36.3313 | 36.2972 | 33.3905 | 95.1343 | 95.6036 | 94.5449
2022-09-08 04:02 | 6:12 | 17.0823 | 17.4282 | 20.0411 | 34.322 | 34.3121 | 33.8295 | 34.555 | 35.3819 | 36.5107 | 37.2832 | 36.8921 | 37.9907 | 34.4106 | 34.4132 | 34.0837 | 34.9846 | 34.9867 | 35.4154 | 36.1429 | 36.5241 | 20.7151 | 16.8892 | 94.535 | 33.0418 | 32.9235 | 34.9425 | 33.1989 | 32.9449 | 33.3366 | 34.6988 | 34.2457 | 34.0108 | 37.1672 | 36.1984 | 33.3358 | 34.3635 | 36.2209 | 36.4723 | 37.3354 | 36.2081 | 33.1633 | 32.395 | 34.2071 | 34.7591 | 32.7494 | 34.3806 | 34.2486 | 34.3513 | 34.3476 | 34.3944 | 34.3646 | 33.8746 | 34.338 | 35.9266 | 35.0862 | 36.3496 | 36.3044 | 33.3892 | 95.1552 | 95.6407 | 94.6266
2022-09-08 04:02 | 6:12 | 17.1409 | 17.4401 | 20.0973 | 34.2929 | 34.3078 | 33.8084 | 34.5639 | 35.4268 | 36.5141 | 37.2957 | 36.869 | 38.0092 | 34.4389 | 34.4238 | 34.0864 | 34.9894 | 34.9966 | 35.4274 | 36.1291 | 36.5006 | 20.7234 | 16.8945 | 94.5093 | 33.0703 | 32.9077 | 34.9224 | 33.1968 | 32.9492 | 33.3483 | 34.6596 | 34.2428 | 34.0217 | 37.1509 | 36.1885 | 33.3252 | 34.3638 | 36.2129 | 36.4801 | 37.3261 | 36.201 | 33.1612 | 32.3939 | 34.1944 | 34.7292 | 32.7476 | 34.3865 | 34.2589 | 34.3606 | 34.3403 | 34.4015 | 34.3543 | 33.9006 | 34.3476 | 35.9105 | 35.0718 | 36.3558 | 36.3076 | 33.3977 | 95.1914 | 95.7477 | 94.5664
2022-09-08 04:03 | 6:13 | 16.9627 | 17.3209 | 19.9887 | 34.3005 | 34.3231 | 33.823 | 34.565 | 35.413 | 36.5112 | 37.2714 | 36.8867 | 37.9915 | 34.4553 | 34.4121 | 34.0767 | 34.9857 | 34.9761 | 35.4117 | 36.1298 | 36.5215 | 20.7176 | 16.8268 | 94.4767 | 33.0107 | 32.9043 | 34.9381 | 33.1946 | 32.9335 | 33.3327 | 34.6613 | 34.2411 | 34.0232 | 37.1564 | 36.1972 | 33.3297 | 34.349 | 36.1984 | 36.4911 | 37.3313 | 36.2 | 33.1673 | 32.3786 | 34.2002 | 34.7258 | 32.7374 | 34.3695 | 34.2389 | 34.3507 | 34.3401 | 34.3947 | 34.3653 | 33.8766 | 34.3403 | 35.9217 | 35.0688 | 36.3454 | 36.3081 | 33.3827 | 95.1217 | 95.6156 | 94.5557
2022-09-08 04:03 | 6:13 | 16.9709 | 17.3005 | 19.9112 | 34.3205 | 34.3181 | 33.8169 | 34.5531 | 35.4066 | 36.5091 | 37.284 | 36.9131 | 37.9791 | 34.423 | 34.4179 | 34.0791 | 35.0062 | 34.982 | 35.4256 | 36.1333 | 36.5126 | 20.6914 | 16.801 | 94.2865 | 32.9453 | 32.906 | 34.9533 | 33.1913 | 32.9415 | 33.3411 | 34.6476 | 34.2529 | 34.0092 | 37.1491 | 36.1865 | 33.3198 | 34.3543 | 36.1885 | 36.503 | 37.3061 | 36.2209 | 33.1698 | 32.3878 | 34.196 | 34.7167 | 32.7207 | 34.3931 | 34.229 | 34.36 | 34.3429 | 34.4125 | 34.3484 | 33.892 | 34.3401 | 35.8973 | 35.0878 | 36.3451 | 36.2906 | 33.3615 | 94.9625 | 95.4012 | 94.3959
2022-09-08 04:03 | 6:13 | 17.0133 | 17.28 | 19.9551 | 34.348 | 34.3252 | 33.8144 | 34.5641 | 35.3872 | 36.5253 | 37.2632 | 36.8715 | 37.9801 | 34.4346 | 34.4172 | 34.089 | 34.9711 | 34.9774 | 35.4074 | 36.1348 | 36.5053 | 20.6674 | 16.7906 | 94.1766 | 32.9322 | 32.8904 | 34.9352 | 33.1633 | 32.9456 | 33.3358 | 34.6736 | 34.2501 | 34.0133 | 37.1433 | 36.199 | 33.3083 | 34.3557 | 36.1972 | 36.4845 | 37.3006 | 36.2129 | 33.1901 | 32.3688 | 34.203 | 34.7254 | 32.737 | 34.3943 | 34.2635 | 34.357 | 34.3268 | 34.4137 | 34.3619 | 33.8799 | 34.3429 | 35.8979 | 35.0733 | 36.3611 | 36.3183 | 33.3544 | 94.7116 | 95.0984 | 94.2398
2022-09-08 04:03 | 6:13 | 16.9505 | 17.3052 | 19.9806 | 34.3563 | 34.3314 | 33.8088 | 34.5576 | 35.3985 | 36.5065 | 37.2721 | 36.8993 | 37.9937 | 34.4469 | 34.4247 | 34.062 | 34.9794 | 34.9847 | 35.4086 | 36.1228 | 36.4964 | 20.6812 | 16.7399 | 94.0542 | 33.0249 | 32.89 | 34.9323 | 33.1612 | 32.9432 | 33.3252 | 34.674 | 34.2406 | 34.0164 | 37.1649 | 36.2071 | 33.3261 | 34.3432 | 36.1865 | 36.4817 | 37.2971 | 36.1984 | 33.1771 | 32.3573 | 34.1877 | 34.7232 | 32.7219 | 34.3859 | 34.2428 | 34.3604 | 34.308 | 34.3845 | 34.3503 | 33.8525 | 34.3268 | 35.9017 | 35.0936 | 36.3308 | 36.3125 | 33.3725 | 94.5681 | 94.8925 | 94.1256
2022-09-08 04:03 | 6:13 | 16.988 | 17.3177 | 19.9148 | 34.2831 | 34.2991 | 33.8207 | 34.5671 | 35.4005 | 36.4961 | 37.2549 | 36.8684 | 37.9932 | 34.4279 | 34.426 | 34.0624 | 34.9652 | 34.9627 | 35.4216 | 36.1307 | 36.4983 | 20.6875 | 16.742 | 93.927 | 32.9807 | 32.8852 | 34.9138 | 33.1673 | 32.9317 | 33.3297 | 34.6489 | 34.2496 | 34.011 | 37.1618 | 36.1838 | 33.3247 | 34.359 | 36.199 | 36.4871 | 37.2953 | 36.1885 | 33.1933 | 32.3638 | 34.1694 | 34.6954 | 32.7186 | 34.3905 | 34.2258 | 34.3585 | 34.3268 | 34.4024 | 34.3664 | 33.8528 | 34.308 | 35.9031 | 35.0861 | 36.3386 | 36.2764 | 33.3646 | 94.3893 | 94.7249 | 93.9295
2022-09-08 04:03 | 6:13 | 16.8999 | 17.2617 | 19.9137 | 34.2664 | 34.3191 | 33.8237 | 34.5574 | 35.4005 | 36.492 | 37.2655 | 36.8823 | 37.9948 | 34.4279 | 34.4326 | 34.0615 | 34.9817 | 34.9784 | 35.397 | 36.1367 | 36.4868 | 20.6996 | 16.7155 | 93.8993 | 33.0107 | 32.885 | 34.9476 | 33.1698 | 32.9338 | 33.3198 | 34.6631 | 34.2523 | 34.0127 | 37.1462 | 36.1957 | 33.3196 | 34.3546 | 36.2071 | 36.4493 | 37.2818 | 36.1972 | 33.1691 | 32.3338 | 34.1747 | 34.6929 | 32.7092 | 34.4121 | 34.2403 | 34.3602 | 34.3219 | 34.391 | 34.3669 | 33.8722 | 34.3268 | 35.8968 | 35.0767 | 36.3461 | 36.3033 | 33.3555 | 94.314 | 94.6042 | 93.9478
2022-09-08 04:04 | 6:14 | 16.9243 | 17.2646 | 19.8862 | 34.2698 | 34.3173 | 33.8168 | 34.5489 | 35.4021 | 36.494 | 37.2694 | 36.9066 | 37.9823 | 34.4199 | 34.4374 | 34.0651 | 34.9742 | 34.9753 | 35.3917 | 36.1345 | 36.4878 | 20.7402 | 16.7153 | 93.8227 | 32.9968 | 32.8852 | 34.9422 | 33.1901 | 32.9175 | 33.3083 | 34.6371 | 34.2348 | 34.0109 | 37.1503 | 36.1949 | 33.3363 | 34.3584 | 36.1838 | 36.47 | 37.2998 | 36.1865 | 33.1594 | 32.3688 | 34.1609 | 34.69 | 32.7127 | 34.3987 | 34.2407 | 34.3558 | 34.3088 | 34.3988 | 34.3692 | 33.8715 | 34.3219 | 35.9001 | 35.0678 | 36.3511 | 36.2938 | 33.3423 | 94.1828 | 94.4873 | 93.8631
2022-09-08 04:04 | 6:14 | 16.9488 | 17.2812 | 19.8486 | 34.2485 | 34.3165 | 33.8243 | 34.5515 | 35.3973 | 36.5006 | 37.2535 | 36.8933 | 37.9888 | 34.4316 | 34.443 | 34.058 | 34.9778 | 34.9741 | 35.4131 | 36.1099 | 36.4833 | 20.7521 | 16.7117 | 93.8884 | 32.9682 | 32.8769 | 34.925 | 33.1771 | 32.9165 | 33.3261 | 34.6501 | 34.2423 | 33.9913 | 37.1628 | 36.1936 | 33.3149 | 34.3409 | 36.1957 | 36.4699 | 37.2756 | 36.199 | 33.1846 | 32.3679 | 34.1692 | 34.7003 | 32.6942 | 34.4099 | 34.2518 | 34.369 | 34.3074 | 34.4069 | 34.3773 | 33.8585 | 34.3088 | 35.899 | 35.0886 | 36.3611 | 36.2995 | 33.3475 | 94.0937 | 94.368 | 93.813
2022-09-08 04:04 | 6:14 | 16.9435 | 17.2126 | 19.8835 | 34.163 | 34.3 | 33.8116 | 34.5576 | 35.3808 | 36.4778 | 37.2595 | 36.9087 | 37.9782 | 34.4469 | 34.4445 | 34.0816 | 34.9794 | 34.949 | 35.4006 | 36.1065 | 36.4881 | 20.7689 | 16.6909 | 93.8103 | 33.1491 | 32.894 | 34.9314 | 33.1933 | 32.9178 | 33.3247 | 34.6424 | 34.2465 | 34.0021 | 37.1483 | 36.1874 | 33.3066 | 34.344 | 36.1949 | 36.469 | 37.3133 | 36.2071 | 33.1719 | 32.3464 | 34.1486 | 34.6754 | 32.7036 | 34.4176 | 34.2593 | 34.3595 | 34.3091 | 34.3873 | 34.3742 | 33.8565 | 34.3074 | 35.8985 | 35.0684 | 36.3497 | 36.2933 | 33.3441 | 94.0409 | 94.2598 | 93.7898
2022-09-08 04:04 | 6:14 | 16.8967 | 17.2319 | 19.8456 | 34.3096 | 34.325 | 33.8178 | 34.56 | 35.3927 | 36.4825 | 37.2632 | 36.8949 | 37.9862 | 34.4431 | 34.4303 | 34.0636 | 34.9657 | 34.973 | 35.4013 | 36.1348 | 36.4932 | 20.7688 | 16.7205 | 93.8055 | 33.0924 | 32.8849 | 34.9421 | 33.1691 | 32.918 | 33.3196 | 34.6571 | 34.2358 | 34.0241 | 37.1471 | 36.1962 | 33.3115 | 34.3704 | 36.1936 | 36.4695 | 37.3002 | 36.1838 | 33.1648 | 32.3346 | 34.168 | 34.676 | 32.693 | 34.4144 | 34.2651 | 34.3511 | 34.2994 | 34.3816 | 34.3805 | 33.8811 | 34.3091 | 35.8856 | 35.0707 | 36.3528 | 36.2902 | 33.3431 | 94.0247 | 94.2411 | 93.7811
2022-09-08 04:04 | 6:14 | 16.9228 | 17.2312 | 19.8774 | 34.2069 | 34.3387 | 33.8366 | 34.5582 | 35.4073 | 36.4988 | 37.2599 | 36.8799 | 37.986 | 34.4472 | 34.4451 | 34.0711 | 34.9824 | 34.9713 | 35.4047 | 36.1101 | 36.4819 | 20.8084 | 16.6889 | 93.6742 | 32.9787 | 32.8734 | 34.9175 | 33.1594 | 32.9208 | 33.3363 | 34.6414 | 34.2518 | 33.9992 | 37.1539 | 36.183 | 33.3213 | 34.3548 | 36.1874 | 36.4626 | 37.2917 | 36.1957 | 33.178 | 32.3052 | 34.1487 | 34.6822 | 32.7036 | 34.4039 | 34.2621 | 34.3678 | 34.3144 | 34.398 | 34.3716 | 33.8495 | 34.2994 | 35.8885 | 35.0615 | 36.3441 | 36.2975 | 33.3096 | 93.9068 | 94.1592 | 93.6466
2022-09-08 04:04 | 6:14 | 16.8858 | 17.2104 | 19.8848 | 34.2672 | 34.3204 | 33.812 | 34.5535 | 35.399 | 36.4878 | 37.2463 | 36.9015 | 37.9969 | 34.4273 | 34.4376 | 34.0492 | 34.9845 | 34.9739 | 35.4043 | 36.1218 | 36.4813 | 20.7936 | 16.698 | 93.6253 | 32.9785 | 32.8903 | 34.9345 | 33.1846 | 32.9198 | 33.3149 | 34.6356 | 34.2426 | 34.0089 | 37.1529 | 36.2041 | 33.3083 | 34.3715 | 36.1962 | 36.4634 | 37.3008 | 36.1949 | 33.1663 | 32.3282 | 34.1618 | 34.6638 | 32.673 | 34.413 | 34.27 | 34.3485 | 34.299 | 34.3923 | 34.3826 | 33.8524 | 34.3144 | 35.8867 | 35.0806 | 36.3269 | 36.2927 | 33.3223 | 93.8519 | 94.118 | 93.6057
2022-09-08 04:05 | 6:14 | 16.9005 | 17.2311 | 19.7983 | 34.2709 | 34.3322 | 33.8198 | 34.5319 | 35.3899 | 36.4957 | 37.266 | 36.8874 | 37.9874 | 34.4391 | 34.4296 | 34.0565 | 34.9782 | 34.9615 | 35.4056 | 36.1227 | 36.4761 | 20.7912 | 16.6968 | 93.6301 | 33.0128 | 32.8906 | 34.9343 | 33.1719 | 32.92 | 33.3066 | 34.6353 | 34.2645 | 33.9936 | 37.1413 | 36.2021 | 33.315 | 34.3676 | 36.183 | 36.4547 | 37.2754 | 36.1936 | 33.1652 | 32.3355 | 34.1468 | 34.6722 | 32.6861 | 34.4088 | 34.2677 | 34.3715 | 34.2968 | 34.3978 | 34.3757 | 33.8437 | 34.299 | 35.8899 | 35.0774 | 36.3508 | 36.2848 | 33.3268 | 93.7904 | 94.017 | 93.6697
2022-09-08 04:05 | 6:15 | 16.8835 | 17.234 | 19.8153 | 34.1058 | 34.3381 | 33.818 | 34.5467 | 35.391 | 36.4838 | 37.2538 | 36.896 | 37.9831 | 34.4219 | 34.4382 | 34.0453 | 34.9665 | 34.9572 | 35.4119 | 36.0941 | 36.4689 | 20.7972 | 16.6969 | 93.5887 | 33.0019 | 32.8732 | 34.9312 | 33.1648 | 32.9194 | 33.3115 | 34.6197 | 34.2541 | 33.9918 | 37.1487 | 36.1814 | 33.3123 | 34.3559 | 36.2041 | 36.4576 | 37.2767 | 36.1874 | 33.1867 | 32.3343 | 34.1404 | 34.662 | 32.6848 | 34.4049 | 34.2653 | 34.3544 | 34.3193 | 34.3691 | 34.3972 | 33.8592 | 34.2968 | 35.8953 | 35.0765 | 36.3518 | 36.2798 | 33.3329 | 93.7087 | 93.8865 | 93.6193
2022-09-08 04:05 | 6:15 | 16.8838 | 17.1974 | 19.8235 | 34.1279 | 34.3467 | 33.816 | 34.5562 | 35.3851 | 36.4966 | 37.2471 | 36.9128 | 37.9938 | 34.4269 | 34.4312 | 34.0345 | 34.9863 | 34.9646 | 35.4024 | 36.1028 | 36.4977 | 20.7767 | 16.6871 | 93.4827 | 33.0461 | 32.8831 | 34.9194 | 33.178 | 32.9271 | 33.3213 | 34.6427 | 34.2547 | 34.0161 | 37.1434 | 36.2025 | 33.312 | 34.3698 | 36.2021 | 36.4706 | 37.2793 | 36.1962 | 33.1592 | 32.3283 | 34.1464 | 34.676 | 32.6755 | 34.4066 | 34.2663 | 34.3497 | 34.2921 | 34.3905 | 34.4101 | 33.8469 | 34.3193 | 35.8993 | 35.0661 | 36.3452 | 36.3073 | 33.3144 | 93.6203 | 93.7423 | 93.5961
2022-09-08 04:05 | 6:15 | 16.8076 | 17.1386 | 19.7759 | 34.2361 | 34.3486 | 33.8287 | 34.5516 | 35.4005 | 36.4834 | 37.2472 | 36.9075 | 38.0019 | 34.4476 | 34.4579 | 34.0544 | 34.9896 | 34.9662 | 35.3998 | 36.1255 | 36.4936 | 20.7739 | 16.7151 | 93.4092 | 32.9731 | 32.8803 | 34.933 | 33.1663 | 32.9073 | 33.3083 | 34.6418 | 34.2517 | 34.0138 | 37.1524 | 36.1968 | 33.3203 | 34.3535 | 36.1814 | 36.4804 | 37.289 | 36.183 | 33.1604 | 32.3311 | 34.1389 | 34.6503 | 32.6692 | 34.4155 | 34.2742 | 34.3436 | 34.2805 | 34.3845 | 34.3942 | 33.8526 | 34.2921 | 35.8952 | 35.0911 | 36.3605 | 36.2972 | 33.3222 | 93.5605 | 93.6087 | 93.5418
2022-09-08 04:05 | 6:15 | 16.9009 | 17.1697 | 19.8032 | 34.2356 | 34.3317 | 33.8168 | 34.5601 | 35.4148 | 36.4796 | 37.2668 | 36.9247 | 38.0102 | 34.449 | 34.4456 | 34.031 | 35.0092 | 34.9464 | 35.4056 | 36.0773 | 36.4729 | 20.7609 | 16.6988 | 93.3968 | 33.0375 | 32.8658 | 34.9257 | 33.1652 | 32.906 | 33.315 | 34.6415 | 34.2534 | 34.0022 | 37.1562 | 36.1904 | 33.3184 | 34.3676 | 36.2025 | 36.489 | 37.2814 | 36.2041 | 33.1685 | 32.3268 | 34.1182 | 34.6604 | 32.6629 | 34.4052 | 34.2957 | 34.3677 | 34.2961 | 34.3658 | 34.3994 | 33.8281 | 34.2805 | 35.8913 | 35.0855 | 36.3522 | 36.293 | 33.3002 | 93.5196 | 93.5407 | 93.5748
2022-09-08 04:05 | 6:15 | 16.8541 | 17.1562 | 19.819 | 34.2095 | 34.3325 | 33.8198 | 34.5633 | 35.4106 | 36.479 | 37.2644 | 36.8936 | 37.9971 | 34.4414 | 34.4412 | 34.0656 | 34.9799 | 34.9678 | 35.4109 | 36.0966 | 36.4731 | 20.7542 | 16.6231 | 93.2499 | 32.7475 | 32.864 | 34.9222 | 33.1867 | 32.9025 | 33.3123 | 34.6612 | 34.265 | 34.0162 | 37.1428 | 36.1729 | 33.2943 | 34.3668 | 36.1968 | 36.4921 | 37.2826 | 36.2021 | 33.1703 | 32.2966 | 34.1448 | 34.6396 | 32.6739 | 34.4237 | 34.2737 | 34.3647 | 34.2845 | 34.3918 | 34.4098 | 33.8394 | 34.2961 | 35.8913 | 35.0753 | 36.3676 | 36.297 | 33.3082 | 93.463 | 93.4168 | 93.4725
2022-09-08 04:06 | 6:16 | 16.8056 | 17.1509 | 19.7472 | 34.2224 | 34.3365 | 33.8038 | 34.5539 | 35.392 | 36.4761 | 37.2649 | 36.9167 | 38.0097 | 34.4258 | 34.4437 | 34.0283 | 34.9786 | 34.9621 | 35.4031 | 36.0968 | 36.4669 | 20.7529 | 16.6577 | 93.1681 | 32.9572 | 32.8713 | 34.9222 | 33.1592 | 32.9168 | 33.312 | 34.6295 | 34.2674 | 34.014 | 37.1447 | 36.1889 | 33.3137 | 34.3525 | 36.1904 | 36.4479 | 37.2889 | 36.1814 | 33.1594 | 32.3134 | 34.1151 | 34.6579 | 32.6501 | 34.4104 | 34.2621 | 34.3769 | 34.2917 | 34.3617 | 34.3983 | 33.8453 | 34.2845 | 35.8845 | 35.076 | 36.345 | 36.273 | 33.3122 | 93.4497 | 93.2818 | 93.41
2022-09-08 04:06 | 6:16 | 16.8227 | 17.1924 | 19.7367 | 34.2501 | 34.3537 | 33.8207 | 34.5349 | 35.4028 | 36.4915 | 37.2521 | 36.9173 | 38.0041 | 34.4204 | 34.4477 | 34.0416 | 34.9669 | 34.9569 | 35.4058 | 36.1058 | 36.4841 | 20.7403 | 16.6467 | 93.1886 | 32.9574 | 32.8644 | 34.9449 | 33.1604 | 32.9064 | 33.3203 | 34.626 | 34.2632 | 34.0011 | 37.1447 | 36.1677 | 33.3075 | 34.3595 | 36.1729 | 36.4616 | 37.2851 | 36.2025 | 33.1527 | 32.3281 | 34.1184 | 34.6611 | 32.6487 | 34.4256 | 34.2724 | 34.3774 | 34.275 | 34.3536 | 34.4123 | 33.8619 | 34.2917 | 35.9057 | 35.0891 | 36.3673 | 36.2845 | 33.3177 | 93.2503 | 93.1925 | 93.3083
2022-09-08 04:06 | 6:16 | 16.8161 | 17.0997 | 19.7635 | 34.1726 | 34.3381 | 33.8275 | 34.549 | 35.3915 | 36.4685 | 37.2667 | 36.9112 | 38.0133 | 34.4527 | 34.4351 | 34.0358 | 34.9819 | 34.9502 | 35.3935 | 36.1052 | 36.4854 | 20.7276 | 16.6316 | 93.1346 | 32.8603 | 32.8696 | 34.9389 | 33.1685 | 32.9189 | 33.3184 | 34.6407 | 34.2666 | 34.0002 | 37.1366 | 36.1869 | 33.3108 | 34.3673 | 36.1889 | 36.4892 | 37.2881 | 36.1968 | 33.1598 | 32.3018 | 34.1259 | 34.6498 | 32.637 | 34.4147 | 34.27 | 34.3715 | 34.2658 | 34.3628 | 34.4114 | 33.8178 | 34.275 | 35.891 | 35.072 | 36.3602 | 36.2856 | 33.298 | 93.1301 | 93.096 | 93.2412
2022-09-08 04:06 | 6:16 | 16.8007 | 17.0676 | 19.6774 | 34.1127 | 34.3456 | 33.8055 | 34.5393 | 35.404 | 36.4695 | 37.2349 | 36.9197 | 38.0006 | 34.4404 | 34.4478 | 34.0377 | 34.9725 | 34.9424 | 35.3997 | 36.0877 | 36.4751 | 20.7183 | 16.6105 | 92.9695 | 32.7577 | 32.8685 | 34.9351 | 33.1703 | 32.9016 | 33.2943 | 34.6416 | 34.2679 | 34.0059 | 37.1594 | 36.1692 | 33.3122 | 34.3779 | 36.1677 | 36.489 | 37.2612 | 36.1904 | 33.169 | 32.3131 | 34.1078 | 34.6419 | 32.6429 | 34.4178 | 34.2821 | 34.3838 | 34.2686 | 34.3686 | 34.4269 | 33.8473 | 34.2658 | 35.8947 | 35.0782 | 36.3601 | 36.3012 | 33.3204 | 92.9763 | 92.9749 | 93.1326
2022-09-08 04:06 | 6:16 | 16.779 | 17.0663 | 19.6645 | 34.2397 | 34.351 | 33.8218 | 34.5338 | 35.4138 | 36.48 | 37.2566 | 36.9119 | 38.0194 | 34.4387 | 34.4459 | 34.0511 | 34.9791 | 34.9588 | 35.397 | 36.1099 | 36.4862 | 20.7133 | 16.5892 | 92.8675 | 32.9918 | 32.8634 | 34.9514 | 33.1594 | 32.9075 | 33.3137 | 34.6331 | 34.2773 | 34.0167 | 37.1482 | 36.1802 | 33.3031 | 34.3585 | 36.1869 | 36.4672 | 37.2754 | 36.1729 | 33.1744 | 32.2822 | 34.1257 | 34.649 | 32.6361 | 34.4085 | 34.2861 | 34.3832 | 34.2785 | 34.3774 | 34.4099 | 33.8216 | 34.2686 | 35.9115 | 35.0865 | 36.3356 | 36.2977 | 33.3042 | 92.8937 | 92.8745 | 93.0767
2022-09-08 04:06 | 6:16 | 16.7778 | 17.0561 | 19.7047 | 34.247 | 34.3601 | 33.8222 | 34.5452 | 35.4119 | 36.4733 | 37.2583 | 36.9121 | 38.0037 | 34.4295 | 34.4329 | 34.0479 | 34.9774 | 34.9616 | 35.4291 | 36.1059 | 36.4787 | 20.686 | 16.5981 | 92.8107 | 33.0609 | 32.8646 | 34.9148 | 33.1527 | 32.9212 | 33.3075 | 34.6453 | 34.2639 | 34.0086 | 37.1533 | 36.1748 | 33.306 | 34.3676 | 36.1692 | 36.4866 | 37.2588 | 36.1889 | 33.1522 | 32.3051 | 34.1061 | 34.6439 | 32.634 | 34.4113 | 34.2656 | 34.3645 | 34.2701 | 34.3532 | 34.4132 | 33.8303 | 34.2785 | 35.884 | 35.0432 | 36.3645 | 36.2841 | 33.3072 | 92.8152 | 92.7831 | 93.0315
2022-09-08 04:07 | 6:16 | 16.8293 | 17.1344 | 19.781 | 34.1931 | 34.3682 | 33.814 | 34.5429 | 35.4076 | 36.5119 | 37.247 | 36.921 | 37.9955 | 34.4209 | 34.4528 | 34.0324 | 34.9772 | 34.9526 | 35.4 | 36.1075 | 36.4917 | 20.663 | 16.6118 | 92.5734 | 32.9285 | 32.8532 | 34.9448 | 33.1598 | 32.9127 | 33.3108 | 34.6457 | 34.2685 | 34.012 | 37.1537 | 36.1808 | 33.3036 | 34.3766 | 36.1802 | 36.4677 | 37.2726 | 36.1677 | 33.1437 | 32.2937 | 34.1146 | 34.6461 | 32.6213 | 34.4305 | 34.2876 | 34.396 | 34.2543 | 34.3604 | 34.4238 | 33.8336 | 34.2701 | 35.8971 | 35.0734 | 36.3586 | 36.28 | 33.3101 | 92.7104 | 92.6865 | 92.9654
2022-09-08 04:07 | 6:17 | 16.7565 | 17.0696 | 19.7762 | 34.2508 | 34.3592 | 33.835 | 34.5466 | 35.3951 | 36.4892 | 37.2644 | 36.9279 | 38.0147 | 34.4295 | 34.4457 | 34.0519 | 34.9729 | 34.9455 | 35.4052 | 36.1088 | 36.4871 | 20.683 | 16.6215 | 92.6372 | 32.9139 | 32.8598 | 34.9346 | 33.169 | 32.8948 | 33.3122 | 34.634 | 34.2576 | 34.0158 | 37.1496 | 36.185 | 33.3215 | 34.3618 | 36.1748 | 36.477 | 37.2718 | 36.1869 | 33.1534 | 32.2792 | 34.1127 | 34.6454 | 32.6024 | 34.4197 | 34.2844 | 34.3882 | 34.2664 | 34.3499 | 34.4121 | 33.8289 | 34.2543 | 35.8959 | 35.0608 | 36.3665 | 36.3041 | 33.2969 | 92.5665 | 92.595 | 92.8478
2022-09-08 04:07 | 6:17 | 16.7362 | 17.0678 | 19.6899 | 34.2119 | 34.3334 | 33.8285 | 34.5384 | 35.4021 | 36.4762 | 37.2544 | 36.9216 | 38.0056 | 34.4387 | 34.4386 | 34.0333 | 34.9845 | 34.9462 | 35.3936 | 36.0992 | 36.5006 | 20.6796 | 16.5478 | 92.5861 | 32.8584 | 32.853 | 34.9432 | 33.1744 | 32.8956 | 33.3031 | 34.6264 | 34.2679 | 34.0177 | 37.1578 | 36.1745 | 33.3003 | 34.3652 | 36.1808 | 36.4648 | 37.2764 | 36.1692 | 33.1487 | 32.2716 | 34.1248 | 34.6541 | 32.6309 | 34.4433 | 34.2697 | 34.3826 | 34.2804 | 34.3373 | 34.4179 | 33.8389 | 34.2664 | 35.8888 | 35.0938 | 36.3536 | 36.2812 | 33.305 | 92.5057 | 92.4641 | 92.7663
2022-09-08 04:07 | 6:17 | 16.7048 | 16.9728 | 19.6482 | 34.1452 | 34.3646 | 33.8267 | 34.552 | 35.394 | 36.4864 | 37.2537 | 36.9292 | 38.0123 | 34.4251 | 34.455 | 34.062 | 34.9808 | 34.96 | 35.4177 | 36.0975 | 36.49 | 20.6419 | 16.5126 | 92.4825 | 32.812 | 32.8487 | 34.9233 | 33.1522 | 32.9014 | 33.306 | 34.6584 | 34.2713 | 34.0146 | 37.1594 | 36.171 | 33.2998 | 34.361 | 36.185 | 36.4781 | 37.2777 | 36.1802 | 33.1465 | 32.2871 | 34.0958 | 34.6493 | 32.6034 | 34.4169 | 34.2787 | 34.3866 | 34.2507 | 34.3479 | 34.4172 | 33.8319 | 34.2804 | 35.9027 | 35.0609 | 36.3669 | 36.2807 | 33.2993 | 92.3618 | 92.3226 | 92.7219
2022-09-08 04:07 | 6:17 | 16.6351 | 16.9709 | 19.6607 | 34.1769 | 34.3543 | 33.811 | 34.5388 | 35.3871 | 36.4763 | 37.2657 | 36.9266 | 38.0105 | 34.4089 | 34.4164 | 34.0606 | 34.9771 | 34.9427 | 35.4174 | 36.099 | 36.4843 | 20.6243 | 16.5214 | 92.4222 | 32.8901 | 32.8597 | 34.9124 | 33.1437 | 32.9103 | 33.3036 | 34.6387 | 34.2623 | 34.0167 | 37.147 | 36.1669 | 33.2965 | 34.3761 | 36.1745 | 36.4983 | 37.2798 | 36.1748 | 33.1342 | 32.2787 | 34.0901 | 34.651 | 32.5687 | 34.4257 | 34.2784 | 34.3785 | 34.2644 | 34.3418 | 34.4247 | 33.8036 | 34.2507 | 35.8968 | 35.0456 | 36.36 | 36.2963 | 33.302 | 92.2516 | 92.1626 | 92.6353
2022-09-08 04:07 | 6:17 | 16.683 | 16.9677 | 19.5932 | 34.0733 | 34.3653 | 33.791 | 34.5534 | 35.4125 | 36.4752 | 37.2656 | 36.9333 | 38.0162 | 34.423 | 34.4336 | 34.0349 | 34.9721 | 34.9549 | 35.4159 | 36.1157 | 36.5027 | 20.5954 | 16.4906 | 92.3902 | 32.9159 | 32.8552 | 34.9061 | 33.1534 | 32.9079 | 33.3215 | 34.632 | 34.2772 | 34.0164 | 37.1477 | 36.1938 | 33.3027 | 34.3634 | 36.171 | 36.4763 | 37.2643 | 36.1808 | 33.1328 | 32.2554 | 34.0983 | 34.6418 | 32.5983 | 34.4334 | 34.2751 | 34.3945 | 34.2642 | 34.3498 | 34.426 | 33.8314 | 34.2644 | 35.9039 | 35.0678 | 36.3504 | 36.2954 | 33.3345 | 92.1452 | 92.091 | 92.5945
2022-09-08 04:08 | 6:18 | 16.6614 | 16.9593 | 19.643 | 34.1089 | 34.3484 | 33.8188 | 34.5338 | 35.3844 | 36.4786 | 37.2599 | 36.932 | 38.0208 | 34.4268 | 34.4273 | 34.0256 | 34.9875 | 34.932 | 35.4034 | 36.0991 | 36.4951 | 20.6013 | 16.4617 | 92.1575 | 32.8229 | 32.8634 | 34.9092 | 33.1487 | 32.9021 | 33.3003 | 34.623 | 34.2721 | 34.0005 | 37.1365 | 36.1615 | 33.3049 | 34.3738 | 36.1669 | 36.4969 | 37.2621 | 36.185 | 33.1372 | 32.2739 | 34.0836 | 34.6397 | 32.5777 | 34.4252 | 34.2755 | 34.3847 | 34.2582 | 34.3176 | 34.4326 | 33.8408 | 34.2642 | 35.9067 | 35.0747 | 36.3546 | 36.2905 | 33.3101 | 91.942 | 91.9277 | 92.5139
2022-09-08 04:08 | 6:18 | 16.6219 | 16.9217 | 19.6137 | 34.098 | 34.3619 | 33.8361 | 34.5483 | 35.4067 | 36.4896 | 37.2568 | 36.936 | 38.0262 | 34.4294 | 34.4329 | 34.0434 | 34.9971 | 34.935 | 35.4092 | 36.0969 | 36.4958 | 20.6042 | 16.4637 | 92.0953 | 32.917 | 32.8515 | 34.9177 | 33.1465 | 32.923 | 33.2998 | 34.6443 | 34.258 | 34.0193 | 37.1627 | 36.1593 | 33.311 | 34.3752 | 36.1938 | 36.4876 | 37.2621 | 36.1745 | 33.138 | 32.2701 | 34.103 | 34.6213 | 32.5607 | 34.4299 | 34.2747 | 34.397 | 34.254 | 34.3354 | 34.4374 | 33.8131 | 34.2582 | 35.8932 | 35.0651 | 36.3507 | 36.29 | 33.3222 | 91.915 | 91.9322 | 92.4873
2022-09-08 04:08 | 6:18 | 16.6886 | 16.9465 | 19.5805 | 34.0405 | 34.3503 | 33.7952 | 34.5335 | 35.4008 | 36.4701 | 37.2717 | 36.9309 | 38.029 | 34.4154 | 34.4172 | 34.0483 | 34.9756 | 34.9408 | 35.4162 | 36.0883 | 36.4903 | 20.5861 | 16.5025 | 92.112 | 33.0173 | 32.8652 | 34.9218 | 33.1342 | 32.9075 | 33.2965 | 34.6362 | 34.2615 | 34.0166 | 37.1675 | 36.1712 | 33.3038 | 34.3838 | 36.1615 | 36.48 | 37.2749 | 36.171 | 33.1162 | 32.2584 | 34.0813 | 34.6514 | 32.5571 | 34.4195 | 34.277 | 34.3948 | 34.2614 | 34.3349 | 34.443 | 33.8371 | 34.254 | 35.899 | 35.0589 | 36.3487 | 36.2725 | 33.3128 | 92.0816 | 91.9358 | 92.4753
2022-09-08 04:08 | 6:18 | 16.6522 | 16.9249 | 19.5769 | 34.0651 | 34.3664 | 33.8295 | 34.5576 | 35.4104 | 36.4732 | 37.2597 | 36.9311 | 38.0236 | 34.4115 | 34.4199 | 34.0613 | 34.9871 | 34.9335 | 35.3996 | 36.0831 | 36.5074 | 20.619 | 16.4683 | 92.1901 | 32.8714 | 32.8539 | 34.9064 | 33.1328 | 32.9066 | 33.3027 | 34.6569 | 34.2646 | 33.9954 | 37.1675 | 36.1582 | 33.2951 | 34.3783 | 36.1593 | 36.4835 | 37.2666 | 36.1669 | 33.1149 | 32.2697 | 34.0861 | 34.6429 | 32.574 | 34.4276 | 34.2969 | 34.3973 | 34.2462 | 34.3052 | 34.4445 | 33.8205 | 34.2614 | 35.9199 | 35.0699 | 36.3714 | 36.288 | 33.3084 | 92.1096 | 91.984 | 92.5077
2022-09-08 04:08 | 6:18 | 16.6575 | 16.9264 | 19.6036 | 34.135 | 34.3669 | 33.818 | 34.5282 | 35.4067 | 36.4573 | 37.2565 | 36.9249 | 38.0284 | 34.4068 | 34.4001 | 34.0604 | 34.9677 | 34.9281 | 35.3946 | 36.1028 | 36.4997 | 20.5831 | 16.5026 | 92.3313 | 32.769 | 32.8594 | 34.9082 | 33.1372 | 32.8966 | 33.3049 | 34.6301 | 34.2811 | 33.9928 | 37.1466 | 36.1646 | 33.2829 | 34.3466 | 36.1712 | 36.4874 | 37.2804 | 36.1938 | 33.1351 | 32.2461 | 34.0989 | 34.6387 | 32.5451 | 34.4221 | 34.2686 | 34.3962 | 34.2474 | 34.3244 | 34.4303 | 33.8168 | 34.2462 | 35.901 | 35.0684 | 36.3828 | 36.2997 | 33.3224 | 92.1098 | 92.1225 | 92.6804
2022-09-08 04:08 | 6:18 | 16.6729 | 16.9534 | 19.5921 | 34.0683 | 34.3692 | 33.8118 | 34.5288 | 35.4058 | 36.473 | 37.257 | 36.9255 | 38.0345 | 34.425 | 34.4151 | 34.0304 | 34.9667 | 34.93 | 35.4074 | 36.0894 | 36.4696 | 20.5602 | 16.524 | 92.3662 | 32.9859 | 32.8575 | 34.9065 | 33.138 | 32.8975 | 33.311 | 34.6377 | 34.252 | 33.9914 | 37.1522 | 36.1577 | 33.2887 | 34.365 | 36.1582 | 36.4658 | 37.2629 | 36.1615 | 33.1168 | 32.25 | 34.0699 | 34.6212 | 32.5476 | 34.4092 | 34.2753 | 34.4005 | 34.2508 | 34.3082 | 34.4451 | 33.8131 | 34.2474 | 35.9083 | 35.0379 | 36.3625 | 36.2888 | 33.3198 | 92.2136 | 92.1658 | 92.6781
2022-09-08 04:09 | 6:18 | 15.4547 | 16.5784 | 19.366 | 34.1349 | 34.3773 | 33.7947 | 34.5348 | 35.3951 | 36.4629 | 37.2385 | 36.9283 | 38.0273 | 34.4166 | 34.4106 | 34.0408 | 34.9681 | 34.9331 | 35.396 | 36.0949 | 36.4781 | 20.5731 | 16.8921 | 92.2691 | 32.9408 | 32.8432 | 34.9028 | 33.1162 | 32.8933 | 33.3038 | 34.6264 | 34.2581 | 34.004 | 37.1488 | 36.1558 | 33.293 | 34.3609 | 36.1646 | 36.4863 | 37.2609 | 36.1593 | 33.1218 | 32.2576 | 34.0723 | 34.6208 | 32.5299 | 34.4068 | 34.3039 | 34.3961 | 34.2349 | 34.3131 | 34.4376 | 33.8113 | 34.2508 | 35.9067 | 35.0446 | 36.3627 | 36.2764 | 33.2868 | 92.2567 | 92.2436 | 92.6767
2022-09-08 04:09 | 6:19 | 15.0346 | 16.2334 | 18.946 | 34.0652 | 34.3742 | 33.7881 | 34.5203 | 35.3803 | 36.455 | 37.2665 | 36.9181 | 38.0083 | 34.4046 | 34.4168 | 34.0494 | 34.9783 | 34.9307 | 35.4022 | 36.0799 | 36.4796 | 20.8806 | 17.6198 | 92.4288 | 32.941 | 32.851 | 34.9124 | 33.1149 | 32.9058 | 33.2951 | 34.6227 | 34.2499 | 33.9943 | 37.1661 | 36.1361 | 33.2973 | 34.3679 | 36.1577 | 36.4871 | 37.2501 | 36.1712 | 33.0975 | 32.2399 | 34.0686 | 34.6229 | 32.5129 | 34.42 | 34.3025 | 34.4038 | 34.2412 | 34.2898 | 34.4296 | 33.8196 | 34.2349 | 35.9094 | 35.0667 | 36.359 | 36.294 | 33.302 | 92.3917 | 92.403 | 92.7721
2022-09-08 04:09 | 6:19 | 14.7962 | 16.0358 | 18.7224 | 33.9603 | 34.3805 | 33.803 | 34.5215 | 35.3818 | 36.4547 | 37.2509 | 36.9145 | 38.037 | 34.3969 | 34.4091 | 34.0434 | 34.9564 | 34.9333 | 35.3774 | 36.0877 | 36.4774 | 21.431 | 18.6313 | 92.3737 | 33.0988 | 32.8674 | 34.9023 | 33.1351 | 32.8934 | 33.2829 | 34.6298 | 34.2385 | 33.9982 | 37.1456 | 36.1578 | 33.2837 | 34.3465 | 36.1558 | 36.4584 | 37.2502 | 36.1582 | 33.1179 | 32.2408 | 34.0762 | 34.6118 | 32.5398 | 34.4177 | 34.2992 | 34.3986 | 34.2477 | 34.3036 | 34.4382 | 33.7998 | 34.2412 | 35.9051 | 35.0523 | 36.3576 | 36.2879 | 33.306 | 92.4775 | 92.5333 | 92.8074
2022-09-08 04:09 | 6:19 | 14.5105 | 15.8275 | 18.5636 | 34.0197 | 34.3716 | 33.7818 | 34.5371 | 35.3996 | 36.4648 | 37.259 | 36.9177 | 38.01 | 34.3927 | 34.4137 | 34.0194 | 34.963 | 34.9095 | 35.3836 | 36.0764 | 36.4762 | 22.1609 | 19.758 | 92.4841 | 32.9245 | 32.8507 | 34.8829 | 33.1168 | 32.8922 | 33.2887 | 34.6198 | 34.263 | 33.9789 | 37.1371 | 36.1193 | 33.2882 | 34.3459 | 36.1361 | 36.4725 | 37.2651 | 36.1646 | 33.0918 | 32.2368 | 34.0643 | 34.6197 | 32.5209 | 34.4024 | 34.2896 | 34.3906 | 34.249 | 34.3063 | 34.4312 | 33.8047 | 34.2477 | 35.8974 | 35.0441 | 36.375 | 36.287 | 33.2935 | 92.5087 | 92.5973 | 92.8099
2022-09-08 04:09 | 6:19 | 14.2944 | 15.6521 | 18.3457 | 33.8651 | 34.3826 | 33.7937 | 34.5212 | 35.3876 | 36.4658 | 37.2588 | 36.9195 | 38.014 | 34.3927 | 34.3952 | 34.0367 | 34.943 | 34.92 | 35.3945 | 36.1 | 36.4648 | 22.9311 | 20.941 | 92.4578 | 33.171 | 32.84 | 34.8668 | 33.1218 | 32.8939 | 33.293 | 34.6342 | 34.2506 | 33.9814 | 37.1344 | 36.1351 | 33.2783 | 34.3579 | 36.1578 | 36.4769 | 37.2487 | 36.1577 | 33.0907 | 32.242 | 34.063 | 34.6203 | 32.5227 | 34.4244 | 34.3013 | 34.4128 | 34.252 | 34.3027 | 34.4579 | 33.8264 | 34.249 | 35.9089 | 35.0457 | 36.3754 | 36.2979 | 33.3221 | 92.6667 | 92.6775 | 92.9222
2022-09-08 04:09 | 6:19 | 14.1527 | 15.5028 | 18.2579 | 33.8652 | 34.3757 | 33.7994 | 34.4965 | 35.3976 | 36.4535 | 37.235 | 36.9026 | 38.0077 | 34.3944 | 34.3969 | 34.0238 | 34.9467 | 34.9022 | 35.3916 | 36.0907 | 36.481 | 23.7333 | 22.1031 | 92.7414 | 33.2454 | 32.8447 | 34.8859 | 33.0975 | 32.906 | 33.2973 | 34.6272 | 34.2469 | 33.9976 | 37.1354 | 36.1228 | 33.3004 | 34.3362 | 36.1193 | 36.4728 | 37.2625 | 36.1558 | 33.0997 | 32.2354 | 34.0684 | 34.5907 | 32.5288 | 34.4303 | 34.2854 | 34.416 | 34.2547 | 34.2816 | 34.4456 | 33.8029 | 34.252 | 35.9151 | 35.0338 | 36.3362 | 36.2801 | 33.3163 | 92.8123 | 92.8182 | 93.0659
2022-09-08 04:10 | 6:20 | 13.9042 | 15.3126 | 18.0373 | 33.8561 | 34.3972 | 33.77 | 34.4941 | 35.3638 | 36.4574 | 37.2452 | 36.9079 | 37.9991 | 34.4015 | 34.3822 | 34.0464 | 34.9353 | 34.9055 | 35.3746 | 36.0808 | 36.4714 | 24.483 | 23.1299 | 92.7413 | 33.2749 | 32.8649 | 34.896 | 33.1179 | 32.9032 | 33.2837 | 34.6289 | 34.2494 | 34.004 | 37.136 | 36.1302 | 33.2915 | 34.3511 | 36.1351 | 36.4705 | 37.2531 | 36.1361 | 33.1058 | 32.2277 | 34.0727 | 34.603 | 32.5388 | 34.3986 | 34.2937 | 34.4246 | 34.252 | 34.2981 | 34.4412 | 33.7924 | 34.2547 | 35.9129 | 35.0356 | 36.3697 | 36.2941 | 33.2914 | 92.8558 | 92.9302 | 93.0496
2022-09-08 04:10 | 6:20 | 13.9419 | 15.1537 | 17.858 | 33.727 | 34.4101 | 33.7783 | 34.4909 | 35.3905 | 36.4603 | 37.2618 | 36.9051 | 37.9918 | 34.3947 | 34.3891 | 34.0186 | 34.9467 | 34.895 | 35.3871 | 36.072 | 36.4776 | 25.1594 | 24.0346 | 92.901 | 33.3558 | 32.8483 | 34.8804 | 33.0918 | 32.9125 | 33.2882 | 34.6286 | 34.2463 | 33.9819 | 37.1346 | 36.137 | 33.2711 | 34.3386 | 36.1228 | 36.474 | 37.2609 | 36.1578 | 33.0862 | 32.225 | 34.0696 | 34.5976 | 32.5294 | 34.4138 | 34.3034 | 34.4275 | 34.2461 | 34.2981 | 34.4437 | 33.8174 | 34.252 | 35.8936 | 35.0442 | 36.3737 | 36.2797 | 33.2985 | 92.9762 | 93.0066 | 93.1584
2022-09-08 04:10 | 6:20 | 13.7655 | 15.0449 | 17.726 | 33.7285 | 34.3942 | 33.7743 | 34.49 | 35.3768 | 36.4565 | 37.255 | 36.9204 | 38.008 | 34.4125 | 34.3849 | 34.0098 | 34.9487 | 34.8975 | 35.3792 | 36.0796 | 36.4663 | 25.7915 | 24.8615 | 92.7235 | 33.484 | 32.8547 | 34.875 | 33.0907 | 32.9178 | 33.2783 | 34.6252 | 34.2395 | 33.9876 | 37.1234 | 36.14 | 33.2802 | 34.3395 | 36.1302 | 36.4752 | 37.2521 | 36.1193 | 33.0846 | 32.2224 | 34.0679 | 34.5977 | 32.5329 | 34.4144 | 34.3116 | 34.4067 | 34.2366 | 34.2827 | 34.4477 | 33.8156 | 34.2461 | 35.9019 | 35.0407 | 36.3626 | 36.2888 | 33.3058 | 93.0703 | 93.117 | 93.1922
2022-09-08 04:10 | 6:20 | 13.6112 | 14.9071 | 17.6223 | 33.7305 | 34.3994 | 33.7714 | 34.4956 | 35.3777 | 36.4546 | 37.248 | 36.909 | 37.991 | 34.4137 | 34.3789 | 34.0305 | 34.9604 | 34.899 | 35.3691 | 36.105 | 36.4917 | 26.389 | 25.5606 | 92.922 | 33.4881 | 32.8407 | 34.8772 | 33.0997 | 32.9073 | 33.3004 | 34.6199 | 34.2379 | 33.975 | 37.115 | 36.1317 | 33.2861 | 34.3385 | 36.137 | 36.4708 | 37.2564 | 36.1351 | 33.0924 | 32.2159 | 34.0677 | 34.5787 | 32.5473 | 34.3916 | 34.3085 | 34.4096 | 34.2515 | 34.2957 | 34.4351 | 33.8016 | 34.2366 | 35.9115 | 35.0399 | 36.3535 | 36.2906 | 33.3074 | 93.2223 | 93.2152 | 93.2823
2022-09-08 04:10 | 6:20 | 13.4043 | 14.7554 | 17.5184 | 33.8505 | 34.4098 | 33.7764 | 34.4713 | 35.3745 | 36.4491 | 37.2432 | 36.898 | 37.9923 | 34.3845 | 34.3824 | 34.0204 | 34.9361 | 34.8985 | 35.387 | 36.0754 | 36.4727 | 26.8941 | 26.1746 | 92.996 | 33.5143 | 32.8417 | 34.8708 | 33.1058 | 32.9169 | 33.2915 | 34.6421 | 34.2457 | 33.9847 | 37.1309 | 36.1298 | 33.2817 | 34.3381 | 36.14 | 36.4716 | 37.2567 | 36.1228 | 33.0888 | 32.2051 | 34.065 | 34.589 | 32.5223 | 34.3969 | 34.3157 | 34.4138 | 34.2602 | 34.2769 | 34.4478 | 33.7976 | 34.2515 | 35.9308 | 35.0424 | 36.3537 | 36.3082 | 33.2895 | 93.4197 | 93.3887 | 93.4113
2022-09-08 04:10 | 6:20 | 13.2533 | 14.6538 | 17.3916 | 33.6766 | 34.3983 | 33.7785 | 34.4558 | 35.3744 | 36.4613 | 37.2503 | 36.9091 | 38.0111 | 34.4024 | 34.3919 | 34.0181 | 34.939 | 34.8903 | 35.3781 | 36.079 | 36.4839 | 27.3395 | 26.6773 | 93.1946 | 33.6151 | 32.834 | 34.8786 | 33.0862 | 32.9047 | 33.2711 | 34.6192 | 34.2301 | 33.9686 | 37.1339 | 36.1262 | 33.2705 | 34.3291 | 36.1317 | 36.4712 | 37.2773 | 36.1302 | 33.0872 | 32.22 | 34.0666 | 34.5904 | 32.531 | 34.4054 | 34.3132 | 34.4143 | 34.2486 | 34.2938 | 34.4459 | 33.7996 | 34.2602 | 35.9133 | 35.0315 | 36.3654 | 36.2916 | 33.2955 | 93.5635 | 93.5622 | 93.4899
2022-09-08 04:11 | 6:20 | 13.1403 | 14.5241 | 17.3244 | 33.6089 | 34.4123 | 33.7698 | 34.4714 | 35.3767 | 36.4552 | 37.2503 | 36.8993 | 37.9953 | 34.391 | 34.385 | 34.0281 | 34.943 | 34.8601 | 35.3604 | 36.0782 | 36.4791 | 27.7598 | 27.1371 | 93.2784 | 33.5943 | 32.8531 | 34.867 | 33.0846 | 32.9155 | 33.2802 | 34.6339 | 34.2356 | 33.9766 | 37.1171 | 36.1237 | 33.2944 | 34.3326 | 36.1298 | 36.4903 | 37.2407 | 36.137 | 33.0794 | 32.2315 | 34.0717 | 34.5724 | 32.5477 | 34.39 | 34.311 | 34.4023 | 34.2589 | 34.2731 | 34.4329 | 33.7857 | 34.2486 | 35.9112 | 35.0446 | 36.3724 | 36.3129 | 33.2971 | 93.7393 | 93.7011 | 93.5797
2022-09-08 04:11 | 6:21 | 12.996 | 14.3917 | 17.1665 | 33.6454 | 34.4114 | 33.7666 | 34.4587 | 35.3633 | 36.4638 | 37.2627 | 36.9068 | 38.0138 | 34.3988 | 34.3715 | 34.0352 | 34.9374 | 34.882 | 35.3786 | 36.0818 | 36.4934 | 28.1079 | 27.5495 | 93.4426 | 33.6034 | 32.8421 | 34.8684 | 33.0924 | 32.928 | 33.2861 | 34.6166 | 34.2361 | 33.9791 | 37.1375 | 36.1242 | 33.2861 | 34.3284 | 36.1262 | 36.4514 | 37.2589 | 36.14 | 33.0812 | 32.2176 | 34.0866 | 34.6013 | 32.5433 | 34.3894 | 34.3103 | 34.4117 | 34.2389 | 34.2923 | 34.4528 | 33.797 | 34.2589 | 35.8986 | 35.0463 | 36.349 | 36.2998 | 33.3081 | 93.8861 | 93.8296 | 93.6746
2022-09-08 04:11 | 6:21 | 12.9205 | 14.3181 | 17.0992 | 33.7498 | 34.4269 | 33.7514 | 34.4674 | 35.3673 | 36.4507 | 37.2477 | 36.8943 | 38.0095 | 34.4069 | 34.3791 | 34.0318 | 34.9319 | 34.8895 | 35.3772 | 36.0712 | 36.4887 | 28.4125 | 27.8659 | 93.4454 | 33.6332 | 32.8524 | 34.8723 | 33.0888 | 32.9429 | 33.2817 | 34.6309 | 34.2427 | 33.9784 | 37.1252 | 36.1403 | 33.2829 | 34.3468 | 36.1237 | 36.4672 | 37.2431 | 36.1317 | 33.0844 | 32.2159 | 34.0903 | 34.5752 | 32.5378 | 34.389 | 34.3166 | 34.4269 | 34.229 | 34.2772 | 34.4457 | 33.8015 | 34.2389 | 35.9286 | 35.0324 | 36.3508 | 36.2941 | 33.2997 | 94.0368 | 94.0358 | 93.7885
2022-09-08 04:11 | 6:21 | 12.8281 | 14.1741 | 17.0176 | 33.7468 | 34.4099 | 33.7731 | 34.46 | 35.3632 | 36.44 | 37.2455 | 36.9031 | 37.9993 | 34.3873 | 34.3557 | 34.0166 | 34.9299 | 34.8827 | 35.3738 | 36.0891 | 36.4716 | 28.6655 | 28.1667 | 93.495 | 33.7172 | 32.862 | 34.8626 | 33.0872 | 32.9527 | 33.2705 | 34.6482 | 34.231 | 33.9693 | 37.1192 | 36.138 | 33.2727 | 34.3351 | 36.1242 | 36.4629 | 37.2562 | 36.1298 | 33.0954 | 32.2073 | 34.0962 | 34.5913 | 32.5739 | 34.3754 | 34.3028 | 34.4253 | 34.2635 | 34.2701 | 34.4386 | 33.7948 | 34.229 | 35.9128 | 35.0338 | 36.3747 | 36.3028 | 33.2966 | 94.2399 | 94.174 | 93.8594
2022-09-08 04:11 | 6:21 | 12.7486 | 14.0756 | 16.9341 | 33.6125 | 34.4132 | 33.7717 | 34.4479 | 35.3551 | 36.4309 | 37.2466 | 36.8916 | 38.0072 | 34.3816 | 34.3709 | 34.0257 | 34.9412 | 34.8685 | 35.3693 | 36.0905 | 36.4772 | 28.9285 | 28.4175 | 93.546 | 33.8584 | 32.8497 | 34.8732 | 33.0794 | 32.923 | 33.2944 | 34.6352 | 34.2341 | 33.9696 | 37.1415 | 36.1173 | 33.285 | 34.3147 | 36.1403 | 36.4759 | 37.2542 | 36.1262 | 33.0783 | 32.2171 | 34.0892 | 34.5901 | 32.5692 | 34.4017 | 34.3171 | 34.4159 | 34.2428 | 34.2775 | 34.455 | 33.7773 | 34.2635 | 35.9064 | 35.0413 | 36.3665 | 36.3097 | 33.3032 | 94.389 | 94.3038 | 93.9795
2022-09-08 04:11 | 6:21 | 12.6452 | 14.0016 | 16.8583 | 33.6476 | 34.4238 | 33.7571 | 34.4595 | 35.3532 | 36.4412 | 37.2346 | 36.9307 | 37.9907 | 34.398 | 34.3693 | 34.0166 | 34.9329 | 34.8716 | 35.3773 | 36.0598 | 36.4736 | 29.1363 | 28.6453 | 93.7209 | 33.8871 | 32.8514 | 34.8708 | 33.0812 | 32.9277 | 33.2861 | 34.6374 | 34.2538 | 33.9626 | 37.1432 | 36.1315 | 33.2815 | 34.3205 | 36.138 | 36.4758 | 37.263 | 36.1237 | 33.0865 | 32.2214 | 34.0955 | 34.5835 | 32.5638 | 34.391 | 34.3077 | 34.4239 | 34.2258 | 34.2698 | 34.4164 | 33.8056 | 34.2428 | 35.9132 | 35.0342 | 36.3742 | 36.3014 | 33.304 | 94.5638 | 94.4912 | 94.1115
2022-09-08 04:12 | 6:22 | 12.7549 | 13.9107 | 16.7289 | 33.5986 | 34.4121 | 33.7593 | 34.4473 | 35.3541 | 36.4592 | 37.2308 | 36.8976 | 37.9935 | 34.3923 | 34.371 | 34.0075 | 34.9425 | 34.865 | 35.3707 | 36.0563 | 36.4665 | 29.3235 | 28.8301 | 93.9266 | 33.8973 | 32.8668 | 34.8563 | 33.0844 | 32.9218 | 33.2829 | 34.631 | 34.2281 | 33.9808 | 37.1242 | 36.1277 | 33.2963 | 34.297 | 36.1173 | 36.4697 | 37.2467 | 36.1242 | 33.0636 | 32.252 | 34.1107 | 34.585 | 32.5763 | 34.3897 | 34.3141 | 34.4084 | 34.2403 | 34.2889 | 34.4336 | 33.8038 | 34.2258 | 35.9104 | 35.0546 | 36.3528 | 36.282 | 33.304 | 94.6477 | 94.6667 | 94.1892
2022-09-08 04:12 | 6:22 | 12.584 | 13.8214 | 16.6824 | 33.5181 | 34.4179 | 33.7482 | 34.4195 | 35.365 | 36.4413 | 37.2523 | 36.8953 | 37.9976 | 34.3978 | 34.3707 | 34.0117 | 34.9427 | 34.8587 | 35.3668 | 36.0788 | 36.4747 | 29.4797 | 29.0231 | 93.8725 | 33.8437 | 32.857 | 34.8625 | 33.0954 | 32.9293 | 33.2727 | 34.6188 | 34.2228 | 33.9729 | 37.1244 | 36.1071 | 33.2817 | 34.3139 | 36.1315 | 36.4723 | 37.2587 | 36.1403 | 33.0705 | 32.234 | 34.1066 | 34.5843 | 32.5719 | 34.4178 | 34.308 | 34.4261 | 34.2407 | 34.2827 | 34.4273 | 33.7812 | 34.2403 | 35.9231 | 35.0338 | 36.3646 | 36.2786 | 33.2907 | 94.8354 | 94.7595 | 94.2119
2022-09-08 04:12 | 6:22 | 12.3753 | 13.7011 | 16.5504 | 33.5161 | 34.4172 | 33.7579 | 34.4451 | 35.3553 | 36.4324 | 37.2409 | 36.8977 | 37.9817 | 34.3691 | 34.3559 | 34.0182 | 34.9241 | 34.8539 | 35.341 | 36.0764 | 36.4644 | 29.6278 | 29.1783 | 93.839 | 33.9176 | 32.8386 | 34.859 | 33.0783 | 32.9327 | 33.285 | 34.6316 | 34.2307 | 33.9741 | 37.1288 | 36.1302 | 33.2626 | 34.33 | 36.1277 | 36.4763 | 37.243 | 36.138 | 33.0739 | 32.2313 | 34.1051 | 34.5937 | 32.5691 | 34.3883 | 34.3024 | 34.4365 | 34.2518 | 34.2647 | 34.4329 | 33.8057 | 34.2407 | 35.9167 | 35.0344 | 36.3632 | 36.2932 | 33.2938 | 94.9154 | 94.8829 | 94.3007
2022-09-08 04:12 | 6:22 | 12.2759 | 13.6337 | 16.4812 | 33.4587 | 34.4247 | 33.7441 | 34.4389 | 35.3472 | 36.4406 | 37.2377 | 36.8931 | 37.9955 | 34.3905 | 34.3669 | 34.0228 | 34.9451 | 34.8502 | 35.3643 | 36.0673 | 36.4746 | 29.7673 | 29.3051 | 94.0952 | 33.8646 | 32.8399 | 34.8492 | 33.0865 | 32.9269 | 33.2815 | 34.6229 | 34.2347 | 33.9801 | 37.1147 | 36.1112 | 33.2921 | 34.3097 | 36.1071 | 36.4574 | 37.2575 | 36.1173 | 33.0678 | 32.233 | 34.097 | 34.6025 | 32.5806 | 34.3888 | 34.3274 | 34.4316 | 34.2593 | 34.2681 | 34.4172 | 33.7841 | 34.2518 | 35.9146 | 35.0482 | 36.3525 | 36.2882 | 33.2897 | 94.9986 | 94.9972 | 94.3734
2022-09-08 04:12 | 6:22 | 12.2029 | 13.524 | 16.4512 | 33.4776 | 34.426 | 33.7287 | 34.4086 | 35.3623 | 36.4217 | 37.238 | 36.9049 | 37.99 | 34.3845 | 34.3586 | 33.9777 | 34.9239 | 34.8465 | 35.3615 | 36.0645 | 36.4545 | 29.8746 | 29.4277 | 94.0653 | 33.949 | 32.8412 | 34.8612 | 33.0636 | 32.9271 | 33.2963 | 34.6302 | 34.2284 | 33.965 | 37.1038 | 36.1212 | 33.2697 | 34.3006 | 36.1302 | 36.4556 | 37.2335 | 36.1315 | 33.0578 | 32.2178 | 34.1188 | 34.5737 | 32.5985 | 34.3921 | 34.3311 | 34.4185 | 34.2651 | 34.283 | 34.4199 | 33.7926 | 34.2593 | 35.9047 | 35.033 | 36.3472 | 36.2874 | 33.2925 | 95.1 | 95.022 | 94.4547
2022-09-08 04:12 | 6:22 | 12.1423 | 13.4312 | 16.3555 | 33.5398 | 34.4326 | 33.7312 | 34.4205 | 35.3416 | 36.4346 | 37.2261 | 36.9095 | 37.9977 | 34.3658 | 34.3725 | 33.9833 | 34.903 | 34.8533 | 35.3658 | 36.0568 | 36.4559 | 29.9706 | 29.5341 | 94.2276 | 33.9547 | 32.8526 | 34.8532 | 33.0705 | 32.9347 | 33.2817 | 34.6205 | 34.2323 | 33.9765 | 37.1119 | 36.1008 | 33.2655 | 34.3249 | 36.1112 | 36.4466 | 37.2428 | 36.1277 | 33.0674 | 32.2487 | 34.0896 | 34.578 | 32.5972 | 34.3827 | 34.3401 | 34.4278 | 34.2621 | 34.2721 | 34.4001 | 33.7946 | 34.2651 | 35.8873 | 35.0288 | 36.3532 | 36.3136 | 33.2788 | 95.0901 | 95.089 | 94.4377
2022-09-08 04:13 | 6:22 | 12.0659 | 13.343 | 16.2293 | 33.5163 | 34.4374 | 33.7226 | 34.4167 | 35.3381 | 36.4101 | 37.2126 | 36.8964 | 37.9928 | 34.3918 | 34.3397 | 33.9997 | 34.9155 | 34.8471 | 35.3642 | 36.053 | 36.4635 | 30.0934 | 29.6523 | 94.1557 | 34.0313 | 32.8296 | 34.8562 | 33.0739 | 32.9344 | 33.2626 | 34.6414 | 34.2154 | 33.9734 | 37.1056 | 36.1068 | 33.2744 | 34.293 | 36.1212 | 36.4548 | 37.2473 | 36.1071 | 33.0532 | 32.235 | 34.1077 | 34.585 | 32.6162 | 34.3639 | 34.3395 | 34.4263 | 34.27 | 34.2586 | 34.4151 | 33.7975 | 34.2621 | 35.8901 | 35.04 | 36.3588 | 36.2893 | 33.2754 | 94.9783 | 95.0921 | 94.3328
2022-09-08 04:13 | 6:23 | 11.6798 | 12.762 | 16.1176 | 33.5095 | 34.443 | 33.7481 | 34.4114 | 35.3315 | 36.4035 | 37.2148 | 36.8987 | 37.9978 | 34.3617 | 34.3448 | 33.9918 | 34.9168 | 34.83 | 35.3459 | 36.0639 | 36.4474 | 30.1843 | 29.7374 | 93.9876 | 33.991 | 32.8342 | 34.8398 | 33.0678 | 32.937 | 33.2921 | 34.6204 | 34.2161 | 33.9691 | 37.1001 | 36.1161 | 33.2554 | 34.2961 | 36.1008 | 36.4547 | 37.2309 | 36.1302 | 33.0575 | 32.2352 | 34.1287 | 34.5904 | 32.5962 | 34.3606 | 34.3134 | 34.4305 | 34.2677 | 34.2583 | 34.4106 | 33.78 | 34.27 | 35.8839 | 35.0303 | 36.355 | 36.3079 | 33.273 | 94.7874 | 94.8837 | 94.1692
2022-09-08 04:13 | 6:23 | 12.2506 | 11.2092 | 15.9962 | 33.5207 | 34.4445 | 33.7258 | 34.3986 | 35.3385 | 36.4197 | 37.2156 | 36.8951 | 37.9744 | 34.3536 | 34.3559 | 33.9782 | 34.925 | 34.8301 | 35.3656 | 36.0484 | 36.4358 | 30.1784 | 29.7874 | 93.8961 | 34.0185 | 32.8408 | 34.864 | 33.0578 | 32.9293 | 33.2697 | 34.6064 | 34.2141 | 33.9495 | 37.0971 | 36.1145 | 33.2589 | 34.3055 | 36.1068 | 36.4501 | 37.2476 | 36.1112 | 33.0507 | 32.2385 | 34.1097 | 34.5886 | 32.5998 | 34.3735 | 34.3389 | 34.4318 | 34.2653 | 34.2704 | 34.4168 | 33.8013 | 34.2677 | 35.8842 | 35.0425 | 36.3634 | 36.2831 | 33.2711 | 94.586 | 94.692 | 94.0454
2022-09-08 04:13 | 6:23 | 14.5469 | 12.1231 | 17.605 | 33.5585 | 34.4303 | 33.7232 | 34.3822 | 35.3322 | 36.4099 | 37.2191 | 36.8839 | 37.9878 | 34.3628 | 34.3519 | 33.9616 | 34.9168 | 34.8299 | 35.3571 | 36.0291 | 36.4456 | 30.2516 | 29.8842 | 93.8133 | 34.0872 | 32.8326 | 34.8479 | 33.0674 | 32.9515 | 33.2655 | 34.6262 | 34.235 | 33.9659 | 37.103 | 36.0984 | 33.2786 | 34.2931 | 36.1161 | 36.455 | 37.253 | 36.1212 | 33.063 | 32.2351 | 34.112 | 34.5764 | 32.6116 | 34.3815 | 34.3305 | 34.438 | 34.2663 | 34.2681 | 34.4091 | 33.7788 | 34.2653 | 35.8857 | 35.0495 | 36.3698 | 36.2965 | 33.2657 | 94.3453 | 94.4656 | 93.9345
2022-09-08 04:13 | 6:23 | 16.4163 | 13.6087 | 19.3981 | 33.7315 | 34.4451 | 33.7199 | 34.3584 | 35.3218 | 36.3917 | 37.2063 | 36.9065 | 38.0085 | 34.3686 | 34.3565 | 33.9728 | 34.9125 | 34.8222 | 35.3599 | 36.0484 | 36.4158 | 30.347 | 29.9661 | 93.7248 | 33.9969 | 32.8209 | 34.8573 | 33.0532 | 32.9273 | 33.2744 | 34.6001 | 34.2369 | 33.9516 | 37.1211 | 36.1076 | 33.262 | 34.2837 | 36.1145 | 36.45 | 37.2274 | 36.1008 | 33.0541 | 32.2323 | 34.1044 | 34.5666 | 32.6146 | 34.3729 | 34.3484 | 34.4235 | 34.2742 | 34.2561 | 34.4137 | 33.7737 | 34.2663 | 35.9032 | 35.0349 | 36.36 | 36.2779 | 33.2549 | 94.1864 | 94.3109 | 93.8496
2022-09-08 04:13 | 6:23 | 17.9191 | 15.2777 | 21.0078 | 33.7649 | 34.4376 | 33.7241 | 34.3961 | 35.35 | 36.4068 | 37.2259 | 36.9041 | 37.9616 | 34.3774 | 34.338 | 33.9517 | 34.8933 | 34.8219 | 35.346 | 36.0332 | 36.4182 | 30.401 | 30.0157 | 93.7015 | 34.1024 | 32.8304 | 34.8346 | 33.0575 | 32.9344 | 33.2554 | 34.6097 | 34.227 | 33.9543 | 37.107 | 36.1187 | 33.2812 | 34.3089 | 36.0984 | 36.4508 | 37.2311 | 36.1068 | 33.0684 | 32.2424 | 34.0922 | 34.5774 | 32.6219 | 34.3434 | 34.3515 | 34.4273 | 34.2957 | 34.2619 | 34.3952 | 33.7763 | 34.2742 | 35.8849 | 35.045 | 36.3482 | 36.2928 | 33.2565 | 94.0348 | 94.2503 | 93.7769
2022-09-08 04:14 | 6:23 | 19.2976 | 16.9103 | 22.2687 | 33.9835 | 34.4296 | 33.7171 | 34.3824 | 35.3126 | 36.4083 | 37.2114 | 36.8911 | 37.997 | 34.3532 | 34.3476 | 33.9601 | 34.897 | 34.8273 | 35.3581 | 36.0398 | 36.4169 | 30.45 | 30.0863 | 93.5208 | 34.1227 | 32.812 | 34.8563 | 33.0507 | 32.9283 | 33.2589 | 34.6141 | 34.2171 | 33.9569 | 37.1005 | 36.1122 | 33.258 | 34.3001 | 36.1076 | 36.4538 | 37.2323 | 36.1161 | 33.0632 | 32.2421 | 34.1096 | 34.5569 | 32.6362 | 34.3884 | 34.3491 | 34.4287 | 34.2737 | 34.2527 | 34.3969 | 33.7867 | 34.2957 | 35.8643 | 35.0384 | 36.353 | 36.2918 | 33.2543 | 93.91 | 94.1418 | 93.6697
2022-09-08 04:14 | 6:24 | 20.3274 | 18.5261 | 23.3704 | 34.1359 | 34.4382 | 33.7252 | 34.3797 | 35.3279 | 36.4094 | 37.2047 | 36.9025 | 37.9809 | 34.3604 | 34.3403 | 33.9439 | 34.9016 | 34.8143 | 35.3541 | 36.0807 | 36.4253 | 30.5349 | 30.1786 | 93.2656 | 34.1913 | 32.8302 | 34.8407 | 33.063 | 32.9343 | 33.2786 | 34.6166 | 34.2207 | 33.9602 | 37.1023 | 36.1108 | 33.2666 | 34.3052 | 36.1187 | 36.442 | 37.229 | 36.1145 | 33.0621 | 32.2468 | 34.1173 | 34.5613 | 32.6432 | 34.3738 | 34.3442 | 34.4297 | 34.2621 | 34.2639 | 34.3822 | 33.7835 | 34.2737 | 35.8939 | 35.0367 | 36.3611 | 36.2931 | 33.2298 | 93.8845 | 94.0323 | 93.6451
2022-09-08 04:14 | 6:24 | 21.269 | 20.0453 | 24.4144 | 34.185 | 34.4312 | 33.739 | 34.3813 | 35.3212 | 36.4077 | 37.2217 | 36.9013 | 37.9825 | 34.3499 | 34.3401 | 33.9433 | 34.9238 | 34.8307 | 35.3394 | 36.0521 | 36.415 | 30.6033 | 30.2102 | 93.3124 | 34.1862 | 32.8128 | 34.8628 | 33.0541 | 32.9286 | 33.262 | 34.6021 | 34.227 | 33.9422 | 37.1118 | 36.1143 | 33.2562 | 34.3011 | 36.1122 | 36.4611 | 37.2126 | 36.0984 | 33.0438 | 32.2524 | 34.1239 | 34.5773 | 32.6334 | 34.3652 | 34.3612 | 34.4286 | 34.2724 | 34.2508 | 34.3891 | 33.7654 | 34.2621 | 35.8777 | 35.0236 | 36.349 | 36.2845 | 33.2535 | 93.8029 | 93.9083 | 93.6312
2022-09-08 04:14 | 6:24 | 22.1134 | 21.4096 | 25.3022 | 34.1901 | 34.4579 | 33.7381 | 34.3886 | 35.3316 | 36.4105 | 37.2377 | 36.8949 | 37.988 | 34.3373 | 34.3429 | 33.9599 | 34.9085 | 34.8042 | 35.3662 | 36.0732 | 36.4213 | 30.6985 | 30.2899 | 93.2307 | 34.2735 | 32.8367 | 34.8607 | 33.0684 | 32.914 | 33.2812 | 34.5935 | 34.2167 | 33.971 | 37.0894 | 36.1148 | 33.2638 | 34.3128 | 36.1108 | 36.4469 | 37.2182 | 36.1076 | 33.0658 | 32.2496 | 34.1158 | 34.5664 | 32.6564 | 34.3593 | 34.356 | 34.4217 | 34.27 | 34.2626 | 34.3849 | 33.7621 | 34.2724 | 35.8663 | 35.0297 | 36.3616 | 36.2743 | 33.2328 | 93.71 | 93.7993 | 93.624
2022-09-08 04:14 | 6:24 | 22.8527 | 22.6027 | 25.8764 | 34.294 | 34.4456 | 33.7313 | 34.395 | 35.313 | 36.4025 | 37.2156 | 36.8921 | 37.993 | 34.3479 | 34.3268 | 33.9697 | 34.9193 | 34.817 | 35.3516 | 36.068 | 36.4293 | 30.7464 | 30.348 | 93.2365 | 34.2948 | 32.8364 | 34.8722 | 33.0632 | 32.9248 | 33.258 | 34.6145 | 34.2341 | 33.9601 | 37.0981 | 36.1227 | 33.2621 | 34.2979 | 36.1143 | 36.4677 | 37.2165 | 36.1187 | 33.0739 | 32.2934 | 34.1176 | 34.5695 | 32.6788 | 34.3494 | 34.3552 | 34.4325 | 34.2821 | 34.2634 | 34.3789 | 33.7931 | 34.27 | 35.8733 | 35.0447 | 36.357 | 36.2933 | 33.2394 | 93.6783 | 93.7811 | 93.5624
2022-09-08 04:14 | 6:24 | 23.5605 | 23.6858 | 26.519 | 34.3971 | 34.4412 | 33.7495 | 34.4045 | 35.3511 | 36.4042 | 37.2228 | 36.889 | 37.9965 | 34.3418 | 34.308 | 33.9516 | 34.9018 | 34.8149 | 35.3441 | 36.0678 | 36.4252 | 30.8094 | 30.4125 | 93.281 | 34.2078 | 32.8283 | 34.8649 | 33.0621 | 32.949 | 33.2666 | 34.6213 | 34.2187 | 33.9593 | 37.0953 | 36.1264 | 33.2599 | 34.3048 | 36.1148 | 36.4372 | 37.2445 | 36.1122 | 33.0586 | 32.2597 | 34.1495 | 34.5836 | 32.6631 | 34.3707 | 34.3595 | 34.4243 | 34.2861 | 34.2439 | 34.3824 | 33.7715 | 34.2821 | 35.8752 | 35.0259 | 36.3558 | 36.2787 | 33.2519 | 93.5992 | 93.6894 | 93.5436
2022-09-08 04:15 | 6:25 | 25.0381 | 23.6561 | 26.8111 | 34.4314 | 34.4437 | 33.7476 | 34.4088 | 35.3193 | 36.4131 | 37.2176 | 36.8899 | 38.003 | 34.3498 | 34.3268 | 33.9758 | 34.9264 | 34.7915 | 35.3519 | 36.0848 | 36.4387 | 30.6204 | 25.4411 | 93.1007 | 34.271 | 32.8387 | 34.8448 | 33.0438 | 32.9402 | 33.2562 | 34.6227 | 34.2225 | 33.9512 | 37.1072 | 36.1165 | 33.2595 | 34.3056 | 36.1227 | 36.4437 | 37.2234 | 36.1108 | 33.0606 | 32.2776 | 34.1246 | 34.5843 | 32.6698 | 34.3494 | 34.3552 | 34.4221 | 34.2656 | 34.2523 | 34.3919 | 33.7896 | 34.2861 | 35.8832 | 35.0429 | 36.3465 | 36.2878 | 33.2397 | 93.5142 | 93.6633 | 93.4113
2022-09-08 04:15 | 6:25 | 28.2821 | 28.3059 | 27.3773 | 34.5565 | 34.4477 | 33.7432 | 34.4102 | 35.3065 | 36.4159 | 37.2214 | 36.906 | 37.9928 | 34.3176 | 34.3219 | 33.9751 | 34.9247 | 34.8193 | 35.3702 | 36.0761 | 36.4263 | 30.7119 | 27.4225 | 93.1763 | 34.3203 | 32.8183 | 34.8578 | 33.0658 | 32.924 | 33.2638 | 34.6083 | 34.219 | 33.9587 | 37.0992 | 36.1174 | 33.2687 | 34.3264 | 36.1264 | 36.4527 | 37.222 | 36.1143 | 33.0507 | 32.2625 | 34.1449 | 34.5865 | 32.6763 | 34.354 | 34.3697 | 34.4357 | 34.2876 | 34.2518 | 34.385 | 33.7915 | 34.2656 | 35.8922 | 35.0296 | 36.3614 | 36.2757 | 33.2602 | 93.4417 | 93.5464 | 93.3305
2022-09-08 04:15 | 6:25 | 30.3263 | 29.6378 | 28.3777 | 34.7578 | 34.4351 | 33.7474 | 34.4273 | 35.3393 | 36.3873 | 37.2283 | 36.9147 | 37.9958 | 34.3354 | 34.3088 | 33.9569 | 34.927 | 34.8204 | 35.3661 | 36.0879 | 36.4305 | 31.5276 | 28.765 | 93.1188 | 34.3212 | 32.8221 | 34.8567 | 33.0739 | 32.9262 | 33.2621 | 34.5982 | 34.2229 | 33.9552 | 37.1076 | 36.1177 | 33.2838 | 34.3048 | 36.1165 | 36.4366 | 37.2106 | 36.1148 | 33.067 | 32.2856 | 34.13 | 34.6017 | 32.676 | 34.3477 | 34.3657 | 34.442 | 34.2844 | 34.2437 | 34.3715 | 33.8026 | 34.2876 | 35.8859 | 35.0277 | 36.3597 | 36.284 | 33.2556 | 93.3471 | 93.4981 | 93.3315
2022-09-08 04:15 | 6:25 | 31.1739 | 30.0147 | 29.0059 | 34.7305 | 34.4478 | 33.7609 | 34.4513 | 35.3318 | 36.3966 | 37.2251 | 36.9236 | 38.0137 | 34.3349 | 34.3074 | 33.97 | 34.9216 | 34.8033 | 35.3701 | 36.0798 | 36.4173 | 32.431 | 29.3114 | 93.0916 | 34.3676 | 32.8345 | 34.8409 | 33.0586 | 32.9508 | 33.2599 | 34.6366 | 34.2237 | 33.9576 | 37.1155 | 36.1134 | 33.275 | 34.3137 | 36.1174 | 36.4414 | 37.209 | 36.1227 | 33.061 | 32.2699 | 34.139 | 34.6004 | 32.6888 | 34.3478 | 34.3775 | 34.4356 | 34.2697 | 34.2599 | 34.3791 | 33.7707 | 34.2844 | 35.8952 | 35.0387 | 36.3593 | 36.2826 | 33.2391 | 93.22 | 93.4553 | 93.2801
2022-09-08 04:15 | 6:25 | 31.7403 | 30.2341 | 29.4969 | 34.7661 | 34.4459 | 33.7541 | 34.455 | 35.3482 | 36.4088 | 37.2404 | 36.9269 | 37.9954 | 34.3052 | 34.3091 | 33.9425 | 34.9311 | 34.8027 | 35.3706 | 36.1079 | 36.4239 | 33.2614 | 29.7086 | 93.0197 | 34.3329 | 32.8382 | 34.8494 | 33.0606 | 32.951 | 33.2595 | 34.6182 | 34.2236 | 33.9447 | 37.1184 | 36.101 | 33.2794 | 34.3248 | 36.1177 | 36.4524 | 37.2177 | 36.1264 | 33.0615 | 32.2806 | 34.1384 | 34.5942 | 32.7041 | 34.3526 | 34.3693 | 34.4194 | 34.2787 | 34.2711 | 34.3557 | 33.7892 | 34.2697 | 35.903 | 35.0319 | 36.3594 | 36.284 | 33.2475 | 93.156 | 93.3458 | 93.1952
2022-09-08 04:15 | 6:25 | 32.1735 | 30.401 | 29.8673 | 34.9191 | 34.4329 | 33.7808 | 34.4761 | 35.3453 | 36.3963 | 37.25 | 36.9136 | 38.0149 | 34.3244 | 34.2994 | 33.9667 | 34.9154 | 34.8052 | 35.3612 | 36.1117 | 36.4247 | 33.8475 | 30.0151 | 92.8576 | 34.4211 | 32.8357 | 34.8609 | 33.0507 | 32.9544 | 33.2687 | 34.6221 | 34.2336 | 33.9485 | 37.0949 | 36.1343 | 33.2637 | 34.3156 | 36.1134 | 36.4499 | 37.2273 | 36.1165 | 33.0627 | 32.269 | 34.1417 | 34.609 | 32.6968 | 34.3511 | 34.3806 | 34.4393 | 34.2784 | 34.2577 | 34.3709 | 33.7969 | 34.2787 | 35.9215 | 35.0445 | 36.3606 | 36.3003 | 33.2424 | 93.0351 | 93.2319 | 93.1643
2022-09-08 04:16 | 6:25 | 32.5125 | 30.5266 | 30.1146 | 34.9799 | 34.4528 | 33.7726 | 34.4883 | 35.3338 | 36.4172 | 37.2413 | 36.9226 | 38.0033 | 34.3082 | 34.3144 | 33.9661 | 34.9399 | 34.8074 | 35.3928 | 36.1076 | 36.419 | 34.2866 | 30.275 | 92.8832 | 34.5142 | 32.8359 | 34.8566 | 33.067 | 32.9557 | 33.2838 | 34.6374 | 34.2514 | 33.9512 | 37.1058 | 36.1212 | 33.2713 | 34.3311 | 36.101 | 36.4421 | 37.2206 | 36.1174 | 33.0505 | 32.2944 | 34.152 | 34.6145 | 32.7034 | 34.3259 | 34.3865 | 34.4234 | 34.2751 | 34.2525 | 34.3693 | 33.7948 | 34.2784 | 35.9053 | 35.0369 | 36.3639 | 36.3016 | 33.2361 | 92.9592 | 93.075 | 93.0887
2022-09-08 04:16 | 6:26 | 32.8796 | 30.6268 | 30.413 | 34.9988 | 34.4457 | 33.763 | 34.482 | 35.3426 | 36.4021 | 37.2424 | 36.9218 | 38.015 | 34.3131 | 34.299 | 33.9504 | 34.928 | 34.8118 | 35.3791 | 36.1159 | 36.4522 | 34.4801 | 30.5201 | 92.8026 | 34.4476 | 32.8437 | 34.8587 | 33.061 | 32.9705 | 33.275 | 34.6178 | 34.2391 | 33.9578 | 37.0874 | 36.1084 | 33.2675 | 34.317 | 36.1343 | 36.4464 | 37.2257 | 36.1177 | 33.0754 | 32.2986 | 34.1599 | 34.6123 | 32.7265 | 34.3255 | 34.3695 | 34.4298 | 34.2755 | 34.2627 | 34.371 | 33.7958 | 34.2751 | 35.8943 | 35.0151 | 36.3635 | 36.2924 | 33.2485 | 92.7798 | 93.0042 | 92.8591
2022-09-08 04:16 | 6:26 | 33.0015 | 30.7054 | 30.6469 | 35.2071 | 34.4386 | 33.7778 | 34.4881 | 35.3547 | 36.4305 | 37.2518 | 36.9044 | 38.005 | 34.2898 | 34.2968 | 33.9651 | 34.9373 | 34.817 | 35.3935 | 36.1328 | 36.446 | 34.5044 | 30.7097 | 92.7735 | 34.4993 | 32.8342 | 34.8576 | 33.0615 | 32.9594 | 33.2794 | 34.6103 | 34.2268 | 33.9589 | 37.0996 | 36.1307 | 33.2763 | 34.3507 | 36.1212 | 36.4534 | 37.2248 | 36.1134 | 33.0651 | 32.3011 | 34.1737 | 34.602 | 32.7156 | 34.3294 | 34.3931 | 34.4169 | 34.2747 | 34.2715 | 34.3707 | 33.793 | 34.2755 | 35.9044 | 35.0512 | 36.3637 | 36.2924 | 33.2609 | 92.7698 | 92.8853 | 92.9308
2022-09-08 04:16 | 6:26 | 33.0718 | 30.8086 | 30.7898 | 35.2321 | 34.455 | 33.7793 | 34.4816 | 35.3582 | 36.417 | 37.2487 | 36.927 | 38.004 | 34.3036 | 34.3193 | 33.9723 | 34.9317 | 34.8148 | 35.3834 | 36.1496 | 36.4519 | 34.4676 | 30.8457 | 92.6374 | 34.5499 | 32.8273 | 34.8499 | 33.0627 | 32.9436 | 33.2637 | 34.6212 | 34.2329 | 33.9659 | 37.1166 | 36.1308 | 33.27 | 34.3381 | 36.1084 | 36.4632 | 37.2363 | 36.101 | 33.0409 | 32.3106 | 34.1892 | 34.6212 | 32.7235 | 34.3144 | 34.3943 | 34.4185 | 34.277 | 34.2733 | 34.3559 | 33.7996 | 34.2747 | 35.888 | 35.0408 | 36.3674 | 36.3018 | 33.2649 | 92.6419 | 92.7555 | 92.8225
2022-09-08 04:16 | 6:26 | 33.2082 | 30.8935 | 30.9712 | 35.2399 | 34.4164 | 33.7844 | 34.501 | 35.3778 | 36.4169 | 37.2585 | 36.916 | 38.0107 | 34.3063 | 34.2921 | 33.9695 | 34.924 | 34.797 | 35.3786 | 36.1628 | 36.4296 | 34.4442 | 30.9564 | 92.4727 | 34.5637 | 32.8468 | 34.8464 | 33.0505 | 32.9573 | 33.2713 | 34.6262 | 34.2331 | 33.9732 | 37.1009 | 36.1334 | 33.2562 | 34.3421 | 36.1307 | 36.4674 | 37.2241 | 36.1343 | 33.0516 | 32.3229 | 34.1708 | 34.6119 | 32.7253 | 34.3282 | 34.3859 | 34.4361 | 34.2969 | 34.2696 | 34.3669 | 33.8042 | 34.277 | 35.9113 | 35.0317 | 36.3826 | 36.3008 | 33.2579 | 92.5348 | 92.6217 | 92.767
2022-09-08 04:16 | 6:26 | 33.3765 | 30.9562 | 31.1115 | 35.2155 | 34.4336 | 33.8003 | 34.4913 | 35.3588 | 36.419 | 37.2574 | 36.9201 | 38.0052 | 34.3027 | 34.2805 | 33.9728 | 34.9401 | 34.8139 | 35.389 | 36.1548 | 36.443 | 34.4198 | 31.0445 | 92.3853 | 34.5704 | 32.8245 | 34.8441 | 33.0754 | 32.9562 | 33.2675 | 34.6329 | 34.2655 | 33.9643 | 37.1136 | 36.1221 | 33.2849 | 34.3299 | 36.1308 | 36.4678 | 37.2429 | 36.1212 | 33.0564 | 32.3217 | 34.1858 | 34.6415 | 32.7364 | 34.3192 | 34.3905 | 34.4201 | 34.2686 | 34.2707 | 34.3586 | 33.8109 | 34.2969 | 35.912 | 35.0385 | 36.3722 | 36.3081 | 33.2577 | 92.4242 | 92.5542 | 92.6132
2022-09-08 04:17 | 6:27 | 33.4532 | 31.0509 | 31.2053 | 35.2985 | 34.4273 | 33.8103 | 34.5098 | 35.3572 | 36.4174 | 37.2744 | 36.9157 | 38.0113 | 34.2816 | 34.2961 | 33.968 | 34.947 | 34.8217 | 35.4053 | 36.1579 | 36.4417 | 34.4026 | 31.1202 | 92.3699 | 34.581 | 32.8363 | 34.856 | 33.0651 | 32.9579 | 33.2763 | 34.622 | 34.254 | 33.9838 | 37.1065 | 36.1249 | 33.2709 | 34.3488 | 36.1334 | 36.4532 | 37.228 | 36.1084 | 33.0628 | 32.3279 | 34.1898 | 34.6216 | 32.748 | 34.3273 | 34.4121 | 34.4205 | 34.2753 | 34.2944 | 34.3725 | 33.8107 | 34.2686 | 35.9044 | 35.035 | 36.3511 | 36.2983 | 33.2603 | 92.3308 | 92.4327 | 92.6075
2022-09-08 04:17 | 6:27 | 33.5293 | 31.099 | 31.3877 | 35.3333 | 34.4329 | 33.7874 | 34.5166 | 35.367 | 36.4069 | 37.2759 | 36.9492 | 38.0234 | 34.2981 | 34.2845 | 33.9816 | 34.9462 | 34.8167 | 35.4038 | 36.1658 | 36.4421 | 34.3474 | 31.1904 | 92.253 | 34.5705 | 32.8643 | 34.8464 | 33.0409 | 32.9566 | 33.27 | 34.6319 | 34.2468 | 33.9637 | 37.1159 | 36.1255 | 33.2767 | 34.3601 | 36.1221 | 36.4563 | 37.2323 | 36.1307 | 33.0736 | 32.3177 | 34.1892 | 34.6524 | 32.7655 | 34.3116 | 34.3987 | 34.4312 | 34.3039 | 34.2814 | 34.3397 | 33.8079 | 34.2753 | 35.9121 | 35.0441 | 36.3618 | 36.3034 | 33.276 | 92.1946 | 92.3263 | 92.4998
2022-09-08 04:17 | 6:27 | 33.5781 | 31.1563 | 31.4969 | 35.4782 | 34.4172 | 33.7911 | 34.4986 | 35.377 | 36.3991 | 37.2793 | 36.9138 | 38.0264 | 34.2981 | 34.2917 | 33.9681 | 34.9412 | 34.8052 | 35.4105 | 36.162 | 36.4555 | 34.29 | 31.2263 | 92.2727 | 34.6825 | 32.8476 | 34.8491 | 33.0516 | 32.9656 | 33.2562 | 34.6257 | 34.2521 | 33.965 | 37.1219 | 36.1334 | 33.29 | 34.3512 | 36.1249 | 36.4705 | 37.2377 | 36.1308 | 33.0594 | 32.3368 | 34.198 | 34.6437 | 32.7723 | 34.3166 | 34.4099 | 34.4222 | 34.3025 | 34.296 | 34.3448 | 33.8114 | 34.3039 | 35.9102 | 35.0436 | 36.3721 | 36.3099 | 33.287 | 92.0955 | 92.1616 | 92.4211
2022-09-08 04:17 | 6:27 | 33.6471 | 31.2049 | 31.6456 | 35.4489 | 34.4199 | 33.8029 | 34.5175 | 35.3556 | 36.4331 | 37.2914 | 36.9213 | 38.0253 | 34.2827 | 34.275 | 33.9794 | 34.9493 | 34.7958 | 35.4096 | 36.1658 | 36.4553 | 34.2305 | 31.271 | 92.1862 | 34.6397 | 32.852 | 34.8638 | 33.0564 | 32.9728 | 33.2849 | 34.6074 | 34.2544 | 33.9666 | 37.1076 | 36.1158 | 33.2712 | 34.3581 | 36.1255 | 36.4616 | 37.2349 | 36.1334 | 33.0587 | 32.3501 | 34.2012 | 34.6542 | 32.7665 | 34.3075 | 34.4176 | 34.4228 | 34.2992 | 34.2778 | 34.3559 | 33.8215 | 34.3025 | 35.91 | 35.0319 | 36.3779 | 36.3061 | 33.2769 | 91.9786 | 92.0818 | 92.361
2022-09-08 04:17 | 6:27 | 33.6613 | 31.2422 | 31.7271 | 35.4035 | 34.4001 | 33.7934 | 34.51 | 35.3851 | 36.4225 | 37.3037 | 36.9175 | 38.0248 | 34.2957 | 34.2658 | 33.9699 | 34.9588 | 34.8001 | 35.4186 | 36.1943 | 36.4488 | 34.1096 | 31.2962 | 92.1009 | 34.6965 | 32.8304 | 34.8535 | 33.0628 | 32.9524 | 33.2709 | 34.6206 | 34.2526 | 33.965 | 37.1191 | 36.107 | 33.2784 | 34.3462 | 36.1334 | 36.4726 | 37.2453 | 36.1221 | 33.0592 | 32.3385 | 34.2159 | 34.6661 | 32.7678 | 34.3067 | 34.4144 | 34.4155 | 34.2896 | 34.2818 | 34.3519 | 33.8234 | 34.2992 | 35.9333 | 35.0351 | 36.3734 | 36.3102 | 33.2831 | 91.8255 | 91.898 | 92.2265
2022-09-08 04:17 | 6:27 | 33.6668 | 31.3004 | 31.8235 | 35.5627 | 34.4151 | 33.7961 | 34.5202 | 35.3814 | 36.4443 | 37.2858 | 36.9047 | 38.0358 | 34.2769 | 34.2686 | 33.9901 | 34.9438 | 34.8019 | 35.4179 | 36.1927 | 36.4586 | 33.9875 | 31.3197 | 91.9311 | 34.8251 | 32.8577 | 34.8506 | 33.0736 | 32.9649 | 33.2767 | 34.631 | 34.2238 | 33.9655 | 37.1069 | 36.1079 | 33.2688 | 34.3614 | 36.1158 | 36.4693 | 37.257 | 36.1249 | 33.0684 | 32.3499 | 34.2082 | 34.6439 | 32.7756 | 34.2951 | 34.4039 | 34.4156 | 34.3013 | 34.2649 | 34.3565 | 33.8199 | 34.2896 | 35.9326 | 35.0202 | 36.3641 | 36.3046 | 33.2763 | 91.7033 | 91.7995 | 92.19
2022-09-08 04:18 | 6:27 | 33.7327 | 31.3321 | 31.895 | 35.6124 | 34.4106 | 33.811 | 34.516 | 35.3829 | 36.417 | 37.2796 | 36.9228 | 38.0241 | 34.2938 | 34.2785 | 33.989 | 34.9376 | 34.8052 | 35.4213 | 36.2102 | 36.4724 | 33.8824 | 31.3554 | 91.8498 | 34.7822 | 32.8612 | 34.8512 | 33.0594 | 32.9765 | 33.29 | 34.6359 | 34.2363 | 33.9606 | 37.1165 | 36.1256 | 33.2724 | 34.3576 | 36.107 | 36.4667 | 37.262 | 36.1255 | 33.0683 | 32.3568 | 34.2303 | 34.6742 | 32.7865 | 34.2843 | 34.413 | 34.4286 | 34.2854 | 34.2739 | 34.338 | 33.818 | 34.3013 | 35.9238 | 35.0205 | 36.3858 | 36.319 | 33.297 | 91.5775 | 91.7758 | 92.0211
2022-09-08 04:18 | 6:28 | 33.8243 | 31.3645 | 31.988 | 35.6509 | 34.4168 | 33.7885 | 34.5209 | 35.3913 | 36.4308 | 37.299 | 36.9249 | 38.0228 | 34.2731 | 34.2701 | 33.9988 | 34.9353 | 34.8086 | 35.4331 | 36.2075 | 36.4527 | 33.8484 | 31.3829 | 91.8585 | 34.7518 | 32.8652 | 34.8629 | 33.0587 | 32.9796 | 33.2712 | 34.6483 | 34.2413 | 33.9572 | 37.1023 | 36.1175 | 33.2926 | 34.3487 | 36.1079 | 36.46 | 37.2386 | 36.1334 | 33.0665 | 32.3532 | 34.2429 | 34.6842 | 32.7971 | 34.2711 | 34.4088 | 34.4215 | 34.2937 | 34.2853 | 34.3476 | 33.8308 | 34.2854 | 35.9494 | 35.0475 | 36.3659 | 36.3104 | 33.2912 | 91.6526 | 91.7941 | 92.2045
2022-09-08 04:18 | 6:28 | 33.8743 | 31.3991 | 32.0817 | 35.5857 | 34.4091 | 33.7939 | 34.5333 | 35.3868 | 36.4172 | 37.3063 | 36.9266 | 38.0253 | 34.2923 | 34.2543 | 34.0013 | 34.9375 | 34.809 | 35.4362 | 36.2078 | 36.4651 | 33.8054 | 31.3947 | 91.8207 | 34.7427 | 32.8651 | 34.861 | 33.0592 | 32.9747 | 33.2784 | 34.6514 | 34.2575 | 33.9587 | 37.1038 | 36.1152 | 33.2809 | 34.3396 | 36.1256 | 36.4514 | 37.2523 | 36.1158 | 33.0491 | 32.3739 | 34.2672 | 34.69 | 32.7968 | 34.281 | 34.4049 | 34.4055 | 34.3034 | 34.2891 | 34.3403 | 33.8471 | 34.2937 | 35.9328 | 35.0166 | 36.3659 | 36.3079 | 33.2936 | 91.6904 | 91.8828 | 92.1892
2022-09-08 04:18 | 6:28 | 33.9595 | 31.4447 | 32.1543 | 35.635 | 34.4137 | 33.7921 | 34.517 | 35.4014 | 36.4219 | 37.3106 | 36.9121 | 38.0402 | 34.2772 | 34.2664 | 34.0002 | 34.9354 | 34.8063 | 35.43 | 36.2143 | 36.4699 | 33.8445 | 31.396 | 91.8188 | 34.8551 | 32.8461 | 34.8541 | 33.0684 | 32.951 | 33.2688 | 34.6318 | 34.2351 | 33.9441 | 37.0955 | 36.1396 | 33.2633 | 34.3569 | 36.1175 | 36.4652 | 37.2819 | 36.107 | 33.0433 | 32.3739 | 34.2415 | 34.6901 | 32.805 | 34.2811 | 34.4066 | 34.4186 | 34.3116 | 34.2936 | 34.3401 | 33.8421 | 34.3034 | 35.9482 | 35.0219 | 36.3658 | 36.3125 | 33.3112 | 91.7607 | 91.9368 | 92.2214
2022-09-08 04:18 | 6:28 | 34.0522 | 31.4584 | 32.2318 | 35.6982 | 34.3952 | 33.8093 | 34.5274 | 35.392 | 36.4216 | 37.3127 | 36.9376 | 38.0179 | 34.2701 | 34.2804 | 34.0014 | 34.926 | 34.7932 | 35.4485 | 36.2098 | 36.46 | 33.8507 | 31.4199 | 91.9623 | 34.7931 | 32.8602 | 34.8447 | 33.0683 | 32.9734 | 33.2724 | 34.6513 | 34.2279 | 33.9577 | 37.1273 | 36.1277 | 33.2679 | 34.3543 | 36.1152 | 36.4413 | 37.2556 | 36.1079 | 33.0601 | 32.3744 | 34.2785 | 34.6917 | 32.7986 | 34.2883 | 34.4155 | 34.4088 | 34.3085 | 34.2927 | 34.3429 | 33.834 | 34.3116 | 35.9463 | 35.0153 | 36.3716 | 36.3336 | 33.3183 | 91.7786 | 92.0197 | 92.2091
2022-09-08 04:18 | 6:28 | 34.2344 | 31.4675 | 32.322 | 35.6517 | 34.3969 | 33.7977 | 34.5278 | 35.3886 | 36.4206 | 37.307 | 36.9247 | 38.0203 | 34.2775 | 34.2507 | 34.0018 | 34.925 | 34.799 | 35.4365 | 36.228 | 36.4631 | 33.9322 | 31.4354 | 92.0486 | 34.812 | 32.8665 | 34.8465 | 33.0665 | 32.9768 | 33.2926 | 34.6616 | 34.2302 | 33.9517 | 37.1058 | 36.1073 | 33.2778 | 34.3391 | 36.1396 | 36.4744 | 37.2653 | 36.1256 | 33.0541 | 32.3878 | 34.2689 | 34.6917 | 32.7896 | 34.2546 | 34.4052 | 34.4159 | 34.3157 | 34.2907 | 34.3268 | 33.8379 | 34.3085 | 35.9412 | 35.0231 | 36.3631 | 36.323 | 33.315 | 91.8848 | 92.1979 | 92.3455
2022-09-08 04:19 | 6:29 | 34.3334 | 31.4988 | 32.4044 | 35.7037 | 34.3822 | 33.7974 | 34.522 | 35.3852 | 36.4342 | 37.3148 | 36.9156 | 38.0247 | 34.2698 | 34.2644 | 33.9988 | 34.9273 | 34.8092 | 35.426 | 36.2243 | 36.4767 | 34.0292 | 31.4134 | 92.1239 | 34.9139 | 32.8799 | 34.8346 | 33.0491 | 32.9661 | 33.2809 | 34.6576 | 34.2251 | 33.9604 | 37.1034 | 36.1279 | 33.2867 | 34.3421 | 36.1277 | 36.4702 | 37.2867 | 36.1175 | 33.0718 | 32.3876 | 34.2716 | 34.7072 | 32.8098 | 34.2671 | 34.4237 | 34.4246 | 34.3132 | 34.2996 | 34.308 | 33.8438 | 34.3157 | 35.9516 | 35.0052 | 36.3694 | 36.3244 | 33.3392 | 92.0388 | 92.3117 | 92.4329
2022-09-08 04:19 | 6:29 | 34.3771 | 31.5282 | 32.4651 | 35.7989 | 34.3891 | 33.7833 | 34.5311 | 35.4005 | 36.4498 | 37.3281 | 36.8946 | 38.0167 | 34.2889 | 34.2642 | 34.0016 | 34.9332 | 34.7838 | 35.4439 | 36.2279 | 36.4854 | 34.0975 | 31.4374 | 92.0611 | 34.8819 | 32.8741 | 34.8485 | 33.0433 | 32.9753 | 33.2633 | 34.6479 | 34.221 | 33.9533 | 37.1202 | 36.1011 | 33.2606 | 34.3294 | 36.1073 | 36.4674 | 37.2783 | 36.1152 | 33.043 | 32.3974 | 34.2634 | 34.7093 | 32.8172 | 34.2517 | 34.4104 | 34.4184 | 34.311 | 34.3058 | 34.3268 | 33.8485 | 34.3132 | 35.9532 | 35.004 | 36.3739 | 36.3184 | 33.3186 | 92.1234 | 92.3525 | 92.5234
2022-09-08 04:19 | 6:29 | 33.3718 | 31.4602 | 32.4779 | 35.8942 | 34.3849 | 33.7993 | 34.5272 | 35.3848 | 36.4298 | 37.3163 | 36.894 | 38.0088 | 34.2827 | 34.2582 | 34 | 34.9306 | 34.8062 | 35.4474 | 36.2154 | 36.4637 | 32.6478 | 31.3004 | 92.2177 | 34.8902 | 32.8701 | 34.8524 | 33.0601 | 32.9805 | 33.2679 | 34.6656 | 34.2251 | 33.9464 | 37.1178 | 36.124 | 33.2717 | 34.3348 | 36.1279 | 36.472 | 37.2584 | 36.1396 | 33.0476 | 32.4008 | 34.2677 | 34.6973 | 32.8043 | 34.24 | 34.4256 | 34.4199 | 34.3103 | 34.2985 | 34.3219 | 33.8668 | 34.311 | 35.9473 | 35.0128 | 36.3808 | 36.3079 | 33.328 | 92.245 | 92.4711 | 92.5225
2022-09-08 04:19 | 6:29 | 30.2914 | 30.4627 | 31.8985 | 35.8395 | 34.3789 | 33.7938 | 34.527 | 35.4006 | 36.4283 | 37.3446 | 36.9112 | 38.0025 | 34.2647 | 34.254 | 33.9947 | 34.9233 | 34.7957 | 35.4303 | 36.2457 | 36.4768 | 29.4117 | 30.8789 | 92.3096 | 34.9342 | 32.8812 | 34.823 | 33.0541 | 32.9596 | 33.2778 | 34.631 | 34.2158 | 33.9597 | 37.0805 | 36.1031 | 33.2762 | 34.3441 | 36.1011 | 36.454 | 37.2675 | 36.1277 | 33.0499 | 32.3971 | 34.2695 | 34.7004 | 32.8126 | 34.2794 | 34.4147 | 34.4174 | 34.3166 | 34.3169 | 34.3088 | 33.8215 | 34.3103 | 35.9636 | 35.0166 | 36.3654 | 36.3135 | 33.3189 | 92.3902 | 92.6036 | 92.5979
2022-09-08 04:19 | 6:29 | 31.0662 | 22.5987 | 31.6422 | 35.7696 | 34.3824 | 33.7798 | 34.5256 | 35.3587 | 36.4233 | 37.3255 | 36.914 | 38.0034 | 34.2681 | 34.2614 | 33.9838 | 34.9209 | 34.7792 | 35.4382 | 36.2394 | 36.4694 | 26.8735 | 29.0545 | 92.4859 | 34.8592 | 32.8614 | 34.8352 | 33.0718 | 32.9596 | 33.2867 | 34.6565 | 34.2292 | 33.9293 | 37.1121 | 36.1167 | 33.2886 | 34.3406 | 36.124 | 36.4684 | 37.2779 | 36.1073 | 33.0396 | 32.4002 | 34.2925 | 34.6985 | 32.8473 | 34.2745 | 34.4178 | 34.4156 | 34.3028 | 34.2959 | 34.3074 | 33.8472 | 34.3166 | 35.9552 | 35.0075 | 36.3618 | 36.3287 | 33.3287 | 92.5253 | 92.7284 | 92.7457
2022-09-08 04:19 | 6:29 | 31.4309 | 23.1439 | 31.8591 | 35.8882 | 34.3919 | 33.7897 | 34.5104 | 35.3883 | 36.4262 | 37.3178 | 36.8923 | 38.0186 | 34.283 | 34.2462 | 33.9951 | 34.9252 | 34.7861 | 35.4499 | 36.2273 | 36.4903 | 27.5301 | 29.4136 | 92.5784 | 34.9263 | 32.8895 | 34.8325 | 33.043 | 32.9681 | 33.2606 | 34.6558 | 34.2236 | 33.9371 | 37.1036 | 36.0954 | 33.2696 | 34.3289 | 36.1031 | 36.4557 | 37.2932 | 36.1279 | 33.0293 | 32.3966 | 34.2777 | 34.7192 | 32.8561 | 34.2607 | 34.4085 | 34.4161 | 34.3171 | 34.2938 | 34.3091 | 33.8416 | 34.3028 | 35.9291 | 35.0039 | 36.3612 | 36.3177 | 33.3347 | 92.6699 | 92.7823 | 92.8043
2022-09-08 04:20 | 6:29 | 31.5437 | 25.7733 | 31.9785 | 35.9022 | 34.385 | 33.802 | 34.5181 | 35.3792 | 36.4438 | 37.3511 | 36.8993 | 37.9978 | 34.2721 | 34.2474 | 34.0025 | 34.9202 | 34.7981 | 35.4275 | 36.2108 | 36.486 | 28.2986 | 29.7693 | 92.425 | 34.8565 | 32.8836 | 34.8325 | 33.0476 | 32.9659 | 33.2717 | 34.6545 | 34.2163 | 33.9281 | 37.0948 | 36.0998 | 33.2687 | 34.3464 | 36.1167 | 36.4622 | 37.2951 | 36.1011 | 33.0461 | 32.4144 | 34.2841 | 34.6933 | 32.839 | 34.2476 | 34.4113 | 34.3989 | 34.3077 | 34.3121 | 34.2994 | 33.852 | 34.3171 | 35.9371 | 34.993 | 36.3832 | 36.3262 | 33.31 | 92.6911 | 92.9202 | 92.8409
2022-09-08 04:20 | 6:30 | 31.5965 | 27.622 | 32.0698 | 35.8254 | 34.3715 | 33.7868 | 34.5335 | 35.3794 | 36.4317 | 37.3339 | 36.8984 | 38.0262 | 34.2586 | 34.2508 | 34.0034 | 34.9175 | 34.7985 | 35.4361 | 36.2377 | 36.493 | 29.0025 | 30.0685 | 92.5865 | 34.9512 | 32.8762 | 34.8389 | 33.0499 | 32.9577 | 33.2762 | 34.6664 | 34.2105 | 33.9501 | 37.1138 | 36.0928 | 33.2814 | 34.322 | 36.0954 | 36.4532 | 37.2863 | 36.124 | 33.0459 | 32.3872 | 34.2861 | 34.7263 | 32.8608 | 34.2379 | 34.4305 | 34.4235 | 34.3141 | 34.3078 | 34.3144 | 33.8443 | 34.3077 | 35.9586 | 35.0055 | 36.3728 | 36.2998 | 33.3137 | 92.8913 | 93.0235 | 92.8755
2022-09-08 04:20 | 6:30 | 31.6782 | 28.8449 | 32.1608 | 35.9344 | 34.3791 | 33.7946 | 34.5078 | 35.3759 | 36.4314 | 37.3266 | 36.8844 | 38.0189 | 34.2583 | 34.2349 | 34.0063 | 34.9206 | 34.7831 | 35.4612 | 36.2254 | 36.4866 | 29.6036 | 30.295 | 92.7317 | 34.926 | 32.8724 | 34.8498 | 33.0396 | 32.9509 | 33.2886 | 34.6644 | 34.2041 | 33.9221 | 37.118 | 36.0976 | 33.2812 | 34.3251 | 36.0998 | 36.4618 | 37.2887 | 36.1031 | 33.0432 | 32.4334 | 34.2871 | 34.7204 | 32.8466 | 34.2642 | 34.4197 | 34.3951 | 34.308 | 34.3231 | 34.299 | 33.8397 | 34.3141 | 35.9652 | 35.0111 | 36.3487 | 36.3137 | 33.3173 | 93.0571 | 93.1324 | 93.0008
2022-09-08 04:20 | 6:30 | 31.7662 | 29.596 | 32.2093 | 35.9246 | 34.3557 | 33.7797 | 34.5101 | 35.3921 | 36.4154 | 37.3467 | 36.893 | 38.011 | 34.2704 | 34.2412 | 33.994 | 34.9071 | 34.7784 | 35.4345 | 36.2448 | 36.4764 | 30.0792 | 30.4859 | 92.8689 | 34.9122 | 32.888 | 34.8442 | 33.0293 | 32.9648 | 33.2696 | 34.6522 | 34.2147 | 33.9189 | 37.1061 | 36.0954 | 33.2757 | 34.342 | 36.0928 | 36.4588 | 37.2928 | 36.1167 | 33.0273 | 32.4305 | 34.2951 | 34.7304 | 32.8487 | 34.257 | 34.4433 | 34.4199 | 34.3024 | 34.3181 | 34.2968 | 33.8513 | 34.308 | 35.9611 | 34.9937 | 36.3818 | 36.313 | 33.3248 | 93.214 | 93.312 | 93.1337
2022-09-08 04:20 | 6:30 | 31.8776 | 30.0847 | 32.2645 | 36.015 | 34.3709 | 33.7895 | 34.5183 | 35.3835 | 36.4272 | 37.3356 | 36.8954 | 38.0149 | 34.2681 | 34.2477 | 34.0027 | 34.8957 | 34.7993 | 35.4394 | 36.2545 | 36.4851 | 30.4725 | 30.6409 | 92.9402 | 34.9517 | 32.8852 | 34.8357 | 33.0461 | 32.9751 | 33.2687 | 34.6756 | 34.1873 | 33.9293 | 37.1127 | 36.1143 | 33.2924 | 34.3321 | 36.0976 | 36.429 | 37.3103 | 36.0954 | 33.0455 | 32.4181 | 34.3083 | 34.7217 | 32.8601 | 34.261 | 34.4169 | 34.4204 | 34.3274 | 34.3252 | 34.3193 | 33.862 | 34.3024 | 35.9542 | 35.002 | 36.3815 | 36.3307 | 33.3197 | 93.335 | 93.4525 | 93.1194
2022-09-08 04:20 | 6:30 | 31.9797 | 30.4247 | 32.3103 | 36.0208 | 34.3693 | 33.7642 | 34.5285 | 35.375 | 36.4388 | 37.3276 | 36.8969 | 38.0203 | 34.2561 | 34.249 | 34.0164 | 34.9201 | 34.7981 | 35.4425 | 36.2467 | 36.4896 | 30.7979 | 30.7476 | 93.0993 | 34.9632 | 32.8918 | 34.8371 | 33.0459 | 32.9763 | 33.2814 | 34.6583 | 34.1973 | 33.9275 | 37.1067 | 36.1014 | 33.2702 | 34.3309 | 36.0954 | 36.4623 | 37.3147 | 36.0998 | 33.0413 | 32.4276 | 34.2875 | 34.7211 | 32.8472 | 34.2401 | 34.4257 | 34.3865 | 34.3311 | 34.3314 | 34.2921 | 33.8557 | 34.3274 | 35.9467 | 35.0003 | 36.384 | 36.3385 | 33.3369 | 93.5244 | 93.6239 | 93.2815
2022-09-08 04:21 | 6:31 | 32.0903 | 30.6564 | 32.334 | 35.9836 | 34.371 | 33.7942 | 34.5245 | 35.3815 | 36.4301 | 37.3571 | 36.8853 | 38.0115 | 34.2619 | 34.252 | 34.0061 | 34.9083 | 34.7916 | 35.4391 | 36.2586 | 36.4739 | 31.0805 | 30.8479 | 92.8205 | 34.9257 | 32.8867 | 34.8273 | 33.0432 | 32.9558 | 33.2812 | 34.6724 | 34.2036 | 33.9372 | 37.1042 | 36.1015 | 33.2884 | 34.3217 | 36.1143 | 36.4566 | 37.287 | 36.0928 | 33.0582 | 32.4207 | 34.3149 | 34.7332 | 32.8684 | 34.2519 | 34.4334 | 34.415 | 34.3401 | 34.2991 | 34.2805 | 33.8496 | 34.3311 | 35.9464 | 34.9914 | 36.3775 | 36.3509 | 33.3183 | 93.6889 | 93.8249 | 93.3633
2022-09-08 04:21 | 6:31 | 32.1618 | 30.8212 | 32.3962 | 36.0625 | 34.3707 | 33.7769 | 34.5223 | 35.3758 | 36.4354 | 37.3423 | 36.9007 | 38.028 | 34.2527 | 34.2547 | 34.003 | 34.8928 | 34.7889 | 35.4346 | 36.256 | 36.4928 | 31.2717 | 30.9285 | 93.0222 | 34.9531 | 32.8941 | 34.8347 | 33.0273 | 32.9735 | 33.2757 | 34.6498 | 34.1983 | 33.9331 | 37.1088 | 36.1136 | 33.2667 | 34.335 | 36.1014 | 36.4616 | 37.3112 | 36.0976 | 33.0465 | 32.4442 | 34.3104 | 34.7321 | 32.8806 | 34.2418 | 34.4252 | 34.4065 | 34.3395 | 34.3191 | 34.2961 | 33.8608 | 34.3401 | 35.9711 | 34.9922 | 36.3501 | 36.3184 | 33.3282 | 93.8397 | 94.0897 | 93.5188
2022-09-08 04:21 | 6:31 | 32.2428 | 30.937 | 32.419 | 36.0913 | 34.3559 | 33.7749 | 34.5152 | 35.3893 | 36.4225 | 37.3363 | 36.8704 | 37.9963 | 34.2639 | 34.252 | 33.9962 | 34.9193 | 34.7957 | 35.4349 | 36.2421 | 36.4963 | 31.4334 | 31.0004 | 93.3859 | 35.0263 | 32.8891 | 34.843 | 33.0455 | 32.9733 | 33.2924 | 34.6697 | 34.1873 | 33.9325 | 37.105 | 36.1147 | 33.2925 | 34.3197 | 36.1015 | 36.4543 | 37.2942 | 36.0954 | 33.0402 | 32.4296 | 34.3223 | 34.7385 | 32.8865 | 34.2244 | 34.4299 | 34.3895 | 34.3134 | 34.3173 | 34.2845 | 33.8728 | 34.3395 | 35.9712 | 34.9962 | 36.361 | 36.3144 | 33.3155 | 94.1017 | 94.2172 | 93.7217
2022-09-08 04:21 | 6:31 | 32.2944 | 31.0381 | 32.4669 | 36.0431 | 34.3669 | 33.7849 | 34.5191 | 35.3728 | 36.4297 | 37.3611 | 36.8937 | 38.0053 | 34.2508 | 34.2461 | 34.0178 | 34.904 | 34.7895 | 35.4427 | 36.2522 | 36.4876 | 31.554 | 31.0453 | 93.2154 | 34.9952 | 32.8965 | 34.8216 | 33.0413 | 32.9661 | 33.2702 | 34.6609 | 34.1986 | 33.9154 | 37.116 | 36.1125 | 33.2873 | 34.3236 | 36.1136 | 36.4596 | 37.3143 | 36.1143 | 33.0556 | 32.4329 | 34.3257 | 34.7308 | 32.9032 | 34.231 | 34.4195 | 34.3977 | 34.3389 | 34.3165 | 34.2917 | 33.8446 | 34.3134 | 35.9677 | 35.0036 | 36.3519 | 36.3194 | 33.3246 | 94.152 | 94.3978 | 93.6039
2022-09-08 04:21 | 6:31 | 32.3071 | 31.1139 | 32.4839 | 36.1151 | 34.3586 | 33.7763 | 34.5307 | 35.3812 | 36.4374 | 37.3426 | 36.8821 | 38.0005 | 34.2626 | 34.2366 | 33.9933 | 34.8978 | 34.7951 | 35.4539 | 36.2627 | 36.4758 | 31.6868 | 31.1051 | 93.1702 | 35.08 | 32.8904 | 34.8412 | 33.0582 | 32.9574 | 33.2884 | 34.6601 | 34.1972 | 33.9228 | 37.1 | 36.1004 | 33.2642 | 34.3169 | 36.1147 | 36.4595 | 37.29 | 36.1014 | 33.0529 | 32.4549 | 34.3338 | 34.7456 | 32.9001 | 34.2241 | 34.4276 | 34.3806 | 34.3305 | 34.3 | 34.275 | 33.8648 | 34.3389 | 35.9745 | 34.9987 | 36.3676 | 36.313 | 33.3376 | 94.3647 | 94.4901 | 93.784
2022-09-08 04:21 | 6:31 | 32.3545 | 31.177 | 32.5156 | 36.1042 | 34.3725 | 33.778 | 34.536 | 35.3834 | 36.4328 | 37.3349 | 36.8894 | 38.0011 | 34.2634 | 34.2515 | 34.0032 | 34.9031 | 34.7666 | 35.429 | 36.272 | 36.4863 | 31.7779 | 31.1532 | 93.2675 | 35.0623 | 32.8851 | 34.836 | 33.0465 | 32.9803 | 33.2667 | 34.6737 | 34.1987 | 33.9255 | 37.1021 | 36.1248 | 33.305 | 34.3334 | 36.1125 | 36.4507 | 37.3198 | 36.1015 | 33.056 | 32.4441 | 34.3157 | 34.7338 | 32.8985 | 34.2276 | 34.4221 | 34.3956 | 34.3484 | 34.325 | 34.2658 | 33.8751 | 34.3305 | 35.9678 | 34.9926 | 36.344 | 36.3495 | 33.313 | 94.4822 | 94.6658 | 93.8203
2022-09-08 04:22 | 6:31 | 32.3927 | 31.2276 | 32.5506 | 36.1032 | 34.3397 | 33.7657 | 34.5252 | 35.3786 | 36.4323 | 37.336 | 36.8826 | 38.0108 | 34.2439 | 34.2602 | 34.0024 | 34.8883 | 34.7861 | 35.4273 | 36.2532 | 36.479 | 31.8723 | 31.166 | 93.4437 | 35.1128 | 32.9073 | 34.8237 | 33.0402 | 32.9732 | 33.2925 | 34.6607 | 34.1997 | 33.9329 | 37.1043 | 36.1278 | 33.2703 | 34.3138 | 36.1004 | 36.4503 | 37.2897 | 36.1136 | 33.0475 | 32.4431 | 34.3342 | 34.7478 | 32.9097 | 34.2263 | 34.4092 | 34.3714 | 34.3515 | 34.3387 | 34.2686 | 33.8648 | 34.3484 | 35.9369 | 34.9938 | 36.3824 | 36.3329 | 33.3266 | 94.6362 | 94.7621 | 93.9889
2022-09-08 04:22 | 6:32 | 32.4287 | 31.282 | 32.572 | 36.1402 | 34.3448 | 33.7848 | 34.5116 | 35.3971 | 36.4336 | 37.3408 | 36.879 | 38.009 | 34.2523 | 34.2486 | 33.9933 | 34.8888 | 34.7781 | 35.4541 | 36.2575 | 36.4795 | 31.9289 | 31.2145 | 93.6667 | 35.0842 | 32.872 | 34.8365 | 33.0556 | 32.9768 | 33.2873 | 34.6723 | 34.1924 | 33.9307 | 37.0906 | 36.1109 | 33.2783 | 34.3102 | 36.1248 | 36.447 | 37.3079 | 36.1147 | 33.0361 | 32.4453 | 34.3428 | 34.7625 | 32.9014 | 34.233 | 34.4068 | 34.3959 | 34.3491 | 34.3204 | 34.2785 | 33.8686 | 34.3515 | 35.9653 | 34.998 | 36.3747 | 36.3062 | 33.3217 | 94.7619 | 94.8727 | 94.1228
2022-09-08 04:22 | 6:32 | 32.4936 | 31.3264 | 32.6235 | 36.1362 | 34.3559 | 33.7902 | 34.5126 | 35.3677 | 36.4269 | 37.3521 | 36.8901 | 38.0109 | 34.2518 | 34.2589 | 34.0157 | 34.895 | 34.807 | 35.4406 | 36.2547 | 36.489 | 32.1219 | 31.2315 | 93.7162 | 35.0629 | 32.8666 | 34.8429 | 33.0529 | 32.9871 | 33.2642 | 34.6703 | 34.194 | 33.9368 | 37.1128 | 36.1242 | 33.2816 | 34.3156 | 36.1278 | 36.4474 | 37.301 | 36.1125 | 33.0559 | 32.4584 | 34.3386 | 34.7457 | 32.9104 | 34.2272 | 34.42 | 34.3591 | 34.3442 | 34.3322 | 34.2701 | 33.8522 | 34.3491 | 35.9575 | 34.9798 | 36.3454 | 36.3294 | 33.3236 | 94.8769 | 94.9841 | 94.0641
2022-09-08 04:22 | 6:32 | 32.5468 | 31.383 | 32.6611 | 36.257 | 34.3519 | 33.7806 | 34.5211 | 35.3688 | 36.4432 | 37.3416 | 36.8885 | 38.0026 | 34.2437 | 34.2389 | 34.014 | 34.9193 | 34.7981 | 35.4521 | 36.2604 | 36.4876 | 32.3107 | 31.2881 | 93.8748 | 35.093 | 32.8919 | 34.8129 | 33.056 | 32.9693 | 33.305 | 34.6518 | 34.2057 | 33.9376 | 37.0998 | 36.1037 | 33.2896 | 34.3202 | 36.1109 | 36.447 | 37.2954 | 36.1004 | 33.052 | 32.4568 | 34.3524 | 34.7484 | 32.9198 | 34.2318 | 34.4177 | 34.3593 | 34.3612 | 34.3381 | 34.2543 | 33.872 | 34.3442 | 35.971 | 34.9847 | 36.3663 | 36.3329 | 33.3192 | 95.0045 | 95.0639 | 94.256
2022-09-08 04:22 | 6:32 | 32.6425 | 31.7468 | 32.7342 | 36.1501 | 34.3565 | 33.7888 | 34.5308 | 35.3744 | 36.4355 | 37.3563 | 36.885 | 37.9918 | 34.2599 | 34.229 | 33.9981 | 34.9009 | 34.7792 | 35.4245 | 36.2517 | 36.4822 | 32.875 | 31.9635 | 93.9002 | 35.0576 | 32.8742 | 34.8336 | 33.0475 | 32.9714 | 33.2703 | 34.6641 | 34.1885 | 33.919 | 37.0955 | 36.1134 | 33.2878 | 34.3087 | 36.1242 | 36.4417 | 37.2864 | 36.1248 | 33.0361 | 32.4564 | 34.3522 | 34.7527 | 32.9169 | 34.2093 | 34.4024 | 34.3825 | 34.356 | 34.3467 | 34.2664 | 33.8388 | 34.3612 | 35.9607 | 35.0145 | 36.3617 | 36.3275 | 33.3126 | 94.9779 | 95.1413 | 94.1716
2022-09-08 04:22 | 6:32 | 33.4047 | 31.6947 | 33 | 36.1927 | 34.338 | 33.7751 | 34.526 | 35.3989 | 36.4219 | 37.3256 | 36.8877 | 38.0109 | 34.2711 | 34.2635 | 33.9964 | 34.8972 | 34.7782 | 35.4312 | 36.2601 | 36.4638 | 33.4824 | 32.2167 | 93.9501 | 35.1289 | 32.8854 | 34.842 | 33.0361 | 32.9616 | 33.2783 | 34.6672 | 34.1919 | 33.9092 | 37.1095 | 36.1243 | 33.2792 | 34.3059 | 36.1037 | 36.4362 | 37.3002 | 36.1278 | 33.0504 | 32.4734 | 34.3712 | 34.7509 | 32.9314 | 34.2245 | 34.4244 | 34.3662 | 34.3552 | 34.3486 | 34.2804 | 33.8847 | 34.356 | 35.9372 | 35.0028 | 36.3643 | 36.3157 | 33.3218 | 94.9502 | 95.068 | 94.1496
2022-09-08 04:23 | 6:32 | 34.4855 | 31.6725 | 33.298 | 36.1665 | 34.3476 | 33.7811 | 34.5228 | 35.3677 | 36.4031 | 37.3399 | 36.8823 | 37.9965 | 34.2577 | 34.2428 | 33.9737 | 34.8867 | 34.7865 | 35.4379 | 36.2521 | 36.4766 | 34.2972 | 32.3561 | 93.8675 | 35.2184 | 32.8871 | 34.8538 | 33.0559 | 32.9689 | 33.2816 | 34.6433 | 34.1992 | 33.9228 | 37.0921 | 36.1288 | 33.2754 | 34.2998 | 36.1134 | 36.455 | 37.3027 | 36.1109 | 33.0675 | 32.468 | 34.3455 | 34.744 | 32.9665 | 34.2142 | 34.4303 | 34.3616 | 34.3595 | 34.3317 | 34.2507 | 33.855 | 34.3552 | 35.9581 | 34.9786 | 36.3583 | 36.3177 | 33.2889 | 94.7116 | 94.8839 | 93.9065
2022-09-08 04:23 | 6:33 | 35.1305 | 31.6579 | 33.5652 | 36.253 | 34.3403 | 33.7866 | 34.5233 | 35.3824 | 36.4367 | 37.341 | 36.8697 | 38.0055 | 34.2525 | 34.2258 | 33.9867 | 34.8836 | 34.7812 | 35.4387 | 36.2537 | 36.4736 | 34.88 | 32.2358 | 93.6867 | 35.2105 | 32.8854 | 34.8403 | 33.052 | 32.9603 | 33.2896 | 34.6556 | 34.1803 | 33.9177 | 37.0929 | 36.1329 | 33.2743 | 34.3076 | 36.1243 | 36.4315 | 37.301 | 36.1242 | 33.0466 | 32.4749 | 34.3504 | 34.733 | 32.96 | 34.2266 | 34.3986 | 34.3556 | 34.3552 | 34.3325 | 34.2644 | 33.8758 | 34.3595 | 35.9566 | 34.9814 | 36.3423 | 36.32 | 33.3121 | 94.4594 | 94.6212 | 93.7898
2022-09-08 04:23 | 6:33 | 35.396 | 31.6601 | 33.6975 | 36.2198 | 34.3401 | 33.7885 | 34.5011 | 35.3639 | 36.4193 | 37.3389 | 36.881 | 37.9874 | 34.2627 | 34.2403 | 33.9879 | 34.8916 | 34.7674 | 35.4427 | 36.2408 | 36.4518 | 35.1388 | 32.1026 | 93.4285 | 35.3073 | 32.878 | 34.8335 | 33.0361 | 32.951 | 33.2878 | 34.6435 | 34.1923 | 33.9108 | 37.0887 | 36.1273 | 33.285 | 34.317 | 36.1288 | 36.4301 | 37.2903 | 36.1037 | 33.0563 | 32.4617 | 34.3557 | 34.7605 | 32.9685 | 34.2283 | 34.4138 | 34.3568 | 34.3697 | 34.3365 | 34.2642 | 33.8646 | 34.3552 | 35.9385 | 34.9968 | 36.3621 | 36.3182 | 33.3102 | 94.1806 | 94.4029 | 93.6082
2022-09-08 04:23 | 6:33 | 35.4735 | 31.6965 | 33.7186 | 36.2478 | 34.3429 | 33.7724 | 34.5264 | 35.3766 | 36.4287 | 37.333 | 36.8737 | 38.0009 | 34.2715 | 34.2407 | 33.9731 | 34.8986 | 34.7575 | 35.4412 | 36.244 | 36.4605 | 35.2228 | 31.9681 | 93.3295 | 35.3146 | 32.8845 | 34.8465 | 33.0504 | 32.9597 | 33.2792 | 34.6376 | 34.2022 | 33.906 | 37.0937 | 36.137 | 33.2829 | 34.318 | 36.1329 | 36.4206 | 37.2874 | 36.1134 | 33.0578 | 32.4874 | 34.3445 | 34.7509 | 32.9703 | 34.2437 | 34.4144 | 34.3491 | 34.3657 | 34.3537 | 34.2582 | 33.8733 | 34.3697 | 35.9473 | 35.0195 | 36.3468 | 36.3185 | 33.2915 | 94.0422 | 94.1526 | 93.5132
2022-09-08 04:23 | 6:33 | 35.3278 | 31.685 | 33.6857 | 36.429 | 34.3268 | 33.7881 | 34.5125 | 35.3674 | 36.4206 | 37.3402 | 36.8906 | 37.9959 | 34.2733 | 34.2518 | 33.9924 | 34.9237 | 34.7894 | 35.4226 | 36.2636 | 36.4411 | 35.0601 | 31.8569 | 93.304 | 35.2947 | 32.895 | 34.841 | 33.0675 | 32.9723 | 33.2754 | 34.6397 | 34.1833 | 33.9128 | 37.0835 | 36.138 | 33.2837 | 34.3155 | 36.1273 | 36.4439 | 37.2852 | 36.1243 | 33.0684 | 32.4951 | 34.357 | 34.7704 | 32.9831 | 34.2337 | 34.3916 | 34.3578 | 34.3775 | 34.3381 | 34.254 | 33.8604 | 34.3657 | 35.9449 | 34.9865 | 36.3576 | 36.3203 | 33.3037 | 93.9086 | 94.0656 | 93.4307
2022-09-08 04:23 | 6:33 | 35.078 | 31.716 | 33.4532 | 36.4135 | 34.308 | 33.7906 | 34.4998 | 35.3837 | 36.4198 | 37.3375 | 36.8779 | 38.0085 | 34.2696 | 34.2593 | 33.9727 | 34.9057 | 34.7849 | 35.421 | 36.2696 | 36.4626 | 35.0139 | 31.825 | 93.21 | 35.3203 | 32.9003 | 34.8478 | 33.0466 | 32.9771 | 33.2743 | 34.658 | 34.2009 | 33.9123 | 37.1043 | 36.1433 | 33.2968 | 34.3038 | 36.137 | 36.4371 | 37.3015 | 36.1288 | 33.0483 | 32.4817 | 34.357 | 34.7411 | 33.0061 | 34.2249 | 34.3969 | 34.3323 | 34.3693 | 34.3456 | 34.2614 | 33.8671 | 34.3775 | 35.9293 | 34.9994 | 36.3498 | 36.3238 | 33.2775 | 93.7223 | 93.9321 | 93.3809
2022-09-08 04:24 | 6:34 | 34.7176 | 31.719 | 33.3351 | 36.3948 | 34.3268 | 33.7829 | 34.5154 | 35.3819 | 36.4208 | 37.3326 | 36.8827 | 37.9968 | 34.2707 | 34.2651 | 33.9743 | 34.8913 | 34.808 | 35.4256 | 36.2516 | 36.4523 | 35.0013 | 31.8334 | 93.2055 | 35.2423 | 32.8745 | 34.8445 | 33.0563 | 32.9566 | 33.285 | 34.6476 | 34.1889 | 33.9136 | 37.0879 | 36.1399 | 33.2792 | 34.3151 | 36.138 | 36.437 | 37.2672 | 36.1329 | 33.0596 | 32.4868 | 34.3785 | 34.7722 | 32.9993 | 34.2222 | 34.4054 | 34.3552 | 34.3806 | 34.351 | 34.2462 | 33.8794 | 34.3693 | 35.9284 | 35.0099 | 36.3747 | 36.3337 | 33.3083 | 93.6636 | 93.8253 | 93.2976
2022-09-08 04:24 | 6:34 | 33.6654 | 31.7274 | 33.3084 | 36.3207 | 34.3219 | 33.7757 | 34.5145 | 35.3754 | 36.4384 | 37.3239 | 36.9028 | 38.0036 | 34.2944 | 34.2621 | 33.9849 | 34.9204 | 34.802 | 35.4426 | 36.2863 | 36.4578 | 34.975 | 31.8446 | 93.1804 | 35.3027 | 32.8912 | 34.8535 | 33.0578 | 32.9741 | 33.2829 | 34.6424 | 34.1753 | 33.9193 | 37.1013 | 36.1292 | 33.2772 | 34.3142 | 36.1433 | 36.4492 | 37.2926 | 36.1273 | 33.0764 | 32.4928 | 34.4058 | 34.7681 | 33.0167 | 34.2036 | 34.39 | 34.3319 | 34.3865 | 34.3601 | 34.2474 | 33.8852 | 34.3806 | 35.9638 | 35.02 | 36.367 | 36.3183 | 33.3102 | 93.5388 | 93.7502 | 93.2354
2022-09-08 04:24 | 6:34 | 33.471 | 31.7315 | 33.342 | 36.2895 | 34.3088 | 33.7946 | 34.526 | 35.3955 | 36.4357 | 37.3389 | 36.8825 | 38.0034 | 34.2814 | 34.27 | 33.9922 | 34.9113 | 34.7956 | 35.4278 | 36.2711 | 36.4576 | 34.9588 | 31.8463 | 93.1318 | 35.3345 | 32.8831 | 34.8526 | 33.0684 | 32.9737 | 33.2837 | 34.6514 | 34.1997 | 33.9284 | 37.095 | 36.1549 | 33.2849 | 34.3179 | 36.1399 | 36.4398 | 37.2953 | 36.137 | 33.0612 | 32.5122 | 34.3815 | 34.77 | 33.0458 | 34.2465 | 34.3894 | 34.3425 | 34.3695 | 34.3682 | 34.2508 | 33.8839 | 34.3865 | 35.9504 | 34.9907 | 36.3592 | 36.3321 | 33.2912 | 93.4774 | 93.6867 | 93.2042
2022-09-08 04:24 | 6:34 | 33.4283 | 31.7502 | 33.3715 | 36.4028 | 34.3074 | 33.7873 | 34.5074 | 35.3632 | 36.4147 | 37.3424 | 36.8869 | 38.0066 | 34.296 | 34.2677 | 33.9904 | 34.895 | 34.7976 | 35.4463 | 36.2677 | 36.4618 | 35.0175 | 31.8358 | 92.999 | 35.3138 | 32.9024 | 34.8283 | 33.0483 | 32.9718 | 33.2968 | 34.6472 | 34.1988 | 33.9153 | 37.0897 | 36.1766 | 33.2885 | 34.3374 | 36.1292 | 36.4413 | 37.2897 | 36.138 | 33.0736 | 32.5116 | 34.3968 | 34.7587 | 33.0388 | 34.2557 | 34.389 | 34.3407 | 34.3931 | 34.3592 | 34.2349 | 33.8867 | 34.3695 | 35.9473 | 34.9919 | 36.3634 | 36.3351 | 33.2967 | 93.4657 | 93.624 | 93.2248
2022-09-08 04:24 | 6:34 | 33.4685 | 31.7567 | 33.4013 | 36.3864 | 34.3091 | 33.8099 | 34.5261 | 35.3735 | 36.4328 | 37.3354 | 36.8993 | 38.0074 | 34.2778 | 34.2653 | 34.0019 | 34.9157 | 34.8015 | 35.4386 | 36.2706 | 36.4584 | 35.0496 | 31.8444 | 93.0306 | 35.3287 | 32.9037 | 34.8489 | 33.0596 | 32.9726 | 33.2792 | 34.6592 | 34.2041 | 33.9253 | 37.0964 | 36.1505 | 33.2951 | 34.3159 | 36.1549 | 36.4462 | 37.2889 | 36.1433 | 33.0726 | 32.5174 | 34.3906 | 34.7608 | 33.0453 | 34.2392 | 34.3754 | 34.3325 | 34.3943 | 34.3334 | 34.2412 | 33.8792 | 34.3931 | 35.929 | 35.0044 | 36.363 | 36.3458 | 33.305 | 93.4357 | 93.5798 | 93.2233
2022-09-08 04:24 | 6:34 | 33.4947 | 31.7566 | 33.4173 | 36.3374 | 34.2994 | 33.8021 | 34.5256 | 35.3856 | 36.4234 | 37.354 | 36.8947 | 38.002 | 34.2818 | 34.2663 | 33.994 | 34.9064 | 34.8011 | 35.4366 | 36.2829 | 36.4544 | 35.0983 | 31.8593 | 92.9864 | 35.4098 | 32.9062 | 34.8647 | 33.0764 | 32.9886 | 33.2772 | 34.6421 | 34.1834 | 33.925 | 37.1103 | 36.1705 | 33.2969 | 34.3263 | 36.1766 | 36.4531 | 37.2876 | 36.1399 | 33.0923 | 32.529 | 34.4095 | 34.7972 | 33.0568 | 34.2272 | 34.4017 | 34.334 | 34.3859 | 34.3646 | 34.2477 | 33.8835 | 34.3943 | 35.9383 | 35.0061 | 36.3684 | 36.3277 | 33.3056 | 93.3705 | 93.5376 | 93.211
2022-09-08 04:25 | 6:34 | 33.587 | 31.7729 | 33.4677 | 36.3764 | 34.3144 | 33.8106 | 34.5243 | 35.3764 | 36.422 | 37.3581 | 36.8887 | 38.0046 | 34.2649 | 34.2742 | 33.989 | 34.9142 | 34.8205 | 35.4266 | 36.2764 | 36.4676 | 35.2376 | 31.8687 | 92.8237 | 35.3781 | 32.9007 | 34.8643 | 33.0612 | 32.9896 | 33.2849 | 34.6454 | 34.203 | 33.9366 | 37.1004 | 36.1486 | 33.2822 | 34.3431 | 36.1505 | 36.427 | 37.3073 | 36.1292 | 33.0898 | 32.5232 | 34.4184 | 34.7838 | 33.0663 | 34.2286 | 34.391 | 34.3285 | 34.3905 | 34.3543 | 34.249 | 33.8909 | 34.3859 | 35.9499 | 34.9969 | 36.3708 | 36.3418 | 33.3102 | 93.2856 | 93.4421 | 93.078
2022-09-08 04:25 | 6:35 | 33.7037 | 31.7944 | 33.5122 | 36.3999 | 34.299 | 33.7936 | 34.5341 | 35.3822 | 36.43 | 37.3563 | 36.9008 | 38.0167 | 34.2739 | 34.2957 | 34.0056 | 34.9057 | 34.8086 | 35.4528 | 36.2649 | 36.4637 | 35.313 | 31.8883 | 92.8077 | 35.4201 | 32.9145 | 34.8626 | 33.0736 | 32.9862 | 33.2885 | 34.6488 | 34.1938 | 33.921 | 37.0961 | 36.1639 | 33.2867 | 34.3254 | 36.1705 | 36.4541 | 37.306 | 36.1549 | 33.0866 | 32.5393 | 34.4104 | 34.781 | 33.0731 | 34.2417 | 34.3897 | 34.3383 | 34.4121 | 34.3653 | 34.252 | 33.8746 | 34.3905 | 35.9333 | 35.0127 | 36.361 | 36.3607 | 33.3113 | 93.1806 | 93.3497 | 92.9942
2022-09-08 04:25 | 6:35 | 33.9127 | 31.793 | 33.5622 | 36.4347 | 34.2968 | 33.819 | 34.5322 | 35.4015 | 36.4382 | 37.3576 | 36.9033 | 37.987 | 34.2853 | 34.2737 | 33.9957 | 34.919 | 34.7963 | 35.4646 | 36.2634 | 36.4689 | 35.3498 | 31.9025 | 92.7883 | 35.4213 | 32.905 | 34.8769 | 33.0726 | 32.9741 | 33.2951 | 34.6409 | 34.2083 | 33.9082 | 37.1124 | 36.1767 | 33.2886 | 34.338 | 36.1486 | 36.4383 | 37.3184 | 36.1766 | 33.0751 | 32.5288 | 34.4303 | 34.7862 | 33.0908 | 34.2426 | 34.4178 | 34.3337 | 34.3987 | 34.3484 | 34.2547 | 33.9129 | 34.4121 | 35.95 | 35.0009 | 36.3702 | 36.3342 | 33.3302 | 93.1186 | 93.3003 | 93.0242
2022-09-08 04:25 | 6:35 | 34.6675 | 31.8371 | 33.5864 | 36.46 | 34.3193 | 33.8028 | 34.525 | 35.3865 | 36.4427 | 37.3645 | 36.912 | 38.028 | 34.2891 | 34.2621 | 34.0142 | 34.9276 | 34.809 | 35.4482 | 36.2848 | 36.4672 | 35.4113 | 31.9169 | 92.7029 | 35.412 | 32.9182 | 34.8849 | 33.0923 | 32.9942 | 33.2969 | 34.6369 | 34.2075 | 33.9211 | 37.1029 | 36.1743 | 33.317 | 34.3367 | 36.1639 | 36.4426 | 37.3197 | 36.1505 | 33.1001 | 32.5556 | 34.4313 | 34.8066 | 33.0995 | 34.2332 | 34.3883 | 34.323 | 34.4099 | 34.3619 | 34.252 | 33.8913 | 34.3987 | 35.9563 | 35.0036 | 36.3758 | 36.3331 | 33.3139 | 93.0431 | 93.2274 | 92.9733
2022-09-08 04:25 | 6:35 | 35.2438 | 31.8312 | 33.6344 | 36.4789 | 34.2921 | 33.8055 | 34.5531 | 35.4041 | 36.4466 | 37.3591 | 36.9045 | 38.0234 | 34.2936 | 34.2724 | 34.0134 | 34.9153 | 34.8127 | 35.4507 | 36.2818 | 36.4714 | 35.4646 | 31.9385 | 92.6511 | 35.4273 | 32.9135 | 34.8801 | 33.0898 | 32.9769 | 33.2822 | 34.6535 | 34.2056 | 33.9258 | 37.1111 | 36.1576 | 33.2973 | 34.3375 | 36.1767 | 36.444 | 37.3066 | 36.1705 | 33.0925 | 32.56 | 34.4338 | 34.7989 | 33.1144 | 34.2406 | 34.3888 | 34.3129 | 34.4176 | 34.3503 | 34.2461 | 33.9051 | 34.4099 | 35.9582 | 35.0098 | 36.3614 | 36.3558 | 33.3322 | 92.9372 | 93.139 | 92.841
2022-09-08 04:25 | 6:35 | 35.5144 | 31.8626 | 33.7271 | 36.4753 | 34.2805 | 33.8028 | 34.5291 | 35.4057 | 36.4297 | 37.3704 | 36.9034 | 38.0206 | 34.2927 | 34.27 | 34.0165 | 34.9013 | 34.8096 | 35.4627 | 36.297 | 36.4685 | 35.4879 | 31.9549 | 92.6077 | 35.3989 | 32.915 | 34.8751 | 33.0866 | 32.9667 | 33.2867 | 34.6653 | 34.2128 | 33.9429 | 37.112 | 36.1854 | 33.3102 | 34.3415 | 36.1743 | 36.4521 | 37.3216 | 36.1486 | 33.0861 | 32.5602 | 34.4416 | 34.8155 | 33.1106 | 34.2448 | 34.3921 | 34.3253 | 34.4144 | 34.3664 | 34.2366 | 33.9081 | 34.4176 | 35.9742 | 35.0068 | 36.3846 | 36.3567 | 33.3353 | 92.7796 | 93.0747 | 92.8133
2022-09-08 04:26 | 6:36 | 35.6327 | 31.9031 | 33.7545 | 36.4962 | 34.2961 | 33.806 | 34.5299 | 35.3986 | 36.4386 | 37.3889 | 36.9041 | 38.021 | 34.2907 | 34.2821 | 34.0268 | 34.9218 | 34.8248 | 35.4607 | 36.2877 | 36.463 | 35.468 | 31.9619 | 92.608 | 35.4716 | 32.9327 | 34.8771 | 33.0751 | 32.9975 | 33.2886 | 34.6439 | 34.1964 | 33.9559 | 37.1313 | 36.1783 | 33.3033 | 34.3299 | 36.1576 | 36.435 | 37.3195 | 36.1639 | 33.0952 | 32.5766 | 34.427 | 34.837 | 33.125 | 34.2515 | 34.3827 | 34.3222 | 34.4039 | 34.3669 | 34.2515 | 33.9113 | 34.4144 | 35.9762 | 35.0008 | 36.3751 | 36.3466 | 33.3312 | 92.6902 | 93.0215 | 92.7911
2022-09-08 04:26 | 6:36 | 35.727 | 31.9137 | 33.8445 | 36.4702 | 34.2845 | 33.8099 | 34.535 | 35.395 | 36.446 | 37.3574 | 36.9216 | 38.0102 | 34.2996 | 34.2861 | 34.0199 | 34.9182 | 34.8181 | 35.4628 | 36.2918 | 36.4802 | 35.4643 | 31.993 | 92.5652 | 35.4585 | 32.9246 | 34.8781 | 33.1001 | 33.004 | 33.317 | 34.6412 | 34.2267 | 33.9381 | 37.1292 | 36.1553 | 33.2883 | 34.3473 | 36.1854 | 36.4463 | 37.3324 | 36.1767 | 33.0973 | 32.5689 | 34.4602 | 34.8406 | 33.1393 | 34.2489 | 34.3639 | 34.3077 | 34.413 | 34.3692 | 34.2602 | 33.9272 | 34.4039 | 35.9858 | 35.0112 | 36.3692 | 36.3514 | 33.3352 | 92.6435 | 92.8723 | 92.6982
2022-09-08 04:26 | 6:36 | 35.7652 | 31.9244 | 33.9825 | 36.6013 | 34.2917 | 33.8179 | 34.5499 | 35.3989 | 36.4498 | 37.3685 | 36.8978 | 37.9998 | 34.3058 | 34.2656 | 34.0156 | 34.9355 | 34.8149 | 35.4663 | 36.2868 | 36.4854 | 35.5192 | 31.9847 | 92.4171 | 35.531 | 32.9357 | 34.8931 | 33.0925 | 33.0021 | 33.2973 | 34.6548 | 34.1939 | 33.9258 | 37.1069 | 36.1839 | 33.29 | 34.3338 | 36.1783 | 36.4511 | 37.3241 | 36.1743 | 33.0967 | 32.5836 | 34.4578 | 34.8613 | 33.11 | 34.2584 | 34.3606 | 34.3097 | 34.4088 | 34.3773 | 34.2486 | 33.9098 | 34.413 | 35.9664 | 35.0084 | 36.3618 | 36.3462 | 33.328 | 92.5115 | 92.7804 | 92.6105
2022-09-08 04:26 | 6:36 | 35.8217 | 31.9403 | 34.0968 | 36.5937 | 34.275 | 33.8111 | 34.533 | 35.4162 | 36.4571 | 37.3717 | 36.9115 | 38.0223 | 34.2985 | 34.2876 | 34.0264 | 34.9281 | 34.8339 | 35.4581 | 36.3086 | 36.4773 | 35.5364 | 32.0101 | 92.3883 | 35.4881 | 32.9471 | 34.8856 | 33.0861 | 33.0018 | 33.3102 | 34.6582 | 34.2094 | 33.9442 | 37.1247 | 36.1872 | 33.319 | 34.3598 | 36.1553 | 36.4694 | 37.3462 | 36.1576 | 33.0952 | 32.5909 | 34.4626 | 34.8467 | 33.1484 | 34.2592 | 34.3735 | 34.2916 | 34.4049 | 34.3742 | 34.2589 | 33.9104 | 34.4088 | 35.9601 | 35.0086 | 36.3733 | 36.355 | 33.3502 | 92.419 | 92.6504 | 92.4787
2022-09-08 04:26 | 6:36 | 35.8831 | 31.9569 | 34.2384 | 36.7139 | 34.2658 | 33.8099 | 34.5575 | 35.3973 | 36.4541 | 37.3957 | 36.9078 | 38.0036 | 34.3169 | 34.2844 | 34.0235 | 34.913 | 34.8354 | 35.4625 | 36.3076 | 36.4775 | 35.2976 | 31.9069 | 92.3454 | 35.4811 | 32.9318 | 34.8886 | 33.0952 | 32.9868 | 33.3033 | 34.6686 | 34.2385 | 33.9495 | 37.1468 | 36.1933 | 33.3061 | 34.3398 | 36.1839 | 36.4673 | 37.3175 | 36.1854 | 33.1002 | 32.5805 | 34.4716 | 34.8796 | 33.135 | 34.2644 | 34.3815 | 34.3064 | 34.4066 | 34.3805 | 34.2389 | 33.9093 | 34.4049 | 35.9912 | 35.0112 | 36.3668 | 36.3467 | 33.3701 | 92.3276 | 92.5409 | 92.5012
2022-09-08 04:26 | 6:36 | 31.1309 | 31.1303 | 33.3186 | 36.6082 | 34.2686 | 33.8269 | 34.5406 | 35.4151 | 36.4602 | 37.3868 | 36.8985 | 38.0183 | 34.2959 | 34.2697 | 34.0266 | 34.9259 | 34.8358 | 35.4547 | 36.3052 | 36.4912 | 30.4571 | 31.4467 | 92.2167 | 35.5483 | 32.9426 | 34.8713 | 33.0973 | 33.0129 | 33.2883 | 34.6711 | 34.2089 | 33.9481 | 37.1317 | 36.1731 | 33.2913 | 34.3366 | 36.1872 | 36.4797 | 37.3449 | 36.1783 | 33.0875 | 32.6271 | 34.4975 | 34.84 | 33.1651 | 34.2636 | 34.3729 | 34.3171 | 34.4155 | 34.3716 | 34.229 | 33.9181 | 34.4066 | 35.976 | 34.9852 | 36.3739 | 36.3487 | 33.3634 | 92.2006 | 92.4217 | 92.3717
2022-09-08 04:27 | 6:36 | 30.5633 | 30.1303 | 32.178 | 36.5637 | 34.2785 | 33.8107 | 34.559 | 35.3988 | 36.4654 | 37.3778 | 36.9274 | 38.0295 | 34.2938 | 34.2787 | 34.0271 | 34.9316 | 34.8394 | 35.4796 | 36.3013 | 36.5005 | 28.4876 | 29.4497 | 92.1418 | 35.3909 | 32.9493 | 34.8816 | 33.0967 | 33.0082 | 33.29 | 34.6731 | 34.2042 | 33.9342 | 37.127 | 36.1832 | 33.3031 | 34.3382 | 36.1933 | 36.4567 | 37.337 | 36.1553 | 33.105 | 32.5884 | 34.4944 | 34.8635 | 33.1638 | 34.249 | 34.3434 | 34.304 | 34.4052 | 34.3826 | 34.2635 | 33.9159 | 34.4155 | 35.9942 | 35.0002 | 36.3676 | 36.3694 | 33.3618 | 92.0526 | 92.2835 | 92.1421
2022-09-08 04:27 | 6:37 | 31.1536 | 28.9928 | 31.9481 | 36.5442 | 34.2701 | 33.8163 | 34.5787 | 35.4006 | 36.4716 | 37.4022 | 36.9154 | 38.0209 | 34.3121 | 34.2784 | 34.0414 | 34.9586 | 34.8285 | 35.4738 | 36.3008 | 36.4926 | 28.8401 | 28.2238 | 91.9292 | 35.2955 | 32.9387 | 34.9006 | 33.0952 | 33.0141 | 33.319 | 34.672 | 34.1977 | 33.9533 | 37.1309 | 36.1784 | 33.3249 | 34.3308 | 36.1731 | 36.4541 | 37.3468 | 36.1839 | 33.0899 | 32.63 | 34.4931 | 34.9012 | 33.1679 | 34.2604 | 34.3884 | 34.3302 | 34.4237 | 34.3757 | 34.2428 | 33.9283 | 34.4052 | 35.9925 | 35.0041 | 36.3847 | 36.3625 | 33.3574 | 91.9347 | 92.1704 | 92.1652
2022-09-08 04:27 | 6:37 | 31.4856 | 28.7148 | 31.9526 | 36.5227 | 34.2543 | 33.8167 | 34.5733 | 35.4175 | 36.4661 | 37.3902 | 36.9019 | 38.0309 | 34.3078 | 34.2751 | 34.0518 | 34.9282 | 34.8528 | 35.4637 | 36.2967 | 36.5149 | 29.0985 | 27.9162 | 91.8826 | 35.2812 | 32.952 | 34.9001 | 33.1002 | 32.989 | 33.3061 | 34.6638 | 34.2047 | 33.954 | 37.1321 | 36.1872 | 33.3083 | 34.3415 | 36.1832 | 36.468 | 37.3603 | 36.1872 | 33.1141 | 32.6262 | 34.492 | 34.8959 | 33.1578 | 34.2658 | 34.3738 | 34.3257 | 34.4104 | 34.3972 | 34.2258 | 33.9505 | 34.4237 | 36.0045 | 35.0086 | 36.3916 | 36.3674 | 33.3554 | 91.7803 | 92.0216 | 92.1941
2022-09-08 04:27 | 6:37 | 31.5365 | 28.3055 | 31.8512 | 36.4465 | 34.2664 | 33.8313 | 34.5949 | 35.4297 | 36.469 | 37.3934 | 36.9093 | 38.0443 | 34.3231 | 34.2755 | 34.0318 | 34.9382 | 34.8516 | 35.4892 | 36.2942 | 36.5126 | 29.4573 | 26.9618 | 91.8954 | 35.3343 | 32.942 | 34.896 | 33.0875 | 32.9928 | 33.2913 | 34.6581 | 34.2238 | 33.9674 | 37.1349 | 36.2 | 33.3177 | 34.3707 | 36.1784 | 36.4747 | 37.3326 | 36.1933 | 33.0905 | 32.6121 | 34.4931 | 34.8847 | 33.1681 | 34.2647 | 34.3652 | 34.3133 | 34.4256 | 34.4101 | 34.2403 | 33.9586 | 34.4104 | 35.982 | 35.0186 | 36.3883 | 36.3851 | 33.3579 | 91.7497 | 91.9295 | 92.1633
2022-09-08 04:27 | 6:37 | 31.5117 | 28.0833 | 31.8475 | 36.5047 | 34.2804 | 33.8044 | 34.5831 | 35.4155 | 36.4648 | 37.4028 | 36.9158 | 38.0339 | 34.3181 | 34.2747 | 34.0665 | 34.9389 | 34.8474 | 35.4619 | 36.3067 | 36.5082 | 29.7413 | 26.4653 | 91.8106 | 35.2848 | 32.9509 | 34.9079 | 33.105 | 33.0163 | 33.3031 | 34.661 | 34.1968 | 33.9464 | 37.1313 | 36.1943 | 33.3282 | 34.3491 | 36.1872 | 36.484 | 37.3563 | 36.1731 | 33.1129 | 32.6083 | 34.5061 | 34.8921 | 33.1598 | 34.2524 | 34.3593 | 34.3169 | 34.4147 | 34.3942 | 34.2407 | 33.9274 | 34.4256 | 35.9868 | 34.9718 | 36.378 | 36.3572 | 33.3775 | 91.6132 | 91.7977 | 92.0892
2022-09-08 04:27 | 6:37 | 31.4346 | 27.905 | 31.5986 | 36.5228 | 34.2507 | 33.8139 | 34.6193 | 35.431 | 36.4706 | 37.3954 | 36.91 | 38.0525 | 34.3252 | 34.277 | 34.0598 | 34.9249 | 34.8585 | 35.475 | 36.3269 | 36.5058 | 29.8451 | 26.1934 | 91.7377 | 35.2987 | 32.9646 | 34.9009 | 33.0899 | 32.9932 | 33.3249 | 34.6628 | 34.1917 | 33.951 | 37.1623 | 36.1864 | 33.3269 | 34.3428 | 36.2 | 36.4607 | 37.3484 | 36.1832 | 33.1103 | 32.6277 | 34.5239 | 34.8905 | 33.1531 | 34.2657 | 34.3494 | 34.2931 | 34.4178 | 34.3994 | 34.2518 | 33.9477 | 34.4147 | 35.9953 | 35.0203 | 36.3694 | 36.3747 | 33.3751 | 91.508 | 91.718 | 92.0624
2022-09-08 04:28 | 6:38 | 31.3408 | 27.8368 | 31.5225 | 36.5145 | 34.2644 | 33.8218 | 34.6121 | 35.4238 | 36.4772 | 37.4032 | 36.9231 | 38.0354 | 34.3314 | 34.2969 | 34.0726 | 34.9291 | 34.8685 | 35.4753 | 36.2991 | 36.5138 | 29.8427 | 25.9874 | 91.6246 | 35.2399 | 32.9559 | 34.8788 | 33.1141 | 32.999 | 33.3083 | 34.6697 | 34.2067 | 33.9552 | 37.1378 | 36.1974 | 33.3233 | 34.3409 | 36.1943 | 36.469 | 37.3274 | 36.1784 | 33.0984 | 32.617 | 34.5276 | 34.8849 | 33.1711 | 34.2619 | 34.3707 | 34.3144 | 34.4085 | 34.4098 | 34.2593 | 33.953 | 34.4178 | 36.0146 | 35.0235 | 36.3872 | 36.3715 | 33.3943 | 91.4342 | 91.6715 | 91.996
2022-09-08 04:28 | 6:38 | 31.197 | 27.8417 | 31.4822 | 36.5694 | 34.2642 | 33.8188 | 34.6157 | 35.4326 | 36.4639 | 37.3954 | 36.9104 | 38.0573 | 34.2991 | 34.2686 | 34.0434 | 34.9245 | 34.8762 | 35.4706 | 36.3084 | 36.5123 | 29.6974 | 25.8865 | 91.6623 | 35.2415 | 32.9556 | 34.897 | 33.0905 | 33.0274 | 33.3177 | 34.6726 | 34.2091 | 33.9569 | 37.1542 | 36.1932 | 33.3008 | 34.3559 | 36.1864 | 36.4753 | 37.3793 | 36.1872 | 33.0874 | 32.6278 | 34.5126 | 34.898 | 33.1628 | 34.2921 | 34.3494 | 34.304 | 34.4113 | 34.3983 | 34.2651 | 33.9431 | 34.4085 | 36.0067 | 35.0134 | 36.3893 | 36.3624 | 33.3837 | 91.5216 | 91.7437 | 92.1216
2022-09-08 04:28 | 6:38 | 31.056 | 27.8482 | 31.3812 | 36.579 | 34.2582 | 33.8177 | 34.6446 | 35.4192 | 36.4743 | 37.3836 | 36.9001 | 38.0135 | 34.3191 | 34.2753 | 34.0348 | 34.9406 | 34.8571 | 35.4647 | 36.3112 | 36.5163 | 29.5361 | 25.7147 | 91.7885 | 35.1888 | 32.947 | 34.889 | 33.1129 | 33.0119 | 33.3282 | 34.6625 | 34.2159 | 33.9421 | 37.1503 | 36.2003 | 33.3229 | 34.3298 | 36.1974 | 36.4787 | 37.3784 | 36.2 | 33.1185 | 32.6483 | 34.5032 | 34.9131 | 33.1819 | 34.2835 | 34.354 | 34.3186 | 34.4305 | 34.4123 | 34.2621 | 33.9445 | 34.4113 | 35.9927 | 35.0038 | 36.3757 | 36.3789 | 33.3987 | 91.6677 | 91.8111 | 92.1924
2022-09-08 04:28 | 6:38 | 30.7698 | 27.766 | 31.1073 | 36.5504 | 34.254 | 33.8111 | 34.6343 | 35.4183 | 36.4723 | 37.4014 | 36.9063 | 38.0385 | 34.3173 | 34.3039 | 34.0754 | 34.9482 | 34.8558 | 35.4681 | 36.3077 | 36.5221 | 29.3918 | 25.5873 | 91.8902 | 35.1447 | 32.9478 | 34.9061 | 33.1103 | 32.9969 | 33.3269 | 34.6633 | 34.2223 | 33.9451 | 37.1315 | 36.1882 | 33.3165 | 34.3567 | 36.1932 | 36.4588 | 37.3648 | 36.1943 | 33.1172 | 32.6419 | 34.52 | 34.9115 | 33.1557 | 34.2763 | 34.3477 | 34.3119 | 34.4197 | 34.4114 | 34.27 | 33.9619 | 34.4305 | 36.0258 | 35 | 36.3774 | 36.3848 | 33.385 | 91.7946 | 91.9291 | 92.1846
2022-09-08 04:28 | 6:38 | 30.042 | 27.7228 | 30.6385 | 36.5135 | 34.2614 | 33.8115 | 34.6451 | 35.43 | 36.4796 | 37.3962 | 36.8875 | 38.0251 | 34.3165 | 34.3025 | 34.0515 | 34.9368 | 34.8704 | 35.4694 | 36.2854 | 36.5185 | 29.2277 | 25.4072 | 91.8757 | 35.0544 | 32.9769 | 34.9058 | 33.0984 | 32.9868 | 33.3233 | 34.6875 | 34.2073 | 33.9439 | 37.1409 | 36.2019 | 33.3034 | 34.3502 | 36.2003 | 36.4754 | 37.3747 | 36.1864 | 33.089 | 32.6425 | 34.5321 | 34.9177 | 33.1729 | 34.2662 | 34.3478 | 34.3025 | 34.4433 | 34.4269 | 34.2677 | 33.9522 | 34.4197 | 36.0311 | 34.997 | 36.3861 | 36.3667 | 33.3977 | 91.8863 | 92.0339 | 92.2774
2022-09-08 04:28 | 6:38 | 26.8319 | 27.6357 | 30.0543 | 36.5764 | 34.2462 | 33.8213 | 34.6569 | 35.4528 | 36.4811 | 37.3888 | 36.9049 | 38.029 | 34.3 | 34.2992 | 34.0622 | 34.928 | 34.8755 | 35.4678 | 36.3062 | 36.5231 | 29.0826 | 25.272 | 91.8838 | 35.0913 | 32.9517 | 34.9002 | 33.0874 | 33.0036 | 33.3008 | 34.6758 | 34.1938 | 33.9597 | 37.134 | 36.1972 | 33.3142 | 34.354 | 36.1882 | 36.481 | 37.3705 | 36.1974 | 33.1062 | 32.6467 | 34.5353 | 34.8919 | 33.1624 | 34.2883 | 34.3526 | 34.3256 | 34.4169 | 34.4099 | 34.2653 | 33.9751 | 34.4433 | 36.0051 | 34.9843 | 36.381 | 36.3835 | 33.3974 | 91.9874 | 92.1472 | 92.3226
2022-09-08 04:29 | 6:38 | 26.1462 | 27.3171 | 29.514 | 36.4729 | 34.2474 | 33.8175 | 34.6396 | 35.4334 | 36.463 | 37.3977 | 36.8974 | 38.0311 | 34.325 | 34.2896 | 34.0688 | 34.9312 | 34.8672 | 35.4514 | 36.2968 | 36.5197 | 28.9027 | 25.1532 | 92.1054 | 35.1711 | 32.9617 | 34.9021 | 33.1185 | 32.9956 | 33.3229 | 34.6658 | 34.196 | 33.9509 | 37.1341 | 36.1838 | 33.3042 | 34.3389 | 36.2019 | 36.4679 | 37.3718 | 36.1932 | 33.1094 | 32.6498 | 34.5265 | 34.9236 | 33.1772 | 34.2702 | 34.3511 | 34.308 | 34.4257 | 34.4132 | 34.2663 | 33.971 | 34.4169 | 36.0244 | 34.988 | 36.3969 | 36.3862 | 33.4009 | 92.2048 | 92.2352 | 92.4303
2022-09-08 04:29 | 6:39 | 25.8935 | 27.1279 | 29.3268 | 36.5436 | 34.2508 | 33.8127 | 34.6657 | 35.445 | 36.4836 | 37.3922 | 36.8924 | 38.0191 | 34.3387 | 34.3013 | 34.0658 | 34.951 | 34.8835 | 35.4963 | 36.2984 | 36.5316 | 28.731 | 25.0083 | 92.1093 | 35.0903 | 32.9626 | 34.9159 | 33.1172 | 33.0111 | 33.3165 | 34.6812 | 34.1862 | 33.9438 | 37.1344 | 36.1862 | 33.3176 | 34.3392 | 36.1972 | 36.4605 | 37.3785 | 36.2003 | 33.0922 | 32.6416 | 34.5119 | 34.9117 | 33.1751 | 34.2901 | 34.3259 | 34.3271 | 34.4334 | 34.4238 | 34.2742 | 33.9606 | 34.4257 | 36.0042 | 34.9954 | 36.3653 | 36.3709 | 33.4145 | 92.27 | 92.4228 | 92.4135
2022-09-08 04:29 | 6:39 | 25.5634 | 26.8312 | 29.025 | 36.3242 | 34.2349 | 33.8056 | 34.643 | 35.4378 | 36.481 | 37.3963 | 36.8683 | 38.0029 | 34.3204 | 34.2854 | 34.0717 | 34.928 | 34.8744 | 35.468 | 36.3106 | 36.5299 | 28.5509 | 24.9238 | 92.2894 | 34.9561 | 32.9414 | 34.8914 | 33.089 | 32.9883 | 33.3034 | 34.6702 | 34.1788 | 33.944 | 37.1331 | 36.184 | 33.3139 | 34.3468 | 36.1838 | 36.4622 | 37.3733 | 36.1882 | 33.0832 | 32.6491 | 34.5058 | 34.9019 | 33.1627 | 34.2698 | 34.3255 | 34.3227 | 34.4252 | 34.4121 | 34.2957 | 33.9731 | 34.4334 | 36.0074 | 34.9965 | 36.3786 | 36.3703 | 33.3977 | 92.4437 | 92.6234 | 92.5148
2022-09-08 04:29 | 6:39 | 25.2606 | 26.5423 | 28.7681 | 36.4061 | 34.2412 | 33.7998 | 34.6414 | 35.4476 | 36.4964 | 37.4052 | 36.9027 | 38.0234 | 34.3322 | 34.2937 | 34.0628 | 34.9291 | 34.8619 | 35.4527 | 36.2972 | 36.5125 | 28.3413 | 24.772 | 92.4594 | 35.0215 | 32.9411 | 34.8898 | 33.1062 | 33.0019 | 33.3142 | 34.6668 | 34.1694 | 33.9473 | 37.1431 | 36.1752 | 33.325 | 34.3428 | 36.1862 | 36.4536 | 37.3918 | 36.2019 | 33.1026 | 32.6389 | 34.5149 | 34.8895 | 33.1468 | 34.2599 | 34.3294 | 34.3273 | 34.4299 | 34.4179 | 34.2737 | 33.9829 | 34.4252 | 35.9867 | 34.9979 | 36.3782 | 36.375 | 33.4023 | 92.6674 | 92.8216 | 92.6828
2022-09-08 04:29 | 6:39 | 25.0169 | 26.2411 | 28.5169 | 36.2435 | 34.2477 | 33.8117 | 34.6379 | 35.4396 | 36.4862 | 37.3901 | 36.8785 | 38.0214 | 34.3381 | 34.3034 | 34.0718 | 34.9268 | 34.8669 | 35.4545 | 36.2781 | 36.5294 | 28.1444 | 24.5862 | 92.6303 | 34.9621 | 32.9427 | 34.8859 | 33.1094 | 33.0082 | 33.3042 | 34.6815 | 34.1862 | 33.9478 | 37.1404 | 36.1915 | 33.3207 | 34.3346 | 36.184 | 36.4643 | 37.3815 | 36.1972 | 33.1104 | 32.6467 | 34.5011 | 34.9129 | 33.1736 | 34.2579 | 34.3144 | 34.3233 | 34.4195 | 34.4172 | 34.2621 | 33.9629 | 34.4299 | 36.0287 | 34.9809 | 36.3828 | 36.3772 | 33.407 | 92.9184 | 93.0659 | 92.8819
2022-09-08 04:29 | 6:39 | 24.8047 | 26.0164 | 28.2801 | 36.3189 | 34.249 | 33.7925 | 34.6461 | 35.4236 | 36.4901 | 37.3854 | 36.89 | 38.0093 | 34.3467 | 34.3116 | 34.0809 | 34.9263 | 34.8819 | 35.4566 | 36.2738 | 36.5253 | 27.9095 | 24.3832 | 92.7962 | 34.9457 | 32.9455 | 34.8974 | 33.0922 | 33.0008 | 33.3176 | 34.6765 | 34.1696 | 33.9342 | 37.1354 | 36.1914 | 33.3164 | 34.3193 | 36.1752 | 36.4635 | 37.3633 | 36.1838 | 33.0943 | 32.6722 | 34.5141 | 34.9085 | 33.1672 | 34.2835 | 34.3282 | 34.3017 | 34.4276 | 34.4247 | 34.2724 | 33.9566 | 34.4195 | 36.0001 | 34.9933 | 36.389 | 36.3895 | 33.4097 | 93.06 | 93.2599 | 92.9695
2022-09-08 04:30 | 6:40 | 24.6722 | 25.8365 | 28.0597 | 36.3945 | 34.252 | 33.8034 | 34.618 | 35.4237 | 36.479 | 37.3941 | 36.9013 | 38.0092 | 34.3486 | 34.3085 | 34.0816 | 34.9263 | 34.8777 | 35.4538 | 36.2751 | 36.5122 | 27.7397 | 24.293 | 92.9032 | 34.9161 | 32.9471 | 34.8882 | 33.0832 | 33.0089 | 33.3139 | 34.6812 | 34.1795 | 33.9254 | 37.1238 | 36.2049 | 33.3226 | 34.3234 | 36.1915 | 36.4696 | 37.3764 | 36.1862 | 33.112 | 32.6542 | 34.5192 | 34.909 | 33.1603 | 34.2687 | 34.3192 | 34.3313 | 34.4221 | 34.426 | 34.27 | 33.9648 | 34.4276 | 36.0017 | 34.9949 | 36.4024 | 36.3798 | 33.4028 | 93.2364 | 93.4784 | 93.0311
2022-09-08 04:30 | 6:40 | 24.4235 | 25.5828 | 27.9152 | 36.3067 | 34.2547 | 33.7847 | 34.6398 | 35.4157 | 36.501 | 37.3937 | 36.8773 | 38.026 | 34.3317 | 34.3157 | 34.0828 | 34.9374 | 34.8541 | 35.4544 | 36.2792 | 36.529 | 27.6327 | 24.1078 | 92.9606 | 34.8727 | 32.9562 | 34.8817 | 33.1026 | 33.0037 | 33.325 | 34.6671 | 34.1831 | 33.9397 | 37.1284 | 36.1923 | 33.3117 | 34.3165 | 36.1914 | 36.4674 | 37.3903 | 36.184 | 33.0994 | 32.6788 | 34.4981 | 34.9034 | 33.1454 | 34.2935 | 34.3273 | 34.3329 | 34.4092 | 34.4326 | 34.2821 | 33.982 | 34.4221 | 36.0166 | 34.9946 | 36.3694 | 36.3676 | 33.4101 | 93.3317 | 93.6512 | 93.0267
2022-09-08 04:30 | 6:40 | 24.2337 | 25.3698 | 27.7382 | 36.2633 | 34.252 | 33.8028 | 34.6173 | 35.44 | 36.4911 | 37.396 | 36.893 | 38.0161 | 34.3325 | 34.3132 | 34.0837 | 34.9383 | 34.892 | 35.4444 | 36.2776 | 36.5212 | 27.3946 | 24.0083 | 93.0985 | 34.8227 | 32.9626 | 34.8978 | 33.1104 | 32.9866 | 33.3207 | 34.6625 | 34.1783 | 33.9362 | 37.1302 | 36.186 | 33.316 | 34.3191 | 36.2049 | 36.4548 | 37.3696 | 36.1752 | 33.123 | 32.6395 | 34.5224 | 34.9187 | 33.1771 | 34.2831 | 34.3116 | 34.3225 | 34.4068 | 34.4374 | 34.2861 | 33.9721 | 34.4092 | 36.0246 | 34.9809 | 36.3687 | 36.3912 | 33.3844 | 93.5367 | 93.8953 | 93.2835
2022-09-08 04:30 | 6:40 | 24.1383 | 25.1801 | 27.5021 | 36.2791 | 34.2461 | 33.7804 | 34.6215 | 35.419 | 36.4793 | 37.3987 | 36.9021 | 38.0148 | 34.3365 | 34.311 | 34.0803 | 34.9301 | 34.8602 | 35.4502 | 36.262 | 36.519 | 27.1561 | 23.7935 | 93.2778 | 34.8803 | 32.9437 | 34.8962 | 33.0943 | 32.9946 | 33.3164 | 34.6711 | 34.1818 | 33.9291 | 37.156 | 36.1926 | 33.3202 | 34.3288 | 36.1923 | 36.4588 | 37.4007 | 36.1915 | 33.0934 | 32.6829 | 34.5071 | 34.9041 | 33.1646 | 34.2733 | 34.3166 | 34.313 | 34.42 | 34.443 | 34.2656 | 33.9853 | 34.4068 | 36.0091 | 34.9865 | 36.4003 | 36.3785 | 33.4113 | 93.7011 | 94.0969 | 93.398
2022-09-08 04:30 | 6:40 | 23.8555 | 24.9608 | 27.4012 | 36.1875 | 34.2366 | 33.7946 | 34.6403 | 35.426 | 36.4979 | 37.3902 | 36.8882 | 38.0121 | 34.3537 | 34.3103 | 34.0987 | 34.9147 | 34.8635 | 35.4256 | 36.2787 | 36.5208 | 26.8661 | 23.6014 | 93.4037 | 34.8425 | 32.9608 | 34.8871 | 33.112 | 32.9879 | 33.3226 | 34.6808 | 34.1638 | 33.9295 | 37.1336 | 36.1843 | 33.32 | 34.3184 | 36.186 | 36.4665 | 37.4029 | 36.1914 | 33.1222 | 32.6664 | 34.4907 | 34.9101 | 33.1337 | 34.27 | 34.3075 | 34.3182 | 34.4177 | 34.4445 | 34.2876 | 33.9752 | 34.42 | 35.9898 | 34.9814 | 36.392 | 36.3788 | 33.4032 | 93.9856 | 94.3292 | 93.5787
2022-09-08 04:30 | 6:40 | 23.7162 | 24.7219 | 27.2302 | 36.1135 | 34.2515 | 33.7886 | 34.6337 | 35.4218 | 36.4953 | 37.3934 | 36.8935 | 38.0086 | 34.3381 | 34.3166 | 34.0683 | 34.9202 | 34.8559 | 35.4365 | 36.257 | 36.5226 | 26.5728 | 23.4715 | 93.5133 | 34.7056 | 32.9499 | 34.8938 | 33.0994 | 33.0031 | 33.3117 | 34.668 | 34.1621 | 33.9455 | 37.1469 | 36.1964 | 33.3017 | 34.3204 | 36.1926 | 36.4529 | 37.3917 | 36.2049 | 33.0973 | 32.6543 | 34.4927 | 34.8979 | 33.1556 | 34.2664 | 34.3067 | 34.338 | 34.4024 | 34.4303 | 34.2844 | 33.9566 | 34.4177 | 36.0047 | 34.9813 | 36.3914 | 36.4033 | 33.4086 | 94.1314 | 94.5209 | 93.6541
2022-09-08 04:31 | 6:40 | 23.621 | 24.5612 | 27.1001 | 36.122 | 34.2602 | 33.7774 | 34.6353 | 35.4269 | 36.4942 | 37.3807 | 36.8983 | 38.0132 | 34.3456 | 34.3028 | 34.0906 | 34.9147 | 34.881 | 35.4372 | 36.2678 | 36.5222 | 26.2848 | 23.2844 | 93.618 | 34.7264 | 32.9609 | 34.8986 | 33.123 | 32.9796 | 33.316 | 34.6743 | 34.1649 | 33.9404 | 37.1406 | 36.1868 | 33.3151 | 34.313 | 36.1843 | 36.4668 | 37.4064 | 36.1923 | 33.1147 | 32.6518 | 34.5031 | 34.9061 | 33.1497 | 34.2876 | 34.2951 | 34.3344 | 34.4244 | 34.4451 | 34.2697 | 33.9552 | 34.4024 | 36.0085 | 34.9837 | 36.3736 | 36.3782 | 33.4008 | 94.2949 | 94.7235 | 93.7193
2022-09-08 04:31 | 6:41 | 23.4008 | 24.3353 | 26.9057 | 36.0645 | 34.2486 | 33.7823 | 34.6304 | 35.4273 | 36.4852 | 37.3902 | 36.8756 | 38.0095 | 34.351 | 34.3171 | 34.0788 | 34.9325 | 34.8855 | 35.4504 | 36.2353 | 36.522 | 26.0046 | 23.122 | 93.6814 | 34.7154 | 32.9619 | 34.886 | 33.0934 | 32.9746 | 33.3202 | 34.681 | 34.1532 | 33.9346 | 37.1217 | 36.1993 | 33.3031 | 34.3243 | 36.1964 | 36.4546 | 37.3936 | 36.186 | 33.1081 | 32.6681 | 34.4934 | 34.8918 | 33.1242 | 34.2728 | 34.2843 | 34.3374 | 34.4303 | 34.4376 | 34.2787 | 33.96 | 34.4244 | 36.0271 | 34.9953 | 36.3881 | 36.3771 | 33.4001 | 94.4943 | 94.9472 | 93.8339
2022-09-08 04:31 | 6:41 | 23.2518 | 24.1669 | 26.7691 | 36.0323 | 34.2589 | 33.8032 | 34.627 | 35.4097 | 36.4969 | 37.3929 | 36.8871 | 38.0084 | 34.3601 | 34.3077 | 34.0786 | 34.919 | 34.8811 | 35.4288 | 36.2558 | 36.5238 | 25.8418 | 22.9031 | 93.8396 | 34.6595 | 32.9477 | 34.8949 | 33.1222 | 32.9948 | 33.32 | 34.6788 | 34.1604 | 33.9387 | 37.1444 | 36.2147 | 33.3097 | 34.3232 | 36.1868 | 36.4567 | 37.4008 | 36.1926 | 33.1149 | 32.6484 | 34.5047 | 34.8971 | 33.1411 | 34.2819 | 34.2711 | 34.3303 | 34.3986 | 34.4296 | 34.2784 | 33.9941 | 34.4303 | 36.0139 | 34.9919 | 36.3849 | 36.381 | 33.3769 | 94.5889 | 95.0899 | 94.0409
2022-09-08 04:31 | 6:41 | 23.1117 | 24.0171 | 26.6389 | 36.0801 | 34.2389 | 33.786 | 34.6233 | 35.4125 | 36.4976 | 37.3937 | 36.8865 | 38.0133 | 34.3682 | 34.3141 | 34.0764 | 34.9163 | 34.8764 | 35.437 | 36.228 | 36.5177 | 25.6266 | 22.7613 | 94.0154 | 34.691 | 32.9546 | 34.9162 | 33.0973 | 32.9703 | 33.3017 | 34.6804 | 34.1716 | 33.939 | 37.132 | 36.2203 | 33.3044 | 34.2986 | 36.1993 | 36.4452 | 37.3671 | 36.1843 | 33.1061 | 32.6605 | 34.4956 | 34.8814 | 33.1223 | 34.2796 | 34.281 | 34.3228 | 34.4138 | 34.4382 | 34.2751 | 33.9773 | 34.3986 | 35.9948 | 34.9814 | 36.3893 | 36.392 | 33.3745 | 94.8134 | 95.2417 | 94.1597
2022-09-08 04:31 | 6:41 | 22.9188 | 23.843 | 26.452 | 36.0266 | 34.229 | 33.7762 | 34.6253 | 35.4055 | 36.4965 | 37.372 | 36.8912 | 38.0005 | 34.3592 | 34.308 | 34.0699 | 34.9282 | 34.8893 | 35.4381 | 36.2504 | 36.5006 | 25.3116 | 22.5912 | 94.1001 | 34.5892 | 32.9572 | 34.9011 | 33.1147 | 32.9942 | 33.3151 | 34.6421 | 34.1522 | 33.9398 | 37.126 | 36.2097 | 33.3067 | 34.2973 | 36.2147 | 36.4604 | 37.381 | 36.1964 | 33.1211 | 32.6563 | 34.4739 | 34.8961 | 33.1222 | 34.3035 | 34.2811 | 34.3372 | 34.4144 | 34.4312 | 34.2755 | 33.9808 | 34.4138 | 35.9971 | 34.9866 | 36.381 | 36.3987 | 33.3786 | 94.9035 | 95.3746 | 94.2116
2022-09-08 04:31 | 6:41 | 22.7595 | 23.6528 | 26.3049 | 35.9476 | 34.2635 | 33.7866 | 34.6263 | 35.4357 | 36.4876 | 37.3609 | 36.9145 | 38.0097 | 34.3334 | 34.3024 | 34.0939 | 34.9178 | 34.8774 | 35.4304 | 36.2353 | 36.5081 | 25.0135 | 22.4061 | 94.165 | 34.6123 | 32.9531 | 34.8984 | 33.1081 | 32.9829 | 33.3031 | 34.6588 | 34.1525 | 33.9262 | 37.1433 | 36.2048 | 33.3134 | 34.3051 | 36.2203 | 36.447 | 37.3771 | 36.1868 | 33.1318 | 32.6383 | 34.4794 | 34.8932 | 33.1355 | 34.3005 | 34.2883 | 34.3556 | 34.3916 | 34.4579 | 34.2747 | 33.9967 | 34.4144 | 35.97 | 34.9776 | 36.3742 | 36.3745 | 33.3928 | 95.0205 | 95.4954 | 94.2769
2022-09-08 04:32 | 6:41 | 22.6559 | 23.5487 | 26.1307 | 35.9498 | 34.2428 | 33.7898 | 34.6345 | 35.4116 | 36.4971 | 37.3652 | 36.8871 | 38.0233 | 34.3646 | 34.3274 | 34.0804 | 34.9274 | 34.8762 | 35.4261 | 36.2357 | 36.4901 | 24.7457 | 22.2385 | 94.1929 | 34.4729 | 32.9527 | 34.9017 | 33.1149 | 32.9813 | 33.3097 | 34.661 | 34.1683 | 33.9263 | 37.1235 | 36.2047 | 33.3082 | 34.3081 | 36.2097 | 36.4537 | 37.363 | 36.1993 | 33.1178 | 32.6568 | 34.4911 | 34.8976 | 33.1241 | 34.302 | 34.2546 | 34.3421 | 34.3969 | 34.4456 | 34.277 | 33.9759 | 34.3916 | 36.0171 | 34.9712 | 36.3921 | 36.365 | 33.3725 | 95.1064 | 95.5845 | 94.348
2022-09-08 04:32 | 6:42 | 22.4166 | 23.313 | 25.9315 | 35.9526 | 34.2258 | 33.7963 | 34.624 | 35.4174 | 36.5096 | 37.3681 | 36.8702 | 38.0118 | 34.3543 | 34.3311 | 34.0614 | 34.917 | 34.8775 | 35.4192 | 36.2156 | 36.4975 | 24.473 | 22.0712 | 94.2619 | 34.5279 | 32.9229 | 34.8993 | 33.1061 | 32.9727 | 33.3044 | 34.6455 | 34.1457 | 33.9432 | 37.1394 | 36.2163 | 33.3148 | 34.3066 | 36.2048 | 36.4305 | 37.3735 | 36.2147 | 33.1152 | 32.6412 | 34.4712 | 34.8758 | 33.1339 | 34.293 | 34.2671 | 34.3439 | 34.4054 | 34.4412 | 34.2969 | 33.9707 | 34.3969 | 36.0082 | 34.9973 | 36.3851 | 36.3641 | 33.3835 | 95.183 | 95.6654 | 94.4414
2022-09-08 04:32 | 6:42 | 22.2817 | 23.1253 | 25.8137 | 35.917 | 34.2403 | 33.7838 | 34.6067 | 35.4188 | 36.4995 | 37.3687 | 36.889 | 37.9928 | 34.3653 | 34.3401 | 34.0847 | 34.9235 | 34.8727 | 35.429 | 36.2373 | 36.4965 | 24.2385 | 21.9781 | 94.3045 | 34.6418 | 32.9389 | 34.9047 | 33.1211 | 32.97 | 33.3067 | 34.6591 | 34.1492 | 33.9218 | 37.1385 | 36.2179 | 33.2989 | 34.3098 | 36.2047 | 36.4556 | 37.3798 | 36.2203 | 33.1071 | 32.6473 | 34.4681 | 34.8717 | 33.1072 | 34.2838 | 34.2517 | 34.3364 | 34.39 | 34.4437 | 34.2686 | 33.975 | 34.4054 | 35.9929 | 34.9758 | 36.3683 | 36.385 | 33.3693 | 95.2449 | 95.705 | 94.3598
2022-09-08 04:32 | 6:42 | 22.1479 | 22.9948 | 25.6463 | 35.8885 | 34.2407 | 33.8013 | 34.6108 | 35.4246 | 36.5085 | 37.3745 | 36.8773 | 38.0046 | 34.3484 | 34.3395 | 34.0794 | 34.9303 | 34.8758 | 35.4136 | 36.2166 | 36.4923 | 24.0229 | 21.7711 | 94.311 | 34.4437 | 32.9325 | 34.8935 | 33.1318 | 32.971 | 33.3134 | 34.6478 | 34.1559 | 33.9192 | 37.1235 | 36.2054 | 33.313 | 34.3125 | 36.2163 | 36.4503 | 37.3679 | 36.2097 | 33.123 | 32.6305 | 34.4675 | 34.8828 | 33.1228 | 34.3006 | 34.24 | 34.3341 | 34.3894 | 34.4477 | 34.2753 | 33.9641 | 34.39 | 36.0098 | 34.99 | 36.383 | 36.3931 | 33.3546 | 95.1504 | 95.5819 | 94.3348
2022-09-08 04:32 | 6:42 | 21.9896 | 22.8281 | 25.511 | 35.9115 | 34.2518 | 33.7777 | 34.6309 | 35.4244 | 36.4933 | 37.349 | 36.8734 | 38.0041 | 34.3619 | 34.3134 | 34.0774 | 34.9171 | 34.8861 | 35.4163 | 36.2264 | 36.4915 | 23.7774 | 21.53 | 94.1839 | 34.3373 | 32.9325 | 34.8993 | 33.1178 | 32.9537 | 33.3082 | 34.6316 | 34.1491 | 33.9233 | 37.1279 | 36.1937 | 33.3054 | 34.3099 | 36.2179 | 36.4464 | 37.3781 | 36.2048 | 33.113 | 32.6354 | 34.457 | 34.8753 | 33.1068 | 34.2917 | 34.2794 | 34.3359 | 34.389 | 34.4351 | 34.3039 | 33.9622 | 34.3894 | 35.9994 | 34.9952 | 36.3641 | 36.3593 | 33.3621 | 94.89 | 95.3334 | 94.1662
2022-09-08 04:32 | 6:42 | 21.7614 | 22.5947 | 25.347 | 35.7963 | 34.2593 | 33.7963 | 34.6128 | 35.4222 | 36.4862 | 37.3626 | 36.8799 | 38.0089 | 34.3503 | 34.3389 | 34.0729 | 34.9113 | 34.8872 | 35.3968 | 36.2017 | 36.4859 | 23.5346 | 21.3766 | 94.0694 | 34.3952 | 32.9283 | 34.9002 | 33.1152 | 32.9577 | 33.3148 | 34.6427 | 34.1583 | 33.922 | 37.1378 | 36.2411 | 33.2896 | 34.313 | 36.2054 | 36.4303 | 37.3668 | 36.2047 | 33.1251 | 32.6431 | 34.4687 | 34.8707 | 33.1109 | 34.2787 | 34.2745 | 34.3354 | 34.3754 | 34.4478 | 34.3025 | 33.9766 | 34.389 | 35.9778 | 34.9769 | 36.3767 | 36.3609 | 33.3705 | 94.7161 | 95.0959 | 93.9536
2022-09-08 04:33 | 6:43 | 21.6551 | 22.5126 | 25.2538 | 35.8122 | 34.2651 | 33.7769 | 34.6227 | 35.4085 | 36.4925 | 37.3591 | 36.863 | 38.0219 | 34.3664 | 34.3305 | 34.0617 | 34.9385 | 34.8787 | 35.4089 | 36.205 | 36.4824 | 23.3762 | 21.158 | 93.9204 | 34.2493 | 32.9374 | 34.9136 | 33.1071 | 32.9544 | 33.2989 | 34.6471 | 34.1643 | 33.9176 | 37.1162 | 36.2092 | 33.3016 | 34.3025 | 36.1937 | 36.461 | 37.3726 | 36.2163 | 33.1159 | 32.6222 | 34.459 | 34.8464 | 33.0991 | 34.2874 | 34.2607 | 34.3367 | 34.4017 | 34.4459 | 34.2992 | 33.9831 | 34.3754 | 35.9923 | 34.993 | 36.3637 | 36.3794 | 33.358 | 94.4557 | 94.8382 | 93.8456
2022-09-08 04:33 | 6:43 | 21.4752 | 22.2989 | 25.0058 | 35.7888 | 34.2621 | 33.7839 | 34.5987 | 35.4192 | 36.4751 | 37.3541 | 36.871 | 38.0119 | 34.3669 | 34.3484 | 34.0595 | 34.9229 | 34.8787 | 35.4141 | 36.1979 | 36.4634 | 23.2061 | 20.9568 | 93.7315 | 34.2776 | 32.9305 | 34.8967 | 33.123 | 32.9425 | 33.313 | 34.6399 | 34.1584 | 33.9315 | 37.1315 | 36.2089 | 33.3086 | 34.3145 | 36.2411 | 36.4347 | 37.37 | 36.2179 | 33.1143 | 32.6499 | 34.437 | 34.8371 | 33.085 | 34.2823 | 34.2476 | 34.3326 | 34.391 | 34.4329 | 34.2896 | 33.9578 | 34.4017 | 35.9873 | 34.9746 | 36.3889 | 36.3821 | 33.3552 | 94.2458 | 94.6554 | 93.6755
2022-09-08 04:33 | 6:43 | 20.6592 | 20.1552 | 24.491 | 35.6712 | 34.27 | 33.7843 | 34.6063 | 35.4162 | 36.4889 | 37.353 | 36.8866 | 37.9918 | 34.3692 | 34.3515 | 34.0711 | 34.9441 | 34.8816 | 35.4236 | 36.1886 | 36.4743 | 22.6383 | 20.2356 | 93.7166 | 34.1424 | 32.9318 | 34.9196 | 33.113 | 32.9373 | 33.3054 | 34.6266 | 34.1467 | 33.9254 | 37.1354 | 36.2225 | 33.3141 | 34.3082 | 36.2092 | 36.4371 | 37.3672 | 36.2054 | 33.1374 | 32.6265 | 34.4316 | 34.8447 | 33.0895 | 34.3038 | 34.2379 | 34.3327 | 34.3897 | 34.4528 | 34.3013 | 33.9811 | 34.391 | 35.9826 | 34.9875 | 36.3735 | 36.3736 | 33.3421 | 94.1995 | 94.5349 | 93.7113
2022-09-08 04:33 | 6:43 | 22.2968 | 20.3174 | 25.3188 | 35.6437 | 34.2677 | 33.7889 | 34.5901 | 35.4076 | 36.5005 | 37.3349 | 36.889 | 38.0069 | 34.3773 | 34.3491 | 34.0606 | 34.9147 | 34.8884 | 35.4029 | 36.1803 | 36.4747 | 22.392 | 20.381 | 93.688 | 34.2418 | 32.9128 | 34.8986 | 33.1251 | 32.9309 | 33.2896 | 34.6297 | 34.1555 | 33.927 | 37.1248 | 36.2206 | 33.2898 | 34.3158 | 36.2089 | 36.4425 | 37.3612 | 36.1937 | 33.1118 | 32.6369 | 34.4301 | 34.83 | 33.0656 | 34.3108 | 34.2642 | 34.3509 | 34.4178 | 34.4457 | 34.2854 | 33.9657 | 34.3897 | 35.9656 | 34.969 | 36.375 | 36.3586 | 33.3355 | 94.1419 | 94.4627 | 93.7299
2022-09-08 04:33 | 6:43 | 24.013 | 21.4974 | 26.6123 | 35.7001 | 34.2653 | 33.7821 | 34.5839 | 35.3888 | 36.4825 | 37.3391 | 36.8782 | 38.0123 | 34.3742 | 34.3442 | 34.0554 | 34.9106 | 34.8795 | 35.3826 | 36.1828 | 36.466 | 22.7557 | 21.0457 | 93.7325 | 34.3179 | 32.9331 | 34.9076 | 33.1159 | 32.9409 | 33.3016 | 34.6314 | 34.1491 | 33.9225 | 37.1306 | 36.2225 | 33.3238 | 34.3096 | 36.2225 | 36.4499 | 37.3435 | 36.2411 | 33.1196 | 32.6122 | 34.4198 | 34.8556 | 33.0702 | 34.307 | 34.257 | 34.3416 | 34.3883 | 34.4386 | 34.2937 | 33.9686 | 34.4178 | 35.9658 | 34.9719 | 36.3919 | 36.3499 | 33.3369 | 94.0327 | 94.3529 | 93.706
2022-09-08 04:33 | 6:43 | 25.3991 | 22.9047 | 27.7424 | 35.8994 | 34.2663 | 33.7969 | 34.5951 | 35.4233 | 36.4822 | 37.3479 | 36.8794 | 38.008 | 34.3805 | 34.3612 | 34.0637 | 34.9256 | 34.8808 | 35.3823 | 36.1925 | 36.47 | 23.4504 | 22.048 | 93.7193 | 34.3928 | 32.9248 | 34.9271 | 33.1143 | 32.9457 | 33.3086 | 34.6327 | 34.1679 | 33.9246 | 37.1282 | 36.2282 | 33.3168 | 34.3285 | 36.2206 | 36.4334 | 37.3482 | 36.2092 | 33.1211 | 32.6129 | 34.4053 | 34.8253 | 33.0759 | 34.3032 | 34.261 | 34.3402 | 34.3888 | 34.455 | 34.3034 | 33.9838 | 34.3883 | 35.9696 | 34.9916 | 36.3849 | 36.3528 | 33.3283 | 93.9855 | 94.2834 | 93.727
2022-09-08 04:34 | 6:43 | 26.3765 | 24.2536 | 28.5988 | 35.953 | 34.2742 | 33.7784 | 34.592 | 35.4252 | 36.484 | 37.3633 | 36.8966 | 38.0039 | 34.3716 | 34.356 | 34.0577 | 34.9171 | 34.896 | 35.3947 | 36.1915 | 36.4663 | 24.2299 | 23.1465 | 93.6109 | 34.4565 | 32.9276 | 34.9096 | 33.1374 | 32.9267 | 33.3141 | 34.647 | 34.1521 | 33.94 | 37.1248 | 36.2076 | 33.3077 | 34.3085 | 36.2225 | 36.4414 | 37.3462 | 36.2089 | 33.134 | 32.6206 | 34.4132 | 34.8206 | 33.0752 | 34.2988 | 34.2401 | 34.3494 | 34.3921 | 34.4164 | 34.3116 | 33.9516 | 34.3888 | 35.9699 | 34.988 | 36.3814 | 36.3632 | 33.3645 | 93.8916 | 94.1816 | 93.6313
2022-09-08 04:34 | 6:44 | 27.1732 | 25.4651 | 29.2504 | 36.0429 | 34.2957 | 33.8111 | 34.5873 | 35.4103 | 36.5006 | 37.3375 | 36.8925 | 38.009 | 34.3826 | 34.3552 | 34.0716 | 34.9429 | 34.8997 | 35.4018 | 36.2089 | 36.4884 | 25.0443 | 24.2206 | 93.627 | 34.5485 | 32.93 | 34.8986 | 33.1118 | 32.9499 | 33.2898 | 34.6329 | 34.1523 | 33.9439 | 37.1398 | 36.2181 | 33.3058 | 34.3161 | 36.2282 | 36.4301 | 37.3719 | 36.2225 | 33.127 | 32.6174 | 34.4227 | 34.8124 | 33.1087 | 34.2945 | 34.2519 | 34.3382 | 34.3827 | 34.4336 | 34.3085 | 33.944 | 34.3921 | 35.959 | 34.9939 | 36.3686 | 36.3698 | 33.3449 | 93.8599 | 94.0982 | 93.5591
2022-09-08 04:34 | 6:44 | 27.868 | 26.5319 | 29.791 | 36.0007 | 34.2737 | 33.799 | 34.6007 | 35.415 | 36.5025 | 37.3371 | 36.9124 | 38.0054 | 34.3757 | 34.3595 | 34.0385 | 34.9276 | 34.8982 | 35.3962 | 36.1942 | 36.4776 | 25.8622 | 25.2199 | 93.4897 | 34.5817 | 32.9472 | 34.9384 | 33.1196 | 32.946 | 33.3238 | 34.6103 | 34.1639 | 33.9357 | 37.1224 | 36.2389 | 33.316 | 34.3205 | 36.2076 | 36.4294 | 37.3626 | 36.2206 | 33.1343 | 32.6135 | 34.4167 | 34.8239 | 33.0853 | 34.3044 | 34.2418 | 34.3397 | 34.3639 | 34.4273 | 34.3157 | 33.9635 | 34.3827 | 35.9843 | 34.9976 | 36.3974 | 36.362 | 33.3515 | 93.7557 | 94.0802 | 93.439
2022-09-08 04:34 | 6:44 | 28.4186 | 27.4094 | 30.2045 | 36.0713 | 34.2621 | 33.8116 | 34.6028 | 35.4118 | 36.5028 | 37.3588 | 36.8931 | 38.0168 | 34.3972 | 34.3552 | 34.0683 | 34.9376 | 34.8951 | 35.3972 | 36.1885 | 36.4681 | 26.5946 | 26.0757 | 93.4834 | 34.5926 | 32.9285 | 34.9311 | 33.1211 | 32.9348 | 33.3168 | 34.6224 | 34.1827 | 33.9288 | 37.1472 | 36.218 | 33.3176 | 34.3104 | 36.2181 | 36.4301 | 37.341 | 36.2225 | 33.1213 | 32.6168 | 34.4085 | 34.8243 | 33.0917 | 34.3057 | 34.2244 | 34.3627 | 34.3606 | 34.4329 | 34.3132 | 33.9542 | 34.3639 | 35.9972 | 35.0052 | 36.3743 | 36.3496 | 33.3598 | 93.7405 | 94.0403 | 93.4817
2022-09-08 04:34 | 6:44 | 28.8741 | 28.1548 | 30.4905 | 36.1305 | 34.2724 | 33.8145 | 34.6052 | 35.4069 | 36.4996 | 37.3392 | 36.9041 | 38.0167 | 34.4101 | 34.3697 | 34.0598 | 34.9545 | 34.9053 | 35.3939 | 36.2179 | 36.4838 | 27.2607 | 26.8376 | 93.459 | 34.6079 | 32.9321 | 34.9427 | 33.134 | 32.955 | 33.3077 | 34.6193 | 34.1606 | 33.9395 | 37.1345 | 36.2326 | 33.316 | 34.3295 | 36.2389 | 36.4428 | 37.3525 | 36.2282 | 33.1279 | 32.6248 | 34.4234 | 34.8162 | 33.0846 | 34.2996 | 34.231 | 34.3474 | 34.3735 | 34.4172 | 34.311 | 33.9632 | 34.3606 | 35.9885 | 34.9877 | 36.3899 | 36.366 | 33.354 | 93.696 | 93.9826 | 93.4251
2022-09-08 04:34 | 6:44 | 29.2711 | 28.7423 | 30.7573 | 36.2007 | 34.27 | 33.8203 | 34.6338 | 35.4388 | 36.4955 | 37.3507 | 36.8971 | 38.0099 | 34.3942 | 34.3657 | 34.0703 | 34.9362 | 34.8988 | 35.3993 | 36.2194 | 36.4815 | 27.8492 | 27.5262 | 93.4329 | 34.6383 | 32.934 | 34.9423 | 33.127 | 32.9668 | 33.3058 | 34.619 | 34.179 | 33.9299 | 37.1346 | 36.2361 | 33.3129 | 34.3184 | 36.218 | 36.4444 | 37.3513 | 36.2076 | 33.1472 | 32.592 | 34.4208 | 34.8145 | 33.0892 | 34.305 | 34.2241 | 34.3434 | 34.3815 | 34.4199 | 34.3103 | 33.9592 | 34.3735 | 35.9882 | 34.9953 | 36.3809 | 36.3689 | 33.3471 | 93.6723 | 93.8973 | 93.4145
2022-09-08 04:35 | 6:45 | 29.5737 | 29.2437 | 30.9652 | 36.2419 | 34.2821 | 33.8244 | 34.6108 | 35.4251 | 36.4894 | 37.3496 | 36.9084 | 38.0291 | 34.3994 | 34.3775 | 34.0746 | 34.9512 | 34.9055 | 35.3933 | 36.2183 | 36.4478 | 28.3659 | 28.0595 | 93.3679 | 34.6049 | 32.9409 | 34.9244 | 33.1343 | 32.9618 | 33.316 | 34.6197 | 34.1823 | 33.9436 | 37.1279 | 36.2469 | 33.3183 | 34.324 | 36.2326 | 36.4613 | 37.3461 | 36.2181 | 33.1364 | 32.6175 | 34.4347 | 34.8185 | 33.0906 | 34.3183 | 34.2276 | 34.3519 | 34.3729 | 34.4001 | 34.3166 | 33.9626 | 34.3815 | 35.9701 | 34.99 | 36.3926 | 36.3618 | 33.3454 | 93.5506 | 93.7867 | 93.3504
2022-09-08 04:35 | 6:45 | 29.8514 | 29.6113 | 31.1167 | 36.3383 | 34.2861 | 33.8304 | 34.6224 | 35.4285 | 36.4939 | 37.3482 | 36.9118 | 38.0385 | 34.4098 | 34.3693 | 34.0722 | 34.9456 | 34.9079 | 35.4207 | 36.2103 | 36.4821 | 28.799 | 28.4931 | 93.3584 | 34.7227 | 32.948 | 34.9311 | 33.1213 | 32.9858 | 33.3176 | 34.621 | 34.1716 | 33.9423 | 37.1439 | 36.2328 | 33.3201 | 34.3322 | 36.2361 | 36.4368 | 37.3462 | 36.2389 | 33.1576 | 32.6191 | 34.4417 | 34.831 | 33.0833 | 34.3151 | 34.2263 | 34.3529 | 34.3434 | 34.4151 | 34.3028 | 33.9753 | 34.3729 | 35.9869 | 35.0108 | 36.4023 | 36.3724 | 33.3345 | 93.4687 | 93.7097 | 93.2883
2022-09-08 04:35 | 6:45 | 30.0746 | 29.9234 | 31.2734 | 36.3618 | 34.2656 | 33.8448 | 34.6159 | 35.4311 | 36.5099 | 37.3621 | 36.9124 | 38.0276 | 34.3983 | 34.3806 | 34.0807 | 34.9501 | 34.9256 | 35.4128 | 36.2278 | 36.4707 | 29.1898 | 28.8874 | 93.3316 | 34.6559 | 32.9396 | 34.9493 | 33.1279 | 32.9769 | 33.316 | 34.6104 | 34.1684 | 33.9491 | 37.1456 | 36.2484 | 33.3195 | 34.3478 | 36.2469 | 36.4564 | 37.3451 | 36.218 | 33.1573 | 32.5968 | 34.4412 | 34.8472 | 33.1129 | 34.3258 | 34.233 | 34.3565 | 34.3884 | 34.4106 | 34.3171 | 33.9658 | 34.3434 | 35.9677 | 35.0196 | 36.3949 | 36.3687 | 33.3552 | 93.4765 | 93.6298 | 93.3342
2022-09-08 04:35 | 6:45 | 30.2743 | 30.1566 | 31.4005 | 36.2893 | 34.2876 | 33.8385 | 34.6178 | 35.4236 | 36.4868 | 37.3623 | 36.9083 | 38.043 | 34.4123 | 34.3865 | 34.0863 | 34.9639 | 34.9052 | 35.4264 | 36.2305 | 36.4851 | 29.5005 | 29.202 | 93.2332 | 34.802 | 32.9392 | 34.9379 | 33.1472 | 32.9644 | 33.3129 | 34.6251 | 34.1893 | 33.9508 | 37.1408 | 36.2469 | 33.3049 | 34.344 | 36.2328 | 36.4457 | 37.3518 | 36.2326 | 33.1519 | 32.6311 | 34.426 | 34.8322 | 33.1104 | 34.3361 | 34.2272 | 34.3655 | 34.3738 | 34.4168 | 34.3077 | 33.953 | 34.3884 | 35.9979 | 34.9978 | 36.4036 | 36.3644 | 33.3616 | 93.3772 | 93.5467 | 93.1949
2022-09-08 04:35 | 6:45 | 30.4421 | 30.3494 | 31.4869 | 36.3477 | 34.2844 | 33.8537 | 34.6153 | 35.4492 | 36.499 | 37.3629 | 36.9058 | 38.0236 | 34.4114 | 34.3695 | 34.0761 | 34.957 | 34.9235 | 35.425 | 36.2314 | 36.5069 | 29.7785 | 29.4703 | 93.1449 | 34.754 | 32.952 | 34.9276 | 33.1364 | 32.9824 | 33.3183 | 34.6133 | 34.1989 | 33.965 | 37.1277 | 36.238 | 33.3135 | 34.3428 | 36.2484 | 36.4409 | 37.3779 | 36.2361 | 33.146 | 32.614 | 34.4442 | 34.8495 | 33.1211 | 34.3346 | 34.2318 | 34.347 | 34.3652 | 34.4091 | 34.3141 | 33.9687 | 34.3738 | 35.9943 | 35.0342 | 36.3871 | 36.3836 | 33.3625 | 93.2595 | 93.4712 | 93.1539
2022-09-08 04:35 | 6:45 | 30.5655 | 30.5185 | 31.5849 | 36.4313 | 34.2697 | 33.857 | 34.6159 | 35.437 | 36.4934 | 37.372 | 36.9072 | 38.0502 | 34.4269 | 34.3931 | 34.0816 | 34.9757 | 34.9258 | 35.4222 | 36.2512 | 36.486 | 30.0411 | 29.7023 | 93.0884 | 34.8215 | 32.9503 | 34.9513 | 33.1576 | 32.984 | 33.3201 | 34.629 | 34.1805 | 33.9578 | 37.1421 | 36.2382 | 33.3252 | 34.3418 | 36.2469 | 36.4609 | 37.3427 | 36.2469 | 33.1621 | 32.6134 | 34.433 | 34.8688 | 33.0963 | 34.3449 | 34.2093 | 34.3498 | 34.3593 | 34.4137 | 34.308 | 33.9698 | 34.3652 | 35.9925 | 35.0198 | 36.3884 | 36.3847 | 33.3812 | 93.1363 | 93.348 | 93.0651
2022-09-08 04:36 | 6:45 | 30.6863 | 30.6455 | 31.6457 | 36.3552 | 34.2787 | 33.8593 | 34.6415 | 35.4516 | 36.5069 | 37.3597 | 36.909 | 38.0386 | 34.4099 | 34.3943 | 34.0819 | 34.9667 | 34.919 | 35.4282 | 36.2554 | 36.4846 | 30.2508 | 29.8958 | 93.0716 | 34.8832 | 32.956 | 34.9727 | 33.1573 | 32.996 | 33.3195 | 34.619 | 34.1982 | 33.9682 | 37.1588 | 36.2479 | 33.3343 | 34.3504 | 36.238 | 36.4636 | 37.3296 | 36.2328 | 33.1501 | 32.629 | 34.4665 | 34.8631 | 33.1258 | 34.3281 | 34.2245 | 34.3728 | 34.3494 | 34.3952 | 34.3024 | 33.9807 | 34.3593 | 35.9796 | 35.0239 | 36.3722 | 36.3659 | 33.3697 | 93.0788 | 93.3104 | 93.0428
2022-09-08 04:36 | 6:46 | 30.8139 | 30.7496 | 31.7316 | 36.433 | 34.2784 | 33.8664 | 34.6203 | 35.4483 | 36.5081 | 37.381 | 36.9047 | 38.0493 | 34.4132 | 34.3859 | 34.0975 | 34.9597 | 34.9222 | 35.4385 | 36.241 | 36.4994 | 30.4109 | 30.0788 | 93.0012 | 34.8839 | 32.9573 | 34.936 | 33.1519 | 32.9847 | 33.3049 | 34.6185 | 34.1979 | 33.9575 | 37.141 | 36.2503 | 33.3199 | 34.3621 | 36.2382 | 36.4681 | 37.3616 | 36.2484 | 33.1572 | 32.6064 | 34.4552 | 34.8561 | 33.1268 | 34.3266 | 34.2142 | 34.3644 | 34.3707 | 34.3969 | 34.3274 | 33.9767 | 34.3494 | 36.0046 | 35.0109 | 36.3862 | 36.389 | 33.3702 | 92.9725 | 93.1495 | 92.8616
2022-09-08 04:36 | 6:46 | 30.9193 | 30.865 | 31.8319 | 36.4887 | 34.2751 | 33.8651 | 34.6216 | 35.4382 | 36.5087 | 37.3796 | 36.9196 | 38.0338 | 34.4238 | 34.3905 | 34.0858 | 34.9944 | 34.9303 | 35.4279 | 36.2703 | 36.4849 | 30.6 | 30.1992 | 92.9112 | 34.8684 | 32.9515 | 34.9422 | 33.146 | 32.9847 | 33.3135 | 34.6138 | 34.1977 | 33.9829 | 37.1459 | 36.2288 | 33.3421 | 34.3663 | 36.2479 | 36.4556 | 37.3504 | 36.2469 | 33.1613 | 32.6388 | 34.4521 | 34.843 | 33.1283 | 34.3258 | 34.2266 | 34.3415 | 34.3494 | 34.3822 | 34.3311 | 33.9795 | 34.3707 | 36.0093 | 35.0145 | 36.3868 | 36.3799 | 33.3921 | 92.8667 | 93.0377 | 92.8665
2022-09-08 04:36 | 6:46 | 31.0487 | 30.973 | 31.8818 | 36.4993 | 34.2755 | 33.8552 | 34.6296 | 35.4498 | 36.5301 | 37.3683 | 36.9294 | 38.0373 | 34.4121 | 34.4121 | 34.084 | 34.9856 | 34.9402 | 35.4321 | 36.2659 | 36.4913 | 31.0214 | 30.3712 | 92.761 | 34.9316 | 32.9618 | 34.9627 | 33.1621 | 33.0111 | 33.3252 | 34.6283 | 34.1773 | 33.9522 | 37.1392 | 36.2494 | 33.3244 | 34.3616 | 36.2503 | 36.4499 | 37.3735 | 36.238 | 33.1654 | 32.6412 | 34.4577 | 34.871 | 33.1366 | 34.3246 | 34.2283 | 34.3632 | 34.354 | 34.3891 | 34.3401 | 33.9553 | 34.3494 | 36.0237 | 35.0211 | 36.3928 | 36.3806 | 33.39 | 92.6914 | 92.924 | 92.6823
2022-09-08 04:36 | 6:46 | 31.1412 | 31.0694 | 31.9398 | 36.4892 | 34.2747 | 33.8926 | 34.6353 | 35.4536 | 36.505 | 37.3816 | 36.9285 | 38.0577 | 34.4179 | 34.3987 | 34.0946 | 34.9919 | 34.9243 | 35.4265 | 36.2521 | 36.4896 | 31.536 | 30.4875 | 92.6408 | 34.9539 | 32.9509 | 34.9352 | 33.1501 | 32.9926 | 33.3343 | 34.6284 | 34.2093 | 33.9756 | 37.1644 | 36.2464 | 33.3364 | 34.3648 | 36.2288 | 36.4696 | 37.3525 | 36.2382 | 33.1571 | 32.6202 | 34.4708 | 34.8642 | 33.1509 | 34.3525 | 34.2437 | 34.3614 | 34.3477 | 34.3849 | 34.3395 | 33.9606 | 34.354 | 36 | 35.0046 | 36.4161 | 36.3802 | 33.3859 | 92.5834 | 92.7941 | 92.5917
2022-09-08 04:36 | 6:46 | 31.9243 | 31.5835 | 32.0503 | 36.5127 | 34.277 | 33.8822 | 34.618 | 35.444 | 36.5279 | 37.3711 | 36.9131 | 38.0528 | 34.4172 | 34.4099 | 34.08 | 34.9838 | 34.9379 | 35.4227 | 36.2758 | 36.5035 | 32.7498 | 31.4363 | 92.6035 | 35.0487 | 32.9629 | 34.9482 | 33.1572 | 32.993 | 33.3199 | 34.6169 | 34.2078 | 33.9736 | 37.1437 | 36.2574 | 33.3357 | 34.3684 | 36.2494 | 36.46 | 37.3641 | 36.2479 | 33.168 | 32.6321 | 34.4731 | 34.869 | 33.1532 | 34.3515 | 34.2337 | 34.3662 | 34.3478 | 34.3789 | 34.3134 | 33.9808 | 34.3477 | 36.0065 | 35.0217 | 36.4046 | 36.3748 | 33.3881 | 92.4665 | 92.6927 | 92.5349
2022-09-08 04:37 | 6:47 | 33.2456 | 31.6209 | 32.2696 | 36.6114 | 34.2969 | 33.8775 | 34.6197 | 35.4515 | 36.5271 | 37.3663 | 36.9302 | 38.0438 | 34.4247 | 34.4176 | 34.0959 | 35.0104 | 34.9148 | 35.466 | 36.2701 | 36.4944 | 33.6174 | 31.5235 | 92.5082 | 35.0276 | 32.9708 | 34.9559 | 33.1613 | 33.0026 | 33.3421 | 34.6377 | 34.193 | 33.9841 | 37.158 | 36.2636 | 33.3382 | 34.3436 | 36.2464 | 36.4659 | 37.3619 | 36.2503 | 33.1551 | 32.6325 | 34.4721 | 34.8689 | 33.1558 | 34.349 | 34.2249 | 34.3685 | 34.3526 | 34.3824 | 34.3389 | 33.9725 | 34.3478 | 36.0312 | 35.0377 | 36.4128 | 36.3883 | 33.389 | 92.3749 | 92.5694 | 92.4409
2022-09-08 04:37 | 6:47 | 34.1374 | 31.6367 | 32.6369 | 36.6401 | 34.2686 | 33.8795 | 34.6349 | 35.452 | 36.5326 | 37.391 | 36.9324 | 38.0529 | 34.426 | 34.4144 | 34.0908 | 34.9832 | 34.9409 | 35.4491 | 36.2689 | 36.5119 | 34.1939 | 31.5426 | 92.4368 | 35.0786 | 32.9676 | 34.9439 | 33.1654 | 33.0052 | 33.3244 | 34.6267 | 34.1898 | 33.9811 | 37.1538 | 36.2558 | 33.3398 | 34.3528 | 36.2574 | 36.4798 | 37.3582 | 36.2288 | 33.155 | 32.6429 | 34.4838 | 34.8838 | 33.1464 | 34.3519 | 34.2222 | 34.3496 | 34.3511 | 34.3919 | 34.3305 | 33.9862 | 34.3526 | 36.0183 | 35.0214 | 36.4039 | 36.4035 | 33.3957 | 92.2814 | 92.4168 | 92.3835
2022-09-08 04:37 | 6:47 | 34.7255 | 31.6575 | 32.9823 | 36.5751 | 34.2753 | 33.8818 | 34.6321 | 35.4721 | 36.5478 | 37.3659 | 36.926 | 38.0451 | 34.4326 | 34.4039 | 34.1019 | 34.9979 | 34.9542 | 35.4389 | 36.2686 | 36.5145 | 34.621 | 31.543 | 92.3385 | 35.0562 | 32.9597 | 34.9469 | 33.1571 | 33.0119 | 33.3364 | 34.6373 | 34.1992 | 33.9694 | 37.1592 | 36.2435 | 33.3453 | 34.369 | 36.2636 | 36.4691 | 37.3761 | 36.2494 | 33.1375 | 32.6417 | 34.4701 | 34.8626 | 33.1631 | 34.3619 | 34.2036 | 34.3672 | 34.3259 | 34.385 | 34.3484 | 33.9817 | 34.3511 | 36.0215 | 35.0357 | 36.4245 | 36.4144 | 33.4093 | 92.1556 | 92.2895 | 92.3486
2022-09-08 04:37 | 6:47 | 34.9978 | 31.6698 | 33.1862 | 36.6529 | 34.3039 | 33.8865 | 34.643 | 35.4777 | 36.5358 | 37.3815 | 36.9512 | 38.0532 | 34.4374 | 34.413 | 34.1111 | 34.9912 | 34.9477 | 35.4562 | 36.2955 | 36.5003 | 34.8339 | 31.5674 | 92.2528 | 35.0975 | 32.9618 | 34.9757 | 33.168 | 33.011 | 33.3357 | 34.646 | 34.2033 | 33.9661 | 37.1603 | 36.2322 | 33.3418 | 34.3655 | 36.2558 | 36.479 | 37.3627 | 36.2464 | 33.1749 | 32.6642 | 34.4965 | 34.8677 | 33.169 | 34.3367 | 34.2465 | 34.3824 | 34.3255 | 34.3715 | 34.3515 | 33.9805 | 34.3259 | 36.0187 | 35.0372 | 36.4114 | 36.4223 | 33.416 | 92.0038 | 92.1742 | 92.1612
2022-09-08 04:37 | 6:47 | 35.0202 | 31.6557 | 33.2895 | 36.7232 | 34.3025 | 33.8823 | 34.6364 | 35.464 | 36.5342 | 37.3835 | 36.9444 | 38.0523 | 34.443 | 34.4088 | 34.0986 | 34.9944 | 34.9453 | 35.4758 | 36.2861 | 36.5091 | 34.8251 | 31.5374 | 92.1974 | 35.1437 | 32.9767 | 34.954 | 33.1551 | 33.0263 | 33.3382 | 34.631 | 34.2099 | 33.9962 | 37.1654 | 36.2532 | 33.3427 | 34.3804 | 36.2435 | 36.4748 | 37.3584 | 36.2574 | 33.1565 | 32.6665 | 34.5081 | 34.8962 | 33.1714 | 34.3546 | 34.2557 | 34.3666 | 34.3294 | 34.3791 | 34.3491 | 33.9911 | 34.3255 | 36.0222 | 35.0234 | 36.4099 | 36.3967 | 33.4262 | 91.9855 | 92.1855 | 92.146
2022-09-08 04:37 | 6:47 | 34.8858 | 31.678 | 33.2364 | 36.6592 | 34.2992 | 33.8928 | 34.6368 | 35.4727 | 36.5238 | 37.4053 | 36.9361 | 38.0572 | 34.4445 | 34.4049 | 34.119 | 35.0167 | 34.9641 | 35.4497 | 36.287 | 36.5138 | 34.6429 | 31.5583 | 92.2348 | 35.187 | 32.9706 | 34.9747 | 33.155 | 33.0001 | 33.3398 | 34.641 | 34.1996 | 33.9857 | 37.1652 | 36.2465 | 33.3542 | 34.3709 | 36.2322 | 36.4765 | 37.3762 | 36.2636 | 33.144 | 32.6585 | 34.5049 | 34.8847 | 33.1872 | 34.3545 | 34.2392 | 34.366 | 34.3144 | 34.3557 | 34.3442 | 33.9889 | 34.3294 | 36.0199 | 35.0284 | 36.4109 | 36.4014 | 33.4402 | 92.0368 | 92.2425 | 92.2299
2022-09-08 04:38 | 6:47 | 34.8304 | 31.6848 | 33.192 | 36.6834 | 34.2896 | 33.9082 | 34.6352 | 35.4844 | 36.5473 | 37.4109 | 36.9257 | 38.0575 | 34.4303 | 34.4066 | 34.125 | 35.0127 | 34.9691 | 35.4666 | 36.2847 | 36.5161 | 34.5218 | 31.5566 | 92.2912 | 35.1152 | 32.9875 | 34.9764 | 33.1375 | 33.0084 | 33.3453 | 34.6488 | 34.1997 | 34.0039 | 37.1747 | 36.2655 | 33.34 | 34.3778 | 36.2532 | 36.491 | 37.3719 | 36.2558 | 33.1543 | 32.6616 | 34.5086 | 34.8895 | 33.1909 | 34.3722 | 34.2272 | 34.355 | 34.3282 | 34.3709 | 34.3612 | 33.993 | 34.3144 | 36.0252 | 35.0257 | 36.4257 | 36.4202 | 33.4362 | 92.1097 | 92.3595 | 92.3023
2022-09-08 04:38 | 6:48 | 34.785 | 31.7014 | 33.1244 | 36.6056 | 34.3013 | 33.92 | 34.6453 | 35.4779 | 36.5442 | 37.4076 | 36.9413 | 38.0523 | 34.4451 | 34.4155 | 34.1122 | 35.0119 | 34.9489 | 35.4514 | 36.2856 | 36.5322 | 34.4781 | 31.5529 | 92.329 | 35.1716 | 32.9733 | 34.9714 | 33.1749 | 33.0131 | 33.3418 | 34.6532 | 34.1957 | 33.9999 | 37.1828 | 36.2451 | 33.3455 | 34.378 | 36.2465 | 36.4856 | 37.359 | 36.2435 | 33.1542 | 32.6726 | 34.5219 | 34.9063 | 33.1894 | 34.3564 | 34.2286 | 34.3646 | 34.3192 | 34.3693 | 34.356 | 33.9967 | 34.3282 | 36.0491 | 35.0335 | 36.4185 | 36.4119 | 33.4455 | 92.1715 | 92.4161 | 92.3818
2022-09-08 04:38 | 6:48 | 34.7776 | 31.7283 | 33.077 | 36.6781 | 34.2854 | 33.8975 | 34.6363 | 35.4674 | 36.5414 | 37.4125 | 36.9199 | 38.0636 | 34.4376 | 34.4052 | 34.1193 | 35.0015 | 34.9662 | 35.4674 | 36.2924 | 36.5351 | 34.4693 | 31.5631 | 92.362 | 35.1812 | 32.9729 | 34.9778 | 33.1565 | 33.0196 | 33.3427 | 34.6446 | 34.2092 | 33.975 | 37.1796 | 36.2395 | 33.346 | 34.3719 | 36.2655 | 36.4851 | 37.4061 | 36.2322 | 33.1484 | 32.6739 | 34.5115 | 34.9161 | 33.1942 | 34.3626 | 34.2417 | 34.3808 | 34.3273 | 34.371 | 34.3552 | 33.9861 | 34.3192 | 36.0439 | 35.0316 | 36.4206 | 36.4073 | 33.4306 | 92.2618 | 92.5038 | 92.3887
2022-09-08 04:38 | 6:48 | 34.8795 | 31.7281 | 33.1802 | 36.7349 | 34.2937 | 33.9225 | 34.6224 | 35.474 | 36.5411 | 37.411 | 36.931 | 38.0615 | 34.4296 | 34.4237 | 34.1239 | 35.0219 | 34.952 | 35.4787 | 36.2877 | 36.5437 | 34.4965 | 31.5564 | 92.4209 | 35.1907 | 32.9872 | 34.9556 | 33.144 | 33.0206 | 33.3542 | 34.6463 | 34.2043 | 33.9828 | 37.1628 | 36.2514 | 33.3323 | 34.3759 | 36.2451 | 36.4731 | 37.374 | 36.2532 | 33.1499 | 32.6724 | 34.5357 | 34.8944 | 33.1856 | 34.3826 | 34.2426 | 34.3791 | 34.3116 | 34.3707 | 34.3595 | 33.9995 | 34.3273 | 36.0405 | 35.051 | 36.4177 | 36.4263 | 33.4642 | 92.3816 | 92.6237 | 92.4838
2022-09-08 04:38 | 6:48 | 34.9036 | 31.7397 | 33.2088 | 36.7263 | 34.3034 | 33.9173 | 34.625 | 35.4568 | 36.5462 | 37.4128 | 36.9374 | 38.0485 | 34.4382 | 34.4104 | 34.1245 | 35.0196 | 34.9643 | 35.465 | 36.3158 | 36.5174 | 34.5148 | 31.5698 | 92.534 | 35.2641 | 32.9964 | 34.9503 | 33.1543 | 33.0087 | 33.34 | 34.6422 | 34.1963 | 33.9744 | 37.168 | 36.2449 | 33.3436 | 34.3779 | 36.2395 | 36.4753 | 37.3729 | 36.2465 | 33.164 | 32.6751 | 34.5229 | 34.9221 | 33.2067 | 34.3874 | 34.2332 | 34.3903 | 34.3166 | 34.3559 | 34.3552 | 34.0043 | 34.3116 | 36.0518 | 35.0334 | 36.4385 | 36.4228 | 33.4496 | 92.4759 | 92.727 | 92.512
2022-09-08 04:38 | 6:48 | 34.9683 | 31.742 | 33.2866 | 36.7855 | 34.3116 | 33.8905 | 34.6567 | 35.4625 | 36.5611 | 37.4207 | 36.9358 | 38.054 | 34.4312 | 34.4256 | 34.1249 | 34.9956 | 34.9506 | 35.4536 | 36.3236 | 36.5229 | 34.5854 | 31.561 | 92.6623 | 35.347 | 32.9936 | 34.9466 | 33.1542 | 33.0186 | 33.3455 | 34.6459 | 34.2008 | 33.9798 | 37.1723 | 36.2158 | 33.3449 | 34.3828 | 36.2514 | 36.4648 | 37.3917 | 36.2655 | 33.1519 | 32.681 | 34.5224 | 34.9136 | 33.2119 | 34.3695 | 34.2406 | 34.3563 | 34.3075 | 34.3669 | 34.3697 | 34.0044 | 34.3166 | 36.0453 | 35.0283 | 36.4325 | 36.4173 | 33.4482 | 92.594 | 92.8688 | 92.6813
2022-09-08 04:39 | 6:49 | 35.0685 | 31.7561 | 33.4044 | 36.7763 | 34.3085 | 33.9027 | 34.6268 | 35.4799 | 36.5409 | 37.4237 | 36.9166 | 38.047 | 34.4579 | 34.4147 | 34.12 | 35.0136 | 34.9553 | 35.4734 | 36.2983 | 36.5366 | 34.6259 | 31.5662 | 92.7096 | 35.311 | 32.9835 | 34.952 | 33.1484 | 33.0338 | 33.346 | 34.64 | 34.199 | 33.989 | 37.1623 | 36.2514 | 33.3519 | 34.3806 | 36.2449 | 36.4906 | 37.373 | 36.2451 | 33.1582 | 32.6792 | 34.5277 | 34.8973 | 33.2119 | 34.3708 | 34.2448 | 34.3596 | 34.3067 | 34.3586 | 34.3657 | 34.0311 | 34.3075 | 36.0538 | 35.0221 | 36.4126 | 36.4055 | 33.4567 | 92.7258 | 93.0039 | 92.8004
2022-09-08 04:39 | 6:49 | 35.1484 | 31.7999 | 33.5269 | 36.7407 | 34.3157 | 33.9038 | 34.6415 | 35.4772 | 36.5621 | 37.4194 | 36.9217 | 38.0519 | 34.4456 | 34.4178 | 34.1365 | 35.0072 | 34.9515 | 35.4644 | 36.3216 | 36.5367 | 34.6955 | 31.5667 | 92.7612 | 35.3291 | 32.9828 | 34.9519 | 33.1499 | 33.0204 | 33.3323 | 34.6382 | 34.1932 | 33.9805 | 37.1669 | 36.2443 | 33.3515 | 34.3682 | 36.2158 | 36.4891 | 37.3854 | 36.2395 | 33.1525 | 32.6773 | 34.5246 | 34.914 | 33.2063 | 34.3836 | 34.2515 | 34.3643 | 34.2951 | 34.3725 | 34.3775 | 34.015 | 34.3067 | 36.0395 | 35.0285 | 36.4359 | 36.4087 | 33.4633 | 92.8096 | 93.1003 | 92.7818
2022-09-08 04:39 | 6:49 | 35.2303 | 31.7911 | 33.6822 | 36.7867 | 34.3132 | 33.8978 | 34.6307 | 35.4848 | 36.5552 | 37.4218 | 36.9327 | 38.0767 | 34.4412 | 34.4085 | 34.1558 | 35.0065 | 34.9554 | 35.467 | 36.3126 | 36.5398 | 34.7968 | 31.5791 | 92.8613 | 35.2663 | 32.9894 | 34.943 | 33.164 | 33.0364 | 33.3436 | 34.6445 | 34.1919 | 33.9937 | 37.1854 | 36.2464 | 33.3576 | 34.3588 | 36.2514 | 36.4787 | 37.369 | 36.2514 | 33.1483 | 32.6795 | 34.5501 | 34.9179 | 33.2145 | 34.388 | 34.2489 | 34.3538 | 34.2843 | 34.3397 | 34.3693 | 34.0052 | 34.2951 | 36.059 | 35.0366 | 36.4138 | 36.432 | 33.4623 | 92.9223 | 93.216 | 92.9058
2022-09-08 04:39 | 6:49 | 35.3812 | 31.8193 | 33.8762 | 36.954 | 34.311 | 33.9043 | 34.6194 | 35.4692 | 36.5586 | 37.4192 | 36.9195 | 38.0639 | 34.4437 | 34.4113 | 34.1228 | 34.9991 | 34.9814 | 35.4802 | 36.3133 | 36.5418 | 34.9596 | 31.5799 | 92.9083 | 35.2942 | 32.9962 | 34.957 | 33.1519 | 33.0261 | 33.3449 | 34.665 | 34.1905 | 33.9891 | 37.181 | 36.2382 | 33.3649 | 34.3714 | 36.2443 | 36.4863 | 37.391 | 36.2449 | 33.1454 | 32.6632 | 34.5471 | 34.9213 | 33.224 | 34.3819 | 34.2584 | 34.3796 | 34.2711 | 34.3448 | 34.3806 | 34.0246 | 34.2843 | 36.0417 | 35.044 | 36.4273 | 36.4197 | 33.4638 | 93.0114 | 93.3345 | 92.9724
2022-09-08 04:39 | 6:49 | 35.4636 | 31.8212 | 33.9513 | 36.759 | 34.3103 | 33.9035 | 34.635 | 35.4604 | 36.5567 | 37.428 | 36.919 | 38.0454 | 34.4477 | 34.4305 | 34.1389 | 35.0177 | 34.96 | 35.4546 | 36.3172 | 36.5356 | 35.0828 | 31.5778 | 92.9692 | 35.2674 | 32.9937 | 34.9489 | 33.1582 | 33.0339 | 33.3519 | 34.6504 | 34.1816 | 34.0037 | 37.176 | 36.2335 | 33.3664 | 34.3637 | 36.2464 | 36.4785 | 37.3955 | 36.2158 | 33.1472 | 32.6813 | 34.5518 | 34.935 | 33.2276 | 34.39 | 34.2592 | 34.3631 | 34.281 | 34.3559 | 34.3865 | 34.0099 | 34.2711 | 36.0391 | 35.0301 | 36.409 | 36.4439 | 33.4655 | 93.1396 | 93.4437 | 93.074
2022-09-08 04:39 | 6:49 | 35.5372 | 31.8338 | 34.008 | 36.8069 | 34.3166 | 33.9048 | 34.6325 | 35.4797 | 36.5548 | 37.4186 | 36.9071 | 38.0683 | 34.4351 | 34.4197 | 34.1378 | 35.0104 | 34.985 | 35.4768 | 36.3128 | 36.5466 | 35.0924 | 31.5832 | 93.0797 | 35.3778 | 33.0057 | 34.9412 | 33.1525 | 33.0271 | 33.3515 | 34.6648 | 34.1922 | 33.9896 | 37.1805 | 36.2543 | 33.3461 | 34.358 | 36.2382 | 36.4768 | 37.3925 | 36.2514 | 33.1367 | 32.6965 | 34.5424 | 34.9174 | 33.2191 | 34.3815 | 34.2644 | 34.3827 | 34.2811 | 34.3519 | 34.3695 | 34.0107 | 34.281 | 36.0627 | 35.0404 | 36.4148 | 36.4361 | 33.4577 | 93.2959 | 93.6119 | 93.1459
2022-09-08 04:40 | 6:50 | 35.5804 | 31.8706 | 34.0932 | 36.8535 | 34.3028 | 33.9237 | 34.6435 | 35.4611 | 36.5499 | 37.4218 | 36.9274 | 38.0724 | 34.4478 | 34.4433 | 34.1428 | 35.0211 | 34.9699 | 35.4808 | 36.3337 | 36.5579 | 35.1327 | 31.6028 | 93.101 | 35.3887 | 32.9892 | 34.9476 | 33.1483 | 33.0108 | 33.3576 | 34.6512 | 34.185 | 33.9756 | 37.1583 | 36.2427 | 33.3674 | 34.3752 | 36.2335 | 36.48 | 37.3957 | 36.2443 | 33.1466 | 32.696 | 34.5534 | 34.9348 | 33.2417 | 34.3946 | 34.2636 | 34.3615 | 34.2883 | 34.3565 | 34.3931 | 34.0094 | 34.2811 | 36.0527 | 35.0434 | 36.4146 | 36.4191 | 33.4724 | 93.4047 | 93.7582 | 93.2225
2022-09-08 04:40 | 6:50 | 35.6564 | 31.879 | 34.1779 | 36.8959 | 34.3171 | 33.9231 | 34.6377 | 35.4606 | 36.5542 | 37.4455 | 36.9103 | 38.0446 | 34.4459 | 34.4169 | 34.1332 | 35.004 | 34.9745 | 35.4772 | 36.3206 | 36.57 | 35.1941 | 31.5885 | 93.2287 | 35.4514 | 32.9934 | 34.951 | 33.1454 | 33.0432 | 33.3649 | 34.6687 | 34.2074 | 33.9859 | 37.1742 | 36.2409 | 33.3641 | 34.3922 | 36.2543 | 36.472 | 37.3936 | 36.2464 | 33.1473 | 32.7046 | 34.5489 | 34.951 | 33.2341 | 34.399 | 34.249 | 34.3912 | 34.2546 | 34.338 | 34.3943 | 34.0194 | 34.2883 | 36.0601 | 35.0201 | 36.3993 | 36.4289 | 33.4796 | 93.5561 | 93.9242 | 93.3127
2022-09-08 04:40 | 6:50 | 35.6937 | 31.8993 | 34.2658 | 36.9291 | 34.3077 | 33.9274 | 34.639 | 35.483 | 36.5722 | 37.4357 | 36.9242 | 38.0507 | 34.4329 | 34.4257 | 34.1317 | 35.0277 | 34.9713 | 35.4653 | 36.3262 | 36.5594 | 35.2365 | 31.6028 | 93.3254 | 35.4796 | 33.0108 | 34.9615 | 33.1472 | 33.0202 | 33.3664 | 34.6637 | 34.1908 | 33.9792 | 37.1837 | 36.2466 | 33.3781 | 34.3807 | 36.2427 | 36.4878 | 37.4248 | 36.2382 | 33.1451 | 32.7092 | 34.5707 | 34.9472 | 33.2596 | 34.394 | 34.2604 | 34.3688 | 34.2671 | 34.3476 | 34.3859 | 34.0082 | 34.2546 | 36.0733 | 35.0421 | 36.4233 | 36.4342 | 33.4952 | 93.7347 | 94.1329 | 93.4656
2022-09-08 04:40 | 6:50 | 35.7659 | 31.9328 | 34.3538 | 36.9676 | 34.3141 | 33.9077 | 34.6332 | 35.4867 | 36.5617 | 37.4368 | 36.9061 | 38.0428 | 34.4528 | 34.4334 | 34.1509 | 35.0201 | 34.9834 | 35.469 | 36.3243 | 36.5549 | 35.2727 | 31.6116 | 93.4629 | 35.4561 | 32.9986 | 34.9275 | 33.1367 | 33.0266 | 33.3461 | 34.6557 | 34.2012 | 33.9917 | 37.1484 | 36.2558 | 33.3653 | 34.3841 | 36.2409 | 36.4789 | 37.4101 | 36.2335 | 33.1548 | 32.7045 | 34.5627 | 34.9298 | 33.2529 | 34.3831 | 34.2658 | 34.3942 | 34.2517 | 34.3403 | 34.3905 | 34.0163 | 34.2671 | 36.0562 | 35.0171 | 36.4337 | 36.4432 | 33.4955 | 93.8805 | 94.3357 | 93.5554
2022-09-08 04:40 | 6:50 | 35.793 | 31.9462 | 34.4248 | 37.0212 | 34.308 | 33.9239 | 34.6578 | 35.5016 | 36.5632 | 37.4416 | 36.9197 | 38.0561 | 34.4457 | 34.4252 | 34.1549 | 35.0157 | 34.9874 | 35.4594 | 36.3248 | 36.5585 | 35.2649 | 31.6245 | 93.5659 | 35.4653 | 33.0104 | 34.955 | 33.1466 | 33.0269 | 33.3674 | 34.667 | 34.1859 | 33.983 | 37.1564 | 36.2281 | 33.3726 | 34.3753 | 36.2466 | 36.4714 | 37.4104 | 36.2543 | 33.1618 | 32.7092 | 34.583 | 34.9474 | 33.2628 | 34.3993 | 34.2647 | 34.4051 | 34.24 | 34.3401 | 34.4121 | 34.0162 | 34.2517 | 36.0655 | 35.0297 | 36.4241 | 36.4359 | 33.4855 | 94.1034 | 94.5225 | 93.7563
2022-09-08 04:40 | 6:50 | 35.8342 | 31.9498 | 34.4949 | 37.0699 | 34.3024 | 33.9308 | 34.6448 | 35.4877 | 36.5702 | 37.4377 | 36.928 | 38.0545 | 34.4386 | 34.4299 | 34.1552 | 35.0114 | 34.9779 | 35.4662 | 36.3372 | 36.564 | 35.3411 | 31.6376 | 93.6816 | 35.5133 | 33.0044 | 34.9377 | 33.1473 | 33.03 | 33.3641 | 34.681 | 34.176 | 33.9887 | 37.1831 | 36.2303 | 33.3331 | 34.3681 | 36.2558 | 36.4978 | 37.4189 | 36.2427 | 33.1857 | 32.7095 | 34.5825 | 34.9603 | 33.2666 | 34.4008 | 34.2524 | 34.3891 | 34.2794 | 34.3429 | 34.3987 | 34.0084 | 34.24 | 36.0663 | 35.0178 | 36.4394 | 36.4382 | 33.4719 | 94.2758 | 94.7292 | 93.8794
2022-09-08 04:41 | 6:50 | 35.9166 | 31.9718 | 34.5569 | 37.0319 | 34.3274 | 33.913 | 34.6538 | 35.4792 | 36.5677 | 37.4264 | 36.911 | 38.059 | 34.455 | 34.4195 | 34.1541 | 35.0092 | 34.9746 | 35.483 | 36.3169 | 36.5523 | 35.3891 | 31.63 | 93.8363 | 35.4992 | 33.0119 | 34.9417 | 33.1451 | 33.0372 | 33.3781 | 34.6737 | 34.1702 | 33.9858 | 37.1929 | 36.246 | 33.3652 | 34.3818 | 36.2281 | 36.4856 | 37.4263 | 36.2409 | 33.1548 | 32.715 | 34.5824 | 34.9549 | 33.278 | 34.3951 | 34.2657 | 34.3939 | 34.2745 | 34.3268 | 34.4099 | 34.0099 | 34.2794 | 36.0662 | 35.0478 | 36.4294 | 36.4435 | 33.4974 | 94.411 | 94.8865 | 94.0291
2022-09-08 04:41 | 6:51 | 33.7887 | 31.8907 | 34.2986 | 37.0281 | 34.3311 | 33.9346 | 34.6398 | 35.4868 | 36.5526 | 37.4323 | 36.8996 | 38.0668 | 34.4164 | 34.4276 | 34.1662 | 35.0207 | 34.9859 | 35.4764 | 36.3266 | 36.5575 | 33.0066 | 31.5587 | 93.9055 | 35.4684 | 33.0179 | 34.959 | 33.1548 | 33.0337 | 33.3653 | 34.6552 | 34.1771 | 33.9905 | 37.1464 | 36.2519 | 33.3678 | 34.3663 | 36.2303 | 36.468 | 37.4109 | 36.2466 | 33.1561 | 32.711 | 34.6016 | 34.9601 | 33.2879 | 34.4079 | 34.2619 | 34.4034 | 34.2607 | 34.308 | 34.4176 | 34.0014 | 34.2745 | 36.0529 | 35.0277 | 36.4214 | 36.4346 | 33.474 | 94.6159 | 95.0879 | 94.0592
2022-09-08 04:41 | 6:51 | 29.3183 | 30.0989 | 32.8889 | 36.8709 | 34.3401 | 33.9193 | 34.6642 | 35.4918 | 36.5633 | 37.4586 | 36.9202 | 38.0569 | 34.4336 | 34.4221 | 34.1639 | 35.0074 | 34.9725 | 35.4706 | 36.3393 | 36.5774 | 28.137 | 31.4953 | 94.0365 | 35.442 | 32.9953 | 34.9294 | 33.1618 | 33.0382 | 33.3726 | 34.6548 | 34.1739 | 33.9752 | 37.162 | 36.2437 | 33.3571 | 34.3802 | 36.246 | 36.4883 | 37.4222 | 36.2558 | 33.1646 | 32.7121 | 34.5873 | 34.9582 | 33.3022 | 34.3948 | 34.2921 | 34.3994 | 34.2476 | 34.3268 | 34.4144 | 34.0327 | 34.2607 | 36.0466 | 35.0434 | 36.4401 | 36.4498 | 33.4893 | 94.8182 | 95.2204 | 94.2523
2022-09-08 04:41 | 6:51 | 30.6478 | 31.5142 | 33.2128 | 36.9092 | 34.3395 | 33.9247 | 34.6508 | 35.501 | 36.5721 | 37.4453 | 36.9371 | 38.0615 | 34.4273 | 34.4092 | 34.1422 | 35.0371 | 34.9834 | 35.4665 | 36.3356 | 36.5618 | 28.1965 | 31.171 | 94.1807 | 35.3815 | 33.0169 | 34.9564 | 33.1857 | 33.0331 | 33.3331 | 34.6597 | 34.1935 | 33.9876 | 37.1784 | 36.2569 | 33.3511 | 34.3764 | 36.2519 | 36.4689 | 37.4015 | 36.2281 | 33.1689 | 32.712 | 34.5913 | 34.9389 | 33.2934 | 34.4045 | 34.2835 | 34.3919 | 34.2379 | 34.3219 | 34.4039 | 34.0192 | 34.2476 | 36.0573 | 35.0407 | 36.4159 | 36.4365 | 33.4704 | 94.896 | 95.3834 | 94.2619
2022-09-08 04:41 | 6:51 | 31.8945 | 31.6761 | 33.5826 | 36.9805 | 34.3134 | 33.9333 | 34.6526 | 35.4918 | 36.5669 | 37.435 | 36.9049 | 38.0531 | 34.4329 | 34.4068 | 34.1624 | 35.0252 | 34.9659 | 35.4696 | 36.3589 | 36.541 | 28.8041 | 31.1757 | 94.2795 | 35.3897 | 33.0037 | 34.9633 | 33.1548 | 33.0466 | 33.3652 | 34.6677 | 34.1678 | 33.9851 | 37.1738 | 36.2618 | 33.3654 | 34.3897 | 36.2437 | 36.4942 | 37.4058 | 36.2303 | 33.1576 | 32.7271 | 34.5969 | 34.9342 | 33.2804 | 34.3886 | 34.2763 | 34.3947 | 34.2642 | 34.3088 | 34.413 | 34.0423 | 34.2379 | 36.0552 | 35.0474 | 36.4227 | 36.4299 | 33.4771 | 95.0503 | 95.4924 | 94.3729
2022-09-08 04:41 | 6:51 | 32.6552 | 31.7324 | 33.8329 | 36.9573 | 34.3389 | 33.9269 | 34.6558 | 35.4955 | 36.5744 | 37.4299 | 36.9081 | 38.0604 | 34.4172 | 34.42 | 34.1646 | 35.0052 | 35.0001 | 35.479 | 36.331 | 36.5576 | 29.4841 | 31.2742 | 94.3015 | 35.5067 | 32.9971 | 34.9547 | 33.1561 | 33.0333 | 33.3678 | 34.6546 | 34.1778 | 33.9966 | 37.1689 | 36.2825 | 33.3784 | 34.3871 | 36.2569 | 36.473 | 37.4235 | 36.246 | 33.1747 | 32.7174 | 34.5583 | 34.9485 | 33.3201 | 34.4131 | 34.2662 | 34.4015 | 34.257 | 34.3074 | 34.4088 | 34.0387 | 34.2642 | 36.0741 | 35.0404 | 36.4257 | 36.4579 | 33.4802 | 95.1672 | 95.5786 | 94.4188
2022-09-08 04:42 | 6:52 | 33.1391 | 31.7659 | 33.9828 | 37.0468 | 34.3305 | 33.9406 | 34.6501 | 35.4929 | 36.5654 | 37.4386 | 36.9 | 38.0372 | 34.4199 | 34.4177 | 34.1417 | 35.0131 | 34.9872 | 35.4802 | 36.335 | 36.5692 | 30.1165 | 31.3685 | 94.4173 | 35.5262 | 33.014 | 34.9543 | 33.1646 | 33.0409 | 33.3571 | 34.6671 | 34.1739 | 33.9945 | 37.1872 | 36.2566 | 33.369 | 34.3648 | 36.2618 | 36.4893 | 37.4179 | 36.2519 | 33.152 | 32.7284 | 34.597 | 34.9652 | 33.2996 | 34.3947 | 34.2883 | 34.3819 | 34.261 | 34.3091 | 34.4049 | 34.0534 | 34.257 | 36.0585 | 35.0273 | 36.4202 | 36.4352 | 33.4926 | 95.1553 | 95.6673 | 94.5202
2022-09-08 04:42 | 6:52 | 33.4008 | 31.7674 | 34.0784 | 37.1126 | 34.3484 | 33.9366 | 34.6463 | 35.508 | 36.5829 | 37.4373 | 36.9102 | 38.0517 | 34.4001 | 34.4024 | 34.1795 | 35.0064 | 34.9845 | 35.4875 | 36.3511 | 36.5408 | 30.6264 | 31.4107 | 94.4784 | 35.4679 | 33.0102 | 34.9463 | 33.1689 | 33.0561 | 33.3511 | 34.6591 | 34.1827 | 33.9812 | 37.1669 | 36.2501 | 33.352 | 34.3817 | 36.2825 | 36.476 | 37.4202 | 36.2437 | 33.1706 | 32.727 | 34.6125 | 34.9643 | 33.3252 | 34.4081 | 34.2702 | 34.3962 | 34.2401 | 34.2994 | 34.4066 | 34.0258 | 34.261 | 36.0607 | 35.0441 | 36.4306 | 36.4363 | 33.5111 | 95.3366 | 95.7839 | 94.5706
2022-09-08 04:42 | 6:52 | 33.571 | 31.796 | 34.1562 | 36.9771 | 34.3515 | 33.9594 | 34.6698 | 35.4939 | 36.5689 | 37.4595 | 36.9093 | 38.06 | 34.4151 | 34.4244 | 34.1589 | 35.0179 | 34.9989 | 35.4764 | 36.3252 | 36.5508 | 31.0465 | 31.4599 | 94.4746 | 35.4632 | 33.0146 | 34.951 | 33.1576 | 33.0433 | 33.3654 | 34.6507 | 34.1797 | 33.9729 | 37.1873 | 36.2539 | 33.368 | 34.3888 | 36.2566 | 36.4847 | 37.4014 | 36.2569 | 33.1576 | 32.7393 | 34.5999 | 34.9504 | 33.3439 | 34.3986 | 34.2901 | 34.4025 | 34.2519 | 34.3144 | 34.4155 | 34.0452 | 34.2401 | 36.0483 | 35.0306 | 36.4338 | 36.4574 | 33.4828 | 95.2563 | 95.7142 | 94.5542
2022-09-08 04:42 | 6:52 | 33.6775 | 31.8064 | 34.1928 | 37.1631 | 34.3491 | 33.9171 | 34.6807 | 35.491 | 36.5695 | 37.4532 | 36.9185 | 38.0552 | 34.4106 | 34.4303 | 34.146 | 35.0062 | 34.9933 | 35.4732 | 36.3443 | 36.5639 | 31.4159 | 31.4535 | 94.3773 | 35.499 | 32.9982 | 34.9587 | 33.1747 | 33.0487 | 33.3784 | 34.648 | 34.1888 | 33.9958 | 37.1616 | 36.2515 | 33.3668 | 34.3885 | 36.2501 | 36.4708 | 37.4216 | 36.2618 | 33.1711 | 32.737 | 34.594 | 34.9517 | 33.3222 | 34.4095 | 34.2698 | 34.4213 | 34.2418 | 34.299 | 34.4052 | 34.0384 | 34.2519 | 36.0577 | 35.0371 | 36.4272 | 36.4349 | 33.4737 | 95.0817 | 95.5216 | 94.4188
2022-09-08 04:42 | 6:52 | 33.7454 | 31.809 | 34.2537 | 37.1131 | 34.3442 | 33.9324 | 34.6523 | 35.4606 | 36.5757 | 37.4656 | 36.912 | 38.0402 | 34.4168 | 34.3986 | 34.1487 | 35.0155 | 34.9946 | 35.4614 | 36.3102 | 36.5577 | 31.67 | 31.5081 | 94.2397 | 35.5152 | 33.0065 | 34.9578 | 33.152 | 33.0595 | 33.369 | 34.642 | 34.1663 | 33.9776 | 37.1646 | 36.278 | 33.3733 | 34.3702 | 36.2539 | 36.4861 | 37.4048 | 36.2825 | 33.1528 | 32.7496 | 34.5986 | 34.9457 | 33.3312 | 34.397 | 34.2599 | 34.4119 | 34.2244 | 34.2968 | 34.4237 | 34.0565 | 34.2418 | 36.0744 | 35.0512 | 36.4194 | 36.4312 | 33.477 | 94.8367 | 95.2685 | 94.1964
2022-09-08 04:42 | 6:52 | 33.8001 | 31.8052 | 34.2548 | 37.0376 | 34.3612 | 33.9388 | 34.6642 | 35.4793 | 36.5652 | 37.4337 | 36.9142 | 38.0573 | 34.4091 | 34.4138 | 34.1701 | 35.0296 | 34.9897 | 35.466 | 36.3141 | 36.553 | 31.9025 | 31.4842 | 93.9979 | 35.4423 | 33.013 | 34.9636 | 33.1706 | 33.0392 | 33.352 | 34.6551 | 34.1692 | 33.9806 | 37.1773 | 36.2694 | 33.3764 | 34.3854 | 36.2515 | 36.4747 | 37.4109 | 36.2566 | 33.1763 | 32.7551 | 34.6064 | 34.9406 | 33.3442 | 34.4005 | 34.2579 | 34.4074 | 34.231 | 34.3193 | 34.4104 | 34.0433 | 34.2244 | 36.0478 | 35.0356 | 36.4253 | 36.4594 | 33.4658 | 94.5849 | 95.0111 | 94.0264
2022-09-08 04:43 | 6:52 | 33.8525 | 31.8326 | 34.2976 | 37.1105 | 34.356 | 33.9404 | 34.675 | 35.4992 | 36.5736 | 37.4156 | 36.9025 | 38.0453 | 34.4137 | 34.4144 | 34.163 | 35.008 | 35.0057 | 35.467 | 36.3341 | 36.5454 | 32.0668 | 31.5094 | 93.9064 | 35.5975 | 32.9958 | 34.9489 | 33.1576 | 33.0355 | 33.368 | 34.6499 | 34.1672 | 33.9833 | 37.1684 | 36.271 | 33.37 | 34.3617 | 36.278 | 36.4807 | 37.4125 | 36.2501 | 33.1831 | 32.7732 | 34.581 | 34.9819 | 33.3363 | 34.4 | 34.2835 | 34.4132 | 34.2241 | 34.2921 | 34.4256 | 34.0358 | 34.231 | 36.031 | 35.0347 | 36.4167 | 36.446 | 33.4726 | 94.3384 | 94.7889 | 93.9156
2022-09-08 04:43 | 6:53 | 33.8801 | 31.8327 | 34.3184 | 37.2151 | 34.3552 | 33.9491 | 34.6727 | 35.4804 | 36.5577 | 37.4604 | 36.9235 | 38.0477 | 34.3952 | 34.3916 | 34.1469 | 35.024 | 34.992 | 35.461 | 36.3164 | 36.5379 | 32.2428 | 31.5228 | 93.8026 | 35.6067 | 33.0104 | 34.9606 | 33.1711 | 33.0468 | 33.3668 | 34.6343 | 34.1621 | 33.9841 | 37.1786 | 36.2823 | 33.3659 | 34.3854 | 36.2694 | 36.4529 | 37.4018 | 36.2539 | 33.1667 | 32.7555 | 34.5745 | 34.9371 | 33.3381 | 34.4074 | 34.2687 | 34.4166 | 34.2276 | 34.2805 | 34.4147 | 34.031 | 34.2241 | 36.029 | 35.0543 | 36.4237 | 36.4328 | 33.4727 | 94.2212 | 94.6393 | 93.8161
2022-09-08 04:43 | 6:53 | 33.8887 | 31.8343 | 34.3401 | 37.1668 | 34.3595 | 33.9445 | 34.6762 | 35.5011 | 36.5719 | 37.4387 | 36.8946 | 38.0493 | 34.3969 | 34.3969 | 34.1531 | 35.0334 | 35.0051 | 35.4765 | 36.3344 | 36.5557 | 32.3491 | 31.5407 | 93.7906 | 35.5398 | 33.003 | 34.9477 | 33.1528 | 33.0341 | 33.3733 | 34.6551 | 34.1954 | 33.9813 | 37.1686 | 36.2927 | 33.3684 | 34.3887 | 36.271 | 36.4667 | 37.4109 | 36.2515 | 33.1801 | 32.7543 | 34.6183 | 34.9393 | 33.3586 | 34.3894 | 34.2935 | 34.4133 | 34.2263 | 34.2961 | 34.4178 | 34.0277 | 34.2276 | 36.0429 | 35.0418 | 36.4217 | 36.4579 | 33.4644 | 94.128 | 94.5246 | 93.7557
2022-09-08 04:43 | 6:53 | 33.8633 | 31.8514 | 34.3672 | 37.0355 | 34.3552 | 33.9377 | 34.6669 | 35.4881 | 36.5553 | 37.4276 | 36.9153 | 38.0506 | 34.3822 | 34.4054 | 34.157 | 35.0207 | 34.9889 | 35.4691 | 36.3409 | 36.5325 | 32.4471 | 31.5474 | 93.759 | 35.6073 | 33.0131 | 34.9651 | 33.1763 | 33.0462 | 33.3764 | 34.6412 | 34.1887 | 33.986 | 37.1555 | 36.2762 | 33.3698 | 34.3831 | 36.2823 | 36.4708 | 37.3971 | 36.278 | 33.1707 | 32.7518 | 34.6187 | 34.9501 | 33.3762 | 34.4099 | 34.2831 | 34.421 | 34.233 | 34.2845 | 34.4085 | 34.0416 | 34.2263 | 36.0517 | 35.0379 | 36.4271 | 36.4269 | 33.4632 | 94.1 | 94.4615 | 93.7602
2022-09-08 04:43 | 6:53 | 33.8863 | 31.8726 | 34.3677 | 37.0961 | 34.3697 | 33.9552 | 34.6735 | 35.49 | 36.5664 | 37.4565 | 36.9051 | 38.0603 | 34.3891 | 34.39 | 34.154 | 35.041 | 35.0073 | 35.4401 | 36.3346 | 36.5457 | 32.5338 | 31.5491 | 93.7299 | 35.5849 | 33.0132 | 34.9657 | 33.1831 | 33.0444 | 33.37 | 34.6454 | 34.1842 | 33.9956 | 37.161 | 36.2884 | 33.3587 | 34.3907 | 36.2927 | 36.484 | 37.4039 | 36.2694 | 33.1796 | 32.7689 | 34.6116 | 34.947 | 33.3764 | 34.4082 | 34.2733 | 34.4104 | 34.2272 | 34.2917 | 34.4113 | 34.0406 | 34.233 | 36.05 | 35.0583 | 36.4401 | 36.447 | 33.4701 | 93.979 | 94.3535 | 93.6486
2022-09-08 04:43 | 6:53 | 33.9388 | 31.8804 | 34.413 | 37.1192 | 34.3657 | 33.9637 | 34.6636 | 35.498 | 36.581 | 37.4506 | 36.9199 | 38.042 | 34.3849 | 34.3894 | 34.1465 | 35.0407 | 35.0072 | 35.4531 | 36.3412 | 36.5608 | 32.6284 | 31.5755 | 93.6437 | 35.6142 | 33.0097 | 34.9736 | 33.1667 | 33.0532 | 33.3659 | 34.6312 | 34.1789 | 33.9997 | 37.1772 | 36.2843 | 33.382 | 34.3806 | 36.2762 | 36.4757 | 37.4057 | 36.271 | 33.1812 | 32.7641 | 34.625 | 34.9591 | 33.3739 | 34.4044 | 34.27 | 34.4134 | 34.2318 | 34.275 | 34.4305 | 34.0336 | 34.2272 | 36.029 | 35.0408 | 36.4159 | 36.4474 | 33.4846 | 93.953 | 94.287 | 93.6095
2022-09-08 04:44 | 6:54 | 33.9899 | 31.9051 | 34.4358 | 37.0802 | 34.3775 | 33.9774 | 34.6735 | 35.4937 | 36.5883 | 37.4442 | 36.9175 | 38.0545 | 34.3789 | 34.389 | 34.1617 | 35.049 | 35.016 | 35.4672 | 36.3314 | 36.5537 | 32.6965 | 31.569 | 93.6419 | 35.6029 | 32.9988 | 34.9776 | 33.1801 | 33.0627 | 33.3684 | 34.6327 | 34.2056 | 33.9883 | 37.1842 | 36.2954 | 33.3657 | 34.3977 | 36.2884 | 36.4841 | 37.4029 | 36.2823 | 33.1988 | 32.767 | 34.5963 | 34.9612 | 33.3899 | 34.394 | 34.2664 | 34.4025 | 34.2093 | 34.2658 | 34.4197 | 34.0456 | 34.2318 | 36.052 | 35.0602 | 36.4423 | 36.4526 | 33.4436 | 93.9419 | 94.219 | 93.6103
2022-09-08 04:44 | 6:54 | 34.0589 | 31.9225 | 34.4734 | 37.1626 | 34.3693 | 33.977 | 34.6948 | 35.5159 | 36.592 | 37.4394 | 36.9178 | 38.0522 | 34.3824 | 34.3754 | 34.1738 | 35.0329 | 35.0121 | 35.4641 | 36.3296 | 36.5527 | 32.7645 | 31.5933 | 93.562 | 35.6464 | 33.0004 | 34.9674 | 33.1707 | 33.0598 | 33.3698 | 34.6234 | 34.1907 | 33.9971 | 37.1621 | 36.2858 | 33.3576 | 34.3861 | 36.2843 | 36.4744 | 37.4078 | 36.2927 | 33.1922 | 32.7837 | 34.6352 | 34.9757 | 33.4041 | 34.3912 | 34.2876 | 34.4135 | 34.2245 | 34.2686 | 34.4433 | 34.0438 | 34.2093 | 36.0451 | 35.0508 | 36.4561 | 36.4427 | 33.4705 | 93.8825 | 94.151 | 93.5868
2022-09-08 04:44 | 6:54 | 34.128 | 31.9723 | 34.4856 | 37.2766 | 34.3806 | 33.9745 | 34.6762 | 35.5059 | 36.575 | 37.4562 | 36.9263 | 38.0691 | 34.3919 | 34.4017 | 34.1548 | 35.0515 | 35.0315 | 35.4732 | 36.3331 | 36.5416 | 32.942 | 31.6 | 93.5283 | 35.6129 | 33.0165 | 34.9908 | 33.1796 | 33.0373 | 33.3587 | 34.6344 | 34.1925 | 33.9956 | 37.1779 | 36.3056 | 33.3902 | 34.4019 | 36.2954 | 36.4709 | 37.4049 | 36.2762 | 33.1972 | 32.7735 | 34.6316 | 34.977 | 33.3929 | 34.4017 | 34.2728 | 34.4239 | 34.2142 | 34.2785 | 34.4169 | 34.0491 | 34.2245 | 36.067 | 35.0654 | 36.4452 | 36.4357 | 33.4629 | 93.8097 | 94.0633 | 93.4558
2022-09-08 04:44 | 6:54 | 34.1711 | 31.954 | 34.5086 | 37.2012 | 34.3865 | 33.97 | 34.6776 | 35.5123 | 36.5796 | 37.444 | 36.9233 | 38.0745 | 34.385 | 34.391 | 34.1693 | 35.0564 | 35.0154 | 35.4696 | 36.3419 | 36.5682 | 33.1067 | 31.6095 | 93.4938 | 35.7058 | 33.0264 | 35.0072 | 33.1812 | 33.0683 | 33.382 | 34.6284 | 34.1978 | 33.9873 | 37.1821 | 36.2998 | 33.383 | 34.4125 | 36.2858 | 36.4787 | 37.402 | 36.2884 | 33.1923 | 32.781 | 34.6249 | 34.9706 | 33.4032 | 34.4007 | 34.2819 | 34.4111 | 34.2266 | 34.2701 | 34.4257 | 34.053 | 34.2142 | 36.0405 | 35.056 | 36.4402 | 36.456 | 33.4806 | 93.7461 | 93.9858 | 93.4631
2022-09-08 04:44 | 6:54 | 34.2315 | 32.6005 | 34.5652 | 37.1868 | 34.3695 | 33.9753 | 34.6974 | 35.5204 | 36.5932 | 37.439 | 36.9253 | 38.0672 | 34.3715 | 34.3897 | 34.1821 | 35.0455 | 35.0228 | 35.4585 | 36.3325 | 36.5578 | 33.6942 | 32.2843 | 93.4572 | 35.63 | 33.0139 | 35.0035 | 33.1988 | 33.0544 | 33.3657 | 34.6474 | 34.186 | 34.0106 | 37.188 | 36.2969 | 33.3673 | 34.4234 | 36.3056 | 36.4716 | 37.4112 | 36.2843 | 33.2018 | 32.7812 | 34.6394 | 34.9915 | 33.4304 | 34.3736 | 34.2796 | 34.4036 | 34.2283 | 34.2543 | 34.4334 | 34.0465 | 34.2266 | 36.0647 | 35.0592 | 36.4343 | 36.4481 | 33.4837 | 93.6376 | 93.9096 | 93.4447
2022-09-08 04:44 | 6:54 | 34.5367 | 33.2935 | 34.7737 | 37.1834 | 34.3931 | 33.9789 | 34.6823 | 35.5147 | 36.5963 | 37.4528 | 36.9479 | 38.0637 | 34.3791 | 34.4178 | 34.1847 | 35.0491 | 35.0242 | 35.4642 | 36.3504 | 36.5566 | 34.4149 | 33.2341 | 93.4153 | 35.7048 | 33.0043 | 34.9808 | 33.1922 | 33.0699 | 33.3576 | 34.6324 | 34.2093 | 34.0027 | 37.1902 | 36.2973 | 33.3913 | 34.4134 | 36.2998 | 36.4893 | 37.4092 | 36.2954 | 33.2086 | 32.7983 | 34.6401 | 34.9891 | 33.4372 | 34.3656 | 34.3035 | 34.4305 | 34.2437 | 34.2664 | 34.4252 | 34.0566 | 34.2283 | 36.045 | 35.0527 | 36.4489 | 36.442 | 33.4821 | 93.6086 | 93.869 | 93.4195
2022-09-08 04:45 | 6:54 | 35.2317 | 33.379 | 35.0165 | 37.2357 | 34.3943 | 33.9986 | 34.7061 | 35.5183 | 36.5953 | 37.4663 | 36.935 | 38.0661 | 34.3557 | 34.3883 | 34.1909 | 35.055 | 35.017 | 35.4794 | 36.3317 | 36.5541 | 35.084 | 33.4375 | 93.3606 | 35.729 | 33.0257 | 35.0095 | 33.1972 | 33.0718 | 33.3902 | 34.6251 | 34.1999 | 34.0071 | 37.1931 | 36.3091 | 33.3847 | 34.4074 | 36.2969 | 36.4969 | 37.4115 | 36.2858 | 33.2134 | 32.7914 | 34.6542 | 34.9923 | 33.4356 | 34.4075 | 34.3005 | 34.4159 | 34.2337 | 34.2804 | 34.4299 | 34.0581 | 34.2437 | 36.0573 | 35.0774 | 36.4356 | 36.4629 | 33.4746 | 93.4873 | 93.7791 | 93.2973
2022-09-08 04:45 | 6:55 | 35.8666 | 33.4301 | 35.2789 | 37.2768 | 34.3859 | 33.9977 | 34.7058 | 35.5179 | 36.6051 | 37.4321 | 36.9373 | 38.0772 | 34.3709 | 34.3888 | 34.1814 | 35.0728 | 35.0383 | 35.4964 | 36.3471 | 36.5718 | 35.6713 | 33.3635 | 93.3436 | 35.7977 | 33.0272 | 35.0018 | 33.1923 | 33.0641 | 33.383 | 34.6465 | 34.213 | 34.0234 | 37.197 | 36.3036 | 33.3974 | 34.4189 | 36.2973 | 36.4876 | 37.4215 | 36.3056 | 33.2126 | 32.8041 | 34.6642 | 35.0064 | 33.4354 | 34.3735 | 34.302 | 34.4245 | 34.2249 | 34.2507 | 34.4195 | 34.0609 | 34.2337 | 36.047 | 35.0625 | 36.4268 | 36.462 | 33.4907 | 93.4857 | 93.7126 | 93.3553
2022-09-08 04:45 | 6:55 | 36.3105 | 33.4427 | 35.4508 | 37.4175 | 34.3905 | 34.0084 | 34.7005 | 35.5141 | 36.5899 | 37.4635 | 36.9258 | 38.0714 | 34.3693 | 34.3921 | 34.1896 | 35.0593 | 35.0477 | 35.4928 | 36.3596 | 36.5528 | 36.0547 | 33.0662 | 93.2765 | 35.8129 | 33.0198 | 35.0084 | 33.2018 | 33.0724 | 33.3673 | 34.6492 | 34.1855 | 34.0153 | 37.1996 | 36.3103 | 33.3963 | 34.4302 | 36.3091 | 36.4922 | 37.4178 | 36.2998 | 33.224 | 32.8137 | 34.6769 | 35.0041 | 33.446 | 34.3871 | 34.293 | 34.4136 | 34.2222 | 34.2644 | 34.4276 | 34.0489 | 34.2249 | 36.061 | 35.0707 | 36.4443 | 36.473 | 33.5152 | 93.4024 | 93.6383 | 93.3024
2022-09-08 04:45 | 6:55 | 36.445 | 33.4021 | 35.5373 | 37.3281 | 34.4121 | 34.0076 | 34.7002 | 35.5107 | 36.5958 | 37.4576 | 36.9411 | 38.0846 | 34.371 | 34.3827 | 34.2086 | 35.0752 | 35.0481 | 35.5033 | 36.3547 | 36.5687 | 36.1512 | 32.7523 | 93.1492 | 35.7844 | 33.0245 | 34.9991 | 33.2086 | 33.0803 | 33.3913 | 34.6442 | 34.2027 | 34.0055 | 37.1864 | 36.3134 | 33.3887 | 34.4329 | 36.3036 | 36.5047 | 37.4107 | 36.2969 | 33.2014 | 32.8173 | 34.676 | 35.0186 | 33.4515 | 34.379 | 34.2838 | 34.4269 | 34.2036 | 34.2642 | 34.4221 | 34.0783 | 34.2222 | 36.0726 | 35.0578 | 36.4325 | 36.4722 | 33.4817 | 93.2956 | 93.5791 | 93.1475
2022-09-08 04:45 | 6:55 | 36.5142 | 33.5175 | 35.5223 | 37.4006 | 34.3987 | 34.0135 | 34.7073 | 35.5197 | 36.5901 | 37.4609 | 36.953 | 38.0769 | 34.3707 | 34.3639 | 34.1906 | 35.0852 | 35.0379 | 35.5 | 36.3681 | 36.5665 | 36.2239 | 32.5999 | 93.1021 | 35.8391 | 33.046 | 35.0099 | 33.2134 | 33.0913 | 33.3847 | 34.6443 | 34.1824 | 34.0163 | 37.1972 | 36.3222 | 33.4054 | 34.4347 | 36.3103 | 36.4972 | 37.426 | 36.2973 | 33.2116 | 32.8255 | 34.6833 | 35.032 | 33.4714 | 34.3906 | 34.3006 | 34.4188 | 34.2465 | 34.2582 | 34.4092 | 34.07 | 34.2036 | 36.0825 | 35.0657 | 36.445 | 36.4723 | 33.503 | 93.2029 | 93.4237 | 93.1156
2022-09-08 04:45 | 6:55 | 36.4271 | 33.7653 | 35.4901 | 37.3376 | 34.4099 | 34.0071 | 34.7194 | 35.5352 | 36.5864 | 37.4631 | 36.9438 | 38.0831 | 34.3559 | 34.3606 | 34.2071 | 35.0849 | 35.0659 | 35.4804 | 36.3769 | 36.5731 | 36.1073 | 32.4004 | 93.0322 | 35.8156 | 33.0433 | 35.0164 | 33.2126 | 33.0882 | 33.3974 | 34.6545 | 34.2058 | 34.0314 | 37.2081 | 36.3185 | 33.3953 | 34.4333 | 36.3134 | 36.5039 | 37.4305 | 36.3091 | 33.2332 | 32.8258 | 34.6948 | 35.0315 | 33.4854 | 34.3708 | 34.2917 | 34.4209 | 34.2557 | 34.254 | 34.4068 | 34.0768 | 34.2465 | 36.0768 | 35.0759 | 36.4554 | 36.4502 | 33.5153 | 93.0775 | 93.3192 | 93.0276
2022-09-08 04:46 | 6:56 | 36.3245 | 33.9404 | 35.448 | 37.4136 | 34.4176 | 34.025 | 34.7373 | 35.5428 | 36.6035 | 37.4777 | 36.9397 | 38.0932 | 34.3669 | 34.3735 | 34.2131 | 35.0886 | 35.0513 | 35.4941 | 36.371 | 36.5806 | 36.0257 | 32.298 | 92.9562 | 35.8334 | 33.0541 | 35.0322 | 33.224 | 33.0843 | 33.3963 | 34.644 | 34.2023 | 34.0164 | 37.2161 | 36.3146 | 33.3958 | 34.4301 | 36.3222 | 36.5097 | 37.4361 | 36.3036 | 33.2265 | 32.8309 | 34.6774 | 35.0104 | 33.5035 | 34.3874 | 34.2787 | 34.4249 | 34.2392 | 34.2614 | 34.42 | 34.073 | 34.2557 | 36.0735 | 35.0647 | 36.4446 | 36.4764 | 33.5172 | 92.9891 | 93.1928 | 92.9156
2022-09-08 04:46 | 6:56 | 36.2788 | 34.0794 | 35.3808 | 37.4483 | 34.4144 | 34.0144 | 34.7112 | 35.5382 | 36.6101 | 37.4614 | 36.9632 | 38.093 | 34.3586 | 34.3815 | 34.1929 | 35.0907 | 35.0516 | 35.5142 | 36.3636 | 36.5695 | 35.9405 | 32.2412 | 92.8581 | 35.8694 | 33.0462 | 35.0279 | 33.2014 | 33.0913 | 33.3887 | 34.6452 | 34.2122 | 34.0279 | 37.2188 | 36.3242 | 33.4118 | 34.4461 | 36.3185 | 36.4921 | 37.4309 | 36.3103 | 33.2322 | 32.8493 | 34.6903 | 35.0182 | 33.5068 | 34.3736 | 34.2874 | 34.4249 | 34.2272 | 34.2462 | 34.4177 | 34.0891 | 34.2392 | 36.0837 | 35.0938 | 36.443 | 36.4592 | 33.5174 | 92.8511 | 93.1052 | 92.8051
2022-09-08 04:46 | 6:56 | 36.2664 | 34.1722 | 35.3289 | 37.502 | 34.4039 | 34.0232 | 34.7331 | 35.5579 | 36.6172 | 37.4664 | 36.9557 | 38.0979 | 34.3725 | 34.3729 | 34.2063 | 35.0762 | 35.066 | 35.5114 | 36.3824 | 36.5899 | 35.892 | 32.2073 | 92.8002 | 35.8776 | 33.0232 | 35.0307 | 33.2116 | 33.1008 | 33.4054 | 34.6327 | 34.1963 | 34.0323 | 37.2037 | 36.3277 | 33.3959 | 34.4513 | 36.3146 | 36.5045 | 37.4493 | 36.3134 | 33.2183 | 32.8493 | 34.703 | 35.0501 | 33.5036 | 34.3689 | 34.2823 | 34.4237 | 34.2286 | 34.2474 | 34.4024 | 34.0888 | 34.2272 | 36.0815 | 35.079 | 36.4702 | 36.4732 | 33.5177 | 92.7434 | 92.9807 | 92.6954
2022-09-08 04:46 | 6:56 | 36.2457 | 34.3533 | 35.2844 | 37.4409 | 34.413 | 34.0151 | 34.7312 | 35.5468 | 36.617 | 37.4783 | 36.9627 | 38.0985 | 34.3397 | 34.3434 | 34.2004 | 35.0872 | 35.0797 | 35.4992 | 36.3898 | 36.5893 | 35.8839 | 32.1917 | 92.6863 | 35.9036 | 33.0585 | 35.036 | 33.2332 | 33.0942 | 33.3953 | 34.6458 | 34.1983 | 34.0228 | 37.2144 | 36.3194 | 33.3964 | 34.4507 | 36.3242 | 36.5083 | 37.4498 | 36.3222 | 33.2367 | 32.8503 | 34.7131 | 35.0622 | 33.5178 | 34.381 | 34.3038 | 34.412 | 34.2417 | 34.2508 | 34.4244 | 34.0901 | 34.2286 | 36.0968 | 35.0927 | 36.4383 | 36.4773 | 33.5342 | 92.6337 | 92.8667 | 92.6198
2022-09-08 04:46 | 6:56 | 36.237 | 34.441 | 35.2312 | 37.4457 | 34.4088 | 34.0399 | 34.729 | 35.5244 | 36.6257 | 37.4678 | 36.96 | 38.071 | 34.3448 | 34.3884 | 34.2183 | 35.0962 | 35.0867 | 35.5111 | 36.3874 | 36.5962 | 35.8755 | 32.1767 | 92.6125 | 35.9193 | 33.044 | 35.035 | 33.2265 | 33.0909 | 33.3958 | 34.6422 | 34.2157 | 34.0341 | 37.2173 | 36.3419 | 33.4139 | 34.4336 | 36.3277 | 36.5241 | 37.4571 | 36.3185 | 33.2392 | 32.8744 | 34.7217 | 35.0818 | 33.5252 | 34.3957 | 34.3108 | 34.4337 | 34.2426 | 34.2349 | 34.4303 | 34.1048 | 34.2417 | 36.0807 | 35.0825 | 36.4567 | 36.4916 | 33.5213 | 92.5383 | 92.7232 | 92.5442
2022-09-08 04:46 | 6:56 | 36.2561 | 34.5368 | 35.2397 | 37.4657 | 34.4049 | 34.0277 | 34.7323 | 35.534 | 36.6228 | 37.4774 | 36.9447 | 38.088 | 34.3559 | 34.3738 | 34.205 | 35.0937 | 35.0711 | 35.5178 | 36.3807 | 36.5841 | 35.909 | 32.1795 | 92.5218 | 35.9416 | 33.0453 | 35.0457 | 33.2322 | 33.101 | 33.4118 | 34.6566 | 34.224 | 34.0281 | 37.2342 | 36.335 | 33.4019 | 34.4405 | 36.3194 | 36.5271 | 37.4441 | 36.3146 | 33.2212 | 32.8768 | 34.7263 | 35.065 | 33.5211 | 34.3959 | 34.307 | 34.4367 | 34.2332 | 34.2412 | 34.3986 | 34.0823 | 34.2426 | 36.0901 | 35.0755 | 36.4624 | 36.4915 | 33.5494 | 92.3488 | 92.5613 | 92.4145
2022-09-08 04:47 | 6:56 | 36.311 | 34.6204 | 35.2958 | 37.4547 | 34.4066 | 34.0406 | 34.7309 | 35.5404 | 36.6228 | 37.4869 | 36.9513 | 38.1117 | 34.3519 | 34.3652 | 34.2311 | 35.0961 | 35.0998 | 35.5165 | 36.4011 | 36.6004 | 35.9844 | 32.1925 | 92.4402 | 35.9225 | 33.0538 | 35.019 | 33.2183 | 33.1132 | 33.3959 | 34.6508 | 34.2293 | 34.0292 | 37.2271 | 36.331 | 33.4015 | 34.4356 | 36.3419 | 36.5184 | 37.4604 | 36.3242 | 33.2451 | 32.8781 | 34.7441 | 35.0924 | 33.5418 | 34.3954 | 34.3032 | 34.4328 | 34.2406 | 34.2477 | 34.4138 | 34.1107 | 34.2332 | 36.0982 | 35.0822 | 36.4458 | 36.4979 | 33.5348 | 92.2306 | 92.4099 | 92.325
2022-09-08 04:47 | 6:57 | 36.3846 | 34.6779 | 35.3474 | 37.6071 | 34.4155 | 34.042 | 34.7374 | 35.5701 | 36.6436 | 37.473 | 36.9653 | 38.0873 | 34.3565 | 34.3593 | 34.2318 | 35.1178 | 35.0914 | 35.5206 | 36.3855 | 36.6017 | 36.0379 | 32.2132 | 92.2891 | 35.9363 | 33.0581 | 35.058 | 33.2367 | 33.1073 | 33.3964 | 34.6519 | 34.2281 | 34.0389 | 37.2307 | 36.3362 | 33.4207 | 34.4491 | 36.335 | 36.5204 | 37.4406 | 36.3277 | 33.2378 | 32.8855 | 34.758 | 35.0822 | 33.5427 | 34.3689 | 34.2988 | 34.4064 | 34.2448 | 34.249 | 34.4144 | 34.0931 | 34.2406 | 36.1096 | 35.0905 | 36.4706 | 36.493 | 33.5671 | 92.09 | 92.2629 | 92.1651
2022-09-08 04:47 | 6:57 | 36.4294 | 34.7581 | 35.4038 | 37.4633 | 34.4052 | 34.0418 | 34.733 | 35.5635 | 36.6296 | 37.4903 | 36.9626 | 38.0923 | 34.338 | 34.3494 | 34.2308 | 35.1177 | 35.1007 | 35.5272 | 36.414 | 36.6148 | 36.0943 | 32.2399 | 92.2119 | 35.9195 | 33.0735 | 35.0388 | 33.2392 | 33.106 | 33.4139 | 34.6718 | 34.2283 | 34.0372 | 37.2297 | 36.3214 | 33.4079 | 34.4598 | 36.331 | 36.5174 | 37.4539 | 36.3194 | 33.2414 | 32.8808 | 34.7575 | 35.084 | 33.5376 | 34.3935 | 34.2945 | 34.4295 | 34.2515 | 34.252 | 34.3916 | 34.1158 | 34.2448 | 36.0992 | 35.0828 | 36.4775 | 36.4875 | 33.5549 | 91.9889 | 92.1864 | 92.104
2022-09-08 04:47 | 6:57 | 36.4956 | 34.8055 | 35.4322 | 37.4842 | 34.4237 | 34.0472 | 34.7285 | 35.5465 | 36.641 | 37.4928 | 36.9634 | 38.1143 | 34.3476 | 34.3707 | 34.2451 | 35.104 | 35.0886 | 35.5286 | 36.4097 | 36.5975 | 36.1568 | 32.2664 | 92.1623 | 35.95 | 33.087 | 35.0353 | 33.2212 | 33.1105 | 33.4019 | 34.6799 | 34.2317 | 34.0511 | 37.2264 | 36.3223 | 33.4143 | 34.4368 | 36.3362 | 36.5144 | 37.4734 | 36.3419 | 33.2288 | 32.8952 | 34.7582 | 35.0908 | 33.5503 | 34.3711 | 34.3044 | 34.4129 | 34.2489 | 34.2547 | 34.3969 | 34.1089 | 34.2515 | 36.1077 | 35.0949 | 36.469 | 36.505 | 33.5698 | 91.9703 | 92.1629 | 92.0837
2022-09-08 04:47 | 6:57 | 36.579 | 34.8555 | 35.5377 | 37.5469 | 34.4104 | 34.0438 | 34.7546 | 35.5563 | 36.6597 | 37.4983 | 36.959 | 38.1025 | 34.3403 | 34.3494 | 34.2242 | 35.1088 | 35.1079 | 35.5244 | 36.4071 | 36.6161 | 36.1802 | 32.2875 | 92.191 | 35.9013 | 33.0747 | 35.0433 | 33.2451 | 33.1113 | 33.4015 | 34.6731 | 34.2226 | 34.0505 | 37.2418 | 36.3423 | 33.4249 | 34.4409 | 36.3214 | 36.5248 | 37.4624 | 36.335 | 33.2601 | 32.9132 | 34.7814 | 35.104 | 33.5648 | 34.3761 | 34.3057 | 34.4178 | 34.2584 | 34.252 | 34.4054 | 34.1128 | 34.2489 | 36.1077 | 35.0859 | 36.4631 | 36.4943 | 33.572 | 92.0098 | 92.2057 | 92.1964
2022-09-08 04:47 | 6:57 | 36.6212 | 34.9268 | 35.5773 | 37.5634 | 34.4256 | 34.0365 | 34.7549 | 35.579 | 36.6593 | 37.5149 | 36.9587 | 38.1163 | 34.3401 | 34.354 | 34.2429 | 35.0954 | 35.0939 | 35.5374 | 36.4047 | 36.6092 | 36.1769 | 32.2929 | 92.2631 | 35.9701 | 33.0834 | 35.0582 | 33.2378 | 33.1162 | 33.4207 | 34.674 | 34.223 | 34.0436 | 37.2462 | 36.3268 | 33.399 | 34.455 | 36.3223 | 36.5291 | 37.4716 | 36.331 | 33.2366 | 32.9033 | 34.7711 | 35.12 | 33.5658 | 34.3829 | 34.2996 | 34.4223 | 34.2592 | 34.2461 | 34.39 | 34.1282 | 34.2584 | 36.1365 | 35.1105 | 36.4629 | 36.497 | 33.5942 | 92.0874 | 92.318 | 92.3001
2022-09-08 04:48 | 6:58 | 36.6317 | 34.9678 | 35.579 | 37.4531 | 34.4147 | 34.0577 | 34.739 | 35.5725 | 36.6335 | 37.4946 | 36.941 | 38.099 | 34.3429 | 34.3477 | 34.2584 | 35.1077 | 35.1198 | 35.5422 | 36.3963 | 36.6186 | 36.1773 | 32.2882 | 92.3256 | 36.0421 | 33.0852 | 35.0474 | 33.2414 | 33.114 | 33.4079 | 34.6687 | 34.2229 | 34.0345 | 37.2411 | 36.3232 | 33.4086 | 34.4614 | 36.3423 | 36.5232 | 37.4629 | 36.3362 | 33.2435 | 32.9196 | 34.7767 | 35.1432 | 33.5879 | 34.3669 | 34.305 | 34.4268 | 34.2644 | 34.2366 | 34.3894 | 34.1206 | 34.2592 | 36.131 | 35.089 | 36.467 | 36.5367 | 33.5765 | 92.1672 | 92.3961 | 92.3591
2022-09-08 04:48 | 6:58 | 36.6035 | 34.9992 | 35.6245 | 37.4985 | 34.4178 | 34.0536 | 34.749 | 35.5752 | 36.6461 | 37.5098 | 36.9603 | 38.1127 | 34.3268 | 34.3478 | 34.2622 | 35.1184 | 35.1082 | 35.5301 | 36.4098 | 36.6274 | 35.7937 | 32.1994 | 92.3928 | 35.986 | 33.0874 | 35.0371 | 33.2288 | 33.1393 | 33.4143 | 34.6647 | 34.2181 | 34.0382 | 37.244 | 36.3295 | 33.3991 | 34.4633 | 36.3268 | 36.5271 | 37.4903 | 36.3214 | 33.2547 | 32.9111 | 34.7927 | 35.1315 | 33.5912 | 34.3615 | 34.3183 | 34.4336 | 34.2636 | 34.2515 | 34.389 | 34.132 | 34.2644 | 36.1344 | 35.0969 | 36.4766 | 36.5163 | 33.6061 | 92.2496 | 92.4852 | 92.413
2022-09-08 04:48 | 6:58 | 31.441 | 32.1645 | 34.5235 | 37.4953 | 34.4085 | 34.0579 | 34.7447 | 35.567 | 36.6503 | 37.5163 | 36.965 | 38.1016 | 34.308 | 34.3526 | 34.2731 | 35.1241 | 35.1173 | 35.5302 | 36.4014 | 36.6428 | 30.8059 | 31.6261 | 92.4489 | 36.0237 | 33.0803 | 35.0349 | 33.2601 | 33.1023 | 33.4249 | 34.6739 | 34.2169 | 34.0481 | 37.2349 | 36.3401 | 33.4359 | 34.4514 | 36.3232 | 36.5112 | 37.4824 | 36.3223 | 33.2418 | 32.9218 | 34.7773 | 35.1204 | 33.6137 | 34.3704 | 34.3151 | 34.4344 | 34.249 | 34.2602 | 34.3754 | 34.1157 | 34.2636 | 36.127 | 35.0926 | 36.4765 | 36.5102 | 33.6015 | 92.4007 | 92.5243 | 92.5866
2022-09-08 04:48 | 6:58 | 30.9538 | 29.2694 | 33.0457 | 37.3321 | 34.4113 | 34.0686 | 34.7361 | 35.5603 | 36.6473 | 37.5084 | 36.9412 | 38.0969 | 34.3268 | 34.3511 | 34.2585 | 35.1124 | 35.1291 | 35.5211 | 36.4135 | 36.6231 | 29.438 | 29.6154 | 92.4946 | 35.8798 | 33.0864 | 35.0486 | 33.2366 | 33.1271 | 33.399 | 34.658 | 34.2187 | 34.0322 | 37.2458 | 36.342 | 33.4216 | 34.4462 | 36.3295 | 36.513 | 37.4931 | 36.3423 | 33.2322 | 32.9222 | 34.7824 | 35.1452 | 33.5772 | 34.3675 | 34.3258 | 34.4054 | 34.2604 | 34.2486 | 34.4017 | 34.1419 | 34.249 | 36.141 | 35.0784 | 36.4674 | 36.5179 | 33.6095 | 92.4369 | 92.5491 | 92.6306
2022-09-08 04:48 | 6:58 | 31.1226 | 28.1334 | 32.5368 | 37.4049 | 34.4305 | 34.0545 | 34.7512 | 35.5681 | 36.6563 | 37.5222 | 36.9639 | 38.1043 | 34.3219 | 34.3259 | 34.2445 | 35.1049 | 35.1016 | 35.5374 | 36.4239 | 36.6466 | 29.5841 | 28.5909 | 92.3945 | 35.8368 | 33.0911 | 35.0373 | 33.2435 | 33.11 | 33.4086 | 34.6675 | 34.2237 | 34.0528 | 37.2423 | 36.3418 | 33.4441 | 34.4451 | 36.3401 | 36.5393 | 37.4679 | 36.3268 | 33.2396 | 32.9435 | 34.8011 | 35.1268 | 33.5869 | 34.3641 | 34.3361 | 34.42 | 34.2658 | 34.2589 | 34.391 | 34.1225 | 34.2604 | 36.1208 | 35.0916 | 36.4634 | 36.4968 | 33.615 | 92.4751 | 92.5757 | 92.6436
2022-09-08 04:48 | 6:58 | 31.0993 | 28.3217 | 32.4212 | 37.3016 | 34.4197 | 34.0664 | 34.7672 | 35.5531 | 36.654 | 37.5386 | 36.9662 | 38.1179 | 34.3088 | 34.3255 | 34.2608 | 35.1121 | 35.1326 | 35.543 | 36.4021 | 36.6365 | 29.4323 | 28.319 | 92.5729 | 35.7413 | 33.095 | 35.0404 | 33.2547 | 33.136 | 33.3991 | 34.6809 | 34.2048 | 34.0498 | 37.2234 | 36.3319 | 33.4387 | 34.4551 | 36.342 | 36.522 | 37.4802 | 36.3232 | 33.2347 | 32.9322 | 34.7804 | 35.1172 | 33.5914 | 34.3676 | 34.3346 | 34.4248 | 34.2647 | 34.2389 | 34.3897 | 34.1434 | 34.2658 | 36.1455 | 35.077 | 36.4712 | 36.5262 | 33.6032 | 92.5585 | 92.6653 | 92.7206
2022-09-08 04:49 | 6:59 | 31.2866 | 29.8765 | 32.4846 | 37.3311 | 34.4433 | 34.0679 | 34.7704 | 35.5627 | 36.6557 | 37.516 | 36.9551 | 38.109 | 34.3074 | 34.3294 | 34.2642 | 35.0882 | 35.1232 | 35.5245 | 36.4094 | 36.6274 | 29.6147 | 27.9661 | 92.6466 | 35.6253 | 33.0996 | 35.0551 | 33.2418 | 33.1123 | 33.4359 | 34.6532 | 34.2069 | 34.0423 | 37.2306 | 36.3205 | 33.4164 | 34.4376 | 36.3418 | 36.5393 | 37.4881 | 36.3295 | 33.2437 | 32.9188 | 34.8224 | 35.1381 | 33.602 | 34.3522 | 34.3449 | 34.4016 | 34.2524 | 34.229 | 34.4178 | 34.1484 | 34.2647 | 36.149 | 35.1028 | 36.459 | 36.5112 | 33.5908 | 92.6488 | 92.7339 | 92.7956
2022-09-08 04:49 | 6:59 | 31.3847 | 29.9612 | 32.4905 | 37.2915 | 34.4169 | 34.0579 | 34.7693 | 35.5767 | 36.6559 | 37.5243 | 36.9469 | 38.1065 | 34.3091 | 34.3144 | 34.2815 | 35.1045 | 35.1065 | 35.5274 | 36.3766 | 36.6469 | 29.8953 | 27.5953 | 92.4997 | 35.7009 | 33.0799 | 35.0447 | 33.2322 | 33.1061 | 33.4216 | 34.671 | 34.2035 | 34.0519 | 37.2355 | 36.3545 | 33.4242 | 34.4276 | 36.3319 | 36.5195 | 37.5005 | 36.3401 | 33.2415 | 32.9346 | 34.7982 | 35.1727 | 33.6131 | 34.3597 | 34.3281 | 34.4262 | 34.2657 | 34.2635 | 34.3883 | 34.1442 | 34.2524 | 36.1461 | 35.0822 | 36.4693 | 36.4956 | 33.6177 | 92.7684 | 92.819 | 92.8349
2022-09-08 04:49 | 6:59 | 31.4535 | 29.8696 | 32.4006 | 37.3206 | 34.4257 | 34.0453 | 34.7874 | 35.5518 | 36.66 | 37.5435 | 36.9504 | 38.1076 | 34.2994 | 34.3282 | 34.29 | 35.0982 | 35.117 | 35.5303 | 36.3804 | 36.6405 | 30.0383 | 27.3319 | 92.617 | 35.606 | 33.0883 | 35.0354 | 33.2396 | 33.1111 | 33.4441 | 34.6931 | 34.2123 | 34.0527 | 37.2404 | 36.3434 | 33.4107 | 34.4551 | 36.3205 | 36.5471 | 37.4924 | 36.342 | 33.2377 | 32.9498 | 34.8164 | 35.1494 | 33.5788 | 34.3612 | 34.3266 | 34.4062 | 34.2619 | 34.2428 | 34.3888 | 34.1481 | 34.2657 | 36.1321 | 35.0774 | 36.4757 | 36.5033 | 33.606 | 92.754 | 92.9119 | 92.7969
2022-09-08 04:49 | 6:59 | 31.4701 | 29.8046 | 32.367 | 37.3506 | 34.4334 | 34.0403 | 34.7863 | 35.5673 | 36.6652 | 37.5291 | 36.9459 | 38.1067 | 34.3144 | 34.3192 | 34.2777 | 35.108 | 35.1165 | 35.5339 | 36.3849 | 36.6523 | 30.095 | 27.0667 | 92.6729 | 35.596 | 33.1026 | 35.0367 | 33.2347 | 33.1138 | 33.4387 | 34.6848 | 34.2145 | 34.0544 | 37.2356 | 36.3311 | 33.4327 | 34.4414 | 36.3545 | 36.5224 | 37.5005 | 36.3418 | 33.2355 | 32.9562 | 34.8036 | 35.1509 | 33.5764 | 34.3588 | 34.3258 | 34.4174 | 34.2921 | 34.2258 | 34.3921 | 34.155 | 34.2619 | 36.1348 | 35.0925 | 36.4777 | 36.5278 | 33.595 | 92.9127 | 93.0447 | 92.932
2022-09-08 04:49 | 6:59 | 31.4164 | 29.6239 | 32.2765 | 37.2141 | 34.4252 | 34.0467 | 34.7953 | 35.5734 | 36.679 | 37.5452 | 36.9576 | 38.1116 | 34.299 | 34.3273 | 34.2935 | 35.1226 | 35.1328 | 35.5264 | 36.4021 | 36.6218 | 30.0874 | 26.8144 | 92.833 | 35.6254 | 33.0864 | 35.0484 | 33.2437 | 33.131 | 33.4164 | 34.6711 | 34.2096 | 34.0535 | 37.2395 | 36.3501 | 33.4319 | 34.4477 | 36.3434 | 36.5273 | 37.5192 | 36.3319 | 33.2362 | 32.9419 | 34.7967 | 35.1537 | 33.5766 | 34.348 | 34.3246 | 34.4225 | 34.2835 | 34.2403 | 34.3827 | 34.163 | 34.2921 | 36.1388 | 35.0763 | 36.4602 | 36.5202 | 33.6218 | 93.0716 | 93.1432 | 93.1025
2022-09-08 04:49 | 6:59 | 31.3302 | 29.2049 | 32.3078 | 37.2206 | 34.4299 | 34.057 | 34.7877 | 35.58 | 36.6842 | 37.545 | 36.9454 | 38.094 | 34.2968 | 34.3116 | 34.2744 | 35.1127 | 35.1465 | 35.5249 | 36.3941 | 36.644 | 30.0278 | 26.6454 | 92.9404 | 35.4817 | 33.1019 | 35.0483 | 33.2415 | 33.1272 | 33.4242 | 34.6845 | 34.2055 | 34.0474 | 37.2325 | 36.3299 | 33.4299 | 34.4533 | 36.3311 | 36.5395 | 37.4926 | 36.3205 | 33.255 | 32.9568 | 34.7903 | 35.1547 | 33.5852 | 34.3584 | 34.3525 | 34.3985 | 34.2763 | 34.2407 | 34.3639 | 34.1613 | 34.2835 | 36.137 | 35.0949 | 36.4768 | 36.5159 | 33.6285 | 93.2174 | 93.2832 | 93.1287
2022-09-08 04:50 | 6:59 | 31.2093 | 28.9561 | 32.218 | 37.2205 | 34.4195 | 34.0426 | 34.8009 | 35.5783 | 36.686 | 37.5371 | 36.9464 | 38.109 | 34.3193 | 34.3166 | 34.2868 | 35.1212 | 35.1129 | 35.5262 | 36.3929 | 36.6448 | 29.9406 | 26.4355 | 93.0476 | 35.5184 | 33.0822 | 35.052 | 33.2377 | 33.131 | 33.4107 | 34.6738 | 34.2064 | 34.0497 | 37.2535 | 36.3463 | 33.4179 | 34.4558 | 36.3501 | 36.5404 | 37.5157 | 36.3545 | 33.2618 | 32.9817 | 34.8149 | 35.1582 | 33.5795 | 34.3529 | 34.3515 | 34.4203 | 34.2662 | 34.2518 | 34.3606 | 34.1473 | 34.2763 | 36.1384 | 35.0829 | 36.4724 | 36.5304 | 33.6339 | 93.3696 | 93.4372 | 93.2315
2022-09-08 04:50 | 7:00 | 31.0707 | 28.7486 | 32.1098 | 37.2155 | 34.4276 | 34.0697 | 34.8114 | 35.5791 | 36.6608 | 37.5428 | 36.9558 | 38.1134 | 34.2921 | 34.3075 | 34.2777 | 35.1101 | 35.1326 | 35.5159 | 36.4013 | 36.6552 | 29.8329 | 26.352 | 93.1123 | 35.5407 | 33.0958 | 35.0545 | 33.2355 | 33.146 | 33.4327 | 34.688 | 34.2044 | 34.057 | 37.2402 | 36.3551 | 33.4211 | 34.4544 | 36.3299 | 36.5193 | 37.5096 | 36.3434 | 33.2339 | 32.9608 | 34.8143 | 35.1425 | 33.594 | 34.3391 | 34.349 | 34.409 | 34.2883 | 34.2593 | 34.3735 | 34.1564 | 34.2662 | 36.154 | 35.0849 | 36.4829 | 36.5164 | 33.6119 | 93.554 | 93.5915 | 93.3279
2022-09-08 04:50 | 7:00 | 30.879 | 28.527 | 31.8918 | 37.2679 | 34.4221 | 34.0481 | 34.8158 | 35.5758 | 36.6667 | 37.5326 | 36.9392 | 38.1146 | 34.2805 | 34.3067 | 34.2886 | 35.1212 | 35.1446 | 35.5092 | 36.3864 | 36.6523 | 29.712 | 26.2061 | 93.212 | 35.5159 | 33.1015 | 35.0327 | 33.2362 | 33.1252 | 33.4319 | 34.697 | 34.2111 | 34.056 | 37.248 | 36.3358 | 33.4368 | 34.4333 | 36.3463 | 36.5252 | 37.5022 | 36.3311 | 33.2442 | 32.9501 | 34.791 | 35.1491 | 33.601 | 34.3411 | 34.3519 | 34.4133 | 34.2702 | 34.2651 | 34.3815 | 34.1587 | 34.2883 | 36.14 | 35.0864 | 36.466 | 36.5336 | 33.6372 | 93.6717 | 93.7259 | 93.4366
2022-09-08 04:50 | 7:00 | 30.6109 | 28.3625 | 31.7121 | 37.2752 | 34.4092 | 34.0699 | 34.8132 | 35.5808 | 36.6765 | 37.5535 | 36.9295 | 38.1244 | 34.2961 | 34.2951 | 34.2921 | 35.1149 | 35.1361 | 35.5199 | 36.3896 | 36.6555 | 29.5772 | 26.0063 | 93.3678 | 35.5229 | 33.0989 | 35.0486 | 33.255 | 33.1299 | 33.4299 | 34.6682 | 34.1958 | 34.0448 | 37.2259 | 36.3541 | 33.4366 | 34.4253 | 36.3551 | 36.5339 | 37.5181 | 36.3501 | 33.2641 | 32.9577 | 34.7905 | 35.1399 | 33.5803 | 34.3517 | 34.3619 | 34.4091 | 34.2901 | 34.2621 | 34.3729 | 34.1535 | 34.2702 | 36.1384 | 35.0767 | 36.4576 | 36.5188 | 33.6095 | 93.8166 | 93.926 | 93.5956
2022-09-08 04:50 | 7:00 | 29.8123 | 28.391 | 31.2326 | 37.3198 | 34.4068 | 34.0427 | 34.8182 | 35.5821 | 36.6852 | 37.5471 | 36.9454 | 38.103 | 34.2845 | 34.2843 | 34.306 | 35.1242 | 35.1479 | 35.5202 | 36.3783 | 36.6665 | 29.4212 | 25.8308 | 93.302 | 35.3418 | 33.0881 | 35.0609 | 33.2618 | 33.1138 | 33.4179 | 34.6784 | 34.2027 | 34.0429 | 37.2613 | 36.3467 | 33.4464 | 34.4445 | 36.3358 | 36.5284 | 37.5049 | 36.3299 | 33.2474 | 32.9888 | 34.7963 | 35.1556 | 33.571 | 34.3372 | 34.3367 | 34.4104 | 34.2698 | 34.27 | 34.3434 | 34.1526 | 34.2901 | 36.1559 | 35.0828 | 36.4697 | 36.5357 | 33.6025 | 93.9953 | 94.1089 | 93.5853
2022-09-08 04:50 | 7:00 | 27.4174 | 28.2068 | 30.728 | 37.2469 | 34.42 | 34.0491 | 34.8374 | 35.5953 | 36.6676 | 37.547 | 36.9595 | 38.1254 | 34.2917 | 34.2711 | 34.3018 | 35.1027 | 35.1383 | 35.5279 | 36.3933 | 36.6486 | 29.3051 | 25.6862 | 93.4017 | 35.4154 | 33.1018 | 35.04 | 33.2339 | 33.1379 | 33.4211 | 34.6776 | 34.1967 | 34.0396 | 37.2489 | 36.3513 | 33.4266 | 34.4427 | 36.3541 | 36.5414 | 37.517 | 36.3463 | 33.2647 | 32.953 | 34.8082 | 35.1548 | 33.5696 | 34.3392 | 34.3546 | 34.409 | 34.2599 | 34.2677 | 34.3884 | 34.1598 | 34.2698 | 36.1368 | 35.072 | 36.4787 | 36.541 | 33.622 | 94.2272 | 94.1958 | 93.747
2022-09-08 04:51 | 7:01 | 26.6114 | 27.921 | 30.2909 | 37.2464 | 34.4177 | 34.0433 | 34.8426 | 35.59 | 36.6955 | 37.5418 | 36.9427 | 38.0902 | 34.275 | 34.281 | 34.2799 | 35.1077 | 35.1481 | 35.5186 | 36.3855 | 36.6551 | 29.1387 | 25.5293 | 93.7114 | 35.3753 | 33.0834 | 35.031 | 33.2442 | 33.1287 | 33.4368 | 34.6966 | 34.1937 | 34.0431 | 37.254 | 36.3351 | 33.4356 | 34.4653 | 36.3467 | 36.5409 | 37.504 | 36.3551 | 33.2557 | 32.9613 | 34.7857 | 35.1405 | 33.5638 | 34.3167 | 34.3545 | 34.4054 | 34.2579 | 34.2653 | 34.3738 | 34.1701 | 34.2599 | 36.128 | 35.08 | 36.4719 | 36.5327 | 33.6116 | 94.3733 | 94.4168 | 93.9113
2022-09-08 04:51 | 7:01 | 26.1966 | 27.6635 | 29.9965 | 37.3055 | 34.4024 | 34.0726 | 34.8374 | 35.5868 | 36.6923 | 37.5433 | 36.9307 | 38.1055 | 34.2658 | 34.2811 | 34.2957 | 35.1014 | 35.1475 | 35.5252 | 36.3779 | 36.654 | 28.9432 | 25.4257 | 93.6281 | 35.2959 | 33.1016 | 35.035 | 33.2641 | 33.1355 | 33.4366 | 34.6801 | 34.2012 | 34.065 | 37.2544 | 36.3777 | 33.4423 | 34.44 | 36.3513 | 36.532 | 37.5255 | 36.3358 | 33.253 | 32.9727 | 34.7944 | 35.136 | 33.5727 | 34.329 | 34.3722 | 34.3984 | 34.2835 | 34.2663 | 34.3652 | 34.1598 | 34.2579 | 36.1349 | 35.0711 | 36.4819 | 36.5279 | 33.6111 | 94.5508 | 94.5736 | 93.8972
2022-09-08 04:51 | 7:01 | 25.9815 | 27.4545 | 29.7247 | 37.1898 | 34.4244 | 34.0538 | 34.8369 | 35.5686 | 36.6924 | 37.5438 | 36.9401 | 38.0895 | 34.2686 | 34.2883 | 34.3033 | 35.1198 | 35.1528 | 35.5165 | 36.3763 | 36.6578 | 28.7574 | 25.2991 | 93.4871 | 35.3479 | 33.0977 | 35.0488 | 33.2474 | 33.1359 | 33.4464 | 34.6922 | 34.1801 | 34.0408 | 37.2645 | 36.3389 | 33.4428 | 34.4479 | 36.3351 | 36.527 | 37.5308 | 36.3541 | 33.2687 | 32.9685 | 34.7792 | 35.1658 | 33.5799 | 34.3248 | 34.3564 | 34.4037 | 34.2687 | 34.2742 | 34.3593 | 34.1788 | 34.2835 | 36.1528 | 35.1022 | 36.4836 | 36.5308 | 33.6166 | 94.6262 | 94.7131 | 93.9073
2022-09-08 04:51 | 7:01 | 25.7519 | 27.1784 | 29.4858 | 37.0652 | 34.4303 | 34.0638 | 34.8355 | 35.5823 | 36.7049 | 37.5539 | 36.941 | 38.1053 | 34.2785 | 34.2546 | 34.3063 | 35.1136 | 35.1621 | 35.4966 | 36.3749 | 36.6527 | 28.5962 | 25.2476 | 93.6835 | 35.2795 | 33.0917 | 35.0575 | 33.2647 | 33.135 | 33.4266 | 34.6773 | 34.1844 | 34.0495 | 37.2454 | 36.3746 | 33.4239 | 34.4538 | 36.3777 | 36.5215 | 37.5127 | 36.3467 | 33.2553 | 32.9638 | 34.7785 | 35.1521 | 33.5698 | 34.284 | 34.3626 | 34.4099 | 34.2935 | 34.2957 | 34.3494 | 34.1708 | 34.2687 | 36.1364 | 35.0834 | 36.4625 | 36.5461 | 33.6094 | 94.7638 | 94.8317 | 93.9787
2022-09-08 04:51 | 7:01 | 25.5636 | 26.8691 | 29.2906 | 37.0089 | 34.3986 | 34.0516 | 34.8224 | 35.5773 | 36.6892 | 37.5314 | 36.9443 | 38.0988 | 34.2701 | 34.2671 | 34.3208 | 35.1225 | 35.1385 | 35.5178 | 36.3796 | 36.6704 | 28.4225 | 25.0404 | 93.8635 | 35.1282 | 33.1163 | 35.0625 | 33.2557 | 33.1287 | 33.4356 | 34.685 | 34.1977 | 34.0467 | 37.2346 | 36.3604 | 33.4421 | 34.4465 | 36.3389 | 36.5293 | 37.5162 | 36.3513 | 33.2622 | 32.962 | 34.7894 | 35.144 | 33.5742 | 34.3202 | 34.3826 | 34.4007 | 34.2831 | 34.2737 | 34.3707 | 34.1726 | 34.2935 | 36.1392 | 35.0807 | 36.4739 | 36.5397 | 33.6046 | 94.8842 | 94.9291 | 94.1048
2022-09-08 04:51 | 7:01 | 25.3752 | 26.6298 | 29.0305 | 37.0842 | 34.4138 | 34.0403 | 34.8419 | 35.5937 | 36.6785 | 37.546 | 36.9635 | 38.1066 | 34.2543 | 34.2517 | 34.2993 | 35.1234 | 35.1682 | 35.5278 | 36.3477 | 36.6504 | 28.2578 | 24.91 | 94.0985 | 35.1744 | 33.1005 | 35.0615 | 33.253 | 33.1504 | 33.4423 | 34.6877 | 34.2062 | 34.0482 | 37.2346 | 36.362 | 33.4182 | 34.4331 | 36.3746 | 36.5304 | 37.511 | 36.3351 | 33.2563 | 32.9607 | 34.7652 | 35.141 | 33.5713 | 34.3241 | 34.3874 | 34.3993 | 34.2733 | 34.2621 | 34.3494 | 34.1701 | 34.2831 | 36.1523 | 35.0827 | 36.4807 | 36.5128 | 33.6226 | 95.0065 | 94.98 | 94.2719
2022-09-08 04:52 | 7:01 | 25.2025 | 26.4459 | 28.8902 | 36.9798 | 34.4144 | 34.0468 | 34.8159 | 35.5804 | 36.6966 | 37.5367 | 36.9275 | 38.1076 | 34.2664 | 34.24 | 34.3029 | 35.119 | 35.1618 | 35.5261 | 36.3643 | 36.6392 | 28.0899 | 24.7309 | 94.0465 | 35.1764 | 33.0964 | 35.0576 | 33.2687 | 33.1295 | 33.4428 | 34.6764 | 34.2159 | 34.0374 | 37.2566 | 36.3705 | 33.4439 | 34.4431 | 36.3604 | 36.5266 | 37.4998 | 36.3777 | 33.2559 | 32.9598 | 34.7937 | 35.1427 | 33.5709 | 34.324 | 34.3695 | 34.4127 | 34.27 | 34.2724 | 34.354 | 34.172 | 34.2733 | 36.1458 | 35.084 | 36.4794 | 36.5282 | 33.6218 | 94.9826 | 95.098 | 94.2391
2022-09-08 04:52 | 7:02 | 24.9284 | 26.1343 | 28.5963 | 36.8968 | 34.3916 | 34.0617 | 34.8391 | 35.5897 | 36.6813 | 37.5351 | 36.9507 | 38.1127 | 34.2804 | 34.2794 | 34.3064 | 35.1279 | 35.1563 | 35.5197 | 36.3455 | 36.6472 | 27.8749 | 24.6531 | 94.0556 | 35.1919 | 33.1004 | 35.0483 | 33.2553 | 33.1329 | 33.4239 | 34.6753 | 34.1883 | 34.0701 | 37.2555 | 36.3595 | 33.43 | 34.4377 | 36.362 | 36.5282 | 37.4986 | 36.3389 | 33.2495 | 32.9639 | 34.7912 | 35.124 | 33.5814 | 34.3012 | 34.3708 | 34.3996 | 34.2664 | 34.27 | 34.3477 | 34.1868 | 34.27 | 36.1563 | 35.0915 | 36.4939 | 36.535 | 33.6096 | 95.0548 | 95.2154 | 94.3559
2022-09-08 04:52 | 7:02 | 24.8095 | 25.943 | 28.4267 | 36.9352 | 34.3969 | 34.0498 | 34.8404 | 35.5841 | 36.6789 | 37.5406 | 36.9617 | 38.0948 | 34.2507 | 34.2745 | 34.3241 | 35.1222 | 35.1679 | 35.5076 | 36.3645 | 36.6501 | 27.764 | 24.4431 | 94.1504 | 35.2159 | 33.1045 | 35.0532 | 33.2622 | 33.1306 | 33.4421 | 34.6676 | 34.2062 | 34.0681 | 37.2634 | 36.379 | 33.4511 | 34.4385 | 36.3705 | 36.5239 | 37.5062 | 36.3746 | 33.2679 | 32.9774 | 34.7859 | 35.1317 | 33.572 | 34.314 | 34.3836 | 34.3892 | 34.2876 | 34.2821 | 34.3478 | 34.1921 | 34.2664 | 36.1316 | 35.0729 | 36.4553 | 36.5132 | 33.5953 | 95.0288 | 95.163 | 94.2938
2022-09-08 04:52 | 7:02 | 24.6519 | 25.8191 | 28.3119 | 37.0386 | 34.4054 | 34.0659 | 34.82 | 35.5943 | 36.6844 | 37.5151 | 36.9347 | 38.1258 | 34.2644 | 34.2607 | 34.3061 | 35.1384 | 35.1665 | 35.5062 | 36.3291 | 36.6302 | 27.5544 | 24.3474 | 93.801 | 35.1581 | 33.0906 | 35.0556 | 33.2563 | 33.1413 | 33.4182 | 34.6692 | 34.1977 | 34.0646 | 37.2499 | 36.3841 | 33.426 | 34.4357 | 36.3595 | 36.5424 | 37.5136 | 36.3604 | 33.2722 | 32.9634 | 34.7612 | 35.1316 | 33.581 | 34.2858 | 34.388 | 34.4122 | 34.2728 | 34.2861 | 34.3526 | 34.1719 | 34.2876 | 36.1472 | 35.072 | 36.4889 | 36.5211 | 33.6161 | 94.8405 | 95.0136 | 94.1362
2022-09-08 04:52 | 7:02 | 24.465 | 25.5541 | 28.0923 | 36.9455 | 34.39 | 34.0692 | 34.8241 | 35.5806 | 36.6965 | 37.5128 | 36.9536 | 38.1096 | 34.2642 | 34.2476 | 34.2865 | 35.1213 | 35.1562 | 35.4966 | 36.3296 | 36.6245 | 27.3677 | 24.1059 | 93.7459 | 35.1009 | 33.0828 | 35.0614 | 33.2559 | 33.1265 | 33.4439 | 34.6699 | 34.1759 | 34.0629 | 37.227 | 36.3667 | 33.4316 | 34.4315 | 36.379 | 36.5162 | 37.5151 | 36.362 | 33.2548 | 32.9524 | 34.7602 | 35.1158 | 33.5642 | 34.3149 | 34.3819 | 34.3923 | 34.2819 | 34.2656 | 34.3511 | 34.175 | 34.2728 | 36.1325 | 35.0842 | 36.4686 | 36.5468 | 33.5936 | 94.6048 | 94.7756 | 93.9559
2022-09-08 04:52 | 7:02 | 24.2602 | 25.3374 | 27.8802 | 36.9654 | 34.3894 | 34.0737 | 34.8244 | 35.5829 | 36.6956 | 37.5289 | 36.9374 | 38.1021 | 34.2582 | 34.2379 | 34.2986 | 35.1235 | 35.1606 | 35.4903 | 36.3278 | 36.6356 | 27.2079 | 23.9355 | 93.6926 | 35.011 | 33.0875 | 35.0623 | 33.2495 | 33.1306 | 33.43 | 34.6739 | 34.2017 | 34.0541 | 37.2599 | 36.3819 | 33.4489 | 34.4395 | 36.3841 | 36.5224 | 37.4973 | 36.3705 | 33.2637 | 32.9781 | 34.7608 | 35.1256 | 33.5673 | 34.2881 | 34.39 | 34.401 | 34.2796 | 34.2876 | 34.3259 | 34.1603 | 34.2819 | 36.1069 | 35.0853 | 36.4815 | 36.5268 | 33.5971 | 94.3555 | 94.5294 | 93.7533
2022-09-08 04:53 | 7:03 | 24.0652 | 25.1344 | 27.6891 | 36.8287 | 34.389 | 34.0595 | 34.8078 | 35.5884 | 36.6914 | 37.5219 | 36.9201 | 38.1163 | 34.254 | 34.2642 | 34.3146 | 35.125 | 35.1594 | 35.5064 | 36.3195 | 36.625 | 27.0297 | 23.8002 | 93.5568 | 34.9841 | 33.0889 | 35.0724 | 33.2679 | 33.1217 | 33.4511 | 34.6511 | 34.189 | 34.0674 | 37.2453 | 36.3831 | 33.4235 | 34.4502 | 36.3667 | 36.5249 | 37.4912 | 36.3595 | 33.2761 | 32.9796 | 34.7635 | 35.1136 | 33.5422 | 34.2811 | 34.3815 | 34.3783 | 34.3035 | 34.2844 | 34.3255 | 34.1718 | 34.2796 | 36.1334 | 35.0936 | 36.4666 | 36.5444 | 33.6132 | 94.221 | 94.4169 | 93.7528
2022-09-08 04:53 | 7:03 | 23.933 | 25.0229 | 27.5685 | 36.8417 | 34.3754 | 34.0699 | 34.812 | 35.5947 | 36.7007 | 37.5152 | 36.9393 | 38.1035 | 34.2614 | 34.257 | 34.2909 | 35.1233 | 35.1695 | 35.4901 | 36.3084 | 36.6288 | 26.8481 | 23.6377 | 93.4033 | 35.0373 | 33.0831 | 35.0786 | 33.2722 | 33.1182 | 33.426 | 34.6724 | 34.1868 | 34.0616 | 37.2455 | 36.3847 | 33.4327 | 34.4387 | 36.3819 | 36.534 | 37.4986 | 36.379 | 33.2687 | 32.9519 | 34.755 | 35.1138 | 33.5567 | 34.2971 | 34.3946 | 34.3928 | 34.3005 | 34.2697 | 34.3294 | 34.1767 | 34.3035 | 36.1492 | 35.092 | 36.4621 | 36.5312 | 33.5846 | 94.0563 | 94.2855 | 93.6776
2022-09-08 04:53 | 7:03 | 23.8226 | 24.8594 | 27.4598 | 36.7211 | 34.4017 | 34.0471 | 34.8115 | 35.5759 | 36.6843 | 37.5224 | 36.9565 | 38.1113 | 34.2462 | 34.261 | 34.3249 | 35.1229 | 35.1762 | 35.4889 | 36.3372 | 36.5913 | 26.7013 | 23.5206 | 93.4251 | 34.9888 | 33.0793 | 35.082 | 33.2548 | 33.1293 | 33.4316 | 34.6627 | 34.1983 | 34.0603 | 37.2387 | 36.3879 | 33.4358 | 34.4295 | 36.3831 | 36.5109 | 37.4837 | 36.3841 | 33.2652 | 32.9594 | 34.743 | 35.1053 | 33.5358 | 34.2868 | 34.399 | 34.3933 | 34.302 | 34.2787 | 34.3144 | 34.1727 | 34.3005 | 36.128 | 35.1031 | 36.4743 | 36.517 | 33.5858 | 93.9418 | 94.1398 | 93.6079
2022-09-08 04:53 | 7:03 | 23.6022 | 24.6155 | 27.2608 | 36.6743 | 34.391 | 34.0587 | 34.8048 | 35.5712 | 36.6823 | 37.5203 | 36.9702 | 38.0986 | 34.2474 | 34.2401 | 34.2943 | 35.1327 | 35.1455 | 35.5025 | 36.3234 | 36.6079 | 26.6113 | 23.3353 | 93.4125 | 35.0408 | 33.0862 | 35.0825 | 33.2637 | 33.1244 | 33.4489 | 34.6648 | 34.1924 | 34.0744 | 37.256 | 36.3862 | 33.4177 | 34.4696 | 36.3847 | 36.5299 | 37.4774 | 36.3667 | 33.2905 | 32.9722 | 34.7468 | 35.1281 | 33.5367 | 34.2945 | 34.394 | 34.3804 | 34.293 | 34.2784 | 34.3282 | 34.1864 | 34.302 | 36.1212 | 35.1186 | 36.4819 | 36.5227 | 33.5766 | 93.8548 | 94.021 | 93.5826
2022-09-08 04:53 | 7:03 | 23.4941 | 24.5029 | 27.1196 | 36.5883 | 34.3897 | 34.0665 | 34.8103 | 35.5735 | 36.6944 | 37.5122 | 36.9404 | 38.0962 | 34.2508 | 34.2519 | 34.2985 | 35.114 | 35.1843 | 35.4896 | 36.3256 | 36.6153 | 26.399 | 23.4056 | 93.2447 | 35.0691 | 33.0729 | 35.0665 | 33.2761 | 33.1278 | 33.4235 | 34.6543 | 34.1952 | 34.0829 | 37.2481 | 36.3825 | 33.435 | 34.4611 | 36.3879 | 36.5249 | 37.5036 | 36.3819 | 33.2924 | 32.9642 | 34.742 | 35.0991 | 33.5471 | 34.2866 | 34.3831 | 34.4116 | 34.2838 | 34.2751 | 34.3192 | 34.1679 | 34.293 | 36.1194 | 35.1029 | 36.4915 | 36.5214 | 33.5976 | 93.7719 | 93.9228 | 93.5336
2022-09-08 04:53 | 7:03 | 23.3453 | 24.3773 | 27.0004 | 36.7905 | 34.4178 | 34.0456 | 34.8171 | 35.5822 | 36.6808 | 37.5167 | 36.9596 | 38.1003 | 34.2349 | 34.2418 | 34.3077 | 35.1508 | 35.1743 | 35.5111 | 36.2954 | 36.6259 | 26.1925 | 23.0806 | 93.3398 | 35.0169 | 33.0736 | 35.0801 | 33.2687 | 33.1324 | 33.4327 | 34.6412 | 34.2145 | 34.0632 | 37.2579 | 36.3835 | 33.4433 | 34.4542 | 36.3862 | 36.526 | 37.5079 | 36.3831 | 33.2863 | 32.9545 | 34.7361 | 35.1028 | 33.5433 | 34.2951 | 34.3993 | 34.3854 | 34.3006 | 34.2755 | 34.3273 | 34.1621 | 34.2838 | 36.1161 | 35.083 | 36.48 | 36.535 | 33.599 | 93.7646 | 93.8893 | 93.5448
2022-09-08 04:54 | 7:03 | 23.1567 | 24.1726 | 26.806 | 36.727 | 34.3883 | 34.061 | 34.8236 | 35.5942 | 36.6724 | 37.5229 | 36.9463 | 38.1226 | 34.2412 | 34.2244 | 34.318 | 35.1385 | 35.1617 | 35.4917 | 36.294 | 36.6213 | 26.0093 | 22.9373 | 93.3532 | 34.9795 | 33.1009 | 35.1019 | 33.2652 | 33.1266 | 33.4358 | 34.6568 | 34.2002 | 34.0802 | 37.2615 | 36.3943 | 33.432 | 34.4549 | 36.3825 | 36.545 | 37.5071 | 36.3847 | 33.2912 | 32.9667 | 34.741 | 35.087 | 33.556 | 34.288 | 34.4008 | 34.4085 | 34.2917 | 34.2747 | 34.3116 | 34.166 | 34.3006 | 36.1298 | 35.1019 | 36.4847 | 36.5311 | 33.5758 | 93.7128 | 93.7729 | 93.4905
2022-09-08 04:54 | 7:04 | 23.047 | 24.0534 | 26.632 | 36.7074 | 34.3888 | 34.0796 | 34.8181 | 35.577 | 36.6906 | 37.5193 | 36.9619 | 38.1052 | 34.2477 | 34.231 | 34.3114 | 35.1353 | 35.1679 | 35.5036 | 36.3085 | 36.6237 | 25.7457 | 22.756 | 93.2629 | 34.7812 | 33.0929 | 35.0942 | 33.2905 | 33.1201 | 33.4177 | 34.6439 | 34.2026 | 34.0722 | 37.2711 | 36.3969 | 33.4345 | 34.4484 | 36.3835 | 36.531 | 37.497 | 36.3879 | 33.2836 | 32.9546 | 34.7463 | 35.1 | 33.5466 | 34.2805 | 34.3951 | 34.3962 | 34.2787 | 34.277 | 34.3166 | 34.1763 | 34.2917 | 36.1107 | 35.1064 | 36.4929 | 36.5255 | 33.576 | 93.7107 | 93.7352 | 93.4987
2022-09-08 04:54 | 7:04 | 22.8852 | 23.866 | 26.5508 | 36.5472 | 34.3921 | 34.0698 | 34.8078 | 35.5835 | 36.6934 | 37.5198 | 36.9719 | 38.1306 | 34.249 | 34.2241 | 34.3311 | 35.1473 | 35.1732 | 35.5007 | 36.31 | 36.6296 | 25.5342 | 22.5969 | 93.1713 | 34.8175 | 33.0913 | 35.0866 | 33.2924 | 33.1409 | 33.435 | 34.6542 | 34.2345 | 34.0676 | 37.2722 | 36.388 | 33.4455 | 34.4576 | 36.3943 | 36.524 | 37.508 | 36.3862 | 33.2755 | 32.9455 | 34.7232 | 35.089 | 33.5608 | 34.2697 | 34.4079 | 34.3828 | 34.2874 | 34.2969 | 34.3075 | 34.1738 | 34.2787 | 36.1292 | 35.1105 | 36.4787 | 36.5289 | 33.5787 | 93.5602 | 93.6777 | 93.3538
2022-09-08 04:54 | 7:04 | 22.7446 | 23.6437 | 26.3352 | 36.5372 | 34.3827 | 34.0799 | 34.7997 | 35.5906 | 36.6897 | 37.4929 | 36.9827 | 38.1123 | 34.252 | 34.2276 | 34.3203 | 35.1369 | 35.1896 | 35.4905 | 36.3006 | 36.6377 | 25.3457 | 22.4626 | 93.1846 | 34.812 | 33.1033 | 35.0904 | 33.2863 | 33.1345 | 33.4433 | 34.6543 | 34.2101 | 34.0733 | 37.2699 | 36.411 | 33.4299 | 34.4628 | 36.3969 | 36.5281 | 37.4914 | 36.3825 | 33.2973 | 32.949 | 34.7432 | 35.1193 | 33.5435 | 34.2489 | 34.3948 | 34.371 | 34.2823 | 34.2686 | 34.3067 | 34.1887 | 34.2874 | 36.1277 | 35.1129 | 36.4904 | 36.5277 | 33.5795 | 93.4958 | 93.6141 | 93.3809
2022-09-08 04:54 | 7:04 | 22.6029 | 23.5509 | 26.2343 | 36.5465 | 34.3639 | 34.0865 | 34.816 | 35.5744 | 36.71 | 37.521 | 36.9591 | 38.1271 | 34.2547 | 34.2263 | 34.3166 | 35.1394 | 35.1944 | 35.5008 | 36.2761 | 36.6119 | 25.2375 | 22.4011 | 93.0745 | 34.6536 | 33.0797 | 35.1078 | 33.2912 | 33.141 | 33.432 | 34.6583 | 34.2214 | 34.0909 | 37.261 | 36.4029 | 33.4334 | 34.4496 | 36.388 | 36.5129 | 37.4886 | 36.3835 | 33.2844 | 32.9668 | 34.7149 | 35.1169 | 33.5183 | 34.2805 | 34.4045 | 34.3776 | 34.3038 | 34.2753 | 34.2951 | 34.1608 | 34.2823 | 36.1272 | 35.0969 | 36.487 | 36.5159 | 33.589 | 93.4168 | 93.5535 | 93.3136
2022-09-08 04:54 | 7:04 | 22.4234 | 23.3267 | 26.095 | 36.5507 | 34.3606 | 34.0726 | 34.8121 | 35.5947 | 36.6914 | 37.5213 | 36.9545 | 38.1071 | 34.252 | 34.233 | 34.3146 | 35.1717 | 35.1796 | 35.4772 | 36.2973 | 36.6028 | 25.0283 | 22.1633 | 92.9685 | 34.6242 | 33.0762 | 35.105 | 33.2836 | 33.1338 | 33.4345 | 34.6587 | 34.2267 | 34.0696 | 37.2683 | 36.4057 | 33.4374 | 34.455 | 36.411 | 36.536 | 37.5114 | 36.3943 | 33.2889 | 32.9419 | 34.7102 | 35.1109 | 33.5198 | 34.2768 | 34.3886 | 34.3658 | 34.3108 | 34.3039 | 34.2843 | 34.1813 | 34.3038 | 36.126 | 35.1031 | 36.4987 | 36.5436 | 33.5804 | 93.2395 | 93.4536 | 93.164
2022-09-08 04:55 | 7:05 | 22.3815 | 23.2536 | 25.9106 | 36.5375 | 34.3735 | 34.0749 | 34.7931 | 35.5802 | 36.7085 | 37.5158 | 36.9579 | 38.1249 | 34.2461 | 34.2272 | 34.3283 | 35.1633 | 35.1769 | 35.4903 | 36.3098 | 36.6334 | 24.8386 | 22.065 | 92.8276 | 34.5797 | 33.0992 | 35.1094 | 33.2755 | 33.141 | 33.4455 | 34.629 | 34.2085 | 34.0919 | 37.2683 | 36.4195 | 33.4357 | 34.4658 | 36.4029 | 36.5407 | 37.4942 | 36.3969 | 33.29 | 32.9419 | 34.7107 | 35.0986 | 33.5419 | 34.2759 | 34.4131 | 34.3654 | 34.307 | 34.3025 | 34.2711 | 34.1853 | 34.3108 | 36.1335 | 35.1133 | 36.4768 | 36.5345 | 33.5752 | 93.1359 | 93.3331 | 93.1635
2022-09-08 04:55 | 7:05 | 22.1611 | 23.0912 | 25.7624 | 36.5242 | 34.3815 | 34.0914 | 34.8055 | 35.5896 | 36.7083 | 37.5078 | 36.9752 | 38.1328 | 34.2366 | 34.2318 | 34.3337 | 35.1628 | 35.1861 | 35.5032 | 36.3049 | 36.6176 | 24.6356 | 21.9022 | 92.9924 | 34.6801 | 33.1131 | 35.1031 | 33.2973 | 33.1299 | 33.4299 | 34.6561 | 34.2366 | 34.0901 | 37.2645 | 36.4068 | 33.4451 | 34.4685 | 36.4057 | 36.5461 | 37.5065 | 36.388 | 33.2961 | 32.9506 | 34.7305 | 35.1182 | 33.5408 | 34.2773 | 34.3947 | 34.3778 | 34.3032 | 34.2992 | 34.281 | 34.1781 | 34.307 | 36.1413 | 35.1096 | 36.4851 | 36.5277 | 33.5968 | 93.1205 | 93.2826 | 93.1554
2022-09-08 04:55 | 7:05 | 22.0041 | 22.9096 | 25.61 | 36.4671 | 34.3729 | 34.0879 | 34.8065 | 35.5954 | 36.6942 | 37.5055 | 36.9625 | 38.1234 | 34.2515 | 34.2093 | 34.3361 | 35.1741 | 35.1866 | 35.4827 | 36.2861 | 36.6135 | 24.4103 | 21.692 | 92.8778 | 34.5917 | 33.0966 | 35.0949 | 33.2844 | 33.1419 | 33.4334 | 34.6382 | 34.2284 | 34.096 | 37.2694 | 36.403 | 33.4406 | 34.4593 | 36.4195 | 36.5354 | 37.5011 | 36.411 | 33.2948 | 32.9402 | 34.7431 | 35.1118 | 33.538 | 34.2559 | 34.4081 | 34.3642 | 34.2988 | 34.2896 | 34.2811 | 34.1786 | 34.3032 | 36.1205 | 35.102 | 36.5039 | 36.5256 | 33.5832 | 93.0772 | 93.1749 | 93.1151
2022-09-08 04:55 | 7:05 | 21.9415 | 22.7945 | 25.4917 | 36.4172 | 34.3434 | 34.0693 | 34.8073 | 35.5812 | 36.7004 | 37.526 | 36.9667 | 38.1309 | 34.2602 | 34.2245 | 34.3186 | 35.1669 | 35.1868 | 35.5055 | 36.2845 | 36.6153 | 24.2437 | 21.5666 | 92.8764 | 34.5707 | 33.0918 | 35.1152 | 33.2889 | 33.1382 | 33.4374 | 34.6469 | 34.2295 | 34.0955 | 37.2685 | 36.4057 | 33.4345 | 34.4729 | 36.4068 | 36.5478 | 37.501 | 36.4029 | 33.3047 | 32.9386 | 34.7332 | 35.1077 | 33.5007 | 34.2679 | 34.3986 | 34.359 | 34.2945 | 34.3013 | 34.2883 | 34.1898 | 34.2988 | 36.1309 | 35.1046 | 36.4896 | 36.5386 | 33.5981 | 93.025 | 93.1036 | 93.0716
2022-09-08 04:55 | 7:05 | 21.7406 | 22.6189 | 25.366 | 36.3748 | 34.3884 | 34.0742 | 34.8016 | 35.5827 | 36.695 | 37.4971 | 36.9744 | 38.147 | 34.2486 | 34.2142 | 34.3263 | 35.156 | 35.2057 | 35.4915 | 36.288 | 36.6232 | 24.0451 | 21.416 | 92.7443 | 34.644 | 33.1023 | 35.0849 | 33.29 | 33.1295 | 33.4357 | 34.6411 | 34.2167 | 34.1045 | 37.2597 | 36.4148 | 33.4318 | 34.4965 | 36.403 | 36.5514 | 37.4771 | 36.4057 | 33.316 | 32.9519 | 34.7274 | 35.1097 | 33.4888 | 34.2634 | 34.4095 | 34.3712 | 34.3044 | 34.2854 | 34.2546 | 34.192 | 34.2945 | 36.1387 | 35.1239 | 36.4839 | 36.5379 | 33.5864 | 92.954 | 92.978 | 92.9969
2022-09-08 04:55 | 7:05 | 21.6177 | 22.5019 | 25.161 | 36.3864 | 34.3738 | 34.0782 | 34.7972 | 35.6012 | 36.7248 | 37.4958 | 36.9644 | 38.134 | 34.2589 | 34.2266 | 34.3385 | 35.1542 | 35.2106 | 35.4781 | 36.2787 | 36.6292 | 23.8815 | 21.2661 | 92.6383 | 34.4072 | 33.0906 | 35.1072 | 33.2961 | 33.1284 | 33.4451 | 34.645 | 34.2246 | 34.0986 | 37.2928 | 36.4052 | 33.459 | 34.4701 | 36.4057 | 36.5428 | 37.4933 | 36.4195 | 33.3079 | 32.9525 | 34.7008 | 35.1185 | 33.5078 | 34.2433 | 34.397 | 34.3432 | 34.3057 | 34.2937 | 34.2671 | 34.1692 | 34.3044 | 36.1493 | 35.095 | 36.5262 | 36.5457 | 33.6165 | 92.7894 | 92.8814 | 92.8669
2022-09-08 04:56 | 7:05 | 21.5766 | 22.3814 | 25.1043 | 36.2754 | 34.3652 | 34.1067 | 34.7991 | 35.6044 | 36.7236 | 37.5164 | 36.9829 | 38.1345 | 34.2389 | 34.2283 | 34.3333 | 35.161 | 35.2121 | 35.4825 | 36.2787 | 36.6159 | 23.7179 | 21.131 | 92.6085 | 34.4439 | 33.0874 | 35.1094 | 33.2948 | 33.1267 | 33.4406 | 34.6526 | 34.2319 | 34.1091 | 37.2745 | 36.4076 | 33.4342 | 34.477 | 36.4148 | 36.5622 | 37.5053 | 36.4068 | 33.3091 | 32.9451 | 34.7299 | 35.1052 | 33.5196 | 34.2467 | 34.4005 | 34.3388 | 34.2996 | 34.3034 | 34.2517 | 34.18 | 34.3057 | 36.158 | 35.1073 | 36.4957 | 36.5374 | 33.6045 | 92.647 | 92.8252 | 92.848
2022-09-08 04:56 | 7:06 | 21.3199 | 22.1536 | 24.9581 | 36.2441 | 34.3593 | 34.0751 | 34.8106 | 35.5859 | 36.7115 | 37.5146 | 36.9844 | 38.1349 | 34.229 | 34.2437 | 34.3444 | 35.1663 | 35.2178 | 35.4857 | 36.2606 | 36.6214 | 23.5896 | 20.9558 | 92.5316 | 34.367 | 33.115 | 35.0967 | 33.3047 | 33.1323 | 33.4345 | 34.6618 | 34.2158 | 34.1123 | 37.2878 | 36.4129 | 33.4227 | 34.4656 | 36.4052 | 36.5564 | 37.4866 | 36.403 | 33.3132 | 32.9166 | 34.7114 | 35.1083 | 33.4977 | 34.2441 | 34.4 | 34.3559 | 34.305 | 34.3116 | 34.24 | 34.19 | 34.2996 | 36.1356 | 35.1168 | 36.4988 | 36.5467 | 33.5966 | 92.553 | 92.6878 | 92.8077
2022-09-08 04:56 | 7:06 | 21.2373 | 22.0812 | 24.823 | 36.2615 | 34.3494 | 34.0989 | 34.7878 | 35.5785 | 36.7032 | 37.522 | 36.9963 | 38.143 | 34.2635 | 34.2337 | 34.3315 | 35.1559 | 35.2033 | 35.4874 | 36.2758 | 36.6146 | 23.4874 | 20.7922 | 92.3804 | 34.4111 | 33.0922 | 35.1161 | 33.316 | 33.1246 | 33.4318 | 34.6494 | 34.2241 | 34.1041 | 37.2775 | 36.4229 | 33.4411 | 34.4926 | 36.4076 | 36.5431 | 37.4989 | 36.4057 | 33.3009 | 32.9579 | 34.6976 | 35.0907 | 33.4813 | 34.2525 | 34.4074 | 34.3475 | 34.3183 | 34.3085 | 34.2794 | 34.185 | 34.305 | 36.1429 | 35.1085 | 36.5142 | 36.5278 | 33.6002 | 92.4367 | 92.5714 | 92.7188
2022-09-08 04:56 | 7:06 | 21.0836 | 21.8918 | 24.6837 | 36.308 | 34.3707 | 34.0995 | 34.7966 | 35.5936 | 36.7183 | 37.536 | 36.9735 | 38.1302 | 34.2428 | 34.2249 | 34.325 | 35.1918 | 35.2204 | 35.4958 | 36.2731 | 36.6435 | 23.367 | 20.6791 | 92.4012 | 34.4103 | 33.1137 | 35.1089 | 33.3079 | 33.1396 | 33.459 | 34.6329 | 34.2327 | 34.1162 | 37.2788 | 36.404 | 33.4531 | 34.4886 | 36.4129 | 36.5538 | 37.4967 | 36.4148 | 33.3072 | 32.9583 | 34.7166 | 35.1049 | 33.4861 | 34.2545 | 34.3894 | 34.3447 | 34.3151 | 34.3157 | 34.2745 | 34.1665 | 34.3183 | 36.1494 | 35.1101 | 36.5066 | 36.5371 | 33.6201 | 92.3444 | 92.4017 | 92.6338
2022-09-08 04:56 | 7:06 | 20.9117 | 21.7481 | 24.5489 | 36.1532 | 34.3494 | 34.09 | 34.7905 | 35.5835 | 36.7302 | 37.5279 | 37.0018 | 38.1365 | 34.2258 | 34.2222 | 34.3563 | 35.1933 | 35.2197 | 35.5018 | 36.2625 | 36.642 | 23.2622 | 20.5276 | 92.4103 | 34.47 | 33.0931 | 35.1121 | 33.3091 | 33.1377 | 33.4342 | 34.6232 | 34.218 | 34.1183 | 37.2924 | 36.401 | 33.4508 | 34.4976 | 36.4229 | 36.5541 | 37.5114 | 36.4052 | 33.3203 | 32.9453 | 34.7002 | 35.089 | 33.4721 | 34.2448 | 34.4099 | 34.3582 | 34.3258 | 34.3132 | 34.2607 | 34.1718 | 34.3151 | 36.1458 | 35.1195 | 36.5161 | 36.5475 | 33.6207 | 92.2541 | 92.3358 | 92.5655
2022-09-08 04:56 | 7:06 | 20.8157 | 21.6265 | 24.4072 | 36.0532 | 34.354 | 34.1082 | 34.8015 | 35.596 | 36.7137 | 37.5201 | 36.9781 | 38.1559 | 34.2403 | 34.2036 | 34.3515 | 35.1945 | 35.2208 | 35.4881 | 36.2748 | 36.648 | 23.2054 | 20.4168 | 92.3549 | 34.208 | 33.0998 | 35.0997 | 33.3132 | 33.1315 | 33.4227 | 34.6464 | 34.2378 | 34.1124 | 37.292 | 36.4246 | 33.4288 | 34.483 | 36.404 | 36.5611 | 37.5083 | 36.4076 | 33.3008 | 32.9422 | 34.6947 | 35.1157 | 33.4564 | 34.2525 | 34.4082 | 34.3384 | 34.3361 | 34.311 | 34.2476 | 34.1734 | 34.3258 | 36.1438 | 35.1191 | 36.5053 | 36.5632 | 33.6245 | 92.1495 | 92.2468 | 92.5193
2022-09-08 04:57 | 7:07 | 20.74 | 21.5316 | 24.3301 | 36.1138 | 34.3477 | 34.0979 | 34.7936 | 35.5922 | 36.7156 | 37.5232 | 37.0058 | 38.1606 | 34.2407 | 34.2465 | 34.3448 | 35.1944 | 35.2139 | 35.4856 | 36.2875 | 36.6386 | 23.117 | 20.2895 | 92.1632 | 34.2937 | 33.0978 | 35.1098 | 33.3009 | 33.1281 | 33.4411 | 34.6582 | 34.2416 | 34.1103 | 37.291 | 36.4147 | 33.4365 | 34.4907 | 36.401 | 36.5611 | 37.5089 | 36.4129 | 33.3179 | 32.9537 | 34.6991 | 35.1094 | 33.4639 | 34.2548 | 34.4044 | 34.3388 | 34.3346 | 34.3103 | 34.2379 | 34.1764 | 34.3361 | 36.1552 | 35.1052 | 36.5012 | 36.5615 | 33.6175 | 91.9586 | 92.052 | 92.3743
2022-09-08 04:57 | 7:07 | 20.6114 | 21.4024 | 24.1887 | 36.1263 | 34.3478 | 34.1033 | 34.8042 | 35.5976 | 36.7177 | 37.5286 | 37.0007 | 38.145 | 34.2518 | 34.2557 | 34.3647 | 35.1876 | 35.2175 | 35.4871 | 36.2696 | 36.6462 | 23.0737 | 20.1483 | 92.0982 | 34.2645 | 33.0945 | 35.0928 | 33.3072 | 33.1345 | 33.4531 | 34.6493 | 34.2286 | 34.1312 | 37.3098 | 36.4132 | 33.4484 | 34.4984 | 36.4246 | 36.5504 | 37.4979 | 36.4229 | 33.3113 | 32.9134 | 34.7047 | 35.1181 | 33.4498 | 34.2212 | 34.394 | 34.3219 | 34.3449 | 34.3166 | 34.2642 | 34.1766 | 34.3346 | 36.1559 | 35.1168 | 36.5048 | 36.5547 | 33.6108 | 91.8264 | 91.9032 | 92.372
2022-09-08 04:57 | 7:07 | 20.4874 | 21.2574 | 24.0953 | 36.07 | 34.3526 | 34.1033 | 34.7892 | 35.5914 | 36.7182 | 37.5355 | 36.974 | 38.17 | 34.2593 | 34.2392 | 34.3565 | 35.1884 | 35.2236 | 35.4844 | 36.284 | 36.639 | 23.0071 | 20.0968 | 92.0646 | 34.1666 | 33.1222 | 35.121 | 33.3203 | 33.1361 | 33.4508 | 34.6505 | 34.2475 | 34.1209 | 37.3078 | 36.4154 | 33.4215 | 34.4834 | 36.4147 | 36.5514 | 37.493 | 36.404 | 33.3195 | 32.9281 | 34.68 | 35.0963 | 33.4467 | 34.2496 | 34.3912 | 34.3218 | 34.3281 | 34.3028 | 34.257 | 34.187 | 34.3449 | 36.1688 | 35.13 | 36.5027 | 36.5509 | 33.6486 | 91.6764 | 91.8413 | 92.264
2022-09-08 04:57 | 7:07 | 20.4295 | 21.167 | 24.0005 | 36.0118 | 34.3511 | 34.112 | 34.7814 | 35.5999 | 36.7293 | 37.5292 | 36.9859 | 38.1705 | 34.2651 | 34.2272 | 34.3517 | 35.2032 | 35.2211 | 35.4998 | 36.2795 | 36.6524 | 22.9304 | 19.9939 | 91.9191 | 34.208 | 33.0925 | 35.1203 | 33.3008 | 33.1095 | 33.4288 | 34.6464 | 34.2322 | 34.1228 | 37.2937 | 36.3995 | 33.436 | 34.4888 | 36.4132 | 36.5478 | 37.497 | 36.401 | 33.3068 | 32.9208 | 34.7034 | 35.101 | 33.4295 | 34.248 | 34.4017 | 34.3323 | 34.3266 | 34.3171 | 34.261 | 34.1678 | 34.3281 | 36.1712 | 35.1104 | 36.5057 | 36.57 | 33.6213 | 91.6895 | 91.8111 | 92.2502
2022-09-08 04:57 | 7:07 | 20.3099 | 21.0762 | 23.8755 | 36.068 | 34.3259 | 34.1122 | 34.78 | 35.5954 | 36.7205 | 37.5223 | 37.0002 | 38.1628 | 34.2621 | 34.2286 | 34.3748 | 35.1944 | 35.2108 | 35.4918 | 36.2669 | 36.6443 | 22.8479 | 19.8325 | 91.8747 | 34.2909 | 33.1172 | 35.1121 | 33.3179 | 33.1068 | 33.4365 | 34.6384 | 34.2524 | 34.1137 | 37.2913 | 36.4192 | 33.4393 | 34.4799 | 36.4154 | 36.5511 | 37.5099 | 36.4246 | 33.2968 | 32.9196 | 34.6945 | 35.1042 | 33.4229 | 34.2409 | 34.4007 | 34.345 | 34.3258 | 34.3077 | 34.2401 | 34.162 | 34.3266 | 36.1684 | 35.1381 | 36.5092 | 36.5474 | 33.6299 | 91.8084 | 91.8277 | 92.2616
2022-09-08 04:57 | 7:07 | 20.3086 | 20.9358 | 23.7748 | 35.9527 | 34.3255 | 34.1108 | 34.7912 | 35.5873 | 36.72 | 37.5227 | 37.0047 | 38.1626 | 34.27 | 34.2417 | 34.3729 | 35.1942 | 35.2295 | 35.4959 | 36.2807 | 36.6452 | 22.7914 | 19.7588 | 92.0682 | 34.2276 | 33.0948 | 35.1036 | 33.3113 | 33.1153 | 33.4484 | 34.6351 | 34.2219 | 34.1207 | 37.3002 | 36.4122 | 33.442 | 34.4796 | 36.3995 | 36.562 | 37.5127 | 36.4147 | 33.2966 | 32.9197 | 34.6911 | 35.107 | 33.4239 | 34.2316 | 34.3736 | 34.3195 | 34.3246 | 34.3141 | 34.2519 | 34.1807 | 34.3258 | 36.1776 | 35.1283 | 36.4931 | 36.55 | 33.6355 | 91.9133 | 91.9077 | 92.3234
2022-09-08 04:58 | 7:08 | 20.0985 | 20.8496 | 23.6452 | 35.8946 | 34.3294 | 34.0967 | 34.7719 | 35.6041 | 36.7283 | 37.5253 | 36.9871 | 38.1391 | 34.2677 | 34.2426 | 34.3642 | 35.2118 | 35.2292 | 35.5002 | 36.2658 | 36.6568 | 22.7492 | 19.6894 | 92.1899 | 34.0472 | 33.1179 | 35.1108 | 33.3195 | 33.1172 | 33.4215 | 34.6308 | 34.2286 | 34.1273 | 37.3005 | 36.4083 | 33.4389 | 34.4848 | 36.4192 | 36.5378 | 37.504 | 36.4132 | 33.2914 | 32.9186 | 34.6686 | 35.09 | 33.4129 | 34.232 | 34.3656 | 34.3116 | 34.3525 | 34.308 | 34.2418 | 34.1746 | 34.3246 | 36.1705 | 35.119 | 36.5143 | 36.5641 | 33.6083 | 91.9591 | 92.0872 | 92.4312
2022-09-08 04:58 | 7:08 | 20.0767 | 20.9947 | 23.5501 | 35.9927 | 34.3144 | 34.1155 | 34.7781 | 35.5966 | 36.7379 | 37.5295 | 36.9964 | 38.1705 | 34.2653 | 34.2332 | 34.3679 | 35.2267 | 35.2402 | 35.4829 | 36.248 | 36.649 | 22.6883 | 19.6135 | 92.1786 | 33.9988 | 33.0943 | 35.093 | 33.3068 | 33.1074 | 33.436 | 34.6529 | 34.2314 | 34.118 | 37.2848 | 36.3931 | 33.4377 | 34.5226 | 36.4122 | 36.565 | 37.5032 | 36.4154 | 33.2978 | 32.9301 | 34.6848 | 35.0934 | 33.4325 | 34.2174 | 34.4075 | 34.3142 | 34.3515 | 34.3024 | 34.2244 | 34.1875 | 34.3525 | 36.1602 | 35.1333 | 36.5342 | 36.5621 | 33.6242 | 92.1305 | 92.2282 | 92.5216
2022-09-08 04:58 | 7:08 | 19.8828 | 20.6385 | 23.4993 | 36.0075 | 34.3282 | 34.1122 | 34.7639 | 35.5918 | 36.7118 | 37.5127 | 36.9993 | 38.1559 | 34.2663 | 34.2406 | 34.3628 | 35.2036 | 35.2429 | 35.4862 | 36.242 | 36.6312 | 22.6041 | 19.4529 | 92.2444 | 34.0246 | 33.1073 | 35.1034 | 33.2968 | 33.0965 | 33.4393 | 34.6423 | 34.2356 | 34.119 | 37.2828 | 36.4143 | 33.4518 | 34.4918 | 36.4083 | 36.5625 | 37.4963 | 36.3995 | 33.2991 | 32.9049 | 34.6874 | 35.0861 | 33.3971 | 34.225 | 34.3735 | 34.3204 | 34.349 | 34.3274 | 34.231 | 34.1623 | 34.3515 | 36.1787 | 35.1095 | 36.5085 | 36.5613 | 33.6365 | 92.144 | 92.3642 | 92.5312
2022-09-08 04:58 | 7:08 | 19.8869 | 20.5445 | 23.3853 | 35.9301 | 34.3192 | 34.0993 | 34.7681 | 35.6001 | 36.7137 | 37.5212 | 36.9798 | 38.1611 | 34.2742 | 34.2448 | 34.37 | 35.2031 | 35.2311 | 35.482 | 36.2441 | 36.6446 | 22.5584 | 19.4713 | 92.2128 | 33.9971 | 33.1125 | 35.1193 | 33.2966 | 33.1142 | 33.442 | 34.6305 | 34.2236 | 34.0916 | 37.306 | 36.4107 | 33.433 | 34.4764 | 36.3931 | 36.5641 | 37.4995 | 36.4192 | 33.3026 | 32.8951 | 34.6643 | 35.096 | 33.4056 | 34.2447 | 34.3871 | 34.3077 | 34.3519 | 34.3311 | 34.2241 | 34.1934 | 34.349 | 36.1692 | 35.1142 | 36.5236 | 36.5515 | 33.6486 | 92.3369 | 92.426 | 92.6102
2022-09-08 04:58 | 7:08 | 19.6985 | 20.4301 | 23.2528 | 35.8641 | 34.3273 | 34.093 | 34.7735 | 35.5898 | 36.7174 | 37.5169 | 36.9768 | 38.1717 | 34.2957 | 34.2515 | 34.3533 | 35.198 | 35.2331 | 35.4773 | 36.2567 | 36.639 | 22.4901 | 19.3233 | 92.2507 | 34.1123 | 33.1074 | 35.1109 | 33.2914 | 33.0962 | 33.4389 | 34.6227 | 34.2303 | 34.1106 | 37.3049 | 36.3836 | 33.4496 | 34.4857 | 36.4143 | 36.5504 | 37.4969 | 36.4122 | 33.2766 | 32.8917 | 34.6701 | 35.0666 | 33.3877 | 34.2409 | 34.379 | 34.314 | 34.3619 | 34.3401 | 34.2276 | 34.1843 | 34.3519 | 36.173 | 35.1045 | 36.5134 | 36.5626 | 33.6324 | 92.5092 | 92.5262 | 92.6645
2022-09-08 04:58 | 7:08 | 19.7136 | 20.4578 | 23.1971 | 35.897 | 34.3116 | 34.1091 | 34.7765 | 35.593 | 36.7289 | 37.5328 | 36.9806 | 38.1635 | 34.2737 | 34.2489 | 34.373 | 35.2053 | 35.2065 | 35.4891 | 36.2362 | 36.6354 | 22.4316 | 19.307 | 92.5256 | 33.925 | 33.1202 | 35.1163 | 33.2978 | 33.1091 | 33.4377 | 34.6445 | 34.2292 | 34.1066 | 37.2978 | 36.411 | 33.4435 | 34.4743 | 36.4107 | 36.5553 | 37.4826 | 36.4083 | 33.2991 | 32.8904 | 34.6758 | 35.0716 | 33.3636 | 34.2475 | 34.3906 | 34.3132 | 34.3367 | 34.3395 | 34.2263 | 34.1634 | 34.3619 | 36.1837 | 35.1034 | 36.5072 | 36.5483 | 33.6252 | 92.6119 | 92.6925 | 92.7878
2022-09-08 04:59 | 7:08 | 19.5822 | 20.2864 | 23.1112 | 35.8385 | 34.3166 | 34.1044 | 34.7591 | 35.5908 | 36.7193 | 37.5347 | 37.0076 | 38.1647 | 34.2621 | 34.2584 | 34.3799 | 35.2081 | 35.2244 | 35.4709 | 36.2546 | 36.6473 | 22.3929 | 19.1575 | 92.516 | 33.8866 | 33.0968 | 35.097 | 33.2991 | 33.0957 | 33.4518 | 34.6458 | 34.2096 | 34.1235 | 37.2951 | 36.401 | 33.4285 | 34.4841 | 36.3836 | 36.5642 | 37.5045 | 36.3931 | 33.3035 | 32.9107 | 34.6441 | 35.067 | 33.3603 | 34.2458 | 34.3708 | 34.2918 | 34.3546 | 34.3134 | 34.233 | 34.1799 | 34.3367 | 36.1683 | 35.1208 | 36.5032 | 36.5588 | 33.6167 | 92.7192 | 92.8264 | 92.8505
2022-09-08 04:59 | 7:09 | 19.5097 | 20.2048 | 23.0284 | 35.8239 | 34.3075 | 34.1095 | 34.7683 | 35.5835 | 36.7183 | 37.5158 | 36.9731 | 38.147 | 34.2724 | 34.2592 | 34.3524 | 35.1924 | 35.2293 | 35.4913 | 36.2285 | 36.6486 | 22.4067 | 19.1414 | 92.7216 | 33.8909 | 33.0916 | 35.0972 | 33.3026 | 33.0895 | 33.433 | 34.6492 | 34.237 | 34.1073 | 37.3083 | 36.3889 | 33.4615 | 34.4958 | 36.411 | 36.5528 | 37.4954 | 36.4143 | 33.2968 | 32.8812 | 34.6478 | 35.0725 | 33.3557 | 34.2386 | 34.3874 | 34.2875 | 34.3545 | 34.3389 | 34.2272 | 34.176 | 34.3546 | 36.1737 | 35.1152 | 36.5139 | 36.553 | 33.6148 | 92.8782 | 92.9361 | 93.0045
2022-09-08 04:59 | 7:09 | 19.3878 | 20.1072 | 22.9323 | 35.8649 | 34.3067 | 34.0912 | 34.7393 | 35.5819 | 36.7221 | 37.5332 | 36.987 | 38.1579 | 34.27 | 34.2644 | 34.3738 | 35.21 | 35.2153 | 35.4826 | 36.2413 | 36.644 | 22.3586 | 19.1235 | 92.718 | 33.9744 | 33.1081 | 35.1096 | 33.2766 | 33.1123 | 33.4496 | 34.6323 | 34.2183 | 34.1068 | 37.2826 | 36.393 | 33.4418 | 34.4841 | 36.401 | 36.5593 | 37.4997 | 36.4107 | 33.2752 | 32.8957 | 34.6589 | 35.0861 | 33.3309 | 34.2449 | 34.3736 | 34.292 | 34.3722 | 34.3305 | 34.2318 | 34.1853 | 34.3545 | 36.1735 | 35.101 | 36.4911 | 36.5428 | 33.6265 | 92.9841 | 93.019 | 92.9819
2022-09-08 04:59 | 7:09 | 19.3567 | 20.069 | 22.8783 | 35.8835 | 34.2951 | 34.1067 | 34.76 | 35.5908 | 36.7262 | 37.5326 | 36.9868 | 38.1572 | 34.2821 | 34.2636 | 34.3616 | 35.206 | 35.2184 | 35.4648 | 36.2356 | 36.6416 | 22.282 | 19.0514 | 92.8087 | 33.8357 | 33.111 | 35.1097 | 33.2991 | 33.09 | 33.4435 | 34.6518 | 34.2117 | 34.1118 | 37.3112 | 36.3862 | 33.4361 | 34.4785 | 36.3889 | 36.5688 | 37.498 | 36.3836 | 33.2949 | 32.8762 | 34.6504 | 35.0815 | 33.3617 | 34.2635 | 34.3689 | 34.2984 | 34.3564 | 34.3484 | 34.2093 | 34.1793 | 34.3722 | 36.1862 | 35.1185 | 36.526 | 36.5621 | 33.6237 | 93.2262 | 93.1622 | 93.1287
2022-09-08 04:59 | 7:09 | 19.3014 | 19.9877 | 22.831 | 35.6348 | 34.2843 | 34.0979 | 34.745 | 35.5758 | 36.724 | 37.5302 | 36.9933 | 38.1687 | 34.2861 | 34.249 | 34.3758 | 35.2157 | 35.2147 | 35.4748 | 36.2338 | 36.6472 | 22.2388 | 18.941 | 92.8848 | 33.949 | 33.1052 | 35.1011 | 33.3035 | 33.0972 | 33.4285 | 34.6477 | 34.2377 | 34.0932 | 37.2934 | 36.3811 | 33.4365 | 34.4778 | 36.393 | 36.5602 | 37.4948 | 36.411 | 33.3016 | 32.8575 | 34.6305 | 35.0562 | 33.36 | 34.24 | 34.381 | 34.3025 | 34.3626 | 34.3515 | 34.2245 | 34.1717 | 34.3564 | 36.1702 | 35.1093 | 36.5137 | 36.5548 | 33.6323 | 93.335 | 93.3383 | 93.2616
2022-09-08 04:59 | 7:09 | 19.2304 | 19.889 | 22.7456 | 35.7347 | 34.2711 | 34.12 | 34.7448 | 35.5961 | 36.7177 | 37.5279 | 36.9772 | 38.1669 | 34.2656 | 34.2604 | 34.3761 | 35.1983 | 35.2073 | 35.4768 | 36.2329 | 36.6413 | 22.1739 | 18.8782 | 92.9078 | 33.8014 | 33.1169 | 35.102 | 33.2968 | 33.0858 | 33.4615 | 34.6468 | 34.2263 | 34.1143 | 37.2887 | 36.3875 | 33.425 | 34.4903 | 36.3862 | 36.569 | 37.5047 | 36.401 | 33.2906 | 32.8568 | 34.6429 | 35.0567 | 33.3278 | 34.2494 | 34.3957 | 34.2946 | 34.3826 | 34.3491 | 34.2142 | 34.1596 | 34.3626 | 36.1698 | 35.1135 | 36.52 | 36.5619 | 33.6206 | 93.5156 | 93.4972 | 93.2943
2022-09-08 05:00 | 7:10 | 19.1858 | 19.8072 | 22.7028 | 35.7808 | 34.281 | 34.1067 | 34.7486 | 35.5864 | 36.7165 | 37.5215 | 36.9935 | 38.1636 | 34.2876 | 34.2658 | 34.3747 | 35.2114 | 35.2299 | 35.4822 | 36.235 | 36.6546 | 22.142 | 18.7726 | 92.7282 | 33.8051 | 33.1101 | 35.0825 | 33.2752 | 33.0889 | 33.4418 | 34.6361 | 34.2169 | 34.1233 | 37.2854 | 36.3929 | 33.4365 | 34.4832 | 36.3811 | 36.5545 | 37.5018 | 36.3889 | 33.2816 | 32.8833 | 34.6294 | 35.0561 | 33.324 | 34.2584 | 34.3959 | 34.2906 | 34.3874 | 34.3442 | 34.2266 | 34.1724 | 34.3826 | 36.1814 | 35.1203 | 36.505 | 36.5728 | 33.6351 | 93.566 | 93.6882 | 93.2688
2022-09-08 05:00 | 7:10 | 19.153 | 19.7598 | 22.6075 | 35.6735 | 34.2811 | 34.1178 | 34.7457 | 35.5767 | 36.7285 | 37.5417 | 36.9918 | 38.1553 | 34.2844 | 34.2647 | 34.3821 | 35.2061 | 35.2057 | 35.4738 | 36.2407 | 36.6654 | 22.0998 | 18.7744 | 92.9373 | 33.8548 | 33.1096 | 35.0959 | 33.2949 | 33.0872 | 33.4361 | 34.6318 | 34.2109 | 34.108 | 37.2638 | 36.3781 | 33.4568 | 34.4762 | 36.3875 | 36.568 | 37.5025 | 36.393 | 33.2884 | 32.8682 | 34.6308 | 35.065 | 33.3188 | 34.2456 | 34.3954 | 34.2902 | 34.3695 | 34.3612 | 34.2283 | 34.1606 | 34.3874 | 36.1912 | 35.1435 | 36.5221 | 36.5509 | 33.6257 | 93.8244 | 93.8697 | 93.4455
2022-09-08 05:00 | 7:10 | 19.0594 | 19.7028 | 22.5364 | 35.6847 | 34.2883 | 34.1048 | 34.7534 | 35.5835 | 36.7198 | 37.539 | 36.9772 | 38.1614 | 34.2697 | 34.2524 | 34.364 | 35.1891 | 35.2181 | 35.474 | 36.2101 | 36.6457 | 22.0389 | 18.7053 | 93.1608 | 33.6305 | 33.0946 | 35.0874 | 33.3016 | 33.0906 | 33.4365 | 34.636 | 34.236 | 34.1091 | 37.294 | 36.3832 | 33.4289 | 34.4705 | 36.3929 | 36.5551 | 37.4772 | 36.3862 | 33.2815 | 32.8541 | 34.6159 | 35.0527 | 33.3236 | 34.2572 | 34.3689 | 34.2858 | 34.3708 | 34.356 | 34.2437 | 34.1601 | 34.3695 | 36.1689 | 35.1159 | 36.5028 | 36.5488 | 33.6276 | 94.0639 | 94.0934 | 93.6382
2022-09-08 05:00 | 7:10 | 18.9853 | 19.6139 | 22.4497 | 35.5648 | 34.2546 | 34.1128 | 34.7455 | 35.5829 | 36.7225 | 37.5382 | 36.975 | 38.1583 | 34.2787 | 34.2657 | 34.3599 | 35.1984 | 35.1974 | 35.4651 | 36.2128 | 36.6426 | 22.0131 | 18.6771 | 93.4218 | 33.7335 | 33.1112 | 35.0923 | 33.2906 | 33.0812 | 33.425 | 34.6293 | 34.227 | 34.1225 | 37.2925 | 36.3892 | 33.4353 | 34.4901 | 36.3781 | 36.566 | 37.4897 | 36.3811 | 33.2961 | 32.8649 | 34.6135 | 35.0323 | 33.2967 | 34.2534 | 34.3935 | 34.286 | 34.3836 | 34.3552 | 34.2337 | 34.1509 | 34.3708 | 36.1925 | 35.1166 | 36.5226 | 36.5484 | 33.6274 | 94.222 | 94.2467 | 93.7256
2022-09-08 05:00 | 7:10 | 18.99 | 19.5816 | 22.3769 | 35.5058 | 34.2671 | 34.1041 | 34.7449 | 35.5869 | 36.7144 | 37.5395 | 36.9852 | 38.1593 | 34.2784 | 34.2619 | 34.3579 | 35.2245 | 35.2055 | 35.4597 | 36.2262 | 36.6479 | 21.9786 | 18.6081 | 93.4874 | 33.734 | 33.1138 | 35.0775 | 33.2816 | 33.0728 | 33.4365 | 34.6336 | 34.2246 | 34.1191 | 37.2974 | 36.3885 | 33.4437 | 34.4851 | 36.3832 | 36.5624 | 37.4846 | 36.3875 | 33.284 | 32.8394 | 34.6027 | 35.0284 | 33.3156 | 34.2681 | 34.3711 | 34.2851 | 34.388 | 34.3595 | 34.2249 | 34.1691 | 34.3836 | 36.1756 | 35.1036 | 36.5297 | 36.5424 | 33.6032 | 94.3429 | 94.4347 | 93.7853
2022-09-08 05:00 | 7:10 | 18.8998 | 19.5488 | 22.326 | 35.6095 | 34.2517 | 34.0984 | 34.7494 | 35.5716 | 36.696 | 37.5455 | 36.9647 | 38.1608 | 34.2751 | 34.2921 | 34.367 | 35.2022 | 35.1882 | 35.4812 | 36.2372 | 36.6407 | 21.9471 | 18.5956 | 93.4209 | 33.6406 | 33.1063 | 35.0904 | 33.2884 | 33.066 | 33.4568 | 34.6211 | 34.2236 | 34.0988 | 37.2933 | 36.3941 | 33.4338 | 34.4599 | 36.3892 | 36.5558 | 37.4858 | 36.3929 | 33.2686 | 32.8396 | 34.6204 | 35.0343 | 33.2904 | 34.2498 | 34.3761 | 34.2716 | 34.3819 | 34.3552 | 34.2222 | 34.142 | 34.388 | 36.1625 | 35.1227 | 36.5097 | 36.5632 | 33.6219 | 94.4337 | 94.6139 | 93.9518
2022-09-08 05:01 | 7:10 | 18.8345 | 19.4398 | 22.2452 | 35.4698 | 34.24 | 34.1202 | 34.7434 | 35.5864 | 36.721 | 37.5455 | 36.9664 | 38.1678 | 34.2755 | 34.2835 | 34.3693 | 35.2012 | 35.1936 | 35.4838 | 36.1961 | 36.6378 | 21.9232 | 18.5666 | 93.6989 | 33.6433 | 33.1096 | 35.0907 | 33.2815 | 33.0689 | 33.4289 | 34.632 | 34.2206 | 34.105 | 37.2949 | 36.404 | 33.4434 | 34.4813 | 36.3885 | 36.5482 | 37.4759 | 36.3781 | 33.2655 | 32.8372 | 34.5893 | 35.0156 | 33.2956 | 34.2512 | 34.3829 | 34.2707 | 34.39 | 34.3697 | 34.2036 | 34.1502 | 34.3819 | 36.1684 | 35.1177 | 36.509 | 36.5603 | 33.6118 | 94.5466 | 94.6918 | 94.0516
2022-09-08 05:01 | 7:11 | 18.8375 | 19.4484 | 22.2142 | 35.5234 | 34.2794 | 34.0967 | 34.7462 | 35.5688 | 36.7142 | 37.5281 | 36.9779 | 38.1492 | 34.2747 | 34.2763 | 34.3808 | 35.1925 | 35.2131 | 35.4584 | 36.1968 | 36.639 | 21.8892 | 18.5017 | 93.5756 | 33.6285 | 33.0948 | 35.0782 | 33.2961 | 33.0712 | 33.4353 | 34.6381 | 34.2224 | 34.1224 | 37.2909 | 36.3996 | 33.4307 | 34.4601 | 36.3941 | 36.5438 | 37.4802 | 36.3832 | 33.2819 | 32.8341 | 34.6002 | 35.0325 | 33.2821 | 34.2606 | 34.3669 | 34.2963 | 34.3815 | 34.3657 | 34.2465 | 34.1445 | 34.39 | 36.1571 | 35.1095 | 36.5072 | 36.5544 | 33.6136 | 94.6899 | 94.8569 | 94.0365
2022-09-08 05:01 | 7:11 | 18.7227 | 19.3349 | 22.1475 | 35.4597 | 34.2745 | 34.1147 | 34.7402 | 35.5742 | 36.7042 | 37.5239 | 36.9896 | 38.1526 | 34.277 | 34.2662 | 34.3788 | 35.1959 | 35.1964 | 35.4629 | 36.2054 | 36.6421 | 21.8796 | 18.4753 | 93.6726 | 33.729 | 33.0922 | 35.0859 | 33.284 | 33.0807 | 33.4437 | 34.6144 | 34.2283 | 34.126 | 37.2958 | 36.3904 | 33.4492 | 34.4839 | 36.404 | 36.556 | 37.4715 | 36.3892 | 33.2714 | 32.8299 | 34.6059 | 35.0018 | 33.2644 | 34.2593 | 34.3615 | 34.2767 | 34.3946 | 34.3775 | 34.2557 | 34.1611 | 34.3815 | 36.1696 | 35.1076 | 36.5185 | 36.5639 | 33.6099 | 94.6853 | 94.8814 | 93.9298
2022-09-08 05:01 | 7:11 | 18.7434 | 19.3301 | 22.0832 | 35.3662 | 34.2607 | 34.1081 | 34.7336 | 35.5768 | 36.7294 | 37.5112 | 36.9763 | 38.1618 | 34.2969 | 34.2883 | 34.3728 | 35.1998 | 35.1993 | 35.4649 | 36.2127 | 36.6236 | 21.8393 | 18.4863 | 93.9151 | 33.7227 | 33.0822 | 35.0732 | 33.2686 | 33.0668 | 33.4338 | 34.6337 | 34.2161 | 34.1056 | 37.2667 | 36.3835 | 33.4374 | 34.4856 | 36.3996 | 36.5583 | 37.4656 | 36.3885 | 33.2658 | 32.8221 | 34.5794 | 35.0056 | 33.2732 | 34.2701 | 34.3704 | 34.2881 | 34.399 | 34.3693 | 34.2392 | 34.1343 | 34.3946 | 36.169 | 35.1069 | 36.508 | 36.5644 | 33.5949 | 94.8962 | 95.0434 | 94.1795
2022-09-08 05:01 | 7:11 | 18.6417 | 19.2528 | 22.0387 | 35.4775 | 34.2476 | 34.1092 | 34.7176 | 35.5847 | 36.7082 | 37.5243 | 36.9828 | 38.156 | 34.2686 | 34.2702 | 34.3497 | 35.2247 | 35.2062 | 35.4513 | 36.1965 | 36.6326 | 21.8204 | 18.4013 | 93.8981 | 33.9111 | 33.0904 | 35.0755 | 33.2655 | 33.0726 | 33.4434 | 34.6273 | 34.227 | 34.1101 | 37.2939 | 36.4025 | 33.4433 | 34.4775 | 36.3904 | 36.5453 | 37.4616 | 36.3941 | 33.2679 | 32.8245 | 34.5722 | 35.0027 | 33.2687 | 34.2762 | 34.3675 | 34.2839 | 34.394 | 34.3806 | 34.2272 | 34.1481 | 34.399 | 36.1597 | 35.1116 | 36.5194 | 36.5464 | 33.598 | 94.964 | 95.0856 | 94.1883
2022-09-08 05:01 | 7:11 | 18.5798 | 19.2116 | 21.9677 | 35.4196 | 34.2379 | 34.0951 | 34.727 | 35.5769 | 36.7241 | 37.5173 | 36.9816 | 38.1421 | 34.2753 | 34.2901 | 34.3653 | 35.1975 | 35.2012 | 35.4567 | 36.2092 | 36.6304 | 21.8232 | 18.3699 | 94.0194 | 33.5605 | 33.0864 | 35.0977 | 33.2819 | 33.0738 | 33.4307 | 34.6232 | 34.2267 | 34.1046 | 37.2764 | 36.3952 | 33.4339 | 34.4766 | 36.3835 | 36.5455 | 37.4828 | 36.404 | 33.2608 | 32.8026 | 34.5862 | 34.9928 | 33.2566 | 34.2689 | 34.3641 | 34.2905 | 34.3831 | 34.3865 | 34.2286 | 34.1588 | 34.394 | 36.1566 | 35.1188 | 36.5224 | 36.5545 | 33.5885 | 94.9853 | 95.1438 | 94.2599
2022-09-08 05:02 | 7:12 | 18.4816 | 19.131 | 21.8931 | 35.4449 | 34.2642 | 34.1114 | 34.7367 | 35.5768 | 36.7169 | 37.5296 | 36.9981 | 38.1566 | 34.3039 | 34.2698 | 34.3507 | 35.2163 | 35.2162 | 35.4433 | 36.1818 | 36.6277 | 21.8085 | 18.3117 | 93.8188 | 33.6919 | 33.0957 | 35.0827 | 33.2714 | 33.0735 | 33.4492 | 34.6266 | 34.2201 | 34.1173 | 37.2816 | 36.3826 | 33.4328 | 34.4742 | 36.4025 | 36.5394 | 37.4643 | 36.3996 | 33.2602 | 32.8038 | 34.5806 | 34.9774 | 33.2305 | 34.2475 | 34.3676 | 34.2812 | 34.3993 | 34.3695 | 34.2417 | 34.1403 | 34.3831 | 36.1579 | 35.1107 | 36.5092 | 36.5605 | 33.5821 | 94.9792 | 95.1667 | 94.263
2022-09-08 05:02 | 7:12 | 18.5889 | 19.0957 | 21.8607 | 35.4145 | 34.257 | 34.1062 | 34.7141 | 35.5546 | 36.702 | 37.5195 | 36.9763 | 38.1629 | 34.3025 | 34.2599 | 34.3581 | 35.2018 | 35.181 | 35.4681 | 36.1968 | 36.6259 | 21.7944 | 18.3213 | 93.9174 | 33.6578 | 33.1043 | 35.0752 | 33.2658 | 33.0523 | 33.4374 | 34.6086 | 34.2276 | 34.0868 | 37.2838 | 36.3846 | 33.4346 | 34.4903 | 36.3952 | 36.5513 | 37.4747 | 36.3904 | 33.2775 | 32.8115 | 34.5433 | 34.9943 | 33.2335 | 34.249 | 34.3522 | 34.2769 | 34.4008 | 34.3931 | 34.2426 | 34.1198 | 34.3993 | 36.1623 | 35.0996 | 36.5238 | 36.5422 | 33.5862 | 94.8806 | 94.9749 | 94.1957
2022-09-08 05:02 | 7:12 | 18.4994 | 19.0931 | 21.8298 | 35.377 | 34.261 | 34.0907 | 34.7159 | 35.5724 | 36.6898 | 37.502 | 36.9961 | 38.1553 | 34.2992 | 34.2579 | 34.3584 | 35.1948 | 35.1964 | 35.4453 | 36.1925 | 36.6089 | 21.7913 | 18.2369 | 93.9513 | 33.7471 | 33.08 | 35.0648 | 33.2679 | 33.0664 | 33.4433 | 34.6175 | 34.2306 | 34.0974 | 37.2745 | 36.4008 | 33.4412 | 34.47 | 36.3826 | 36.5413 | 37.4633 | 36.3835 | 33.2711 | 32.7995 | 34.5466 | 34.9947 | 33.2511 | 34.2628 | 34.3597 | 34.2715 | 34.3951 | 34.3943 | 34.2332 | 34.1266 | 34.4008 | 36.1463 | 35.0993 | 36.5074 | 36.5484 | 33.5741 | 94.6874 | 94.8022 | 94.119
2022-09-08 05:02 | 7:12 | 18.4471 | 19.0272 | 21.7632 | 35.4532 | 34.2401 | 34.1231 | 34.7296 | 35.5757 | 36.7085 | 37.5099 | 36.9907 | 38.1546 | 34.2896 | 34.2835 | 34.3516 | 35.2066 | 35.184 | 35.46 | 36.1848 | 36.6233 | 21.7972 | 18.1893 | 93.7475 | 33.6083 | 33.0743 | 35.0796 | 33.2608 | 33.0703 | 33.4339 | 34.6074 | 34.2342 | 34.0969 | 37.2669 | 36.3589 | 33.4158 | 34.4575 | 36.3846 | 36.5436 | 37.4555 | 36.4025 | 33.2602 | 32.8001 | 34.5257 | 34.9607 | 33.2051 | 34.2939 | 34.3612 | 34.2877 | 34.4079 | 34.3859 | 34.2406 | 34.1331 | 34.3951 | 36.1304 | 35.113 | 36.5168 | 36.5652 | 33.578 | 94.3952 | 94.5732 | 93.9114
2022-09-08 05:02 | 7:12 | 18.3542 | 18.9639 | 21.7041 | 35.3946 | 34.2519 | 34.1051 | 34.7315 | 35.5686 | 36.6901 | 37.4969 | 36.9761 | 38.1624 | 34.3013 | 34.2687 | 34.3559 | 35.207 | 35.1897 | 35.4307 | 36.18 | 36.6001 | 21.7761 | 18.1769 | 93.5239 | 33.5863 | 33.0854 | 35.0638 | 33.2602 | 33.0594 | 33.4328 | 34.6104 | 34.2112 | 34.1204 | 37.2788 | 36.3714 | 33.4184 | 34.4607 | 36.4008 | 36.5283 | 37.459 | 36.3952 | 33.2622 | 32.7871 | 34.5616 | 34.9831 | 33.2298 | 34.2703 | 34.3588 | 34.2848 | 34.3948 | 34.3905 | 34.2448 | 34.1384 | 34.4079 | 36.1452 | 35.129 | 36.5099 | 36.5381 | 33.5821 | 94.117 | 94.3016 | 93.7629
2022-09-08 05:02 | 7:12 | 18.3459 | 18.9656 | 21.6617 | 35.315 | 34.2418 | 34.0896 | 34.7131 | 35.5703 | 36.694 | 37.505 | 36.9689 | 38.1509 | 34.2854 | 34.2935 | 34.3515 | 35.1945 | 35.1651 | 35.4268 | 36.1609 | 36.616 | 21.797 | 18.1162 | 93.4364 | 33.535 | 33.0969 | 35.0707 | 33.2775 | 33.0528 | 33.4346 | 34.5964 | 34.2212 | 34.0944 | 37.2884 | 36.3872 | 33.4265 | 34.4663 | 36.3589 | 36.5463 | 37.4471 | 36.3826 | 33.2604 | 32.7783 | 34.5308 | 34.9564 | 33.2231 | 34.286 | 34.348 | 34.2906 | 34.4045 | 34.4121 | 34.2515 | 34.1162 | 34.3948 | 36.1471 | 35.107 | 36.5354 | 36.5376 | 33.5639 | 93.9686 | 94.1228 | 93.641
2022-09-08 05:03 | 7:12 | 18.2837 | 18.8509 | 21.6319 | 35.2904 | 34.2244 | 34.1242 | 34.7298 | 35.5705 | 36.6936 | 37.5021 | 37.0083 | 38.1675 | 34.2937 | 34.2831 | 34.3516 | 35.2094 | 35.1666 | 35.4378 | 36.169 | 36.6137 | 21.8034 | 18.0404 | 93.3341 | 33.631 | 33.0973 | 35.0825 | 33.2711 | 33.0507 | 33.4412 | 34.6048 | 34.2339 | 34.0938 | 37.2784 | 36.3781 | 33.4306 | 34.4688 | 36.3714 | 36.5379 | 37.4387 | 36.3846 | 33.2684 | 32.7887 | 34.5175 | 34.9609 | 33.1971 | 34.2558 | 34.3584 | 34.2847 | 34.3886 | 34.3987 | 34.2489 | 34.1155 | 34.4045 | 36.1473 | 35.1127 | 36.52 | 36.5422 | 33.5564 | 93.8587 | 93.9716 | 93.567
2022-09-08 05:03 | 7:13 | 18.2984 | 18.904 | 21.5929 | 35.3327 | 34.231 | 34.0954 | 34.7297 | 35.5786 | 36.7074 | 37.4914 | 36.9806 | 38.1529 | 34.3034 | 34.2733 | 34.3702 | 35.2043 | 35.1848 | 35.4406 | 36.1561 | 36.6046 | 21.8331 | 18.0702 | 93.3344 | 33.3019 | 33.0748 | 35.0822 | 33.2602 | 33.0623 | 33.4158 | 34.6069 | 34.2116 | 34.1133 | 37.2816 | 36.3754 | 33.4235 | 34.5064 | 36.3872 | 36.5477 | 37.4545 | 36.4008 | 33.2699 | 32.7722 | 34.5292 | 34.9337 | 33.1928 | 34.2534 | 34.3529 | 34.2827 | 34.4131 | 34.4099 | 34.2584 | 34.1212 | 34.3886 | 36.1249 | 35.131 | 36.5406 | 36.5328 | 33.5684 | 93.7308 | 93.9442 | 93.5173
2022-09-08 05:03 | 7:13 | 18.2745 | 18.7744 | 21.5487 | 35.3531 | 34.2241 | 34.1113 | 34.7252 | 35.5632 | 36.7081 | 37.5117 | 36.9814 | 38.1533 | 34.3116 | 34.27 | 34.3546 | 35.2303 | 35.189 | 35.4362 | 36.1487 | 36.6046 | 21.8501 | 18.0341 | 93.1476 | 33.6442 | 33.082 | 35.0812 | 33.2622 | 33.0535 | 33.4184 | 34.6044 | 34.2323 | 34.114 | 37.28 | 36.3862 | 33.4374 | 34.4948 | 36.3781 | 36.5501 | 37.4446 | 36.3589 | 33.2497 | 32.7598 | 34.5296 | 34.9548 | 33.1883 | 34.2879 | 34.3391 | 34.2799 | 34.3947 | 34.4176 | 34.2592 | 34.1175 | 34.4131 | 36.1324 | 35.1172 | 36.5247 | 36.534 | 33.5463 | 93.6391 | 93.8745 | 93.4944
2022-09-08 05:03 | 7:13 | 18.1431 | 18.7713 | 21.5279 | 35.2285 | 34.2276 | 34.1141 | 34.7253 | 35.5814 | 36.6859 | 37.4893 | 36.9874 | 38.1783 | 34.3085 | 34.2664 | 34.3569 | 35.2349 | 35.1707 | 35.4339 | 36.1474 | 36.6148 | 21.8409 | 17.9833 | 93.1296 | 33.5913 | 33.075 | 35.0862 | 33.2604 | 33.071 | 33.4265 | 34.621 | 34.2297 | 34.1209 | 37.2799 | 36.3795 | 33.4217 | 34.4909 | 36.3754 | 36.5277 | 37.4456 | 36.3714 | 33.259 | 32.7546 | 34.5162 | 34.9227 | 33.1888 | 34.2669 | 34.3411 | 34.2827 | 34.4081 | 34.4144 | 34.2644 | 34.0952 | 34.3947 | 36.1478 | 35.1227 | 36.5379 | 36.543 | 33.5383 | 93.6424 | 93.767 | 93.4377
2022-09-08 05:03 | 7:13 | 18.1807 | 18.7744 | 21.4747 | 35.266 | 34.2263 | 34.1096 | 34.722 | 35.5752 | 36.6946 | 37.483 | 37.0089 | 38.1618 | 34.3157 | 34.2876 | 34.34 | 35.2212 | 35.188 | 35.4307 | 36.1695 | 36.6257 | 21.8466 | 18.0222 | 93.2252 | 33.4285 | 33.0699 | 35.0852 | 33.2684 | 33.072 | 33.4306 | 34.6091 | 34.2404 | 34.103 | 37.2966 | 36.3839 | 33.4216 | 34.4954 | 36.3862 | 36.5399 | 37.449 | 36.3872 | 33.2847 | 32.7657 | 34.5249 | 34.9337 | 33.1857 | 34.2662 | 34.3517 | 34.2812 | 34.3986 | 34.4039 | 34.2636 | 34.0975 | 34.4081 | 36.1367 | 35.1176 | 36.5199 | 36.5555 | 33.5376 | 93.5437 | 93.6658 | 93.4418
2022-09-08 05:03 | 7:13 | 18.1083 | 18.6752 | 21.3822 | 35.3233 | 34.233 | 34.116 | 34.7225 | 35.557 | 36.7062 | 37.4897 | 36.9924 | 38.158 | 34.3132 | 34.2728 | 34.3476 | 35.2291 | 35.1929 | 35.4556 | 36.1589 | 36.5874 | 21.8411 | 17.9439 | 93.0875 | 33.3718 | 33.0661 | 35.0808 | 33.2699 | 33.0724 | 33.4235 | 34.5834 | 34.2266 | 34.1133 | 37.2828 | 36.4024 | 33.4401 | 34.4883 | 36.3795 | 36.534 | 37.4464 | 36.3781 | 33.2751 | 32.7537 | 34.5124 | 34.9268 | 33.1787 | 34.275 | 34.3372 | 34.2935 | 34.4095 | 34.413 | 34.249 | 34.1121 | 34.3986 | 36.1527 | 35.1278 | 36.5165 | 36.5261 | 33.5484 | 93.5741 | 93.6557 | 93.4551
2022-09-08 05:04 | 7:14 | 18.1197 | 18.6732 | 21.425 | 35.1871 | 34.2272 | 34.1115 | 34.7193 | 35.5669 | 36.6984 | 37.4912 | 36.9957 | 38.1707 | 34.311 | 34.2819 | 34.3477 | 35.2278 | 35.1943 | 35.4397 | 36.1633 | 36.5979 | 21.8447 | 17.9607 | 93.1221 | 33.4203 | 33.0807 | 35.0701 | 33.2497 | 33.065 | 33.4374 | 34.5945 | 34.2497 | 34.1066 | 37.2723 | 36.3645 | 33.4351 | 34.4849 | 36.3839 | 36.5401 | 37.435 | 36.3754 | 33.2674 | 32.7584 | 34.5076 | 34.9357 | 33.1634 | 34.2634 | 34.3392 | 34.3064 | 34.397 | 34.4088 | 34.2604 | 34.1303 | 34.4095 | 36.1494 | 35.1301 | 36.5286 | 36.5371 | 33.5502 | 93.5101 | 93.5681 | 93.3563
2022-09-08 05:04 | 7:14 | 18.0407 | 18.5716 | 21.3508 | 35.2971 | 34.2318 | 34.1074 | 34.7137 | 35.5768 | 36.6972 | 37.4882 | 36.992 | 38.1623 | 34.3103 | 34.2796 | 34.3365 | 35.2113 | 35.1775 | 35.4226 | 36.1453 | 36.6056 | 21.8317 | 17.865 | 92.9263 | 33.4695 | 33.072 | 35.0877 | 33.259 | 33.0572 | 33.4217 | 34.6169 | 34.2273 | 34.1253 | 37.2906 | 36.3914 | 33.4256 | 34.4802 | 36.4024 | 36.5523 | 37.4289 | 36.3862 | 33.2646 | 32.7393 | 34.5024 | 34.9408 | 33.167 | 34.2786 | 34.3167 | 34.2832 | 34.4005 | 34.4049 | 34.2658 | 34.1048 | 34.397 | 36.1272 | 35.0959 | 36.5067 | 36.5324 | 33.5495 | 93.4395 | 93.443 | 93.2872
2022-09-08 05:04 | 7:14 | 18.0373 | 18.5612 | 21.3432 | 35.1412 | 34.2093 | 34.1084 | 34.7172 | 35.5779 | 36.7087 | 37.5132 | 36.9934 | 38.1576 | 34.3166 | 34.3035 | 34.3455 | 35.2281 | 35.1758 | 35.4131 | 36.1593 | 36.6023 | 21.8076 | 17.8747 | 92.8306 | 33.6135 | 33.0777 | 35.0791 | 33.2847 | 33.0522 | 33.4216 | 34.602 | 34.2264 | 34.1061 | 37.2727 | 36.3753 | 33.4134 | 34.4923 | 36.3645 | 36.5531 | 37.4238 | 36.3795 | 33.2551 | 32.7368 | 34.4946 | 34.9284 | 33.1528 | 34.2697 | 34.329 | 34.3067 | 34.4 | 34.4066 | 34.2647 | 34.1076 | 34.4005 | 36.1351 | 35.1066 | 36.5177 | 36.5498 | 33.557 | 93.3511 | 93.3666 | 93.2613
2022-09-08 05:04 | 7:14 | 18.0687 | 18.5552 | 21.3044 | 35.201 | 34.2245 | 34.1205 | 34.7068 | 35.5734 | 36.7097 | 37.5035 | 36.9907 | 38.1715 | 34.3028 | 34.3005 | 34.3451 | 35.2183 | 35.1868 | 35.4265 | 36.1494 | 36.5979 | 21.7931 | 17.872 | 93.0353 | 33.5534 | 33.0711 | 35.0786 | 33.2751 | 33.0572 | 33.4401 | 34.6099 | 34.2341 | 34.1217 | 37.27 | 36.3747 | 33.414 | 34.4878 | 36.3914 | 36.5545 | 37.4315 | 36.3839 | 33.2715 | 32.727 | 34.506 | 34.928 | 33.1422 | 34.2917 | 34.3248 | 34.304 | 34.4074 | 34.4155 | 34.2524 | 34.0989 | 34.4 | 36.1351 | 35.1159 | 36.5203 | 36.5234 | 33.5704 | 93.3726 | 93.275 | 93.2429
2022-09-08 05:04 | 7:14 | 17.9386 | 18.4035 | 21.1857 | 35.2192 | 34.2142 | 34.1087 | 34.7282 | 35.5695 | 36.7061 | 37.499 | 37.0166 | 38.1816 | 34.3171 | 34.302 | 34.3341 | 35.2483 | 35.1951 | 35.4302 | 36.1567 | 36.6122 | 21.7644 | 17.8078 | 93.1532 | 33.5713 | 33.0709 | 35.0856 | 33.2674 | 33.0671 | 33.4351 | 34.5986 | 34.2444 | 34.1249 | 37.2998 | 36.3931 | 33.4284 | 34.5079 | 36.3753 | 36.5582 | 37.4366 | 36.4024 | 33.2555 | 32.7316 | 34.4856 | 34.9114 | 33.1488 | 34.2805 | 34.284 | 34.3165 | 34.3894 | 34.4052 | 34.2657 | 34.1201 | 34.4074 | 36.1449 | 35.1253 | 36.5315 | 36.5497 | 33.5568 | 93.3054 | 93.346 | 93.2626
2022-09-08 05:04 | 7:14 | 17.9672 | 18.4393 | 21.1764 | 35.1689 | 34.2266 | 34.1153 | 34.7184 | 35.5648 | 36.6933 | 37.5022 | 36.9997 | 38.1657 | 34.3077 | 34.293 | 34.3471 | 35.2366 | 35.1867 | 35.4463 | 36.1471 | 36.5998 | 21.7424 | 17.7938 | 93.0096 | 33.4998 | 33.0735 | 35.0836 | 33.2646 | 33.0555 | 33.4256 | 34.5977 | 34.2431 | 34.1267 | 37.2867 | 36.3796 | 33.41 | 34.488 | 36.3747 | 36.5419 | 37.4279 | 36.3645 | 33.2597 | 32.7529 | 34.4739 | 34.9274 | 33.1508 | 34.2874 | 34.3202 | 34.296 | 34.4099 | 34.4237 | 34.2619 | 34.1118 | 34.3894 | 36.1343 | 35.1193 | 36.5337 | 36.5511 | 33.5591 | 93.1881 | 93.23 | 93.145
2022-09-08 05:05 | 7:14 | 17.9936 | 18.4131 | 21.1396 | 35.1711 | 34.2283 | 34.1226 | 34.7218 | 35.5797 | 36.6999 | 37.519 | 37.0081 | 38.1746 | 34.3141 | 34.2838 | 34.3419 | 35.2451 | 35.1791 | 35.4462 | 36.1631 | 36.6134 | 21.7271 | 17.7937 | 92.8916 | 33.4939 | 33.0941 | 35.0877 | 33.2551 | 33.0717 | 33.4134 | 34.602 | 34.2404 | 34.1372 | 37.2746 | 36.3753 | 33.4373 | 34.4889 | 36.3931 | 36.5649 | 37.4467 | 36.3914 | 33.2608 | 32.7244 | 34.4754 | 34.9266 | 33.1533 | 34.2894 | 34.3241 | 34.2982 | 34.4082 | 34.4104 | 34.2921 | 34.1007 | 34.4099 | 36.1469 | 35.1013 | 36.523 | 36.5545 | 33.5488 | 93.1504 | 93.0421 | 93.0866
2022-09-08 05:05 | 7:15 | 17.8834 | 18.3548 | 21.1113 | 35.1037 | 34.2437 | 34.1378 | 34.7047 | 35.5759 | 36.6991 | 37.5141 | 37.0056 | 38.1578 | 34.308 | 34.3006 | 34.3604 | 35.2321 | 35.189 | 35.4479 | 36.1742 | 36.5982 | 21.7145 | 17.7328 | 92.8042 | 33.4849 | 33.077 | 35.0933 | 33.2715 | 33.0472 | 33.414 | 34.6077 | 34.234 | 34.1599 | 37.2691 | 36.362 | 33.4228 | 34.4868 | 36.3796 | 36.5622 | 37.4364 | 36.3753 | 33.2578 | 32.7451 | 34.4998 | 34.9225 | 33.1309 | 34.2747 | 34.324 | 34.3148 | 34.4044 | 34.4256 | 34.2835 | 34.1061 | 34.4082 | 36.1535 | 35.1233 | 36.5213 | 36.5438 | 33.5506 | 93.0304 | 92.9672 | 93.0197
2022-09-08 05:05 | 7:15 | 17.8531 | 18.3228 | 21.1022 | 35.0037 | 34.2337 | 34.1304 | 34.7088 | 35.5743 | 36.7079 | 37.5148 | 37.003 | 38.178 | 34.3024 | 34.2917 | 34.3459 | 35.2337 | 35.1914 | 35.4448 | 36.1437 | 36.6104 | 21.6867 | 17.7036 | 92.8829 | 33.3088 | 33.0595 | 35.0881 | 33.2555 | 33.0656 | 33.4284 | 34.5979 | 34.2473 | 34.1168 | 37.2951 | 36.3837 | 33.4155 | 34.5102 | 36.3753 | 36.5532 | 37.4261 | 36.3747 | 33.2552 | 32.7383 | 34.5001 | 34.9294 | 33.1119 | 34.2704 | 34.3012 | 34.2949 | 34.394 | 34.4147 | 34.2763 | 34.1056 | 34.4044 | 36.1409 | 35.1032 | 36.5428 | 36.5471 | 33.5551 | 92.9383 | 92.9132 | 93.0398
2022-09-08 05:05 | 7:15 | 17.8652 | 18.2818 | 21.0364 | 35.0363 | 34.2249 | 34.1255 | 34.7221 | 35.5676 | 36.6867 | 37.5154 | 37.0284 | 38.1893 | 34.3274 | 34.2787 | 34.3422 | 35.2509 | 35.1842 | 35.472 | 36.1497 | 36.624 | 21.6949 | 17.7264 | 92.7662 | 33.3364 | 33.0753 | 35.0736 | 33.2597 | 33.0638 | 33.41 | 34.6071 | 34.2457 | 34.1237 | 37.2978 | 36.3666 | 33.4225 | 34.5097 | 36.362 | 36.5582 | 37.4371 | 36.3931 | 33.2554 | 32.7232 | 34.4829 | 34.933 | 33.1075 | 34.2749 | 34.314 | 34.3084 | 34.3912 | 34.4178 | 34.2662 | 34.0904 | 34.394 | 36.1452 | 35.1268 | 36.521 | 36.5589 | 33.5728 | 92.7694 | 92.7579 | 92.94
2022-09-08 05:05 | 7:15 | 17.7647 | 18.2821 | 21.0288 | 35.0501 | 34.2222 | 34.1155 | 34.7089 | 35.5731 | 36.7042 | 37.5243 | 37.016 | 38.1941 | 34.3311 | 34.2874 | 34.3379 | 35.2416 | 35.1924 | 35.4314 | 36.1488 | 36.6242 | 21.6687 | 17.665 | 92.6053 | 33.4355 | 33.0799 | 35.0733 | 33.2608 | 33.0632 | 33.4373 | 34.6113 | 34.2601 | 34.1364 | 37.2834 | 36.3651 | 33.4282 | 34.4953 | 36.3837 | 36.5506 | 37.4368 | 36.3796 | 33.2492 | 32.7222 | 34.4856 | 34.9017 | 33.1114 | 34.2869 | 34.2858 | 34.2919 | 34.4017 | 34.4085 | 34.2883 | 34.0911 | 34.3912 | 36.1659 | 35.1187 | 36.5241 | 36.5437 | 33.5615 | 92.6345 | 92.7077 | 92.8874
2022-09-08 05:05 | 7:15 | 17.8704 | 18.2737 | 21.0087 | 34.9465 | 34.2036 | 34.1354 | 34.7073 | 35.5742 | 36.7031 | 37.5132 | 37.0039 | 38.1601 | 34.3401 | 34.2823 | 34.3474 | 35.2386 | 35.1938 | 35.4198 | 36.1546 | 36.6155 | 21.6599 | 17.6449 | 92.5789 | 33.4296 | 33.0697 | 35.0742 | 33.2578 | 33.0664 | 33.4228 | 34.5885 | 34.2586 | 34.1431 | 37.2846 | 36.3784 | 33.4413 | 34.4922 | 36.3666 | 36.5566 | 37.4324 | 36.3753 | 33.2488 | 32.7239 | 34.4615 | 34.915 | 33.1013 | 34.2694 | 34.3149 | 34.3071 | 34.4007 | 34.4113 | 34.2702 | 34.1029 | 34.4017 | 36.1498 | 35.1246 | 36.5401 | 36.5515 | 33.5679 | 92.5948 | 92.5688 | 92.7507
2022-09-08 05:06 | 7:16 | 17.8253 | 18.2348 | 20.976 | 35.1498 | 34.2465 | 34.1463 | 34.723 | 35.5856 | 36.7102 | 37.5306 | 37.0201 | 38.2013 | 34.3395 | 34.3038 | 34.3471 | 35.2312 | 35.1901 | 35.4362 | 36.1537 | 36.6299 | 21.6523 | 17.6276 | 92.3713 | 33.4959 | 33.0758 | 35.07 | 33.2552 | 33.0526 | 33.4155 | 34.6129 | 34.2367 | 34.1296 | 37.2871 | 36.3851 | 33.4244 | 34.5043 | 36.3651 | 36.5565 | 37.4378 | 36.362 | 33.2629 | 32.6996 | 34.463 | 34.9039 | 33.0976 | 34.2996 | 34.2881 | 34.3096 | 34.3736 | 34.4305 | 34.2901 | 34.1027 | 34.4007 | 36.1592 | 35.1294 | 36.5222 | 36.5533 | 33.5748 | 92.4354 | 92.3773 | 92.6668
2022-09-08 05:06 | 7:16 | 17.7407 | 18.1816 | 20.9382 | 35.0333 | 34.2557 | 34.1318 | 34.7165 | 35.5707 | 36.7197 | 37.5296 | 37.0078 | 38.193 | 34.3134 | 34.3108 | 34.3502 | 35.2409 | 35.1904 | 35.4456 | 36.1643 | 36.625 | 21.6407 | 17.5654 | 92.3471 | 33.4309 | 33.0675 | 35.0706 | 33.2554 | 33.0505 | 33.4225 | 34.5929 | 34.2668 | 34.1268 | 37.286 | 36.3794 | 33.4098 | 34.4962 | 36.3784 | 36.5859 | 37.4313 | 36.3837 | 33.2659 | 32.7047 | 34.4597 | 34.8991 | 33.0841 | 34.2873 | 34.2811 | 34.3162 | 34.3656 | 34.4197 | 34.2698 | 34.1106 | 34.3736 | 36.1479 | 35.1267 | 36.5416 | 36.5544 | 33.5846 | 92.2935 | 92.2937 | 92.5486
2022-09-08 05:06 | 7:16 | 17.6592 | 18.1377 | 20.8722 | 34.993 | 34.2392 | 34.1219 | 34.7147 | 35.5919 | 36.7009 | 37.5074 | 37.0204 | 38.1976 | 34.3389 | 34.307 | 34.359 | 35.2623 | 35.1908 | 35.4496 | 36.1604 | 36.6162 | 21.6235 | 17.5618 | 92.235 | 33.2774 | 33.0756 | 35.0841 | 33.2492 | 33.0606 | 33.4282 | 34.5944 | 34.2488 | 34.1335 | 37.3006 | 36.3901 | 33.4317 | 34.5158 | 36.3851 | 36.5636 | 37.4402 | 36.3666 | 33.2386 | 32.6998 | 34.4699 | 34.925 | 33.0853 | 34.2894 | 34.2971 | 34.321 | 34.4075 | 34.4433 | 34.2599 | 34.0831 | 34.3656 | 36.1503 | 35.1062 | 36.5257 | 36.5558 | 33.5622 | 92.132 | 92.1751 | 92.4923
2022-09-08 05:06 | 7:16 | 17.6236 | 18.1097 | 20.8197 | 35.0055 | 34.2272 | 34.1406 | 34.7074 | 35.5779 | 36.7072 | 37.5232 | 37.0166 | 38.2005 | 34.3305 | 34.3032 | 34.3539 | 35.2317 | 35.1924 | 35.4579 | 36.1576 | 36.6037 | 21.6097 | 17.5209 | 92.0841 | 33.2669 | 33.0728 | 35.0737 | 33.2488 | 33.066 | 33.4413 | 34.6109 | 34.2466 | 34.1175 | 37.3077 | 36.3806 | 33.427 | 34.5181 | 36.3794 | 36.5603 | 37.4467 | 36.3651 | 33.2312 | 32.7058 | 34.4715 | 34.9073 | 33.0862 | 34.3071 | 34.2868 | 34.3144 | 34.3735 | 34.4169 | 34.2579 | 34.1048 | 34.4075 | 36.1516 | 35.092 | 36.533 | 36.5616 | 33.5598 | 91.9779 | 92.0091 | 92.3532
2022-09-08 05:06 | 7:16 | 17.6388 | 18.1119 | 20.8078 | 34.8731 | 34.2286 | 34.1265 | 34.6979 | 35.5889 | 36.6993 | 37.5177 | 37.0198 | 38.1839 | 34.3484 | 34.2988 | 34.3458 | 35.2572 | 35.1744 | 35.4596 | 36.1691 | 36.6204 | 21.58 | 17.5028 | 92.1156 | 33.2847 | 33.052 | 35.0857 | 33.2629 | 33.0568 | 33.4244 | 34.6033 | 34.2599 | 34.1332 | 37.2937 | 36.354 | 33.4228 | 34.4911 | 36.3901 | 36.5771 | 37.4156 | 36.3784 | 33.2411 | 32.6834 | 34.4674 | 34.9169 | 33.065 | 34.2902 | 34.2945 | 34.318 | 34.3871 | 34.4257 | 34.2835 | 34.0854 | 34.3735 | 36.1833 | 35.125 | 36.5233 | 36.5489 | 33.5644 | 91.8731 | 91.8802 | 92.2829
2022-09-08 05:06 | 7:16 | 17.5759 | 18.026 | 20.7852 | 34.8482 | 34.2417 | 34.1471 | 34.7237 | 35.5749 | 36.725 | 37.5301 | 37.0183 | 38.1974 | 34.3515 | 34.2945 | 34.3529 | 35.2259 | 35.1805 | 35.4363 | 36.1463 | 36.6246 | 21.5684 | 17.4788 | 92.0451 | 33.2663 | 33.0589 | 35.0753 | 33.2659 | 33.0591 | 33.4098 | 34.5943 | 34.2465 | 34.1306 | 37.2879 | 36.3518 | 33.4197 | 34.4901 | 36.3806 | 36.5751 | 37.4285 | 36.3851 | 33.2411 | 32.7035 | 34.4623 | 34.9311 | 33.0574 | 34.3048 | 34.2866 | 34.3345 | 34.379 | 34.4334 | 34.2687 | 34.0851 | 34.3871 | 36.1698 | 35.1163 | 36.5151 | 36.5303 | 33.5623 | 91.7136 | 91.736 | 92.2234
2022-09-08 05:07 | 7:16 | 17.5789 | 18.0163 | 20.7248 | 34.8877 | 34.2426 | 34.143 | 34.705 | 35.5918 | 36.7029 | 37.5278 | 37.0198 | 38.2113 | 34.3491 | 34.3044 | 34.354 | 35.2679 | 35.1783 | 35.447 | 36.1412 | 36.6273 | 21.5427 | 17.4471 | 91.8651 | 33.3775 | 33.0806 | 35.074 | 33.2386 | 33.0485 | 33.4317 | 34.6001 | 34.2661 | 34.1306 | 37.2967 | 36.3383 | 33.4349 | 34.5151 | 36.354 | 36.5678 | 37.4329 | 36.3794 | 33.2515 | 32.6855 | 34.4528 | 34.9063 | 33.054 | 34.3002 | 34.2951 | 34.3127 | 34.3906 | 34.4252 | 34.2935 | 34.1024 | 34.379 | 36.1594 | 35.1261 | 36.5444 | 36.5407 | 33.5692 | 91.6496 | 91.6319 | 92.1239
2022-09-08 05:07 | 7:17 | 17.5694 | 18.0154 | 20.7353 | 34.9976 | 34.2332 | 34.1344 | 34.6986 | 35.592 | 36.6973 | 37.5359 | 37.0158 | 38.2039 | 34.3442 | 34.3057 | 34.3497 | 35.2429 | 35.1901 | 35.4527 | 36.1717 | 36.6292 | 21.5636 | 17.4397 | 91.745 | 33.3621 | 33.0728 | 35.0601 | 33.2312 | 33.0561 | 33.427 | 34.5938 | 34.2755 | 34.1469 | 37.2869 | 36.3589 | 33.4182 | 34.5186 | 36.3518 | 36.5834 | 37.4253 | 36.3901 | 33.2405 | 32.686 | 34.4724 | 34.904 | 33.0547 | 34.2874 | 34.288 | 34.3299 | 34.3708 | 34.4299 | 34.2831 | 34.0948 | 34.3906 | 36.1676 | 35.1119 | 36.5229 | 36.5595 | 33.5761 | 91.4922 | 91.569 | 92.0986
2022-09-08 05:07 | 7:17 | 17.5007 | 17.9894 | 20.6927 | 34.9354 | 34.2406 | 34.1408 | 34.7134 | 35.5921 | 36.7189 | 37.5414 | 37.0237 | 38.2217 | 34.3612 | 34.2996 | 34.342 | 35.2451 | 35.1734 | 35.4555 | 36.1619 | 36.6185 | 21.5414 | 17.405 | 91.7532 | 33.1776 | 33.0578 | 35.0684 | 33.2411 | 33.057 | 33.4228 | 34.6127 | 34.257 | 34.1434 | 37.2932 | 36.3664 | 33.4245 | 34.516 | 36.3383 | 36.558 | 37.4252 | 36.3806 | 33.2393 | 32.6911 | 34.4728 | 34.8994 | 33.0567 | 34.3012 | 34.2805 | 34.3448 | 34.3874 | 34.4195 | 34.2733 | 34.0848 | 34.3708 | 36.1651 | 35.1092 | 36.5323 | 36.5529 | 33.5579 | 91.5316 | 91.5909 | 92.2076
2022-09-08 05:07 | 7:17 | 17.5432 | 18.0068 | 20.7055 | 34.9526 | 34.2448 | 34.1354 | 34.7274 | 35.5836 | 36.7148 | 37.535 | 37.0306 | 38.2056 | 34.356 | 34.305 | 34.3417 | 35.2548 | 35.1725 | 35.4544 | 36.151 | 36.6378 | 21.5112 | 17.4227 | 91.9184 | 33.2903 | 33.0705 | 35.0588 | 33.2411 | 33.0538 | 33.4197 | 34.5904 | 34.2645 | 34.1461 | 37.3055 | 36.3623 | 33.4168 | 34.5164 | 36.3589 | 36.5823 | 37.4353 | 36.354 | 33.2448 | 32.6802 | 34.4667 | 34.9064 | 33.0448 | 34.3003 | 34.2697 | 34.3212 | 34.3736 | 34.4276 | 34.27 | 34.0795 | 34.3874 | 36.1862 | 35.1228 | 36.5386 | 36.5594 | 33.552 | 91.6841 | 91.7111 | 92.2733
2022-09-08 05:07 | 7:17 | 17.5001 | 17.9495 | 20.6764 | 34.8679 | 34.2515 | 34.1553 | 34.7025 | 35.6025 | 36.7132 | 37.5317 | 37.0152 | 38.2056 | 34.3552 | 34.3183 | 34.3547 | 35.248 | 35.1643 | 35.453 | 36.1387 | 36.6253 | 21.4955 | 17.4105 | 92.0688 | 33.2523 | 33.0634 | 35.048 | 33.2515 | 33.0539 | 33.4349 | 34.6175 | 34.2613 | 34.1285 | 37.3056 | 36.3576 | 33.4108 | 34.5015 | 36.3664 | 36.5612 | 37.4304 | 36.3518 | 33.2278 | 32.6644 | 34.443 | 34.9162 | 33.0427 | 34.2999 | 34.2489 | 34.3263 | 34.3689 | 34.4221 | 34.2664 | 34.086 | 34.3736 | 36.2019 | 35.1185 | 36.5483 | 36.5736 | 33.5781 | 91.8578 | 91.8152 | 92.325
2022-09-08 05:07 | 7:17 | 17.4787 | 17.9059 | 20.6314 | 34.7885 | 34.2489 | 34.1349 | 34.7012 | 35.5944 | 36.7161 | 37.5282 | 37.0276 | 38.2058 | 34.3595 | 34.3151 | 34.3457 | 35.2473 | 35.1628 | 35.447 | 36.1651 | 36.6463 | 21.4814 | 17.4268 | 92.0684 | 33.2163 | 33.0718 | 35.0504 | 33.2405 | 33.0502 | 33.4182 | 34.6068 | 34.2551 | 34.1264 | 37.2941 | 36.3534 | 33.4205 | 34.5169 | 36.3623 | 36.5597 | 37.4277 | 36.3383 | 33.2037 | 32.6591 | 34.4464 | 34.8903 | 33.014 | 34.2937 | 34.2805 | 34.3437 | 34.381 | 34.4092 | 34.2876 | 34.101 | 34.3689 | 36.1749 | 35.1265 | 36.5111 | 36.565 | 33.5768 | 91.9148 | 91.9574 | 92.4222
2022-09-08 05:08 | 7:17 | 17.4757 | 17.9948 | 20.6135 | 34.8559 | 34.2584 | 34.1479 | 34.7203 | 35.579 | 36.6958 | 37.5279 | 37.0259 | 38.2055 | 34.3552 | 34.3258 | 34.3643 | 35.2546 | 35.1557 | 35.4478 | 36.1592 | 36.6134 | 21.4706 | 17.3948 | 92.1121 | 33.2895 | 33.0806 | 35.0528 | 33.2393 | 33.0557 | 33.4245 | 34.6077 | 34.2361 | 34.1331 | 37.2933 | 36.363 | 33.4181 | 34.4982 | 36.3576 | 36.5732 | 37.4273 | 36.3589 | 33.2198 | 32.6803 | 34.4435 | 34.8919 | 33.0004 | 34.299 | 34.2768 | 34.331 | 34.3957 | 34.4068 | 34.2728 | 34.0875 | 34.381 | 36.1666 | 35.1198 | 36.5325 | 36.5493 | 33.5528 | 91.9993 | 92.1002 | 92.4561
2022-09-08 05:08 | 7:18 | 17.4594 | 17.8851 | 20.5992 | 34.9252 | 34.2592 | 34.1396 | 34.7067 | 35.5811 | 36.698 | 37.5278 | 37.0265 | 38.2005 | 34.3697 | 34.3361 | 34.3542 | 35.242 | 35.1628 | 35.4443 | 36.1566 | 36.6158 | 21.4208 | 17.3825 | 92.2683 | 33.0885 | 33.0648 | 35.073 | 33.2448 | 33.0412 | 33.4168 | 34.6158 | 34.253 | 34.137 | 37.2792 | 36.3263 | 33.4284 | 34.4964 | 36.3534 | 36.5588 | 37.4161 | 36.3664 | 33.2197 | 32.6609 | 34.437 | 34.8832 | 32.9946 | 34.2969 | 34.2759 | 34.3357 | 34.3959 | 34.42 | 34.2819 | 34.0784 | 34.3957 | 36.171 | 35.1238 | 36.5309 | 36.5537 | 33.5676 | 92.2837 | 92.2616 | 92.5928
2022-09-08 05:08 | 7:18 | 17.4192 | 17.8483 | 20.6093 | 34.8427 | 34.2644 | 34.1465 | 34.7166 | 35.571 | 36.6912 | 37.5208 | 37.0377 | 38.2073 | 34.3657 | 34.3346 | 34.3568 | 35.2445 | 35.1728 | 35.4345 | 36.1338 | 36.6521 | 21.3998 | 17.3229 | 92.4444 | 33.4232 | 33.0736 | 35.0317 | 33.2278 | 33.038 | 33.4108 | 34.6103 | 34.2597 | 34.1302 | 37.294 | 36.3579 | 33.4271 | 34.4977 | 36.363 | 36.571 | 37.4377 | 36.3623 | 33.2212 | 32.6699 | 34.4325 | 34.8938 | 33.0027 | 34.3258 | 34.2773 | 34.3207 | 34.3954 | 34.4177 | 34.2796 | 34.0735 | 34.3959 | 36.1787 | 35.1084 | 36.5434 | 36.5533 | 33.5584 | 92.5 | 92.4496 | 92.7381
2022-09-08 05:08 | 7:18 | 17.3591 | 17.7944 | 20.5267 | 34.8006 | 34.2636 | 34.1454 | 34.6977 | 35.5896 | 36.7104 | 37.532 | 37.0084 | 38.2043 | 34.3775 | 34.3449 | 34.3652 | 35.247 | 35.1634 | 35.463 | 36.1568 | 36.6375 | 21.3689 | 17.3335 | 92.4219 | 33.3698 | 33.0564 | 35.0453 | 33.2037 | 33.0377 | 33.4205 | 34.6065 | 34.2442 | 34.1273 | 37.2931 | 36.3479 | 33.4031 | 34.4917 | 36.3263 | 36.5481 | 37.4242 | 36.3576 | 33.2106 | 32.6655 | 34.4327 | 34.8743 | 32.9789 | 34.3029 | 34.2559 | 34.3302 | 34.3689 | 34.4024 | 34.3035 | 34.0633 | 34.3954 | 36.1778 | 35.1146 | 36.5461 | 36.5446 | 33.5698 | 92.6212 | 92.5884 | 92.7946
2022-09-08 05:08 | 7:18 | 17.4516 | 17.8455 | 20.5474 | 34.8157 | 34.249 | 34.1468 | 34.7069 | 35.5743 | 36.7015 | 37.533 | 37.0101 | 38.2069 | 34.3693 | 34.3281 | 34.3526 | 35.2447 | 35.1545 | 35.4494 | 36.1462 | 36.6348 | 21.3485 | 17.3326 | 92.5829 | 33.3295 | 33.0642 | 35.0514 | 33.2198 | 33.0496 | 33.4181 | 34.6027 | 34.2512 | 34.1397 | 37.291 | 36.3299 | 33.4142 | 34.5157 | 36.3579 | 36.5787 | 37.4261 | 36.3534 | 33.2023 | 32.6482 | 34.4221 | 34.8743 | 32.9892 | 34.3067 | 34.2679 | 34.3411 | 34.3935 | 34.4244 | 34.3005 | 34.0638 | 34.3689 | 36.1728 | 35.0983 | 36.5364 | 36.5779 | 33.571 | 92.6867 | 92.8013 | 92.8957
2022-09-08 05:08 | 7:18 | 17.4733 | 17.7734 | 20.5358 | 34.8366 | 34.2604 | 34.1217 | 34.6895 | 35.5781 | 36.7028 | 37.542 | 37.0012 | 38.1923 | 34.3806 | 34.3266 | 34.3505 | 35.2371 | 35.1617 | 35.4407 | 36.1416 | 36.6216 | 21.3063 | 17.3153 | 92.6046 | 33.0532 | 33.0704 | 35.0521 | 33.2197 | 33.0426 | 33.4284 | 34.6253 | 34.2506 | 34.1358 | 37.2902 | 36.3313 | 33.4262 | 34.4911 | 36.3479 | 36.5478 | 37.4311 | 36.363 | 33.2111 | 32.6327 | 34.4299 | 34.8599 | 32.9679 | 34.2895 | 34.2634 | 34.3387 | 34.3711 | 34.4303 | 34.302 | 34.0726 | 34.3935 | 36.1687 | 35.1055 | 36.5436 | 36.5662 | 33.5492 | 92.8411 | 92.9368 | 93.0179
2022-09-08 05:09 | 7:19 | 17.415 | 17.7394 | 20.4523 | 34.8183 | 34.2658 | 34.1321 | 34.6795 | 35.5881 | 36.6903 | 37.5565 | 37.0131 | 38.2163 | 34.3865 | 34.3258 | 34.3631 | 35.2467 | 35.137 | 35.4516 | 36.1394 | 36.6259 | 21.2814 | 17.2788 | 92.8155 | 33.2039 | 33.0637 | 35.0397 | 33.2212 | 33.042 | 33.4271 | 34.6083 | 34.249 | 34.1352 | 37.2899 | 36.3462 | 33.4115 | 34.477 | 36.3299 | 36.5612 | 37.4273 | 36.3263 | 33.2055 | 32.648 | 34.4323 | 34.8564 | 32.9683 | 34.3012 | 34.2433 | 34.3405 | 34.3761 | 34.3986 | 34.293 | 34.0653 | 34.3711 | 36.1762 | 35.1197 | 36.5407 | 36.5497 | 33.5556 | 93.0575 | 93.1798 | 93.108
2022-09-08 05:09 | 7:19 | 17.3775 | 17.9296 | 20.4476 | 34.8027 | 34.2647 | 34.1203 | 34.6898 | 35.5839 | 36.7121 | 37.5411 | 37.009 | 38.1878 | 34.3695 | 34.3246 | 34.3454 | 35.2351 | 35.1448 | 35.4457 | 36.1324 | 36.6287 | 21.2242 | 17.2654 | 92.7426 | 33.1264 | 33.0476 | 35.035 | 33.2106 | 33.0266 | 33.4031 | 34.6102 | 34.2331 | 34.1212 | 37.2561 | 36.319 | 33.4234 | 34.4888 | 36.3313 | 36.5715 | 37.4308 | 36.3579 | 33.1885 | 32.6558 | 34.4247 | 34.8514 | 32.9393 | 34.3086 | 34.2467 | 34.3314 | 34.3829 | 34.4138 | 34.2838 | 34.0542 | 34.3761 | 36.1733 | 35.1054 | 36.5373 | 36.5336 | 33.545 | 93.3024 | 93.2557 | 93.1397
2022-09-08 05:09 | 7:19 | 17.3462 | 17.9492 | 20.4601 | 34.7532 | 34.2524 | 34.1214 | 34.6864 | 35.5616 | 36.7035 | 37.5502 | 37.0169 | 38.2009 | 34.3931 | 34.3525 | 34.3446 | 35.2421 | 35.1481 | 35.4435 | 36.1349 | 36.6362 | 21.2138 | 17.2899 | 93.0768 | 33.1979 | 33.042 | 35.0387 | 33.2023 | 33.0287 | 33.4142 | 34.5958 | 34.2356 | 34.1285 | 37.291 | 36.3366 | 33.3969 | 34.4984 | 36.3462 | 36.5553 | 37.4355 | 36.3479 | 33.1959 | 32.6337 | 34.3959 | 34.8347 | 32.9486 | 34.3017 | 34.2441 | 34.3627 | 34.3669 | 34.4144 | 34.3006 | 34.0609 | 34.3829 | 36.1797 | 35.1029 | 36.5329 | 36.551 | 33.5535 | 93.5208 | 93.4438 | 93.3431
2022-09-08 05:09 | 7:19 | 17.3257 | 17.6976 | 20.4246 | 34.8107 | 34.2657 | 34.1285 | 34.6666 | 35.5614 | 36.7088 | 37.5367 | 37.0208 | 38.2083 | 34.3943 | 34.3515 | 34.348 | 35.2304 | 35.1609 | 35.4351 | 36.137 | 36.6317 | 21.1899 | 17.2455 | 93.0675 | 33.1116 | 33.0502 | 35.0335 | 33.2111 | 33.0355 | 33.4262 | 34.6205 | 34.2334 | 34.1197 | 37.2776 | 36.3257 | 33.4065 | 34.4888 | 36.319 | 36.5587 | 37.4307 | 36.3299 | 33.1927 | 32.6193 | 34.4116 | 34.8604 | 32.9392 | 34.2989 | 34.2525 | 34.3524 | 34.3615 | 34.3916 | 34.2917 | 34.0638 | 34.3669 | 36.1699 | 35.1178 | 36.5303 | 36.5374 | 33.5744 | 93.6987 | 93.5893 | 93.3931
2022-09-08 05:09 | 7:19 | 17.2546 | 17.6691 | 20.3999 | 34.6647 | 34.2619 | 34.1167 | 34.6852 | 35.5822 | 36.6923 | 37.5259 | 37.0151 | 38.2039 | 34.3859 | 34.349 | 34.3493 | 35.2291 | 35.1234 | 35.4415 | 36.151 | 36.6212 | 21.189 | 17.2252 | 93.2726 | 32.9052 | 33.053 | 35.0193 | 33.2055 | 33.0489 | 33.4115 | 34.6033 | 34.227 | 34.1196 | 37.2971 | 36.3435 | 33.3964 | 34.4896 | 36.3366 | 36.5603 | 37.4139 | 36.3313 | 33.2066 | 32.6298 | 34.4124 | 34.8345 | 32.9209 | 34.3104 | 34.2545 | 34.339 | 34.3704 | 34.3969 | 34.2787 | 34.0554 | 34.3615 | 36.1773 | 35.0812 | 36.5386 | 36.5496 | 33.5335 | 93.8677 | 93.8091 | 93.5616
2022-09-08 05:09 | 7:19 | 17.2691 | 17.6723 | 20.4189 | 34.7213 | 34.2921 | 34.1155 | 34.6666 | 35.5693 | 36.7001 | 37.5428 | 37.0056 | 38.1894 | 34.3905 | 34.3519 | 34.3346 | 35.2537 | 35.1412 | 35.4386 | 36.1397 | 36.6334 | 21.1731 | 17.2589 | 93.196 | 33.08 | 33.0438 | 35.019 | 33.1885 | 33.064 | 33.4234 | 34.6226 | 34.2268 | 34.1212 | 37.2845 | 36.3177 | 33.4133 | 34.4838 | 36.3257 | 36.567 | 37.4201 | 36.3462 | 33.1823 | 32.6251 | 34.3694 | 34.8336 | 32.9298 | 34.3215 | 34.2448 | 34.3447 | 34.3675 | 34.4054 | 34.2874 | 34.0593 | 34.3704 | 36.1638 | 35.0813 | 36.5363 | 36.5379 | 33.551 | 93.9415 | 93.972 | 93.6596
2022-09-08 05:10 | 7:19 | 17.4543 | 17.6478 | 20.3673 | 34.6979 | 34.2835 | 34.1115 | 34.6896 | 35.5879 | 36.6757 | 37.5078 | 37.019 | 38.1952 | 34.4121 | 34.3619 | 34.3393 | 35.2242 | 35.1424 | 35.4435 | 36.1432 | 36.6186 | 21.1427 | 17.2112 | 93.2369 | 33.2838 | 33.0453 | 35.0137 | 33.1959 | 33.0545 | 33.3969 | 34.6073 | 34.2306 | 34.1152 | 37.2853 | 36.3334 | 33.4096 | 34.4844 | 36.3435 | 36.5646 | 37.4233 | 36.319 | 33.1993 | 32.5968 | 34.3901 | 34.8502 | 32.9199 | 34.3095 | 34.2525 | 34.3445 | 34.3641 | 34.39 | 34.2823 | 34.0283 | 34.3675 | 36.1795 | 35.102 | 36.5381 | 36.5573 | 33.5273 | 94.0665 | 94.1766 | 93.7485
2022-09-08 05:10 | 7:20 | 17.1732 | 17.5673 | 20.3157 | 34.7154 | 34.2763 | 34.1274 | 34.6797 | 35.5634 | 36.7113 | 37.5222 | 37.0022 | 38.1919 | 34.3987 | 34.3367 | 34.348 | 35.233 | 35.1274 | 35.413 | 36.1192 | 36.6343 | 21.1199 | 17.1349 | 93.4668 | 33.1269 | 33.0427 | 35.0111 | 33.1927 | 33.0344 | 33.4065 | 34.6052 | 34.2193 | 34.1091 | 37.2583 | 36.34 | 33.3992 | 34.4584 | 36.3177 | 36.5543 | 37.4082 | 36.3366 | 33.193 | 32.6209 | 34.3738 | 34.8156 | 32.9114 | 34.3237 | 34.2548 | 34.3313 | 34.3676 | 34.3894 | 34.3038 | 34.0399 | 34.3641 | 36.1493 | 35.1056 | 36.5211 | 36.535 | 33.5339 | 94.1938 | 94.3721 | 93.8433
2022-09-08 05:10 | 7:20 | 17.2032 | 17.6026 | 20.3302 | 34.7325 | 34.2662 | 34.0881 | 34.6792 | 35.558 | 36.692 | 37.5438 | 36.9976 | 38.1802 | 34.4099 | 34.3546 | 34.3188 | 35.2499 | 35.138 | 35.4193 | 36.1348 | 36.6084 | 21.1069 | 17.2062 | 93.6809 | 33.1506 | 33.0336 | 35.0303 | 33.2066 | 33.0506 | 33.3964 | 34.5983 | 34.2341 | 34.1016 | 37.2763 | 36.3139 | 33.4192 | 34.4779 | 36.3334 | 36.5801 | 37.4161 | 36.3257 | 33.1927 | 32.5886 | 34.3794 | 34.8176 | 32.9125 | 34.3314 | 34.2212 | 34.3636 | 34.3522 | 34.389 | 34.3108 | 34.0582 | 34.3676 | 36.1557 | 35.0924 | 36.5278 | 36.5313 | 33.527 | 94.4198 | 94.528 | 93.9343
2022-09-08 05:10 | 7:20 | 17.203 | 17.602 | 20.3184 | 34.7063 | 34.2883 | 34.1125 | 34.6695 | 35.5628 | 36.6827 | 37.5357 | 37.0113 | 38.1765 | 34.4176 | 34.3545 | 34.3387 | 35.2374 | 35.1181 | 35.4263 | 36.1172 | 36.608 | 21.0898 | 17.1645 | 93.8119 | 33.046 | 33.0426 | 35.0215 | 33.1823 | 33.0323 | 33.4133 | 34.5951 | 34.2132 | 34.1102 | 37.2777 | 36.3263 | 33.4092 | 34.4809 | 36.34 | 36.5669 | 37.434 | 36.3435 | 33.1902 | 32.6005 | 34.3746 | 34.8128 | 32.8924 | 34.3381 | 34.2496 | 34.3523 | 34.3597 | 34.3754 | 34.307 | 34.0349 | 34.3522 | 36.1734 | 35.0811 | 36.5202 | 36.5418 | 33.5124 | 94.5808 | 94.6239 | 94.0711
2022-09-08 05:10 | 7:20 | 17.2548 | 17.6115 | 20.2975 | 34.6541 | 34.2702 | 34.1172 | 34.6767 | 35.5583 | 36.6976 | 37.5351 | 37.0118 | 38.1955 | 34.4144 | 34.3722 | 34.3354 | 35.2321 | 35.136 | 35.4252 | 36.1176 | 36.5947 | 21.0719 | 17.1799 | 93.4914 | 33.0451 | 33.065 | 35.0174 | 33.1993 | 33.0318 | 33.4096 | 34.6073 | 34.2318 | 34.1031 | 37.2775 | 36.3108 | 33.4202 | 34.4597 | 36.3139 | 36.5541 | 37.3979 | 36.3177 | 33.1691 | 32.5753 | 34.3693 | 34.805 | 32.8874 | 34.3392 | 34.248 | 34.3511 | 34.3612 | 34.4017 | 34.3032 | 34.0339 | 34.3597 | 36.1641 | 35.097 | 36.5368 | 36.5541 | 33.5179 | 94.6009 | 94.7479 | 94.0332
2022-09-08 05:10 | 7:20 | 17.2281 | 17.6384 | 20.3286 | 34.5626 | 34.2901 | 34.1134 | 34.6801 | 35.5764 | 36.6833 | 37.5278 | 36.994 | 38.1896 | 34.4039 | 34.3564 | 34.3257 | 35.2333 | 35.1145 | 35.4201 | 36.1186 | 36.617 | 21.0479 | 17.161 | 93.4209 | 33.0887 | 33.0502 | 35.0221 | 33.193 | 33.0231 | 33.3992 | 34.5882 | 34.2109 | 34.0951 | 37.2742 | 36.3031 | 33.3958 | 34.4757 | 36.3263 | 36.5382 | 37.4076 | 36.3334 | 33.1731 | 32.5844 | 34.3441 | 34.7831 | 32.8811 | 34.3358 | 34.2409 | 34.3342 | 34.3588 | 34.391 | 34.2988 | 34.0301 | 34.3612 | 36.1525 | 35.0838 | 36.5216 | 36.5463 | 33.5174 | 94.7514 | 94.8469 | 94.016
2022-09-08 05:11 | 7:21 | 17.1997 | 17.6041 | 20.2616 | 34.5553 | 34.2698 | 34.1199 | 34.669 | 35.5836 | 36.6793 | 37.5373 | 36.9984 | 38.1887 | 34.413 | 34.3626 | 34.333 | 35.211 | 35.1036 | 35.4248 | 36.1298 | 36.6302 | 21.0678 | 17.1483 | 93.7021 | 32.9231 | 33.0437 | 35.0109 | 33.1927 | 33.0297 | 33.4192 | 34.602 | 34.2207 | 34.0978 | 37.2887 | 36.321 | 33.4134 | 34.4815 | 36.3108 | 36.5547 | 37.4078 | 36.34 | 33.1746 | 32.6028 | 34.3539 | 34.7787 | 32.8763 | 34.3331 | 34.2316 | 34.3608 | 34.348 | 34.3897 | 34.2945 | 34.0239 | 34.3588 | 36.1508 | 35.0858 | 36.5562 | 36.5318 | 33.5032 | 94.858 | 94.9028 | 94.1958
2022-09-08 05:11 | 7:21 | 17.1374 | 17.5483 | 20.2333 | 34.6816 | 34.2599 | 34.1009 | 34.6675 | 35.5628 | 36.6923 | 37.5304 | 37.0075 | 38.1825 | 34.4088 | 34.3826 | 34.3106 | 35.2099 | 35.1087 | 35.4476 | 36.1061 | 36.619 | 21.0561 | 17.0681 | 93.7811 | 33.0549 | 33.0292 | 35.008 | 33.1902 | 33.0197 | 33.4092 | 34.6074 | 34.2286 | 34.0912 | 37.2569 | 36.3097 | 33.3958 | 34.4734 | 36.3031 | 36.5461 | 37.4004 | 36.3139 | 33.1824 | 32.5592 | 34.3613 | 34.7899 | 32.8803 | 34.3338 | 34.232 | 34.3525 | 34.3584 | 34.4178 | 34.3044 | 34.0166 | 34.348 | 36.1527 | 35.0973 | 36.5234 | 36.5375 | 33.4909 | 94.8219 | 95.0689 | 94.2691
2022-09-08 05:11 | 7:21 | 17.0658 | 17.4491 | 20.2027 | 34.6915 | 34.2579 | 34.109 | 34.6765 | 35.5567 | 36.6889 | 37.5204 | 36.9916 | 38.1902 | 34.4049 | 34.3874 | 34.3142 | 35.2401 | 35.0825 | 35.4037 | 36.101 | 36.6088 | 21.0413 | 17.0358 | 94.012 | 33.1235 | 33.0294 | 34.9977 | 33.1691 | 33.0087 | 33.4202 | 34.5923 | 34.2172 | 34.0934 | 37.277 | 36.3113 | 33.3918 | 34.4671 | 36.321 | 36.5656 | 37.394 | 36.3263 | 33.1877 | 32.5806 | 34.3345 | 34.7947 | 32.8787 | 34.3394 | 34.2174 | 34.3616 | 34.3529 | 34.3883 | 34.3057 | 34.0261 | 34.3584 | 36.1501 | 35.0726 | 36.5448 | 36.5474 | 33.4964 | 94.8135 | 95.1323 | 94.3263
2022-09-08 05:11 | 7:21 | 17.1805 | 17.4891 | 20.1566 | 34.6583 | 34.2835 | 34.1229 | 34.6649 | 35.5565 | 36.663 | 37.5241 | 36.9819 | 38.1829 | 34.4066 | 34.3695 | 34.3154 | 35.2045 | 35.1048 | 35.4319 | 36.106 | 36.581 | 21.0026 | 17.1176 | 94.059 | 33.0289 | 33.0399 | 35.0029 | 33.1731 | 33.018 | 33.3958 | 34.6004 | 34.2173 | 34.084 | 37.2729 | 36.3009 | 33.3995 | 34.4545 | 36.3097 | 36.5495 | 37.4064 | 36.3108 | 33.1627 | 32.5612 | 34.3167 | 34.7853 | 32.8636 | 34.3469 | 34.225 | 34.3556 | 34.3391 | 34.3888 | 34.2996 | 34.0023 | 34.3529 | 36.1566 | 35.0777 | 36.5381 | 36.5169 | 33.4798 | 94.8882 | 95.1222 | 94.3255
2022-09-08 05:11 | 7:21 | 17.0971 | 17.5072 | 20.1799 | 34.6182 | 34.2687 | 34.1116 | 34.6637 | 35.551 | 36.6829 | 37.5179 | 36.9886 | 38.1867 | 34.4155 | 34.3708 | 34.3017 | 35.2423 | 35.0809 | 35.4225 | 36.1069 | 36.6004 | 21.027 | 17.0911 | 93.9526 | 33.062 | 33.0305 | 35.0126 | 33.1746 | 33.0083 | 33.4134 | 34.5946 | 34.2254 | 34.0899 | 37.2696 | 36.3099 | 33.3984 | 34.4685 | 36.3113 | 36.5363 | 37.3942 | 36.3031 | 33.1664 | 32.5605 | 34.3286 | 34.7588 | 32.8495 | 34.3445 | 34.2447 | 34.3518 | 34.3411 | 34.3921 | 34.305 | 34.0267 | 34.3391 | 36.1373 | 35.0796 | 36.5449 | 36.5195 | 33.5069 | 94.7575 | 94.954 | 94.1087
2022-09-08 05:11 | 7:21 | 17.0924 | 17.4681 | 20.1723 | 34.4401 | 34.2935 | 34.1127 | 34.6658 | 35.5473 | 36.6555 | 37.5046 | 36.992 | 38.197 | 34.4052 | 34.3836 | 34.3199 | 35.2074 | 35.0904 | 35.4275 | 36.0956 | 36.5924 | 21.0006 | 17.0161 | 93.7443 | 33.0239 | 33.0276 | 34.9937 | 33.1824 | 33.0022 | 33.3958 | 34.5899 | 34.2436 | 34.0797 | 37.256 | 36.3081 | 33.3805 | 34.4695 | 36.3009 | 36.5463 | 37.3949 | 36.321 | 33.1671 | 32.548 | 34.3319 | 34.7765 | 32.8657 | 34.3536 | 34.2409 | 34.3473 | 34.3517 | 34.3827 | 34.3183 | 34.0074 | 34.3411 | 36.1553 | 35.0971 | 36.5337 | 36.5345 | 33.4524 | 94.5667 | 94.7082 | 93.9532
2022-09-08 05:12 | 7:21 | 17.0421 | 17.4419 | 20.1012 | 34.6194 | 34.2831 | 34.1031 | 34.6668 | 35.5717 | 36.678 | 37.5053 | 37.0104 | 38.193 | 34.4237 | 34.388 | 34.3031 | 35.2403 | 35.0963 | 35.423 | 36.0992 | 36.5753 | 21.0074 | 16.9819 | 93.6383 | 33.0306 | 33.0308 | 35.0137 | 33.1877 | 33.0175 | 33.3918 | 34.5849 | 34.2067 | 34.0845 | 37.2648 | 36.3068 | 33.3868 | 34.4546 | 36.3099 | 36.5595 | 37.407 | 36.3097 | 33.1764 | 32.5508 | 34.3255 | 34.7781 | 32.8394 | 34.3582 | 34.2475 | 34.3631 | 34.3372 | 34.3639 | 34.3151 | 34.0121 | 34.3517 | 36.129 | 35.1097 | 36.5233 | 36.5351 | 33.4779 | 94.3122 | 94.4691 | 93.7904
2022-09-08 05:12 | 7:22 | 17.0737 | 17.4664 | 20.1062 | 34.6335 | 34.2733 | 34.1111 | 34.655 | 35.5671 | 36.6606 | 37.4877 | 36.9937 | 38.2122 | 34.4104 | 34.3819 | 34.3146 | 35.2164 | 35.0881 | 35.4178 | 36.0959 | 36.5929 | 21.0285 | 16.9799 | 93.5148 | 33.0426 | 33.0369 | 34.9877 | 33.1627 | 33.0042 | 33.3995 | 34.5814 | 34.2269 | 34.0903 | 37.2638 | 36.2853 | 33.3781 | 34.4701 | 36.3081 | 36.5412 | 37.3869 | 36.3113 | 33.1773 | 32.5399 | 34.3135 | 34.7656 | 32.8447 | 34.3729 | 34.2458 | 34.3588 | 34.3392 | 34.3606 | 34.3258 | 34.0035 | 34.3372 | 36.1412 | 35.077 | 36.5409 | 36.5235 | 33.4974 | 94.0324 | 94.1181 | 93.653
2022-09-08 05:12 | 7:22 | 17.1904 | 17.4701 | 20.0983 | 34.5801 | 34.27 | 34.1194 | 34.659 | 35.5617 | 36.664 | 37.5251 | 37.0236 | 38.1981 | 34.4256 | 34.39 | 34.2945 | 35.2104 | 35.0889 | 35.4079 | 36.092 | 36.5873 | 21.033 | 16.9806 | 93.4163 | 33.0768 | 33.024 | 34.9878 | 33.1664 | 33.0112 | 33.3984 | 34.5948 | 34.2178 | 34.1016 | 37.2633 | 36.3284 | 33.374 | 34.4745 | 36.3068 | 36.5545 | 37.38 | 36.3009 | 33.1606 | 32.5448 | 34.3182 | 34.7588 | 32.8423 | 34.3713 | 34.2386 | 34.3765 | 34.3167 | 34.3735 | 34.3361 | 34.0111 | 34.3392 | 36.1461 | 35.0874 | 36.538 | 36.5215 | 33.4879 | 93.8833 | 93.9254 | 93.5693
2022-09-08 05:12 | 7:22 | 17.1001 | 17.4961 | 20.1109 | 34.5322 | 34.2664 | 34.1197 | 34.6688 | 35.5581 | 36.6861 | 37.5183 | 37.0138 | 38.1824 | 34.4147 | 34.3815 | 34.3086 | 35.2389 | 35.0874 | 35.4102 | 36.0926 | 36.5747 | 21.0595 | 16.9631 | 93.2328 | 33.0131 | 33.0141 | 35.0012 | 33.1671 | 33.0108 | 33.3805 | 34.579 | 34.2162 | 34.1032 | 37.242 | 36.3077 | 33.3869 | 34.4878 | 36.2853 | 36.5539 | 37.3811 | 36.3099 | 33.1605 | 32.553 | 34.3232 | 34.7292 | 32.8428 | 34.3734 | 34.2449 | 34.3375 | 34.329 | 34.3815 | 34.3346 | 34.0076 | 34.3167 | 36.1481 | 35.0731 | 36.5202 | 36.5144 | 33.4843 | 93.7566 | 93.8229 | 93.4857
2022-09-08 05:12 | 7:22 | 17.089 | 17.4846 | 20.112 | 34.548 | 34.2876 | 34.1187 | 34.6746 | 35.5531 | 36.6763 | 37.5311 | 37.0193 | 38.1865 | 34.4178 | 34.3946 | 34.2921 | 35.2258 | 35.0827 | 35.4117 | 36.1037 | 36.571 | 21.0986 | 16.9647 | 93.2838 | 33.0616 | 33.0013 | 34.9869 | 33.1764 | 32.9982 | 33.3868 | 34.576 | 34.2363 | 34.0891 | 37.2568 | 36.3042 | 33.3755 | 34.4735 | 36.3284 | 36.5431 | 37.3786 | 36.3081 | 33.1605 | 32.5445 | 34.3074 | 34.7553 | 32.8334 | 34.3648 | 34.2635 | 34.3617 | 34.3248 | 34.3729 | 34.3449 | 34.0029 | 34.329 | 36.1306 | 35.0906 | 36.5165 | 36.5356 | 33.4636 | 93.6033 | 93.7382 | 93.3643
2022-09-08 05:12 | 7:22 | 17.0959 | 17.4666 | 20.1096 | 34.4769 | 34.2728 | 34.1111 | 34.6685 | 35.5629 | 36.662 | 37.5213 | 37.0096 | 38.1827 | 34.4085 | 34.399 | 34.2914 | 35.2448 | 35.1013 | 35.436 | 36.1095 | 36.5862 | 21.1025 | 16.9528 | 93.1966 | 32.8654 | 33.0116 | 34.9981 | 33.1773 | 32.9958 | 33.3781 | 34.5913 | 34.2449 | 34.088 | 37.2466 | 36.3016 | 33.3892 | 34.4738 | 36.3077 | 36.5454 | 37.3622 | 36.3068 | 33.1526 | 32.5283 | 34.3069 | 34.7336 | 32.8203 | 34.3543 | 34.24 | 34.362 | 34.284 | 34.3434 | 34.3281 | 34.007 | 34.3248 | 36.1446 | 35.0677 | 36.5359 | 36.5211 | 33.4836 | 93.4576 | 93.6165 | 93.2571
2022-09-08 05:13 | 7:23 | 17.0493 | 17.4204 | 20.085 | 34.5439 | 34.2819 | 34.1188 | 34.6431 | 35.5556 | 36.6742 | 37.4959 | 36.9978 | 38.1984 | 34.4113 | 34.394 | 34.298 | 35.2233 | 35.0796 | 35.4109 | 36.106 | 36.5754 | 21.1212 | 17.0001 | 93.1944 | 32.9218 | 33.0193 | 35.0054 | 33.1606 | 32.9862 | 33.374 | 34.5694 | 34.231 | 34.0951 | 37.2643 | 36.2966 | 33.3741 | 34.4516 | 36.3042 | 36.5422 | 37.3823 | 36.2853 | 33.169 | 32.512 | 34.2917 | 34.7352 | 32.831 | 34.3762 | 34.2494 | 34.3398 | 34.3202 | 34.3884 | 34.3266 | 33.9938 | 34.284 | 36.1351 | 35.0856 | 36.5354 | 36.5299 | 33.4649 | 93.4154 | 93.5575 | 93.2602
2022-09-08 05:13 | 7:23 | 17.015 | 17.402 | 20.073 | 34.4633 | 34.2796 | 34.1181 | 34.6692 | 35.5525 | 36.6814 | 37.5138 | 37.0191 | 38.1712 | 34.4305 | 34.3831 | 34.2979 | 35.2215 | 35.0758 | 35.4006 | 36.0853 | 36.5658 | 21.1169 | 16.9666 | 93.2064 | 33.0419 | 33.0053 | 35.0001 | 33.1605 | 33.0059 | 33.3869 | 34.563 | 34.2332 | 34.0893 | 37.2555 | 36.3082 | 33.3898 | 34.4925 | 36.3016 | 36.5622 | 37.3625 | 36.3284 | 33.1612 | 32.5483 | 34.298 | 34.7356 | 32.8141 | 34.3655 | 34.2584 | 34.3747 | 34.3241 | 34.3738 | 34.3258 | 33.9962 | 34.3202 | 36.135 | 35.0809 | 36.5293 | 36.5246 | 33.4677 | 93.3559 | 93.4737 | 93.2133
2022-09-08 05:13 | 7:23 | 17.0229 | 17.4134 | 20.0249 | 34.4791 | 34.3035 | 34.1121 | 34.6648 | 35.5563 | 36.6575 | 37.5171 | 37.0312 | 38.1977 | 34.4197 | 34.3993 | 34.2972 | 35.2153 | 35.0993 | 35.4203 | 36.0842 | 36.5872 | 21.0979 | 16.9437 | 93.1723 | 32.9419 | 33.0232 | 34.9884 | 33.1605 | 33.0057 | 33.3755 | 34.5898 | 34.236 | 34.0943 | 37.2528 | 36.3281 | 33.3812 | 34.4558 | 36.2966 | 36.5449 | 37.363 | 36.3077 | 33.1528 | 32.527 | 34.3024 | 34.7307 | 32.8197 | 34.3598 | 34.2456 | 34.3511 | 34.324 | 34.3652 | 34.3246 | 33.9961 | 34.3241 | 36.1375 | 35.084 | 36.5307 | 36.5136 | 33.4481 | 93.3102 | 93.4294 | 93.2863
2022-09-08 05:13 | 7:23 | 17.0147 | 17.4662 | 20.0385 | 34.5324 | 34.3005 | 34.1071 | 34.6483 | 35.5493 | 36.6585 | 37.4971 | 37.0081 | 38.1955 | 34.4433 | 34.4008 | 34.3004 | 35.2239 | 35.0725 | 35.4241 | 36.0881 | 36.5663 | 21.0954 | 16.9435 | 93.1372 | 32.9124 | 32.9943 | 34.9903 | 33.1526 | 32.9948 | 33.3892 | 34.5653 | 34.2125 | 34.0892 | 37.2567 | 36.3082 | 33.38 | 34.4721 | 36.3082 | 36.5357 | 37.3815 | 36.3042 | 33.1533 | 32.5004 | 34.27 | 34.7197 | 32.8044 | 34.3743 | 34.2572 | 34.3657 | 34.3012 | 34.3593 | 34.3525 | 33.9932 | 34.324 | 36.1168 | 35.0707 | 36.5305 | 36.5298 | 33.4587 | 93.2947 | 93.4132 | 93.2483
2022-09-08 05:13 | 7:23 | 17.029 | 17.7135 | 20.0268 | 34.4124 | 34.302 | 34.1132 | 34.6656 | 35.5636 | 36.6705 | 37.5068 | 37.0259 | 38.203 | 34.4169 | 34.3951 | 34.2848 | 35.2197 | 35.0957 | 35.413 | 36.0881 | 36.5667 | 21.1019 | 16.9801 | 93.1333 | 32.8954 | 33.0051 | 34.9871 | 33.169 | 33.0119 | 33.3741 | 34.5686 | 34.2244 | 34.098 | 37.2456 | 36.3054 | 33.3771 | 34.4625 | 36.3281 | 36.5513 | 37.3525 | 36.3016 | 33.1573 | 32.5205 | 34.2806 | 34.7217 | 32.7943 | 34.3795 | 34.2534 | 34.3894 | 34.314 | 34.3494 | 34.3515 | 33.9804 | 34.3012 | 36.1318 | 35.0617 | 36.5521 | 36.5231 | 33.4577 | 93.2423 | 93.425 | 93.1696
2022-09-08 05:13 | 7:23 | 17.0227 | 17.3933 | 20.0206 | 34.5099 | 34.293 | 34.1233 | 34.6601 | 35.5575 | 36.6642 | 37.5065 | 37.0192 | 38.1923 | 34.4257 | 34.4079 | 34.2962 | 35.2247 | 35.0742 | 35.4209 | 36.0924 | 36.5642 | 21.0755 | 16.923 | 93.0967 | 32.9543 | 32.9942 | 35.0069 | 33.1612 | 32.9976 | 33.3898 | 34.5855 | 34.2427 | 34.0855 | 37.2624 | 36.2939 | 33.3699 | 34.4841 | 36.3082 | 36.5603 | 37.3773 | 36.2966 | 33.1638 | 32.501 | 34.2956 | 34.7117 | 32.8131 | 34.3848 | 34.2681 | 34.3594 | 34.2858 | 34.3707 | 34.349 | 33.9832 | 34.314 | 36.1355 | 35.0675 | 36.5287 | 36.5406 | 33.4597 | 93.1782 | 93.3605 | 93.1472
2022-09-08 05:14 | 7:23 | 16.917 | 17.3445 | 19.9575 | 34.4497 | 34.2838 | 34.1121 | 34.6724 | 35.5722 | 36.6648 | 37.5013 | 37.0273 | 38.2031 | 34.4334 | 34.3948 | 34.281 | 35.2185 | 35.0813 | 35.4381 | 36.0873 | 36.5764 | 21.0687 | 16.955 | 93.0539 | 32.9815 | 32.9985 | 35.011 | 33.1528 | 33.0021 | 33.3812 | 34.5774 | 34.2342 | 34.0899 | 37.269 | 36.3107 | 33.3587 | 34.4722 | 36.3054 | 36.5569 | 37.3632 | 36.3082 | 33.1695 | 32.5135 | 34.2648 | 34.7199 | 32.7882 | 34.3667 | 34.2498 | 34.3858 | 34.3149 | 34.3494 | 34.3519 | 33.9832 | 34.2858 | 36.1269 | 35.0815 | 36.5603 | 36.5373 | 33.453 | 93.134 | 93.3285 | 93.0552
2022-09-08 05:14 | 7:24 | 17.0058 | 17.3877 | 20.013 | 34.5015 | 34.3006 | 34.1452 | 34.6568 | 35.5663 | 36.6511 | 37.4939 | 37.0164 | 38.2045 | 34.4252 | 34.4045 | 34.3074 | 35.2159 | 35.0763 | 35.4177 | 36.0829 | 36.5733 | 21.0338 | 16.9284 | 93.0679 | 32.98 | 33.005 | 34.9932 | 33.1533 | 33.0132 | 33.38 | 34.5635 | 34.2291 | 34.094 | 37.2463 | 36.3059 | 33.3886 | 34.4854 | 36.2939 | 36.553 | 37.378 | 36.3281 | 33.1394 | 32.5127 | 34.2698 | 34.6968 | 32.7836 | 34.3972 | 34.2512 | 34.3832 | 34.2881 | 34.354 | 34.3619 | 33.9656 | 34.3149 | 36.1406 | 35.0684 | 36.5412 | 36.5502 | 33.4359 | 93.1083 | 93.2347 | 93.0724
2022-09-08 05:14 | 7:24 | 16.9397 | 17.272 | 19.975 | 34.3237 | 34.2917 | 34.1232 | 34.6549 | 35.5513 | 36.6573 | 37.5191 | 37.0316 | 38.2096 | 34.4299 | 34.3886 | 34.2951 | 35.2195 | 35.0808 | 35.4293 | 36.0739 | 36.5672 | 21.0329 | 16.9156 | 93.0399 | 33.036 | 32.9983 | 35.0077 | 33.1573 | 32.9913 | 33.3771 | 34.5912 | 34.215 | 34.0877 | 37.2732 | 36.2951 | 33.3628 | 34.4814 | 36.3107 | 36.5663 | 37.3328 | 36.3082 | 33.1475 | 32.5079 | 34.246 | 34.715 | 32.7843 | 34.376 | 34.2606 | 34.4034 | 34.2811 | 34.3477 | 34.3367 | 33.9753 | 34.2881 | 36.1347 | 35.0904 | 36.5446 | 36.5289 | 33.4371 | 93.0358 | 93.1364 | 92.9173
2022-09-08 05:14 | 7:24 | 17.024 | 17.3548 | 19.9893 | 34.4359 | 34.2787 | 34.1237 | 34.6543 | 35.5516 | 36.667 | 37.5249 | 37.0353 | 38.2022 | 34.4195 | 34.4131 | 34.286 | 35.2155 | 35.0728 | 35.4088 | 36.0788 | 36.5817 | 21.0036 | 16.9285 | 92.9193 | 32.9479 | 32.9954 | 34.9942 | 33.1638 | 32.9914 | 33.3699 | 34.5679 | 34.2308 | 34.0711 | 37.2461 | 36.2929 | 33.3628 | 34.4983 | 36.3059 | 36.5587 | 37.3661 | 36.3054 | 33.153 | 32.4971 | 34.2771 | 34.6909 | 32.7801 | 34.3885 | 34.2593 | 34.3836 | 34.2971 | 34.3478 | 34.3546 | 33.9726 | 34.2811 | 36.1447 | 35.0547 | 36.5398 | 36.5237 | 33.45 | 92.8844 | 93.0511 | 92.8544
2022-09-08 05:14 | 7:24 | 16.9856 | 17.3038 | 19.9705 | 34.4867 | 34.2874 | 34.1232 | 34.6689 | 35.5587 | 36.6644 | 37.5263 | 37.0237 | 38.2084 | 34.4276 | 34.3947 | 34.2736 | 35.2192 | 35.0693 | 35.4115 | 36.0883 | 36.5678 | 21.0051 | 16.9045 | 92.9156 | 32.9911 | 32.9893 | 35.0014 | 33.1695 | 33.0116 | 33.3587 | 34.5692 | 34.2383 | 34.1054 | 37.2537 | 36.269 | 33.3768 | 34.4803 | 36.2951 | 36.5515 | 37.353 | 36.2939 | 33.142 | 32.492 | 34.2792 | 34.6805 | 32.7571 | 34.3854 | 34.2701 | 34.392 | 34.2868 | 34.3526 | 34.3545 | 33.9553 | 34.2971 | 36.1344 | 35.0642 | 36.5372 | 36.5362 | 33.4303 | 92.8153 | 92.9932 | 92.8473
2022-09-08 05:14 | 7:24 | 16.905 | 17.2564 | 19.9588 | 34.3765 | 34.2823 | 34.125 | 34.6563 | 35.5539 | 36.67 | 37.5076 | 37.0142 | 38.2112 | 34.4221 | 34.4081 | 34.283 | 35.2313 | 35.0722 | 35.4197 | 36.074 | 36.563 | 20.986 | 16.8966 | 92.8421 | 32.8836 | 32.9876 | 34.9881 | 33.1394 | 32.9914 | 33.3886 | 34.5722 | 34.2374 | 34.088 | 37.2587 | 36.2891 | 33.3942 | 34.4858 | 36.2929 | 36.5638 | 37.3518 | 36.3107 | 33.1249 | 32.4966 | 34.2582 | 34.702 | 32.7505 | 34.3899 | 34.2762 | 34.3863 | 34.2945 | 34.3511 | 34.3722 | 33.9794 | 34.2868 | 36.1433 | 35.0775 | 36.5339 | 36.546 | 33.4534 | 92.7524 | 92.9086 | 92.7776
2022-09-08 05:15 | 7:25 | 16.8715 | 17.2321 | 19.8961 | 34.3385 | 34.3038 | 34.1202 | 34.6683 | 35.5657 | 36.6545 | 37.5322 | 37.0187 | 38.2099 | 34.4092 | 34.3986 | 34.2692 | 35.2298 | 35.0652 | 35.4225 | 36.0805 | 36.5608 | 20.9779 | 16.8397 | 92.7472 | 32.8686 | 32.9773 | 34.9852 | 33.1475 | 33.0099 | 33.3628 | 34.5667 | 34.2394 | 34.09 | 37.2735 | 36.2894 | 33.3647 | 34.4619 | 36.269 | 36.5477 | 37.3482 | 36.3059 | 33.1386 | 32.4876 | 34.2627 | 34.6877 | 32.7416 | 34.4002 | 34.2689 | 34.3792 | 34.2866 | 34.3259 | 34.3564 | 33.9653 | 34.2945 | 36.1408 | 35.0667 | 36.5367 | 36.5455 | 33.4627 | 92.6532 | 92.8124 | 92.6787
2022-09-08 05:15 | 7:25 | 16.9957 | 17.204 | 19.9163 | 34.4178 | 34.3108 | 34.123 | 34.6534 | 35.5475 | 36.6665 | 37.5166 | 37.0457 | 38.2061 | 34.4068 | 34.4095 | 34.2794 | 35.2287 | 35.0705 | 35.4166 | 36.0727 | 36.5756 | 20.923 | 16.8098 | 92.6373 | 32.9316 | 32.9897 | 34.9803 | 33.153 | 33.0075 | 33.3628 | 34.5827 | 34.2368 | 34.095 | 37.2728 | 36.2914 | 33.3832 | 34.4767 | 36.2891 | 36.5515 | 37.3554 | 36.2951 | 33.1385 | 32.4821 | 34.2445 | 34.7082 | 32.7438 | 34.398 | 34.2475 | 34.3816 | 34.2951 | 34.3255 | 34.3626 | 33.9678 | 34.2866 | 36.1436 | 35.0821 | 36.5495 | 36.5271 | 33.4521 | 92.5264 | 92.7216 | 92.5732
2022-09-08 05:15 | 7:25 | 17.0031 | 17.2478 | 19.8824 | 34.2788 | 34.307 | 34.1095 | 34.6717 | 35.5809 | 36.6624 | 37.5106 | 37.04 | 38.2135 | 34.42 | 34.397 | 34.2629 | 35.2288 | 35.0555 | 35.4182 | 36.0705 | 36.5786 | 20.9457 | 16.7723 | 92.6615 | 32.9574 | 32.9782 | 34.9685 | 33.142 | 32.9926 | 33.3768 | 34.5726 | 34.2364 | 34.1008 | 37.2492 | 36.2791 | 33.3767 | 34.4539 | 36.2894 | 36.5574 | 37.3565 | 36.2929 | 33.1365 | 32.5057 | 34.2507 | 34.7046 | 32.7598 | 34.3715 | 34.249 | 34.4022 | 34.288 | 34.3294 | 34.3826 | 33.9652 | 34.2951 | 36.14 | 35.0744 | 36.5337 | 36.513 | 33.4214 | 92.5188 | 92.6047 | 92.6409
2022-09-08 05:15 | 7:25 | 16.9419 | 17.2414 | 19.8759 | 34.4242 | 34.3032 | 34.1272 | 34.6725 | 35.5665 | 36.6571 | 37.5277 | 37.0113 | 38.2092 | 34.4177 | 34.4005 | 34.2745 | 35.2223 | 35.0575 | 35.4113 | 36.0627 | 36.5785 | 20.9315 | 16.8072 | 92.6634 | 32.8828 | 32.9789 | 34.9655 | 33.1249 | 32.9952 | 33.3942 | 34.5693 | 34.2467 | 34.0979 | 37.2495 | 36.2608 | 33.3716 | 34.4905 | 36.2914 | 36.564 | 37.3714 | 36.269 | 33.1362 | 32.4975 | 34.255 | 34.6904 | 32.7398 | 34.3947 | 34.2628 | 34.418 | 34.2805 | 34.3144 | 34.3874 | 33.9662 | 34.288 | 36.1535 | 35.0615 | 36.5432 | 36.5437 | 33.4555 | 92.4269 | 92.5136 | 92.5882
2022-09-08 05:15 | 7:25 | 16.8568 | 17.1718 | 19.8316 | 34.3546 | 34.2988 | 34.1087 | 34.6593 | 35.5705 | 36.6646 | 37.5085 | 37.0099 | 38.2196 | 34.4024 | 34.4 | 34.2542 | 35.2346 | 35.0463 | 35.406 | 36.0728 | 36.5705 | 20.9107 | 16.7681 | 92.515 | 32.9612 | 32.9799 | 34.9629 | 33.1386 | 33.0008 | 33.3647 | 34.5896 | 34.2385 | 34.0843 | 37.2418 | 36.29 | 33.3869 | 34.4844 | 36.2791 | 36.5675 | 37.3518 | 36.2891 | 33.1394 | 32.4815 | 34.2419 | 34.6874 | 32.7329 | 34.4099 | 34.2939 | 34.3974 | 34.2697 | 34.3282 | 34.3695 | 33.9487 | 34.2805 | 36.1379 | 35.0667 | 36.5346 | 36.5328 | 33.4616 | 92.2903 | 92.4324 | 92.5409
2022-09-08 05:15 | 7:25 | 16.8306 | 17.1577 | 19.8308 | 34.3132 | 34.2945 | 34.123 | 34.6731 | 35.5673 | 36.6597 | 37.5208 | 37.0272 | 38.2056 | 34.4244 | 34.4074 | 34.283 | 35.2314 | 35.0601 | 35.4112 | 36.0865 | 36.5518 | 20.9167 | 16.7351 | 92.3923 | 32.8586 | 32.9822 | 34.9742 | 33.1385 | 33.0053 | 33.3832 | 34.6001 | 34.2514 | 34.0919 | 37.2582 | 36.2668 | 33.3698 | 34.4741 | 36.2608 | 36.5628 | 37.3747 | 36.2894 | 33.1118 | 32.4682 | 34.2389 | 34.6768 | 32.7259 | 34.3943 | 34.2703 | 34.3967 | 34.2489 | 34.3192 | 34.3708 | 33.9741 | 34.2697 | 36.1282 | 35.0687 | 36.5338 | 36.5182 | 33.4365 | 92.1811 | 92.344 | 92.331
2022-09-08 05:16 | 7:26 | 16.8039 | 17.1108 | 19.8099 | 34.2646 | 34.3044 | 34.1253 | 34.6519 | 35.5567 | 36.6674 | 37.5204 | 37.0229 | 38.2132 | 34.4303 | 34.3894 | 34.2721 | 35.2251 | 35.0629 | 35.4135 | 36.0722 | 36.561 | 20.9277 | 16.7599 | 92.3251 | 32.704 | 32.9729 | 34.9669 | 33.1365 | 33.016 | 33.3767 | 34.5757 | 34.2287 | 34.0859 | 37.2427 | 36.2937 | 33.3668 | 34.4696 | 36.29 | 36.5634 | 37.3798 | 36.2914 | 33.1169 | 32.4865 | 34.2368 | 34.6527 | 32.7345 | 34.3855 | 34.286 | 34.3908 | 34.2805 | 34.3273 | 34.3836 | 33.9561 | 34.2489 | 36.1144 | 35.0488 | 36.5379 | 36.5215 | 33.4556 | 92.0617 | 92.2082 | 92.2705
2022-09-08 05:16 | 7:26 | 16.8748 | 17.1642 | 19.8035 | 34.3573 | 34.3057 | 34.129 | 34.6519 | 35.5699 | 36.6624 | 37.5302 | 37.0373 | 38.2055 | 34.3986 | 34.4099 | 34.2638 | 35.2236 | 35.056 | 35.4101 | 36.0787 | 36.5872 | 20.8946 | 16.7186 | 92.2946 | 32.8959 | 32.9937 | 34.9641 | 33.1362 | 33.0179 | 33.3716 | 34.5789 | 34.2281 | 34.0721 | 37.2583 | 36.2771 | 33.382 | 34.4813 | 36.2668 | 36.5726 | 37.3476 | 36.2791 | 33.1401 | 32.4663 | 34.2249 | 34.678 | 32.7135 | 34.3752 | 34.2558 | 34.4089 | 34.2768 | 34.3116 | 34.388 | 33.9537 | 34.2805 | 36.1543 | 35.0542 | 36.5433 | 36.5147 | 33.453 | 92.0199 | 92.1569 | 92.2441
2022-09-08 05:16 | 7:26 | 16.8051 | 17.1198 | 19.7623 | 34.4168 | 34.2996 | 34.1278 | 34.6511 | 35.5777 | 36.6471 | 37.5351 | 37.0391 | 38.2328 | 34.4138 | 34.4082 | 34.2733 | 35.2457 | 35.0437 | 35.4249 | 36.0798 | 36.5777 | 20.8965 | 16.7458 | 92.3022 | 32.8212 | 32.9793 | 34.9565 | 33.1394 | 33.0063 | 33.3869 | 34.5795 | 34.2283 | 34.0901 | 37.2732 | 36.2831 | 33.3684 | 34.465 | 36.2937 | 36.5633 | 37.358 | 36.2608 | 33.117 | 32.481 | 34.2372 | 34.6646 | 32.7143 | 34.391 | 34.2534 | 34.4226 | 34.2759 | 34.3166 | 34.3819 | 33.9603 | 34.2768 | 36.1448 | 35.0657 | 36.5502 | 36.5382 | 33.4486 | 92.0377 | 92.1314 | 92.312
2022-09-08 05:16 | 7:26 | 16.7805 | 17.0992 | 19.7875 | 34.3648 | 34.305 | 34.1247 | 34.6531 | 35.5677 | 36.6562 | 37.5349 | 37.0461 | 38.2159 | 34.4144 | 34.4044 | 34.2644 | 35.2254 | 35.045 | 35.4067 | 36.1011 | 36.5774 | 20.8826 | 16.6785 | 92.3539 | 32.8397 | 32.9983 | 34.9501 | 33.1118 | 33.0153 | 33.3698 | 34.5854 | 34.2448 | 34.0907 | 37.2371 | 36.2784 | 33.377 | 34.487 | 36.2771 | 36.5553 | 37.3493 | 36.29 | 33.124 | 32.46 | 34.2407 | 34.6681 | 32.7045 | 34.3965 | 34.2879 | 34.4184 | 34.2773 | 34.3075 | 34.39 | 33.946 | 34.2759 | 36.1364 | 35.0579 | 36.5408 | 36.5364 | 33.4421 | 92.0802 | 92.2248 | 92.3485
2022-09-08 05:16 | 7:26 | 16.8001 | 17.1215 | 19.7793 | 34.2593 | 34.3183 | 34.1171 | 34.6623 | 35.5854 | 36.663 | 37.5388 | 37.0268 | 38.22 | 34.3916 | 34.394 | 34.2709 | 35.2006 | 35.0622 | 35.4253 | 36.0803 | 36.583 | 20.8728 | 16.727 | 92.5197 | 32.7432 | 32.9726 | 34.981 | 33.1169 | 32.9886 | 33.3668 | 34.5705 | 34.2345 | 34.1029 | 37.2267 | 36.2631 | 33.3664 | 34.4621 | 36.2831 | 36.554 | 37.3564 | 36.2668 | 33.1188 | 32.4526 | 34.2332 | 34.6639 | 32.6936 | 34.4021 | 34.2669 | 34.4196 | 34.2559 | 34.3067 | 34.3815 | 33.9491 | 34.2773 | 36.144 | 35.0403 | 36.5292 | 36.5326 | 33.4223 | 92.2993 | 92.3985 | 92.5797
2022-09-08 05:16 | 7:26 | 16.7748 | 17.075 | 19.7907 | 34.3327 | 34.3151 | 34.1133 | 34.6654 | 35.5685 | 36.6748 | 37.5487 | 37.0366 | 38.2264 | 34.3969 | 34.3912 | 34.2669 | 35.2139 | 35.0435 | 35.4105 | 36.0783 | 36.5693 | 20.8474 | 16.7014 | 92.6103 | 32.7464 | 32.973 | 34.9579 | 33.1401 | 33.0077 | 33.382 | 34.5761 | 34.2466 | 34.0778 | 37.2533 | 36.2484 | 33.3708 | 34.4706 | 36.2784 | 36.5475 | 37.3593 | 36.2937 | 33.1041 | 32.4531 | 34.2209 | 34.6615 | 32.6804 | 34.3889 | 34.2662 | 34.4232 | 34.2679 | 34.2951 | 34.3946 | 33.973 | 34.2559 | 36.1534 | 35.0582 | 36.5494 | 36.5345 | 33.4319 | 92.4547 | 92.601 | 92.7408
2022-09-08 05:17 | 7:26 | 16.7788 | 17.0999 | 19.7516 | 34.2305 | 34.3258 | 34.1224 | 34.6616 | 35.5882 | 36.6535 | 37.5465 | 37.0399 | 38.232 | 34.4054 | 34.4017 | 34.2752 | 35.2334 | 35.0326 | 35.4329 | 36.0933 | 36.5771 | 20.847 | 16.7026 | 92.7245 | 32.7956 | 32.9749 | 34.9624 | 33.117 | 33.0068 | 33.3684 | 34.579 | 34.2559 | 34.0808 | 37.2613 | 36.2654 | 33.3717 | 34.4648 | 36.2631 | 36.5565 | 37.3518 | 36.2771 | 33.0922 | 32.4421 | 34.2078 | 34.673 | 32.6692 | 34.378 | 34.275 | 34.4102 | 34.2634 | 34.2843 | 34.399 | 33.9742 | 34.2679 | 36.1472 | 35.0507 | 36.544 | 36.5296 | 33.4553 | 92.6937 | 92.7828 | 92.8719
2022-09-08 05:17 | 7:27 | 16.7757 | 17.1023 | 19.764 | 34.4377 | 34.3361 | 34.1027 | 34.6594 | 35.578 | 36.6684 | 37.5411 | 37.0267 | 38.216 | 34.39 | 34.4007 | 34.2667 | 35.2204 | 35.0485 | 35.4176 | 36.087 | 36.5879 | 20.8185 | 16.7459 | 92.9413 | 32.992 | 32.9656 | 34.9531 | 33.124 | 32.9923 | 33.377 | 34.5843 | 34.22 | 34.0748 | 37.2481 | 36.249 | 33.3697 | 34.4792 | 36.2484 | 36.5404 | 37.3466 | 36.2831 | 33.1052 | 32.4303 | 34.2174 | 34.6479 | 32.6701 | 34.3996 | 34.2634 | 34.4409 | 34.2433 | 34.2711 | 34.394 | 33.9558 | 34.2634 | 36.1613 | 35.0564 | 36.5371 | 36.5362 | 33.4508 | 92.85 | 92.9928 | 92.9334
2022-09-08 05:17 | 7:27 | 16.7881 | 17.0847 | 19.755 | 34.3945 | 34.3346 | 34.1166 | 34.6543 | 35.5755 | 36.6819 | 37.5327 | 37.0323 | 38.2158 | 34.3894 | 34.3736 | 34.2517 | 35.2201 | 35.0416 | 35.3986 | 36.0814 | 36.5631 | 20.8267 | 16.7057 | 92.9812 | 32.7565 | 32.9659 | 34.9453 | 33.1188 | 32.9946 | 33.3664 | 34.5797 | 34.2198 | 34.0717 | 37.2313 | 36.2483 | 33.3595 | 34.4753 | 36.2654 | 36.5692 | 37.3478 | 36.2784 | 33.0987 | 32.4618 | 34.2275 | 34.6429 | 32.6775 | 34.3981 | 34.2786 | 34.4239 | 34.2467 | 34.281 | 34.3831 | 33.9509 | 34.2433 | 36.14 | 35.0586 | 36.5407 | 36.5229 | 33.4427 | 92.986 | 93.1846 | 92.9647
2022-09-08 05:17 | 7:27 | 16.6679 | 16.9683 | 19.7243 | 34.2726 | 34.3449 | 34.1305 | 34.6496 | 35.5674 | 36.669 | 37.5178 | 37.0315 | 38.1998 | 34.389 | 34.3656 | 34.252 | 35.2224 | 35.0376 | 35.4088 | 36.0701 | 36.5686 | 20.7805 | 16.6781 | 93.0639 | 32.809 | 32.9668 | 34.9361 | 33.1041 | 32.9933 | 33.3708 | 34.5706 | 34.2294 | 34.0859 | 37.2507 | 36.2549 | 33.3517 | 34.4659 | 36.249 | 36.532 | 37.3584 | 36.2631 | 33.0857 | 32.4216 | 34.2119 | 34.6443 | 32.6525 | 34.3971 | 34.2697 | 34.4106 | 34.2441 | 34.2811 | 34.3993 | 33.955 | 34.2467 | 36.1517 | 35.0517 | 36.5406 | 36.5293 | 33.4387 | 93.1493 | 93.3716 | 93.0859
2022-09-08 05:17 | 7:27 | 16.6666 | 16.8938 | 19.6914 | 34.2043 | 34.3281 | 34.1197 | 34.6449 | 35.5724 | 36.6441 | 37.5297 | 37.0188 | 38.2094 | 34.3754 | 34.4075 | 34.2557 | 35.1945 | 35.0239 | 35.4044 | 36.06 | 36.5649 | 20.7382 | 16.6461 | 93.1321 | 32.7782 | 32.9598 | 34.9404 | 33.0922 | 32.9872 | 33.3717 | 34.5806 | 34.2351 | 34.0646 | 37.2362 | 36.2483 | 33.3658 | 34.4664 | 36.2483 | 36.5429 | 37.3481 | 36.2484 | 33.1024 | 32.4334 | 34.2086 | 34.6457 | 32.6496 | 34.3947 | 34.2917 | 34.4389 | 34.2525 | 34.2883 | 34.4008 | 33.9312 | 34.2441 | 36.1194 | 35.0585 | 36.5282 | 36.5361 | 33.4345 | 93.2707 | 93.5577 | 93.1535
2022-09-08 05:17 | 7:27 | 16.6834 | 16.9422 | 19.6586 | 34.2835 | 34.3266 | 34.1107 | 34.642 | 35.5643 | 36.6571 | 37.5471 | 37.0065 | 38.1985 | 34.4017 | 34.3735 | 34.2589 | 35.218 | 35.021 | 35.4168 | 36.077 | 36.5512 | 20.6967 | 16.6652 | 93.2263 | 32.874 | 32.9589 | 34.9431 | 33.1052 | 33.0033 | 33.3697 | 34.5756 | 34.2213 | 34.0595 | 37.236 | 36.2508 | 33.3727 | 34.4638 | 36.2549 | 36.5688 | 37.3588 | 36.2654 | 33.108 | 32.4081 | 34.1775 | 34.6318 | 32.6411 | 34.3805 | 34.2805 | 34.4553 | 34.2545 | 34.2546 | 34.3951 | 33.9424 | 34.2525 | 36.1382 | 35.0376 | 36.5469 | 36.5256 | 33.4134 | 93.4786 | 93.7718 | 93.3584
2022-09-08 05:18 | 7:28 | 16.6215 | 16.9058 | 19.6293 | 34.3563 | 34.3258 | 34.1159 | 34.6477 | 35.5727 | 36.6492 | 37.5367 | 37.01 | 38.1984 | 34.391 | 34.3871 | 34.2512 | 35.2108 | 35.0228 | 35.4112 | 36.0639 | 36.5775 | 20.6437 | 16.5925 | 93.3258 | 32.7646 | 32.9554 | 34.9166 | 33.0987 | 32.9845 | 33.3595 | 34.5813 | 34.2203 | 34.0669 | 37.2433 | 36.2488 | 33.3445 | 34.4497 | 36.2483 | 36.5627 | 37.3437 | 36.249 | 33.0903 | 32.4248 | 34.1996 | 34.621 | 32.6216 | 34.374 | 34.2874 | 34.423 | 34.2448 | 34.2671 | 34.4079 | 33.9437 | 34.2545 | 36.121 | 35.0409 | 36.561 | 36.518 | 33.4213 | 93.664 | 94.0031 | 93.4822
2022-09-08 05:18 | 7:28 | 16.6384 | 16.9397 | 19.6398 | 34.298 | 34.3246 | 34.111 | 34.623 | 35.5591 | 36.6601 | 37.5464 | 37.0182 | 38.2211 | 34.3897 | 34.379 | 34.2519 | 35.2068 | 35.0085 | 35.3988 | 36.0669 | 36.5458 | 20.6362 | 16.6258 | 93.5117 | 32.9229 | 32.9498 | 34.9169 | 33.0857 | 32.9656 | 33.3517 | 34.5731 | 34.231 | 34.0613 | 37.242 | 36.2566 | 33.3521 | 34.4466 | 36.2508 | 36.5486 | 37.3549 | 36.2483 | 33.071 | 32.4113 | 34.1815 | 34.6253 | 32.6214 | 34.3944 | 34.2894 | 34.4346 | 34.2525 | 34.2517 | 34.3948 | 33.9462 | 34.2448 | 36.1414 | 35.0426 | 36.5416 | 36.5277 | 33.415 | 93.8352 | 94.2082 | 93.6544
2022-09-08 05:18 | 7:28 | 16.6604 | 16.9194 | 19.5879 | 34.2939 | 34.3525 | 34.0962 | 34.6341 | 35.5707 | 36.6623 | 37.5187 | 37.0207 | 38.2033 | 34.4178 | 34.3906 | 34.2422 | 35.1985 | 35.0165 | 35.4138 | 36.0577 | 36.5457 | 20.6186 | 16.5912 | 93.7033 | 32.8024 | 32.9671 | 34.9156 | 33.1024 | 32.9845 | 33.3658 | 34.5678 | 34.2198 | 34.0584 | 37.211 | 36.2326 | 33.3666 | 34.4499 | 36.2488 | 36.5414 | 37.3489 | 36.2549 | 33.0668 | 32.4033 | 34.1899 | 34.6183 | 32.6136 | 34.3735 | 34.2747 | 34.4469 | 34.2548 | 34.24 | 34.4045 | 33.9248 | 34.2525 | 36.1533 | 35.0304 | 36.5487 | 36.5197 | 33.4055 | 94.0786 | 94.4429 | 93.8409
2022-09-08 05:18 | 7:28 | 16.6261 | 16.9277 | 19.5897 | 34.2197 | 34.3515 | 34.0981 | 34.6305 | 35.5561 | 36.6409 | 37.53 | 36.9978 | 38.1941 | 34.3883 | 34.3708 | 34.2527 | 35.1893 | 35.0123 | 35.3977 | 36.06 | 36.5447 | 20.599 | 16.602 | 93.8136 | 32.9077 | 32.9475 | 34.9212 | 33.108 | 32.9598 | 33.3727 | 34.5697 | 34.2141 | 34.0468 | 37.2283 | 36.2372 | 33.3363 | 34.4553 | 36.2566 | 36.5519 | 37.3542 | 36.2483 | 33.0806 | 32.4163 | 34.1724 | 34.6041 | 32.6153 | 34.3824 | 34.2704 | 34.4279 | 34.2212 | 34.2794 | 34.3886 | 33.9305 | 34.2548 | 36.1302 | 35.0287 | 36.5525 | 36.5285 | 33.419 | 94.2006 | 94.6295 | 93.8496
2022-09-08 05:18 | 7:28 | 16.618 | 16.9173 | 19.6216 | 34.2831 | 34.349 | 34.098 | 34.6409 | 35.5658 | 36.6439 | 37.5344 | 37.0136 | 38.2024 | 34.3888 | 34.3874 | 34.254 | 35.1938 | 34.9938 | 35.4117 | 36.064 | 36.5609 | 20.6035 | 16.6162 | 93.9514 | 32.8033 | 32.9557 | 34.9206 | 33.0903 | 32.9616 | 33.3445 | 34.5765 | 34.1886 | 34.0607 | 37.22 | 36.2328 | 33.349 | 34.431 | 36.2326 | 36.5338 | 37.339 | 36.2508 | 33.0658 | 32.3937 | 34.1636 | 34.5904 | 32.6034 | 34.3984 | 34.2749 | 34.4279 | 34.2496 | 34.2745 | 34.4131 | 33.9409 | 34.2212 | 36.1465 | 35.0213 | 36.5508 | 36.5361 | 33.4106 | 94.39 | 94.8396 | 94.0568
2022-09-08 05:18 | 7:28 | 16.6314 | 16.9526 | 19.6287 | 34.2518 | 34.3519 | 34.0874 | 34.6327 | 35.558 | 36.6449 | 37.5184 | 37.0139 | 38.1956 | 34.3921 | 34.3736 | 34.2285 | 35.1831 | 35.0012 | 35.3898 | 36.0529 | 36.5583 | 20.5888 | 16.5979 | 94.0168 | 32.8643 | 32.9284 | 34.9453 | 33.071 | 32.9672 | 33.3521 | 34.5665 | 34.2034 | 34.0492 | 37.24 | 36.2492 | 33.3453 | 34.4406 | 36.2372 | 36.5441 | 37.3377 | 36.2488 | 33.0723 | 32.3702 | 34.1629 | 34.6028 | 32.6031 | 34.3694 | 34.2869 | 34.4199 | 34.248 | 34.2607 | 34.3947 | 33.9323 | 34.2496 | 36.1302 | 35.0346 | 36.5368 | 36.5163 | 33.4065 | 94.6024 | 95.0834 | 94.1744
2022-09-08 05:19 | 7:28 | 16.6155 | 16.912 | 19.5883 | 34.2449 | 34.3619 | 34.0993 | 34.6242 | 35.5534 | 36.6439 | 37.5322 | 37.021 | 38.2 | 34.3827 | 34.3689 | 34.2217 | 35.1935 | 35.0045 | 35.3946 | 36.0434 | 36.5437 | 20.5527 | 16.595 | 94.1448 | 32.7028 | 32.9273 | 34.9226 | 33.0668 | 32.9746 | 33.3666 | 34.5739 | 34.2133 | 34.0327 | 37.2162 | 36.2281 | 33.3534 | 34.4374 | 36.2328 | 36.5377 | 37.3216 | 36.2566 | 33.0426 | 32.3823 | 34.1638 | 34.5837 | 32.5875 | 34.3869 | 34.2694 | 34.4316 | 34.2409 | 34.2476 | 34.4081 | 33.9303 | 34.248 | 36.1237 | 35.0132 | 36.5278 | 36.5153 | 33.3961 | 94.8309 | 95.2497 | 94.3758
2022-09-08 05:19 | 7:29 | 16.6433 | 16.9182 | 19.6038 | 34.1533 | 34.3367 | 34.0945 | 34.6151 | 35.5442 | 36.6338 | 37.5278 | 36.9933 | 38.1943 | 34.3639 | 34.381 | 34.2315 | 35.194 | 34.9887 | 35.3942 | 36.0468 | 36.5651 | 20.5556 | 16.5654 | 94.2635 | 32.7347 | 32.9419 | 34.8967 | 33.0806 | 32.9557 | 33.3363 | 34.565 | 34.2044 | 34.0446 | 37.2012 | 36.2219 | 33.3465 | 34.4465 | 36.2492 | 36.5519 | 37.3311 | 36.2326 | 33.047 | 32.359 | 34.1564 | 34.5788 | 32.5858 | 34.3765 | 34.2996 | 34.4469 | 34.2316 | 34.2379 | 34.3986 | 33.941 | 34.2409 | 36.1267 | 35.0174 | 36.5244 | 36.5082 | 33.3831 | 94.9789 | 95.3726 | 94.4821
2022-09-08 05:19 | 7:29 | 16.6061 | 16.8988 | 19.5811 | 34.1752 | 34.3546 | 34.0924 | 34.6305 | 35.5613 | 36.6351 | 37.5282 | 36.9952 | 38.1833 | 34.3606 | 34.3957 | 34.2325 | 35.1942 | 34.9835 | 35.3871 | 36.057 | 36.5235 | 20.532 | 16.5703 | 94.3358 | 32.8158 | 32.9273 | 34.9005 | 33.0658 | 32.9634 | 33.349 | 34.565 | 34.1979 | 34.0463 | 37.2195 | 36.2331 | 33.3386 | 34.4201 | 36.2281 | 36.5246 | 37.3253 | 36.2372 | 33.0655 | 32.384 | 34.1262 | 34.5805 | 32.5964 | 34.3905 | 34.2873 | 34.4431 | 34.232 | 34.2642 | 34.4095 | 33.9202 | 34.2316 | 36.1115 | 35.0409 | 36.5361 | 36.5281 | 33.3897 | 95.1759 | 95.5464 | 94.5387
2022-09-08 05:19 | 7:29 | 16.6683 | 16.932 | 19.5949 | 34.2214 | 34.3545 | 34.0916 | 34.6328 | 35.5482 | 36.6396 | 37.5388 | 37.0106 | 38.1836 | 34.3735 | 34.3959 | 34.2258 | 35.1799 | 34.9914 | 35.3929 | 36.0441 | 36.5466 | 20.537 | 16.6506 | 94.3803 | 32.6677 | 32.9244 | 34.8918 | 33.0723 | 32.9567 | 33.3453 | 34.5749 | 34.2025 | 34.0339 | 37.2265 | 36.216 | 33.3123 | 34.4194 | 36.2219 | 36.5184 | 37.3356 | 36.2328 | 33.0504 | 32.3686 | 34.1363 | 34.5515 | 32.5812 | 34.3809 | 34.2894 | 34.4472 | 34.2174 | 34.257 | 34.397 | 33.919 | 34.232 | 36.1264 | 35.0299 | 36.5483 | 36.509 | 33.3755 | 95.1956 | 95.6531 | 94.5715
2022-09-08 05:19 | 7:29 | 16.665 | 16.9409 | 19.5822 | 34.1332 | 34.3722 | 34.0952 | 34.643 | 35.545 | 36.6249 | 37.5279 | 36.99 | 38.184 | 34.3815 | 34.3954 | 34.2315 | 35.1741 | 34.9802 | 35.3922 | 36.0588 | 36.527 | 20.5395 | 16.598 | 94.5392 | 32.6801 | 32.9268 | 34.9135 | 33.0426 | 32.9564 | 33.3534 | 34.5715 | 34.2131 | 34.047 | 37.2069 | 36.212 | 33.3208 | 34.4327 | 36.2331 | 36.5175 | 37.3358 | 36.2492 | 33.0638 | 32.3736 | 34.1392 | 34.5632 | 32.5679 | 34.3786 | 34.3071 | 34.4273 | 34.225 | 34.261 | 34.4005 | 33.9177 | 34.2174 | 36.1239 | 35.0202 | 36.5363 | 36.5121 | 33.3724 | 95.3323 | 95.7022 | 94.6141
2022-09-08 05:19 | 7:29 | 16.6069 | 16.9084 | 19.5902 | 34.0881 | 34.3564 | 34.0652 | 34.6273 | 35.5491 | 36.6239 | 37.5207 | 37.0189 | 38.1932 | 34.3729 | 34.3689 | 34.2178 | 35.187 | 34.9688 | 35.3816 | 36.0503 | 36.5326 | 20.5534 | 16.608 | 94.5236 | 32.6621 | 32.9268 | 34.8972 | 33.047 | 32.9804 | 33.3465 | 34.5718 | 34.2107 | 34.0446 | 37.2144 | 36.2155 | 33.3413 | 34.4268 | 36.216 | 36.5219 | 37.3227 | 36.2281 | 33.0567 | 32.359 | 34.1264 | 34.5411 | 32.5688 | 34.3724 | 34.2902 | 34.4391 | 34.2447 | 34.2401 | 34.4 | 33.9117 | 34.225 | 36.1095 | 35.0366 | 36.5278 | 36.5145 | 33.3735 | 95.3976 | 95.7848 | 94.6974
2022-09-08 05:20 | 7:30 | 16.6826 | 16.9248 | 19.5688 | 34.0957 | 34.3626 | 34.0719 | 34.6259 | 35.5472 | 36.6215 | 37.5269 | 37.0038 | 38.1969 | 34.3434 | 34.3935 | 34.204 | 35.1753 | 34.9734 | 35.3822 | 36.0464 | 36.5346 | 20.5526 | 16.6462 | 94.6316 | 32.7138 | 32.9161 | 34.8928 | 33.0655 | 32.9649 | 33.3386 | 34.5691 | 34.193 | 34.0286 | 37.2166 | 36.2052 | 33.315 | 34.4316 | 36.212 | 36.5344 | 37.3165 | 36.2219 | 33.0768 | 32.3353 | 34.1118 | 34.544 | 32.5629 | 34.3617 | 34.3048 | 34.4219 | 34.2409 | 34.2519 | 34.4074 | 33.9148 | 34.2447 | 36.1006 | 35.0296 | 36.5213 | 36.4937 | 33.3559 | 95.4128 | 95.7444 | 94.7051
2022-09-08 05:20 | 7:30 | 16.5711 | 16.8975 | 19.5242 | 34.0573 | 34.3826 | 34.0645 | 34.6307 | 35.5416 | 36.6309 | 37.5233 | 36.9988 | 38.1862 | 34.3884 | 34.3711 | 34.217 | 35.1764 | 34.9487 | 35.3758 | 36.0466 | 36.5338 | 20.5524 | 16.548 | 94.4712 | 32.6842 | 32.8962 | 34.9011 | 33.0504 | 32.978 | 33.3123 | 34.5665 | 34.2064 | 34.0395 | 37.2054 | 36.212 | 33.3271 | 34.4239 | 36.2155 | 36.5356 | 37.3269 | 36.2331 | 33.0648 | 32.3527 | 34.0972 | 34.552 | 32.5726 | 34.3917 | 34.3002 | 34.4269 | 34.2475 | 34.2418 | 34.3894 | 33.9032 | 34.2409 | 36.1001 | 35.0099 | 36.5492 | 36.5172 | 33.3507 | 95.2702 | 95.6145 | 94.4962
2022-09-08 05:20 | 7:30 | 16.5677 | 16.8523 | 19.5367 | 34.1713 | 34.3874 | 34.0629 | 34.6189 | 35.5335 | 36.6305 | 37.5256 | 36.9915 | 38.1829 | 34.3738 | 34.3761 | 34.2131 | 35.1703 | 34.9455 | 35.3814 | 36.0327 | 36.5149 | 20.551 | 16.5325 | 94.2947 | 32.5867 | 32.9058 | 34.9018 | 33.0638 | 32.9698 | 33.3208 | 34.5558 | 34.1914 | 34.0341 | 37.2148 | 36.2003 | 33.3276 | 34.4378 | 36.2052 | 36.5163 | 37.3219 | 36.216 | 33.0477 | 32.3663 | 34.1223 | 34.5341 | 32.5487 | 34.3685 | 34.2874 | 34.4476 | 34.2458 | 34.2244 | 34.4099 | 33.8947 | 34.2475 | 36.1014 | 35.0158 | 36.5155 | 36.4858 | 33.3681 | 95.0379 | 95.4014 | 94.3183
2022-09-08 05:20 | 7:30 | 16.5291 | 16.8378 | 19.535 | 34.1564 | 34.3695 | 34.0773 | 34.6095 | 35.5487 | 36.6194 | 37.5274 | 36.9847 | 38.1727 | 34.3652 | 34.3829 | 34.2031 | 35.159 | 34.9721 | 35.3825 | 36.032 | 36.5198 | 20.5409 | 16.5092 | 94.2974 | 32.5596 | 32.8994 | 34.8895 | 33.0567 | 32.955 | 33.3413 | 34.5442 | 34.1855 | 34.0351 | 37.1969 | 36.2107 | 33.3272 | 34.4198 | 36.212 | 36.5122 | 37.3092 | 36.212 | 33.0626 | 32.3166 | 34.1039 | 34.5142 | 32.5523 | 34.3758 | 34.3012 | 34.449 | 34.2386 | 34.231 | 34.4082 | 33.8866 | 34.2458 | 36.1057 | 35.016 | 36.5422 | 36.5276 | 33.3506 | 94.782 | 95.1235 | 94.2378
2022-09-08 05:20 | 7:30 | 16.6032 | 16.896 | 19.5242 | 34.0513 | 34.3708 | 34.0915 | 34.6103 | 35.5458 | 36.614 | 37.5105 | 36.9831 | 38.178 | 34.3593 | 34.3669 | 34.1719 | 35.1773 | 34.9481 | 35.3815 | 36.0188 | 36.5067 | 20.5494 | 16.5276 | 94.0513 | 32.7057 | 32.9106 | 34.9067 | 33.0768 | 32.9742 | 33.315 | 34.5507 | 34.1988 | 34.0303 | 37.1941 | 36.2123 | 33.3132 | 34.4347 | 36.2003 | 36.5187 | 37.292 | 36.2155 | 33.0582 | 32.3425 | 34.0925 | 34.5201 | 32.5366 | 34.3758 | 34.3003 | 34.4414 | 34.2449 | 34.2241 | 34.4044 | 33.9059 | 34.2386 | 36.0943 | 35.0113 | 36.5384 | 36.4785 | 33.3351 | 94.5462 | 94.8757 | 94.0243
2022-09-08 05:20 | 7:30 | 16.6562 | 16.9221 | 19.5365 | 34.069 | 34.3836 | 34.0779 | 34.6228 | 35.5423 | 36.6313 | 37.5291 | 37.0014 | 38.1825 | 34.3494 | 34.3615 | 34.2046 | 35.1524 | 34.933 | 35.3845 | 36.0087 | 36.5395 | 20.551 | 16.5421 | 93.9015 | 32.5806 | 32.8954 | 34.8918 | 33.0648 | 32.9623 | 33.3271 | 34.5615 | 34.2155 | 34.0187 | 37.2019 | 36.2054 | 33.3253 | 34.4101 | 36.2107 | 36.5198 | 37.2919 | 36.2052 | 33.0508 | 32.3284 | 34.0806 | 34.5027 | 32.5587 | 34.3582 | 34.2999 | 34.4258 | 34.2635 | 34.2276 | 34.394 | 33.8858 | 34.2449 | 36.0869 | 35.0091 | 36.5278 | 36.4922 | 33.3253 | 94.3359 | 94.6945 | 93.8956
2022-09-08 05:21 | 7:30 | 16.6104 | 16.8846 | 19.5044 | 34.1366 | 34.388 | 34.0956 | 34.619 | 35.5473 | 36.6105 | 37.5006 | 37.0095 | 38.1878 | 34.3707 | 34.3704 | 34.2026 | 35.1694 | 34.9531 | 35.3827 | 36.0137 | 36.4979 | 20.5929 | 16.511 | 93.9108 | 32.6236 | 32.8931 | 34.8833 | 33.0477 | 32.9571 | 33.3276 | 34.5622 | 34.1972 | 34.0174 | 37.203 | 36.2256 | 33.3317 | 34.4188 | 36.2123 | 36.5192 | 37.3052 | 36.212 | 33.0486 | 32.3299 | 34.0746 | 34.5046 | 32.5597 | 34.3744 | 34.2937 | 34.4204 | 34.24 | 34.2263 | 34.3912 | 33.8802 | 34.2635 | 36.0933 | 35.0193 | 36.5176 | 36.5087 | 33.3083 | 94.2023 | 94.5338 | 93.7782
2022-09-08 05:21 | 7:31 | 16.6068 | 16.895 | 19.4986 | 34.0771 | 34.3819 | 34.063 | 34.6041 | 35.5362 | 36.6058 | 37.5087 | 37.025 | 38.2067 | 34.3494 | 34.3675 | 34.2024 | 35.1703 | 34.9512 | 35.3879 | 36.0304 | 36.5102 | 20.6108 | 16.4899 | 93.7853 | 32.8219 | 32.9155 | 34.8932 | 33.0626 | 32.9441 | 33.3272 | 34.5348 | 34.1961 | 34.0131 | 37.1864 | 36.2203 | 33.3162 | 34.432 | 36.2054 | 36.5198 | 37.2907 | 36.2003 | 33.0354 | 32.3189 | 34.0733 | 34.5008 | 32.5376 | 34.3915 | 34.299 | 34.4527 | 34.2494 | 34.233 | 34.4017 | 33.8879 | 34.24 | 36.0823 | 35.0152 | 36.5434 | 36.5024 | 33.3213 | 94.1544 | 94.4222 | 93.7885
2022-09-08 05:21 | 7:31 | 16.609 | 16.8715 | 19.522 | 34.1809 | 34.39 | 34.0785 | 34.6064 | 35.5384 | 36.6214 | 37.5017 | 37.0201 | 38.1791 | 34.354 | 34.3641 | 34.1759 | 35.1787 | 34.958 | 35.3599 | 36.0197 | 36.4889 | 20.6201 | 16.4932 | 93.7578 | 32.6342 | 32.8954 | 34.8909 | 33.0582 | 32.9399 | 33.3132 | 34.557 | 34.208 | 34.0296 | 37.2219 | 36.2182 | 33.3228 | 34.4293 | 36.2256 | 36.5089 | 37.2978 | 36.2107 | 33.0408 | 32.3183 | 34.0784 | 34.4988 | 32.547 | 34.355 | 34.2969 | 34.4404 | 34.2584 | 34.2272 | 34.4007 | 33.883 | 34.2494 | 36.0797 | 35.0023 | 36.536 | 36.487 | 33.316 | 94.0141 | 94.3204 | 93.7342
2022-09-08 05:21 | 7:31 | 16.5877 | 16.8939 | 19.4999 | 34.1216 | 34.3815 | 34.074 | 34.6305 | 35.5383 | 36.6105 | 37.522 | 37.0068 | 38.2003 | 34.3477 | 34.3676 | 34.1768 | 35.1702 | 34.9598 | 35.3686 | 36.0175 | 36.5023 | 20.6418 | 16.5168 | 93.6968 | 32.7086 | 32.8871 | 34.8954 | 33.0508 | 32.9487 | 33.3253 | 34.557 | 34.205 | 34.0272 | 37.2016 | 36.2125 | 33.303 | 34.392 | 36.2203 | 36.5144 | 37.2914 | 36.2123 | 33.0524 | 32.3167 | 34.0685 | 34.5016 | 32.5335 | 34.3686 | 34.3258 | 34.4387 | 34.2456 | 34.2318 | 34.3736 | 33.9019 | 34.2584 | 36.0988 | 35.0041 | 36.5415 | 36.4913 | 33.3095 | 93.9526 | 94.1419 | 93.7632
2022-09-08 05:21 | 7:31 | 16.6621 | 16.7109 | 19.4874 | 34.0042 | 34.3946 | 34.0996 | 34.6254 | 35.55 | 36.6005 | 37.5158 | 37.0124 | 38.195 | 34.3478 | 34.3522 | 34.187 | 35.1838 | 34.9237 | 35.3874 | 35.9993 | 36.4975 | 20.6629 | 16.4377 | 93.6433 | 32.8971 | 32.8809 | 34.8741 | 33.0486 | 32.9569 | 33.3317 | 34.5424 | 34.2093 | 34.0232 | 37.1985 | 36.2089 | 33.3046 | 34.4159 | 36.2182 | 36.5179 | 37.2684 | 36.2054 | 33.0411 | 32.3079 | 34.0798 | 34.4933 | 32.517 | 34.3723 | 34.3029 | 34.4295 | 34.2572 | 34.2093 | 34.3656 | 33.8703 | 34.2456 | 36.095 | 35.0111 | 36.5372 | 36.4948 | 33.3092 | 93.7801 | 93.9983 | 93.5544
2022-09-08 05:21 | 7:31 | 17.0238 | 16.3661 | 19.5243 | 34.1609 | 34.399 | 34.0847 | 34.5932 | 35.5351 | 36.6052 | 37.5214 | 37.006 | 38.1851 | 34.3526 | 34.3597 | 34.1827 | 35.1619 | 34.9528 | 35.3648 | 36.0056 | 36.4877 | 20.6327 | 16.2508 | 93.5999 | 32.6431 | 32.8992 | 34.8947 | 33.0354 | 32.9447 | 33.3162 | 34.5468 | 34.1923 | 34.0353 | 37.2021 | 36.1992 | 33.3161 | 34.4284 | 36.2125 | 36.5146 | 37.2769 | 36.2256 | 33.0525 | 32.3162 | 34.0779 | 34.4895 | 32.5122 | 34.3692 | 34.3067 | 34.4209 | 34.2534 | 34.2245 | 34.4075 | 33.8872 | 34.2572 | 36.0831 | 35.0058 | 36.5326 | 36.4975 | 33.2911 | 93.7001 | 93.9474 | 93.4996
2022-09-08 05:22 | 7:32 | 18.2854 | 15.7897 | 20.4526 | 34.0491 | 34.394 | 34.0718 | 34.6206 | 35.543 | 36.5962 | 37.5064 | 37.0132 | 38.2009 | 34.3511 | 34.3612 | 34.192 | 35.1641 | 34.9374 | 35.3676 | 36.0216 | 36.4801 | 20.2976 | 14.8903 | 93.5489 | 32.7478 | 32.8712 | 34.887 | 33.0408 | 32.951 | 33.3228 | 34.5497 | 34.2063 | 34.0365 | 37.1825 | 36.2162 | 33.3205 | 34.4237 | 36.2089 | 36.526 | 37.2837 | 36.2203 | 33.0466 | 32.3118 | 34.0707 | 34.4669 | 32.5116 | 34.3657 | 34.2895 | 34.4295 | 34.2681 | 34.2142 | 34.3735 | 33.8826 | 34.2534 | 36.0754 | 34.9829 | 36.54 | 36.4859 | 33.2868 | 93.633 | 93.8835 | 93.4931
2022-09-08 05:22 | 7:32 | 19.6163 | 16.7677 | 21.9391 | 34.2278 | 34.3831 | 34.0929 | 34.6072 | 35.5306 | 36.5912 | 37.5221 | 37.0044 | 38.2007 | 34.3259 | 34.3588 | 34.1829 | 35.1728 | 34.9428 | 35.3577 | 35.9911 | 36.4914 | 19.8518 | 15.2496 | 93.5147 | 32.4323 | 32.8698 | 34.8849 | 33.0524 | 32.957 | 33.303 | 34.5421 | 34.2099 | 34.034 | 37.189 | 36.23 | 33.3166 | 34.4237 | 36.1992 | 36.5016 | 37.2916 | 36.2182 | 33.0388 | 32.2749 | 34.0687 | 34.4913 | 32.507 | 34.3557 | 34.3012 | 34.4387 | 34.2498 | 34.2266 | 34.3871 | 33.8656 | 34.2681 | 36.0865 | 35.0133 | 36.5305 | 36.4941 | 33.279 | 93.5961 | 93.8632 | 93.4232
2022-09-08 05:22 | 7:32 | 20.8015 | 18.3463 | 23.3433 | 34.3051 | 34.3993 | 34.0827 | 34.6021 | 35.5443 | 36.5847 | 37.5121 | 37.0046 | 38.1838 | 34.3255 | 34.348 | 34.1664 | 35.167 | 34.9457 | 35.3684 | 36.0217 | 36.4765 | 20.0074 | 16.0494 | 93.428 | 32.724 | 32.8929 | 34.897 | 33.0411 | 32.939 | 33.3046 | 34.5351 | 34.1857 | 34.0354 | 37.1939 | 36.2266 | 33.3206 | 34.4144 | 36.2162 | 36.5189 | 37.2773 | 36.2125 | 33.0455 | 32.2966 | 34.0638 | 34.4964 | 32.5116 | 34.3825 | 34.3086 | 34.4251 | 34.2512 | 34.2283 | 34.379 | 33.8595 | 34.2498 | 36.1001 | 34.9914 | 36.5288 | 36.494 | 33.2837 | 93.5676 | 93.8191 | 93.4175
2022-09-08 05:22 | 7:32 | 21.8769 | 20.008 | 24.5054 | 34.3214 | 34.4008 | 34.0851 | 34.6017 | 35.5377 | 36.606 | 37.5052 | 37.0217 | 38.2044 | 34.3294 | 34.3584 | 34.1734 | 35.1766 | 34.9237 | 35.3861 | 36.0045 | 36.4717 | 20.518 | 17.2217 | 93.4533 | 32.6976 | 32.8707 | 34.8683 | 33.0525 | 32.953 | 33.3161 | 34.5486 | 34.2106 | 34.0201 | 37.1904 | 36.2037 | 33.3172 | 34.4241 | 36.23 | 36.5315 | 37.278 | 36.2089 | 33.029 | 32.3035 | 34.0624 | 34.4692 | 32.4834 | 34.3747 | 34.3017 | 34.4089 | 34.2606 | 34.2437 | 34.3906 | 33.8715 | 34.2512 | 36.0672 | 35.028 | 36.5331 | 36.4953 | 33.2951 | 93.5143 | 93.764 | 93.3982
2022-09-08 05:22 | 7:32 | 22.814 | 21.5264 | 25.4691 | 34.563 | 34.3951 | 34.0633 | 34.6257 | 35.5405 | 36.6019 | 37.493 | 37.0159 | 38.1921 | 34.3144 | 34.3529 | 34.17 | 35.1649 | 34.9204 | 35.3722 | 36.0067 | 36.4756 | 21.1876 | 18.5192 | 93.4053 | 32.8545 | 32.8525 | 34.8813 | 33.0466 | 32.9511 | 33.3205 | 34.5445 | 34.2092 | 34.0257 | 37.1915 | 36.2214 | 33.3242 | 34.4317 | 36.2266 | 36.5107 | 37.2803 | 36.1992 | 33.0397 | 32.2843 | 34.0442 | 34.4667 | 32.5053 | 34.3441 | 34.2989 | 34.423 | 34.2593 | 34.2337 | 34.3708 | 33.8768 | 34.2606 | 36.0962 | 35.0052 | 36.5275 | 36.4883 | 33.2958 | 93.4599 | 93.6703 | 93.2676
2022-09-08 05:22 | 7:32 | 23.6524 | 22.9199 | 26.309 | 34.479 | 34.4079 | 34.0856 | 34.6145 | 35.5544 | 36.6038 | 37.5135 | 37.0054 | 38.1953 | 34.3282 | 34.3391 | 34.1672 | 35.1826 | 34.9249 | 35.3865 | 36.0298 | 36.4763 | 22.051 | 19.8525 | 93.4159 | 32.9571 | 32.861 | 34.8936 | 33.0388 | 32.9539 | 33.3166 | 34.5454 | 34.2072 | 34.0397 | 37.2017 | 36.2135 | 33.3041 | 34.4129 | 36.2037 | 36.5169 | 37.2606 | 36.2162 | 33.0468 | 32.2923 | 34.0641 | 34.4657 | 32.5035 | 34.3611 | 34.3104 | 34.4268 | 34.2701 | 34.2249 | 34.3874 | 33.8652 | 34.2593 | 36.085 | 35.0141 | 36.5239 | 36.4839 | 33.2894 | 93.4134 | 93.5494 | 93.3391
2022-09-08 05:23 | 7:32 | 24.4004 | 24.1134 | 26.9364 | 34.6436 | 34.3948 | 34.1095 | 34.6198 | 35.5464 | 36.6029 | 37.5192 | 37.0204 | 38.1989 | 34.3192 | 34.3411 | 34.1645 | 35.1698 | 34.9257 | 35.3747 | 36.0205 | 36.4794 | 22.8908 | 21.0772 | 93.3433 | 33.0342 | 32.8764 | 34.8843 | 33.0455 | 32.9672 | 33.3206 | 34.5495 | 34.2079 | 34.0333 | 37.1843 | 36.1842 | 33.3041 | 34.4325 | 36.2214 | 36.5182 | 37.2866 | 36.23 | 33.0366 | 32.288 | 34.0643 | 34.4656 | 32.5127 | 34.363 | 34.3215 | 34.4294 | 34.2762 | 34.2222 | 34.3736 | 33.8721 | 34.2701 | 36.0851 | 35.0195 | 36.522 | 36.4975 | 33.2964 | 93.3339 | 93.4638 | 93.2656
2022-09-08 05:23 | 7:33 | 25.0626 | 25.1592 | 27.515 | 34.8419 | 34.4045 | 34.0919 | 34.6276 | 35.5429 | 36.6188 | 37.5091 | 37.0176 | 38.2096 | 34.3273 | 34.3517 | 34.1671 | 35.1676 | 34.9293 | 35.3902 | 36.0446 | 36.5011 | 23.753 | 22.2299 | 93.2702 | 33.2801 | 32.88 | 34.8801 | 33.029 | 32.9602 | 33.3172 | 34.5412 | 34.2238 | 34.0188 | 37.1833 | 36.2059 | 33.3145 | 34.4397 | 36.2135 | 36.5123 | 37.2852 | 36.2266 | 33.0315 | 32.2855 | 34.0518 | 34.4746 | 32.497 | 34.3513 | 34.3095 | 34.4154 | 34.2689 | 34.2036 | 34.3689 | 33.8657 | 34.2762 | 36.1097 | 35.0024 | 36.5357 | 36.4898 | 33.2837 | 93.1523 | 93.3711 | 93.1196
2022-09-08 05:23 | 7:33 | 25.6584 | 26.0449 | 27.9257 | 34.8171 | 34.3886 | 34.1083 | 34.636 | 35.5505 | 36.5812 | 37.5075 | 37.0164 | 38.1985 | 34.3116 | 34.3372 | 34.1593 | 35.1689 | 34.9331 | 35.3992 | 36.0667 | 36.4847 | 24.5456 | 23.2906 | 93.1803 | 33.242 | 32.872 | 34.8763 | 33.0397 | 32.9601 | 33.3242 | 34.5498 | 34.203 | 34.0202 | 37.209 | 36.2094 | 33.3306 | 34.4534 | 36.1842 | 36.4981 | 37.2775 | 36.2037 | 33.0269 | 32.3056 | 34.0578 | 34.466 | 32.5113 | 34.3515 | 34.3237 | 34.4115 | 34.2475 | 34.2465 | 34.381 | 33.8795 | 34.2689 | 36.0856 | 35.0136 | 36.5416 | 36.4952 | 33.3092 | 93.0648 | 93.2817 | 93.1394
2022-09-08 05:23 | 7:33 | 26.168 | 26.7692 | 28.3381 | 35.04 | 34.4131 | 34.1282 | 34.6422 | 35.553 | 36.5895 | 37.5268 | 37.0188 | 38.1886 | 34.3166 | 34.3392 | 34.1825 | 35.1858 | 34.9275 | 35.3971 | 36.0739 | 36.4927 | 25.2657 | 24.2026 | 93.1007 | 33.2783 | 32.873 | 34.8845 | 33.0468 | 32.9747 | 33.3041 | 34.5401 | 34.2123 | 34.0181 | 37.1948 | 36.1962 | 33.3172 | 34.4373 | 36.2059 | 36.53 | 37.2856 | 36.2214 | 33.0267 | 32.2846 | 34.0559 | 34.4779 | 32.5027 | 34.3565 | 34.3314 | 34.4068 | 34.249 | 34.2557 | 34.3957 | 33.8616 | 34.2475 | 36.0893 | 35.0164 | 36.5361 | 36.4913 | 33.3085 | 93.0862 | 93.2142 | 93.1175
2022-09-08 05:23 | 7:33 | 26.6314 | 27.4024 | 28.6735 | 35.1235 | 34.3947 | 34.1147 | 34.6362 | 35.5771 | 36.6232 | 37.5179 | 37.0292 | 38.2037 | 34.3075 | 34.3167 | 34.1671 | 35.1804 | 34.9218 | 35.4058 | 36.0685 | 36.4896 | 25.9597 | 25.0292 | 93.0309 | 33.3513 | 32.8768 | 34.8742 | 33.0366 | 32.9552 | 33.3041 | 34.5719 | 34.197 | 34.0286 | 37.1691 | 36.2056 | 33.3095 | 34.4554 | 36.2094 | 36.5157 | 37.2647 | 36.2135 | 33.0258 | 32.2936 | 34.0665 | 34.4531 | 32.5158 | 34.3451 | 34.3381 | 34.425 | 34.2628 | 34.2392 | 34.3959 | 33.8559 | 34.249 | 36.0913 | 35.0189 | 36.5315 | 36.4713 | 33.2765 | 92.894 | 93.0796 | 92.9821
2022-09-08 05:23 | 7:33 | 27.0298 | 27.9181 | 28.9513 | 35.0752 | 34.4081 | 34.1189 | 34.6463 | 35.5603 | 36.5979 | 37.5159 | 37.0353 | 38.213 | 34.3067 | 34.329 | 34.1669 | 35.206 | 34.9132 | 35.4028 | 36.0879 | 36.4918 | 26.5498 | 25.7203 | 92.9768 | 33.4474 | 32.891 | 34.8866 | 33.0315 | 32.9782 | 33.3145 | 34.5563 | 34.2247 | 34.0254 | 37.1839 | 36.1938 | 33.3212 | 34.452 | 36.1962 | 36.518 | 37.2598 | 36.1842 | 33.0309 | 32.2824 | 34.0734 | 34.4643 | 32.511 | 34.3516 | 34.3392 | 34.4166 | 34.2939 | 34.2272 | 34.3954 | 33.8646 | 34.2628 | 36.0907 | 35.0119 | 36.53 | 36.5099 | 33.3011 | 92.7725 | 92.9671 | 92.8695
2022-09-08 05:24 | 7:34 | 27.3759 | 28.3576 | 29.2234 | 35.2322 | 34.3986 | 34.116 | 34.6457 | 35.565 | 36.5931 | 37.5264 | 37.0291 | 38.2246 | 34.2951 | 34.3248 | 34.1689 | 35.2035 | 34.9321 | 35.3871 | 36.0984 | 36.4947 | 27.0762 | 26.3466 | 92.8632 | 33.5809 | 32.8683 | 34.8768 | 33.0269 | 32.9778 | 33.3306 | 34.557 | 34.2196 | 34.0378 | 37.1932 | 36.1948 | 33.315 | 34.456 | 36.2056 | 36.5135 | 37.2814 | 36.2059 | 33.0204 | 32.2779 | 34.0768 | 34.4649 | 32.5107 | 34.3424 | 34.3358 | 34.4046 | 34.2703 | 34.2286 | 34.3689 | 33.8725 | 34.2939 | 36.0931 | 34.9956 | 36.5448 | 36.5005 | 33.2915 | 92.7498 | 92.8667 | 92.8144
2022-09-08 05:24 | 7:34 | 27.6978 | 28.7308 | 29.447 | 35.2953 | 34.4095 | 34.1241 | 34.6642 | 35.5672 | 36.5988 | 37.5288 | 37.0329 | 38.2119 | 34.2843 | 34.284 | 34.158 | 35.1861 | 34.9165 | 35.4047 | 36.0827 | 36.4974 | 27.5781 | 26.8743 | 92.8543 | 33.5749 | 32.8783 | 34.8818 | 33.0267 | 32.9811 | 33.3172 | 34.5474 | 34.2329 | 34.0266 | 37.1914 | 36.1976 | 33.3283 | 34.4361 | 36.1938 | 36.5306 | 37.2888 | 36.2094 | 33.0221 | 32.3 | 34.0616 | 34.4677 | 32.5116 | 34.3396 | 34.3331 | 34.3969 | 34.286 | 34.2417 | 34.3935 | 33.8623 | 34.2703 | 36.1096 | 35.0047 | 36.546 | 36.4942 | 33.3259 | 92.6193 | 92.7461 | 92.7124
2022-09-08 05:24 | 7:34 | 28.6911 | 23.3647 | 29.0688 | 35.3436 | 34.397 | 34.1363 | 34.6679 | 35.5653 | 36.6085 | 37.5336 | 37.0332 | 38.2161 | 34.2711 | 34.3202 | 34.1664 | 35.1948 | 34.914 | 35.4242 | 36.0976 | 36.5076 | 27.8992 | 23.2384 | 92.7956 | 33.4836 | 32.8867 | 34.8736 | 33.0258 | 32.9785 | 33.3095 | 34.5316 | 34.2137 | 34.0235 | 37.1777 | 36.1947 | 33.3232 | 34.4408 | 36.1948 | 36.5324 | 37.2733 | 36.1962 | 33.0137 | 32.3021 | 34.0936 | 34.4687 | 32.5048 | 34.3479 | 34.3338 | 34.3927 | 34.2558 | 34.2426 | 34.3711 | 33.8751 | 34.286 | 36.1034 | 34.9976 | 36.5519 | 36.502 | 33.3135 | 92.5261 | 92.6181 | 92.6954
2022-09-08 05:24 | 7:34 | 29.2432 | 28.3495 | 29.162 | 35.3426 | 34.4005 | 34.1261 | 34.6676 | 35.5813 | 36.6039 | 37.5468 | 37.0298 | 38.2062 | 34.281 | 34.3241 | 34.1811 | 35.2092 | 34.9097 | 35.4278 | 36.1144 | 36.5075 | 29.2043 | 27.6662 | 92.618 | 33.6321 | 32.8762 | 34.8718 | 33.0309 | 32.9612 | 33.3212 | 34.5623 | 34.2266 | 34.0206 | 37.1995 | 36.1978 | 33.3135 | 34.4468 | 36.1976 | 36.5253 | 37.2768 | 36.2056 | 33.0442 | 32.2859 | 34.0996 | 34.476 | 32.5167 | 34.3382 | 34.3394 | 34.3927 | 34.2534 | 34.2332 | 34.3761 | 33.8693 | 34.2558 | 36.1158 | 34.9959 | 36.5452 | 36.4932 | 33.3174 | 92.3538 | 92.5231 | 92.6046
2022-09-08 05:24 | 7:34 | 30.8048 | 30.5269 | 29.7608 | 35.3727 | 34.4 | 34.145 | 34.6883 | 35.5581 | 36.5973 | 37.5331 | 37.0321 | 38.225 | 34.2811 | 34.324 | 34.1856 | 35.197 | 34.9309 | 35.4265 | 36.1174 | 36.5104 | 30.895 | 29.6741 | 92.5187 | 33.7878 | 32.8719 | 34.8683 | 33.0204 | 32.9974 | 33.315 | 34.5323 | 34.2084 | 34.0225 | 37.1796 | 36.2029 | 33.3155 | 34.4592 | 36.1947 | 36.5256 | 37.2635 | 36.1938 | 33.0177 | 32.2984 | 34.0721 | 34.4845 | 32.5201 | 34.3254 | 34.3469 | 34.3944 | 34.2879 | 34.2406 | 34.3829 | 33.8618 | 34.2534 | 36.1097 | 34.9885 | 36.5416 | 36.4827 | 33.3141 | 92.2913 | 92.4006 | 92.4481
2022-09-08 05:24 | 7:34 | 31.5668 | 30.6628 | 30.2016 | 35.4582 | 34.4074 | 34.1367 | 34.6916 | 35.5738 | 36.6085 | 37.5497 | 37.0323 | 38.2107 | 34.2883 | 34.3012 | 34.1797 | 35.2047 | 34.9207 | 35.4143 | 36.1126 | 36.5084 | 32.0399 | 30.2263 | 92.4347 | 33.7874 | 32.8787 | 34.8671 | 33.0221 | 33.0001 | 33.3283 | 34.5377 | 34.2182 | 34.0186 | 37.1955 | 36.2102 | 33.3174 | 34.4393 | 36.1978 | 36.5228 | 37.2908 | 36.1948 | 33.0039 | 32.3065 | 34.0941 | 34.4879 | 32.537 | 34.3443 | 34.3445 | 34.4015 | 34.2669 | 34.2448 | 34.3669 | 33.8606 | 34.2879 | 36.0987 | 35.0033 | 36.5501 | 36.5078 | 33.3076 | 92.1915 | 92.3134 | 92.3962
2022-09-08 05:25 | 7:34 | 32.0865 | 30.7218 | 30.4854 | 35.511 | 34.3894 | 34.1432 | 34.6967 | 35.5883 | 36.5876 | 37.5545 | 37.0381 | 38.22 | 34.2546 | 34.314 | 34.1942 | 35.2007 | 34.9116 | 35.4349 | 36.1331 | 36.525 | 32.9048 | 30.5392 | 92.4755 | 33.8081 | 32.8821 | 34.8836 | 33.0137 | 32.9987 | 33.3232 | 34.5417 | 34.219 | 34.0289 | 37.204 | 36.1907 | 33.3098 | 34.4743 | 36.2029 | 36.5373 | 37.3018 | 36.1976 | 32.9922 | 32.2984 | 34.0935 | 34.4854 | 32.5196 | 34.3375 | 34.3536 | 34.3947 | 34.2662 | 34.2515 | 34.3615 | 33.8588 | 34.2669 | 36.1004 | 35.0279 | 36.5555 | 36.5187 | 33.3195 | 92.1885 | 92.3653 | 92.4408
2022-09-08 05:25 | 7:35 | 32.6332 | 30.7644 | 30.7367 | 35.5249 | 34.4099 | 34.1386 | 34.6924 | 35.5726 | 36.6129 | 37.577 | 37.0437 | 38.2144 | 34.2671 | 34.2858 | 34.1775 | 35.2049 | 34.9272 | 35.4259 | 36.1506 | 36.5158 | 33.5429 | 30.689 | 92.5342 | 33.8851 | 32.8765 | 34.8775 | 33.0442 | 32.992 | 33.3135 | 34.5563 | 34.2274 | 34.0222 | 37.1937 | 36.1999 | 33.3198 | 34.4646 | 36.2102 | 36.544 | 37.283 | 36.1947 | 33.0186 | 32.3043 | 34.1041 | 34.4846 | 32.5417 | 34.3347 | 34.3582 | 34.4125 | 34.275 | 34.2489 | 34.3704 | 33.8805 | 34.2662 | 36.1091 | 34.9931 | 36.5548 | 36.5046 | 33.3109 | 92.2197 | 92.4175 | 92.4724
2022-09-08 05:25 | 7:35 | 33.0109 | 30.8037 | 30.9704 | 35.6144 | 34.4082 | 34.1433 | 34.7083 | 35.5846 | 36.6111 | 37.5727 | 37.0204 | 38.2229 | 34.2517 | 34.3149 | 34.1673 | 35.2108 | 34.9191 | 35.4384 | 36.1535 | 36.5115 | 33.8734 | 30.7461 | 92.5337 | 33.916 | 32.8808 | 34.8761 | 33.0177 | 32.9935 | 33.3155 | 34.5498 | 34.2208 | 34.0174 | 37.1938 | 36.177 | 33.306 | 34.4696 | 36.1907 | 36.5329 | 37.2835 | 36.1978 | 33.0032 | 32.304 | 34.115 | 34.4846 | 32.5403 | 34.313 | 34.3729 | 34.4137 | 34.2634 | 34.2584 | 34.3675 | 33.8783 | 34.275 | 36.1157 | 34.9976 | 36.5632 | 36.5131 | 33.3322 | 92.3276 | 92.5058 | 92.491
2022-09-08 05:25 | 7:35 | 33.0568 | 30.8519 | 31.1668 | 35.699 | 34.4044 | 34.1306 | 34.6872 | 35.5977 | 36.6173 | 37.5757 | 37.0307 | 38.2415 | 34.24 | 34.2881 | 34.1799 | 35.2179 | 34.913 | 35.4239 | 36.1495 | 36.5186 | 33.9322 | 30.777 | 92.558 | 33.9814 | 32.8824 | 34.8593 | 33.0039 | 32.9957 | 33.3174 | 34.551 | 34.2107 | 34.0037 | 37.1966 | 36.1863 | 33.3156 | 34.4455 | 36.1999 | 36.5268 | 37.2724 | 36.2029 | 33.0037 | 32.3037 | 34.1187 | 34.4905 | 32.5571 | 34.3244 | 34.3713 | 34.3845 | 34.2786 | 34.2592 | 34.3641 | 33.874 | 34.2634 | 36.1225 | 34.9946 | 36.5661 | 36.5095 | 33.3168 | 92.3834 | 92.6051 | 92.558
2022-09-08 05:25 | 7:35 | 33.1314 | 30.8873 | 31.275 | 35.6604 | 34.394 | 34.1411 | 34.6999 | 35.5874 | 36.6151 | 37.562 | 37.0369 | 38.2242 | 34.2794 | 34.2811 | 34.1709 | 35.1959 | 34.9255 | 35.4572 | 36.1424 | 36.5175 | 33.8545 | 30.8169 | 92.6651 | 34.0262 | 32.8932 | 34.8763 | 32.9922 | 32.999 | 33.3098 | 34.5463 | 34.2313 | 34.0274 | 37.194 | 36.178 | 33.328 | 34.4623 | 36.177 | 36.5294 | 37.296 | 36.2102 | 33.0008 | 32.3272 | 34.1137 | 34.483 | 32.5532 | 34.3288 | 34.3734 | 34.4024 | 34.2697 | 34.2644 | 34.3676 | 33.8709 | 34.2786 | 36.1087 | 35.0055 | 36.5498 | 36.4948 | 33.3383 | 92.4733 | 92.705 | 92.6103
2022-09-08 05:25 | 7:35 | 33.1874 | 30.7804 | 31.4115 | 35.7711 | 34.3912 | 34.1479 | 34.6784 | 35.5816 | 36.6257 | 37.5743 | 37.0421 | 38.2263 | 34.2745 | 34.2971 | 34.1589 | 35.2025 | 34.9213 | 35.4533 | 36.176 | 36.5271 | 33.8085 | 30.8429 | 92.7095 | 34.1175 | 32.8776 | 34.8502 | 33.0186 | 32.9841 | 33.3198 | 34.5649 | 34.2229 | 34.003 | 37.1848 | 36.1647 | 33.3086 | 34.4508 | 36.1863 | 36.5355 | 37.2734 | 36.1907 | 32.9892 | 32.3222 | 34.1111 | 34.4761 | 32.55 | 34.3239 | 34.3648 | 34.391 | 34.2917 | 34.2636 | 34.3522 | 33.8683 | 34.2697 | 36.1174 | 34.9996 | 36.5313 | 36.5136 | 33.3304 | 92.5585 | 92.8193 | 92.6548
2022-09-08 05:26 | 7:35 | 33.2789 | 30.7618 | 31.4727 | 35.8088 | 34.4017 | 34.154 | 34.7146 | 35.5909 | 36.6041 | 37.569 | 37.0438 | 38.2151 | 34.2607 | 34.2868 | 34.1711 | 35.2068 | 34.9269 | 35.4427 | 36.1705 | 36.5085 | 33.7993 | 30.8727 | 92.7602 | 34.1948 | 32.8745 | 34.8368 | 33.0032 | 32.9984 | 33.306 | 34.5537 | 34.2201 | 33.999 | 37.204 | 36.1521 | 33.3056 | 34.4472 | 36.178 | 36.5328 | 37.2807 | 36.1999 | 33.0032 | 32.3175 | 34.1168 | 34.479 | 32.5585 | 34.3225 | 34.3543 | 34.3988 | 34.2805 | 34.249 | 34.3597 | 33.8783 | 34.2917 | 36.1064 | 35.017 | 36.5477 | 36.5189 | 33.3379 | 92.6668 | 92.9168 | 92.7738
2022-09-08 05:26 | 7:36 | 33.5072 | 30.7986 | 31.6482 | 35.8264 | 34.4007 | 34.1407 | 34.7055 | 35.5752 | 36.6029 | 37.5759 | 37.0227 | 38.2075 | 34.2476 | 34.2945 | 34.1854 | 35.2094 | 34.8861 | 35.4703 | 36.1682 | 36.5157 | 33.8283 | 30.9106 | 92.7924 | 34.1701 | 32.8811 | 34.8475 | 33.0037 | 32.9894 | 33.3156 | 34.5631 | 34.2293 | 33.9964 | 37.1839 | 36.171 | 33.302 | 34.4714 | 36.1647 | 36.5223 | 37.2925 | 36.177 | 32.9892 | 32.3204 | 34.1351 | 34.4748 | 32.5717 | 34.3261 | 34.3762 | 34.4069 | 34.2874 | 34.2604 | 34.3612 | 33.8677 | 34.2805 | 36.1269 | 34.9928 | 36.5442 | 36.4909 | 33.3232 | 92.7535 | 93.0109 | 92.8736
2022-09-08 05:26 | 7:36 | 33.5763 | 30.8565 | 31.7378 | 35.8796 | 34.3736 | 34.138 | 34.7055 | 35.585 | 36.6048 | 37.5777 | 37.024 | 38.2228 | 34.2379 | 34.2866 | 34.1745 | 35.2029 | 34.9046 | 35.4554 | 36.1786 | 36.5158 | 33.8772 | 30.9732 | 92.8734 | 34.102 | 32.8856 | 34.8607 | 33.0008 | 33.0095 | 33.328 | 34.5415 | 34.2202 | 34.0293 | 37.1866 | 36.1566 | 33.3194 | 34.4474 | 36.1521 | 36.5233 | 37.2932 | 36.1863 | 32.9747 | 32.3173 | 34.1156 | 34.4827 | 32.568 | 34.3142 | 34.3655 | 34.3873 | 34.2894 | 34.2658 | 34.3588 | 33.8676 | 34.2874 | 36.1218 | 34.9845 | 36.5467 | 36.5073 | 33.3345 | 92.8257 | 93.1237 | 92.9205
2022-09-08 05:26 | 7:36 | 33.5444 | 30.9501 | 31.7289 | 35.9922 | 34.3656 | 34.1467 | 34.7011 | 35.5728 | 36.6058 | 37.5948 | 37.0313 | 38.2132 | 34.2642 | 34.2951 | 34.1709 | 35.2069 | 34.876 | 35.4427 | 36.1791 | 36.5308 | 33.8799 | 31.0106 | 92.9064 | 34.1956 | 32.8862 | 34.8364 | 32.9892 | 33.0006 | 33.3086 | 34.5705 | 34.1995 | 34.0234 | 37.1709 | 36.1741 | 33.3209 | 34.4464 | 36.171 | 36.5253 | 37.2861 | 36.178 | 32.9902 | 32.3078 | 34.148 | 34.4949 | 32.5633 | 34.3062 | 34.3598 | 34.3816 | 34.2747 | 34.2647 | 34.348 | 33.8607 | 34.2894 | 36.0996 | 34.9929 | 36.5549 | 36.509 | 33.3238 | 92.9613 | 93.2879 | 92.9886
2022-09-08 05:26 | 7:36 | 33.8558 | 31.0396 | 31.867 | 35.9398 | 34.4075 | 34.1475 | 34.6885 | 35.5773 | 36.6188 | 37.608 | 37.0144 | 38.2042 | 34.257 | 34.288 | 34.1565 | 35.2114 | 34.8934 | 35.4611 | 36.187 | 36.5156 | 33.861 | 31.0461 | 93.0226 | 34.2199 | 32.8806 | 34.8477 | 33.0032 | 32.9769 | 33.3056 | 34.5669 | 34.2193 | 33.9998 | 37.1838 | 36.1638 | 33.3152 | 34.4434 | 36.1566 | 36.535 | 37.2954 | 36.1647 | 32.9986 | 32.3253 | 34.1284 | 34.4977 | 32.5888 | 34.2966 | 34.3743 | 34.398 | 34.2704 | 34.2524 | 34.3584 | 33.8732 | 34.2747 | 36.1287 | 35.0003 | 36.5322 | 36.4932 | 33.336 | 93.0374 | 93.3842 | 93.0301
2022-09-08 05:26 | 7:36 | 33.9088 | 31.1327 | 32.0635 | 35.9755 | 34.3735 | 34.1398 | 34.6861 | 35.5979 | 36.6075 | 37.5925 | 37.0175 | 38.2218 | 34.261 | 34.2805 | 34.1719 | 35.2005 | 34.898 | 35.4649 | 36.1844 | 36.5234 | 33.8837 | 31.1068 | 93.0373 | 34.3241 | 32.8981 | 34.8266 | 32.9892 | 33.004 | 33.302 | 34.5883 | 34.2107 | 33.9926 | 37.1879 | 36.1723 | 33.3241 | 34.4691 | 36.1741 | 36.5192 | 37.2859 | 36.1521 | 32.9865 | 32.3111 | 34.1339 | 34.4954 | 32.5956 | 34.2999 | 34.3795 | 34.3923 | 34.2749 | 34.2657 | 34.3529 | 33.8839 | 34.2704 | 36.1159 | 34.9815 | 36.5474 | 36.5157 | 33.3272 | 93.1575 | 93.4909 | 93.1283
2022-09-08 05:27 | 7:37 | 33.9379 | 31.2031 | 32.1673 | 35.9723 | 34.3871 | 34.1354 | 34.7129 | 35.5962 | 36.5964 | 37.6087 | 37.0207 | 38.2005 | 34.2401 | 34.2697 | 34.1741 | 35.2061 | 34.9073 | 35.462 | 36.1921 | 36.5206 | 33.8375 | 31.1245 | 93.1228 | 34.388 | 32.8773 | 34.8314 | 32.9747 | 33.0029 | 33.3194 | 34.5757 | 34.191 | 33.9879 | 37.1718 | 36.1751 | 33.3293 | 34.4543 | 36.1638 | 36.5283 | 37.3047 | 36.171 | 32.9753 | 32.3227 | 34.1352 | 34.5012 | 32.5793 | 34.2922 | 34.3848 | 34.3978 | 34.2869 | 34.2619 | 34.3391 | 33.8726 | 34.2749 | 36.1148 | 34.9915 | 36.5355 | 36.5209 | 33.327 | 93.3163 | 93.6084 | 93.1822
2022-09-08 05:27 | 7:37 | 34.0003 | 31.2516 | 32.222 | 36.0082 | 34.379 | 34.1493 | 34.6833 | 35.5888 | 36.6142 | 37.5968 | 37.0228 | 38.2024 | 34.2519 | 34.2489 | 34.1643 | 35.2085 | 34.8976 | 35.4712 | 36.2039 | 36.5294 | 33.7721 | 31.154 | 93.1859 | 34.4282 | 32.8732 | 34.844 | 32.9902 | 32.9989 | 33.3209 | 34.5557 | 34.2103 | 33.9895 | 37.1594 | 36.164 | 33.3154 | 34.4391 | 36.1723 | 36.5187 | 37.3135 | 36.1566 | 32.9917 | 32.3278 | 34.1395 | 34.4995 | 32.5898 | 34.2822 | 34.3667 | 34.3691 | 34.2694 | 34.2921 | 34.3411 | 33.8626 | 34.2869 | 36.1196 | 34.9812 | 36.5414 | 36.5093 | 33.3442 | 93.4348 | 93.7606 | 93.3411
2022-09-08 05:27 | 7:37 | 34.0001 | 31.3065 | 32.2812 | 36.12 | 34.3906 | 34.1427 | 34.7104 | 35.5964 | 36.6245 | 37.6115 | 37.0154 | 38.2142 | 34.2418 | 34.2805 | 34.1809 | 35.2005 | 34.9009 | 35.4769 | 36.1914 | 36.5434 | 33.7187 | 31.1623 | 93.269 | 34.3748 | 32.8928 | 34.8243 | 32.9986 | 33.0114 | 33.3152 | 34.5653 | 34.2182 | 33.9906 | 37.1847 | 36.1648 | 33.3189 | 34.4425 | 36.1751 | 36.5464 | 37.3028 | 36.1741 | 32.9854 | 32.3271 | 34.1439 | 34.5006 | 32.6013 | 34.294 | 34.3972 | 34.3905 | 34.2996 | 34.2835 | 34.3517 | 33.8807 | 34.2694 | 36.125 | 34.9972 | 36.5516 | 36.5055 | 33.3436 | 93.5838 | 93.9232 | 93.4323
2022-09-08 05:27 | 7:37 | 34.0587 | 31.3604 | 32.3235 | 36.0872 | 34.3708 | 34.1478 | 34.6979 | 35.5724 | 36.6008 | 37.5941 | 37.0191 | 38.2063 | 34.2244 | 34.2768 | 34.1758 | 35.2006 | 34.8834 | 35.4789 | 36.203 | 36.5358 | 33.7231 | 31.1807 | 93.3647 | 34.4092 | 32.8758 | 34.814 | 32.9865 | 32.9992 | 33.3241 | 34.5763 | 34.1884 | 33.9947 | 37.1961 | 36.1699 | 33.3117 | 34.4514 | 36.164 | 36.5351 | 37.2996 | 36.1638 | 32.989 | 32.3416 | 34.169 | 34.4963 | 32.6109 | 34.2755 | 34.376 | 34.3845 | 34.2873 | 34.2763 | 34.3372 | 33.8606 | 34.2996 | 36.1289 | 34.976 | 36.5336 | 36.5115 | 33.3257 | 93.7554 | 94.1264 | 93.5518
2022-09-08 05:27 | 7:37 | 34.1357 | 31.3868 | 32.4184 | 36.0961 | 34.3874 | 34.1563 | 34.6952 | 35.5904 | 36.6104 | 37.6173 | 37.0012 | 38.1944 | 34.231 | 34.2759 | 34.1841 | 35.2044 | 34.8773 | 35.4655 | 36.1982 | 36.508 | 33.6905 | 31.2025 | 93.568 | 34.4726 | 32.8881 | 34.8176 | 32.9753 | 33.0089 | 33.3293 | 34.5713 | 34.2048 | 33.9903 | 37.1739 | 36.1632 | 33.3062 | 34.4487 | 36.1648 | 36.5147 | 37.3194 | 36.1723 | 32.9662 | 32.3382 | 34.1593 | 34.5223 | 32.5969 | 34.2824 | 34.3885 | 34.3658 | 34.2894 | 34.2662 | 34.3392 | 33.8835 | 34.2873 | 36.12 | 34.9846 | 36.5336 | 36.5349 | 33.3291 | 93.9012 | 94.3173 | 93.599
2022-09-08 05:27 | 7:37 | 34.2004 | 31.4457 | 32.4973 | 36.1243 | 34.3736 | 34.1325 | 34.69 | 35.5845 | 36.5921 | 37.632 | 36.9982 | 38.2193 | 34.2241 | 34.2773 | 34.1809 | 35.2022 | 34.8903 | 35.4528 | 36.22 | 36.5327 | 33.7899 | 31.2086 | 93.6754 | 34.4394 | 32.9 | 34.8169 | 32.9917 | 33.009 | 33.3154 | 34.5871 | 34.2169 | 33.9911 | 37.1597 | 36.1653 | 33.3185 | 34.446 | 36.1699 | 36.5247 | 37.2986 | 36.1751 | 32.9664 | 32.3439 | 34.1697 | 34.4961 | 32.6172 | 34.2851 | 34.3854 | 34.3918 | 34.3071 | 34.2883 | 34.3167 | 33.8709 | 34.2894 | 36.1203 | 34.977 | 36.5351 | 36.5074 | 33.3549 | 94.1432 | 94.5221 | 93.7812
2022-09-08 05:28 | 7:37 | 34.3129 | 31.4635 | 32.5971 | 36.1719 | 34.3689 | 34.1441 | 34.7022 | 35.5869 | 36.6152 | 37.6148 | 37.0061 | 38.2049 | 34.2276 | 34.2559 | 34.1936 | 35.1926 | 34.8846 | 35.4825 | 36.2219 | 36.5374 | 33.865 | 31.2205 | 93.7602 | 34.5478 | 32.8847 | 34.8244 | 32.9854 | 33.0097 | 33.3189 | 34.5801 | 34.1978 | 33.9828 | 37.1826 | 36.1374 | 33.3103 | 34.4303 | 36.1632 | 36.5172 | 37.3106 | 36.164 | 32.9839 | 32.3424 | 34.153 | 34.5043 | 32.6141 | 34.3019 | 34.3899 | 34.3617 | 34.2902 | 34.2702 | 34.329 | 33.8622 | 34.3071 | 36.133 | 34.9681 | 36.5404 | 36.5255 | 33.3262 | 94.2589 | 94.6997 | 93.9104
2022-09-08 05:28 | 7:38 | 34.4547 | 31.4833 | 32.6881 | 36.304 | 34.381 | 34.1426 | 34.6949 | 35.585 | 36.6171 | 37.6179 | 37.0158 | 38.2179 | 34.2263 | 34.2679 | 34.1803 | 35.2035 | 34.8879 | 35.4773 | 36.2207 | 36.5508 | 33.9779 | 31.2266 | 93.8475 | 34.5286 | 32.8745 | 34.8249 | 32.989 | 32.9875 | 33.3117 | 34.5824 | 34.197 | 33.9845 | 37.1701 | 36.1673 | 33.3309 | 34.454 | 36.1653 | 36.5111 | 37.2875 | 36.1648 | 32.9768 | 32.3348 | 34.1497 | 34.5092 | 32.6419 | 34.2693 | 34.4002 | 34.3536 | 34.3048 | 34.2901 | 34.3248 | 33.8951 | 34.2902 | 36.1157 | 34.9677 | 36.5366 | 36.5084 | 33.3338 | 94.4286 | 94.8846 | 94.032
2022-09-08 05:28 | 7:38 | 34.5182 | 31.5328 | 32.7729 | 36.1399 | 34.3957 | 34.1487 | 34.7024 | 35.5982 | 36.6109 | 37.6168 | 37.0089 | 38.2108 | 34.233 | 34.2634 | 34.177 | 35.2033 | 34.8779 | 35.4671 | 36.2232 | 36.5263 | 34.0442 | 31.2595 | 93.9938 | 34.4978 | 32.8881 | 34.8258 | 32.9662 | 32.9999 | 33.3062 | 34.5757 | 34.2056 | 33.9761 | 37.1841 | 36.1741 | 33.3137 | 34.4478 | 36.1374 | 36.5183 | 37.2997 | 36.1699 | 32.9686 | 32.3507 | 34.1645 | 34.4995 | 32.6487 | 34.2663 | 34.398 | 34.3628 | 34.3002 | 34.2698 | 34.284 | 33.886 | 34.3048 | 36.1363 | 34.9772 | 36.5334 | 36.5269 | 33.3232 | 94.6034 | 95.0656 | 94.1296
2022-09-08 05:28 | 7:38 | 34.5845 | 31.5303 | 32.8318 | 36.201 | 34.3959 | 34.145 | 34.7148 | 35.5841 | 36.6247 | 37.6135 | 37.0167 | 38.2065 | 34.2272 | 34.2433 | 34.1656 | 35.1915 | 34.8869 | 35.4678 | 36.2139 | 36.5357 | 34.0972 | 31.274 | 94.0293 | 34.5771 | 32.8805 | 34.8304 | 32.9664 | 33.0103 | 33.3185 | 34.6047 | 34.1825 | 33.9687 | 37.1764 | 36.1529 | 33.3267 | 34.4318 | 36.1673 | 36.5122 | 37.308 | 36.1632 | 32.9847 | 32.3547 | 34.1694 | 34.4959 | 32.6471 | 34.2629 | 34.3715 | 34.3686 | 34.2874 | 34.2599 | 34.3202 | 33.8765 | 34.3002 | 36.1153 | 34.9744 | 36.5353 | 36.5282 | 33.3307 | 94.7642 | 95.2276 | 94.2785
2022-09-08 05:28 | 7:38 | 34.6116 | 31.5778 | 32.8959 | 36.278 | 34.3954 | 34.1439 | 34.7007 | 35.6068 | 36.6124 | 37.614 | 37.0035 | 38.2074 | 34.2318 | 34.2467 | 34.1785 | 35.1843 | 34.8907 | 35.4919 | 36.2421 | 36.5413 | 34.1671 | 31.2823 | 94.1028 | 34.6108 | 32.8894 | 34.81 | 32.9839 | 33.0097 | 33.3103 | 34.5919 | 34.2011 | 33.966 | 37.1798 | 36.1412 | 33.3083 | 34.4514 | 36.1741 | 36.527 | 37.2985 | 36.1653 | 32.9631 | 32.3686 | 34.1825 | 34.5242 | 32.6512 | 34.2881 | 34.3947 | 34.3774 | 34.3012 | 34.2579 | 34.3241 | 33.8751 | 34.2874 | 36.1318 | 34.9722 | 36.5334 | 36.509 | 33.3121 | 94.9669 | 95.4062 | 94.2968
2022-09-08 05:28 | 7:38 | 34.6848 | 31.59 | 32.9538 | 36.21 | 34.3689 | 34.134 | 34.718 | 35.5965 | 36.6216 | 37.6103 | 36.9959 | 38.2172 | 34.2093 | 34.2441 | 34.1668 | 35.1911 | 34.8702 | 35.4833 | 36.2343 | 36.5371 | 33.9352 | 31.2053 | 94.1933 | 34.6506 | 32.867 | 34.8229 | 32.9768 | 32.9959 | 33.3309 | 34.5843 | 34.1836 | 33.9753 | 37.1767 | 36.1686 | 33.3126 | 34.4514 | 36.1529 | 36.5171 | 37.3144 | 36.1374 | 32.9633 | 32.34 | 34.1849 | 34.5104 | 32.6634 | 34.2826 | 34.4099 | 34.3532 | 34.3003 | 34.2835 | 34.324 | 33.8846 | 34.3012 | 36.1392 | 34.9652 | 36.5319 | 36.5154 | 33.3161 | 95.0317 | 95.5288 | 94.4236
2022-09-08 05:29 | 7:39 | 31.2773 | 31.2771 | 32.4577 | 36.3505 | 34.3935 | 34.1247 | 34.6824 | 35.5765 | 36.6064 | 37.6161 | 36.9861 | 38.2111 | 34.2245 | 34.2525 | 34.1742 | 35.1804 | 34.8699 | 35.4828 | 36.2316 | 36.5467 | 30.3558 | 30.8449 | 94.3513 | 34.692 | 32.8858 | 34.8172 | 32.9686 | 33.0076 | 33.3137 | 34.5941 | 34.1925 | 33.9799 | 37.159 | 36.1411 | 33.3229 | 34.4385 | 36.1412 | 36.508 | 37.3108 | 36.1673 | 32.9723 | 32.3342 | 34.1849 | 34.5058 | 32.6619 | 34.2842 | 34.3943 | 34.3604 | 34.2999 | 34.2687 | 34.3012 | 33.885 | 34.3003 | 36.1253 | 34.9803 | 36.5205 | 36.5043 | 33.3231 | 95.1639 | 95.6418 | 94.5395
2022-09-08 05:29 | 7:39 | 30.2644 | 26.623 | 31.9699 | 36.3572 | 34.3711 | 34.1275 | 34.7051 | 35.5976 | 36.5979 | 37.6115 | 37.024 | 38.196 | 34.2142 | 34.2545 | 34.1562 | 35.1883 | 34.8785 | 35.4872 | 36.2267 | 36.5314 | 27.1196 | 28.179 | 94.3798 | 34.6075 | 32.8729 | 34.8178 | 32.9847 | 33.0013 | 33.3267 | 34.5909 | 34.1776 | 33.9724 | 37.1727 | 36.155 | 33.3061 | 34.4277 | 36.1686 | 36.5137 | 37.302 | 36.1741 | 32.9552 | 32.3735 | 34.2067 | 34.5187 | 32.6633 | 34.3017 | 34.3855 | 34.3499 | 34.2937 | 34.2935 | 34.314 | 33.8577 | 34.2999 | 36.144 | 34.9543 | 36.5499 | 36.5114 | 33.3172 | 95.159 | 95.7023 | 94.5684
2022-09-08 05:29 | 7:39 | 31.17 | 24.0141 | 32.2281 | 36.2863 | 34.3761 | 34.1289 | 34.6925 | 35.5879 | 36.6187 | 37.608 | 37.0131 | 38.2142 | 34.2266 | 34.2448 | 34.1462 | 35.1834 | 34.8814 | 35.4642 | 36.2304 | 36.5373 | 27.5057 | 28.0708 | 94.4366 | 34.6247 | 32.8846 | 34.814 | 32.9631 | 33.0043 | 33.3083 | 34.5769 | 34.1783 | 33.9607 | 37.149 | 36.1529 | 33.3141 | 34.4278 | 36.1411 | 36.5229 | 37.317 | 36.1529 | 32.9497 | 32.3731 | 34.1714 | 34.5179 | 32.69 | 34.2799 | 34.3752 | 34.3373 | 34.299 | 34.2831 | 34.2858 | 33.8623 | 34.2937 | 36.1159 | 34.9864 | 36.534 | 36.503 | 33.3269 | 95.2524 | 95.8093 | 94.575
2022-09-08 05:29 | 7:39 | 31.7257 | 24.4606 | 32.3219 | 36.2279 | 34.3829 | 34.1554 | 34.7003 | 35.6026 | 36.6002 | 37.6105 | 37.0168 | 38.2008 | 34.2283 | 34.2525 | 34.1659 | 35.1922 | 34.882 | 35.4735 | 36.2363 | 36.5123 | 28.2737 | 28.413 | 94.4698 | 34.648 | 32.8792 | 34.8177 | 32.9633 | 32.9982 | 33.3126 | 34.5739 | 34.1829 | 33.9739 | 37.1707 | 36.1503 | 33.2957 | 34.4173 | 36.155 | 36.5079 | 37.3074 | 36.1412 | 32.9787 | 32.3702 | 34.1833 | 34.5153 | 32.6771 | 34.2571 | 34.391 | 34.3479 | 34.2969 | 34.2733 | 34.3149 | 33.8735 | 34.299 | 36.1217 | 34.9735 | 36.5431 | 36.5115 | 33.3089 | 95.312 | 95.9162 | 94.7191
2022-09-08 05:29 | 7:39 | 29.4246 | 25.6459 | 30.993 | 36.3659 | 34.3669 | 34.1221 | 34.6955 | 35.5876 | 36.6116 | 37.6149 | 37.0244 | 38.1925 | 34.2437 | 34.2548 | 34.16 | 35.1797 | 34.8796 | 35.4716 | 36.2261 | 36.5229 | 28.9633 | 28.793 | 94.4671 | 34.6818 | 32.8801 | 34.8094 | 32.9723 | 33.0058 | 33.3229 | 34.5714 | 34.2034 | 33.9594 | 37.1681 | 36.1775 | 33.2986 | 34.4201 | 36.1529 | 36.5101 | 37.3006 | 36.1686 | 32.9724 | 32.392 | 34.1818 | 34.4984 | 32.6835 | 34.2722 | 34.3965 | 34.3418 | 34.3258 | 34.27 | 34.2881 | 33.8865 | 34.2969 | 36.1281 | 34.9672 | 36.5269 | 36.5067 | 33.3001 | 95.3197 | 95.7623 | 94.6289
2022-09-08 05:29 | 7:39 | 30.2176 | 24.9698 | 30.2876 | 36.2484 | 34.3615 | 34.1263 | 34.7092 | 35.5862 | 36.6069 | 37.6093 | 37.0065 | 38.202 | 34.2337 | 34.2212 | 34.129 | 35.181 | 34.8862 | 35.4765 | 36.2061 | 36.5199 | 29.4424 | 29.13 | 94.342 | 34.6734 | 32.8592 | 34.818 | 32.9552 | 33.009 | 33.3061 | 34.5772 | 34.1699 | 33.9661 | 37.1568 | 36.1647 | 33.31 | 34.4305 | 36.1503 | 36.5187 | 37.2846 | 36.1411 | 32.961 | 32.3763 | 34.1846 | 34.5024 | 32.6952 | 34.2711 | 34.4021 | 34.3498 | 34.3029 | 34.2664 | 34.2811 | 33.8939 | 34.3258 | 36.1194 | 34.9764 | 36.5209 | 36.5235 | 33.2944 | 95.0244 | 95.4726 | 94.4095
2022-09-08 05:30 | 7:39 | 29.2505 | 24.5721 | 29.4216 | 36.0294 | 34.3704 | 34.148 | 34.7106 | 35.5782 | 36.6037 | 37.6022 | 36.9916 | 38.1835 | 34.2249 | 34.2496 | 34.1504 | 35.1796 | 34.8886 | 35.4611 | 36.2169 | 36.4926 | 29.872 | 29.4878 | 94.1558 | 34.7183 | 32.8668 | 34.8072 | 32.9497 | 33.0114 | 33.3141 | 34.5719 | 34.1865 | 33.9603 | 37.1462 | 36.1746 | 33.2942 | 34.4259 | 36.1775 | 36.4853 | 37.3047 | 36.155 | 32.9612 | 32.3854 | 34.1786 | 34.511 | 32.6879 | 34.2737 | 34.3889 | 34.3176 | 34.3067 | 34.2876 | 34.2971 | 33.8779 | 34.3029 | 36.0886 | 34.9529 | 36.5376 | 36.5047 | 33.2839 | 94.8216 | 95.2538 | 94.2318
2022-09-08 05:30 | 7:40 | 22.7381 | 24.495 | 27.5621 | 36.0286 | 34.3675 | 34.1312 | 34.7051 | 35.5842 | 36.5876 | 37.6026 | 37.0029 | 38.1877 | 34.2222 | 34.248 | 34.1419 | 35.1655 | 34.8572 | 35.4627 | 36.2228 | 36.4983 | 30.1936 | 29.79 | 94.0303 | 34.6684 | 32.8449 | 34.8138 | 32.9787 | 33.0022 | 33.2957 | 34.5666 | 34.1667 | 33.957 | 37.1697 | 36.1691 | 33.2955 | 34.4221 | 36.1647 | 36.5019 | 37.2943 | 36.1529 | 32.9551 | 32.3742 | 34.1849 | 34.4983 | 32.7171 | 34.2811 | 34.378 | 34.3354 | 34.2895 | 34.2728 | 34.2868 | 33.8859 | 34.3067 | 36.1129 | 34.9782 | 36.5415 | 36.4894 | 33.2987 | 94.581 | 94.9667 | 94.1147
2022-09-08 05:30 | 7:40 | 21.7563 | 24.433 | 26.7326 | 35.8921 | 34.3641 | 34.1316 | 34.7101 | 35.571 | 36.6084 | 37.5876 | 36.9998 | 38.2088 | 34.2036 | 34.2409 | 34.1502 | 35.1761 | 34.8758 | 35.4493 | 36.2112 | 36.5069 | 30.4902 | 30.0208 | 93.9102 | 34.7058 | 32.8646 | 34.8024 | 32.9724 | 32.9935 | 33.2986 | 34.5648 | 34.1861 | 33.9782 | 37.1431 | 36.1649 | 33.2882 | 34.4246 | 36.1746 | 36.5182 | 37.3009 | 36.1503 | 32.9649 | 32.3889 | 34.1927 | 34.5108 | 32.7061 | 34.2745 | 34.3996 | 34.3349 | 34.3012 | 34.2819 | 34.2945 | 33.8862 | 34.2895 | 36.0919 | 34.9487 | 36.537 | 36.5191 | 33.296 | 94.4595 | 94.7485 | 93.9374
2022-09-08 05:30 | 7:40 | 21.3631 | 24.2097 | 26.2072 | 35.842 | 34.3676 | 34.1394 | 34.7188 | 35.5668 | 36.5852 | 37.5883 | 37.0063 | 38.1947 | 34.2465 | 34.2316 | 34.1465 | 35.1823 | 34.8704 | 35.456 | 36.2037 | 36.507 | 30.7223 | 30.2228 | 93.8724 | 34.7741 | 32.8468 | 34.815 | 32.961 | 32.9894 | 33.31 | 34.5608 | 34.1753 | 33.9662 | 37.1609 | 36.1872 | 33.313 | 34.4239 | 36.1691 | 36.501 | 37.2881 | 36.1775 | 32.9807 | 32.3829 | 34.1933 | 34.4972 | 32.7305 | 34.2622 | 34.3981 | 34.3052 | 34.3086 | 34.2796 | 34.2866 | 33.8728 | 34.3012 | 36.0932 | 34.9616 | 36.5187 | 36.4938 | 33.2905 | 94.3132 | 94.6399 | 93.8871
2022-09-08 05:30 | 7:40 | 21.1978 | 23.9316 | 25.8754 | 35.7956 | 34.3522 | 34.1258 | 34.6895 | 35.5871 | 36.5934 | 37.5845 | 37.0151 | 38.1915 | 34.2557 | 34.232 | 34.1467 | 35.1694 | 34.8492 | 35.4618 | 36.1834 | 36.504 | 30.9131 | 30.3792 | 93.8288 | 34.8019 | 32.8687 | 34.807 | 32.9612 | 33.0086 | 33.2942 | 34.5479 | 34.1784 | 33.9679 | 37.1449 | 36.1691 | 33.2778 | 34.4267 | 36.1649 | 36.4941 | 37.3012 | 36.1647 | 32.9883 | 32.3803 | 34.2179 | 34.5114 | 32.7278 | 34.27 | 34.3971 | 34.3244 | 34.3017 | 34.3035 | 34.2951 | 33.899 | 34.3086 | 36.0857 | 34.9468 | 36.5401 | 36.5033 | 33.2795 | 94.2213 | 94.5426 | 93.8219
2022-09-08 05:30 | 7:40 | 20.9001 | 23.607 | 25.5736 | 35.7099 | 34.3597 | 34.1159 | 34.688 | 35.5927 | 36.5741 | 37.5713 | 37.0005 | 38.1782 | 34.2392 | 34.2174 | 34.1385 | 35.1477 | 34.8752 | 35.4534 | 36.173 | 36.4737 | 31.0483 | 30.5083 | 93.8036 | 34.7816 | 32.863 | 34.8432 | 32.9551 | 32.9882 | 33.2955 | 34.5444 | 34.1691 | 33.9505 | 37.1588 | 36.1763 | 33.3038 | 34.4272 | 36.1872 | 36.4942 | 37.2731 | 36.1746 | 32.9936 | 32.3697 | 34.2047 | 34.5111 | 32.7453 | 34.2511 | 34.3947 | 34.3082 | 34.2989 | 34.3005 | 34.288 | 33.8725 | 34.3017 | 36.1032 | 34.9639 | 36.542 | 36.5168 | 33.2839 | 94.1401 | 94.463 | 93.8131
2022-09-08 05:31 | 7:41 | 20.6239 | 23.2622 | 25.2779 | 35.6733 | 34.3612 | 34.1168 | 34.7103 | 35.5619 | 36.5917 | 37.5665 | 36.999 | 38.1965 | 34.2272 | 34.225 | 34.1424 | 35.1692 | 34.8625 | 35.4345 | 36.174 | 36.4912 | 31.1853 | 30.6147 | 93.7964 | 34.7986 | 32.8591 | 34.8314 | 32.9649 | 32.9865 | 33.2882 | 34.5607 | 34.1698 | 33.9708 | 37.1483 | 36.1712 | 33.2899 | 34.4263 | 36.1691 | 36.5083 | 37.301 | 36.1691 | 32.9747 | 32.3968 | 34.2072 | 34.511 | 32.7458 | 34.2481 | 34.3805 | 34.3131 | 34.3104 | 34.302 | 34.2805 | 33.8834 | 34.2989 | 36.0925 | 34.9812 | 36.5347 | 36.5176 | 33.2745 | 94.089 | 94.4045 | 93.7792
2022-09-08 05:31 | 7:41 | 20.2898 | 22.8494 | 24.9978 | 35.5392 | 34.3588 | 34.1018 | 34.6857 | 35.5751 | 36.5906 | 37.5765 | 36.9948 | 38.1761 | 34.2286 | 34.2447 | 34.1346 | 35.1783 | 34.8797 | 35.4152 | 36.1863 | 36.4743 | 31.2609 | 30.7075 | 93.7332 | 34.7803 | 32.8578 | 34.8013 | 32.9807 | 33.0023 | 33.313 | 34.5511 | 34.1736 | 33.9582 | 37.1441 | 36.174 | 33.2929 | 34.4237 | 36.1763 | 36.5038 | 37.2726 | 36.1649 | 33.0003 | 32.4037 | 34.2156 | 34.5118 | 32.7519 | 34.2468 | 34.374 | 34.2898 | 34.3215 | 34.293 | 34.2697 | 33.8903 | 34.3104 | 36.0919 | 34.9603 | 36.5288 | 36.4887 | 33.2629 | 94.0504 | 94.3097 | 93.7335
2022-09-08 05:31 | 7:41 | 20.1432 | 22.4947 | 24.712 | 35.6142 | 34.348 | 34.1221 | 34.6845 | 35.5709 | 36.5968 | 37.5843 | 36.9868 | 38.178 | 34.2417 | 34.2409 | 34.1373 | 35.1769 | 34.8642 | 35.4361 | 36.1538 | 36.4851 | 31.3689 | 30.7825 | 93.7544 | 34.8521 | 32.8513 | 34.8208 | 32.9883 | 32.988 | 33.2778 | 34.5524 | 34.1754 | 33.9603 | 37.1502 | 36.1774 | 33.2861 | 34.4288 | 36.1712 | 36.4951 | 37.2791 | 36.1872 | 32.9752 | 32.4213 | 34.2029 | 34.5121 | 32.7814 | 34.261 | 34.3944 | 34.3036 | 34.3095 | 34.2838 | 34.2489 | 33.8896 | 34.3215 | 36.1111 | 34.987 | 36.537 | 36.4887 | 33.2717 | 93.963 | 94.2354 | 93.7318
2022-09-08 05:31 | 7:41 | 19.702 | 22.1316 | 24.4559 | 35.4979 | 34.3584 | 34.1095 | 34.687 | 35.57 | 36.5831 | 37.573 | 37.0036 | 38.1849 | 34.2426 | 34.2475 | 34.1471 | 35.1659 | 34.8666 | 35.4365 | 36.1872 | 36.4971 | 31.4484 | 30.8189 | 93.6883 | 34.8104 | 32.8601 | 34.8159 | 32.9936 | 32.9851 | 33.3038 | 34.5552 | 34.1756 | 33.954 | 37.1561 | 36.2061 | 33.2971 | 34.4274 | 36.174 | 36.5181 | 37.2888 | 36.1691 | 32.9926 | 32.3947 | 34.233 | 34.5125 | 32.7645 | 34.2557 | 34.3735 | 34.3063 | 34.3237 | 34.3006 | 34.2805 | 33.8949 | 34.3095 | 36.0904 | 34.9431 | 36.5363 | 36.5052 | 33.277 | 93.8714 | 94.1776 | 93.6464
2022-09-08 05:31 | 7:41 | 19.4235 | 21.8071 | 24.2154 | 35.6482 | 34.3529 | 34.1154 | 34.6856 | 35.5624 | 36.6014 | 37.5781 | 37.0119 | 38.1904 | 34.2332 | 34.2458 | 34.1319 | 35.1767 | 34.8735 | 35.4321 | 36.1756 | 36.4649 | 31.491 | 30.9042 | 93.647 | 34.7978 | 32.8738 | 34.8261 | 32.9747 | 32.9869 | 33.2899 | 34.5662 | 34.1817 | 33.9594 | 37.1534 | 36.1895 | 33.2893 | 34.4057 | 36.1774 | 36.5106 | 37.2816 | 36.1763 | 32.988 | 32.4055 | 34.229 | 34.5199 | 32.7798 | 34.2413 | 34.3824 | 34.3027 | 34.3314 | 34.2917 | 34.2768 | 33.8941 | 34.3237 | 36.0826 | 34.9648 | 36.539 | 36.5075 | 33.273 | 93.8283 | 94.1154 | 93.6327
2022-09-08 05:31 | 7:41 | 19.1391 | 21.4689 | 23.9235 | 35.4594 | 34.3391 | 34.0916 | 34.6785 | 35.5654 | 36.5815 | 37.5726 | 37.0271 | 38.1871 | 34.2406 | 34.2386 | 34.1347 | 35.1687 | 34.8828 | 35.4359 | 36.1705 | 36.4736 | 31.5584 | 30.9534 | 93.6251 | 34.8817 | 32.8639 | 34.8325 | 33.0003 | 32.9933 | 33.2929 | 34.5594 | 34.1939 | 33.9601 | 37.1546 | 36.1773 | 33.2965 | 34.4153 | 36.2061 | 36.5158 | 37.299 | 36.1712 | 32.9954 | 32.4092 | 34.2127 | 34.5118 | 32.7885 | 34.2545 | 34.3984 | 34.2816 | 34.3381 | 34.2787 | 34.2759 | 33.8984 | 34.3314 | 36.0936 | 34.9676 | 36.5408 | 36.5106 | 33.2749 | 93.8294 | 94.0619 | 93.653
2022-09-08 05:32 | 7:41 | 18.8878 | 21.1806 | 23.6661 | 35.4373 | 34.3411 | 34.1056 | 34.6745 | 35.5546 | 36.5982 | 37.578 | 37.0093 | 38.1913 | 34.2448 | 34.2449 | 34.1358 | 35.1758 | 34.863 | 35.4405 | 36.1692 | 36.4785 | 31.6058 | 30.9889 | 93.6118 | 34.8955 | 32.8574 | 34.8362 | 32.9752 | 33.0021 | 33.2861 | 34.5686 | 34.184 | 33.9583 | 37.1593 | 36.1828 | 33.2955 | 34.4248 | 36.1895 | 36.5166 | 37.2731 | 36.174 | 32.9986 | 32.415 | 34.2439 | 34.5116 | 32.7969 | 34.2747 | 34.3694 | 34.2981 | 34.3392 | 34.2874 | 34.2773 | 33.8964 | 34.3381 | 36.1007 | 34.9649 | 36.5566 | 36.513 | 33.2693 | 93.7758 | 93.9153 | 93.6599
2022-09-08 05:32 | 7:42 | 18.5999 | 20.8788 | 23.4526 | 35.2983 | 34.3517 | 34.0908 | 34.6761 | 35.5739 | 36.6089 | 37.5663 | 37.0014 | 38.1777 | 34.2515 | 34.2635 | 34.1221 | 35.166 | 34.8718 | 35.453 | 36.1734 | 36.4827 | 31.6527 | 31.0312 | 93.538 | 34.8152 | 32.8631 | 34.8299 | 32.9926 | 32.9954 | 33.2971 | 34.5416 | 34.1937 | 33.9706 | 37.15 | 36.1763 | 33.3143 | 34.3999 | 36.1773 | 36.5222 | 37.2769 | 36.1774 | 32.9866 | 32.429 | 34.2432 | 34.5364 | 32.8003 | 34.2582 | 34.3869 | 34.2981 | 34.3358 | 34.2823 | 34.2559 | 33.9008 | 34.3392 | 36.1001 | 34.9717 | 36.5434 | 36.514 | 33.2929 | 93.6758 | 93.7758 | 93.6116
2022-09-08 05:32 | 7:42 | 18.3481 | 20.5507 | 23.1422 | 35.2696 | 34.3372 | 34.093 | 34.6516 | 35.5578 | 36.6111 | 37.5757 | 37.0047 | 38.2104 | 34.2489 | 34.24 | 34.1295 | 35.1862 | 34.8826 | 35.4237 | 36.1539 | 36.486 | 31.6947 | 31.0532 | 93.33 | 34.862 | 32.8686 | 34.847 | 32.988 | 33.0023 | 33.2893 | 34.5681 | 34.188 | 33.9603 | 37.1526 | 36.1947 | 33.3068 | 34.4145 | 36.1828 | 36.493 | 37.2989 | 36.2061 | 32.9971 | 32.4351 | 34.2358 | 34.5459 | 32.8257 | 34.2571 | 34.3765 | 34.2827 | 34.3331 | 34.3038 | 34.2679 | 33.9175 | 34.3358 | 36.0968 | 34.9707 | 36.5478 | 36.5216 | 33.2556 | 93.5759 | 93.636 | 93.5521
2022-09-08 05:32 | 7:42 | 18.1055 | 20.2757 | 22.8833 | 35.1811 | 34.3392 | 34.1024 | 34.683 | 35.5563 | 36.6148 | 37.5643 | 37.0091 | 38.1864 | 34.2584 | 34.2494 | 34.1291 | 35.1775 | 34.8835 | 35.4403 | 36.1445 | 36.4849 | 31.7045 | 31.0825 | 93.3248 | 34.8584 | 32.8424 | 34.8464 | 32.9954 | 33.0067 | 33.2965 | 34.55 | 34.1865 | 33.9752 | 37.1723 | 36.1785 | 33.2916 | 34.417 | 36.1763 | 36.4889 | 37.2875 | 36.1895 | 32.988 | 32.4415 | 34.2438 | 34.5369 | 32.8079 | 34.2629 | 34.3905 | 34.2957 | 34.3338 | 34.3108 | 34.2634 | 33.902 | 34.3331 | 36.0997 | 34.9635 | 36.524 | 36.5162 | 33.2815 | 93.4502 | 93.5519 | 93.4789
2022-09-08 05:32 | 7:42 | 17.8939 | 20.0154 | 22.653 | 35.1752 | 34.3167 | 34.1022 | 34.661 | 35.5593 | 36.5934 | 37.5732 | 37.0107 | 38.1938 | 34.2592 | 34.2584 | 34.1128 | 35.1694 | 34.8861 | 35.4213 | 36.1539 | 36.4757 | 31.7716 | 31.1107 | 93.2516 | 34.8358 | 32.867 | 34.8411 | 32.9986 | 33.0005 | 33.2955 | 34.5543 | 34.1927 | 33.9694 | 37.1611 | 36.207 | 33.3041 | 34.4228 | 36.1947 | 36.5162 | 37.2829 | 36.1773 | 32.9998 | 32.4402 | 34.2493 | 34.5208 | 32.8376 | 34.2689 | 34.3809 | 34.2769 | 34.3394 | 34.307 | 34.2433 | 33.9158 | 34.3338 | 36.0976 | 34.9635 | 36.5322 | 36.5293 | 33.282 | 93.333 | 93.4015 | 93.3782
2022-09-08 05:32 | 7:42 | 17.6283 | 19.7458 | 22.4063 | 35.134 | 34.329 | 34.0926 | 34.6488 | 35.5694 | 36.5972 | 37.5767 | 37.011 | 38.2102 | 34.2644 | 34.2456 | 34.136 | 35.1713 | 34.8812 | 35.4389 | 36.1555 | 36.4614 | 31.8005 | 31.1473 | 93.0801 | 34.8741 | 32.8727 | 34.8409 | 32.9866 | 33.0046 | 33.3143 | 34.5543 | 34.1789 | 33.9658 | 37.158 | 36.2117 | 33.3052 | 34.4039 | 36.1785 | 36.5093 | 37.276 | 36.1828 | 33.0168 | 32.4545 | 34.2505 | 34.5567 | 32.827 | 34.2512 | 34.3786 | 34.2938 | 34.3469 | 34.3032 | 34.2467 | 33.9058 | 34.3394 | 36.1054 | 34.9801 | 36.5488 | 36.5256 | 33.3019 | 93.2241 | 93.3115 | 93.2878
2022-09-08 05:33 | 7:43 | 17.5238 | 19.4702 | 22.1478 | 35.0953 | 34.3248 | 34.114 | 34.6511 | 35.5724 | 36.587 | 37.5877 | 37.0091 | 38.1968 | 34.2636 | 34.2572 | 34.118 | 35.1865 | 34.8946 | 35.4332 | 36.1452 | 36.4744 | 31.8194 | 31.1645 | 93.0059 | 34.9325 | 32.8615 | 34.8439 | 32.9971 | 32.9967 | 33.3068 | 34.5574 | 34.1868 | 33.977 | 37.1529 | 36.1779 | 33.3078 | 34.4249 | 36.207 | 36.5041 | 37.2791 | 36.1763 | 32.9919 | 32.4608 | 34.2527 | 34.5615 | 32.8391 | 34.28 | 34.3724 | 34.2731 | 34.3445 | 34.2988 | 34.2441 | 33.8964 | 34.3469 | 36.1066 | 34.9785 | 36.5399 | 36.51 | 33.2866 | 93.1017 | 93.235 | 93.2683
2022-09-08 05:33 | 7:43 | 17.1894 | 19.2227 | 21.9537 | 35.156 | 34.284 | 34.0972 | 34.6345 | 35.554 | 36.5988 | 37.565 | 37.0172 | 38.2021 | 34.249 | 34.2534 | 34.1292 | 35.1537 | 34.8721 | 35.4367 | 36.1445 | 36.472 | 31.85 | 31.1823 | 92.9783 | 34.8418 | 32.8604 | 34.8351 | 32.988 | 32.9842 | 33.2916 | 34.5486 | 34.1718 | 33.9693 | 37.1679 | 36.2027 | 33.2829 | 34.4361 | 36.2117 | 36.4961 | 37.2747 | 36.1947 | 33.0033 | 32.469 | 34.2805 | 34.5707 | 32.8647 | 34.251 | 34.3617 | 34.2923 | 34.3536 | 34.2945 | 34.2525 | 33.9283 | 34.3445 | 36.1082 | 34.9893 | 36.533 | 36.5198 | 33.2794 | 92.943 | 93.0914 | 93.1213
2022-09-08 05:33 | 7:43 | 17.0113 | 19.0022 | 21.7239 | 35.1155 | 34.3202 | 34.0978 | 34.6389 | 35.5778 | 36.5911 | 37.5578 | 37.0371 | 38.2048 | 34.2604 | 34.2681 | 34.111 | 35.1728 | 34.8897 | 35.4154 | 36.1473 | 36.4938 | 31.8559 | 31.2193 | 92.9625 | 34.8659 | 32.8622 | 34.8543 | 32.9998 | 33.0189 | 33.3041 | 34.5568 | 34.1904 | 33.9845 | 37.1425 | 36.2005 | 33.3012 | 34.4233 | 36.1779 | 36.5237 | 37.2888 | 36.1785 | 33.0012 | 32.4786 | 34.2673 | 34.5747 | 32.8492 | 34.2677 | 34.3917 | 34.2772 | 34.3582 | 34.3044 | 34.2545 | 33.9078 | 34.3536 | 36.1158 | 34.9945 | 36.5333 | 36.5214 | 33.278 | 92.8673 | 93.0316 | 93.0884
2022-09-08 05:33 | 7:43 | 16.7755 | 18.765 | 21.5291 | 35.0155 | 34.3241 | 34.1029 | 34.644 | 35.5668 | 36.5911 | 37.5698 | 37.0222 | 38.2139 | 34.2658 | 34.2498 | 34.1139 | 35.1717 | 34.8871 | 35.4352 | 36.1352 | 36.4607 | 31.8931 | 31.2095 | 92.8479 | 34.9257 | 32.8666 | 34.8634 | 33.0168 | 32.9996 | 33.3052 | 34.5483 | 34.1855 | 33.9568 | 37.1764 | 36.2059 | 33.2808 | 34.4189 | 36.2027 | 36.5062 | 37.3042 | 36.207 | 33.0008 | 32.4693 | 34.2913 | 34.5782 | 32.8593 | 34.2712 | 34.3685 | 34.2701 | 34.3729 | 34.3057 | 34.2448 | 33.9238 | 34.3582 | 36.1362 | 34.9871 | 36.5412 | 36.5157 | 33.2992 | 92.7573 | 92.9418 | 93.0506
2022-09-08 05:33 | 7:43 | 16.551 | 18.513 | 21.3015 | 34.8852 | 34.324 | 34.0896 | 34.6276 | 35.5476 | 36.5829 | 37.57 | 37.0238 | 38.2206 | 34.2647 | 34.2512 | 34.1247 | 35.1636 | 34.8716 | 35.4274 | 36.1406 | 36.4681 | 31.9123 | 31.2343 | 92.6382 | 34.9452 | 32.8706 | 34.8501 | 32.9919 | 33.007 | 33.3078 | 34.5613 | 34.182 | 33.9642 | 37.1554 | 36.2035 | 33.3012 | 34.4337 | 36.2005 | 36.5249 | 37.2888 | 36.2117 | 33.0001 | 32.4745 | 34.2904 | 34.5602 | 32.8763 | 34.2596 | 34.3758 | 34.2775 | 34.3713 | 34.2996 | 34.2525 | 33.928 | 34.3729 | 36.1244 | 34.9851 | 36.5524 | 36.5212 | 33.298 | 92.6755 | 92.7521 | 92.9619
2022-09-08 05:33 | 7:43 | 16.3731 | 18.2884 | 21.1195 | 34.8637 | 34.3012 | 34.1031 | 34.6272 | 35.5615 | 36.6001 | 37.567 | 37.0117 | 38.2154 | 34.2524 | 34.2606 | 34.1272 | 35.1737 | 34.8856 | 35.4216 | 36.1591 | 36.4747 | 31.9246 | 31.2613 | 92.479 | 34.9233 | 32.877 | 34.8531 | 33.0033 | 32.9926 | 33.2829 | 34.5575 | 34.1911 | 33.9763 | 37.1762 | 36.196 | 33.2938 | 34.4085 | 36.2059 | 36.5097 | 37.2933 | 36.1779 | 33.0193 | 32.464 | 34.2984 | 34.5789 | 32.8852 | 34.265 | 34.3758 | 34.2698 | 34.3734 | 34.305 | 34.2548 | 33.9223 | 34.3713 | 36.1243 | 34.9692 | 36.5353 | 36.5174 | 33.2791 | 92.5298 | 92.6278 | 92.7913
2022-09-08 05:34 | 7:44 | 16.1768 | 18.0716 | 20.8299 | 34.8531 | 34.314 | 34.0828 | 34.6285 | 35.5562 | 36.6001 | 37.5685 | 37.0219 | 38.2145 | 34.2657 | 34.2593 | 34.1291 | 35.1691 | 34.8812 | 35.4354 | 36.1315 | 36.4819 | 31.9491 | 31.2908 | 92.4867 | 34.9767 | 32.8664 | 34.8751 | 33.0012 | 32.9958 | 33.3012 | 34.5444 | 34.1854 | 33.977 | 37.1692 | 36.2022 | 33.3156 | 34.4173 | 36.2035 | 36.5019 | 37.2959 | 36.2027 | 33.0092 | 32.4776 | 34.2972 | 34.5669 | 32.8863 | 34.2678 | 34.3582 | 34.2889 | 34.3648 | 34.3183 | 34.2212 | 33.9182 | 34.3734 | 36.1032 | 34.9658 | 36.5397 | 36.531 | 33.3165 | 92.4701 | 92.5324 | 92.7932
2022-09-08 05:34 | 7:44 | 16.0195 | 17.883 | 20.7057 | 34.8239 | 34.2858 | 34.0845 | 34.642 | 35.5561 | 36.5843 | 37.5576 | 37.0159 | 38.2172 | 34.2619 | 34.2701 | 34.1391 | 35.1755 | 34.8855 | 35.4396 | 36.1256 | 36.4785 | 31.969 | 31.2789 | 92.4027 | 34.8832 | 32.8854 | 34.8811 | 33.0008 | 33.0019 | 33.2808 | 34.5523 | 34.1945 | 33.9848 | 37.1794 | 36.199 | 33.3206 | 34.4168 | 36.196 | 36.5169 | 37.313 | 36.2005 | 33.0017 | 32.4881 | 34.2878 | 34.5991 | 32.898 | 34.2611 | 34.3744 | 34.2827 | 34.3543 | 34.3151 | 34.2496 | 33.9367 | 34.3648 | 36.1283 | 34.9825 | 36.5492 | 36.5227 | 33.299 | 92.3202 | 92.4328 | 92.7016
2022-09-08 05:34 | 7:44 | 15.7769 | 17.6655 | 20.4524 | 34.8683 | 34.3149 | 34.0823 | 34.6336 | 35.5475 | 36.6065 | 37.5679 | 37.0213 | 38.2041 | 34.2921 | 34.2762 | 34.1188 | 35.1784 | 34.9027 | 35.4372 | 36.1335 | 36.4853 | 31.9942 | 31.2959 | 92.288 | 34.9008 | 32.8834 | 34.8566 | 33.0001 | 33.0093 | 33.3012 | 34.558 | 34.192 | 33.9789 | 37.1731 | 36.2099 | 33.2996 | 34.4179 | 36.2022 | 36.5131 | 37.2824 | 36.2059 | 33.0022 | 32.4932 | 34.3049 | 34.6117 | 32.8811 | 34.2842 | 34.3915 | 34.2647 | 34.3762 | 34.3258 | 34.248 | 33.9251 | 34.3543 | 36.1114 | 34.9876 | 36.5457 | 36.5038 | 33.2836 | 92.1753 | 92.248 | 92.5897
2022-09-08 05:34 | 7:44 | 15.6534 | 17.465 | 20.2246 | 34.7291 | 34.2881 | 34.093 | 34.6181 | 35.5639 | 36.5952 | 37.5585 | 37.0409 | 38.2086 | 34.2835 | 34.2689 | 34.1324 | 35.1706 | 34.9036 | 35.4235 | 36.1341 | 36.4654 | 32.0191 | 31.2964 | 92.2626 | 34.8914 | 32.88 | 34.8509 | 33.0193 | 33.0061 | 33.2938 | 34.5661 | 34.1928 | 33.9758 | 37.185 | 36.2086 | 33.2968 | 34.4014 | 36.199 | 36.5212 | 37.3092 | 36.2035 | 33.0226 | 32.5136 | 34.3166 | 34.6096 | 32.8967 | 34.2468 | 34.355 | 34.2681 | 34.3655 | 34.3361 | 34.2409 | 33.9563 | 34.3762 | 36.1153 | 34.9718 | 36.5523 | 36.5229 | 33.307 | 92.0391 | 92.0688 | 92.4765
2022-09-08 05:34 | 7:44 | 15.4767 | 17.2788 | 20.0387 | 34.7504 | 34.2811 | 34.0934 | 34.5895 | 35.5518 | 36.6034 | 37.5446 | 37.0233 | 38.214 | 34.2763 | 34.2475 | 34.1321 | 35.1672 | 34.8849 | 35.4237 | 36.1362 | 36.4794 | 32.0478 | 31.3324 | 92.2262 | 34.8941 | 32.8791 | 34.8755 | 33.0092 | 32.9952 | 33.3156 | 34.5522 | 34.1965 | 33.9968 | 37.1654 | 36.2045 | 33.3201 | 34.4074 | 36.2099 | 36.4961 | 37.3019 | 36.196 | 33.014 | 32.5022 | 34.3103 | 34.6085 | 32.9191 | 34.2913 | 34.3686 | 34.283 | 34.3598 | 34.3346 | 34.2316 | 33.9566 | 34.3655 | 36.1195 | 34.9586 | 36.5543 | 36.5184 | 33.3092 | 91.9715 | 91.9604 | 92.4204
2022-09-08 05:34 | 7:44 | 15.3079 | 17.1098 | 19.9176 | 34.7568 | 34.2971 | 34.0733 | 34.6038 | 35.5443 | 36.6123 | 37.5585 | 37.0216 | 38.2132 | 34.2662 | 34.249 | 34.1324 | 35.1553 | 34.9022 | 35.427 | 36.1281 | 36.4634 | 32.069 | 31.328 | 92.1223 | 35.0015 | 32.8505 | 34.8732 | 33.0017 | 33.0028 | 33.3206 | 34.5468 | 34.1879 | 33.9749 | 37.1678 | 36.2164 | 33.3116 | 34.409 | 36.2086 | 36.5159 | 37.3153 | 36.2022 | 33.0024 | 32.5067 | 34.3208 | 34.6223 | 32.907 | 34.2656 | 34.3723 | 34.2721 | 34.3743 | 34.3449 | 34.232 | 33.9311 | 34.3598 | 36.1311 | 34.9778 | 36.5504 | 36.5343 | 33.303 | 91.8462 | 91.8528 | 92.3585
2022-09-08 05:35 | 7:44 | 15.1264 | 16.9152 | 19.7184 | 34.6544 | 34.2868 | 34.0742 | 34.5935 | 35.5523 | 36.602 | 37.5572 | 37.0179 | 38.1983 | 34.2883 | 34.2628 | 34.1552 | 35.1801 | 34.8836 | 35.4 | 36.1206 | 36.481 | 32.0611 | 31.3372 | 92.033 | 34.9254 | 32.8747 | 34.8517 | 33.0022 | 32.9924 | 33.2996 | 34.5595 | 34.1909 | 33.9786 | 37.1644 | 36.2062 | 33.3081 | 34.4171 | 36.2045 | 36.5164 | 37.3146 | 36.199 | 33.0194 | 32.5216 | 34.3369 | 34.6137 | 32.9266 | 34.2704 | 34.3692 | 34.2586 | 34.3795 | 34.3281 | 34.2174 | 33.9455 | 34.3743 | 36.1346 | 34.9479 | 36.5322 | 36.5364 | 33.3248 | 91.7896 | 91.8573 | 92.3514
2022-09-08 05:35 | 7:45 | 15.0262 | 16.7549 | 19.5644 | 34.6283 | 34.2945 | 34.0789 | 34.5994 | 35.5472 | 36.6136 | 37.5585 | 37.0187 | 38.216 | 34.2702 | 34.2939 | 34.1316 | 35.181 | 34.879 | 35.4241 | 36.1487 | 36.4778 | 32.0952 | 31.3577 | 92.0722 | 35.0044 | 32.8626 | 34.871 | 33.0226 | 33.0104 | 33.2968 | 34.5742 | 34.1719 | 33.9772 | 37.1658 | 36.1979 | 33.2935 | 34.4076 | 36.2164 | 36.5197 | 37.297 | 36.2099 | 33.0057 | 32.5181 | 34.3315 | 34.6189 | 32.9347 | 34.2802 | 34.3657 | 34.2583 | 34.3848 | 34.3266 | 34.225 | 33.9258 | 34.3795 | 36.1417 | 34.9794 | 36.5486 | 36.5353 | 33.3185 | 91.8635 | 91.9423 | 92.4251
2022-09-08 05:35 | 7:45 | 14.7966 | 16.5753 | 19.4096 | 34.7154 | 34.2866 | 34.0814 | 34.6022 | 35.5378 | 36.5963 | 37.5564 | 37.0334 | 38.2019 | 34.2901 | 34.2703 | 34.1299 | 35.1728 | 34.887 | 35.4261 | 36.1258 | 36.4999 | 32.1156 | 31.3653 | 92.0419 | 34.8918 | 32.8685 | 34.886 | 33.014 | 33.0027 | 33.3201 | 34.5435 | 34.1908 | 33.9785 | 37.1656 | 36.2044 | 33.3129 | 34.4129 | 36.2062 | 36.5206 | 37.2946 | 36.2086 | 33.0136 | 32.5256 | 34.3387 | 34.6442 | 32.9312 | 34.2751 | 34.3557 | 34.2704 | 34.3667 | 34.3258 | 34.2447 | 33.9433 | 34.3848 | 36.1428 | 34.9852 | 36.558 | 36.5365 | 33.3058 | 91.8498 | 91.9691 | 92.4806
2022-09-08 05:35 | 7:45 | 14.6644 | 16.4604 | 19.2237 | 34.5667 | 34.2951 | 34.076 | 34.5778 | 35.5502 | 36.598 | 37.5641 | 37.0235 | 38.2127 | 34.2698 | 34.286 | 34.1255 | 35.1729 | 34.8618 | 35.428 | 36.1191 | 36.4623 | 32.1249 | 31.3722 | 92.1554 | 34.9974 | 32.865 | 34.8728 | 33.0024 | 33.0224 | 33.3116 | 34.5659 | 34.1765 | 33.9796 | 37.1777 | 36.1983 | 33.305 | 34.4073 | 36.1979 | 36.5177 | 37.322 | 36.2045 | 32.9952 | 32.5345 | 34.3488 | 34.6341 | 32.9397 | 34.2851 | 34.3825 | 34.2681 | 34.3972 | 34.3246 | 34.2409 | 33.955 | 34.3667 | 36.1335 | 34.9734 | 36.5402 | 36.5355 | 33.3365 | 92.0073 | 92.0683 | 92.5878
2022-09-08 05:35 | 7:45 | 14.6112 | 16.2672 | 19.0783 | 34.4654 | 34.288 | 34.0626 | 34.5823 | 35.549 | 36.5902 | 37.5534 | 37.0105 | 38.2121 | 34.2599 | 34.2558 | 34.1306 | 35.1643 | 34.8873 | 35.4323 | 36.127 | 36.4727 | 32.1316 | 31.3795 | 92.3227 | 34.9677 | 32.8999 | 34.8784 | 33.0194 | 33.0135 | 33.3081 | 34.5574 | 34.1905 | 33.989 | 37.1741 | 36.2058 | 33.3021 | 34.4016 | 36.2044 | 36.5112 | 37.2838 | 36.2164 | 32.9955 | 32.5386 | 34.3591 | 34.6395 | 32.9429 | 34.2754 | 34.3747 | 34.2561 | 34.376 | 34.3525 | 34.2475 | 33.9535 | 34.3972 | 36.1429 | 34.9516 | 36.5397 | 36.5268 | 33.3237 | 92.1317 | 92.2266 | 92.6272
2022-09-08 05:35 | 7:45 | 14.5158 | 16.1447 | 18.9175 | 34.413 | 34.2805 | 34.05 | 34.5739 | 35.535 | 36.5989 | 37.5473 | 37.0111 | 38.2016 | 34.2579 | 34.2534 | 34.1101 | 35.1586 | 34.8934 | 35.4156 | 36.1058 | 36.4861 | 32.1491 | 31.4041 | 92.2498 | 35.0361 | 32.8945 | 34.8563 | 33.0057 | 32.9821 | 33.2935 | 34.5557 | 34.1805 | 33.9642 | 37.1629 | 36.1997 | 33.3001 | 34.3901 | 36.1983 | 36.5301 | 37.2937 | 36.2062 | 33.0092 | 32.5214 | 34.3609 | 34.6494 | 32.9485 | 34.2948 | 34.3441 | 34.2619 | 34.3885 | 34.3515 | 34.2458 | 33.9371 | 34.376 | 36.1228 | 34.959 | 36.548 | 36.5401 | 33.3135 | 92.2062 | 92.3058 | 92.6523
2022-09-08 05:36 | 7:46 | 14.2223 | 15.9388 | 18.751 | 34.3796 | 34.2697 | 34.068 | 34.5582 | 35.5484 | 36.582 | 37.5578 | 37.0192 | 38.2043 | 34.2835 | 34.2879 | 34.131 | 35.1494 | 34.8741 | 35.4259 | 36.1147 | 36.4802 | 32.1495 | 31.3983 | 92.4029 | 34.9806 | 32.8975 | 34.8724 | 33.0136 | 32.9881 | 33.3129 | 34.5547 | 34.1727 | 33.9864 | 37.1738 | 36.2037 | 33.293 | 34.3943 | 36.2058 | 36.511 | 37.2938 | 36.1979 | 32.996 | 32.5479 | 34.3512 | 34.6521 | 32.9586 | 34.2815 | 34.3611 | 34.2527 | 34.3854 | 34.349 | 34.2386 | 33.9681 | 34.3885 | 36.1334 | 34.9648 | 36.5655 | 36.5284 | 33.3154 | 92.3712 | 92.3582 | 92.7227
2022-09-08 05:36 | 7:46 | 14.1044 | 15.8347 | 18.6727 | 34.4106 | 34.2489 | 34.0534 | 34.551 | 35.5446 | 36.5883 | 37.5445 | 37.0098 | 38.2011 | 34.2687 | 34.2669 | 34.1206 | 35.1608 | 34.8801 | 35.4128 | 36.1268 | 36.4988 | 32.1754 | 31.414 | 92.4462 | 34.9674 | 32.871 | 34.8687 | 32.9952 | 32.9918 | 33.305 | 34.5462 | 34.1796 | 33.9716 | 37.1687 | 36.176 | 33.2912 | 34.3915 | 36.1997 | 36.5026 | 37.2944 | 36.2044 | 33.0152 | 32.5487 | 34.3495 | 34.6327 | 32.9509 | 34.2925 | 34.363 | 34.2639 | 34.3899 | 34.3519 | 34.2449 | 33.9523 | 34.3854 | 36.1364 | 34.9613 | 36.5523 | 36.5245 | 33.3315 | 92.4586 | 92.5235 | 92.7912
2022-09-08 05:36 | 7:46 | 14.1092 | 15.6997 | 18.5533 | 34.3846 | 34.2805 | 34.0415 | 34.5481 | 35.5192 | 36.611 | 37.543 | 37.0313 | 38.2073 | 34.2935 | 34.2662 | 34.1249 | 35.1624 | 34.8688 | 35.4166 | 36.1023 | 36.4752 | 32.1929 | 31.4057 | 92.6406 | 34.9732 | 32.8951 | 34.8658 | 32.9955 | 32.9913 | 33.3021 | 34.5533 | 34.1683 | 33.9871 | 37.1699 | 36.1945 | 33.3042 | 34.3784 | 36.2037 | 36.5034 | 37.2907 | 36.1983 | 33.0001 | 32.558 | 34.3555 | 34.6272 | 32.9765 | 34.2835 | 34.3513 | 34.2508 | 34.4002 | 34.3619 | 34.2635 | 33.968 | 34.3899 | 36.1398 | 34.96 | 36.5455 | 36.5342 | 33.3474 | 92.6456 | 92.6577 | 92.9088
2022-09-08 05:36 | 7:46 | 13.8856 | 15.5317 | 18.3446 | 34.4688 | 34.2768 | 34.0394 | 34.5334 | 35.5226 | 36.5916 | 37.5501 | 37.0107 | 38.1996 | 34.2831 | 34.275 | 34.1262 | 35.1426 | 34.8713 | 35.4129 | 36.1082 | 36.4774 | 32.1925 | 31.4181 | 92.6547 | 34.9892 | 32.8783 | 34.8665 | 33.0092 | 32.9941 | 33.3001 | 34.552 | 34.1617 | 33.9514 | 37.1652 | 36.2094 | 33.3028 | 34.3788 | 36.176 | 36.4966 | 37.3065 | 36.2058 | 33.0076 | 32.5511 | 34.3712 | 34.6617 | 32.9741 | 34.2959 | 34.3515 | 34.2626 | 34.398 | 34.3367 | 34.24 | 33.9645 | 34.4002 | 36.1452 | 34.9524 | 36.5289 | 36.5244 | 33.3297 | 92.7665 | 92.772 | 93.0321
2022-09-08 05:36 | 7:46 | 13.7276 | 15.3999 | 18.1866 | 34.2278 | 34.2759 | 34.039 | 34.5316 | 35.5307 | 36.6024 | 37.5544 | 37.007 | 38.2056 | 34.2733 | 34.2634 | 34.1199 | 35.1658 | 34.875 | 35.4157 | 36.1064 | 36.4827 | 32.2102 | 31.4124 | 92.7966 | 34.9983 | 32.8977 | 34.8627 | 32.996 | 32.9843 | 33.293 | 34.5483 | 34.1733 | 33.9647 | 37.1655 | 36.1871 | 33.3036 | 34.389 | 36.1945 | 36.5048 | 37.2988 | 36.1997 | 33.01 | 32.5426 | 34.3634 | 34.6499 | 32.9871 | 34.28 | 34.3565 | 34.2634 | 34.3715 | 34.3546 | 34.2494 | 33.9843 | 34.398 | 36.1326 | 34.9505 | 36.5388 | 36.5381 | 33.3418 | 92.8455 | 92.9582 | 93.0872
2022-09-08 05:36 | 7:46 | 13.6088 | 15.2691 | 18.0834 | 34.2609 | 34.2773 | 34.0417 | 34.5271 | 35.5028 | 36.5953 | 37.5562 | 37.0157 | 38.213 | 34.27 | 34.2786 | 34.1136 | 35.1409 | 34.8665 | 35.4126 | 36.0963 | 36.4835 | 32.1997 | 31.4254 | 92.729 | 34.9784 | 32.8846 | 34.8553 | 33.0152 | 33.0046 | 33.2912 | 34.5446 | 34.1675 | 33.9633 | 37.1656 | 36.1895 | 33.2868 | 34.3677 | 36.2094 | 36.4971 | 37.3137 | 36.2037 | 33.0048 | 32.5641 | 34.3667 | 34.6616 | 32.9701 | 34.271 | 34.3451 | 34.2439 | 34.3947 | 34.3545 | 34.2584 | 33.968 | 34.3715 | 36.1369 | 34.9785 | 36.5437 | 36.522 | 33.3286 | 93.0142 | 93.0934 | 93.1286
2022-09-08 05:37 | 7:46 | 13.5007 | 15.1318 | 17.9753 | 34.2308 | 34.2559 | 34.0493 | 34.5371 | 35.5131 | 36.5876 | 37.5476 | 37.0086 | 38.1886 | 34.2664 | 34.2697 | 34.1241 | 35.1542 | 34.8659 | 35.409 | 36.0949 | 36.4874 | 32.2411 | 31.4284 | 92.9369 | 35.0079 | 32.8768 | 34.8757 | 33.0001 | 32.9885 | 33.3042 | 34.5538 | 34.1739 | 33.9504 | 37.166 | 36.1932 | 33.3052 | 34.3609 | 36.1871 | 36.5038 | 37.2944 | 36.176 | 32.9921 | 32.5737 | 34.3701 | 34.651 | 32.9924 | 34.2752 | 34.3516 | 34.2523 | 34.4099 | 34.3722 | 34.2456 | 33.9608 | 34.3947 | 36.1176 | 34.9657 | 36.5382 | 36.5614 | 33.3251 | 93.1566 | 93.1991 | 93.2062
2022-09-08 05:37 | 7:47 | 13.4065 | 15.0107 | 17.8371 | 34.1118 | 34.2679 | 34.0389 | 34.514 | 35.5209 | 36.5831 | 37.5412 | 37.0058 | 38.1876 | 34.2876 | 34.2917 | 34.118 | 35.1468 | 34.8662 | 35.3987 | 36.1047 | 36.476 | 32.2432 | 31.4547 | 93.0394 | 35.0176 | 32.8786 | 34.8588 | 33.0076 | 32.9829 | 33.3028 | 34.5335 | 34.1592 | 33.9709 | 37.1544 | 36.1833 | 33.303 | 34.3815 | 36.1895 | 36.505 | 37.2923 | 36.1945 | 33.0168 | 32.5519 | 34.3874 | 34.6555 | 32.9916 | 34.3047 | 34.3424 | 34.2518 | 34.3943 | 34.3564 | 34.2572 | 33.9713 | 34.4099 | 36.1331 | 34.9721 | 36.5466 | 36.553 | 33.3366 | 93.3074 | 93.3333 | 93.2669
2022-09-08 05:37 | 7:47 | 13.2581 | 14.8915 | 17.6998 | 34.0738 | 34.2634 | 34.0441 | 34.5259 | 35.5253 | 36.5848 | 37.54 | 37.0014 | 38.192 | 34.2728 | 34.2805 | 34.1239 | 35.1525 | 34.8589 | 35.404 | 36.0847 | 36.4792 | 32.2506 | 31.4373 | 93.0063 | 35.0584 | 32.8834 | 34.8644 | 33.01 | 32.9896 | 33.3036 | 34.5429 | 34.1613 | 33.971 | 37.142 | 36.1912 | 33.2895 | 34.372 | 36.1932 | 36.5111 | 37.3085 | 36.2094 | 32.9984 | 32.5794 | 34.358 | 34.678 | 32.9958 | 34.2929 | 34.3396 | 34.2437 | 34.3855 | 34.3626 | 34.2534 | 33.974 | 34.3943 | 36.153 | 34.9606 | 36.5431 | 36.5501 | 33.3424 | 93.3809 | 93.5237 | 93.3227
2022-09-08 05:37 | 7:47 | 13.186 | 14.7733 | 17.5876 | 34.053 | 34.2433 | 34.0207 | 34.5 | 35.5141 | 36.5711 | 37.5594 | 37.0073 | 38.2091 | 34.2819 | 34.2874 | 34.1195 | 35.1612 | 34.8598 | 35.3895 | 36.0973 | 36.4716 | 32.264 | 31.4465 | 93.1021 | 35.0612 | 32.9095 | 34.8721 | 33.0048 | 32.9809 | 33.2868 | 34.5432 | 34.1531 | 33.9713 | 37.1537 | 36.2074 | 33.3103 | 34.3942 | 36.1833 | 36.4962 | 37.3164 | 36.1871 | 33.0105 | 32.5539 | 34.4007 | 34.6653 | 33.0141 | 34.2865 | 34.3479 | 34.2599 | 34.3752 | 34.3826 | 34.2681 | 33.9654 | 34.3855 | 36.1481 | 34.9702 | 36.5587 | 36.5402 | 33.3367 | 93.562 | 93.6388 | 93.4685
2022-09-08 05:37 | 7:47 | 13.0914 | 14.6643 | 17.4983 | 34.0908 | 34.2467 | 34.0311 | 34.4981 | 35.5008 | 36.5907 | 37.5372 | 37.0153 | 38.1915 | 34.2796 | 34.2894 | 34.1093 | 35.148 | 34.8541 | 35.391 | 36.0798 | 36.4767 | 32.2816 | 31.453 | 93.1123 | 35.0104 | 32.8978 | 34.8747 | 32.9921 | 32.974 | 33.3052 | 34.5458 | 34.1558 | 33.947 | 37.156 | 36.1863 | 33.2953 | 34.3699 | 36.1912 | 36.4971 | 37.3257 | 36.1895 | 33.0117 | 32.5676 | 34.3949 | 34.6524 | 32.9981 | 34.2938 | 34.3382 | 34.2711 | 34.391 | 34.3874 | 34.2498 | 33.9735 | 34.3752 | 36.1398 | 34.9513 | 36.5711 | 36.5486 | 33.3472 | 93.727 | 93.7827 | 93.6022
2022-09-08 05:37 | 7:47 | 12.9713 | 14.561 | 17.3596 | 34.0622 | 34.2441 | 34.0187 | 34.5179 | 35.5166 | 36.5918 | 37.5301 | 37.0168 | 38.1866 | 34.3035 | 34.2747 | 34.1061 | 35.144 | 34.8572 | 35.4058 | 36.0827 | 36.4826 | 32.2887 | 31.4843 | 93.318 | 35.0367 | 32.8814 | 34.8647 | 33.0168 | 32.9964 | 33.303 | 34.5554 | 34.165 | 33.9704 | 37.1394 | 36.2101 | 33.3123 | 34.3746 | 36.2074 | 36.5076 | 37.3054 | 36.1932 | 32.9988 | 32.5729 | 34.3992 | 34.6485 | 33.0114 | 34.2823 | 34.3254 | 34.2577 | 34.3965 | 34.3695 | 34.2512 | 33.9804 | 34.391 | 36.15 | 34.9592 | 36.5475 | 36.5438 | 33.3346 | 93.9859 | 93.9914 | 93.715
2022-09-08 05:38 | 7:48 | 12.6601 | 14.0108 | 17.1861 | 34.0626 | 34.2525 | 34.0246 | 34.4943 | 35.505 | 36.5906 | 37.5314 | 37.0114 | 38.1945 | 34.3005 | 34.2704 | 34.0931 | 35.1387 | 34.8632 | 35.3794 | 36.0875 | 36.4727 | 32.2944 | 31.4568 | 93.3575 | 35.0874 | 32.8895 | 34.8779 | 32.9984 | 32.9817 | 33.2895 | 34.5585 | 34.1537 | 33.9667 | 37.1555 | 36.2059 | 33.3032 | 34.3398 | 36.1863 | 36.5046 | 37.317 | 36.1833 | 33.008 | 32.5937 | 34.3906 | 34.6801 | 33.0141 | 34.2969 | 34.3443 | 34.2525 | 34.4021 | 34.3708 | 34.2606 | 33.9713 | 34.3965 | 36.1456 | 34.9551 | 36.5573 | 36.5397 | 33.3496 | 94.1413 | 94.1583 | 93.8255
2022-09-08 05:38 | 7:48 | 13.1314 | 12.2094 | 17.1627 | 33.862 | 34.2545 | 34.0085 | 34.493 | 35.4951 | 36.5873 | 37.5324 | 37.0104 | 38.1796 | 34.302 | 34.2749 | 34.104 | 35.1367 | 34.8488 | 35.4012 | 36.0607 | 36.48 | 32.2353 | 31.4673 | 93.495 | 35.023 | 32.9008 | 34.869 | 33.0105 | 33.011 | 33.3103 | 34.5473 | 34.1481 | 33.9605 | 37.1637 | 36.2135 | 33.2938 | 34.3547 | 36.2101 | 36.4968 | 37.2904 | 36.1912 | 33.0155 | 32.5829 | 34.417 | 34.6679 | 33.0353 | 34.2948 | 34.3375 | 34.2627 | 34.3889 | 34.3836 | 34.2593 | 33.9908 | 34.4021 | 36.1371 | 34.945 | 36.5311 | 36.5338 | 33.3513 | 94.2585 | 94.3601 | 93.9006
2022-09-08 05:38 | 7:48 | 15.5829 | 13.2591 | 19.004 | 34.008 | 34.2448 | 34.0215 | 34.4803 | 35.495 | 36.5938 | 37.5241 | 37.0093 | 38.186 | 34.293 | 34.2869 | 34.1154 | 35.1544 | 34.8448 | 35.389 | 36.0819 | 36.4572 | 32.239 | 31.4541 | 93.5284 | 34.9981 | 32.9056 | 34.8648 | 33.0117 | 32.9947 | 33.2953 | 34.5618 | 34.1623 | 33.9511 | 37.1347 | 36.2127 | 33.2949 | 34.3489 | 36.2059 | 36.4999 | 37.2992 | 36.2074 | 33.017 | 32.5936 | 34.4113 | 34.6561 | 33.0315 | 34.2814 | 34.3347 | 34.2715 | 34.378 | 34.388 | 34.2701 | 33.9975 | 34.3889 | 36.1363 | 34.9646 | 36.555 | 36.5405 | 33.3335 | 94.4263 | 94.4835 | 93.9657
2022-09-08 05:38 | 7:48 | 17.5385 | 14.888 | 20.9269 | 34.1358 | 34.2525 | 34.0136 | 34.4759 | 35.4932 | 36.5701 | 37.5091 | 37.0036 | 38.1914 | 34.2838 | 34.2694 | 34.1011 | 35.144 | 34.8371 | 35.3993 | 36.0765 | 36.4704 | 32.2444 | 31.4812 | 93.7325 | 35.0735 | 32.9184 | 34.867 | 32.9988 | 33.0038 | 33.3123 | 34.554 | 34.1585 | 33.9499 | 37.1643 | 36.2107 | 33.3094 | 34.3648 | 36.2135 | 36.4957 | 37.3226 | 36.1863 | 33.0173 | 32.609 | 34.4123 | 34.6966 | 33.0456 | 34.2944 | 34.313 | 34.2733 | 34.3996 | 34.3819 | 34.2762 | 33.9944 | 34.378 | 36.1358 | 34.9747 | 36.5407 | 36.5377 | 33.3337 | 94.6332 | 94.6031 | 94.1173
2022-09-08 05:38 | 7:48 | 19.1901 | 16.7581 | 22.5904 | 34.3708 | 34.2548 | 34.0063 | 34.4642 | 35.5026 | 36.5752 | 37.5099 | 37.0102 | 38.2031 | 34.3006 | 34.2996 | 34.1219 | 35.1232 | 34.8416 | 35.383 | 36.0777 | 36.4581 | 32.2794 | 31.4827 | 93.8932 | 35.055 | 32.8945 | 34.8683 | 33.008 | 32.9952 | 33.3032 | 34.5658 | 34.138 | 33.9516 | 37.1445 | 36.2067 | 33.3106 | 34.3549 | 36.2127 | 36.4932 | 37.3057 | 36.2101 | 33.0061 | 32.6219 | 34.4314 | 34.6748 | 33.0631 | 34.2867 | 34.3244 | 34.2696 | 34.3981 | 34.39 | 34.2689 | 33.9674 | 34.3996 | 36.135 | 34.9533 | 36.5511 | 36.5532 | 33.3417 | 94.7768 | 94.7667 | 94.1899
2022-09-08 05:38 | 7:48 | 20.5108 | 18.5696 | 23.9269 | 34.3217 | 34.2212 | 34.0312 | 34.4729 | 35.5156 | 36.5907 | 37.5159 | 37.0038 | 38.1847 | 34.2917 | 34.2873 | 34.086 | 35.1434 | 34.8368 | 35.3918 | 36.0922 | 36.4692 | 32.3023 | 31.4648 | 93.6799 | 35.0452 | 32.8939 | 34.8795 | 33.0155 | 32.9903 | 33.2938 | 34.5494 | 34.1266 | 33.9423 | 37.1582 | 36.1955 | 33.3098 | 34.3568 | 36.2107 | 36.4942 | 37.3061 | 36.2059 | 33.0196 | 32.6171 | 34.4202 | 34.6823 | 33.0556 | 34.2902 | 34.3288 | 34.2707 | 34.3971 | 34.3815 | 34.2475 | 33.9973 | 34.3981 | 36.1495 | 34.9714 | 36.539 | 36.5368 | 33.3266 | 94.8358 | 94.9108 | 94.2092
2022-09-08 05:39 | 7:48 | 21.6471 | 20.2425 | 25.0636 | 34.5303 | 34.2496 | 34.0433 | 34.4769 | 35.5052 | 36.5951 | 37.5073 | 36.9874 | 38.1787 | 34.2787 | 34.2894 | 34.0958 | 35.134 | 34.8329 | 35.3937 | 36.0979 | 36.4746 | 32.3457 | 31.4779 | 94.0537 | 35.1247 | 32.8768 | 34.8699 | 33.017 | 32.9971 | 33.2949 | 34.5385 | 34.1581 | 33.9399 | 37.147 | 36.1904 | 33.3092 | 34.3467 | 36.2067 | 36.4989 | 37.3026 | 36.2135 | 33.0076 | 32.6105 | 34.4287 | 34.6738 | 33.0655 | 34.3059 | 34.3239 | 34.2944 | 34.3947 | 34.3946 | 34.249 | 33.995 | 34.3971 | 36.1219 | 34.9595 | 36.5381 | 36.5462 | 33.3121 | 94.935 | 95.0242 | 94.3399
2022-09-08 05:39 | 7:49 | 22.6766 | 21.7905 | 26.0303 | 34.6069 | 34.248 | 34.0138 | 34.4846 | 35.4877 | 36.582 | 37.522 | 37.0046 | 38.1917 | 34.2874 | 34.3071 | 34.0847 | 35.133 | 34.8338 | 35.3876 | 36.0845 | 36.4604 | 32.3804 | 31.4955 | 94.09 | 35.097 | 32.8752 | 34.8792 | 33.0173 | 32.9965 | 33.3094 | 34.5465 | 34.144 | 33.9457 | 37.1478 | 36.2168 | 33.2886 | 34.3554 | 36.1955 | 36.4878 | 37.2832 | 36.2127 | 33.0218 | 32.6023 | 34.4359 | 34.6833 | 33.0813 | 34.2955 | 34.3225 | 34.2814 | 34.3805 | 34.399 | 34.2628 | 34.0091 | 34.3947 | 36.1378 | 34.9534 | 36.5566 | 36.5561 | 33.3282 | 95.0186 | 95.1131 | 94.3397
2022-09-08 05:39 | 7:49 | 23.5498 | 23.1592 | 26.8187 | 34.6987 | 34.2409 | 34.036 | 34.4815 | 35.5137 | 36.5745 | 37.5028 | 37.007 | 38.1834 | 34.2823 | 34.2902 | 34.1179 | 35.1334 | 34.8205 | 35.3954 | 36.092 | 36.4518 | 32.4097 | 31.5205 | 94.0713 | 35.1689 | 32.8957 | 34.884 | 33.0061 | 32.9861 | 33.3106 | 34.5353 | 34.1434 | 33.9337 | 37.1364 | 36.2088 | 33.2993 | 34.369 | 36.1904 | 36.4946 | 37.3091 | 36.2107 | 33.0191 | 32.6203 | 34.4318 | 34.6751 | 33.087 | 34.306 | 34.3261 | 34.296 | 34.374 | 34.394 | 34.2939 | 33.9886 | 34.3805 | 36.1429 | 34.9751 | 36.5337 | 36.5163 | 33.3259 | 95.0763 | 95.2177 | 94.455
2022-09-08 05:39 | 7:49 | 24.3084 | 24.3395 | 27.4489 | 34.7722 | 34.2316 | 34.032 | 34.5 | 35.4772 | 36.5697 | 37.5143 | 36.9912 | 38.1744 | 34.3038 | 34.3048 | 34.0973 | 35.1275 | 34.8305 | 35.3796 | 36.0778 | 36.4552 | 32.4411 | 31.5158 | 94.1996 | 35.0964 | 32.8997 | 34.8708 | 33.0196 | 32.9924 | 33.3098 | 34.5427 | 34.1398 | 33.9672 | 37.1557 | 36.1977 | 33.2854 | 34.3591 | 36.2168 | 36.4924 | 37.2901 | 36.2067 | 32.9927 | 32.6052 | 34.4443 | 34.6773 | 33.0848 | 34.3017 | 34.3142 | 34.2778 | 34.3944 | 34.3831 | 34.2703 | 34.0139 | 34.374 | 36.1296 | 34.9478 | 36.5363 | 36.5495 | 33.317 | 95.1098 | 95.2266 | 94.4438
2022-09-08 05:39 | 7:49 | 24.9361 | 25.3337 | 27.8797 | 34.9789 | 34.232 | 34.0236 | 34.4963 | 35.493 | 36.5615 | 37.5097 | 36.9898 | 38.1856 | 34.3108 | 34.3002 | 34.1016 | 35.1329 | 34.8368 | 35.3908 | 36.1029 | 36.457 | 32.4822 | 31.5033 | 94.133 | 35.1658 | 32.9009 | 34.8593 | 33.0076 | 33.0105 | 33.3092 | 34.537 | 34.1548 | 33.9266 | 37.1555 | 36.211 | 33.2966 | 34.3607 | 36.2088 | 36.4772 | 37.2923 | 36.1955 | 33.0214 | 32.6093 | 34.4265 | 34.6664 | 33.0907 | 34.3127 | 34.3062 | 34.2818 | 34.3735 | 34.3993 | 34.286 | 33.9956 | 34.3944 | 36.1425 | 34.9775 | 36.5571 | 36.548 | 33.3277 | 94.9302 | 95.0915 | 94.3104
2022-09-08 05:39 | 7:49 | 25.5248 | 26.1546 | 28.3742 | 34.9155 | 34.2174 | 34.0437 | 34.4972 | 35.4879 | 36.5746 | 37.5087 | 36.9874 | 38.1758 | 34.307 | 34.2874 | 34.0704 | 35.13 | 34.8168 | 35.4163 | 36.1126 | 36.4578 | 32.5189 | 31.5113 | 93.8694 | 35.1624 | 32.9004 | 34.8655 | 33.0218 | 32.9955 | 33.2886 | 34.5379 | 34.1504 | 33.9472 | 37.1415 | 36.204 | 33.297 | 34.3575 | 36.1977 | 36.4814 | 37.2769 | 36.1904 | 33.0255 | 32.6144 | 34.447 | 34.6862 | 33.1059 | 34.2973 | 34.2966 | 34.2649 | 34.3824 | 34.4008 | 34.2558 | 33.9994 | 34.3735 | 36.1357 | 34.9728 | 36.5402 | 36.555 | 33.3427 | 94.7187 | 94.916 | 94.1469
2022-09-08 05:40 | 7:50 | 27.1359 | 19.9131 | 26.8754 | 34.9684 | 34.225 | 34.0252 | 34.4957 | 35.4894 | 36.5705 | 37.5202 | 37.0027 | 38.1884 | 34.3032 | 34.3012 | 34.0708 | 35.1451 | 34.8198 | 35.3894 | 36.1032 | 36.4425 | 32.8855 | 31.532 | 93.7805 | 35.2124 | 32.9102 | 34.8844 | 33.0191 | 32.985 | 33.2993 | 34.5333 | 34.151 | 33.9495 | 37.1391 | 36.2072 | 33.2891 | 34.3655 | 36.211 | 36.4904 | 37.2841 | 36.2168 | 33.0234 | 32.6234 | 34.4487 | 34.6874 | 33.105 | 34.2945 | 34.2999 | 34.2739 | 34.3984 | 34.3951 | 34.2534 | 33.9907 | 34.3824 | 36.1296 | 34.9794 | 36.5433 | 36.5418 | 33.3234 | 94.4856 | 94.6996 | 94.0147
2022-09-08 05:40 | 7:50 | 27.3263 | 23.903 | 26.8875 | 34.9503 | 34.2447 | 34.0484 | 34.5 | 35.4965 | 36.5622 | 37.5168 | 37.0129 | 38.1955 | 34.2988 | 34.3003 | 34.0605 | 35.1465 | 34.8228 | 35.3947 | 36.1109 | 36.4466 | 33.0516 | 31.5453 | 93.7107 | 35.2118 | 32.8997 | 34.8582 | 32.9927 | 32.9765 | 33.2854 | 34.5416 | 34.1407 | 33.9371 | 37.1338 | 36.2057 | 33.3044 | 34.3599 | 36.204 | 36.49 | 37.2907 | 36.2088 | 33.0177 | 32.6236 | 34.4264 | 34.6966 | 33.1073 | 34.3198 | 34.2922 | 34.2853 | 34.3694 | 34.4079 | 34.2879 | 33.9936 | 34.3984 | 36.1223 | 34.9637 | 36.5383 | 36.5409 | 33.31 | 94.2493 | 94.4819 | 93.8628
2022-09-08 05:40 | 7:50 | 30.1458 | 29.4603 | 28.2797 | 35.0326 | 34.2409 | 34.0401 | 34.5289 | 35.4974 | 36.5576 | 37.5244 | 36.9942 | 38.1912 | 34.2945 | 34.2999 | 34.0795 | 35.1285 | 34.8211 | 35.3965 | 36.1061 | 36.4301 | 33.254 | 31.7882 | 93.5086 | 35.1976 | 32.8981 | 34.8894 | 33.0214 | 32.9848 | 33.2966 | 34.5496 | 34.1352 | 33.9404 | 37.1296 | 36.2126 | 33.2935 | 34.3627 | 36.2072 | 36.4766 | 37.279 | 36.1977 | 33.0228 | 32.6301 | 34.4228 | 34.6932 | 33.14 | 34.2975 | 34.2822 | 34.2891 | 34.3869 | 34.3948 | 34.2669 | 34.006 | 34.3694 | 36.1183 | 34.9689 | 36.5356 | 36.5361 | 33.3423 | 94.0789 | 94.306 | 93.8007
2022-09-08 05:40 | 7:50 | 31.8826 | 30.2519 | 29.4393 | 35.2559 | 34.2475 | 34.0414 | 34.5295 | 35.5041 | 36.5545 | 37.5107 | 37.0123 | 38.1813 | 34.3044 | 34.2937 | 34.0981 | 35.1429 | 34.8163 | 35.3829 | 36.1071 | 36.4415 | 33.5408 | 32.4893 | 93.4648 | 35.2161 | 32.8963 | 34.8761 | 33.0255 | 32.9877 | 33.297 | 34.5328 | 34.1446 | 33.9417 | 37.1401 | 36.2125 | 33.3037 | 34.3743 | 36.2057 | 36.4605 | 37.287 | 36.211 | 33.0224 | 32.6343 | 34.4391 | 34.6979 | 33.1387 | 34.311 | 34.294 | 34.2936 | 34.3765 | 34.4045 | 34.2662 | 33.9928 | 34.3869 | 36.1359 | 34.9713 | 36.5449 | 36.5362 | 33.3085 | 93.9594 | 94.1535 | 93.7086
2022-09-08 05:40 | 7:50 | 32.9695 | 30.4521 | 29.9452 | 35.3309 | 34.2458 | 34.0534 | 34.5366 | 35.504 | 36.5566 | 37.5223 | 37.0062 | 38.1932 | 34.3057 | 34.299 | 34.0738 | 35.1384 | 34.8271 | 35.3927 | 36.1059 | 36.4496 | 34.0148 | 33.0072 | 93.4196 | 35.3041 | 32.8928 | 34.8618 | 33.0234 | 32.9915 | 33.2891 | 34.5276 | 34.1371 | 33.9454 | 37.137 | 36.2204 | 33.3149 | 34.3486 | 36.2126 | 36.4886 | 37.2736 | 36.204 | 33.0336 | 32.6366 | 34.4542 | 34.7056 | 33.1478 | 34.2995 | 34.2755 | 34.2927 | 34.3905 | 34.3886 | 34.275 | 33.994 | 34.3765 | 36.1332 | 34.973 | 36.551 | 36.5463 | 33.3186 | 93.8548 | 94.047 | 93.6475
2022-09-08 05:40 | 7:50 | 33.7893 | 30.5482 | 30.3856 | 35.2966 | 34.2386 | 34.06 | 34.541 | 35.5061 | 36.5555 | 37.5275 | 37.0063 | 38.1772 | 34.2996 | 34.2969 | 34.1079 | 35.1338 | 34.8135 | 35.3822 | 36.1184 | 36.4404 | 34.3939 | 32.9573 | 93.3194 | 35.2716 | 32.8923 | 34.8796 | 33.0177 | 32.9989 | 33.3044 | 34.529 | 34.1408 | 33.9453 | 37.1391 | 36.2141 | 33.3026 | 34.3789 | 36.2125 | 36.4913 | 37.2731 | 36.2072 | 33.0394 | 32.6468 | 34.4609 | 34.6916 | 33.1483 | 34.3152 | 34.2824 | 34.2907 | 34.3809 | 34.4131 | 34.2634 | 34.0051 | 34.3905 | 36.113 | 34.9831 | 36.5521 | 36.5118 | 33.3077 | 93.7574 | 93.8984 | 93.5899
2022-09-08 05:41 | 7:50 | 34.1788 | 30.6453 | 30.7598 | 35.3453 | 34.2449 | 34.074 | 34.5619 | 35.5227 | 36.5641 | 37.5035 | 36.9952 | 38.1769 | 34.305 | 34.3258 | 34.0781 | 35.1392 | 34.8083 | 35.4015 | 36.1223 | 36.441 | 34.6439 | 32.846 | 93.3157 | 35.3351 | 32.8897 | 34.8835 | 33.0228 | 33.0012 | 33.2935 | 34.5209 | 34.1339 | 33.9399 | 37.1293 | 36.2119 | 33.3238 | 34.3617 | 36.2204 | 36.4906 | 37.278 | 36.2057 | 33.0386 | 32.6635 | 34.4521 | 34.7009 | 33.1608 | 34.312 | 34.2851 | 34.2996 | 34.3786 | 34.3947 | 34.2786 | 34.0249 | 34.3809 | 36.12 | 34.9453 | 36.54 | 36.5519 | 33.3246 | 93.6642 | 93.8424 | 93.4648
2022-09-08 05:41 | 7:51 | 34.3083 | 30.7576 | 31.0463 | 35.5019 | 34.2635 | 34.0783 | 34.5678 | 35.515 | 36.5751 | 37.5092 | 37.012 | 38.1665 | 34.3183 | 34.3029 | 34.0641 | 35.1406 | 34.8099 | 35.4181 | 36.1453 | 36.4304 | 34.7013 | 32.5968 | 93.196 | 35.3175 | 32.9072 | 34.9087 | 33.0224 | 32.9896 | 33.3037 | 34.5142 | 34.1622 | 33.9458 | 37.1414 | 36.2257 | 33.3232 | 34.3778 | 36.2141 | 36.4752 | 37.2989 | 36.2126 | 33.0471 | 32.6609 | 34.4504 | 34.709 | 33.1623 | 34.3025 | 34.3019 | 34.3058 | 34.3724 | 34.4081 | 34.2697 | 34.0232 | 34.3786 | 36.1269 | 34.9773 | 36.5335 | 36.5499 | 33.3221 | 93.5814 | 93.727 | 93.4312
2022-09-08 05:41 | 7:51 | 34.2916 | 30.8286 | 31.1033 | 35.547 | 34.24 | 34.0713 | 34.5515 | 35.5075 | 36.5545 | 37.5227 | 37.0005 | 38.1887 | 34.3151 | 34.3067 | 34.0789 | 35.1561 | 34.807 | 35.4108 | 36.1243 | 36.4504 | 34.7559 | 32.5421 | 93.1082 | 35.3584 | 32.9245 | 34.9023 | 33.0336 | 33.0029 | 33.3149 | 34.5347 | 34.1368 | 33.9616 | 37.1433 | 36.2301 | 33.3223 | 34.3947 | 36.2119 | 36.4959 | 37.2863 | 36.2125 | 33.0229 | 32.6686 | 34.4659 | 34.6961 | 33.1859 | 34.3123 | 34.2693 | 34.2985 | 34.3617 | 34.3986 | 34.2917 | 34.0222 | 34.3724 | 36.1363 | 34.9778 | 36.5385 | 36.541 | 33.323 | 93.5394 | 93.6796 | 93.3977
2022-09-08 05:41 | 7:51 | 34.2894 | 30.9051 | 31.1477 | 35.5681 | 34.2494 | 34.0792 | 34.5678 | 35.5152 | 36.5583 | 37.5339 | 37.0203 | 38.2044 | 34.3258 | 34.2895 | 34.0802 | 35.1498 | 34.8128 | 35.3978 | 36.1363 | 36.4498 | 34.8115 | 32.493 | 93.1094 | 35.3824 | 32.9276 | 34.8965 | 33.0394 | 33.0102 | 33.3026 | 34.5401 | 34.1623 | 33.9475 | 37.1521 | 36.2195 | 33.3198 | 34.3736 | 36.2257 | 36.4866 | 37.2843 | 36.2204 | 33.0395 | 32.6674 | 34.4781 | 34.7209 | 33.1812 | 34.2951 | 34.2663 | 34.3169 | 34.3917 | 34.4095 | 34.2805 | 34.011 | 34.3617 | 36.1096 | 34.992 | 36.551 | 36.5524 | 33.3257 | 93.4721 | 93.6132 | 93.3587
2022-09-08 05:41 | 7:51 | 33.9367 | 30.965 | 31.1277 | 35.5867 | 34.2584 | 34.0811 | 34.5659 | 35.5198 | 36.5578 | 37.5367 | 37.0132 | 38.1801 | 34.3361 | 34.3012 | 34.0879 | 35.1602 | 34.8145 | 35.4174 | 36.1577 | 36.4441 | 34.8026 | 32.3479 | 93.0296 | 35.3927 | 32.9188 | 34.9107 | 33.0386 | 32.9996 | 33.3238 | 34.5371 | 34.1577 | 33.9607 | 37.1255 | 36.2554 | 33.3211 | 34.3929 | 36.2301 | 36.5024 | 37.2856 | 36.2141 | 33.0478 | 32.68 | 34.4688 | 34.7323 | 33.18 | 34.3191 | 34.2629 | 34.2959 | 34.3685 | 34.397 | 34.2874 | 34.0279 | 34.3917 | 36.1309 | 34.9908 | 36.542 | 36.5502 | 33.3192 | 93.3922 | 93.5076 | 93.211
2022-09-08 05:41 | 7:51 | 32.6442 | 30.9938 | 31.2283 | 35.6322 | 34.2456 | 34.0879 | 34.5632 | 35.5194 | 36.5573 | 37.5389 | 37.0061 | 38.1782 | 34.3346 | 34.3086 | 34.0855 | 35.1563 | 34.8204 | 35.412 | 36.1469 | 36.4432 | 34.7907 | 32.2261 | 92.9873 | 35.4241 | 32.929 | 34.9014 | 33.0471 | 32.9907 | 33.3232 | 34.5421 | 34.1731 | 33.9555 | 37.1478 | 36.2266 | 33.3273 | 34.405 | 36.2195 | 36.4937 | 37.2882 | 36.2119 | 33.0338 | 32.6763 | 34.4912 | 34.7343 | 33.2027 | 34.326 | 34.2881 | 34.2938 | 34.3758 | 34.4005 | 34.2894 | 34.017 | 34.3685 | 36.1231 | 34.9794 | 36.5511 | 36.5537 | 33.3418 | 93.2972 | 93.4492 | 93.1841
2022-09-08 05:42 | 7:52 | 32.0549 | 31.0219 | 31.2999 | 35.5894 | 34.2572 | 34.0963 | 34.5741 | 35.5319 | 36.561 | 37.5453 | 37.0092 | 38.2019 | 34.3449 | 34.3017 | 34.0951 | 35.1625 | 34.8316 | 35.4153 | 36.1503 | 36.4671 | 34.7957 | 32.2057 | 92.9508 | 35.4423 | 32.9169 | 34.9094 | 33.0229 | 33.001 | 33.3223 | 34.5442 | 34.1728 | 33.9717 | 37.1548 | 36.2293 | 33.303 | 34.3914 | 36.2554 | 36.4924 | 37.293 | 36.2257 | 33.0406 | 32.6925 | 34.4794 | 34.7398 | 33.2197 | 34.3135 | 34.2826 | 34.3121 | 34.3758 | 34.4 | 34.2747 | 34.0237 | 34.3758 | 36.1266 | 34.9953 | 36.5454 | 36.5487 | 33.3317 | 93.2263 | 93.4293 | 93.1572
2022-09-08 05:42 | 7:52 | 31.6817 | 31.0598 | 31.3704 | 35.6549 | 34.2534 | 34.0876 | 34.5836 | 35.529 | 36.5607 | 37.5384 | 37.0223 | 38.1966 | 34.3281 | 34.2989 | 34.0847 | 35.161 | 34.8105 | 35.4121 | 36.1588 | 36.4666 | 34.8276 | 32.2163 | 92.9084 | 35.4352 | 32.9298 | 34.9064 | 33.0395 | 33.0164 | 33.3198 | 34.5506 | 34.1624 | 33.9429 | 37.1581 | 36.2407 | 33.3061 | 34.4052 | 36.2266 | 36.499 | 37.2913 | 36.2301 | 33.0407 | 32.6949 | 34.4888 | 34.743 | 33.2263 | 34.3122 | 34.2842 | 34.3078 | 34.3582 | 34.4074 | 34.2704 | 34.0218 | 34.3758 | 36.1397 | 34.9699 | 36.5446 | 36.5652 | 33.3438 | 93.1871 | 93.3369 | 93.1501
2022-09-08 05:42 | 7:52 | 31.7096 | 31.0917 | 31.4531 | 35.7203 | 34.2681 | 34.1233 | 34.5819 | 35.5471 | 36.5715 | 37.5394 | 37.0127 | 38.2069 | 34.3266 | 34.3104 | 34.0742 | 35.1399 | 34.8191 | 35.4328 | 36.1514 | 36.4552 | 34.814 | 32.1572 | 92.8353 | 35.4272 | 32.9245 | 34.9219 | 33.0478 | 33.0204 | 33.3211 | 34.5434 | 34.1588 | 33.9596 | 37.1584 | 36.2381 | 33.32 | 34.401 | 36.2293 | 36.5087 | 37.2841 | 36.2195 | 33.0545 | 32.6889 | 34.4787 | 34.7588 | 33.2428 | 34.3412 | 34.3017 | 34.3231 | 34.3744 | 34.3894 | 34.2749 | 34.0158 | 34.3582 | 36.1404 | 34.9653 | 36.5688 | 36.5467 | 33.3485 | 93.0379 | 93.2463 | 92.9925
2022-09-08 05:42 | 7:52 | 31.7252 | 31.1199 | 31.5124 | 35.7828 | 34.2498 | 34.0941 | 34.5899 | 35.5357 | 36.5599 | 37.5356 | 37.0196 | 38.2133 | 34.3258 | 34.3215 | 34.0923 | 35.1727 | 34.828 | 35.4101 | 36.1696 | 36.4599 | 34.8076 | 32.1399 | 92.8242 | 35.4629 | 32.9375 | 34.9038 | 33.0338 | 33.0176 | 33.3273 | 34.5467 | 34.1637 | 33.9585 | 37.1461 | 36.2423 | 33.3217 | 34.4044 | 36.2407 | 36.4982 | 37.3101 | 36.2554 | 33.0532 | 32.7052 | 34.5134 | 34.7636 | 33.2307 | 34.3055 | 34.2799 | 34.3181 | 34.3915 | 34.4099 | 34.2869 | 34.021 | 34.3744 | 36.1606 | 34.9918 | 36.5574 | 36.5623 | 33.3749 | 92.9601 | 93.1705 | 92.9453
2022-09-08 05:42 | 7:52 | 31.7048 | 31.1157 | 31.5858 | 35.9246 | 34.2512 | 34.0898 | 34.588 | 35.5559 | 36.5862 | 37.5551 | 37.0177 | 38.1984 | 34.3246 | 34.3095 | 34.0744 | 35.186 | 34.8267 | 35.4357 | 36.1748 | 36.4706 | 34.8204 | 32.1506 | 92.8252 | 35.5769 | 32.934 | 34.9091 | 33.0406 | 33.0184 | 33.303 | 34.5345 | 34.1496 | 33.9753 | 37.1574 | 36.2249 | 33.3175 | 34.4107 | 36.2381 | 36.5197 | 37.3021 | 36.2266 | 33.0369 | 32.7166 | 34.5339 | 34.7705 | 33.2446 | 34.3285 | 34.2571 | 34.3252 | 34.355 | 34.4082 | 34.2694 | 34.0195 | 34.3915 | 36.157 | 34.9924 | 36.5563 | 36.5636 | 33.3582 | 92.8846 | 93.0563 | 92.9566
2022-09-08 05:42 | 7:52 | 31.706 | 31.1662 | 31.6548 | 35.8677 | 34.2606 | 34.1059 | 34.5924 | 35.5436 | 36.5694 | 37.5543 | 37.0318 | 38.1993 | 34.3525 | 34.3237 | 34.0902 | 35.1588 | 34.8016 | 35.439 | 36.175 | 36.4771 | 34.8244 | 32.1607 | 92.7007 | 35.4528 | 32.936 | 34.9238 | 33.0407 | 33.0255 | 33.3061 | 34.5453 | 34.1713 | 33.9675 | 37.1644 | 36.2586 | 33.3197 | 34.3964 | 36.2423 | 36.4982 | 37.2927 | 36.2293 | 33.0431 | 32.7096 | 34.5253 | 34.778 | 33.252 | 34.3392 | 34.2722 | 34.3314 | 34.3686 | 34.4044 | 34.2996 | 34.0426 | 34.355 | 36.1331 | 34.9824 | 36.5598 | 36.5634 | 33.3641 | 92.8197 | 92.9781 | 92.9253
2022-09-08 05:43 | 7:52 | 31.7207 | 31.1965 | 31.7105 | 35.9922 | 34.2593 | 34.1088 | 34.5955 | 35.5576 | 36.5617 | 37.5611 | 37.0251 | 38.2039 | 34.3515 | 34.3314 | 34.0911 | 35.1768 | 34.8335 | 35.4501 | 36.1717 | 36.4607 | 34.8802 | 32.1496 | 92.5817 | 35.5286 | 32.9738 | 34.9122 | 33.0545 | 33.0208 | 33.32 | 34.5505 | 34.1671 | 33.949 | 37.1599 | 36.2414 | 33.3323 | 34.406 | 36.2249 | 36.4893 | 37.2823 | 36.2407 | 33.0575 | 32.7168 | 34.5366 | 34.7898 | 33.2622 | 34.32 | 34.2711 | 34.2991 | 34.3723 | 34.394 | 34.2873 | 34.0503 | 34.3686 | 36.16 | 34.9743 | 36.5661 | 36.5505 | 33.3649 | 92.7053 | 92.8711 | 92.789
2022-09-08 05:43 | 7:53 | 31.4804 | 31.2301 | 31.7614 | 36.0169 | 34.2701 | 34.1091 | 34.6105 | 35.5427 | 36.5664 | 37.5588 | 37.0212 | 38.2084 | 34.349 | 34.3381 | 34.0876 | 35.1752 | 34.8252 | 35.4433 | 36.1995 | 36.4763 | 35.002 | 32.2561 | 92.5814 | 35.5543 | 32.9576 | 34.9171 | 33.0532 | 33.0374 | 33.3217 | 34.5523 | 34.1619 | 33.9781 | 37.1513 | 36.2388 | 33.3471 | 34.415 | 36.2586 | 36.498 | 37.3187 | 36.2381 | 33.0478 | 32.7481 | 34.5529 | 34.8125 | 33.2625 | 34.3113 | 34.2737 | 34.3191 | 34.3692 | 34.3912 | 34.2894 | 34.0448 | 34.3723 | 36.1637 | 34.9958 | 36.556 | 36.5747 | 33.3784 | 92.5344 | 92.7473 | 92.722
2022-09-08 05:43 | 7:53 | 31.5742 | 31.2423 | 31.8023 | 35.863 | 34.2762 | 34.1075 | 34.6101 | 35.5523 | 36.585 | 37.578 | 37.0306 | 38.2021 | 34.3519 | 34.3392 | 34.0984 | 35.1592 | 34.8256 | 35.4636 | 36.2037 | 36.4666 | 35.1858 | 32.296 | 92.4813 | 35.5386 | 32.9479 | 34.9294 | 33.0369 | 33.0371 | 33.3175 | 34.5474 | 34.1699 | 33.964 | 37.1678 | 36.2379 | 33.3348 | 34.4043 | 36.2414 | 36.5183 | 37.3107 | 36.2423 | 33.0663 | 32.7288 | 34.5452 | 34.7923 | 33.2736 | 34.3247 | 34.2811 | 34.3173 | 34.3657 | 34.4017 | 34.3071 | 34.0625 | 34.3692 | 36.1368 | 34.9809 | 36.564 | 36.5826 | 33.3899 | 92.4535 | 92.6594 | 92.6285
2022-09-08 05:43 | 7:53 | 31.6625 | 31.2715 | 31.8771 | 36.0252 | 34.2689 | 34.1106 | 34.6101 | 35.549 | 36.5737 | 37.5878 | 37.0374 | 38.2211 | 34.3619 | 34.3358 | 34.0959 | 35.1852 | 34.8292 | 35.4448 | 36.1985 | 36.4785 | 35.3331 | 32.3319 | 92.4461 | 35.5575 | 32.9314 | 34.9189 | 33.0431 | 33.013 | 33.3197 | 34.551 | 34.163 | 33.9744 | 37.159 | 36.2286 | 33.3285 | 34.4082 | 36.2388 | 36.5032 | 37.3043 | 36.2249 | 33.0542 | 32.7333 | 34.5598 | 34.8105 | 33.292 | 34.3203 | 34.2745 | 34.3165 | 34.3557 | 34.4007 | 34.2902 | 34.073 | 34.3657 | 36.1698 | 34.9814 | 36.5496 | 36.5668 | 33.3962 | 92.2743 | 92.5196 | 92.5248
2022-09-08 05:43 | 7:53 | 32.4602 | 31.3101 | 31.9368 | 36.0284 | 34.2475 | 34.1137 | 34.5976 | 35.5452 | 36.5851 | 37.5672 | 37.009 | 38.2238 | 34.3367 | 34.3331 | 34.0903 | 35.1896 | 34.8168 | 35.454 | 36.216 | 36.4743 | 35.3914 | 32.3215 | 92.3111 | 35.5413 | 32.9671 | 34.93 | 33.0575 | 33.0363 | 33.3323 | 34.5377 | 34.1785 | 33.9831 | 37.1628 | 36.2373 | 33.3338 | 34.4177 | 36.2379 | 36.5131 | 37.3158 | 36.2586 | 33.0586 | 32.7525 | 34.5819 | 34.8162 | 33.3092 | 34.3395 | 34.2622 | 34.3 | 34.3825 | 34.3736 | 34.3048 | 34.0546 | 34.3557 | 36.1694 | 34.983 | 36.5825 | 36.5663 | 33.3961 | 92.1798 | 92.4146 | 92.5495
2022-09-08 05:43 | 7:53 | 33.6685 | 31.3381 | 32.0084 | 36.068 | 34.249 | 34.1155 | 34.5949 | 35.5576 | 36.594 | 37.5699 | 37.0368 | 38.2111 | 34.3546 | 34.3338 | 34.0992 | 35.202 | 34.8367 | 35.451 | 36.2225 | 36.4847 | 35.4111 | 32.3221 | 92.2099 | 35.5645 | 32.9742 | 34.9252 | 33.0478 | 33.0213 | 33.3471 | 34.5542 | 34.1782 | 33.9823 | 37.1767 | 36.2315 | 33.3436 | 34.3989 | 36.2286 | 36.5034 | 37.3265 | 36.2414 | 33.0795 | 32.7515 | 34.5701 | 34.8353 | 33.2959 | 34.3274 | 34.27 | 34.325 | 34.3747 | 34.3656 | 34.3002 | 34.0733 | 34.3825 | 36.2085 | 34.9801 | 36.5588 | 36.5663 | 33.3789 | 92.103 | 92.2902 | 92.4518
2022-09-08 05:44 | 7:53 | 34.8043 | 31.3621 | 32.059 | 36.0599 | 34.2628 | 34.1162 | 34.6015 | 35.5631 | 36.5872 | 37.5803 | 37.0237 | 38.2179 | 34.3545 | 34.3394 | 34.11 | 35.1697 | 34.8366 | 35.4597 | 36.2046 | 36.4858 | 35.4029 | 32.3265 | 92.1454 | 35.613 | 32.9668 | 34.9246 | 33.0663 | 33.0233 | 33.3348 | 34.566 | 34.1699 | 33.9807 | 37.1786 | 36.2471 | 33.3388 | 34.4294 | 36.2373 | 36.5234 | 37.3228 | 36.2388 | 33.0634 | 32.766 | 34.5564 | 34.8415 | 33.3107 | 34.3328 | 34.2511 | 34.3387 | 34.3441 | 34.4075 | 34.2874 | 34.0754 | 34.3747 | 36.1828 | 34.9814 | 36.5605 | 36.5866 | 33.4117 | 91.9459 | 92.2145 | 92.2682
2022-09-08 05:44 | 7:54 | 34.6137 | 31.3606 | 32.1556 | 36.1223 | 34.2939 | 34.105 | 34.6081 | 35.5628 | 36.5859 | 37.5932 | 37.0335 | 38.2306 | 34.3722 | 34.3469 | 34.1186 | 35.1655 | 34.8393 | 35.4454 | 36.2132 | 36.4767 | 34.5461 | 32.1724 | 92.0494 | 35.6265 | 32.97 | 34.9232 | 33.0542 | 33.0471 | 33.3285 | 34.5666 | 34.167 | 33.9684 | 37.1535 | 36.2373 | 33.3384 | 34.4099 | 36.2315 | 36.5249 | 37.3471 | 36.2379 | 33.0663 | 32.7814 | 34.5997 | 34.8601 | 33.3106 | 34.3128 | 34.2481 | 34.3204 | 34.3611 | 34.3735 | 34.3012 | 34.0363 | 34.3441 | 36.1976 | 34.9901 | 36.5658 | 36.5899 | 33.3963 | 91.8198 | 92.0885 | 92.2312
2022-09-08 05:44 | 7:54 | 30.5819 | 31.0433 | 31.9515 | 36.1615 | 34.2703 | 34.1266 | 34.5936 | 35.5671 | 36.5902 | 37.5947 | 37.0333 | 38.2096 | 34.3564 | 34.3445 | 34.1224 | 35.19 | 34.8536 | 35.4604 | 36.2295 | 36.4963 | 30.5817 | 31.6632 | 91.9528 | 35.5818 | 32.9724 | 34.9336 | 33.0586 | 33.0336 | 33.3338 | 34.5721 | 34.1621 | 33.9787 | 37.1765 | 36.2538 | 33.3421 | 34.4231 | 36.2471 | 36.536 | 37.3182 | 36.2286 | 33.0681 | 32.7521 | 34.604 | 34.8398 | 33.3107 | 34.3345 | 34.2468 | 34.3322 | 34.363 | 34.3871 | 34.3003 | 34.0873 | 34.3611 | 36.1826 | 34.9773 | 36.5371 | 36.5802 | 33.4072 | 91.7431 | 91.9254 | 92.1705
2022-09-08 05:44 | 7:54 | 30.9496 | 27.5915 | 31.675 | 36.1405 | 34.286 | 34.1314 | 34.6064 | 35.5642 | 36.5634 | 37.5926 | 37.0201 | 38.2166 | 34.3626 | 34.3536 | 34.1134 | 35.1845 | 34.8366 | 35.4604 | 36.2185 | 36.5096 | 29.1883 | 28.8707 | 91.8116 | 35.5129 | 32.9809 | 34.936 | 33.0795 | 33.0477 | 33.3436 | 34.567 | 34.1529 | 33.9688 | 37.1541 | 36.2455 | 33.3436 | 34.4213 | 36.2373 | 36.5342 | 37.311 | 36.2373 | 33.0779 | 32.7816 | 34.5798 | 34.8554 | 33.3347 | 34.3254 | 34.261 | 34.3381 | 34.3513 | 34.379 | 34.2999 | 34.0725 | 34.363 | 36.2067 | 34.9839 | 36.5774 | 36.5906 | 33.4424 | 91.6267 | 91.7764 | 92.0934
2022-09-08 05:44 | 7:54 | 31.4824 | 26.6159 | 31.8202 | 36.2777 | 34.2558 | 34.1119 | 34.611 | 35.5626 | 36.5783 | 37.5936 | 37.0304 | 38.2183 | 34.3826 | 34.3582 | 34.1082 | 35.1822 | 34.8306 | 35.4603 | 36.2189 | 36.5268 | 28.1793 | 27.5131 | 91.7555 | 35.3882 | 32.9875 | 34.9271 | 33.0634 | 33.0572 | 33.3388 | 34.5733 | 34.1865 | 33.9772 | 37.1751 | 36.2545 | 33.3689 | 34.4127 | 36.2538 | 36.5176 | 37.3508 | 36.2315 | 33.0667 | 32.7652 | 34.5947 | 34.8526 | 33.3444 | 34.3324 | 34.2557 | 34.3467 | 34.3515 | 34.3906 | 34.2937 | 34.0773 | 34.3513 | 36.1883 | 34.9699 | 36.5576 | 36.593 | 33.4119 | 91.5063 | 91.6554 | 92.0269
2022-09-08 05:44 | 7:54 | 31.6844 | 26.7631 | 31.9442 | 36.1254 | 34.2534 | 34.135 | 34.6016 | 35.5748 | 36.5869 | 37.6009 | 37.0214 | 38.2194 | 34.3874 | 34.3729 | 34.1149 | 35.1753 | 34.8422 | 35.4803 | 36.2271 | 36.519 | 28.0847 | 26.4104 | 91.8067 | 35.3338 | 32.9906 | 34.9377 | 33.0663 | 33.0429 | 33.3384 | 34.5804 | 34.1628 | 33.9823 | 37.1678 | 36.2358 | 33.3383 | 34.4152 | 36.2455 | 36.523 | 37.3562 | 36.2471 | 33.0545 | 32.7764 | 34.6259 | 34.8905 | 33.2998 | 34.3556 | 34.2413 | 34.3486 | 34.3565 | 34.3708 | 34.299 | 34.0978 | 34.3515 | 36.216 | 34.9907 | 36.5863 | 36.5698 | 33.4448 | 91.4494 | 91.5709 | 92.0087
2022-09-08 05:45 | 7:55 | 31.7849 | 27.2614 | 32.0089 | 36.2889 | 34.2879 | 34.1305 | 34.6096 | 35.5703 | 36.6085 | 37.5932 | 37.038 | 38.2225 | 34.3695 | 34.3713 | 34.1179 | 35.1809 | 34.8476 | 35.4837 | 36.2396 | 36.5212 | 28.4831 | 25.3371 | 91.7365 | 35.251 | 32.9754 | 34.938 | 33.0681 | 33.0281 | 33.3421 | 34.5834 | 34.1734 | 33.9729 | 37.185 | 36.2373 | 33.3412 | 34.4433 | 36.2545 | 36.5182 | 37.3575 | 36.2373 | 33.0809 | 32.7821 | 34.6044 | 34.8841 | 33.3345 | 34.3549 | 34.2545 | 34.3317 | 34.3451 | 34.3874 | 34.2969 | 34.0955 | 34.3565 | 36.1982 | 34.9801 | 36.5636 | 36.5885 | 33.4294 | 91.4785 | 91.603 | 92.0373
2022-09-08 05:45 | 7:55 | 31.8073 | 28.0904 | 32.0862 | 36.2254 | 34.2669 | 34.1221 | 34.6424 | 35.5824 | 36.5781 | 37.5964 | 37.0296 | 38.2295 | 34.3708 | 34.3734 | 34.1112 | 35.199 | 34.865 | 35.4619 | 36.2152 | 36.5204 | 28.5724 | 24.4939 | 91.8557 | 35.1659 | 32.9759 | 34.9407 | 33.0779 | 33.0417 | 33.3436 | 34.5702 | 34.1598 | 33.9716 | 37.1894 | 36.2428 | 33.3489 | 34.4075 | 36.2358 | 36.52 | 37.3487 | 36.2538 | 33.0601 | 32.7978 | 34.6084 | 34.8858 | 33.3198 | 34.3554 | 34.2747 | 34.3325 | 34.3516 | 34.3736 | 34.3258 | 34.1011 | 34.3451 | 36.2286 | 34.991 | 36.5783 | 36.5887 | 33.4362 | 91.6185 | 91.689 | 92.1513
2022-09-08 05:45 | 7:55 | 31.8272 | 29.061 | 32.1665 | 36.3531 | 34.2662 | 34.1298 | 34.6352 | 35.5861 | 36.5781 | 37.6063 | 37.0432 | 38.2169 | 34.3836 | 34.3648 | 34.1423 | 35.1698 | 34.8361 | 35.4873 | 36.2348 | 36.4913 | 28.4649 | 23.8608 | 91.863 | 35.1139 | 32.9782 | 34.9407 | 33.0667 | 33.0339 | 33.3689 | 34.5776 | 34.1697 | 33.9794 | 37.1763 | 36.249 | 33.3431 | 34.3993 | 36.2373 | 36.528 | 37.3455 | 36.2455 | 33.0674 | 32.8059 | 34.617 | 34.8728 | 33.3104 | 34.3584 | 34.2582 | 34.3365 | 34.3424 | 34.3689 | 34.3029 | 34.093 | 34.3516 | 36.1924 | 34.9693 | 36.5804 | 36.6027 | 33.4273 | 91.6639 | 91.8524 | 92.1815
2022-09-08 05:45 | 7:55 | 31.8822 | 29.7603 | 32.2303 | 36.3352 | 34.275 | 34.1182 | 34.6335 | 35.5657 | 36.5903 | 37.6048 | 37.0253 | 38.2312 | 34.388 | 34.3543 | 34.1259 | 35.1632 | 34.8477 | 35.496 | 36.245 | 36.5149 | 28.0942 | 23.4633 | 91.9385 | 35.0291 | 33.0088 | 34.9305 | 33.0545 | 33.0421 | 33.3383 | 34.5735 | 34.1546 | 33.9793 | 37.1976 | 36.2364 | 33.3422 | 34.4175 | 36.2428 | 36.5345 | 37.3499 | 36.2545 | 33.0583 | 32.8105 | 34.6262 | 34.8811 | 33.3163 | 34.3529 | 34.2571 | 34.3537 | 34.3396 | 34.381 | 34.3067 | 34.0914 | 34.3424 | 36.1919 | 34.9896 | 36.5583 | 36.5864 | 33.4509 | 91.7644 | 91.9546 | 92.2825
2022-09-08 05:45 | 7:55 | 31.9459 | 30.209 | 32.2968 | 36.3688 | 34.2634 | 34.1248 | 34.6475 | 35.5691 | 36.5998 | 37.6313 | 37.0126 | 38.2142 | 34.3819 | 34.3762 | 34.1173 | 35.1938 | 34.8501 | 35.4688 | 36.2188 | 36.531 | 27.6262 | 22.9642 | 91.9814 | 35.0446 | 32.9787 | 34.9339 | 33.0809 | 33.0303 | 33.3412 | 34.5906 | 34.1573 | 33.9755 | 37.1627 | 36.2377 | 33.3476 | 34.4076 | 36.249 | 36.5199 | 37.3486 | 36.2358 | 33.0667 | 32.8023 | 34.6215 | 34.9036 | 33.3079 | 34.3337 | 34.2629 | 34.3381 | 34.3479 | 34.3957 | 34.2895 | 34.0992 | 34.3396 | 36.2124 | 34.9648 | 36.5695 | 36.5884 | 33.4442 | 91.8907 | 92.0616 | 92.3464
2022-09-08 05:45 | 7:55 | 32.0433 | 30.5284 | 32.3194 | 36.3909 | 34.2786 | 34.1303 | 34.6381 | 35.5882 | 36.6055 | 37.626 | 37.0371 | 38.2212 | 34.39 | 34.3655 | 34.1289 | 35.1657 | 34.839 | 35.4607 | 36.2474 | 36.52 | 27.177 | 22.6494 | 92.1106 | 35.0145 | 32.9926 | 34.9157 | 33.0601 | 33.0566 | 33.3489 | 34.5849 | 34.1555 | 33.9753 | 37.171 | 36.2434 | 33.3446 | 34.4075 | 36.2364 | 36.535 | 37.3622 | 36.2373 | 33.0466 | 32.8014 | 34.5865 | 34.8927 | 33.2957 | 34.3691 | 34.2689 | 34.3456 | 34.3382 | 34.3959 | 34.3012 | 34.096 | 34.3479 | 36.1994 | 34.9492 | 36.5728 | 36.604 | 33.4472 | 92.0813 | 92.2869 | 92.4731
2022-09-08 05:46 | 7:55 | 32.1196 | 30.7514 | 32.3903 | 36.4945 | 34.2697 | 34.1245 | 34.6582 | 35.587 | 36.5859 | 37.6141 | 37.0266 | 38.2094 | 34.3815 | 34.3598 | 34.1212 | 35.1586 | 34.8505 | 35.4867 | 36.2331 | 36.5125 | 26.7219 | 22.3737 | 92.2425 | 34.8983 | 32.9857 | 34.9273 | 33.0674 | 33.0287 | 33.3431 | 34.5859 | 34.1498 | 33.9845 | 37.1768 | 36.261 | 33.3639 | 34.4198 | 36.2377 | 36.5102 | 37.3659 | 36.2428 | 33.0511 | 32.8251 | 34.6216 | 34.9042 | 33.3025 | 34.3538 | 34.2512 | 34.351 | 34.3254 | 34.3954 | 34.3086 | 34.0949 | 34.3382 | 36.2074 | 34.9733 | 36.5736 | 36.5937 | 33.4455 | 92.2645 | 92.4336 | 92.586
2022-09-08 05:46 | 7:56 | 32.1742 | 30.9246 | 32.4191 | 36.5181 | 34.2917 | 34.1205 | 34.6311 | 35.5657 | 36.5975 | 37.6153 | 37.0187 | 38.2313 | 34.3946 | 34.3743 | 34.1366 | 35.1823 | 34.8355 | 35.5005 | 36.2285 | 36.5243 | 26.2571 | 22.1506 | 92.3036 | 34.9583 | 32.9963 | 34.9085 | 33.0583 | 33.033 | 33.3422 | 34.6011 | 34.1469 | 33.9742 | 37.1723 | 36.2393 | 33.3543 | 34.3987 | 36.2434 | 36.526 | 37.3626 | 36.249 | 33.0476 | 32.8133 | 34.608 | 34.9055 | 33.2959 | 34.3608 | 34.28 | 34.3601 | 34.3443 | 34.3689 | 34.3017 | 34.0924 | 34.3254 | 36.2111 | 34.9358 | 36.562 | 36.6107 | 33.4268 | 92.3671 | 92.6051 | 92.6605
2022-09-08 05:46 | 7:56 | 32.237 | 31.0187 | 32.4672 | 36.4836 | 34.2805 | 34.1125 | 34.6457 | 35.5664 | 36.5855 | 37.6029 | 37.0328 | 38.2307 | 34.399 | 34.3795 | 34.1152 | 35.1767 | 34.8385 | 35.4672 | 36.2318 | 36.5137 | 25.869 | 21.9225 | 92.3248 | 34.751 | 32.9856 | 34.9137 | 33.0667 | 33.0285 | 33.3476 | 34.5846 | 34.1347 | 33.9692 | 37.1589 | 36.2354 | 33.3475 | 34.3987 | 36.261 | 36.5168 | 37.3694 | 36.2364 | 33.0571 | 32.8114 | 34.6081 | 34.8982 | 33.2721 | 34.3752 | 34.251 | 34.3682 | 34.3375 | 34.3935 | 34.2989 | 34.0993 | 34.3443 | 36.2333 | 34.9731 | 36.5634 | 36.5879 | 33.4433 | 92.5341 | 92.7974 | 92.757
2022-09-08 05:46 | 7:56 | 32.2759 | 31.0956 | 32.5176 | 36.517 | 34.2874 | 34.1043 | 34.6617 | 35.5657 | 36.5894 | 37.5999 | 37.0108 | 38.208 | 34.394 | 34.3848 | 34.1173 | 35.1773 | 34.8329 | 35.4749 | 36.2286 | 36.5229 | 25.4154 | 21.723 | 92.4395 | 34.7786 | 32.9836 | 34.9091 | 33.0466 | 33.0257 | 33.3446 | 34.5958 | 34.14 | 33.9445 | 37.1679 | 36.2551 | 33.3563 | 34.4142 | 36.2393 | 36.5322 | 37.3756 | 36.2377 | 33.0377 | 32.7895 | 34.6113 | 34.8823 | 33.2772 | 34.3791 | 34.2677 | 34.3592 | 34.3347 | 34.3711 | 34.3104 | 34.0939 | 34.3375 | 36.2225 | 34.9629 | 36.5663 | 36.5876 | 33.4473 | 92.6717 | 92.9849 | 92.8497
2022-09-08 05:46 | 7:56 | 32.3127 | 31.1762 | 32.5384 | 36.5814 | 34.2894 | 34.1108 | 34.6569 | 35.5764 | 36.6113 | 37.6141 | 37.0045 | 38.2074 | 34.3831 | 34.3667 | 34.1372 | 35.1675 | 34.8436 | 35.4744 | 36.2419 | 36.5265 | 24.8472 | 21.5123 | 92.5361 | 34.7539 | 32.9836 | 34.9251 | 33.0511 | 33.0166 | 33.3639 | 34.5826 | 34.1179 | 33.9672 | 37.172 | 36.2409 | 33.3392 | 34.3915 | 36.2354 | 36.5209 | 37.3655 | 36.2434 | 33.0547 | 32.8042 | 34.6075 | 34.8945 | 33.2731 | 34.3809 | 34.2712 | 34.3334 | 34.313 | 34.3761 | 34.3215 | 34.0925 | 34.3347 | 36.179 | 34.9444 | 36.5668 | 36.5791 | 33.4212 | 92.8701 | 93.0752 | 92.9672
2022-09-08 05:46 | 7:56 | 32.3768 | 31.2529 | 32.5962 | 36.4614 | 34.2747 | 34.1133 | 34.6489 | 35.5813 | 36.6041 | 37.6364 | 37.0066 | 38.2162 | 34.3993 | 34.3972 | 34.1372 | 35.1789 | 34.8251 | 35.4705 | 36.2454 | 36.5193 | 24.2131 | 21.2101 | 92.7738 | 34.5919 | 32.9888 | 34.9128 | 33.0476 | 33.0222 | 33.3543 | 34.591 | 34.1362 | 33.9648 | 37.1735 | 36.228 | 33.3225 | 34.4048 | 36.2551 | 36.5004 | 37.365 | 36.261 | 33.0676 | 32.8316 | 34.6019 | 34.8937 | 33.2562 | 34.3785 | 34.2596 | 34.3646 | 34.3244 | 34.3829 | 34.3095 | 34.0961 | 34.313 | 36.2097 | 34.9438 | 36.5761 | 36.5894 | 33.4444 | 93.0881 | 93.236 | 93.0764
2022-09-08 05:47 | 7:57 | 32.407 | 31.2946 | 32.6324 | 36.5049 | 34.2704 | 34.103 | 34.6575 | 35.5803 | 36.6026 | 37.6232 | 37.008 | 38.2009 | 34.4008 | 34.376 | 34.1347 | 35.1519 | 34.8264 | 35.4839 | 36.2432 | 36.5298 | 23.4942 | 20.9548 | 92.584 | 34.656 | 32.9858 | 34.9196 | 33.0571 | 33.0227 | 33.3475 | 34.5877 | 34.1242 | 33.9589 | 37.179 | 36.2388 | 33.3213 | 34.3936 | 36.2409 | 36.5064 | 37.3731 | 36.2393 | 33.0667 | 32.8295 | 34.5967 | 34.8967 | 33.2596 | 34.3936 | 34.265 | 34.3543 | 34.3288 | 34.3669 | 34.3237 | 34.0966 | 34.3244 | 36.2165 | 34.9571 | 36.5516 | 36.5924 | 33.4401 | 93.2389 | 93.3271 | 93.0889
2022-09-08 05:47 | 7:57 | 32.4528 | 31.3558 | 32.6814 | 36.5782 | 34.2749 | 34.1173 | 34.6783 | 35.5736 | 36.5945 | 37.6271 | 37.0138 | 38.2167 | 34.3951 | 34.3885 | 34.1221 | 35.1744 | 34.8457 | 35.4771 | 36.2354 | 36.5447 | 22.6396 | 20.5587 | 92.6335 | 34.4226 | 32.9971 | 34.9309 | 33.0377 | 33.0053 | 33.3563 | 34.6057 | 34.1361 | 33.9566 | 37.1867 | 36.2549 | 33.3348 | 34.4163 | 36.228 | 36.501 | 37.3913 | 36.2354 | 33.0641 | 32.8068 | 34.6042 | 34.8751 | 33.2536 | 34.3852 | 34.2678 | 34.3653 | 34.3239 | 34.3615 | 34.3314 | 34.1125 | 34.3288 | 36.2096 | 34.9566 | 36.5707 | 36.5549 | 33.4348 | 93.3433 | 93.4741 | 93.1513
2022-09-08 05:47 | 7:57 | 32.5074 | 31.3626 | 32.7384 | 36.6224 | 34.2869 | 34.11 | 34.6625 | 35.5679 | 36.6111 | 37.634 | 36.9976 | 38.2158 | 34.4079 | 34.3854 | 34.1288 | 35.1643 | 34.852 | 35.4561 | 36.2498 | 36.528 | 21.5392 | 20.1811 | 92.9018 | 34.3023 | 32.9739 | 34.9162 | 33.0547 | 33.0216 | 33.3392 | 34.6003 | 34.1384 | 33.9603 | 37.1801 | 36.2396 | 33.3412 | 34.3908 | 36.2388 | 36.5182 | 37.3805 | 36.2551 | 33.0571 | 32.7982 | 34.6008 | 34.8939 | 33.2429 | 34.3935 | 34.2611 | 34.3484 | 34.3225 | 34.3704 | 34.3381 | 34.1062 | 34.3239 | 36.2149 | 34.9533 | 36.5676 | 36.5651 | 33.4368 | 93.6 | 93.6313 | 93.3456
2022-09-08 05:47 | 7:57 | 32.547 | 31.4283 | 32.7887 | 36.6009 | 34.2694 | 34.1083 | 34.6795 | 35.5789 | 36.5919 | 37.6256 | 36.99 | 38.207 | 34.3948 | 34.3899 | 34.1404 | 35.1637 | 34.8367 | 35.4866 | 36.2487 | 36.5307 | 19.5606 | 19.7799 | 93.2063 | 34.1933 | 32.9875 | 34.9213 | 33.0676 | 33.0055 | 33.3225 | 34.5894 | 34.1393 | 33.9774 | 37.1762 | 36.2627 | 33.358 | 34.3988 | 36.2549 | 36.4961 | 37.3777 | 36.2409 | 33.071 | 32.7881 | 34.5913 | 34.8835 | 33.2503 | 34.3933 | 34.2842 | 34.3619 | 34.3261 | 34.3675 | 34.3392 | 34.1106 | 34.3225 | 36.2207 | 34.9536 | 36.5658 | 36.5804 | 33.4425 | 93.8263 | 93.8318 | 93.4349
2022-09-08 05:47 | 7:57 | 32.5654 | 31.4279 | 32.8218 | 36.627 | 34.2996 | 34.1243 | 34.6764 | 35.56 | 36.5916 | 37.6374 | 36.9956 | 38.2104 | 34.4045 | 34.4002 | 34.1424 | 35.1708 | 34.8452 | 35.4923 | 36.2322 | 36.5378 | 17.743 | 19.2183 | 93.2072 | 34.271 | 32.9803 | 34.9121 | 33.0667 | 32.9956 | 33.3213 | 34.596 | 34.1354 | 33.9445 | 37.1583 | 36.251 | 33.3464 | 34.4085 | 36.2396 | 36.4994 | 37.3732 | 36.228 | 33.0618 | 32.8172 | 34.5793 | 34.891 | 33.2396 | 34.4112 | 34.2468 | 34.3503 | 34.3142 | 34.3641 | 34.3358 | 34.0912 | 34.3261 | 36.2127 | 34.9375 | 36.5456 | 36.5828 | 33.4103 | 93.9207 | 94.0124 | 93.5392
2022-09-08 05:47 | 7:57 | 32.6375 | 31.4681 | 32.8822 | 36.6461 | 34.2873 | 34.1095 | 34.6833 | 35.5674 | 36.6079 | 37.6295 | 36.9939 | 38.2229 | 34.3886 | 34.398 | 34.1472 | 35.1537 | 34.8478 | 35.4672 | 36.2422 | 36.5374 | 17.863 | 18.5736 | 93.2679 | 34.1196 | 32.9791 | 34.9107 | 33.0641 | 32.9952 | 33.3348 | 34.5928 | 34.1284 | 33.9633 | 37.161 | 36.2479 | 33.3377 | 34.3929 | 36.2627 | 36.5018 | 37.3844 | 36.2388 | 33.0643 | 32.7979 | 34.5811 | 34.8845 | 33.2421 | 34.4102 | 34.2913 | 34.3664 | 34.3062 | 34.3676 | 34.3331 | 34.1126 | 34.3142 | 36.2155 | 34.9531 | 36.5564 | 36.586 | 33.4368 | 94.0974 | 94.1358 | 93.5544
2022-09-08 05:48 | 7:57 | 32.6668 | 31.4841 | 32.9668 | 36.7109 | 34.2894 | 34.1232 | 34.6811 | 35.5784 | 36.5925 | 37.6291 | 37.0061 | 38.221 | 34.4131 | 34.3715 | 34.1275 | 35.1681 | 34.8378 | 35.467 | 36.2481 | 36.5155 | 17.9983 | 18.3375 | 93.4771 | 34.0942 | 32.9726 | 34.9034 | 33.0571 | 32.9914 | 33.3412 | 34.5916 | 34.1162 | 33.9661 | 37.1841 | 36.2558 | 33.3513 | 34.4076 | 36.251 | 36.4998 | 37.357 | 36.2549 | 33.0685 | 32.7944 | 34.5656 | 34.8721 | 33.2171 | 34.3972 | 34.2656 | 34.3669 | 34.2966 | 34.3522 | 34.3338 | 34.1072 | 34.3062 | 36.1976 | 34.9484 | 36.5619 | 36.5852 | 33.4331 | 94.2322 | 94.3393 | 93.7389
2022-09-08 05:48 | 7:58 | 31.9058 | 26.2254 | 31.9658 | 36.7152 | 34.3071 | 34.112 | 34.6964 | 35.5885 | 36.578 | 37.6278 | 37.02 | 38.198 | 34.3947 | 34.3947 | 34.1335 | 35.15 | 34.8261 | 35.4615 | 36.2231 | 36.5443 | 20.2173 | 20.0354 | 93.5097 | 34.0463 | 32.9648 | 34.9148 | 33.071 | 32.9934 | 33.358 | 34.5767 | 34.1217 | 33.9411 | 37.1601 | 36.2427 | 33.3483 | 34.3821 | 36.2479 | 36.5132 | 37.3866 | 36.2396 | 33.0651 | 32.769 | 34.5632 | 34.8466 | 33.2142 | 34.399 | 34.2704 | 34.3692 | 34.2999 | 34.3597 | 34.3394 | 34.0955 | 34.2966 | 36.2131 | 34.9442 | 36.5658 | 36.5742 | 33.4403 | 94.3066 | 94.4662 | 93.8046
2022-09-08 05:48 | 7:58 | 31.559 | 24.4504 | 31.2252 | 36.5612 | 34.2902 | 34.1136 | 34.6966 | 35.5781 | 36.594 | 37.6216 | 36.9986 | 38.2151 | 34.4081 | 34.4099 | 34.1249 | 35.1745 | 34.8403 | 35.4845 | 36.2473 | 36.5207 | 20.3611 | 19.9171 | 93.7089 | 34.0899 | 32.9662 | 34.9198 | 33.0618 | 32.9833 | 33.3464 | 34.5852 | 34.1144 | 33.9487 | 37.1635 | 36.2824 | 33.3276 | 34.3738 | 36.2558 | 36.5131 | 37.3733 | 36.2627 | 33.0407 | 32.7799 | 34.5511 | 34.8775 | 33.2008 | 34.3997 | 34.2802 | 34.3773 | 34.2922 | 34.3612 | 34.3469 | 34.0926 | 34.2999 | 36.2252 | 34.9364 | 36.5637 | 36.593 | 33.4195 | 94.5352 | 94.5404 | 93.9289
2022-09-08 05:48 | 7:58 | 31.237 | 23.9482 | 30.5713 | 36.6134 | 34.3048 | 34.1093 | 34.7112 | 35.599 | 36.6087 | 37.6332 | 36.9956 | 38.2046 | 34.3986 | 34.3943 | 34.145 | 35.1486 | 34.8422 | 35.4584 | 36.2355 | 36.5187 | 20.2999 | 19.6341 | 93.6064 | 34.0205 | 32.9565 | 34.91 | 33.0643 | 32.9856 | 33.3377 | 34.5735 | 34.1363 | 33.9373 | 37.1544 | 36.2377 | 33.3412 | 34.3883 | 36.2427 | 36.5024 | 37.3663 | 36.251 | 33.0631 | 32.7787 | 34.5623 | 34.8784 | 33.1793 | 34.3953 | 34.2751 | 34.3742 | 34.2822 | 34.3588 | 34.3445 | 34.0971 | 34.2922 | 36.2165 | 34.9338 | 36.5648 | 36.597 | 33.4077 | 94.6102 | 94.702 | 93.922
2022-09-08 05:48 | 7:58 | 30.9612 | 23.9509 | 30.0552 | 36.4396 | 34.3002 | 34.1046 | 34.7043 | 35.5801 | 36.5991 | 37.6356 | 36.9903 | 38.2072 | 34.4095 | 34.3855 | 34.1253 | 35.1573 | 34.8622 | 35.4716 | 36.236 | 36.5262 | 20.994 | 19.6776 | 93.7477 | 34.1052 | 32.9696 | 34.921 | 33.0685 | 32.9784 | 33.3513 | 34.5977 | 34.1307 | 33.9404 | 37.1716 | 36.2599 | 33.3233 | 34.3952 | 36.2824 | 36.504 | 37.3822 | 36.2479 | 33.0604 | 32.7858 | 34.527 | 34.8798 | 33.191 | 34.3881 | 34.2851 | 34.3805 | 34.294 | 34.348 | 34.3536 | 34.0858 | 34.2822 | 36.2323 | 34.9452 | 36.5662 | 36.5954 | 33.4144 | 94.7595 | 94.7998 | 94.0256
2022-09-08 05:48 | 7:58 | 30.6719 | 23.9806 | 29.7452 | 36.3814 | 34.2874 | 34.11 | 34.7013 | 35.5746 | 36.5979 | 37.6264 | 37.0051 | 38.2186 | 34.397 | 34.3752 | 34.1209 | 35.1561 | 34.8478 | 35.4774 | 36.2323 | 36.5324 | 21.8959 | 19.7559 | 93.8788 | 33.9899 | 32.9609 | 34.9074 | 33.0651 | 32.9781 | 33.3483 | 34.583 | 34.1293 | 33.9339 | 37.1805 | 36.2607 | 33.3314 | 34.3963 | 36.2377 | 36.4992 | 37.3716 | 36.2558 | 33.0511 | 32.7641 | 34.5571 | 34.8671 | 33.1619 | 34.3895 | 34.2754 | 34.3716 | 34.2755 | 34.3584 | 34.3582 | 34.1067 | 34.294 | 36.1984 | 34.9396 | 36.5622 | 36.5734 | 33.4129 | 94.878 | 94.8896 | 94.1337
2022-09-08 05:49 | 7:59 | 30.3447 | 23.9186 | 29.6533 | 36.4559 | 34.3012 | 34.1041 | 34.7298 | 35.5739 | 36.5955 | 37.6262 | 37.0006 | 38.2073 | 34.4005 | 34.391 | 34.1375 | 35.1512 | 34.8518 | 35.4819 | 36.2265 | 36.5139 | 22.5903 | 19.8787 | 93.8495 | 34.1194 | 32.9639 | 34.9266 | 33.0407 | 32.9779 | 33.3276 | 34.5849 | 34.1251 | 33.9461 | 37.1766 | 36.2408 | 33.3286 | 34.3909 | 36.2599 | 36.5163 | 37.3856 | 36.2427 | 33.0746 | 32.7792 | 34.5203 | 34.8648 | 33.1792 | 34.3994 | 34.2948 | 34.3826 | 34.2824 | 34.3529 | 34.3729 | 34.0924 | 34.2755 | 36.2021 | 34.9361 | 36.5575 | 36.575 | 33.4205 | 94.9036 | 94.9499 | 94.1569
2022-09-08 05:49 | 7:59 | 30.0015 | 23.8861 | 29.2806 | 36.5073 | 34.3003 | 34.097 | 34.7273 | 35.5962 | 36.5893 | 37.6196 | 37.0057 | 38.1975 | 34.4 | 34.3965 | 34.1227 | 35.1615 | 34.8511 | 35.4745 | 36.2427 | 36.5193 | 23.1303 | 19.9121 | 93.8251 | 33.9135 | 32.9802 | 34.9282 | 33.0631 | 32.9701 | 33.3412 | 34.5907 | 34.1191 | 33.9415 | 37.1686 | 36.2622 | 33.3482 | 34.3701 | 36.2607 | 36.4995 | 37.3791 | 36.2824 | 33.0599 | 32.7504 | 34.5197 | 34.8703 | 33.1699 | 34.4104 | 34.2815 | 34.3757 | 34.2851 | 34.3391 | 34.3713 | 34.1087 | 34.2824 | 36.1939 | 34.9423 | 36.5703 | 36.5699 | 33.4065 | 94.9715 | 95.0417 | 94.1366
2022-09-08 05:49 | 7:59 | 29.4569 | 23.8591 | 29.0262 | 36.2812 | 34.2999 | 34.1045 | 34.7226 | 35.573 | 36.5958 | 37.6114 | 36.9945 | 38.1874 | 34.4074 | 34.4021 | 34.1307 | 35.1353 | 34.8513 | 35.4703 | 36.2254 | 36.502 | 23.5062 | 19.9336 | 93.8119 | 34.1015 | 32.9675 | 34.8928 | 33.0604 | 32.9807 | 33.3233 | 34.5742 | 34.1108 | 33.9553 | 37.1709 | 36.2607 | 33.3182 | 34.3855 | 36.2408 | 36.4899 | 37.3877 | 36.2377 | 33.052 | 32.7642 | 34.5404 | 34.8327 | 33.1737 | 34.41 | 34.2925 | 34.3972 | 34.3019 | 34.3411 | 34.3734 | 34.0774 | 34.2851 | 36.2107 | 34.9491 | 36.5492 | 36.5705 | 33.4129 | 94.9315 | 95.0562 | 94.1967
2022-09-08 05:49 | 7:59 | 29 | 23.8326 | 28.7965 | 36.3824 | 34.2937 | 34.1152 | 34.7316 | 35.5803 | 36.5695 | 37.6112 | 36.9835 | 38.2053 | 34.3894 | 34.3889 | 34.1131 | 35.1514 | 34.8476 | 35.46 | 36.2294 | 36.4989 | 23.77 | 20.0133 | 93.8843 | 33.9611 | 32.9827 | 34.9027 | 33.0511 | 32.9782 | 33.3314 | 34.564 | 34.1214 | 33.93 | 37.1669 | 36.2683 | 33.3353 | 34.3892 | 36.2622 | 36.4984 | 37.3756 | 36.2599 | 33.0743 | 32.7574 | 34.5282 | 34.8477 | 33.1503 | 34.4086 | 34.2835 | 34.4101 | 34.2693 | 34.3517 | 34.3648 | 34.077 | 34.3019 | 36.203 | 34.9425 | 36.5564 | 36.5778 | 33.3978 | 94.7681 | 94.9518 | 94.0601
2022-09-08 05:49 | 7:59 | 28.5278 | 23.5586 | 28.5136 | 36.2825 | 34.299 | 34.0715 | 34.7231 | 35.5698 | 36.596 | 37.6063 | 37.0063 | 38.209 | 34.4099 | 34.378 | 34.1284 | 35.1488 | 34.8575 | 35.4584 | 36.2212 | 36.5092 | 23.9372 | 19.8965 | 93.8291 | 34.0615 | 32.9813 | 34.9142 | 33.0746 | 32.988 | 33.3286 | 34.582 | 34.1186 | 33.9382 | 37.1578 | 36.257 | 33.3323 | 34.3852 | 36.2607 | 36.5008 | 37.3652 | 36.2607 | 33.061 | 32.7621 | 34.5228 | 34.8181 | 33.1649 | 34.3999 | 34.2959 | 34.3942 | 34.2663 | 34.3372 | 34.3543 | 34.0877 | 34.2693 | 36.185 | 34.9428 | 36.5687 | 36.5831 | 33.4063 | 94.5714 | 94.7816 | 93.9542
2022-09-08 05:49 | 7:59 | 28.1669 | 23.4997 | 28.3702 | 36.3277 | 34.2969 | 34.0873 | 34.736 | 35.5928 | 36.589 | 37.621 | 37.0057 | 38.2059 | 34.4082 | 34.3996 | 34.1225 | 35.1452 | 34.844 | 35.4533 | 36.2179 | 36.5033 | 24.1067 | 19.8787 | 93.5259 | 33.975 | 32.9671 | 34.8926 | 33.0599 | 32.9849 | 33.3482 | 34.5673 | 34.12 | 33.9319 | 37.155 | 36.2695 | 33.3321 | 34.3796 | 36.2683 | 36.5003 | 37.3482 | 36.2408 | 33.0766 | 32.7569 | 34.521 | 34.8257 | 33.1622 | 34.4051 | 34.28 | 34.3994 | 34.2629 | 34.3392 | 34.3762 | 34.0936 | 34.2663 | 36.1944 | 34.9393 | 36.556 | 36.5831 | 33.4014 | 94.2939 | 94.4875 | 93.7289
2022-09-08 05:50 | 7:59 | 27.8296 | 23.5 | 28.1095 | 36.3029 | 34.3258 | 34.1051 | 34.7173 | 35.5954 | 36.5815 | 37.6126 | 36.98 | 38.1996 | 34.4044 | 34.3981 | 34.1265 | 35.1521 | 34.8375 | 35.4452 | 36.217 | 36.4946 | 24.2199 | 19.8564 | 93.3456 | 33.9956 | 32.963 | 34.9169 | 33.052 | 32.9676 | 33.3182 | 34.5642 | 34.1239 | 33.9388 | 37.1509 | 36.2703 | 33.3242 | 34.3893 | 36.257 | 36.4997 | 37.3699 | 36.2622 | 33.0409 | 32.7467 | 34.5361 | 34.8289 | 33.1368 | 34.408 | 34.271 | 34.4098 | 34.2881 | 34.3167 | 34.3655 | 34.0849 | 34.2629 | 36.1781 | 34.9554 | 36.5481 | 36.5538 | 33.3997 | 94.0709 | 94.2643 | 93.5783
2022-09-08 05:50 | 8:00 | 27.6509 | 23.4634 | 27.9912 | 36.1782 | 34.3029 | 34.1062 | 34.7198 | 35.6002 | 36.5949 | 37.6066 | 36.9924 | 38.1948 | 34.394 | 34.3971 | 34.1048 | 35.1403 | 34.8545 | 35.4328 | 36.1963 | 36.4983 | 24.3263 | 19.8354 | 93.3265 | 34.0023 | 32.968 | 34.9171 | 33.0743 | 32.9858 | 33.3353 | 34.5538 | 34.111 | 33.9513 | 37.1764 | 36.2607 | 33.3299 | 34.3737 | 36.2695 | 36.4754 | 37.3716 | 36.2607 | 33.0745 | 32.7387 | 34.5071 | 34.8275 | 33.157 | 34.3934 | 34.2752 | 34.3983 | 34.2826 | 34.329 | 34.3598 | 34.0961 | 34.2881 | 36.1623 | 34.9744 | 36.5662 | 36.5621 | 33.408 | 93.9115 | 94.0781 | 93.5034
2022-09-08 05:50 | 8:00 | 27.4806 | 23.3843 | 27.9137 | 36.2229 | 34.3067 | 34.0982 | 34.7393 | 35.5802 | 36.5771 | 37.606 | 36.9839 | 38.1995 | 34.3912 | 34.3947 | 34.1127 | 35.145 | 34.8468 | 35.445 | 36.2018 | 36.5001 | 24.42 | 19.7768 | 93.3301 | 33.8969 | 32.9575 | 34.9167 | 33.061 | 32.9834 | 33.3323 | 34.5632 | 34.1128 | 33.9447 | 37.1614 | 36.2709 | 33.3265 | 34.3894 | 36.2703 | 36.4938 | 37.3577 | 36.2683 | 33.0524 | 32.7348 | 34.4945 | 34.8447 | 33.1413 | 34.4028 | 34.3047 | 34.4123 | 34.2842 | 34.3248 | 34.3743 | 34.0866 | 34.2826 | 36.2129 | 34.9411 | 36.5675 | 36.567 | 33.3682 | 93.7955 | 93.9476 | 93.4647
2022-09-08 05:50 | 8:00 | 27.3724 | 23.4202 | 27.9125 | 36.2761 | 34.2895 | 34.096 | 34.738 | 35.5649 | 36.5849 | 37.6062 | 36.9919 | 38.1895 | 34.4017 | 34.3805 | 34.1212 | 35.159 | 34.8573 | 35.4417 | 36.1925 | 36.4995 | 24.4947 | 19.8631 | 93.1282 | 33.9858 | 32.9682 | 34.9192 | 33.0766 | 32.973 | 33.3321 | 34.559 | 34.1179 | 33.9521 | 37.1755 | 36.2708 | 33.3462 | 34.3803 | 36.2607 | 36.4875 | 37.3652 | 36.257 | 33.0663 | 32.7275 | 34.5058 | 34.8057 | 33.1331 | 34.3976 | 34.2929 | 34.4114 | 34.3017 | 34.284 | 34.3795 | 34.0753 | 34.2842 | 36.185 | 34.956 | 36.5615 | 36.5799 | 33.3937 | 93.7287 | 93.8646 | 93.5033
2022-09-08 05:50 | 8:00 | 27.2581 | 23.4066 | 27.8394 | 36.1795 | 34.3012 | 34.0803 | 34.7308 | 35.5764 | 36.5804 | 37.6255 | 37.0078 | 38.1995 | 34.4007 | 34.374 | 34.12 | 35.1661 | 34.849 | 35.4284 | 36.1885 | 36.4895 | 24.5737 | 19.8874 | 93.0176 | 34.0488 | 32.9596 | 34.8996 | 33.0409 | 32.9891 | 33.3242 | 34.5691 | 34.123 | 33.948 | 37.16 | 36.2948 | 33.3383 | 34.3747 | 36.2709 | 36.5005 | 37.364 | 36.2695 | 33.0749 | 32.7389 | 34.4895 | 34.8018 | 33.1608 | 34.396 | 34.2865 | 34.4269 | 34.2799 | 34.3202 | 34.3848 | 34.065 | 34.3017 | 36.1829 | 34.9401 | 36.5651 | 36.5759 | 33.3727 | 93.5956 | 93.8232 | 93.4464
2022-09-08 05:50 | 8:00 | 27.0388 | 23.4104 | 27.5981 | 36.1807 | 34.3086 | 34.1 | 34.7599 | 35.5818 | 36.579 | 37.6025 | 36.9924 | 38.198 | 34.3736 | 34.3944 | 34.1172 | 35.1493 | 34.8591 | 35.4508 | 36.2057 | 36.4895 | 24.6469 | 19.9679 | 93.0772 | 34.0731 | 32.95 | 34.9365 | 33.0745 | 32.9809 | 33.3299 | 34.5538 | 34.1254 | 33.9474 | 37.1571 | 36.2725 | 33.3426 | 34.3857 | 36.2708 | 36.5004 | 37.3693 | 36.2703 | 33.0811 | 32.7312 | 34.49 | 34.8067 | 33.1493 | 34.3892 | 34.2938 | 34.4099 | 34.2571 | 34.3241 | 34.3667 | 34.0554 | 34.2799 | 36.1831 | 34.9577 | 36.5538 | 36.563 | 33.3841 | 93.5518 | 93.7848 | 93.4057
2022-09-08 05:51 | 8:01 | 26.7822 | 23.5392 | 27.4202 | 36.1898 | 34.3017 | 34.1078 | 34.7447 | 35.5699 | 36.5871 | 37.6094 | 37.0085 | 38.1931 | 34.3656 | 34.3735 | 34.1138 | 35.1628 | 34.8523 | 35.4291 | 36.2044 | 36.4887 | 24.6351 | 19.8974 | 93.1611 | 33.9839 | 32.9754 | 34.9367 | 33.0524 | 32.9815 | 33.3265 | 34.5356 | 34.1206 | 33.9616 | 37.1695 | 36.2826 | 33.3305 | 34.4038 | 36.2948 | 36.4746 | 37.3484 | 36.2607 | 33.066 | 32.713 | 34.4777 | 34.8127 | 33.1351 | 34.3887 | 34.2823 | 34.4132 | 34.2722 | 34.324 | 34.3972 | 34.062 | 34.2571 | 36.195 | 34.9502 | 36.5413 | 36.5652 | 33.3681 | 93.5272 | 93.7544 | 93.3661
2022-09-08 05:51 | 8:01 | 26.5283 | 23.4744 | 27.3072 | 36.0507 | 34.2989 | 34.1065 | 34.7326 | 35.5865 | 36.5767 | 37.6166 | 36.9971 | 38.1951 | 34.4075 | 34.3824 | 34.1032 | 35.1641 | 34.8584 | 35.4325 | 36.1746 | 36.4723 | 24.6309 | 19.8431 | 93.0895 | 33.8803 | 32.9834 | 34.919 | 33.0663 | 32.971 | 33.3462 | 34.5503 | 34.1211 | 33.9583 | 37.1575 | 36.2841 | 33.3185 | 34.4032 | 36.2725 | 36.4861 | 37.355 | 36.2709 | 33.0884 | 32.7293 | 34.4862 | 34.8127 | 33.1453 | 34.3996 | 34.2969 | 34.4238 | 34.2711 | 34.3012 | 34.376 | 34.0776 | 34.2722 | 36.1832 | 34.956 | 36.556 | 36.5725 | 33.3976 | 93.5089 | 93.6785 | 93.3159
2022-09-08 05:51 | 8:01 | 26.1091 | 23.3312 | 27.0659 | 36.0641 | 34.3104 | 34.098 | 34.7402 | 35.589 | 36.5876 | 37.6112 | 37.0135 | 38.2125 | 34.3735 | 34.3984 | 34.1028 | 35.1637 | 34.8615 | 35.4459 | 36.1763 | 36.4799 | 24.5866 | 19.6325 | 92.8811 | 33.7881 | 32.9651 | 34.9414 | 33.0749 | 32.971 | 33.3383 | 34.55 | 34.1237 | 33.9407 | 37.1729 | 36.285 | 33.3414 | 34.3708 | 36.2826 | 36.4978 | 37.3519 | 36.2708 | 33.0713 | 32.7136 | 34.4892 | 34.797 | 33.1194 | 34.3967 | 34.2948 | 34.4121 | 34.2737 | 34.314 | 34.3885 | 34.088 | 34.2711 | 36.1817 | 34.956 | 36.5535 | 36.578 | 33.3728 | 93.4073 | 93.6025 | 93.2064
2022-09-08 05:51 | 8:01 | 25.5577 | 23.407 | 26.6818 | 36.0946 | 34.3215 | 34.098 | 34.7398 | 35.5773 | 36.5983 | 37.6126 | 37.0094 | 38.1947 | 34.3871 | 34.3694 | 34.1191 | 35.1527 | 34.8654 | 35.4362 | 36.2004 | 36.4802 | 24.4874 | 19.6697 | 93.0561 | 33.919 | 32.9858 | 34.9252 | 33.0811 | 32.9858 | 33.3426 | 34.5637 | 34.1261 | 33.9564 | 37.1784 | 36.2652 | 33.3479 | 34.3912 | 36.2841 | 36.497 | 37.3664 | 36.2948 | 33.0759 | 32.7219 | 34.4851 | 34.8014 | 33.1099 | 34.4045 | 34.2814 | 34.4179 | 34.2811 | 34.2858 | 34.3854 | 34.0785 | 34.2737 | 36.1749 | 34.9476 | 36.5785 | 36.5628 | 33.378 | 93.366 | 93.4751 | 93.1919
2022-09-08 05:51 | 8:01 | 22.4127 | 23.3068 | 26.0555 | 35.9978 | 34.3095 | 34.0963 | 34.7609 | 35.5925 | 36.602 | 37.5969 | 37.0167 | 38.2107 | 34.379 | 34.3869 | 34.1082 | 35.1676 | 34.8787 | 35.4355 | 36.1663 | 36.4706 | 24.3457 | 19.7363 | 92.8884 | 33.943 | 32.9895 | 34.9209 | 33.066 | 32.9739 | 33.3305 | 34.5687 | 34.1296 | 33.9563 | 37.1808 | 36.289 | 33.3482 | 34.389 | 36.285 | 36.5074 | 37.3786 | 36.2725 | 33.0705 | 32.7131 | 34.5026 | 34.8053 | 33.131 | 34.393 | 34.2944 | 34.4172 | 34.2745 | 34.3149 | 34.3899 | 34.0915 | 34.2811 | 36.1982 | 34.9756 | 36.558 | 36.5671 | 33.3882 | 93.2907 | 93.4183 | 93.2577
2022-09-08 05:51 | 8:01 | 21.6922 | 23.1949 | 25.639 | 35.9848 | 34.3237 | 34.1135 | 34.7375 | 35.586 | 36.602 | 37.6127 | 37.0046 | 38.2164 | 34.3906 | 34.3765 | 34.109 | 35.1577 | 34.8587 | 35.4341 | 36.1736 | 36.4802 | 24.1713 | 19.7616 | 92.9434 | 33.9555 | 32.9759 | 34.9456 | 33.0884 | 32.9898 | 33.3185 | 34.565 | 34.1372 | 33.952 | 37.1686 | 36.2777 | 33.3326 | 34.3979 | 36.2652 | 36.5018 | 37.3806 | 36.2826 | 33.0771 | 32.7193 | 34.4941 | 34.8242 | 33.1171 | 34.3789 | 34.2867 | 34.4247 | 34.2622 | 34.2881 | 34.4002 | 34.0934 | 34.2745 | 36.1805 | 34.9433 | 36.55 | 36.5445 | 33.3811 | 93.1825 | 93.4111 | 93.1804
2022-09-08 05:52 | 8:01 | 21.5173 | 23.0363 | 25.4216 | 35.9245 | 34.3314 | 34.1068 | 34.7427 | 35.5871 | 36.5871 | 37.6001 | 36.999 | 38.2256 | 34.3708 | 34.3905 | 34.1128 | 35.1536 | 34.8546 | 35.4373 | 36.1941 | 36.4763 | 23.9618 | 19.72 | 92.9279 | 33.9879 | 32.9586 | 34.9291 | 33.0713 | 32.9853 | 33.3414 | 34.5386 | 34.1173 | 33.9654 | 37.1754 | 36.2711 | 33.3354 | 34.3899 | 36.289 | 36.5033 | 37.3687 | 36.2841 | 33.0573 | 32.7415 | 34.4833 | 34.7989 | 33.1275 | 34.4024 | 34.2902 | 34.426 | 34.27 | 34.2811 | 34.398 | 34.0834 | 34.2622 | 36.1796 | 34.9629 | 36.5537 | 36.5691 | 33.4108 | 93.1963 | 93.3122 | 93.1713
2022-09-08 05:52 | 8:02 | 21.2554 | 22.8152 | 25.181 | 35.9725 | 34.3381 | 34.1071 | 34.731 | 35.5852 | 36.5982 | 37.5945 | 37.0426 | 38.2012 | 34.3874 | 34.3809 | 34.1161 | 35.1536 | 34.8931 | 35.4542 | 36.1652 | 36.4913 | 23.7431 | 19.6829 | 92.7705 | 33.8901 | 32.9817 | 34.9475 | 33.0759 | 32.9844 | 33.3479 | 34.5558 | 34.1151 | 33.959 | 37.1801 | 36.2866 | 33.3555 | 34.3713 | 36.2777 | 36.5038 | 37.3677 | 36.285 | 33.0741 | 32.7226 | 34.4843 | 34.828 | 33.1196 | 34.3758 | 34.3059 | 34.4326 | 34.2511 | 34.2971 | 34.3715 | 34.0685 | 34.27 | 36.177 | 34.9509 | 36.5717 | 36.5741 | 33.3856 | 93.1362 | 93.1803 | 93.0487
2022-09-08 05:52 | 8:02 | 21.2803 | 22.7375 | 25.082 | 35.8831 | 34.3392 | 34.0986 | 34.7278 | 35.5763 | 36.6068 | 37.5973 | 37.0132 | 38.2184 | 34.3736 | 34.3786 | 34.1043 | 35.1659 | 34.8631 | 35.4423 | 36.1751 | 36.4889 | 23.5153 | 19.79 | 92.7507 | 33.8076 | 32.986 | 34.9238 | 33.0705 | 32.9961 | 33.3482 | 34.5439 | 34.1199 | 33.9952 | 37.1781 | 36.2898 | 33.3451 | 34.4068 | 36.2711 | 36.5028 | 37.3533 | 36.2652 | 33.0858 | 32.7141 | 34.4999 | 34.8114 | 33.1082 | 34.3835 | 34.2955 | 34.4374 | 34.2481 | 34.2868 | 34.3947 | 34.0765 | 34.2511 | 36.1904 | 34.9344 | 36.5626 | 36.5789 | 33.3935 | 93.0261 | 93.0941 | 93.0337
2022-09-08 05:52 | 8:02 | 21.1089 | 22.5244 | 24.9748 | 35.869 | 34.3358 | 34.0923 | 34.7379 | 35.5919 | 36.5931 | 37.6014 | 37.0388 | 38.2121 | 34.3689 | 34.3724 | 34.1247 | 35.165 | 34.8766 | 35.4308 | 36.1589 | 36.4832 | 23.2637 | 19.9959 | 92.82 | 33.7527 | 32.982 | 34.941 | 33.0771 | 32.9832 | 33.3326 | 34.5533 | 34.1283 | 33.9652 | 37.179 | 36.2994 | 33.3408 | 34.3933 | 36.2866 | 36.5053 | 37.3503 | 36.289 | 33.0919 | 32.7168 | 34.4837 | 34.8133 | 33.1008 | 34.394 | 34.306 | 34.443 | 34.2468 | 34.2945 | 34.4099 | 34.0995 | 34.2481 | 36.1903 | 34.9559 | 36.5865 | 36.5859 | 33.3864 | 92.9646 | 92.9652 | 92.9461
2022-09-08 05:52 | 8:02 | 21.1981 | 22.3943 | 24.8081 | 35.8557 | 34.3331 | 34.1031 | 34.7294 | 35.5912 | 36.5956 | 37.5988 | 37.0341 | 38.2269 | 34.381 | 34.3617 | 34.1311 | 35.1761 | 34.881 | 35.4439 | 36.1648 | 36.4823 | 22.9947 | 19.9944 | 92.6222 | 33.6345 | 32.9604 | 34.9542 | 33.0573 | 32.9786 | 33.3354 | 34.5483 | 34.1308 | 33.9518 | 37.1718 | 36.272 | 33.3383 | 34.3928 | 36.2898 | 36.4997 | 37.3625 | 36.2777 | 33.0814 | 32.7014 | 34.4878 | 34.813 | 33.1039 | 34.3846 | 34.3017 | 34.4445 | 34.261 | 34.2866 | 34.3943 | 34.0647 | 34.2468 | 36.2093 | 34.9661 | 36.5717 | 36.5823 | 33.3841 | 92.7909 | 92.8432 | 92.9116
2022-09-08 05:52 | 8:02 | 20.7754 | 22.1139 | 24.615 | 35.7727 | 34.3338 | 34.1107 | 34.7112 | 35.5977 | 36.5965 | 37.5956 | 37.011 | 38.222 | 34.3957 | 34.3917 | 34.1403 | 35.1753 | 34.8912 | 35.4237 | 36.177 | 36.4852 | 22.7678 | 19.7897 | 92.446 | 33.8866 | 32.981 | 34.926 | 33.0741 | 32.9787 | 33.3555 | 34.5298 | 34.1307 | 33.9675 | 37.1843 | 36.2702 | 33.3617 | 34.3711 | 36.2994 | 36.4982 | 37.3718 | 36.2711 | 33.0635 | 32.7111 | 34.4786 | 34.804 | 33.0737 | 34.3948 | 34.3127 | 34.4303 | 34.2557 | 34.2951 | 34.3855 | 34.0911 | 34.261 | 36.208 | 34.9526 | 36.576 | 36.5807 | 33.3981 | 92.6701 | 92.767 | 92.8105
2022-09-08 05:53 | 8:02 | 20.7576 | 22.0391 | 24.4742 | 35.8195 | 34.3394 | 34.1032 | 34.7115 | 35.5949 | 36.6019 | 37.6057 | 37.0203 | 38.2195 | 34.3959 | 34.3685 | 34.1137 | 35.1686 | 34.8765 | 35.4319 | 36.1776 | 36.4925 | 22.6049 | 19.8056 | 92.3136 | 33.6507 | 32.9636 | 34.9418 | 33.0858 | 32.9783 | 33.3451 | 34.545 | 34.1335 | 33.9703 | 37.1808 | 36.2818 | 33.3292 | 34.4115 | 36.272 | 36.5423 | 37.3754 | 36.2866 | 33.0778 | 32.7101 | 34.4646 | 34.8274 | 33.0777 | 34.3811 | 34.2973 | 34.4451 | 34.2413 | 34.288 | 34.3752 | 34.0847 | 34.2557 | 36.1922 | 34.9689 | 36.5735 | 36.5743 | 33.414 | 92.6077 | 92.6395 | 92.7744
2022-09-08 05:53 | 8:03 | 20.6218 | 21.8718 | 24.3081 | 35.7447 | 34.3469 | 34.088 | 34.7142 | 35.5906 | 36.6014 | 37.5996 | 37.0147 | 38.2423 | 34.3954 | 34.3758 | 34.1213 | 35.18 | 34.8863 | 35.4492 | 36.1648 | 36.4869 | 22.4132 | 19.6242 | 92.3275 | 33.6214 | 32.9831 | 34.9426 | 33.0919 | 32.9967 | 33.3408 | 34.5447 | 34.1427 | 33.9693 | 37.1931 | 36.274 | 33.3366 | 34.3909 | 36.2702 | 36.52 | 37.3507 | 36.2898 | 33.0867 | 32.7243 | 34.4768 | 34.8181 | 33.0822 | 34.3827 | 34.2945 | 34.4376 | 34.2545 | 34.2805 | 34.391 | 34.0961 | 34.2413 | 36.2177 | 34.9622 | 36.5682 | 36.5945 | 33.3975 | 92.4822 | 92.5217 | 92.678
2022-09-08 05:53 | 8:03 | 20.4653 | 21.6865 | 24.1549 | 35.7177 | 34.3445 | 34.1083 | 34.7264 | 35.5817 | 36.5886 | 37.6146 | 37.024 | 38.2096 | 34.3689 | 34.3758 | 34.1341 | 35.1871 | 34.8842 | 35.4365 | 36.14 | 36.4974 | 22.2695 | 19.4771 | 92.4621 | 33.493 | 32.9754 | 34.9284 | 33.0814 | 32.9862 | 33.3383 | 34.5645 | 34.1198 | 33.9693 | 37.2001 | 36.2797 | 33.3477 | 34.3829 | 36.2818 | 36.5081 | 37.3622 | 36.2994 | 33.0819 | 32.7044 | 34.4834 | 34.8172 | 33.0949 | 34.3788 | 34.3198 | 34.4296 | 34.2747 | 34.2697 | 34.3965 | 34.0809 | 34.2545 | 36.1981 | 34.9454 | 36.5574 | 36.5693 | 33.4001 | 92.4266 | 92.5083 | 92.6112
2022-09-08 05:53 | 8:03 | 20.3237 | 21.5366 | 24.0038 | 35.6281 | 34.3536 | 34.1019 | 34.7191 | 35.5817 | 36.6157 | 37.5941 | 37.0202 | 38.2182 | 34.3935 | 34.3582 | 34.1265 | 35.1846 | 34.8924 | 35.4304 | 36.1673 | 36.4893 | 22.1686 | 19.3727 | 92.2336 | 33.5709 | 32.9842 | 34.951 | 33.0635 | 32.975 | 33.3617 | 34.5423 | 34.1534 | 33.9846 | 37.1849 | 36.2642 | 33.3368 | 34.4073 | 36.274 | 36.5113 | 37.3623 | 36.272 | 33.0808 | 32.712 | 34.4751 | 34.816 | 33.0761 | 34.3685 | 34.2975 | 34.4382 | 34.2582 | 34.2489 | 34.4021 | 34.0857 | 34.2747 | 36.2041 | 34.9515 | 36.5539 | 36.5675 | 33.4117 | 92.2811 | 92.3919 | 92.5509
2022-09-08 05:53 | 8:03 | 20.1647 | 21.3643 | 23.8837 | 35.6489 | 34.3582 | 34.1034 | 34.7099 | 35.5829 | 36.6212 | 37.6044 | 37.0342 | 38.2462 | 34.3711 | 34.3744 | 34.1392 | 35.1855 | 34.8732 | 35.4332 | 36.1508 | 36.507 | 22.1179 | 19.404 | 92.133 | 33.5335 | 32.9723 | 34.9496 | 33.0778 | 32.9749 | 33.3292 | 34.5446 | 34.1254 | 33.9825 | 37.1999 | 36.288 | 33.3362 | 34.393 | 36.2797 | 36.5214 | 37.3681 | 36.2702 | 33.0812 | 32.702 | 34.4647 | 34.8248 | 33.0645 | 34.3588 | 34.311 | 34.4312 | 34.2571 | 34.2805 | 34.3889 | 34.0769 | 34.2582 | 36.2047 | 34.9845 | 36.5703 | 36.5787 | 33.4183 | 92.1347 | 92.2134 | 92.4394
2022-09-08 05:53 | 8:03 | 20.1183 | 21.2826 | 23.7598 | 35.6434 | 34.3729 | 34.1116 | 34.6981 | 35.5894 | 36.5998 | 37.5818 | 37.0113 | 38.2228 | 34.3761 | 34.3915 | 34.1096 | 35.1873 | 34.8954 | 35.4266 | 36.1355 | 36.5136 | 22.1045 | 19.2953 | 92.0874 | 33.5337 | 32.9675 | 34.9369 | 33.0867 | 32.9756 | 33.3366 | 34.556 | 34.1312 | 33.9802 | 37.207 | 36.2685 | 33.3486 | 34.3988 | 36.2642 | 36.503 | 37.3613 | 36.2818 | 33.0886 | 32.7002 | 34.4653 | 34.8278 | 33.056 | 34.3591 | 34.2995 | 34.4579 | 34.2629 | 34.2768 | 34.378 | 34.0633 | 34.2571 | 36.2203 | 34.9597 | 36.5639 | 36.5722 | 33.3986 | 92.096 | 92.102 | 92.3999
2022-09-08 05:54 | 8:04 | 20.0217 | 21.1335 | 23.612 | 35.6722 | 34.3713 | 34.0904 | 34.699 | 35.5788 | 36.6112 | 37.5906 | 37.0147 | 38.2288 | 34.3829 | 34.355 | 34.1291 | 35.185 | 34.9041 | 35.4303 | 36.1563 | 36.5034 | 22.0603 | 19.1722 | 91.9817 | 33.5745 | 32.9684 | 34.942 | 33.0819 | 32.986 | 33.3477 | 34.5579 | 34.1349 | 33.9728 | 37.1821 | 36.297 | 33.3458 | 34.3958 | 36.288 | 36.5224 | 37.3748 | 36.274 | 33.0701 | 32.7016 | 34.4771 | 34.8085 | 33.0596 | 34.3635 | 34.3152 | 34.4456 | 34.2689 | 34.2759 | 34.3996 | 34.076 | 34.2629 | 36.2037 | 34.9616 | 36.5817 | 36.5808 | 33.4172 | 91.8821 | 91.9444 | 92.2508
2022-09-08 05:54 | 8:04 | 19.8891 | 20.9359 | 23.4629 | 35.5088 | 34.3734 | 34.0939 | 34.6956 | 35.5704 | 36.6159 | 37.5979 | 37.0006 | 38.23 | 34.3669 | 34.3686 | 34.123 | 35.1708 | 34.9046 | 35.4335 | 36.1538 | 36.5029 | 22.0328 | 19.0907 | 91.8522 | 33.5254 | 32.9688 | 34.9455 | 33.0808 | 32.9746 | 33.3368 | 34.5599 | 34.1357 | 33.989 | 37.1935 | 36.2729 | 33.3585 | 34.4123 | 36.2685 | 36.5099 | 37.3678 | 36.2797 | 33.0545 | 32.7099 | 34.4616 | 34.806 | 33.0514 | 34.3685 | 34.312 | 34.4412 | 34.2512 | 34.2773 | 34.3981 | 34.0837 | 34.2689 | 36.2081 | 34.9469 | 36.5699 | 36.5859 | 33.409 | 91.7341 | 91.8055 | 92.191
2022-09-08 05:54 | 8:04 | 19.746 | 20.8502 | 23.3481 | 35.6438 | 34.3648 | 34.1031 | 34.7029 | 35.5935 | 36.608 | 37.6017 | 37.0193 | 38.2427 | 34.3615 | 34.3723 | 34.1213 | 35.1826 | 34.9045 | 35.4278 | 36.16 | 36.5162 | 21.9966 | 18.9537 | 91.81 | 33.5134 | 32.9681 | 34.9354 | 33.0812 | 32.98 | 33.3362 | 34.5541 | 34.1363 | 33.9875 | 37.1733 | 36.2925 | 33.3351 | 34.3961 | 36.297 | 36.516 | 37.3674 | 36.2642 | 33.0577 | 32.6943 | 34.476 | 34.8092 | 33.0493 | 34.3706 | 34.3025 | 34.4437 | 34.28 | 34.2559 | 34.3971 | 34.0998 | 34.2512 | 36.2063 | 34.9506 | 36.5838 | 36.5834 | 33.4124 | 91.6856 | 91.6675 | 92.1196
2022-09-08 05:54 | 8:04 | 19.7381 | 20.7698 | 23.252 | 35.4406 | 34.3543 | 34.1091 | 34.6784 | 35.5839 | 36.5924 | 37.6105 | 37.0078 | 38.2202 | 34.3704 | 34.3692 | 34.1344 | 35.18 | 34.8887 | 35.4338 | 36.1596 | 36.5127 | 21.9376 | 18.9167 | 91.7156 | 33.5828 | 32.9758 | 34.9462 | 33.0886 | 32.9744 | 33.3486 | 34.567 | 34.1334 | 33.9657 | 37.2043 | 36.2627 | 33.3548 | 34.3901 | 36.2729 | 36.5197 | 37.3761 | 36.288 | 33.0804 | 32.6882 | 34.4675 | 34.8216 | 33.0191 | 34.341 | 34.3123 | 34.4477 | 34.251 | 34.2679 | 34.3947 | 34.0547 | 34.28 | 36.2184 | 34.9496 | 36.5699 | 36.5819 | 33.4145 | 91.6136 | 91.5546 | 92.0222
2022-09-08 05:54 | 8:04 | 19.7849 | 20.6174 | 23.1617 | 35.5037 | 34.3762 | 34.1014 | 34.685 | 35.5795 | 36.6211 | 37.6015 | 37.0215 | 38.2335 | 34.3675 | 34.3657 | 34.129 | 35.1717 | 34.8933 | 35.4257 | 36.141 | 36.5131 | 21.8828 | 18.8768 | 91.8418 | 33.4571 | 32.9917 | 34.9271 | 33.0701 | 32.9654 | 33.3458 | 34.5508 | 34.1292 | 33.9729 | 37.1916 | 36.268 | 33.3366 | 34.3759 | 36.2925 | 36.5168 | 37.3775 | 36.2685 | 33.0667 | 32.6839 | 34.4702 | 34.8128 | 33.0322 | 34.3583 | 34.2951 | 34.4351 | 34.2677 | 34.2634 | 34.3805 | 34.0644 | 34.251 | 36.2141 | 34.9346 | 36.574 | 36.5828 | 33.4066 | 91.6253 | 91.6111 | 92.0906
2022-09-08 05:54 | 8:04 | 19.5863 | 20.5636 | 23.097 | 35.4312 | 34.3655 | 34.104 | 34.6685 | 35.5787 | 36.6181 | 37.6112 | 37.0245 | 38.2297 | 34.3641 | 34.3557 | 34.131 | 35.1876 | 34.8941 | 35.434 | 36.1522 | 36.5122 | 21.8643 | 18.7611 | 91.823 | 33.3884 | 32.9896 | 34.9313 | 33.0545 | 32.9718 | 33.3585 | 34.5505 | 34.1373 | 33.9838 | 37.1822 | 36.2744 | 33.3507 | 34.374 | 36.2627 | 36.5182 | 37.3797 | 36.297 | 33.0735 | 32.6833 | 34.4613 | 34.8303 | 32.9974 | 34.3644 | 34.3191 | 34.4478 | 34.2712 | 34.2433 | 34.374 | 34.0762 | 34.2677 | 36.2364 | 34.9492 | 36.5769 | 36.5865 | 33.4343 | 91.7463 | 91.637 | 92.1594
2022-09-08 05:55 | 8:04 | 19.3821 | 20.3591 | 22.9546 | 35.4361 | 34.3598 | 34.1033 | 34.6723 | 35.5673 | 36.6149 | 37.5949 | 37.0271 | 38.235 | 34.3676 | 34.3825 | 34.1356 | 35.1637 | 34.9069 | 35.4462 | 36.1417 | 36.516 | 21.8238 | 18.6875 | 91.8762 | 33.5738 | 32.9906 | 34.9209 | 33.0577 | 32.9818 | 33.3351 | 34.5652 | 34.1385 | 33.971 | 37.1891 | 36.2692 | 33.3441 | 34.4029 | 36.268 | 36.5174 | 37.3721 | 36.2729 | 33.0778 | 32.6825 | 34.4537 | 34.8247 | 33.0167 | 34.3421 | 34.326 | 34.4459 | 34.2596 | 34.2467 | 34.3944 | 34.0864 | 34.2712 | 36.218 | 34.9555 | 36.5861 | 36.5717 | 33.4268 | 91.8346 | 91.7645 | 92.2373
2022-09-08 05:55 | 8:05 | 19.3835 | 20.2763 | 22.8604 | 35.3497 | 34.3743 | 34.1157 | 34.6684 | 35.5824 | 36.62 | 37.6056 | 37.0195 | 38.2241 | 34.3522 | 34.3747 | 34.1563 | 35.1758 | 34.9008 | 35.4273 | 36.1459 | 36.5244 | 21.7805 | 18.6652 | 92.0118 | 33.5172 | 32.9652 | 34.9116 | 33.0804 | 32.965 | 33.3548 | 34.5472 | 34.1374 | 33.9869 | 37.1899 | 36.2714 | 33.3295 | 34.4019 | 36.2744 | 36.5361 | 37.3769 | 36.2925 | 33.0696 | 32.6861 | 34.4685 | 34.8066 | 33.0057 | 34.3474 | 34.3135 | 34.4329 | 34.265 | 34.2441 | 34.3735 | 34.0787 | 34.2596 | 36.2174 | 34.9489 | 36.5669 | 36.5749 | 33.4092 | 91.9522 | 91.9194 | 92.3143
2022-09-08 05:55 | 8:05 | 19.2188 | 20.1234 | 22.7129 | 35.4025 | 34.3795 | 34.0989 | 34.6571 | 35.5878 | 36.6127 | 37.6127 | 37.0204 | 38.2308 | 34.3597 | 34.3441 | 34.1332 | 35.1812 | 34.9159 | 35.4277 | 36.1382 | 36.5131 | 21.726 | 18.5771 | 92.1625 | 33.5261 | 32.9616 | 34.9181 | 33.0667 | 32.9776 | 33.3366 | 34.5446 | 34.1373 | 33.9784 | 37.1948 | 36.2674 | 33.3319 | 34.389 | 36.2692 | 36.5109 | 37.3709 | 36.2627 | 33.059 | 32.677 | 34.4583 | 34.7957 | 32.9875 | 34.3342 | 34.3122 | 34.4528 | 34.2678 | 34.2525 | 34.3824 | 34.0788 | 34.265 | 36.2328 | 34.9325 | 36.5871 | 36.5924 | 33.4118 | 92.1619 | 92.1276 | 92.463
2022-09-08 05:55 | 8:05 | 19.0652 | 19.9915 | 22.5627 | 35.3957 | 34.3848 | 34.1068 | 34.6654 | 35.5665 | 36.6163 | 37.606 | 37.0157 | 38.2276 | 34.3612 | 34.3611 | 34.1399 | 35.1746 | 34.8945 | 35.4156 | 36.1381 | 36.5232 | 21.6705 | 18.4575 | 92.2238 | 33.391 | 32.965 | 34.9221 | 33.0735 | 32.9582 | 33.3507 | 34.5677 | 34.1288 | 33.9703 | 37.1895 | 36.2642 | 33.3385 | 34.3883 | 36.2714 | 36.5253 | 37.3642 | 36.268 | 33.0521 | 32.6951 | 34.4301 | 34.8047 | 32.9801 | 34.3607 | 34.3412 | 34.4457 | 34.2611 | 34.2545 | 34.3984 | 34.0629 | 34.2678 | 36.2288 | 34.9331 | 36.5596 | 36.5873 | 33.4292 | 92.2818 | 92.3662 | 92.6219
2022-09-08 05:55 | 8:05 | 19.0672 | 19.9377 | 22.4991 | 35.3572 | 34.3667 | 34.0885 | 34.6596 | 35.5759 | 36.6064 | 37.5898 | 37.0294 | 38.2265 | 34.3588 | 34.363 | 34.1373 | 35.1775 | 34.8987 | 35.4194 | 36.127 | 36.5044 | 21.6132 | 18.4557 | 92.2484 | 33.4922 | 32.9654 | 34.931 | 33.0778 | 32.9608 | 33.3441 | 34.5508 | 34.1287 | 33.9819 | 37.1816 | 36.2504 | 33.3248 | 34.3861 | 36.2674 | 36.5134 | 37.3628 | 36.2744 | 33.0584 | 32.6534 | 34.4549 | 34.7906 | 32.9724 | 34.3311 | 34.3055 | 34.4386 | 34.2842 | 34.2448 | 34.3694 | 34.0591 | 34.2611 | 36.2157 | 34.9284 | 36.5726 | 36.6045 | 33.419 | 92.4649 | 92.5506 | 92.7184
2022-09-08 05:55 | 8:05 | 19.0359 | 19.8731 | 22.4006 | 35.2794 | 34.3972 | 34.1031 | 34.6559 | 35.5723 | 36.6073 | 37.5926 | 37.0101 | 38.2281 | 34.348 | 34.3513 | 34.1474 | 35.1801 | 34.8999 | 35.4043 | 36.1174 | 36.5165 | 21.5715 | 18.3588 | 92.3019 | 33.3816 | 32.9557 | 34.8995 | 33.0696 | 32.984 | 33.3295 | 34.5415 | 34.1253 | 33.9778 | 37.1874 | 36.2621 | 33.3485 | 34.3826 | 36.2642 | 36.5072 | 37.3732 | 36.2692 | 33.0442 | 32.6562 | 34.4204 | 34.8017 | 32.9782 | 34.3288 | 34.3285 | 34.455 | 34.2468 | 34.2525 | 34.3869 | 34.0681 | 34.2842 | 36.2303 | 34.9366 | 36.5807 | 36.5842 | 33.4219 | 92.6714 | 92.6991 | 92.7873
2022-09-08 05:56 | 8:06 | 18.9022 | 19.6975 | 22.3115 | 35.3429 | 34.376 | 34.0885 | 34.6476 | 35.5683 | 36.6225 | 37.5957 | 37.029 | 38.224 | 34.3584 | 34.3515 | 34.1441 | 35.1702 | 34.9032 | 35.4186 | 36.1211 | 36.5118 | 21.5189 | 18.3051 | 92.3493 | 33.1399 | 32.972 | 34.9174 | 33.059 | 32.9608 | 33.3319 | 34.5447 | 34.1252 | 33.9574 | 37.1979 | 36.2549 | 33.3324 | 34.3713 | 36.2504 | 36.5112 | 37.3563 | 36.2714 | 33.062 | 32.6528 | 34.4311 | 34.8128 | 32.9585 | 34.345 | 34.3392 | 34.4164 | 34.2913 | 34.2548 | 34.3765 | 34.0578 | 34.2468 | 36.2299 | 34.9357 | 36.5759 | 36.5797 | 33.41 | 92.8361 | 92.9046 | 92.8481
2022-09-08 05:56 | 8:06 | 18.8505 | 19.6047 | 22.2005 | 35.2985 | 34.3885 | 34.0769 | 34.6438 | 35.564 | 36.6215 | 37.5969 | 36.9929 | 38.2365 | 34.3529 | 34.3565 | 34.1461 | 35.1803 | 34.8935 | 35.4061 | 36.1154 | 36.5183 | 21.4823 | 18.269 | 92.7104 | 33.156 | 32.9648 | 34.9033 | 33.0521 | 32.9569 | 33.3385 | 34.5467 | 34.1243 | 33.9631 | 37.1742 | 36.2556 | 33.342 | 34.3845 | 36.2621 | 36.5085 | 37.3677 | 36.2674 | 33.0359 | 32.6501 | 34.4335 | 34.7935 | 32.9504 | 34.3416 | 34.32 | 34.4336 | 34.2656 | 34.2212 | 34.3905 | 34.066 | 34.2913 | 36.2278 | 34.9322 | 36.5778 | 36.6031 | 33.4217 | 93.0419 | 93.1493 | 93.0352
2022-09-08 05:56 | 8:06 | 18.8776 | 19.5617 | 22.1354 | 35.2396 | 34.3854 | 34.0706 | 34.638 | 35.5696 | 36.609 | 37.5923 | 37.0073 | 38.2165 | 34.3391 | 34.3451 | 34.1529 | 35.164 | 34.8934 | 35.4006 | 36.1133 | 36.5185 | 21.4568 | 18.1957 | 92.8233 | 33.4152 | 32.9694 | 34.8978 | 33.0584 | 32.963 | 33.3248 | 34.5553 | 34.1013 | 33.9624 | 37.2012 | 36.2529 | 33.328 | 34.3724 | 36.2549 | 36.5145 | 37.3676 | 36.2642 | 33.0209 | 32.6564 | 34.4372 | 34.7935 | 32.9422 | 34.3332 | 34.3113 | 34.4273 | 34.2704 | 34.2496 | 34.3809 | 34.0692 | 34.2656 | 36.2061 | 34.9256 | 36.5988 | 36.5827 | 33.4113 | 93.2024 | 93.402 | 93.0253
2022-09-08 05:56 | 8:06 | 18.7244 | 19.4468 | 22.0414 | 35.1818 | 34.3899 | 34.0925 | 34.6219 | 35.5671 | 36.6165 | 37.5919 | 37.0043 | 38.222 | 34.3411 | 34.3516 | 34.1271 | 35.1539 | 34.8973 | 35.4092 | 36.1291 | 36.5078 | 21.4036 | 18.169 | 92.938 | 33.3067 | 32.9559 | 34.9052 | 33.0442 | 32.9569 | 33.3485 | 34.5443 | 34.1129 | 33.964 | 37.1795 | 36.2594 | 33.3466 | 34.367 | 36.2556 | 36.5254 | 37.3655 | 36.2504 | 33.0334 | 32.6247 | 34.4278 | 34.7696 | 32.9269 | 34.3311 | 34.3247 | 34.4329 | 34.2802 | 34.248 | 34.3786 | 34.048 | 34.2704 | 36.2264 | 34.9413 | 36.5772 | 36.5731 | 33.4019 | 93.4584 | 93.6741 | 93.2103
2022-09-08 05:56 | 8:06 | 18.753 | 19.4166 | 21.9617 | 35.2258 | 34.4002 | 34.113 | 34.631 | 35.5695 | 36.6128 | 37.62 | 36.9933 | 38.2127 | 34.3517 | 34.3424 | 34.1484 | 35.1735 | 34.8965 | 35.4008 | 36.1129 | 36.5123 | 21.3683 | 18.1452 | 93.0828 | 33.3109 | 32.9628 | 34.9014 | 33.062 | 32.9413 | 33.3324 | 34.5447 | 34.0981 | 33.9756 | 37.2009 | 36.2595 | 33.3226 | 34.3683 | 36.2529 | 36.5104 | 37.3703 | 36.2621 | 33.0455 | 32.6491 | 34.4142 | 34.7687 | 32.9276 | 34.3335 | 34.3203 | 34.4172 | 34.2751 | 34.2409 | 34.3724 | 34.0474 | 34.2802 | 36.219 | 34.9517 | 36.5923 | 36.5875 | 33.4043 | 93.6873 | 93.9177 | 93.3278
2022-09-08 05:56 | 8:06 | 18.5302 | 19.2409 | 21.874 | 35.2471 | 34.398 | 34.1023 | 34.6296 | 35.554 | 36.6035 | 37.5953 | 37.0015 | 38.2326 | 34.3372 | 34.3396 | 34.1334 | 35.1825 | 34.889 | 35.4005 | 36.1094 | 36.5031 | 21.3371 | 17.9896 | 93.2438 | 33.2726 | 32.9619 | 34.8972 | 33.0359 | 32.9558 | 33.342 | 34.5394 | 34.1122 | 33.9622 | 37.1927 | 36.2488 | 33.3388 | 34.3809 | 36.2594 | 36.5051 | 37.3503 | 36.2549 | 33.0407 | 32.6323 | 34.413 | 34.7808 | 32.9177 | 34.3579 | 34.3395 | 34.4199 | 34.2851 | 34.2316 | 34.3617 | 34.046 | 34.2751 | 36.2102 | 34.9367 | 36.565 | 36.5896 | 33.4118 | 93.9124 | 94.1689 | 93.4702
2022-09-08 05:57 | 8:06 | 18.535 | 19.216 | 21.7908 | 35.1504 | 34.3715 | 34.0724 | 34.6229 | 35.5521 | 36.6017 | 37.5887 | 36.9924 | 38.2197 | 34.3392 | 34.3479 | 34.1373 | 35.1647 | 34.8862 | 35.3951 | 36.0918 | 36.4893 | 21.3078 | 17.994 | 93.4524 | 33.1029 | 32.9667 | 34.9068 | 33.0209 | 32.9483 | 33.328 | 34.5392 | 34.1083 | 33.9732 | 37.1795 | 36.2427 | 33.3263 | 34.3708 | 36.2595 | 36.5043 | 37.354 | 36.2556 | 33.0457 | 32.6361 | 34.406 | 34.7614 | 32.9051 | 34.3336 | 34.3274 | 34.4001 | 34.2754 | 34.232 | 34.3917 | 34.0527 | 34.2851 | 36.2102 | 34.9363 | 36.5663 | 36.5881 | 33.404 | 94.0685 | 94.3426 | 93.6205
2022-09-08 05:57 | 8:07 | 18.4565 | 19.1133 | 21.7001 | 35.1332 | 34.3947 | 34.0828 | 34.6062 | 35.5442 | 36.5913 | 37.5824 | 36.9961 | 38.2233 | 34.3167 | 34.3382 | 34.1338 | 35.162 | 34.8668 | 35.3925 | 36.088 | 36.5054 | 21.2708 | 17.9391 | 93.5429 | 33.3845 | 32.9591 | 34.8893 | 33.0334 | 32.9433 | 33.3466 | 34.5511 | 34.0908 | 33.954 | 37.1851 | 36.2415 | 33.3353 | 34.3619 | 36.2488 | 36.4995 | 37.3625 | 36.2529 | 33.0375 | 32.6201 | 34.4015 | 34.7645 | 32.9161 | 34.344 | 34.3328 | 34.4151 | 34.2948 | 34.2174 | 34.3685 | 34.0376 | 34.2754 | 36.2102 | 34.9184 | 36.5778 | 36.5838 | 33.4062 | 94.3184 | 94.5926 | 93.7969
2022-09-08 05:57 | 8:07 | 18.4465 | 19.0997 | 21.6853 | 35.1221 | 34.4099 | 34.0766 | 34.6161 | 35.5538 | 36.5964 | 37.5933 | 37.0015 | 38.2172 | 34.329 | 34.3254 | 34.1404 | 35.1657 | 34.8752 | 35.3923 | 36.0907 | 36.5115 | 21.2427 | 17.8943 | 93.7036 | 33.311 | 32.9782 | 34.8845 | 33.0455 | 32.9331 | 33.3226 | 34.538 | 34.1103 | 33.9628 | 37.1745 | 36.2614 | 33.3291 | 34.3718 | 36.2427 | 36.5179 | 37.376 | 36.2594 | 33.0444 | 32.6058 | 34.3941 | 34.7407 | 32.9151 | 34.3444 | 34.3128 | 34.4106 | 34.2815 | 34.225 | 34.3758 | 34.0379 | 34.2948 | 36.2129 | 34.9374 | 36.5697 | 36.5817 | 33.4131 | 94.4618 | 94.7859 | 93.9181
2022-09-08 05:57 | 8:07 | 18.3086 | 18.9346 | 21.5903 | 35.1447 | 34.3943 | 34.0822 | 34.5983 | 35.5672 | 36.5966 | 37.5905 | 36.9898 | 38.2039 | 34.3248 | 34.3443 | 34.1337 | 35.1461 | 34.8752 | 35.4133 | 36.0919 | 36.4924 | 21.2191 | 17.8603 | 93.873 | 33.1715 | 32.9564 | 34.8999 | 33.0407 | 32.9238 | 33.3388 | 34.5268 | 34.1087 | 33.9619 | 37.1691 | 36.2745 | 33.3466 | 34.364 | 36.2415 | 36.4977 | 37.3438 | 36.2595 | 33.0289 | 32.605 | 34.3983 | 34.7567 | 32.9036 | 34.3359 | 34.3345 | 34.4168 | 34.2925 | 34.2447 | 34.3758 | 34.0539 | 34.2815 | 36.2197 | 34.9403 | 36.5651 | 36.5922 | 33.4058 | 94.6734 | 95.0121 | 94.0885
2022-09-08 05:57 | 8:07 | 18.3129 | 18.9323 | 21.5337 | 35.1373 | 34.3855 | 34.0831 | 34.6128 | 35.5429 | 36.6104 | 37.6019 | 37.0043 | 38.201 | 34.284 | 34.3375 | 34.1327 | 35.1565 | 34.8763 | 35.3976 | 36.1084 | 36.4998 | 21.2169 | 17.8831 | 94.0155 | 33.3362 | 32.9292 | 34.9025 | 33.0457 | 32.9214 | 33.3263 | 34.5402 | 34.1004 | 33.9508 | 37.1601 | 36.2381 | 33.3255 | 34.3498 | 36.2614 | 36.5113 | 37.3539 | 36.2488 | 33.0232 | 32.6006 | 34.3816 | 34.7369 | 32.9014 | 34.3496 | 34.3254 | 34.4091 | 34.2835 | 34.2409 | 34.3582 | 34.0547 | 34.2925 | 36.1869 | 34.946 | 36.5881 | 36.5872 | 33.3767 | 94.7808 | 95.2025 | 94.1887
2022-09-08 05:57 | 8:07 | 18.2273 | 18.8763 | 21.4643 | 35.082 | 34.3752 | 34.0737 | 34.6188 | 35.5585 | 36.5985 | 37.594 | 36.9938 | 38.2139 | 34.3202 | 34.3347 | 34.1441 | 35.1562 | 34.8777 | 35.3839 | 36.0823 | 36.4951 | 21.1756 | 17.7886 | 94.1161 | 33.291 | 32.9626 | 34.8965 | 33.0375 | 32.9232 | 33.3353 | 34.5411 | 34.0871 | 33.9516 | 37.1983 | 36.2394 | 33.3314 | 34.373 | 36.2745 | 36.4931 | 37.3445 | 36.2427 | 33.0316 | 32.5886 | 34.3791 | 34.7228 | 32.8762 | 34.349 | 34.3324 | 34.4137 | 34.2959 | 34.2475 | 34.3744 | 34.0361 | 34.2835 | 36.2016 | 34.9376 | 36.5759 | 36.5801 | 33.3681 | 94.9052 | 95.3533 | 94.2154
2022-09-08 05:58 | 8:08 | 18.2307 | 18.7842 | 21.4176 | 34.9411 | 34.391 | 34.0881 | 34.6141 | 35.5583 | 36.5912 | 37.5882 | 37.01 | 38.2045 | 34.3241 | 34.313 | 34.1194 | 35.1749 | 34.8649 | 35.3739 | 36.0754 | 36.4998 | 21.1717 | 17.7926 | 94.1907 | 33.2315 | 32.9346 | 34.8795 | 33.0444 | 32.939 | 33.3291 | 34.5317 | 34.0817 | 33.9581 | 37.175 | 36.2538 | 33.3148 | 34.3602 | 36.2381 | 36.5029 | 37.3314 | 36.2415 | 33.029 | 32.5984 | 34.389 | 34.7236 | 32.8779 | 34.3373 | 34.3556 | 34.3952 | 34.28 | 34.2458 | 34.3915 | 34.0465 | 34.2959 | 36.1948 | 34.935 | 36.5876 | 36.5627 | 33.377 | 95.1165 | 95.5205 | 94.3726
2022-09-08 05:58 | 8:08 | 18.1763 | 18.7625 | 21.3556 | 35.0686 | 34.3965 | 34.0776 | 34.6089 | 35.554 | 36.6037 | 37.58 | 36.9995 | 38.2007 | 34.324 | 34.3244 | 34.1402 | 35.1521 | 34.8872 | 35.386 | 36.0954 | 36.4825 | 21.1412 | 17.7645 | 94.336 | 33.0922 | 32.9505 | 34.8733 | 33.0289 | 32.9347 | 33.3466 | 34.5418 | 34.0885 | 33.9672 | 37.1834 | 36.244 | 33.3215 | 34.3633 | 36.2394 | 36.5156 | 37.3515 | 36.2614 | 33.0267 | 32.6164 | 34.3639 | 34.726 | 32.8691 | 34.3445 | 34.3549 | 34.3969 | 34.271 | 34.2386 | 34.355 | 34.0412 | 34.28 | 36.1925 | 34.9328 | 36.5842 | 36.5639 | 33.389 | 95.2245 | 95.5944 | 94.3663
2022-09-08 05:58 | 8:08 | 18.1055 | 18.7037 | 21.2894 | 35.0443 | 34.4021 | 34.0735 | 34.6063 | 35.5537 | 36.5994 | 37.5775 | 36.9944 | 38.2121 | 34.3012 | 34.3288 | 34.124 | 35.1539 | 34.8938 | 35.3858 | 36.0767 | 36.4757 | 21.1243 | 17.6897 | 94.3565 | 33.345 | 32.9529 | 34.8752 | 33.0232 | 32.91 | 33.3255 | 34.5323 | 34.0968 | 33.9462 | 37.166 | 36.2577 | 33.3043 | 34.3585 | 36.2538 | 36.5045 | 37.3295 | 36.2745 | 33.0253 | 32.5747 | 34.3668 | 34.7204 | 32.8653 | 34.315 | 34.3554 | 34.3822 | 34.2752 | 34.2449 | 34.3686 | 34.0449 | 34.271 | 36.18 | 34.9357 | 36.5761 | 36.5611 | 33.3715 | 95.3944 | 95.6703 | 94.5804
2022-09-08 05:58 | 8:08 | 18.0117 | 18.631 | 21.2095 | 35.0715 | 34.3889 | 34.0875 | 34.587 | 35.5705 | 36.5857 | 37.5552 | 36.9832 | 38.2117 | 34.314 | 34.3239 | 34.1247 | 35.1458 | 34.8712 | 35.3778 | 36.0682 | 36.482 | 21.1353 | 17.6483 | 94.4129 | 33.0642 | 32.9354 | 34.8578 | 33.0316 | 32.9076 | 33.3314 | 34.5216 | 34.0915 | 33.932 | 37.1763 | 36.25 | 33.3085 | 34.3567 | 36.244 | 36.507 | 37.3403 | 36.2381 | 33.0189 | 32.5826 | 34.365 | 34.7115 | 32.8644 | 34.341 | 34.3584 | 34.3891 | 34.3047 | 34.2635 | 34.3723 | 34.0307 | 34.2752 | 36.1827 | 34.9237 | 36.5658 | 36.5526 | 33.3566 | 95.4387 | 95.7271 | 94.667
2022-09-08 05:58 | 8:08 | 18.0724 | 18.598 | 21.1467 | 34.9127 | 34.378 | 34.0552 | 34.591 | 35.5676 | 36.5993 | 37.565 | 36.9877 | 38.2019 | 34.2858 | 34.3225 | 34.1121 | 35.1686 | 34.8785 | 35.3862 | 36.06 | 36.4666 | 21.1289 | 17.6421 | 94.4304 | 33.2559 | 32.9475 | 34.8721 | 33.029 | 32.9178 | 33.3148 | 34.5207 | 34.0927 | 33.9494 | 37.1725 | 36.224 | 33.3161 | 34.3533 | 36.2577 | 36.4918 | 37.3198 | 36.2394 | 33.0208 | 32.5764 | 34.3546 | 34.6844 | 32.8475 | 34.3511 | 34.3529 | 34.3849 | 34.2929 | 34.24 | 34.3692 | 34.0157 | 34.3047 | 36.1764 | 34.9388 | 36.5622 | 36.5541 | 33.3552 | 95.3131 | 95.6879 | 94.5444
2022-09-08 05:58 | 8:08 | 17.9761 | 18.5482 | 21.1207 | 34.9892 | 34.3996 | 34.086 | 34.5963 | 35.548 | 36.5973 | 37.5703 | 37.0115 | 38.1961 | 34.3149 | 34.3261 | 34.1226 | 35.1604 | 34.8599 | 35.3646 | 36.0589 | 36.46 | 21.1177 | 17.5843 | 94.3681 | 33.0401 | 32.9294 | 34.8691 | 33.0267 | 32.9207 | 33.3215 | 34.5364 | 34.0936 | 33.9433 | 37.172 | 36.2469 | 33.317 | 34.3579 | 36.25 | 36.5059 | 37.3452 | 36.2538 | 33.031 | 32.5683 | 34.3501 | 34.6839 | 32.8642 | 34.3333 | 34.3337 | 34.3789 | 34.2865 | 34.2494 | 34.3657 | 34.0343 | 34.2929 | 36.1942 | 34.9335 | 36.5584 | 36.5666 | 33.3374 | 95.152 | 95.5542 | 94.3924
2022-09-08 05:59 | 8:08 | 17.9367 | 18.4982 | 21.0728 | 34.956 | 34.3981 | 34.0735 | 34.5869 | 35.5405 | 36.5905 | 37.561 | 36.9907 | 38.1955 | 34.2881 | 34.3142 | 34.1161 | 35.146 | 34.8689 | 35.3684 | 36.0709 | 36.4763 | 21.1495 | 17.5859 | 94.1287 | 33.1776 | 32.9267 | 34.8872 | 33.0253 | 32.9135 | 33.3043 | 34.519 | 34.0975 | 33.949 | 37.1651 | 36.2251 | 33.296 | 34.3791 | 36.224 | 36.4967 | 37.3366 | 36.244 | 32.9997 | 32.5614 | 34.3364 | 34.6934 | 32.8485 | 34.3394 | 34.3691 | 34.3824 | 34.2938 | 34.2584 | 34.3557 | 34.0343 | 34.2865 | 36.1843 | 34.9154 | 36.5644 | 36.5665 | 33.3473 | 94.8559 | 95.2485 | 94.1109
2022-09-08 05:59 | 8:09 | 17.9668 | 18.4673 | 21.0443 | 34.9444 | 34.3971 | 34.0613 | 34.5879 | 35.5349 | 36.5732 | 37.5739 | 36.9869 | 38.1944 | 34.2811 | 34.3062 | 34.128 | 35.1679 | 34.8764 | 35.3744 | 36.0492 | 36.4531 | 21.1403 | 17.5268 | 94.0038 | 32.8412 | 32.9301 | 34.8613 | 33.0189 | 32.9142 | 33.3085 | 34.526 | 34.0962 | 33.9567 | 37.172 | 36.2404 | 33.3121 | 34.3525 | 36.2469 | 36.4907 | 37.327 | 36.2577 | 33.022 | 32.5455 | 34.3439 | 34.6839 | 32.8364 | 34.3388 | 34.3538 | 34.3919 | 34.2823 | 34.2456 | 34.3825 | 34.0064 | 34.2938 | 36.18 | 34.9194 | 36.5703 | 36.5525 | 33.3554 | 94.6105 | 94.9981 | 94.092
2022-09-08 05:59 | 8:09 | 17.8757 | 18.4115 | 20.9845 | 34.9316 | 34.3947 | 34.0721 | 34.5929 | 35.5474 | 36.6024 | 37.5637 | 36.9902 | 38.2146 | 34.2971 | 34.2966 | 34.1028 | 35.1527 | 34.8735 | 35.3624 | 36.0542 | 36.4591 | 21.1975 | 17.5184 | 93.9498 | 33.0662 | 32.9289 | 34.8846 | 33.0208 | 32.8972 | 33.3161 | 34.5075 | 34.0911 | 33.9552 | 37.1552 | 36.2523 | 33.3186 | 34.3525 | 36.2251 | 36.494 | 37.3192 | 36.25 | 33.0022 | 32.5413 | 34.3445 | 34.6975 | 32.8126 | 34.326 | 34.3608 | 34.385 | 34.2969 | 34.2572 | 34.3747 | 33.9968 | 34.2823 | 36.1672 | 34.9288 | 36.5646 | 36.554 | 33.3376 | 94.4348 | 94.7653 | 93.9735
2022-09-08 05:59 | 8:09 | 17.884 | 18.393 | 20.9566 | 34.8219 | 34.3805 | 34.0877 | 34.5869 | 35.5401 | 36.6019 | 37.5587 | 37.0047 | 38.2044 | 34.2868 | 34.2999 | 34.1071 | 35.1501 | 34.8756 | 35.3728 | 36.0519 | 36.4667 | 21.2144 | 17.5001 | 93.8181 | 33.2263 | 32.9324 | 34.8738 | 33.031 | 32.9113 | 33.317 | 34.5151 | 34.1019 | 33.9356 | 37.1624 | 36.235 | 33.3064 | 34.3546 | 36.2404 | 36.4786 | 37.3212 | 36.224 | 33.0256 | 32.5324 | 34.3442 | 34.6678 | 32.8354 | 34.3241 | 34.3752 | 34.3715 | 34.2948 | 34.2534 | 34.3441 | 33.9901 | 34.2969 | 36.1788 | 34.9306 | 36.5791 | 36.5585 | 33.3334 | 94.2303 | 94.5938 | 93.7974
2022-09-08 05:59 | 8:09 | 17.8714 | 18.3561 | 20.9206 | 34.8015 | 34.374 | 34.0871 | 34.578 | 35.5337 | 36.5942 | 37.5661 | 36.9918 | 38.2084 | 34.2945 | 34.2922 | 34.1105 | 35.1604 | 34.8616 | 35.3576 | 36.0567 | 36.4685 | 21.2518 | 17.4504 | 93.8398 | 33.071 | 32.9065 | 34.8777 | 32.9997 | 32.9226 | 33.296 | 34.5145 | 34.0865 | 33.9485 | 37.1761 | 36.2468 | 33.3122 | 34.3403 | 36.2523 | 36.4776 | 37.3192 | 36.2469 | 33.0225 | 32.5391 | 34.3375 | 34.6581 | 32.8253 | 34.3041 | 34.3791 | 34.3791 | 34.2814 | 34.2681 | 34.3611 | 33.999 | 34.2948 | 36.1843 | 34.9263 | 36.5729 | 36.5522 | 33.3134 | 94.1241 | 94.4657 | 93.811
2022-09-08 05:59 | 8:09 | 17.8266 | 18.3579 | 20.9257 | 34.7957 | 34.3944 | 34.088 | 34.5976 | 35.5286 | 36.5793 | 37.5591 | 37.0025 | 38.2144 | 34.2866 | 34.2822 | 34.117 | 35.1553 | 34.8578 | 35.3539 | 36.0441 | 36.4504 | 21.2666 | 17.4724 | 93.7821 | 33.0769 | 32.9042 | 34.86 | 33.022 | 32.8943 | 33.3121 | 34.4977 | 34.1036 | 33.9541 | 37.1667 | 36.2417 | 33.3077 | 34.3327 | 36.235 | 36.4916 | 37.3204 | 36.2251 | 33.0231 | 32.5363 | 34.3115 | 34.6462 | 32.8214 | 34.323 | 34.3809 | 34.3557 | 34.2944 | 34.2498 | 34.363 | 33.9898 | 34.2814 | 36.1656 | 34.9333 | 36.5762 | 36.5505 | 33.3317 | 94.0175 | 94.4001 | 93.7511
2022-09-08 06:00 | 8:10 | 17.7732 | 18.2449 | 20.864 | 34.7817 | 34.3735 | 34.0877 | 34.5874 | 35.5435 | 36.5955 | 37.5461 | 37.0114 | 38.2178 | 34.2951 | 34.294 | 34.1149 | 35.1716 | 34.8669 | 35.3631 | 36.0239 | 36.4553 | 21.2939 | 17.4577 | 93.6973 | 32.8948 | 32.9201 | 34.8799 | 33.0022 | 32.9025 | 33.3186 | 34.5079 | 34.108 | 33.936 | 37.169 | 36.2472 | 33.3122 | 34.3588 | 36.2468 | 36.4823 | 37.3082 | 36.2404 | 33.0222 | 32.5435 | 34.3132 | 34.6553 | 32.8142 | 34.3222 | 34.3785 | 34.3709 | 34.2867 | 34.2512 | 34.3513 | 33.9863 | 34.2944 | 36.1761 | 34.9488 | 36.567 | 36.5555 | 33.3144 | 93.969 | 94.3159 | 93.6775
2022-09-08 06:00 | 8:10 | 17.7129 | 18.2212 | 20.8153 | 34.8453 | 34.3824 | 34.0679 | 34.5981 | 35.5338 | 36.5723 | 37.5558 | 36.9973 | 38.2051 | 34.288 | 34.2755 | 34.1129 | 35.1806 | 34.8535 | 35.347 | 36.0202 | 36.4492 | 21.3151 | 17.3987 | 93.6982 | 33.169 | 32.9162 | 34.8711 | 33.0256 | 32.8977 | 33.3064 | 34.5145 | 34.1031 | 33.9577 | 37.1532 | 36.2342 | 33.3113 | 34.3571 | 36.2417 | 36.4959 | 37.3162 | 36.2523 | 33.0297 | 32.5212 | 34.307 | 34.6602 | 32.8003 | 34.3071 | 34.3936 | 34.3693 | 34.2902 | 34.2606 | 34.3515 | 33.9969 | 34.2867 | 36.1762 | 34.9276 | 36.5845 | 36.54 | 33.322 | 93.8804 | 94.244 | 93.676
2022-09-08 06:00 | 8:10 | 17.8337 | 18.2387 | 20.7807 | 34.6849 | 34.3984 | 34.0823 | 34.5966 | 35.5382 | 36.5816 | 37.5468 | 36.9927 | 38.2296 | 34.2805 | 34.2824 | 34.1086 | 35.1559 | 34.8789 | 35.36 | 36.0216 | 36.4477 | 21.317 | 17.4656 | 93.6132 | 33.2068 | 32.9242 | 34.854 | 33.0225 | 32.8786 | 33.3122 | 34.5085 | 34.1121 | 33.956 | 37.1452 | 36.2575 | 33.3082 | 34.3724 | 36.2472 | 36.502 | 37.2973 | 36.235 | 33.0215 | 32.5205 | 34.2989 | 34.6477 | 32.8062 | 34.3169 | 34.3852 | 34.371 | 34.3059 | 34.2593 | 34.3565 | 33.9951 | 34.2902 | 36.149 | 34.9273 | 36.5805 | 36.5453 | 33.3033 | 93.8376 | 94.1607 | 93.618
2022-09-08 06:00 | 8:10 | 17.6933 | 18.1565 | 20.7243 | 34.7582 | 34.3694 | 34.0841 | 34.6102 | 35.5484 | 36.5845 | 37.5564 | 37.0125 | 38.1997 | 34.2697 | 34.2851 | 34.0913 | 35.1546 | 34.882 | 35.3603 | 36.0244 | 36.4537 | 21.3174 | 17.3875 | 93.5741 | 33.0052 | 32.9167 | 34.8787 | 33.0231 | 32.8946 | 33.3077 | 34.4957 | 34.0979 | 33.9578 | 37.1544 | 36.2529 | 33.3042 | 34.3638 | 36.2342 | 36.5027 | 37.2922 | 36.2468 | 33.002 | 32.5147 | 34.3013 | 34.6633 | 32.7893 | 34.3129 | 34.3935 | 34.3707 | 34.2955 | 34.2701 | 34.3451 | 33.9951 | 34.3059 | 36.1771 | 34.9427 | 36.5659 | 36.5463 | 33.3233 | 93.7641 | 94.0856 | 93.5255
2022-09-08 06:00 | 8:10 | 17.672 | 18.1548 | 20.7092 | 34.7802 | 34.3869 | 34.0937 | 34.5873 | 35.5409 | 36.5806 | 37.5463 | 37.0181 | 38.2095 | 34.2489 | 34.3019 | 34.1095 | 35.1578 | 34.8771 | 35.3557 | 36.0283 | 36.4458 | 21.3088 | 17.413 | 93.5286 | 32.9774 | 32.9171 | 34.8828 | 33.0222 | 32.8916 | 33.3122 | 34.4992 | 34.1126 | 33.9434 | 37.1638 | 36.2416 | 33.2966 | 34.3768 | 36.2575 | 36.4701 | 37.3081 | 36.2417 | 33.0403 | 32.5337 | 34.301 | 34.6429 | 32.7907 | 34.3319 | 34.3933 | 34.3559 | 34.306 | 34.2762 | 34.3516 | 33.9993 | 34.2955 | 36.1777 | 34.9332 | 36.5747 | 36.5523 | 33.3198 | 93.7469 | 94.0365 | 93.5086
2022-09-08 06:00 | 8:10 | 17.6743 | 18.0817 | 20.661 | 34.8174 | 34.3765 | 34.0871 | 34.5894 | 35.5376 | 36.5999 | 37.5449 | 37.0072 | 38.2033 | 34.2805 | 34.2693 | 34.0936 | 35.1585 | 34.8566 | 35.3648 | 36.0371 | 36.4316 | 21.3025 | 17.3292 | 93.5444 | 32.8419 | 32.9165 | 34.8722 | 33.0297 | 32.8914 | 33.3113 | 34.511 | 34.1057 | 33.9511 | 37.134 | 36.224 | 33.3 | 34.3591 | 36.2529 | 36.511 | 37.2959 | 36.2472 | 33.0412 | 32.5094 | 34.3044 | 34.6429 | 32.7883 | 34.2932 | 34.4112 | 34.3669 | 34.3017 | 34.2689 | 34.3424 | 33.9833 | 34.306 | 36.1594 | 34.9453 | 36.5858 | 36.5499 | 33.3073 | 93.7306 | 93.9806 | 93.5877
2022-09-08 06:01 | 8:10 | 17.6065 | 18.062 | 20.6233 | 34.6373 | 34.3905 | 34.0837 | 34.6086 | 35.5439 | 36.5872 | 37.5588 | 37.0063 | 38.2179 | 34.2768 | 34.2663 | 34.0944 | 35.1713 | 34.8818 | 35.3571 | 36.034 | 36.4418 | 21.3026 | 17.3144 | 93.4994 | 33.105 | 32.9055 | 34.8669 | 33.0215 | 32.8888 | 33.3082 | 34.4975 | 34.1112 | 33.942 | 37.1677 | 36.2396 | 33.3049 | 34.374 | 36.2416 | 36.4958 | 37.3095 | 36.2342 | 32.9899 | 32.5088 | 34.2793 | 34.6594 | 32.7793 | 34.3274 | 34.4102 | 34.3586 | 34.3127 | 34.2475 | 34.3396 | 33.9906 | 34.3017 | 36.1703 | 34.9321 | 36.5766 | 36.5577 | 33.3186 | 93.6878 | 93.9152 | 93.5176
2022-09-08 06:01 | 8:11 | 17.6183 | 18.0291 | 20.605 | 34.687 | 34.3809 | 34.1004 | 34.5776 | 35.5428 | 36.5918 | 37.5539 | 37.0134 | 38.2201 | 34.2759 | 34.2629 | 34.0819 | 35.1675 | 34.8654 | 35.3518 | 36.024 | 36.4446 | 21.293 | 17.2985 | 93.5557 | 33.2099 | 32.9077 | 34.886 | 33.002 | 32.9025 | 33.3042 | 34.5051 | 34.0973 | 33.9614 | 37.1529 | 36.222 | 33.2969 | 34.3803 | 36.224 | 36.5055 | 37.3018 | 36.2575 | 33.0114 | 32.5125 | 34.2952 | 34.6428 | 32.7777 | 34.3211 | 34.3972 | 34.3725 | 34.2973 | 34.249 | 34.3479 | 33.974 | 34.3127 | 36.1721 | 34.9304 | 36.5816 | 36.559 | 33.3177 | 93.6855 | 93.8602 | 93.4869
2022-09-08 06:01 | 8:11 | 17.5651 | 18.0019 | 20.5515 | 34.6317 | 34.3786 | 34.1019 | 34.59 | 35.548 | 36.5917 | 37.5401 | 37.0305 | 38.2137 | 34.2773 | 34.2881 | 34.1017 | 35.1778 | 34.8738 | 35.3479 | 36.006 | 36.4498 | 21.2693 | 17.3087 | 93.4227 | 32.8505 | 32.9046 | 34.8843 | 33.0403 | 32.8928 | 33.2966 | 34.4933 | 34.0984 | 33.9593 | 37.159 | 36.2543 | 33.301 | 34.3668 | 36.2396 | 36.4864 | 37.2869 | 36.2529 | 33.02 | 32.5199 | 34.2938 | 34.6506 | 32.7726 | 34.2981 | 34.399 | 34.3397 | 34.2945 | 34.2628 | 34.3382 | 33.9764 | 34.2973 | 36.1736 | 34.9343 | 36.5663 | 36.5427 | 33.3009 | 93.5288 | 93.767 | 93.3689
2022-09-08 06:01 | 8:11 | 17.5313 | 17.9925 | 20.5314 | 34.6078 | 34.3724 | 34.1011 | 34.6042 | 35.5528 | 36.5826 | 37.5622 | 37.0062 | 38.2228 | 34.2559 | 34.2826 | 34.1152 | 35.1819 | 34.8806 | 35.3528 | 36.0291 | 36.4492 | 21.2577 | 17.2921 | 93.4171 | 33.1765 | 32.8905 | 34.8854 | 33.0412 | 32.9027 | 33.3 | 34.5091 | 34.1033 | 33.9493 | 37.1645 | 36.2542 | 33.2994 | 34.3576 | 36.222 | 36.507 | 37.3023 | 36.2416 | 33.0222 | 32.5081 | 34.2668 | 34.653 | 32.7834 | 34.3031 | 34.3997 | 34.3448 | 34.3198 | 34.2939 | 34.3254 | 33.9867 | 34.2945 | 36.1836 | 34.9163 | 36.5643 | 36.5545 | 33.3243 | 93.4489 | 93.6906 | 93.329
2022-09-08 06:01 | 8:11 | 17.5138 | 17.923 | 20.4905 | 34.6493 | 34.3617 | 34.0963 | 34.588 | 35.555 | 36.5785 | 37.5566 | 37.0178 | 38.2233 | 34.2679 | 34.2842 | 34.0833 | 35.1717 | 34.8837 | 35.3616 | 36.0258 | 36.434 | 21.2715 | 17.2707 | 93.2847 | 32.9765 | 32.9002 | 34.8654 | 32.9899 | 32.8825 | 33.3049 | 34.5076 | 34.1043 | 33.9596 | 37.1743 | 36.2291 | 33.3047 | 34.3701 | 36.2543 | 36.4845 | 37.3128 | 36.224 | 33.0138 | 32.51 | 34.2801 | 34.6575 | 32.7605 | 34.3331 | 34.3953 | 34.3559 | 34.2975 | 34.2703 | 34.3443 | 33.966 | 34.3198 | 36.1616 | 34.8936 | 36.5894 | 36.546 | 33.3045 | 93.3524 | 93.575 | 93.1916
2022-09-08 06:01 | 8:11 | 17.4783 | 17.9156 | 20.4413 | 34.7011 | 34.3917 | 34.09 | 34.5894 | 35.5494 | 36.5865 | 37.5541 | 37.0155 | 38.2152 | 34.2634 | 34.3017 | 34.1045 | 35.165 | 34.8729 | 35.3574 | 36.0337 | 36.4335 | 21.2522 | 17.233 | 93.2404 | 32.9716 | 32.9158 | 34.855 | 33.0114 | 32.8864 | 33.2969 | 34.4904 | 34.1045 | 33.9535 | 37.1723 | 36.2493 | 33.2941 | 34.3609 | 36.2542 | 36.4937 | 37.2909 | 36.2396 | 33.0161 | 32.4976 | 34.2683 | 34.6493 | 32.7604 | 34.3046 | 34.3881 | 34.3519 | 34.311 | 34.286 | 34.3375 | 33.9633 | 34.2975 | 36.1653 | 34.9413 | 36.5769 | 36.5533 | 33.326 | 93.2691 | 93.4985 | 93.156
2022-09-08 06:02 | 8:11 | 17.4559 | 17.8824 | 20.4175 | 34.6508 | 34.3685 | 34.1032 | 34.5904 | 35.563 | 36.6011 | 37.5483 | 37.0388 | 38.2113 | 34.2433 | 34.2799 | 34.1018 | 35.1587 | 34.8665 | 35.3571 | 36.0254 | 36.4464 | 21.2434 | 17.2315 | 93.225 | 33.0209 | 32.8955 | 34.872 | 33.02 | 32.8868 | 33.301 | 34.4947 | 34.0885 | 33.9562 | 37.1674 | 36.2636 | 33.2906 | 34.3805 | 36.2291 | 36.4989 | 37.3031 | 36.222 | 33.0256 | 32.5119 | 34.2978 | 34.6143 | 32.7512 | 34.3074 | 34.3895 | 34.3565 | 34.2995 | 34.2558 | 34.3347 | 33.9676 | 34.311 | 36.1617 | 34.9332 | 36.5726 | 36.5654 | 33.3106 | 93.2399 | 93.4381 | 93.1435
2022-09-08 06:02 | 8:12 | 17.4056 | 17.8195 | 20.3805 | 34.5906 | 34.3758 | 34.0957 | 34.6006 | 35.5455 | 36.5963 | 37.5464 | 37.0199 | 38.2112 | 34.2467 | 34.2571 | 34.1042 | 35.1688 | 34.8838 | 35.3558 | 36.0212 | 36.4515 | 21.2515 | 17.196 | 93.2137 | 33.039 | 32.915 | 34.8647 | 33.0222 | 32.896 | 33.2994 | 34.4952 | 34.1206 | 33.9581 | 37.1803 | 36.239 | 33.2921 | 34.3589 | 36.2493 | 36.4924 | 37.2999 | 36.2543 | 33.0167 | 32.4922 | 34.2781 | 34.6372 | 32.752 | 34.31 | 34.3994 | 34.338 | 34.3152 | 34.2534 | 34.313 | 33.9833 | 34.2995 | 36.1581 | 34.9473 | 36.602 | 36.5509 | 33.3142 | 93.1569 | 93.3501 | 93.0986
2022-09-08 06:02 | 8:12 | 17.4471 | 17.8147 | 20.3665 | 34.6869 | 34.3758 | 34.1116 | 34.5948 | 35.5423 | 36.5848 | 37.5506 | 37.0159 | 38.2118 | 34.2441 | 34.2722 | 34.1054 | 35.1592 | 34.8698 | 35.3541 | 36.0083 | 36.4348 | 21.2364 | 17.2254 | 93.0987 | 32.8841 | 32.8912 | 34.8769 | 33.0138 | 32.8926 | 33.3047 | 34.4781 | 34.123 | 33.95 | 37.1604 | 36.2362 | 33.2908 | 34.3729 | 36.2636 | 36.5053 | 37.2903 | 36.2542 | 33.0176 | 32.4877 | 34.2537 | 34.6414 | 32.7368 | 34.3083 | 34.4104 | 34.3476 | 34.312 | 34.2879 | 34.3244 | 33.9606 | 34.3152 | 36.1728 | 34.9212 | 36.5752 | 36.5411 | 33.3248 | 93.0345 | 93.243 | 92.9704
2022-09-08 06:02 | 8:12 | 17.4283 | 17.799 | 20.3528 | 34.6349 | 34.3582 | 34.1034 | 34.5837 | 35.5493 | 36.5714 | 37.5569 | 37.0276 | 38.2312 | 34.2525 | 34.2711 | 34.1105 | 35.1743 | 34.8656 | 35.3458 | 36.0311 | 36.4405 | 21.2145 | 17.1992 | 93.0003 | 32.8004 | 32.8903 | 34.8747 | 33.0161 | 32.8981 | 33.2941 | 34.4847 | 34.1132 | 33.9609 | 37.1644 | 36.2247 | 33.292 | 34.3622 | 36.239 | 36.5056 | 37.303 | 36.2291 | 33.0002 | 32.4879 | 34.2872 | 34.632 | 32.7474 | 34.3052 | 34.41 | 34.3403 | 34.3025 | 34.2669 | 34.3288 | 33.9531 | 34.312 | 36.1671 | 34.9382 | 36.5866 | 36.5548 | 33.2999 | 92.9613 | 93.1388 | 92.9272
2022-09-08 06:02 | 8:12 | 17.3123 | 17.6963 | 20.3062 | 34.5053 | 34.3744 | 34.0984 | 34.5914 | 35.5545 | 36.5892 | 37.5411 | 37.0159 | 38.2348 | 34.2545 | 34.2737 | 34.0903 | 35.1752 | 34.8713 | 35.3645 | 36.008 | 36.4317 | 21.1903 | 17.1179 | 92.95 | 33.0567 | 32.8962 | 34.8738 | 33.0256 | 32.8846 | 33.2906 | 34.4864 | 34.1115 | 33.9509 | 37.1554 | 36.2539 | 33.2836 | 34.3691 | 36.2362 | 36.4885 | 37.2937 | 36.2493 | 32.996 | 32.482 | 34.2547 | 34.6381 | 32.7336 | 34.3101 | 34.4086 | 34.3401 | 34.3123 | 34.2662 | 34.3239 | 33.9626 | 34.3025 | 36.1792 | 34.9404 | 36.5977 | 36.5395 | 33.3182 | 92.818 | 92.9825 | 92.8362
2022-09-08 06:02 | 8:12 | 17.3859 | 17.7024 | 20.2718 | 34.6687 | 34.3915 | 34.1086 | 34.6005 | 35.5522 | 36.5796 | 37.5474 | 37.0271 | 38.2198 | 34.2448 | 34.2811 | 34.092 | 35.1669 | 34.8743 | 35.3653 | 36.019 | 36.4467 | 21.1564 | 17.1433 | 92.9009 | 32.9973 | 32.8978 | 34.8683 | 33.0167 | 32.8963 | 33.2921 | 34.4947 | 34.1272 | 33.9637 | 37.1735 | 36.2376 | 33.2872 | 34.3769 | 36.2247 | 36.5065 | 37.2821 | 36.2636 | 33.0142 | 32.4684 | 34.2722 | 34.6502 | 32.7052 | 34.2874 | 34.3999 | 34.3429 | 34.2951 | 34.275 | 34.3225 | 33.9663 | 34.3123 | 36.1796 | 34.9399 | 36.5712 | 36.5514 | 33.3131 | 92.7646 | 92.9204 | 92.81
2022-09-08 06:03 | 8:13 | 17.3592 | 17.6956 | 20.2538 | 34.6637 | 34.355 | 34.1129 | 34.5953 | 35.5468 | 36.5862 | 37.5483 | 37.0255 | 38.2139 | 34.2525 | 34.2745 | 34.0818 | 35.1731 | 34.8565 | 35.3482 | 35.9979 | 36.4532 | 21.1654 | 17.1404 | 92.797 | 32.8441 | 32.9002 | 34.866 | 33.0176 | 32.9 | 33.2908 | 34.5058 | 34.1281 | 33.9732 | 37.1606 | 36.2078 | 33.2852 | 34.3733 | 36.2539 | 36.5094 | 37.2885 | 36.239 | 32.9955 | 32.4681 | 34.2456 | 34.6221 | 32.7127 | 34.2824 | 34.4051 | 34.3268 | 34.3191 | 34.2634 | 34.3261 | 33.9588 | 34.2951 | 36.168 | 34.9246 | 36.5844 | 36.5556 | 33.3087 | 92.5999 | 92.7609 | 92.6811
2022-09-08 06:03 | 8:13 | 17.2902 | 17.6326 | 20.1925 | 34.5592 | 34.3686 | 34.0887 | 34.5711 | 35.5506 | 36.5703 | 37.5513 | 37.0292 | 38.2363 | 34.2548 | 34.2622 | 34.0875 | 35.1683 | 34.8793 | 35.3678 | 36.0194 | 36.4502 | 21.1489 | 17.1115 | 92.6931 | 32.6908 | 32.8942 | 34.859 | 33.0002 | 32.9098 | 33.292 | 34.497 | 34.1264 | 33.9574 | 37.1755 | 36.2431 | 33.2988 | 34.371 | 36.2376 | 36.4928 | 37.3031 | 36.2362 | 32.9972 | 32.4738 | 34.2602 | 34.6312 | 32.7116 | 34.2803 | 34.408 | 34.308 | 34.326 | 34.2786 | 34.3142 | 33.9686 | 34.3191 | 36.1912 | 34.9289 | 36.5869 | 36.5434 | 33.3049 | 92.4595 | 92.594 | 92.5762
2022-09-08 06:03 | 8:13 | 17.318 | 17.6683 | 20.1864 | 34.4791 | 34.3723 | 34.1007 | 34.5893 | 35.5791 | 36.5827 | 37.5722 | 37.018 | 38.2196 | 34.2212 | 34.27 | 34.0943 | 35.1685 | 34.8723 | 35.3612 | 36.0089 | 36.4643 | 21.1173 | 17.0722 | 92.6717 | 32.821 | 32.8858 | 34.8427 | 32.996 | 32.8921 | 33.2836 | 34.4903 | 34.1102 | 33.9532 | 37.1719 | 36.2358 | 33.285 | 34.3644 | 36.2078 | 36.4999 | 37.2846 | 36.2247 | 32.9986 | 32.4917 | 34.2555 | 34.6306 | 32.6929 | 34.2928 | 34.3934 | 34.3268 | 34.3135 | 34.2697 | 34.3062 | 33.9573 | 34.326 | 36.1882 | 34.9242 | 36.5844 | 36.531 | 33.3013 | 92.3657 | 92.5354 | 92.514
2022-09-08 06:03 | 8:13 | 17.2375 | 17.5957 | 20.1562 | 34.5735 | 34.3692 | 34.0954 | 34.5897 | 35.5585 | 36.5877 | 37.5622 | 37.0222 | 38.2338 | 34.2496 | 34.2511 | 34.085 | 35.1931 | 34.8509 | 35.3486 | 36.0171 | 36.4453 | 21.1176 | 16.9848 | 92.4653 | 32.9014 | 32.8934 | 34.8468 | 33.0142 | 32.8936 | 33.2872 | 34.5045 | 34.1043 | 33.95 | 37.1783 | 36.2375 | 33.2906 | 34.3616 | 36.2431 | 36.524 | 37.3056 | 36.2539 | 32.9694 | 32.4856 | 34.265 | 34.6283 | 32.6949 | 34.3179 | 34.4028 | 34.3219 | 34.3122 | 34.2917 | 34.2966 | 33.9522 | 34.3135 | 36.177 | 34.9282 | 36.5892 | 36.5541 | 33.2966 | 92.2133 | 92.3984 | 92.2928
2022-09-08 06:03 | 8:13 | 17.2719 | 17.5926 | 20.1257 | 34.5409 | 34.3657 | 34.1196 | 34.6147 | 35.5524 | 36.6011 | 37.5376 | 37.0251 | 38.2181 | 34.248 | 34.2481 | 34.0907 | 35.1824 | 34.8618 | 35.3551 | 36.0165 | 36.4613 | 21.0943 | 17.0364 | 92.4213 | 32.8747 | 32.8972 | 34.864 | 32.9955 | 32.8963 | 33.2852 | 34.5022 | 34.1222 | 33.9567 | 37.1668 | 36.2054 | 33.2832 | 34.359 | 36.2358 | 36.5037 | 37.2943 | 36.2376 | 32.9788 | 32.4688 | 34.2658 | 34.6174 | 32.6831 | 34.285 | 34.3976 | 34.3088 | 34.3412 | 34.2805 | 34.2999 | 33.9701 | 34.3122 | 36.2056 | 34.9151 | 36.5783 | 36.5394 | 33.319 | 92.1229 | 92.2829 | 92.3917
2022-09-08 06:03 | 8:13 | 17.1903 | 17.5706 | 20.1024 | 34.4599 | 34.3557 | 34.106 | 34.5885 | 35.5643 | 36.5851 | 37.5709 | 37.0131 | 38.2393 | 34.2409 | 34.2468 | 34.0929 | 35.172 | 34.8439 | 35.3513 | 36.0284 | 36.4765 | 21.0971 | 17.0026 | 92.5045 | 32.6928 | 32.9053 | 34.8545 | 32.9972 | 32.896 | 33.2988 | 34.4924 | 34.1115 | 33.9606 | 37.1599 | 36.2213 | 33.3041 | 34.3755 | 36.2375 | 36.4997 | 37.2901 | 36.2078 | 32.9943 | 32.4735 | 34.2591 | 34.6287 | 32.6848 | 34.2998 | 34.396 | 34.3074 | 34.3055 | 34.2874 | 34.2922 | 33.9564 | 34.3412 | 36.1895 | 34.9315 | 36.5788 | 36.5488 | 33.3135 | 92.2491 | 92.3622 | 92.5025
2022-09-08 06:04 | 8:13 | 17.2245 | 17.5693 | 20.078 | 34.5318 | 34.3825 | 34.0984 | 34.5774 | 35.572 | 36.6063 | 37.5509 | 37.028 | 38.231 | 34.2316 | 34.261 | 34.0887 | 35.1762 | 34.8621 | 35.367 | 36.0199 | 36.4585 | 21.0767 | 17.0234 | 92.5531 | 32.8001 | 32.879 | 34.8414 | 32.9986 | 32.8931 | 33.285 | 34.4991 | 34.1318 | 33.9573 | 37.1773 | 36.2108 | 33.3029 | 34.3773 | 36.2054 | 36.5189 | 37.3094 | 36.2431 | 32.9935 | 32.4704 | 34.2568 | 34.615 | 32.6637 | 34.2824 | 34.3892 | 34.3091 | 34.3285 | 34.2894 | 34.2822 | 33.959 | 34.3055 | 36.1979 | 34.9269 | 36.5919 | 36.5404 | 33.3104 | 92.3362 | 92.4033 | 92.6011
2022-09-08 06:04 | 8:14 | 17.1653 | 17.4962 | 20.0479 | 34.4893 | 34.3747 | 34.1002 | 34.5911 | 35.5426 | 36.5799 | 37.5378 | 37.0251 | 38.2421 | 34.232 | 34.2557 | 34.0919 | 35.1532 | 34.8564 | 35.3364 | 36.0252 | 36.4593 | 21.0782 | 16.9937 | 92.5668 | 33.011 | 32.8821 | 34.842 | 32.9694 | 32.8953 | 33.2906 | 34.4995 | 34.1157 | 33.9637 | 37.1683 | 36.214 | 33.279 | 34.3559 | 36.2213 | 36.5006 | 37.318 | 36.2358 | 32.9958 | 32.4667 | 34.2548 | 34.6092 | 32.6639 | 34.2983 | 34.3887 | 34.2994 | 34.3392 | 34.2747 | 34.294 | 33.9525 | 34.3285 | 36.1832 | 34.922 | 36.5832 | 36.5453 | 33.2985 | 92.3926 | 92.494 | 92.5055
2022-09-08 06:04 | 8:14 | 17.1589 | 17.5113 | 20.0442 | 34.4136 | 34.3441 | 34.1029 | 34.5795 | 35.5469 | 36.6003 | 37.5404 | 37.0331 | 38.2273 | 34.2174 | 34.2413 | 34.086 | 35.181 | 34.8696 | 35.3633 | 36.0099 | 36.4516 | 21.0617 | 16.9614 | 92.6663 | 32.8564 | 32.8884 | 34.831 | 32.9788 | 32.8978 | 33.2832 | 34.4907 | 34.0862 | 33.9687 | 37.1613 | 36.1948 | 33.2921 | 34.3637 | 36.2108 | 36.4887 | 37.3077 | 36.2375 | 32.9715 | 32.4582 | 34.2546 | 34.6008 | 32.6594 | 34.2804 | 34.3996 | 34.3144 | 34.32 | 34.2704 | 34.2755 | 33.9642 | 34.3392 | 36.1941 | 34.9108 | 36.5924 | 36.5751 | 33.3067 | 92.4824 | 92.5667 | 92.6229
2022-09-08 06:04 | 8:14 | 17.1418 | 17.4694 | 20.0188 | 34.4043 | 34.3611 | 34.081 | 34.5932 | 35.5555 | 36.5929 | 37.5384 | 37.0331 | 38.2327 | 34.225 | 34.2545 | 34.1006 | 35.1663 | 34.8734 | 35.3459 | 36.0018 | 36.4575 | 21.0177 | 16.9371 | 92.6928 | 32.8372 | 32.8827 | 34.8386 | 32.9943 | 32.8934 | 33.3041 | 34.4887 | 34.1169 | 33.9697 | 37.1739 | 36.22 | 33.2698 | 34.3804 | 36.214 | 36.5055 | 37.2876 | 36.2054 | 32.9722 | 32.4427 | 34.2306 | 34.6192 | 32.6666 | 34.303 | 34.3967 | 34.299 | 34.3113 | 34.2749 | 34.2824 | 33.9562 | 34.32 | 36.1752 | 34.9303 | 36.5845 | 36.555 | 33.3073 | 92.5524 | 92.6617 | 92.7703
2022-09-08 06:04 | 8:14 | 17.1291 | 17.443 | 20.0003 | 34.4973 | 34.363 | 34.0939 | 34.5844 | 35.5574 | 36.5846 | 37.5328 | 37.0274 | 38.235 | 34.2447 | 34.2747 | 34.0919 | 35.1692 | 34.8552 | 35.3668 | 36.007 | 36.453 | 20.996 | 16.9774 | 92.8698 | 32.8614 | 32.8803 | 34.8282 | 32.9935 | 32.8903 | 33.3029 | 34.4956 | 34.0962 | 33.9575 | 37.1585 | 36.2087 | 33.283 | 34.3645 | 36.1948 | 36.4932 | 37.2844 | 36.2213 | 32.9684 | 32.4475 | 34.2324 | 34.6127 | 32.65 | 34.2928 | 34.4045 | 34.2968 | 34.3247 | 34.2869 | 34.2851 | 33.9348 | 34.3113 | 36.1639 | 34.9087 | 36.5868 | 36.5621 | 33.2921 | 92.7157 | 92.8029 | 92.8948
2022-09-08 06:04 | 8:14 | 17.1077 | 17.4158 | 19.9748 | 34.366 | 34.3513 | 34.0908 | 34.5699 | 35.5548 | 36.5932 | 37.5537 | 37.0121 | 38.2411 | 34.2409 | 34.2582 | 34.0899 | 35.164 | 34.8367 | 35.3396 | 35.993 | 36.4633 | 20.9727 | 16.946 | 92.8584 | 32.8052 | 32.8642 | 34.825 | 32.9958 | 32.895 | 33.279 | 34.5035 | 34.1115 | 33.9617 | 37.1679 | 36.187 | 33.2961 | 34.3767 | 36.22 | 36.501 | 37.3025 | 36.2108 | 32.9655 | 32.4231 | 34.2211 | 34.5908 | 32.6398 | 34.2835 | 34.393 | 34.3193 | 34.3203 | 34.2694 | 34.3019 | 33.9644 | 34.3247 | 36.1777 | 34.912 | 36.5895 | 36.5423 | 33.3212 | 92.7891 | 92.9037 | 92.9094
2022-09-08 06:05 | 8:15 | 17.0797 | 17.3886 | 19.9521 | 34.3997 | 34.3515 | 34.087 | 34.5673 | 35.5434 | 36.5709 | 37.5375 | 37.0031 | 38.2283 | 34.2475 | 34.2571 | 34.0658 | 35.1506 | 34.8732 | 35.3608 | 36.0099 | 36.4593 | 20.9406 | 16.9086 | 92.847 | 32.8376 | 32.8723 | 34.828 | 32.9715 | 32.8776 | 33.2921 | 34.4845 | 34.1053 | 33.9467 | 37.1602 | 36.2083 | 33.2829 | 34.3497 | 36.2087 | 36.483 | 37.2956 | 36.214 | 32.9784 | 32.4265 | 34.2257 | 34.605 | 32.6167 | 34.272 | 34.3789 | 34.2921 | 34.3395 | 34.2996 | 34.2693 | 33.9639 | 34.3203 | 36.1818 | 34.9142 | 36.5729 | 36.5542 | 33.2998 | 92.8654 | 93.0271 | 92.91
2022-09-08 06:05 | 8:15 | 17.0414 | 17.3774 | 19.9245 | 34.3651 | 34.3565 | 34.0901 | 34.5822 | 35.5652 | 36.5908 | 37.5448 | 37.0145 | 38.227 | 34.2458 | 34.2629 | 34.0842 | 35.1799 | 34.859 | 35.3425 | 35.9803 | 36.4579 | 20.9291 | 16.8991 | 92.9053 | 32.6529 | 32.8549 | 34.8133 | 32.9722 | 32.8728 | 33.2698 | 34.4947 | 34.0844 | 33.9555 | 37.1561 | 36.2015 | 33.2685 | 34.3428 | 36.187 | 36.5001 | 37.2887 | 36.1948 | 32.9672 | 32.4197 | 34.2404 | 34.5858 | 32.6296 | 34.3029 | 34.4024 | 34.2805 | 34.3274 | 34.2873 | 34.2663 | 33.9543 | 34.3395 | 36.18 | 34.9108 | 36.5829 | 36.5617 | 33.2964 | 92.9768 | 93.1523 | 92.9113
2022-09-08 06:05 | 8:15 | 17.0716 | 17.3923 | 19.9297 | 34.3455 | 34.3451 | 34.0858 | 34.578 | 35.5456 | 36.5658 | 37.5401 | 37.0409 | 38.2215 | 34.2386 | 34.2689 | 34.0878 | 35.1733 | 34.8574 | 35.3312 | 35.9974 | 36.4285 | 20.9058 | 16.8754 | 92.9568 | 32.7442 | 32.8546 | 34.8308 | 32.9684 | 32.8744 | 33.283 | 34.4694 | 34.1125 | 33.9677 | 37.149 | 36.1934 | 33.2683 | 34.3593 | 36.2083 | 36.4964 | 37.2844 | 36.22 | 32.9626 | 32.4243 | 34.2066 | 34.5864 | 32.6219 | 34.2874 | 34.3758 | 34.2961 | 34.3328 | 34.2894 | 34.2629 | 33.9734 | 34.3274 | 36.1868 | 34.9179 | 36.5859 | 36.5267 | 33.2935 | 93.0429 | 93.3108 | 92.9959
2022-09-08 06:05 | 8:15 | 17.0439 | 17.355 | 19.9074 | 34.3228 | 34.3516 | 34.0953 | 34.5719 | 35.5454 | 36.574 | 37.5636 | 37.0089 | 38.2281 | 34.2449 | 34.2512 | 34.0884 | 35.1533 | 34.8359 | 35.3252 | 36.0016 | 36.4323 | 20.8829 | 16.8882 | 93.1318 | 32.6344 | 32.8478 | 34.8107 | 32.9655 | 32.875 | 33.2961 | 34.4867 | 34.0952 | 33.9364 | 37.1547 | 36.2081 | 33.2705 | 34.37 | 36.2015 | 36.4962 | 37.2825 | 36.2087 | 32.9539 | 32.408 | 34.2406 | 34.5691 | 32.6132 | 34.2985 | 34.3835 | 34.2845 | 34.3128 | 34.3071 | 34.2881 | 33.9392 | 34.3328 | 36.1875 | 34.8946 | 36.566 | 36.5417 | 33.293 | 93.1837 | 93.4087 | 93.1569
2022-09-08 06:05 | 8:15 | 17.0076 | 17.3492 | 19.8951 | 34.3078 | 34.3424 | 34.096 | 34.5624 | 35.5435 | 36.5741 | 37.5597 | 37.0078 | 38.227 | 34.2635 | 34.28 | 34.0754 | 35.1649 | 34.8329 | 35.3332 | 35.9778 | 36.4578 | 20.8528 | 16.8284 | 93.1441 | 32.8602 | 32.8557 | 34.8247 | 32.9784 | 32.8747 | 33.2829 | 34.4908 | 34.0951 | 33.9383 | 37.1469 | 36.1816 | 33.2844 | 34.3693 | 36.1934 | 36.4835 | 37.2852 | 36.187 | 32.946 | 32.4123 | 34.2258 | 34.5737 | 32.5889 | 34.302 | 34.394 | 34.2917 | 34.3345 | 34.2902 | 34.2826 | 33.9255 | 34.3128 | 36.1757 | 34.9062 | 36.5763 | 36.5473 | 33.2693 | 93.2767 | 93.5169 | 93.1637
2022-09-08 06:05 | 8:15 | 17.0305 | 17.3332 | 19.8554 | 34.3003 | 34.3396 | 34.0815 | 34.5632 | 35.5375 | 36.5908 | 37.5584 | 37.0101 | 38.2165 | 34.24 | 34.251 | 34.0734 | 35.1636 | 34.857 | 35.3384 | 35.9893 | 36.444 | 20.8278 | 16.8407 | 93.2265 | 32.7286 | 32.8376 | 34.8091 | 32.9672 | 32.8795 | 33.2685 | 34.4898 | 34.0952 | 33.9415 | 37.1498 | 36.1879 | 33.2618 | 34.3507 | 36.2081 | 36.5015 | 37.2823 | 36.2083 | 32.9573 | 32.42 | 34.2017 | 34.5539 | 32.5847 | 34.3034 | 34.3846 | 34.275 | 34.3254 | 34.3048 | 34.2842 | 33.916 | 34.3345 | 36.2027 | 34.915 | 36.591 | 36.5445 | 33.3004 | 93.3904 | 93.6356 | 93.2664
2022-09-08 06:06 | 8:15 | 16.9491 | 17.3343 | 19.8339 | 34.3213 | 34.3479 | 34.0897 | 34.5579 | 35.543 | 36.5632 | 37.5548 | 37.0169 | 38.2398 | 34.2494 | 34.2677 | 34.0739 | 35.1442 | 34.8624 | 35.3222 | 35.9983 | 36.4342 | 20.8195 | 16.8349 | 93.315 | 32.892 | 32.8516 | 34.8154 | 32.9626 | 32.866 | 33.2683 | 34.4921 | 34.0988 | 33.9485 | 37.1381 | 36.178 | 33.273 | 34.3362 | 36.1816 | 36.4948 | 37.2912 | 36.2015 | 32.9506 | 32.4081 | 34.2106 | 34.5478 | 32.5756 | 34.3089 | 34.3948 | 34.2658 | 34.3324 | 34.3002 | 34.3017 | 33.936 | 34.3254 | 36.1859 | 34.9002 | 36.5664 | 36.5419 | 33.2726 | 93.4773 | 93.7575 | 93.3654
2022-09-08 06:06 | 8:16 | 16.9814 | 17.3414 | 19.8168 | 34.3813 | 34.3382 | 34.0928 | 34.5603 | 35.5467 | 36.5645 | 37.5379 | 37.0157 | 38.2161 | 34.2584 | 34.2712 | 34.0644 | 35.1487 | 34.8528 | 35.3356 | 35.9953 | 36.4368 | 20.7939 | 16.8384 | 93.3785 | 32.7123 | 32.8478 | 34.7872 | 32.9539 | 32.8714 | 33.2705 | 34.4942 | 34.0921 | 33.9481 | 37.1379 | 36.1728 | 33.2731 | 34.3364 | 36.1879 | 36.4907 | 37.2658 | 36.1934 | 32.9362 | 32.402 | 34.1765 | 34.5599 | 32.5926 | 34.3035 | 34.3811 | 34.2686 | 34.3556 | 34.2874 | 34.2799 | 33.9377 | 34.3324 | 36.1882 | 34.8778 | 36.5764 | 36.538 | 33.2741 | 93.6177 | 93.947 | 93.4517
2022-09-08 06:06 | 8:16 | 16.9624 | 17.2857 | 19.8055 | 34.3405 | 34.3254 | 34.0911 | 34.5554 | 35.5416 | 36.5749 | 37.5386 | 37.005 | 38.2141 | 34.2456 | 34.2596 | 34.0759 | 35.1521 | 34.8343 | 35.341 | 35.9766 | 36.4408 | 20.784 | 16.8165 | 93.5746 | 32.9023 | 32.8434 | 34.8018 | 32.946 | 32.8664 | 33.2844 | 34.4998 | 34.0938 | 33.9397 | 37.1448 | 36.1763 | 33.2868 | 34.3327 | 36.178 | 36.506 | 37.2713 | 36.2081 | 32.9362 | 32.3873 | 34.2012 | 34.5681 | 32.5715 | 34.3069 | 34.3827 | 34.2785 | 34.3549 | 34.3012 | 34.2571 | 33.9141 | 34.3556 | 36.1653 | 34.891 | 36.5832 | 36.5399 | 33.2787 | 93.842 | 94.1582 | 93.6563
2022-09-08 06:06 | 8:16 | 17.016 | 17.3385 | 19.7944 | 34.3112 | 34.3443 | 34.0861 | 34.5576 | 35.5515 | 36.5699 | 37.5486 | 37.0124 | 38.2231 | 34.2572 | 34.265 | 34.0779 | 35.1396 | 34.8341 | 35.3314 | 35.9851 | 36.4368 | 20.7979 | 16.8405 | 93.6429 | 32.7695 | 32.8392 | 34.7887 | 32.9573 | 32.8644 | 33.2618 | 34.5014 | 34.0664 | 33.9323 | 37.1371 | 36.1775 | 33.2647 | 34.3386 | 36.1728 | 36.4938 | 37.2831 | 36.1816 | 32.9409 | 32.3918 | 34.1957 | 34.5449 | 32.5808 | 34.3106 | 34.3788 | 34.2701 | 34.3554 | 34.3003 | 34.2722 | 33.9559 | 34.3549 | 36.1875 | 34.9001 | 36.5938 | 36.5544 | 33.2818 | 94.0388 | 94.3503 | 93.7926
2022-09-08 06:06 | 8:16 | 16.9866 | 17.2634 | 19.7709 | 34.2851 | 34.3375 | 34.0865 | 34.5602 | 35.5372 | 36.5598 | 37.5467 | 37.0187 | 38.2132 | 34.2534 | 34.2678 | 34.0773 | 35.1484 | 34.8319 | 35.3233 | 35.9802 | 36.4388 | 20.7467 | 16.7974 | 93.739 | 32.6901 | 32.8321 | 34.7994 | 32.9506 | 32.8688 | 33.273 | 34.498 | 34.0995 | 33.9403 | 37.138 | 36.1684 | 33.2571 | 34.3435 | 36.1763 | 36.4649 | 37.2793 | 36.1879 | 32.9181 | 32.3742 | 34.1756 | 34.5574 | 32.5718 | 34.2978 | 34.3685 | 34.2543 | 34.3584 | 34.2999 | 34.2711 | 33.9159 | 34.3554 | 36.1485 | 34.8967 | 36.5661 | 36.5157 | 33.2645 | 94.2069 | 94.5211 | 93.855
2022-09-08 06:06 | 8:16 | 16.9393 | 17.2551 | 19.7845 | 34.2764 | 34.3347 | 34.0879 | 34.5781 | 35.5576 | 36.5698 | 37.5452 | 37.0016 | 38.2156 | 34.2681 | 34.2611 | 34.066 | 35.1523 | 34.8227 | 35.3201 | 35.9825 | 36.4397 | 20.755 | 16.8199 | 93.9266 | 32.7673 | 32.8449 | 34.778 | 32.9362 | 32.8894 | 33.2731 | 34.5007 | 34.0915 | 33.9236 | 37.1622 | 36.1873 | 33.2675 | 34.3453 | 36.1775 | 36.4859 | 37.2761 | 36.178 | 32.9446 | 32.3782 | 34.1824 | 34.5556 | 32.5485 | 34.2906 | 34.3588 | 34.2664 | 34.3529 | 34.2937 | 34.2737 | 33.9405 | 34.3584 | 36.1852 | 34.896 | 36.5768 | 36.5278 | 33.2735 | 94.3156 | 94.7267 | 93.9815
2022-09-08 06:07 | 8:17 | 16.9206 | 17.2442 | 19.7492 | 34.2896 | 34.313 | 34.0791 | 34.5372 | 35.545 | 36.5716 | 37.5373 | 36.9963 | 38.208 | 34.2498 | 34.2842 | 34.071 | 35.1417 | 34.8224 | 35.3323 | 35.9827 | 36.4253 | 20.7124 | 16.8119 | 93.9794 | 32.6529 | 32.8235 | 34.7883 | 32.9362 | 32.8335 | 33.2868 | 34.4851 | 34.0866 | 33.9326 | 37.1456 | 36.1834 | 33.2565 | 34.3419 | 36.1684 | 36.4729 | 37.248 | 36.1728 | 32.9274 | 32.3753 | 34.1823 | 34.5311 | 32.5402 | 34.303 | 34.3591 | 34.2804 | 34.3337 | 34.299 | 34.2811 | 33.906 | 34.3529 | 36.1705 | 34.9027 | 36.5642 | 36.5333 | 33.2712 | 94.5012 | 94.917 | 94.1318
2022-09-08 06:07 | 8:17 | 16.9405 | 17.2293 | 19.7462 | 34.33 | 34.3244 | 34.0721 | 34.5441 | 35.5312 | 36.5807 | 37.551 | 37.0036 | 38.2055 | 34.2512 | 34.2468 | 34.0641 | 35.1394 | 34.8228 | 35.3159 | 35.9807 | 36.4348 | 20.6882 | 16.8277 | 94.0944 | 32.7267 | 32.8353 | 34.7868 | 32.9409 | 32.8751 | 33.2647 | 34.4937 | 34.0832 | 33.9419 | 37.1612 | 36.1805 | 33.2556 | 34.349 | 36.1873 | 36.4856 | 37.2664 | 36.1763 | 32.9337 | 32.37 | 34.1664 | 34.5346 | 32.5371 | 34.3096 | 34.3635 | 34.2507 | 34.3691 | 34.2969 | 34.2745 | 33.9224 | 34.3337 | 36.17 | 34.9055 | 36.5854 | 36.5359 | 33.2711 | 94.716 | 95.1022 | 94.2366
2022-09-08 06:07 | 8:17 | 17.0958 | 17.3085 | 19.7379 | 34.2839 | 34.3288 | 34.0625 | 34.5455 | 35.5517 | 36.5793 | 37.5519 | 37.0119 | 38.2162 | 34.2606 | 34.2913 | 34.0694 | 35.1535 | 34.8327 | 35.308 | 35.9828 | 36.4325 | 20.6821 | 16.8079 | 94.2209 | 32.661 | 32.8364 | 34.7769 | 32.9181 | 32.8633 | 33.2571 | 34.4973 | 34.0701 | 33.9321 | 37.1451 | 36.1759 | 33.2566 | 34.3472 | 36.1834 | 36.4937 | 37.2582 | 36.1775 | 32.9366 | 32.363 | 34.175 | 34.5248 | 32.5444 | 34.3166 | 34.3685 | 34.2644 | 34.3538 | 34.3258 | 34.2622 | 33.8994 | 34.3691 | 36.1707 | 34.878 | 36.5777 | 36.5333 | 33.2587 | 94.8721 | 95.2519 | 94.359
2022-09-08 06:07 | 8:17 | 17.0916 | 17.2557 | 19.7394 | 34.3431 | 34.3239 | 34.0675 | 34.5617 | 35.5381 | 36.5662 | 37.5499 | 37.0083 | 38.2252 | 34.2593 | 34.2656 | 34.0675 | 35.1379 | 34.8249 | 35.3274 | 35.9739 | 36.4246 | 20.6719 | 16.7951 | 94.2778 | 32.7512 | 32.8417 | 34.7803 | 32.9446 | 32.8427 | 33.2675 | 34.4904 | 34.0676 | 33.9391 | 37.139 | 36.1729 | 33.2612 | 34.3376 | 36.1805 | 36.4734 | 37.2854 | 36.1684 | 32.9238 | 32.3552 | 34.1741 | 34.5217 | 32.5209 | 34.3011 | 34.3706 | 34.2642 | 34.3608 | 34.3029 | 34.27 | 33.9019 | 34.3538 | 36.1634 | 34.9113 | 36.5806 | 36.5289 | 33.2805 | 94.9409 | 95.4036 | 94.3056
2022-09-08 06:07 | 8:17 | 16.8788 | 17.1889 | 19.718 | 34.2993 | 34.3225 | 34.0758 | 34.5348 | 35.5482 | 36.5588 | 37.5369 | 37.0207 | 38.1931 | 34.2701 | 34.2704 | 34.0482 | 35.1377 | 34.815 | 35.3235 | 35.9625 | 36.432 | 20.6492 | 16.775 | 94.3419 | 32.7191 | 32.8385 | 34.7711 | 32.9274 | 32.8538 | 33.2565 | 34.4821 | 34.0711 | 33.9368 | 37.145 | 36.1752 | 33.2569 | 34.3268 | 36.1759 | 36.4847 | 37.2687 | 36.1873 | 32.9252 | 32.3618 | 34.1573 | 34.5141 | 32.5325 | 34.3074 | 34.341 | 34.2582 | 34.3752 | 34.3067 | 34.2511 | 33.9117 | 34.3608 | 36.1721 | 34.8765 | 36.5898 | 36.5263 | 33.2348 | 95.0721 | 95.5314 | 94.4774
2022-09-08 06:07 | 8:17 | 16.8721 | 17.1565 | 19.6613 | 34.2767 | 34.3261 | 34.0743 | 34.5482 | 35.5586 | 36.5568 | 37.5447 | 36.9926 | 38.1934 | 34.2762 | 34.2802 | 34.0442 | 35.1302 | 34.8204 | 35.3335 | 35.9594 | 36.4268 | 20.6247 | 16.7617 | 94.5063 | 32.6236 | 32.8241 | 34.7737 | 32.9337 | 32.84 | 33.2556 | 34.4763 | 34.068 | 33.9195 | 37.1197 | 36.1794 | 33.2479 | 34.3368 | 36.1729 | 36.4729 | 37.2543 | 36.1834 | 32.9338 | 32.3613 | 34.1619 | 34.5089 | 32.5217 | 34.314 | 34.3583 | 34.254 | 34.3791 | 34.2895 | 34.2481 | 33.9238 | 34.3752 | 36.1501 | 34.8818 | 36.5788 | 36.533 | 33.2381 | 95.2721 | 95.6295 | 94.6386
2022-09-08 06:08 | 8:17 | 16.8457 | 17.1527 | 19.671 | 34.3149 | 34.3142 | 34.0789 | 34.5578 | 35.5484 | 36.5595 | 37.5466 | 36.9988 | 38.2041 | 34.2689 | 34.2751 | 34.0442 | 35.1348 | 34.808 | 35.3244 | 35.9757 | 36.4214 | 20.6225 | 16.7319 | 94.6221 | 32.6942 | 32.792 | 34.775 | 32.9366 | 32.8571 | 33.2566 | 34.4712 | 34.0865 | 33.9394 | 37.1438 | 36.1836 | 33.2291 | 34.3294 | 36.1752 | 36.4664 | 37.2565 | 36.1805 | 32.9149 | 32.3388 | 34.1483 | 34.5029 | 32.5155 | 34.3114 | 34.3644 | 34.2614 | 34.3809 | 34.3012 | 34.2468 | 33.8932 | 34.3791 | 36.1509 | 34.8751 | 36.5684 | 36.503 | 33.2192 | 95.3781 | 95.783 | 94.8489
2022-09-08 06:08 | 8:18 | 16.8629 | 17.1425 | 19.6427 | 34.1344 | 34.3062 | 34.0794 | 34.5546 | 35.5475 | 36.5657 | 37.5305 | 36.9981 | 38.2016 | 34.2475 | 34.2851 | 34.0088 | 35.1415 | 34.8169 | 35.3105 | 35.9504 | 36.4146 | 20.5989 | 16.7044 | 94.6988 | 32.7375 | 32.8095 | 34.7472 | 32.9238 | 32.8656 | 33.2612 | 34.4808 | 34.0684 | 33.9019 | 37.1236 | 36.1599 | 33.2351 | 34.3385 | 36.1794 | 36.4826 | 37.2248 | 36.1759 | 32.9157 | 32.336 | 34.1339 | 34.4818 | 32.5203 | 34.3255 | 34.3421 | 34.2462 | 34.3785 | 34.3086 | 34.261 | 33.8947 | 34.3809 | 36.1656 | 34.8896 | 36.5561 | 36.5058 | 33.2293 | 95.4473 | 95.8285 | 94.7403
2022-09-08 06:08 | 8:18 | 16.8695 | 17.2021 | 19.6552 | 34.2787 | 34.2966 | 34.0717 | 34.5586 | 35.5401 | 36.5454 | 37.5315 | 37.0076 | 38.1914 | 34.249 | 34.2754 | 34.046 | 35.1333 | 34.8158 | 35.3154 | 35.9529 | 36.4209 | 20.608 | 16.7077 | 94.6501 | 32.6304 | 32.7953 | 34.7727 | 32.9252 | 32.8575 | 33.2569 | 34.4769 | 34.0822 | 33.9233 | 37.145 | 36.1632 | 33.2194 | 34.324 | 36.1836 | 36.479 | 37.2451 | 36.1729 | 32.9087 | 32.3473 | 34.1386 | 34.4804 | 32.4971 | 34.3178 | 34.3474 | 34.2474 | 34.3936 | 34.3017 | 34.2557 | 33.8983 | 34.3785 | 36.1691 | 34.8937 | 36.5589 | 36.5249 | 33.2284 | 95.4323 | 95.8313 | 94.7238
2022-09-08 06:08 | 8:18 | 16.9236 | 17.2402 | 19.6783 | 34.0943 | 34.2999 | 34.0763 | 34.5549 | 35.5421 | 36.5542 | 37.5275 | 37.0152 | 38.2002 | 34.2628 | 34.2948 | 34.0506 | 35.1224 | 34.8005 | 35.3011 | 35.9517 | 36.411 | 20.6131 | 16.7099 | 94.6192 | 32.6625 | 32.8062 | 34.7843 | 32.9338 | 32.8296 | 33.2479 | 34.473 | 34.0754 | 33.9173 | 37.1163 | 36.1686 | 33.2365 | 34.3285 | 36.1599 | 36.4635 | 37.2457 | 36.1752 | 32.916 | 32.3422 | 34.1492 | 34.4744 | 32.4764 | 34.3201 | 34.3342 | 34.2508 | 34.3852 | 34.2989 | 34.2413 | 33.9017 | 34.3936 | 36.1349 | 34.8708 | 36.5899 | 36.509 | 33.2204 | 95.2413 | 95.6809 | 94.6935
2022-09-08 06:08 | 8:18 | 16.8036 | 17.1193 | 19.6422 | 34.2529 | 34.2922 | 34.0734 | 34.5274 | 35.5264 | 36.5506 | 37.4932 | 37.0066 | 38.2039 | 34.2939 | 34.2815 | 34.0263 | 35.1317 | 34.8199 | 35.2944 | 35.9496 | 36.4016 | 20.6188 | 16.6711 | 94.3992 | 32.6304 | 32.7934 | 34.7585 | 32.9149 | 32.8423 | 33.2291 | 34.4617 | 34.0774 | 33.9299 | 37.1179 | 36.1595 | 33.2153 | 34.3359 | 36.1632 | 36.4588 | 37.2448 | 36.1794 | 32.9189 | 32.3256 | 34.1247 | 34.4657 | 32.5085 | 34.3068 | 34.3607 | 34.2349 | 34.3935 | 34.3104 | 34.2545 | 33.8778 | 34.3852 | 36.13 | 34.8785 | 36.5748 | 36.5193 | 33.2133 | 94.9777 | 95.4059 | 94.3698
2022-09-08 06:08 | 8:18 | 16.825 | 17.1138 | 19.6299 | 34.1661 | 34.2822 | 34.0682 | 34.5196 | 35.5371 | 36.5377 | 37.5175 | 36.9997 | 38.2017 | 34.2703 | 34.2925 | 34.0449 | 35.1189 | 34.8096 | 35.3002 | 35.9353 | 36.3996 | 20.6219 | 16.6467 | 94.2165 | 32.6758 | 32.7769 | 34.7518 | 32.9157 | 32.8336 | 33.2351 | 34.4554 | 34.0829 | 33.9301 | 37.1266 | 36.1742 | 33.2244 | 34.3147 | 36.1686 | 36.4428 | 37.2231 | 36.1836 | 32.9102 | 32.3381 | 34.1081 | 34.4676 | 32.4959 | 34.3392 | 34.3311 | 34.2412 | 34.3933 | 34.3215 | 34.2747 | 33.8852 | 34.3935 | 36.1318 | 34.8926 | 36.574 | 36.4994 | 33.2145 | 94.6689 | 95.135 | 94.1758
2022-09-08 06:09 | 8:19 | 16.819 | 17.1201 | 19.5838 | 34.1051 | 34.294 | 34.0642 | 34.5545 | 35.5354 | 36.544 | 37.5305 | 37.0031 | 38.1988 | 34.286 | 34.2835 | 34.026 | 35.134 | 34.7904 | 35.2897 | 35.9458 | 36.3932 | 20.6341 | 16.6242 | 94.179 | 32.6213 | 32.7835 | 34.7547 | 32.9087 | 32.8188 | 33.2194 | 34.4621 | 34.056 | 33.9093 | 37.124 | 36.1529 | 33.2326 | 34.3206 | 36.1595 | 36.471 | 37.2325 | 36.1599 | 32.9129 | 32.3203 | 34.1193 | 34.4472 | 32.493 | 34.3227 | 34.3288 | 34.2477 | 34.4112 | 34.3095 | 34.2582 | 33.8641 | 34.3933 | 36.1363 | 34.8779 | 36.5633 | 36.506 | 33.193 | 94.5083 | 94.8954 | 94.1773
2022-09-08 06:09 | 8:19 | 16.8457 | 17.1559 | 19.5801 | 34.2535 | 34.2755 | 34.0671 | 34.538 | 35.5202 | 36.5382 | 37.5136 | 36.9963 | 38.2043 | 34.2558 | 34.2959 | 34.019 | 35.1176 | 34.787 | 35.2777 | 35.9249 | 36.407 | 20.6495 | 16.6386 | 94.129 | 32.5536 | 32.7899 | 34.7505 | 32.916 | 32.8212 | 33.2365 | 34.4377 | 34.0731 | 33.9048 | 37.1138 | 36.1678 | 33.2212 | 34.3161 | 36.1742 | 36.4557 | 37.2403 | 36.1632 | 32.9085 | 32.3328 | 34.097 | 34.4428 | 32.4905 | 34.3351 | 34.345 | 34.249 | 34.4102 | 34.3237 | 34.2571 | 33.8653 | 34.4112 | 36.1287 | 34.8585 | 36.5722 | 36.5231 | 33.2084 | 94.4292 | 94.7413 | 94.0795
2022-09-08 06:09 | 8:19 | 16.7891 | 17.1133 | 19.5903 | 34.0811 | 34.2824 | 34.0796 | 34.507 | 35.5214 | 36.5353 | 37.4971 | 36.9795 | 38.2089 | 34.2534 | 34.28 | 34.0331 | 35.1209 | 34.7976 | 35.2779 | 35.9378 | 36.3789 | 20.6767 | 16.613 | 93.9498 | 32.5605 | 32.7835 | 34.7585 | 32.9189 | 32.8297 | 33.2153 | 34.4653 | 34.0791 | 33.9201 | 37.115 | 36.1734 | 33.2272 | 34.3375 | 36.1529 | 36.4763 | 37.2256 | 36.1686 | 32.8962 | 32.3122 | 34.0889 | 34.4207 | 32.4616 | 34.3438 | 34.3416 | 34.252 | 34.3972 | 34.3314 | 34.2629 | 33.8652 | 34.4102 | 36.1205 | 34.8713 | 36.5874 | 36.4922 | 33.1842 | 94.3542 | 94.6166 | 93.9397
2022-09-08 06:09 | 8:19 | 16.8122 | 17.1302 | 19.5566 | 34.2043 | 34.2851 | 34.0498 | 34.5288 | 35.531 | 36.5316 | 37.5075 | 37.0049 | 38.1895 | 34.2879 | 34.271 | 34.0124 | 35.1013 | 34.7842 | 35.2838 | 35.9474 | 36.3855 | 20.7144 | 16.5921 | 93.8911 | 32.7748 | 32.7756 | 34.7656 | 32.9102 | 32.8307 | 33.2244 | 34.4634 | 34.0768 | 33.8997 | 37.1134 | 36.175 | 33.2282 | 34.3301 | 36.1678 | 36.4492 | 37.2317 | 36.1595 | 32.9064 | 32.3085 | 34.0907 | 34.4533 | 32.4735 | 34.332 | 34.3332 | 34.2547 | 34.399 | 34.3381 | 34.2689 | 33.8863 | 34.3972 | 36.1055 | 34.895 | 36.5592 | 36.5138 | 33.193 | 94.1698 | 94.5141 | 93.8441
2022-09-08 06:09 | 8:19 | 16.8345 | 17.1184 | 19.5755 | 34.0433 | 34.3019 | 34.0508 | 34.5177 | 35.522 | 36.544 | 37.4979 | 37.0152 | 38.2133 | 34.2669 | 34.2752 | 34.0002 | 35.1122 | 34.786 | 35.2906 | 35.9196 | 36.3828 | 20.7244 | 16.6234 | 93.866 | 32.6235 | 32.7742 | 34.7521 | 32.9129 | 32.8143 | 33.2326 | 34.4492 | 34.0746 | 33.8995 | 37.0966 | 36.1699 | 33.2383 | 34.3128 | 36.1734 | 36.4552 | 37.2176 | 36.1742 | 32.901 | 32.311 | 34.0979 | 34.4364 | 32.4815 | 34.3407 | 34.3311 | 34.252 | 34.3997 | 34.3392 | 34.2512 | 33.8605 | 34.399 | 36.1154 | 34.8698 | 36.5802 | 36.5062 | 33.1757 | 94.1649 | 94.4471 | 93.8175
2022-09-08 06:09 | 8:19 | 16.7899 | 17.0907 | 19.5628 | 34.0958 | 34.2693 | 34.068 | 34.514 | 35.5258 | 36.5433 | 37.4979 | 36.9869 | 38.2134 | 34.2662 | 34.3047 | 33.9952 | 35.1166 | 34.7887 | 35.2953 | 35.9228 | 36.3716 | 20.7711 | 16.5994 | 93.7856 | 32.5235 | 32.7652 | 34.7485 | 32.9085 | 32.8136 | 33.2212 | 34.449 | 34.0649 | 33.9056 | 37.1008 | 36.1534 | 33.1953 | 34.3293 | 36.175 | 36.4474 | 37.2001 | 36.1529 | 32.9016 | 32.2937 | 34.0705 | 34.437 | 32.4886 | 34.3383 | 34.3335 | 34.2461 | 34.3953 | 34.3358 | 34.28 | 33.8463 | 34.3997 | 36.1278 | 34.8828 | 36.5706 | 36.5099 | 33.1686 | 94.0478 | 94.3681 | 93.7224
2022-09-08 06:10 | 8:20 | 16.804 | 17.1022 | 19.5506 | 34.1769 | 34.2663 | 34.0569 | 34.5385 | 35.5235 | 36.507 | 37.5103 | 36.9906 | 38.1893 | 34.275 | 34.2929 | 34.0047 | 35.1083 | 34.7739 | 35.2862 | 35.9244 | 36.3728 | 20.7797 | 16.6161 | 93.8061 | 32.4991 | 32.7665 | 34.7405 | 32.8962 | 32.8384 | 33.2272 | 34.4323 | 34.0924 | 33.9145 | 37.1079 | 36.1708 | 33.2228 | 34.3365 | 36.1699 | 36.4715 | 37.2217 | 36.1678 | 32.896 | 32.2918 | 34.1041 | 34.444 | 32.4813 | 34.3452 | 34.3579 | 34.2366 | 34.3881 | 34.3331 | 34.251 | 33.8931 | 34.3953 | 36.1122 | 34.8511 | 36.5845 | 36.5026 | 33.1598 | 93.9807 | 94.2856 | 93.7557
2022-09-08 06:10 | 8:20 | 16.8142 | 17.117 | 19.5598 | 34.0456 | 34.2629 | 34.0634 | 34.5169 | 35.5253 | 36.519 | 37.5116 | 37.014 | 38.1971 | 34.2634 | 34.2865 | 34 | 35.1204 | 34.7588 | 35.2889 | 35.9002 | 36.3653 | 20.7815 | 16.6238 | 93.8386 | 32.5256 | 32.7548 | 34.7518 | 32.9064 | 32.8237 | 33.2282 | 34.4454 | 34.0743 | 33.9168 | 37.1063 | 36.1608 | 33.2225 | 34.3248 | 36.1534 | 36.4799 | 37.2079 | 36.1734 | 32.9003 | 32.2974 | 34.0943 | 34.412 | 32.4542 | 34.3527 | 34.3336 | 34.2515 | 34.3895 | 34.3338 | 34.2677 | 33.8601 | 34.3881 | 36.1333 | 34.8666 | 36.5839 | 36.4961 | 33.1679 | 93.9887 | 94.2065 | 93.8716
2022-09-08 06:10 | 8:20 | 16.8174 | 17.1334 | 19.56 | 34.123 | 34.2881 | 34.0763 | 34.5435 | 35.5281 | 36.5354 | 37.5002 | 37.0111 | 38.1998 | 34.2786 | 34.2938 | 34.0012 | 35.1144 | 34.794 | 35.2789 | 35.928 | 36.3662 | 20.7733 | 16.6266 | 93.8189 | 32.6017 | 32.7626 | 34.7375 | 32.901 | 32.8112 | 33.2383 | 34.4567 | 34.0746 | 33.9118 | 37.0962 | 36.171 | 33.2225 | 34.3297 | 36.1708 | 36.4574 | 37.1992 | 36.175 | 32.9011 | 32.2953 | 34.063 | 34.4171 | 32.4483 | 34.3428 | 34.344 | 34.2602 | 34.3994 | 34.3394 | 34.2712 | 33.8683 | 34.3895 | 36.1136 | 34.8682 | 36.5841 | 36.4813 | 33.1753 | 93.9075 | 94.1193 | 93.7775
2022-09-08 06:10 | 8:20 | 16.8586 | 17.1087 | 19.5866 | 34.0806 | 34.2826 | 34.0678 | 34.5454 | 35.5236 | 36.5161 | 37.5012 | 37.0162 | 38.1955 | 34.2697 | 34.2823 | 33.9963 | 35.1244 | 34.781 | 35.2782 | 35.9348 | 36.3799 | 20.7887 | 16.662 | 93.7844 | 32.8215 | 32.7731 | 34.7329 | 32.9016 | 32.8261 | 33.1953 | 34.4317 | 34.0636 | 33.9108 | 37.1032 | 36.1521 | 33.2158 | 34.3348 | 36.1608 | 36.4568 | 37.2022 | 36.1699 | 32.922 | 32.2716 | 34.0871 | 34.4181 | 32.4459 | 34.3482 | 34.3444 | 34.2486 | 34.4104 | 34.3469 | 34.2596 | 33.852 | 34.3994 | 36.1274 | 34.8698 | 36.5742 | 36.4978 | 33.1497 | 93.8089 | 94.0673 | 93.7089
2022-09-08 06:10 | 8:20 | 16.7934 | 17.0671 | 19.5357 | 34.121 | 34.2842 | 34.0674 | 34.5318 | 35.5231 | 36.5275 | 37.4955 | 37.0113 | 38.1994 | 34.2917 | 34.2969 | 34.0157 | 35.1187 | 34.7741 | 35.2767 | 35.9126 | 36.3727 | 20.7764 | 16.6291 | 93.7205 | 32.8005 | 32.7669 | 34.7441 | 32.896 | 32.8232 | 33.2228 | 34.4427 | 34.0913 | 33.915 | 37.1258 | 36.1634 | 33.233 | 34.3309 | 36.171 | 36.4504 | 37.2077 | 36.1534 | 32.8993 | 32.2643 | 34.0713 | 34.3976 | 32.4333 | 34.3473 | 34.3359 | 34.2589 | 34.41 | 34.3445 | 34.265 | 33.8512 | 34.4104 | 36.1206 | 34.8816 | 36.5867 | 36.5061 | 33.1519 | 93.8348 | 94.0135 | 93.7171
2022-09-08 06:10 | 8:20 | 16.8017 | 17.0409 | 19.508 | 34.0853 | 34.3017 | 34.0561 | 34.5281 | 35.5254 | 36.5242 | 37.5001 | 37.0095 | 38.2103 | 34.2805 | 34.2948 | 33.9962 | 35.1234 | 34.7829 | 35.2951 | 35.9199 | 36.3804 | 20.7637 | 16.6287 | 93.6731 | 32.6902 | 32.764 | 34.7456 | 32.9003 | 32.821 | 33.2225 | 34.4446 | 34.0777 | 33.924 | 37.0949 | 36.1628 | 33.2278 | 34.3379 | 36.1521 | 36.4715 | 37.2007 | 36.1708 | 32.8937 | 32.2752 | 34.0542 | 34.425 | 32.4443 | 34.3667 | 34.3496 | 34.2389 | 34.4086 | 34.3536 | 34.2678 | 33.8532 | 34.41 | 36.1327 | 34.8835 | 36.5735 | 36.4831 | 33.1682 | 93.7442 | 93.9512 | 93.5687
2022-09-08 06:11 | 8:20 | 16.7525 | 17.0221 | 19.492 | 34.1557 | 34.2799 | 34.0908 | 34.5274 | 35.5329 | 36.513 | 37.5035 | 36.9935 | 38.2047 | 34.2874 | 34.2814 | 34.002 | 35.1203 | 34.7761 | 35.2793 | 35.9263 | 36.3729 | 20.7798 | 16.6594 | 93.7444 | 32.5402 | 32.7692 | 34.7123 | 32.9011 | 32.8168 | 33.2225 | 34.4393 | 34.0935 | 33.9035 | 37.0947 | 36.1608 | 33.2118 | 34.3317 | 36.1634 | 36.4808 | 37.2116 | 36.1608 | 32.8775 | 32.2681 | 34.0622 | 34.398 | 32.4398 | 34.3587 | 34.349 | 34.229 | 34.3999 | 34.3582 | 34.2611 | 33.8602 | 34.4086 | 36.1073 | 34.8753 | 36.5806 | 36.5213 | 33.1552 | 93.7565 | 93.9186 | 93.6737
2022-09-08 06:11 | 8:21 | 16.7424 | 17.034 | 19.4873 | 34.1043 | 34.2571 | 34.0669 | 34.5352 | 35.5215 | 36.5252 | 37.5005 | 37.0178 | 38.226 | 34.2894 | 34.2944 | 34.0108 | 35.1166 | 34.7643 | 35.3058 | 35.9106 | 36.3725 | 20.7459 | 16.6412 | 93.6516 | 32.6886 | 32.7596 | 34.7491 | 32.922 | 32.8372 | 33.2158 | 34.4272 | 34.076 | 33.9011 | 37.1106 | 36.169 | 33.2282 | 34.3295 | 36.1628 | 36.453 | 37.2104 | 36.171 | 32.8924 | 32.2657 | 34.0746 | 34.3992 | 32.432 | 34.3461 | 34.3373 | 34.2635 | 34.4051 | 34.3729 | 34.2842 | 33.8575 | 34.3999 | 36.1285 | 34.875 | 36.5568 | 36.4862 | 33.1316 | 93.6571 | 93.841 | 93.5712
2022-09-08 06:11 | 8:21 | 16.7482 | 17.0077 | 19.4802 | 34.1349 | 34.2722 | 34.0684 | 34.5346 | 35.5361 | 36.5459 | 37.5102 | 37.0075 | 38.2234 | 34.2747 | 34.2867 | 33.9985 | 35.1165 | 34.7685 | 35.2813 | 35.918 | 36.3535 | 20.7312 | 16.6214 | 93.5121 | 32.591 | 32.7578 | 34.7501 | 32.8993 | 32.8323 | 33.233 | 34.4419 | 34.0839 | 33.9117 | 37.1118 | 36.1421 | 33.2022 | 34.3592 | 36.1608 | 36.4545 | 37.2182 | 36.1521 | 32.9 | 32.2809 | 34.0561 | 34.4142 | 32.4119 | 34.3722 | 34.3445 | 34.2428 | 34.408 | 34.3713 | 34.2468 | 33.8671 | 34.4051 | 36.11 | 34.8814 | 36.5875 | 36.5083 | 33.1674 | 93.5506 | 93.7612 | 93.4582
2022-09-08 06:11 | 8:21 | 16.6987 | 16.9687 | 19.4537 | 34.02 | 34.2711 | 34.0584 | 34.5271 | 35.5256 | 36.5224 | 37.5043 | 36.9992 | 38.2129 | 34.2704 | 34.2902 | 34.0018 | 35.1222 | 34.761 | 35.2831 | 35.9097 | 36.3847 | 20.7219 | 16.5945 | 93.4511 | 32.4467 | 32.7656 | 34.7445 | 32.8937 | 32.8046 | 33.2278 | 34.4306 | 34.0909 | 33.9138 | 37.0978 | 36.1456 | 33.2101 | 34.3314 | 36.169 | 36.464 | 37.2226 | 36.1634 | 32.8937 | 32.2699 | 34.0637 | 34.4044 | 32.4081 | 34.3576 | 34.315 | 34.2258 | 34.3934 | 34.3734 | 34.2913 | 33.8481 | 34.408 | 36.1129 | 34.8757 | 36.5704 | 36.5043 | 33.1442 | 93.4848 | 93.6586 | 93.3932
2022-09-08 06:11 | 8:21 | 16.6905 | 16.9374 | 19.4517 | 34.0078 | 34.2737 | 34.0711 | 34.5384 | 35.5282 | 36.5219 | 37.5054 | 37.0121 | 38.2338 | 34.2749 | 34.3059 | 34.0078 | 35.1193 | 34.7603 | 35.264 | 35.9066 | 36.364 | 20.684 | 16.5567 | 93.3528 | 32.5366 | 32.7651 | 34.7334 | 32.8775 | 32.8322 | 33.2118 | 34.4476 | 34.0864 | 33.9104 | 37.1094 | 36.1584 | 33.2113 | 34.337 | 36.1421 | 36.4685 | 37.2065 | 36.1628 | 32.889 | 32.2618 | 34.0686 | 34.4119 | 32.4228 | 34.3737 | 34.341 | 34.2403 | 34.4028 | 34.3648 | 34.2656 | 33.8433 | 34.3934 | 36.1122 | 34.8572 | 36.5712 | 36.4905 | 33.1327 | 93.347 | 93.5555 | 93.3131
2022-09-08 06:11 | 8:21 | 16.6884 | 17.0134 | 19.4409 | 34.1516 | 34.2811 | 34.08 | 34.5321 | 35.5417 | 36.5204 | 37.503 | 37.0067 | 38.2255 | 34.2869 | 34.2955 | 33.99 | 35.1422 | 34.764 | 35.286 | 35.9182 | 36.3897 | 20.6573 | 16.5746 | 93.3052 | 32.6928 | 32.7381 | 34.7326 | 32.8924 | 32.8143 | 33.2282 | 34.4424 | 34.1115 | 33.9119 | 37.1137 | 36.1585 | 33.2003 | 34.3312 | 36.1456 | 36.4656 | 37.2104 | 36.1608 | 32.895 | 32.2522 | 34.0635 | 34.4018 | 32.4032 | 34.3758 | 34.3511 | 34.2407 | 34.3976 | 34.3543 | 34.2704 | 33.8536 | 34.4028 | 36.1224 | 34.8632 | 36.5632 | 36.5095 | 33.1433 | 93.269 | 93.4489 | 93.2482
2022-09-08 06:12 | 8:22 | 16.725 | 16.685 | 19.372 | 34.101 | 34.2745 | 34.0723 | 34.5428 | 35.5312 | 36.5324 | 37.4973 | 37.0113 | 38.1953 | 34.2694 | 34.306 | 33.9782 | 35.1283 | 34.7664 | 35.2946 | 35.9188 | 36.3747 | 20.6461 | 16.3829 | 93.2309 | 32.6375 | 32.751 | 34.7378 | 32.9 | 32.8219 | 33.2022 | 34.4408 | 34.0833 | 33.9032 | 37.1153 | 36.1603 | 33.1981 | 34.329 | 36.1584 | 36.4622 | 37.2148 | 36.169 | 32.8768 | 32.2624 | 34.0635 | 34.381 | 32.4141 | 34.3654 | 34.3333 | 34.2518 | 34.396 | 34.3762 | 34.2802 | 33.853 | 34.3976 | 36.1255 | 34.8748 | 36.5757 | 36.5126 | 33.1441 | 93.1774 | 93.3655 | 93.1562
2022-09-08 06:12 | 8:22 | 17.5339 | 15.7837 | 19.4378 | 33.9874 | 34.2622 | 34.0744 | 34.5311 | 35.5145 | 36.5241 | 37.4787 | 37.0093 | 38.2053 | 34.2996 | 34.3017 | 34.0005 | 35.1364 | 34.7629 | 35.2791 | 35.9099 | 36.3489 | 20.5166 | 16.0814 | 93.1422 | 32.4753 | 32.7376 | 34.7349 | 32.8937 | 32.8013 | 33.2101 | 34.4367 | 34.0836 | 33.9125 | 37.1166 | 36.1593 | 33.2103 | 34.3457 | 36.1585 | 36.4563 | 37.2078 | 36.1421 | 32.872 | 32.2647 | 34.0653 | 34.4119 | 32.4129 | 34.3736 | 34.3394 | 34.2593 | 34.3892 | 34.3655 | 34.2751 | 33.838 | 34.396 | 36.1291 | 34.8817 | 36.5804 | 36.5028 | 33.1463 | 93.1171 | 93.2792 | 93.219
2022-09-08 06:12 | 8:22 | 18.9664 | 16.1901 | 20.8545 | 34.0718 | 34.27 | 34.0532 | 34.5231 | 35.5212 | 36.5115 | 37.4832 | 37.0129 | 38.2141 | 34.2873 | 34.3127 | 33.9935 | 35.1105 | 34.7773 | 35.279 | 35.9049 | 36.3855 | 20.0578 | 15.7236 | 93.1269 | 32.4316 | 32.7382 | 34.7235 | 32.889 | 32.8128 | 33.2113 | 34.4402 | 34.0827 | 33.9266 | 37.1055 | 36.1368 | 33.2043 | 34.3283 | 36.1603 | 36.4658 | 37.193 | 36.1456 | 32.882 | 32.254 | 34.0502 | 34.3908 | 32.3919 | 34.365 | 34.3388 | 34.2651 | 34.3887 | 34.3598 | 34.2851 | 33.8295 | 34.3892 | 36.1314 | 34.8565 | 36.5688 | 36.4969 | 33.1511 | 93.0005 | 93.1441 | 93.0907
2022-09-08 06:12 | 8:22 | 20.5099 | 17.4084 | 22.4141 | 34.2026 | 34.2511 | 34.0699 | 34.5438 | 35.5334 | 36.505 | 37.4629 | 37.0239 | 38.2172 | 34.2894 | 34.2973 | 33.9901 | 35.1169 | 34.7752 | 35.2826 | 35.9232 | 36.3627 | 19.2176 | 15.4886 | 93.0402 | 32.4243 | 32.7385 | 34.7291 | 32.895 | 32.8019 | 33.2003 | 34.441 | 34.0852 | 33.901 | 37.1171 | 36.1412 | 33.1909 | 34.3366 | 36.1593 | 36.4649 | 37.1889 | 36.1584 | 32.8671 | 32.2247 | 34.0464 | 34.3831 | 32.385 | 34.3742 | 34.326 | 34.2621 | 34.3996 | 34.3743 | 34.2754 | 33.8377 | 34.3887 | 36.1144 | 34.8648 | 36.5653 | 36.5035 | 33.1461 | 92.8571 | 93.0354 | 92.9565
2022-09-08 06:12 | 8:22 | 21.7223 | 18.9508 | 23.7668 | 34.362 | 34.2481 | 34.0842 | 34.5377 | 35.5189 | 36.5163 | 37.5108 | 37.016 | 38.2176 | 34.3071 | 34.2945 | 33.9988 | 35.1282 | 34.7677 | 35.3006 | 35.8942 | 36.3646 | 18.1373 | 15.1189 | 92.9761 | 32.282 | 32.7413 | 34.7405 | 32.8768 | 32.7996 | 33.1981 | 34.4232 | 34.1207 | 33.8847 | 37.1049 | 36.1561 | 33.1955 | 34.3266 | 36.1368 | 36.4794 | 37.1928 | 36.1585 | 32.8853 | 32.2656 | 34.0424 | 34.3953 | 32.3718 | 34.3771 | 34.3241 | 34.27 | 34.3967 | 34.3795 | 34.2948 | 33.8305 | 34.3996 | 36.1219 | 34.8416 | 36.571 | 36.5003 | 33.1389 | 92.7541 | 92.9201 | 92.877
2022-09-08 06:12 | 8:22 | 22.6757 | 20.461 | 24.8969 | 34.4652 | 34.2468 | 34.0729 | 34.5292 | 35.5143 | 36.5322 | 37.4996 | 37.022 | 38.2039 | 34.2902 | 34.3198 | 33.9967 | 35.1223 | 34.7724 | 35.2873 | 35.9345 | 36.375 | 16.538 | 14.8619 | 92.9373 | 32.3094 | 32.7278 | 34.7139 | 32.872 | 32.8177 | 33.2103 | 34.4388 | 34.0894 | 33.8928 | 37.1144 | 36.1624 | 33.2084 | 34.3298 | 36.1412 | 36.4779 | 37.2062 | 36.1603 | 32.886 | 32.2499 | 34.0511 | 34.3831 | 32.3795 | 34.3799 | 34.3041 | 34.2677 | 34.4045 | 34.3848 | 34.2815 | 33.8403 | 34.3967 | 36.1189 | 34.8475 | 36.5751 | 36.5081 | 33.1359 | 92.6494 | 92.7742 | 92.796
2022-09-08 06:13 | 8:22 | 23.4691 | 21.8323 | 25.81 | 34.5647 | 34.261 | 34.0891 | 34.5238 | 35.5389 | 36.5188 | 37.4969 | 37.0204 | 38.2274 | 34.3048 | 34.2975 | 33.9768 | 35.1163 | 34.7544 | 35.2928 | 35.9314 | 36.349 | 15.1368 | 14.4102 | 92.7895 | 32.1604 | 32.718 | 34.7262 | 32.882 | 32.8024 | 33.2043 | 34.4492 | 34.0854 | 33.9025 | 37.1009 | 36.1357 | 33.1779 | 34.3388 | 36.1561 | 36.4743 | 37.2028 | 36.1593 | 32.8764 | 32.2612 | 34.0392 | 34.3789 | 32.3677 | 34.3882 | 34.323 | 34.2653 | 34.393 | 34.3667 | 34.2925 | 33.8419 | 34.4045 | 36.1178 | 34.8651 | 36.5664 | 36.477 | 33.1417 | 92.4916 | 92.6051 | 92.6711
2022-09-08 06:13 | 8:23 | 24.1915 | 23.0945 | 26.5819 | 34.7302 | 34.2557 | 34.0772 | 34.5467 | 35.523 | 36.518 | 37.5089 | 37.0199 | 38.2108 | 34.3002 | 34.311 | 33.9907 | 35.1146 | 34.744 | 35.2996 | 35.9209 | 36.3745 | 13.9193 | 13.2169 | 92.7394 | 32.1069 | 32.7174 | 34.7242 | 32.8671 | 32.7936 | 33.1909 | 34.4498 | 34.0978 | 33.9115 | 37.1116 | 36.1422 | 33.1809 | 34.3398 | 36.1624 | 36.4552 | 37.1891 | 36.1368 | 32.8817 | 32.2471 | 34.0341 | 34.3905 | 32.3421 | 34.3901 | 34.3222 | 34.2663 | 34.3789 | 34.3972 | 34.2835 | 33.8384 | 34.393 | 36.124 | 34.8725 | 36.5702 | 36.4763 | 33.1423 | 92.396 | 92.4852 | 92.6144
2022-09-08 06:13 | 8:23 | 24.8995 | 24.1506 | 27.1702 | 34.6825 | 34.2413 | 34.0799 | 34.5637 | 35.5215 | 36.5429 | 37.5228 | 37.0168 | 38.2136 | 34.2874 | 34.2995 | 33.9913 | 35.1244 | 34.7584 | 35.3065 | 35.9138 | 36.3811 | 13.4651 | 13.2253 | 92.6355 | 32.1428 | 32.7255 | 34.7243 | 32.8853 | 32.7719 | 33.1955 | 34.4291 | 34.102 | 33.9009 | 37.1191 | 36.1333 | 33.2 | 34.3492 | 36.1357 | 36.4539 | 37.2041 | 36.1412 | 32.8583 | 32.2354 | 34.0424 | 34.3786 | 32.3474 | 34.3811 | 34.3071 | 34.2742 | 34.4024 | 34.376 | 34.2959 | 33.8282 | 34.3789 | 36.1298 | 34.8353 | 36.573 | 36.4896 | 33.1158 | 92.3257 | 92.3737 | 92.5516
2022-09-08 06:13 | 8:23 | 25.4151 | 25.1299 | 27.7789 | 34.8769 | 34.2545 | 34.0922 | 34.5663 | 35.5111 | 36.5375 | 37.5194 | 37.0205 | 38.2381 | 34.3012 | 34.3152 | 33.9865 | 35.122 | 34.7621 | 35.3164 | 35.939 | 36.3848 | 14.3338 | 13.928 | 92.5515 | 32.5199 | 32.7081 | 34.7061 | 32.886 | 32.7815 | 33.2084 | 34.4395 | 34.096 | 33.9118 | 37.114 | 36.1493 | 33.1922 | 34.3559 | 36.1422 | 36.4703 | 37.2045 | 36.1561 | 32.8561 | 32.2367 | 34.0352 | 34.3826 | 32.3508 | 34.3834 | 34.3169 | 34.2957 | 34.3758 | 34.3885 | 34.28 | 33.8263 | 34.4024 | 36.1363 | 34.8266 | 36.5742 | 36.493 | 33.1261 | 92.2163 | 92.3123 | 92.3559
2022-09-08 06:13 | 8:23 | 25.9334 | 25.9486 | 28.1964 | 34.8611 | 34.2747 | 34.0817 | 34.571 | 35.53 | 36.52 | 37.5099 | 37.0243 | 38.2224 | 34.3003 | 34.312 | 33.9909 | 35.1221 | 34.7469 | 35.2978 | 35.9458 | 36.377 | 15.5617 | 15.1197 | 92.4719 | 32.458 | 32.715 | 34.7057 | 32.8764 | 32.78 | 33.1779 | 34.4469 | 34.1084 | 33.9253 | 37.1103 | 36.1456 | 33.1927 | 34.3537 | 36.1333 | 36.4665 | 37.2008 | 36.1624 | 32.8736 | 32.2215 | 34.0178 | 34.3661 | 32.3413 | 34.3804 | 34.3129 | 34.2737 | 34.3835 | 34.3854 | 34.271 | 33.8277 | 34.3758 | 36.1255 | 34.8439 | 36.5685 | 36.4898 | 33.1361 | 92.1296 | 92.2568 | 92.4733
2022-09-08 06:13 | 8:23 | 26.4145 | 26.6402 | 28.6035 | 35.0592 | 34.2582 | 34.0722 | 34.5871 | 35.5481 | 36.5243 | 37.5298 | 37.0201 | 38.2329 | 34.2999 | 34.3025 | 34.0037 | 35.1232 | 34.7412 | 35.3006 | 35.9311 | 36.3717 | 16.9183 | 16.5278 | 92.5096 | 32.4298 | 32.7182 | 34.7034 | 32.8817 | 32.7919 | 33.1809 | 34.454 | 34.0697 | 33.9122 | 37.1145 | 36.1173 | 33.1893 | 34.3501 | 36.1493 | 36.4527 | 37.1945 | 36.1357 | 32.8549 | 32.2244 | 33.9914 | 34.3753 | 32.3312 | 34.3854 | 34.3319 | 34.2621 | 34.394 | 34.3899 | 34.2752 | 33.8225 | 34.3835 | 36.129 | 34.8407 | 36.5699 | 36.4915 | 33.1235 | 92.2418 | 92.3111 | 92.429
2022-09-08 06:14 | 8:24 | 26.8831 | 27.2668 | 28.9552 | 35.0463 | 34.2571 | 34.0929 | 34.5913 | 35.5316 | 36.5368 | 37.5265 | 37.028 | 38.2372 | 34.2937 | 34.3123 | 33.9895 | 35.1244 | 34.7499 | 35.3033 | 35.9509 | 36.3713 | 18.4016 | 18.0366 | 92.5479 | 32.7029 | 32.7251 | 34.7026 | 32.8583 | 32.7769 | 33.2 | 34.456 | 34.1015 | 33.8913 | 37.1213 | 36.1069 | 33.1823 | 34.3656 | 36.1456 | 36.4707 | 37.1859 | 36.1422 | 32.8533 | 32.2097 | 34.0201 | 34.3701 | 32.3209 | 34.387 | 34.2932 | 34.2724 | 34.3846 | 34.4002 | 34.3047 | 33.8476 | 34.394 | 36.1205 | 34.8543 | 36.5821 | 36.4859 | 33.144 | 92.2788 | 92.4303 | 92.4914
2022-09-08 06:14 | 8:24 | 27.2526 | 27.7647 | 29.1954 | 35.1439 | 34.2629 | 34.1032 | 34.5994 | 35.537 | 36.5487 | 37.5196 | 37.0192 | 38.2067 | 34.299 | 34.2951 | 33.999 | 35.1321 | 34.7512 | 35.3016 | 35.9751 | 36.3761 | 19.813 | 19.4732 | 92.632 | 32.8875 | 32.7231 | 34.7061 | 32.8561 | 32.7754 | 33.1922 | 34.4493 | 34.087 | 33.916 | 37.1027 | 36.1397 | 33.1878 | 34.3521 | 36.1173 | 36.4537 | 37.2014 | 36.1333 | 32.8508 | 32.209 | 34.0143 | 34.3757 | 32.3323 | 34.3774 | 34.3274 | 34.27 | 34.3948 | 34.398 | 34.2929 | 33.8291 | 34.3846 | 36.1458 | 34.8455 | 36.5922 | 36.5015 | 33.1641 | 92.4027 | 92.521 | 92.6727
2022-09-08 06:14 | 8:24 | 27.5658 | 28.1754 | 29.3916 | 35.1401 | 34.2689 | 34.0921 | 34.5813 | 35.56 | 36.5216 | 37.5172 | 37.0256 | 38.226 | 34.2969 | 34.3191 | 34.0048 | 35.1296 | 34.7598 | 35.3172 | 35.9707 | 36.3858 | 21.1044 | 20.823 | 92.7103 | 32.9156 | 32.7147 | 34.6957 | 32.8736 | 32.7793 | 33.1927 | 34.4405 | 34.0769 | 33.9179 | 37.0898 | 36.1139 | 33.2036 | 34.3665 | 36.1069 | 36.458 | 37.1947 | 36.1493 | 32.846 | 32.2177 | 34.0326 | 34.3678 | 32.3202 | 34.3795 | 34.3211 | 34.2821 | 34.3811 | 34.3715 | 34.2865 | 33.8515 | 34.3948 | 36.1302 | 34.8307 | 36.5796 | 36.4883 | 33.1305 | 92.4963 | 92.6192 | 92.7539
2022-09-08 06:14 | 8:24 | 27.8788 | 28.5603 | 29.6359 | 35.203 | 34.2512 | 34.1066 | 34.6029 | 35.5509 | 36.5251 | 37.5265 | 37.0236 | 38.2418 | 34.3258 | 34.326 | 33.9897 | 35.1363 | 34.7383 | 35.3094 | 35.9785 | 36.3759 | 22.3401 | 22.0315 | 92.8178 | 33.1212 | 32.7064 | 34.695 | 32.8549 | 32.7698 | 33.1893 | 34.4457 | 34.0986 | 33.8903 | 37.1125 | 36.1075 | 33.1955 | 34.3496 | 36.1397 | 36.4706 | 37.2019 | 36.1456 | 32.8387 | 32.2185 | 34.0281 | 34.3732 | 32.3075 | 34.372 | 34.2981 | 34.2861 | 34.3827 | 34.3947 | 34.2938 | 33.8428 | 34.3811 | 36.1526 | 34.8377 | 36.5903 | 36.4894 | 33.143 | 92.5967 | 92.7862 | 92.8803
2022-09-08 06:14 | 8:24 | 28.1533 | 28.8974 | 29.7978 | 35.2096 | 34.28 | 34.1087 | 34.5945 | 35.5529 | 36.5276 | 37.5282 | 37.0156 | 38.2189 | 34.3029 | 34.3135 | 33.9886 | 35.1363 | 34.7367 | 35.2978 | 35.98 | 36.3834 | 23.4402 | 23.164 | 92.839 | 33.1602 | 32.7188 | 34.6898 | 32.8533 | 32.7821 | 33.1823 | 34.4511 | 34.0887 | 33.9004 | 37.1053 | 36.1121 | 33.1827 | 34.3449 | 36.1139 | 36.4581 | 37.1892 | 36.1173 | 32.8443 | 32.2038 | 34.023 | 34.3669 | 32.3053 | 34.3821 | 34.3031 | 34.2656 | 34.3788 | 34.4099 | 34.2823 | 33.8299 | 34.3827 | 36.1472 | 34.8363 | 36.5587 | 36.4996 | 33.1498 | 92.6764 | 92.8505 | 92.8537
2022-09-08 06:14 | 8:24 | 28.3862 | 29.1339 | 29.9649 | 35.282 | 34.251 | 34.1091 | 34.6038 | 35.5627 | 36.5243 | 37.5275 | 37.021 | 38.223 | 34.3067 | 34.3122 | 34.0169 | 35.1246 | 34.7526 | 35.3143 | 35.9879 | 36.3946 | 24.3891 | 24.0776 | 92.8625 | 33.1171 | 32.6988 | 34.6905 | 32.8508 | 32.7911 | 33.1878 | 34.443 | 34.0969 | 33.8969 | 37.0801 | 36.0879 | 33.1915 | 34.3424 | 36.1075 | 36.4653 | 37.1888 | 36.1069 | 32.834 | 32.2022 | 34.0236 | 34.3753 | 32.3013 | 34.3728 | 34.3331 | 34.2876 | 34.3685 | 34.3943 | 34.2969 | 33.8319 | 34.3788 | 36.1284 | 34.8223 | 36.5738 | 36.4899 | 33.1493 | 92.784 | 93.001 | 92.9226
2022-09-08 06:15 | 8:24 | 28.6249 | 29.3808 | 30.1485 | 35.3836 | 34.2677 | 34.113 | 34.5915 | 35.5558 | 36.519 | 37.5289 | 37.0166 | 38.2429 | 34.2895 | 34.3412 | 33.9906 | 35.1205 | 34.7249 | 35.3212 | 35.9892 | 36.3933 | 25.254 | 24.9434 | 92.9887 | 33.0348 | 32.7238 | 34.6702 | 32.846 | 32.7888 | 33.2036 | 34.4445 | 34.0842 | 33.885 | 37.0953 | 36.1038 | 33.1818 | 34.3589 | 36.1121 | 36.4798 | 37.1968 | 36.1397 | 32.8374 | 32.1944 | 34.037 | 34.3881 | 32.3098 | 34.3738 | 34.3046 | 34.2844 | 34.3588 | 34.3855 | 34.2948 | 33.8155 | 34.3685 | 36.128 | 34.8422 | 36.57 | 36.4857 | 33.1636 | 92.9611 | 93.1367 | 93.08
2022-09-08 06:15 | 8:25 | 28.804 | 29.5833 | 30.3072 | 35.428 | 34.2712 | 34.1187 | 34.6198 | 35.5558 | 36.528 | 37.5324 | 37.0189 | 38.224 | 34.3012 | 34.3055 | 33.9895 | 35.1191 | 34.7494 | 35.3374 | 35.9973 | 36.3803 | 25.963 | 25.6384 | 93.0839 | 33.2951 | 32.7026 | 34.6805 | 32.8387 | 32.8081 | 33.1955 | 34.4659 | 34.079 | 33.8764 | 37.105 | 36.1045 | 33.1821 | 34.3391 | 36.0879 | 36.4584 | 37.1908 | 36.1139 | 32.8186 | 32.2048 | 34.0119 | 34.3513 | 32.3081 | 34.3427 | 34.3074 | 34.2697 | 34.3591 | 34.3752 | 34.2814 | 33.8055 | 34.3588 | 36.1455 | 34.844 | 36.5742 | 36.4948 | 33.1325 | 93.0735 | 93.2482 | 93.2027
2022-09-08 06:15 | 8:25 | 29.4802 | 24.5903 | 30.084 | 35.4413 | 34.2596 | 34.0968 | 34.5914 | 35.5555 | 36.5107 | 37.5466 | 36.9901 | 38.206 | 34.3086 | 34.3285 | 34.0035 | 35.1278 | 34.7411 | 35.3246 | 36.0172 | 36.3638 | 26.9555 | 22.1524 | 93.1335 | 33.356 | 32.7163 | 34.6835 | 32.8443 | 32.7989 | 33.1827 | 34.4553 | 34.0826 | 33.8783 | 37.1041 | 36.0929 | 33.1993 | 34.3377 | 36.1038 | 36.4407 | 37.1896 | 36.1075 | 32.8369 | 32.2007 | 34.0381 | 34.3748 | 32.3134 | 34.3797 | 34.31 | 34.2787 | 34.3635 | 34.391 | 34.2944 | 33.8288 | 34.3591 | 36.1461 | 34.8296 | 36.5675 | 36.4829 | 33.137 | 93.183 | 93.291 | 93.296
2022-09-08 06:15 | 8:25 | 29.4644 | 25.5757 | 29.3277 | 35.4114 | 34.265 | 34.1085 | 34.6028 | 35.5593 | 36.5413 | 37.5301 | 36.9882 | 38.2141 | 34.3017 | 34.3392 | 33.997 | 35.1381 | 34.7424 | 35.3313 | 36.0092 | 36.4096 | 28.0827 | 26.1388 | 93.1493 | 33.3372 | 32.7153 | 34.682 | 32.834 | 32.8053 | 33.1915 | 34.4492 | 34.0871 | 33.8781 | 37.101 | 36.0988 | 33.1941 | 34.3405 | 36.1045 | 36.4608 | 37.1925 | 36.1121 | 32.8452 | 32.1929 | 34.011 | 34.3768 | 32.3299 | 34.3911 | 34.3083 | 34.2784 | 34.3685 | 34.3965 | 34.2867 | 33.8146 | 34.3635 | 36.123 | 34.8278 | 36.5845 | 36.4943 | 33.146 | 93.2252 | 93.3046 | 93.32
2022-09-08 06:15 | 8:25 | 30.3575 | 27.3291 | 29.9063 | 35.4997 | 34.2678 | 34.1156 | 34.6034 | 35.5632 | 36.5279 | 37.5424 | 36.9996 | 38.215 | 34.2989 | 34.32 | 33.9903 | 35.1205 | 34.7223 | 35.3383 | 36.0112 | 36.3794 | 30.1116 | 29.1936 | 93.0833 | 33.3938 | 32.7152 | 34.6878 | 32.8374 | 32.7991 | 33.1818 | 34.4488 | 34.0844 | 33.8802 | 37.105 | 36.0883 | 33.1932 | 34.3586 | 36.0929 | 36.4614 | 37.1917 | 36.0879 | 32.8198 | 32.1826 | 34.0299 | 34.3502 | 32.3174 | 34.3755 | 34.3052 | 34.2751 | 34.3706 | 34.4021 | 34.2902 | 33.8169 | 34.3685 | 36.1219 | 34.828 | 36.5857 | 36.4888 | 33.1601 | 93.2698 | 93.3341 | 93.3097
2022-09-08 06:15 | 8:25 | 31.2776 | 28.826 | 30.3869 | 35.5046 | 34.2611 | 34.1112 | 34.6165 | 35.5525 | 36.5314 | 37.5432 | 37.0087 | 38.2227 | 34.3104 | 34.3113 | 33.9843 | 35.1185 | 34.7356 | 35.331 | 36.0237 | 36.4079 | 31.3484 | 29.9539 | 93.1081 | 33.5045 | 32.7151 | 34.6736 | 32.8186 | 32.8094 | 33.1821 | 34.4489 | 34.077 | 33.8897 | 37.0885 | 36.1025 | 33.1783 | 34.3452 | 36.0988 | 36.4524 | 37.1909 | 36.1038 | 32.8396 | 32.1894 | 34.0157 | 34.3561 | 32.3108 | 34.382 | 34.3101 | 34.2755 | 34.341 | 34.3889 | 34.3059 | 33.8192 | 34.3706 | 36.1182 | 34.8327 | 36.5848 | 36.4855 | 33.1347 | 93.3159 | 93.3102 | 93.3237
2022-09-08 06:16 | 8:26 | 31.9074 | 29.309 | 30.7016 | 35.565 | 34.2842 | 34.1136 | 34.6222 | 35.5812 | 36.5151 | 37.5429 | 37.01 | 38.1989 | 34.3215 | 34.3247 | 34.0009 | 35.109 | 34.7257 | 35.3455 | 36.026 | 36.385 | 32.4257 | 30.2744 | 93.2223 | 33.5015 | 32.7346 | 34.6757 | 32.8369 | 32.807 | 33.1993 | 34.4577 | 34.0741 | 33.8815 | 37.0922 | 36.1025 | 33.1866 | 34.3532 | 36.0883 | 36.4554 | 37.1911 | 36.1045 | 32.8242 | 32.2028 | 34.0246 | 34.3631 | 32.3252 | 34.3912 | 34.2874 | 34.2747 | 34.3583 | 34.378 | 34.2955 | 33.8003 | 34.341 | 36.1365 | 34.8372 | 36.5782 | 36.4907 | 33.1462 | 93.4166 | 93.4141 | 93.4039
2022-09-08 06:16 | 8:26 | 32.5348 | 29.6628 | 30.9493 | 35.6381 | 34.2468 | 34.1015 | 34.61 | 35.5582 | 36.5353 | 37.5434 | 37.0053 | 38.2011 | 34.3095 | 34.3203 | 33.9962 | 35.1089 | 34.7194 | 35.3332 | 36.0281 | 36.3908 | 33.1438 | 30.4917 | 93.3511 | 33.6083 | 32.7241 | 34.668 | 32.8452 | 32.8213 | 33.1941 | 34.4546 | 34.0741 | 33.8848 | 37.0857 | 36.0939 | 33.1755 | 34.3426 | 36.1025 | 36.4602 | 37.1952 | 36.0929 | 32.8241 | 32.1891 | 34.0258 | 34.358 | 32.3351 | 34.3907 | 34.2824 | 34.277 | 34.3644 | 34.3996 | 34.306 | 33.8036 | 34.3583 | 36.1436 | 34.8207 | 36.5901 | 36.4859 | 33.1394 | 93.5903 | 93.5369 | 93.5298
2022-09-08 06:16 | 8:26 | 32.9662 | 29.9429 | 31.1259 | 35.7034 | 34.2913 | 34.1086 | 34.6248 | 35.5653 | 36.5207 | 37.5607 | 36.9923 | 38.2187 | 34.3237 | 34.3395 | 33.9984 | 35.1186 | 34.7221 | 35.3233 | 36.0307 | 36.3914 | 33.5537 | 30.619 | 93.3483 | 33.7863 | 32.7094 | 34.6586 | 32.8198 | 32.8139 | 33.1932 | 34.4661 | 34.0748 | 33.8788 | 37.0981 | 36.0615 | 33.1816 | 34.3426 | 36.1025 | 36.4617 | 37.2067 | 36.0988 | 32.8194 | 32.1886 | 34.0399 | 34.3573 | 32.3507 | 34.3867 | 34.2803 | 34.2969 | 34.3421 | 34.3981 | 34.3017 | 33.8029 | 34.3644 | 36.1331 | 34.8293 | 36.5637 | 36.4814 | 33.1356 | 93.7119 | 93.6541 | 93.6131
2022-09-08 06:16 | 8:26 | 33.047 | 30.1701 | 31.2511 | 35.7525 | 34.2656 | 34.1039 | 34.6267 | 35.5617 | 36.5292 | 37.5712 | 37.0147 | 38.2123 | 34.3314 | 34.3274 | 34.0037 | 35.1308 | 34.7274 | 35.3393 | 36.046 | 36.4122 | 33.664 | 30.6957 | 93.442 | 33.7643 | 32.7186 | 34.6632 | 32.8396 | 32.8143 | 33.1783 | 34.446 | 34.0788 | 33.8775 | 37.0752 | 36.0939 | 33.1936 | 34.3515 | 36.0939 | 36.4681 | 37.1989 | 36.0883 | 32.823 | 32.1884 | 34.0373 | 34.3472 | 32.3437 | 34.3711 | 34.2928 | 34.2686 | 34.3474 | 34.3971 | 34.3127 | 33.8072 | 34.3421 | 36.1403 | 34.8179 | 36.5726 | 36.4896 | 33.1483 | 93.8211 | 93.894 | 93.5832
2022-09-08 06:16 | 8:26 | 33.0448 | 30.3434 | 31.3136 | 35.939 | 34.2704 | 34.1012 | 34.6222 | 35.5676 | 36.5346 | 37.5541 | 37.0044 | 38.2234 | 34.3381 | 34.3328 | 34.0109 | 35.1335 | 34.7289 | 35.3421 | 36.0252 | 36.3983 | 33.6452 | 30.7305 | 93.4041 | 33.786 | 32.7026 | 34.6633 | 32.8242 | 32.8292 | 33.1866 | 34.4415 | 34.0592 | 33.8644 | 37.0895 | 36.0936 | 33.1902 | 34.3504 | 36.0615 | 36.4631 | 37.1971 | 36.1025 | 32.8174 | 32.1806 | 34.0508 | 34.3547 | 32.3501 | 34.3948 | 34.3179 | 34.2753 | 34.3342 | 34.3947 | 34.2973 | 33.8049 | 34.3474 | 36.1293 | 34.817 | 36.5861 | 36.492 | 33.1564 | 93.9568 | 94.0023 | 93.7317
2022-09-08 06:16 | 8:26 | 32.8417 | 30.4939 | 31.3987 | 35.8631 | 34.2802 | 34.1033 | 34.6119 | 35.5631 | 36.5169 | 37.5609 | 37.002 | 38.208 | 34.3392 | 34.3128 | 33.9888 | 35.1292 | 34.7238 | 35.3516 | 36.0498 | 36.3773 | 33.5887 | 30.7779 | 93.5385 | 33.8972 | 32.7215 | 34.6472 | 32.8241 | 32.821 | 33.1755 | 34.4495 | 34.0762 | 33.8769 | 37.081 | 36.0939 | 33.1909 | 34.3512 | 36.0939 | 36.4372 | 37.1861 | 36.1025 | 32.8041 | 32.1814 | 34.0553 | 34.366 | 32.3462 | 34.3971 | 34.285 | 34.3039 | 34.3607 | 34.3805 | 34.2945 | 33.8038 | 34.3342 | 36.1133 | 34.8269 | 36.5774 | 36.507 | 33.1451 | 94.0998 | 94.2188 | 93.842
2022-09-08 06:17 | 8:26 | 32.5916 | 30.6254 | 31.4716 | 35.848 | 34.2751 | 34.1081 | 34.6424 | 35.5573 | 36.5294 | 37.5678 | 36.9859 | 38.2178 | 34.3358 | 34.3345 | 33.9952 | 35.1313 | 34.7036 | 35.3518 | 36.0547 | 36.3809 | 33.4983 | 30.8013 | 93.6276 | 34.0309 | 32.7295 | 34.665 | 32.8194 | 32.8041 | 33.1816 | 34.4481 | 34.0688 | 33.8773 | 37.0921 | 36.0943 | 33.194 | 34.3447 | 36.0936 | 36.4528 | 37.2059 | 36.0939 | 32.812 | 32.1975 | 34.0534 | 34.3572 | 32.3479 | 34.3993 | 34.2998 | 34.3025 | 34.3311 | 34.374 | 34.3198 | 33.7921 | 34.3607 | 36.1208 | 34.8203 | 36.5729 | 36.4885 | 33.1733 | 94.1209 | 94.3459 | 93.7682
2022-09-08 06:17 | 8:27 | 32.2782 | 30.7447 | 31.5488 | 35.8905 | 34.2851 | 34.1002 | 34.6136 | 35.5516 | 36.5255 | 37.5882 | 37.001 | 38.2063 | 34.3331 | 34.3254 | 33.9787 | 35.1163 | 34.7207 | 35.3168 | 36.0519 | 36.3745 | 33.3842 | 30.7924 | 93.5028 | 34.0404 | 32.7239 | 34.6568 | 32.823 | 32.8332 | 33.1936 | 34.4529 | 34.0693 | 33.8762 | 37.0864 | 36.1052 | 33.1847 | 34.3624 | 36.0939 | 36.4474 | 37.1839 | 36.0615 | 32.8042 | 32.162 | 34.0472 | 34.3368 | 32.3623 | 34.3896 | 34.2824 | 34.2992 | 34.3288 | 34.3944 | 34.2975 | 33.807 | 34.3311 | 36.1123 | 34.8168 | 36.565 | 36.4739 | 33.1424 | 94.3029 | 94.4712 | 93.8782
2022-09-08 06:17 | 8:27 | 31.9944 | 30.8102 | 31.5997 | 35.8457 | 34.2754 | 34.0969 | 34.6117 | 35.5585 | 36.5139 | 37.5489 | 36.9927 | 38.2102 | 34.3338 | 34.3324 | 33.9856 | 35.1184 | 34.7021 | 35.3344 | 36.0551 | 36.3909 | 33.3398 | 30.8108 | 93.7947 | 34.0339 | 32.7196 | 34.6533 | 32.8174 | 32.812 | 33.1902 | 34.4504 | 34.0789 | 33.8603 | 37.0817 | 36.1095 | 33.1725 | 34.3472 | 36.0943 | 36.4368 | 37.1934 | 36.0939 | 32.8006 | 32.1922 | 34.055 | 34.3415 | 32.3493 | 34.4007 | 34.2983 | 34.2896 | 34.345 | 34.3735 | 34.311 | 33.8009 | 34.3288 | 36.1111 | 34.8132 | 36.5632 | 36.4855 | 33.1382 | 94.4914 | 94.6198 | 94.0281
2022-09-08 06:17 | 8:27 | 32.012 | 30.9112 | 31.6735 | 35.9239 | 34.2948 | 34.1126 | 34.6083 | 35.5681 | 36.5259 | 37.5831 | 37.0149 | 38.2157 | 34.3394 | 34.3556 | 33.993 | 35.1103 | 34.7084 | 35.3343 | 36.0585 | 36.3891 | 33.3788 | 30.7911 | 94.0577 | 33.9965 | 32.7548 | 34.6405 | 32.8041 | 32.813 | 33.1909 | 34.44 | 34.0732 | 33.8702 | 37.0622 | 36.0918 | 33.1955 | 34.3363 | 36.1052 | 36.4603 | 37.1918 | 36.0936 | 32.815 | 32.2165 | 34.0601 | 34.3405 | 32.3629 | 34.4009 | 34.2804 | 34.3013 | 34.3416 | 34.3824 | 34.2995 | 33.7932 | 34.345 | 36.129 | 34.838 | 36.5823 | 36.4899 | 33.1323 | 94.7185 | 94.7403 | 94.2428
2022-09-08 06:17 | 8:27 | 32.6074 | 30.9585 | 31.7097 | 35.9662 | 34.2815 | 34.1287 | 34.6189 | 35.562 | 36.5269 | 37.5583 | 36.9904 | 38.2118 | 34.3469 | 34.3549 | 33.9841 | 35.1311 | 34.7299 | 35.3447 | 36.0719 | 36.3798 | 33.456 | 30.8109 | 93.9776 | 34.1327 | 32.7415 | 34.6314 | 32.812 | 32.8238 | 33.194 | 34.4745 | 34.0595 | 33.871 | 37.1084 | 36.1014 | 33.1822 | 34.3434 | 36.1095 | 36.4432 | 37.1861 | 36.0939 | 32.8052 | 32.2163 | 34.0579 | 34.3363 | 32.3769 | 34.4088 | 34.303 | 34.2854 | 34.3332 | 34.3984 | 34.3152 | 33.7982 | 34.3416 | 36.1061 | 34.8139 | 36.5815 | 36.4927 | 33.1476 | 94.8555 | 94.8342 | 94.2382
2022-09-08 06:17 | 8:27 | 33.7761 | 31.0165 | 31.8168 | 35.9084 | 34.2925 | 34.1188 | 34.5921 | 35.5594 | 36.4955 | 37.5626 | 37.0009 | 38.1997 | 34.3445 | 34.3554 | 33.9915 | 35.1071 | 34.7026 | 35.3463 | 36.063 | 36.3825 | 33.5612 | 30.8152 | 93.9303 | 34.1084 | 32.7266 | 34.6348 | 32.8042 | 32.8231 | 33.1847 | 34.4586 | 34.0796 | 33.8646 | 37.0884 | 36.0567 | 33.1775 | 34.3372 | 36.0918 | 36.4415 | 37.1932 | 36.0943 | 32.8209 | 32.1829 | 34.0526 | 34.3311 | 32.3782 | 34.4076 | 34.2928 | 34.2937 | 34.3311 | 34.3694 | 34.312 | 33.7803 | 34.3332 | 36.1203 | 34.8207 | 36.5675 | 36.4883 | 33.1384 | 94.9033 | 94.9404 | 94.2751
2022-09-08 06:18 | 8:28 | 34.0578 | 31.0887 | 31.9288 | 35.9994 | 34.2835 | 34.1189 | 34.6214 | 35.5629 | 36.5119 | 37.5653 | 36.9979 | 38.195 | 34.3536 | 34.3584 | 33.9932 | 35.1084 | 34.718 | 35.3513 | 36.0722 | 36.4003 | 33.7305 | 30.8603 | 94.0747 | 34.2098 | 32.7004 | 34.6561 | 32.8006 | 32.8286 | 33.1725 | 34.4562 | 34.0714 | 33.8664 | 37.0739 | 36.0707 | 33.1988 | 34.3364 | 36.1014 | 36.4478 | 37.188 | 36.1052 | 32.8152 | 32.2098 | 34.0655 | 34.3613 | 32.3935 | 34.4104 | 34.2835 | 34.3034 | 34.3335 | 34.3869 | 34.3025 | 33.7973 | 34.3311 | 36.1269 | 34.8252 | 36.574 | 36.5011 | 33.1365 | 95.0226 | 95.0179 | 94.3743
2022-09-08 06:18 | 8:28 | 34.1625 | 31.1529 | 32.0941 | 36.0304 | 34.2959 | 34.1195 | 34.6287 | 35.5407 | 36.5126 | 37.5756 | 37.0068 | 38.2129 | 34.3582 | 34.3529 | 33.996 | 35.1236 | 34.7287 | 35.3765 | 36.0414 | 36.3792 | 33.6633 | 30.883 | 93.9112 | 34.1784 | 32.7258 | 34.6477 | 32.815 | 32.8245 | 33.1955 | 34.4524 | 34.0851 | 33.8614 | 37.0806 | 36.0745 | 33.1726 | 34.3311 | 36.0567 | 36.4414 | 37.1959 | 36.1095 | 32.801 | 32.2163 | 34.0664 | 34.3539 | 32.4021 | 34.3919 | 34.272 | 34.3116 | 34.3579 | 34.3765 | 34.3123 | 33.8136 | 34.3335 | 36.1209 | 34.8126 | 36.5869 | 36.4867 | 33.1399 | 95.1086 | 95.0891 | 94.3879
2022-09-08 06:18 | 8:28 | 34.1154 | 31.2097 | 32.2227 | 36.0721 | 34.28 | 34.0962 | 34.6165 | 35.5585 | 36.5226 | 37.5809 | 37.0181 | 38.1923 | 34.3729 | 34.3337 | 33.99 | 35.1197 | 34.7157 | 35.3444 | 36.0614 | 36.3533 | 33.6373 | 30.9244 | 94.2178 | 34.1564 | 32.7189 | 34.641 | 32.8052 | 32.8188 | 33.1822 | 34.4504 | 34.0662 | 33.8676 | 37.0715 | 36.0988 | 33.1852 | 34.3463 | 36.0707 | 36.4515 | 37.201 | 36.0918 | 32.8021 | 32.2161 | 34.073 | 34.3591 | 32.429 | 34.415 | 34.3029 | 34.3085 | 34.3336 | 34.3905 | 34.2951 | 33.8024 | 34.3579 | 36.127 | 34.824 | 36.5691 | 36.4946 | 33.1336 | 95.1221 | 95.1158 | 94.5025
2022-09-08 06:18 | 8:28 | 34.1064 | 31.2554 | 32.3277 | 36.1345 | 34.271 | 34.1065 | 34.6289 | 35.5628 | 36.5132 | 37.5739 | 36.997 | 38.2026 | 34.3713 | 34.3691 | 33.9899 | 35.0994 | 34.7112 | 35.3437 | 36.0525 | 36.3816 | 33.7017 | 30.9553 | 94.153 | 34.1698 | 32.7126 | 34.6447 | 32.8209 | 32.8228 | 33.1775 | 34.4605 | 34.065 | 33.8611 | 37.0652 | 36.0643 | 33.1995 | 34.3378 | 36.0745 | 36.458 | 37.1908 | 36.1014 | 32.8163 | 32.2197 | 34.0694 | 34.3627 | 32.4157 | 34.4018 | 34.2874 | 34.3157 | 34.344 | 34.3809 | 34.3191 | 33.8058 | 34.3336 | 36.1272 | 34.8061 | 36.5754 | 36.4823 | 33.1354 | 94.9569 | 95.0501 | 94.3041
2022-09-08 06:18 | 8:28 | 34.2808 | 31.2705 | 32.4062 | 36.0622 | 34.2752 | 34.1125 | 34.6248 | 35.5639 | 36.5022 | 37.5633 | 36.994 | 38.1913 | 34.3734 | 34.3538 | 33.9618 | 35.1165 | 34.7022 | 35.3429 | 36.0552 | 36.3711 | 33.9145 | 30.9952 | 93.9993 | 34.3043 | 32.7058 | 34.6361 | 32.8152 | 32.8175 | 33.1988 | 34.4413 | 34.0639 | 33.861 | 37.0748 | 36.0902 | 33.1676 | 34.3296 | 36.0988 | 36.4408 | 37.1988 | 36.0567 | 32.7911 | 32.1825 | 34.0539 | 34.3204 | 32.4028 | 34.3877 | 34.2985 | 34.3132 | 34.3444 | 34.3786 | 34.326 | 33.7917 | 34.344 | 36.0768 | 34.8147 | 36.5695 | 36.476 | 33.1275 | 94.6693 | 94.8481 | 94.1495
2022-09-08 06:18 | 8:28 | 34.3069 | 31.237 | 32.4708 | 36.1347 | 34.3047 | 34.1063 | 34.5387 | 35.5506 | 36.4909 | 37.5701 | 36.9831 | 38.1965 | 34.3648 | 34.3608 | 33.9797 | 35.1128 | 34.6977 | 35.3398 | 36.0626 | 36.3582 | 33.9655 | 30.9972 | 93.8491 | 34.4238 | 32.708 | 34.6342 | 32.801 | 32.8334 | 33.1726 | 34.4554 | 34.0572 | 33.8661 | 37.0812 | 36.1076 | 33.1737 | 34.3351 | 36.0643 | 36.4302 | 37.1683 | 36.0707 | 32.7898 | 32.2052 | 34.0578 | 34.3371 | 32.3997 | 34.4101 | 34.302 | 34.311 | 34.3359 | 34.3724 | 34.3135 | 33.7766 | 34.3444 | 36.1005 | 34.8328 | 36.5574 | 36.4854 | 33.1189 | 94.3947 | 94.5975 | 94.007
2022-09-08 06:19 | 8:29 | 34.3814 | 31.3504 | 32.5518 | 36.1099 | 34.2929 | 34.1111 | 34.6083 | 35.5636 | 36.5003 | 37.5519 | 36.995 | 38.2082 | 34.3543 | 34.3752 | 33.9859 | 35.1127 | 34.7083 | 35.3415 | 36.0768 | 36.3739 | 33.8659 | 31.0505 | 93.7377 | 34.3381 | 32.705 | 34.6426 | 32.8021 | 32.8162 | 33.1852 | 34.4517 | 34.0559 | 33.8597 | 37.0538 | 36.0954 | 33.1754 | 34.3254 | 36.0902 | 36.4345 | 37.1885 | 36.0745 | 32.78 | 32.2217 | 34.0714 | 34.3472 | 32.4353 | 34.4087 | 34.3034 | 34.3103 | 34.3496 | 34.3617 | 34.3122 | 33.7878 | 34.3359 | 36.1082 | 34.8044 | 36.5686 | 36.4928 | 33.1088 | 94.1911 | 94.3865 | 93.8569
2022-09-08 06:19 | 8:29 | 34.4269 | 31.3855 | 32.6187 | 36.1484 | 34.2865 | 34.124 | 34.61 | 35.5404 | 36.5124 | 37.576 | 36.9878 | 38.2228 | 34.3762 | 34.3791 | 33.9776 | 35.1124 | 34.7072 | 35.3338 | 36.0739 | 36.3617 | 33.9168 | 31.076 | 93.5139 | 34.3667 | 32.7141 | 34.6342 | 32.8163 | 32.829 | 33.1995 | 34.4499 | 34.0579 | 33.8731 | 37.0689 | 36.091 | 33.1774 | 34.3455 | 36.1076 | 36.444 | 37.1862 | 36.0988 | 32.7973 | 32.2248 | 34.0917 | 34.337 | 32.4511 | 34.4137 | 34.3089 | 34.3166 | 34.349 | 34.3917 | 34.3412 | 33.8063 | 34.3496 | 36.1108 | 34.8039 | 36.5584 | 36.4898 | 33.1009 | 94.0472 | 94.2119 | 93.7423
2022-09-08 06:19 | 8:29 | 34.5249 | 31.4222 | 32.6903 | 36.1624 | 34.2938 | 34.1206 | 34.6123 | 35.5405 | 36.5134 | 37.5524 | 36.9742 | 38.1953 | 34.3655 | 34.3809 | 33.9843 | 35.1171 | 34.7078 | 35.3427 | 36.0782 | 36.3886 | 34.0024 | 31.0749 | 93.4514 | 34.3327 | 32.6906 | 34.6321 | 32.7911 | 32.8342 | 33.1676 | 34.4468 | 34.0636 | 33.8572 | 37.0709 | 36.0947 | 33.1598 | 34.3373 | 36.0954 | 36.4414 | 37.1831 | 36.0643 | 32.8168 | 32.2071 | 34.0643 | 34.3383 | 32.4342 | 34.4213 | 34.3035 | 34.3028 | 34.3373 | 34.3685 | 34.3055 | 33.7927 | 34.349 | 36.0839 | 34.8079 | 36.5512 | 36.4752 | 33.0841 | 93.8809 | 94.0261 | 93.644
2022-09-08 06:19 | 8:29 | 34.576 | 31.4435 | 32.7474 | 36.1643 | 34.2823 | 34.1246 | 34.601 | 35.551 | 36.5022 | 37.5704 | 36.9846 | 38.2072 | 34.3598 | 34.3785 | 33.9631 | 35.1123 | 34.7037 | 35.3409 | 36.0708 | 36.3663 | 34.0936 | 31.048 | 93.381 | 34.4354 | 32.706 | 34.6382 | 32.7898 | 32.8136 | 33.1737 | 34.4462 | 34.0788 | 33.8519 | 37.0615 | 36.109 | 33.1713 | 34.3358 | 36.091 | 36.4455 | 37.1922 | 36.0902 | 32.7967 | 32.2311 | 34.0898 | 34.3391 | 32.4855 | 34.4203 | 34.3069 | 34.3171 | 34.3445 | 34.3758 | 34.3285 | 33.8021 | 34.3373 | 36.1034 | 34.8061 | 36.5591 | 36.5002 | 33.1125 | 93.8423 | 93.9473 | 93.6223
2022-09-08 06:19 | 8:29 | 34.6974 | 31.4936 | 32.8364 | 36.2668 | 34.2969 | 34.1063 | 34.6154 | 35.564 | 36.505 | 37.5703 | 37.0067 | 38.1894 | 34.3743 | 34.3936 | 33.9699 | 35.1291 | 34.6997 | 35.3467 | 36.1001 | 36.3724 | 34.2038 | 31.1267 | 93.3891 | 34.4101 | 32.7085 | 34.6368 | 32.78 | 32.8389 | 33.1754 | 34.4421 | 34.067 | 33.8561 | 37.0659 | 36.0859 | 33.1825 | 34.3328 | 36.0947 | 36.418 | 37.184 | 36.1076 | 32.8143 | 32.2273 | 34.1097 | 34.3569 | 32.4644 | 34.4138 | 34.3106 | 34.3077 | 34.315 | 34.3758 | 34.3392 | 33.8152 | 34.3445 | 36.1038 | 34.7991 | 36.5548 | 36.5062 | 33.0878 | 93.7189 | 93.9139 | 93.5349
2022-09-08 06:19 | 8:29 | 34.8209 | 31.5319 | 32.9094 | 36.3446 | 34.2948 | 34.1192 | 34.6101 | 35.5554 | 36.4971 | 37.566 | 37.0107 | 38.2043 | 34.3795 | 34.3852 | 33.9792 | 35.1098 | 34.7201 | 35.3686 | 36.0965 | 36.3603 | 34.2437 | 31.1402 | 93.3464 | 34.5006 | 32.7198 | 34.638 | 32.7973 | 32.8324 | 33.1774 | 34.4322 | 34.0642 | 33.8437 | 37.0792 | 36.0543 | 33.1852 | 34.3281 | 36.109 | 36.4283 | 37.1779 | 36.0954 | 32.8024 | 32.2382 | 34.0999 | 34.3411 | 32.4789 | 34.4019 | 34.2978 | 34.3141 | 34.341 | 34.3582 | 34.32 | 33.7949 | 34.315 | 36.0874 | 34.7973 | 36.5648 | 36.4732 | 33.0894 | 93.6622 | 93.8331 | 93.529
2022-09-08 06:20 | 8:29 | 31.8022 | 31.6502 | 32.5712 | 36.3273 | 34.2814 | 34.1393 | 34.6021 | 35.5382 | 36.4966 | 37.5645 | 37.0055 | 38.1909 | 34.3848 | 34.3935 | 33.9933 | 35.1226 | 34.7172 | 35.3537 | 36.1048 | 36.3695 | 30.686 | 30.7537 | 93.2438 | 34.4526 | 32.7115 | 34.6368 | 32.8168 | 32.8194 | 33.1598 | 34.4567 | 34.076 | 33.8607 | 37.0813 | 36.0877 | 33.1793 | 34.3308 | 36.0859 | 36.4204 | 37.1806 | 36.091 | 32.8039 | 32.2465 | 34.1179 | 34.3649 | 32.4674 | 34.4181 | 34.2906 | 34.308 | 34.3511 | 34.3744 | 34.3113 | 33.7884 | 34.341 | 36.0912 | 34.8059 | 36.5635 | 36.4886 | 33.1091 | 93.6103 | 93.715 | 93.5023
2022-09-08 06:20 | 8:30 | 30.4259 | 29.9775 | 31.8316 | 36.3044 | 34.2944 | 34.1167 | 34.6118 | 35.5671 | 36.5023 | 37.5774 | 36.9963 | 38.2053 | 34.3667 | 34.3933 | 33.9913 | 35.124 | 34.7274 | 35.3524 | 36.0797 | 36.3902 | 28.0779 | 28.9753 | 93.0539 | 34.4394 | 32.6957 | 34.6161 | 32.7967 | 32.8341 | 33.1713 | 34.4574 | 34.0543 | 33.8433 | 37.0708 | 36.074 | 33.1683 | 34.3518 | 36.0543 | 36.4514 | 37.1847 | 36.0947 | 32.8044 | 32.2173 | 34.0829 | 34.359 | 32.5029 | 34.4279 | 34.303 | 34.3024 | 34.3333 | 34.3915 | 34.3247 | 33.7927 | 34.3511 | 36.0973 | 34.8203 | 36.5547 | 36.4876 | 33.114 | 93.4766 | 93.6253 | 93.407
2022-09-08 06:20 | 8:30 | 31.1737 | 28.1625 | 31.3682 | 36.2171 | 34.2867 | 34.1248 | 34.6287 | 35.5596 | 36.52 | 37.5695 | 37.0171 | 38.2082 | 34.3972 | 34.4112 | 33.9959 | 35.1189 | 34.6962 | 35.3402 | 36.0914 | 36.3695 | 28.1915 | 27.2345 | 93.0673 | 34.4845 | 32.7221 | 34.6568 | 32.8143 | 32.8347 | 33.1825 | 34.4509 | 34.0703 | 33.8442 | 37.0782 | 36.0963 | 33.1696 | 34.35 | 36.0877 | 36.4366 | 37.178 | 36.109 | 32.8089 | 32.2391 | 34.1039 | 34.3839 | 32.5037 | 34.4259 | 34.3096 | 34.3274 | 34.3394 | 34.355 | 34.3203 | 33.7932 | 34.3333 | 36.0999 | 34.8317 | 36.5642 | 36.4867 | 33.0867 | 93.426 | 93.548 | 93.4129
2022-09-08 06:20 | 8:30 | 31.0732 | 27.168 | 30.909 | 36.1642 | 34.2902 | 34.118 | 34.6434 | 35.5564 | 36.5109 | 37.5887 | 37.0149 | 38.2047 | 34.376 | 34.4102 | 33.9826 | 35.1246 | 34.6947 | 35.3506 | 36.0852 | 36.3908 | 28.5409 | 27.0109 | 93.0937 | 34.5475 | 32.7135 | 34.6442 | 32.8024 | 32.823 | 33.1852 | 34.4578 | 34.0602 | 33.8592 | 37.0738 | 36.1051 | 33.1799 | 34.3425 | 36.074 | 36.4298 | 37.1812 | 36.0859 | 32.7974 | 32.2635 | 34.1278 | 34.379 | 32.5282 | 34.429 | 34.3166 | 34.3311 | 34.3388 | 34.3686 | 34.3395 | 33.7951 | 34.3394 | 36.1166 | 34.7989 | 36.5838 | 36.4721 | 33.1146 | 93.3568 | 93.4825 | 93.4051
2022-09-08 06:20 | 8:30 | 29.9658 | 26.8781 | 30.1399 | 36.1254 | 34.3059 | 34.1071 | 34.6468 | 35.5739 | 36.5206 | 37.5838 | 37.0112 | 38.2046 | 34.3885 | 34.3972 | 33.9877 | 35.1186 | 34.7079 | 35.3497 | 36.0785 | 36.3969 | 28.8136 | 26.8284 | 93.1187 | 34.5847 | 32.7193 | 34.6437 | 32.8039 | 32.8319 | 33.1793 | 34.4721 | 34.0781 | 33.8659 | 37.0822 | 36.0841 | 33.1772 | 34.3501 | 36.0963 | 36.4405 | 37.1863 | 36.0543 | 32.7979 | 32.2307 | 34.0852 | 34.3428 | 32.478 | 34.4305 | 34.3011 | 34.3401 | 34.326 | 34.3723 | 34.3274 | 33.7737 | 34.3388 | 36.1182 | 34.7945 | 36.5642 | 36.4845 | 33.1125 | 93.323 | 93.4887 | 93.3447
2022-09-08 06:20 | 8:30 | 24.667 | 26.638 | 28.7977 | 36.0285 | 34.2955 | 34.1166 | 34.6674 | 35.5655 | 36.519 | 37.5796 | 37.032 | 38.2235 | 34.3854 | 34.399 | 33.9781 | 35.1254 | 34.7002 | 35.3721 | 36.0819 | 36.3741 | 29.1261 | 26.7823 | 92.9406 | 34.614 | 32.7252 | 34.6624 | 32.8044 | 32.8451 | 33.1683 | 34.4616 | 34.0663 | 33.8546 | 37.0746 | 36.0939 | 33.1808 | 34.3472 | 36.1051 | 36.4396 | 37.1923 | 36.0877 | 32.8124 | 32.2614 | 34.1449 | 34.3703 | 32.5274 | 34.4485 | 34.3074 | 34.3395 | 34.3241 | 34.3692 | 34.3328 | 33.8161 | 34.326 | 36.1229 | 34.8197 | 36.5783 | 36.4851 | 33.1138 | 93.2861 | 93.459 | 93.2895
2022-09-08 06:21 | 8:31 | 23.4913 | 25.9013 | 27.8384 | 36.0276 | 34.306 | 34.1137 | 34.6351 | 35.5673 | 36.5157 | 37.5721 | 37.007 | 38.2074 | 34.3899 | 34.3997 | 34.0091 | 35.0984 | 34.7036 | 35.3735 | 36.0912 | 36.3853 | 29.3489 | 26.8394 | 93.0424 | 34.5445 | 32.7121 | 34.6407 | 32.8089 | 32.8282 | 33.1696 | 34.4476 | 34.0638 | 33.8664 | 37.074 | 36.1047 | 33.176 | 34.3462 | 36.0841 | 36.4535 | 37.1888 | 36.074 | 32.805 | 32.2695 | 34.1343 | 34.3538 | 32.5275 | 34.4344 | 34.314 | 34.3134 | 34.3041 | 34.3657 | 34.3128 | 33.7991 | 34.3241 | 36.0796 | 34.8005 | 36.5694 | 36.4697 | 33.1038 | 93.2401 | 93.4063 | 93.2616
2022-09-08 06:21 | 8:31 | 22.9604 | 25.4043 | 27.231 | 35.8959 | 34.3017 | 34.0982 | 34.6332 | 35.5531 | 36.5055 | 37.6084 | 37.0108 | 38.2123 | 34.4002 | 34.3953 | 34.0015 | 35.1096 | 34.718 | 35.3666 | 36.0972 | 36.3657 | 29.5954 | 27.11 | 92.7888 | 34.571 | 32.7007 | 34.6392 | 32.7974 | 32.8363 | 33.1799 | 34.4503 | 34.0694 | 33.8656 | 37.09 | 36.1162 | 33.1708 | 34.3427 | 36.0939 | 36.454 | 37.2064 | 36.0963 | 32.813 | 32.3079 | 34.1385 | 34.4142 | 32.5299 | 34.4402 | 34.3114 | 34.3389 | 34.323 | 34.3557 | 34.3345 | 33.8276 | 34.3041 | 36.1184 | 34.8165 | 36.569 | 36.5025 | 33.1171 | 93.0679 | 93.3789 | 93.2062
2022-09-08 06:21 | 8:31 | 22.4737 | 24.8636 | 26.7163 | 35.8903 | 34.3127 | 34.1287 | 34.6438 | 35.5599 | 36.5305 | 37.5922 | 37.0036 | 38.2122 | 34.398 | 34.3881 | 33.9911 | 35.1303 | 34.7177 | 35.3424 | 36.1097 | 36.4022 | 29.9359 | 27.4444 | 92.8581 | 34.6289 | 32.7269 | 34.6371 | 32.7979 | 32.8238 | 33.1772 | 34.4481 | 34.0892 | 33.8513 | 37.0719 | 36.1281 | 33.1691 | 34.3469 | 36.1047 | 36.4358 | 37.2082 | 36.1051 | 32.8169 | 32.2781 | 34.133 | 34.3884 | 32.5393 | 34.4501 | 34.3255 | 34.3305 | 34.3222 | 34.3825 | 34.3254 | 33.806 | 34.323 | 36.1108 | 34.8134 | 36.5647 | 36.4829 | 33.1366 | 93.0546 | 93.1248 | 93.1725
2022-09-08 06:21 | 8:31 | 22.1432 | 24.3753 | 26.28 | 35.7529 | 34.2973 | 34.1032 | 34.6441 | 35.5773 | 36.5211 | 37.5887 | 37.0223 | 38.2299 | 34.3715 | 34.3895 | 34.0024 | 35.1177 | 34.7231 | 35.3571 | 36.0636 | 36.3937 | 30.1885 | 27.8538 | 92.8718 | 34.6081 | 32.7124 | 34.6355 | 32.8124 | 32.8424 | 33.1808 | 34.4532 | 34.0754 | 33.8509 | 37.0872 | 36.1126 | 33.1945 | 34.3549 | 36.1162 | 36.4459 | 37.207 | 36.0841 | 32.8144 | 32.2641 | 34.1262 | 34.3954 | 32.5364 | 34.4605 | 34.3178 | 34.3484 | 34.3071 | 34.3747 | 34.3324 | 33.8185 | 34.3222 | 36.1127 | 34.8074 | 36.5732 | 36.4969 | 33.1053 | 92.9902 | 93.0467 | 93.092
2022-09-08 06:21 | 8:31 | 21.5459 | 23.9167 | 25.8376 | 35.7541 | 34.2945 | 34.0979 | 34.6184 | 35.5744 | 36.5111 | 37.5956 | 36.9916 | 38.2156 | 34.3947 | 34.3994 | 33.9937 | 35.1099 | 34.73 | 35.3644 | 36.0776 | 36.399 | 30.4094 | 28.3955 | 92.8446 | 34.575 | 32.7146 | 34.6406 | 32.805 | 32.8505 | 33.176 | 34.4451 | 34.0647 | 33.8559 | 37.0602 | 36.1116 | 33.1719 | 34.345 | 36.1281 | 36.4505 | 37.2117 | 36.0939 | 32.815 | 32.2953 | 34.133 | 34.3972 | 32.5581 | 34.4474 | 34.3201 | 34.3515 | 34.3169 | 34.3441 | 34.3556 | 33.818 | 34.3071 | 36.1341 | 34.8091 | 36.5796 | 36.4823 | 33.1335 | 92.9003 | 93.0303 | 93.0471
2022-09-08 06:21 | 8:31 | 21.1497 | 23.4577 | 25.5031 | 35.7481 | 34.3198 | 34.1071 | 34.6544 | 35.5645 | 36.501 | 37.5861 | 37.0129 | 38.2161 | 34.4099 | 34.4104 | 34.0021 | 35.1164 | 34.7306 | 35.355 | 36.0711 | 36.3766 | 30.6318 | 28.9545 | 92.7633 | 34.6606 | 32.7108 | 34.6455 | 32.813 | 32.8341 | 33.1708 | 34.4557 | 34.0665 | 33.8549 | 37.0776 | 36.1253 | 33.1651 | 34.341 | 36.1126 | 36.4719 | 37.207 | 36.1047 | 32.8011 | 32.295 | 34.1503 | 34.4113 | 32.5396 | 34.4614 | 34.3068 | 34.3491 | 34.3129 | 34.3611 | 34.3549 | 33.8334 | 34.3169 | 36.1327 | 34.8011 | 36.5761 | 36.49 | 33.1305 | 92.8073 | 92.9629 | 93.0134
2022-09-08 06:22 | 8:31 | 20.7167 | 23.0226 | 25.1295 | 35.6018 | 34.2975 | 34.1106 | 34.6662 | 35.5452 | 36.5262 | 37.572 | 37.0137 | 38.2143 | 34.3943 | 34.41 | 34.0043 | 35.1089 | 34.7375 | 35.3618 | 36.0693 | 36.3964 | 30.8259 | 29.4334 | 92.6891 | 34.6086 | 32.724 | 34.6466 | 32.8169 | 32.8434 | 33.1691 | 34.45 | 34.0621 | 33.8625 | 37.078 | 36.14 | 33.1778 | 34.358 | 36.1116 | 36.4379 | 37.2004 | 36.1162 | 32.8124 | 32.3279 | 34.1647 | 34.4087 | 32.5523 | 34.4744 | 34.3392 | 34.3442 | 34.3319 | 34.363 | 34.3554 | 33.8355 | 34.3129 | 36.1298 | 34.8156 | 36.5885 | 36.4902 | 33.1215 | 92.6962 | 92.8248 | 92.9808
2022-09-08 06:22 | 8:32 | 20.3483 | 22.591 | 24.7949 | 35.5901 | 34.311 | 34.1124 | 34.6566 | 35.5687 | 36.537 | 37.5913 | 37.0174 | 38.2162 | 34.3855 | 34.4086 | 34.0079 | 35.1109 | 34.7202 | 35.3434 | 36.082 | 36.3819 | 30.9808 | 29.7927 | 92.5282 | 34.6435 | 32.7218 | 34.6324 | 32.8144 | 32.8451 | 33.1945 | 34.4436 | 34.0687 | 33.8637 | 37.1003 | 36.127 | 33.1761 | 34.3418 | 36.1253 | 36.4389 | 37.2219 | 36.1281 | 32.8156 | 32.301 | 34.182 | 34.4319 | 32.545 | 34.4566 | 34.3227 | 34.3612 | 34.2932 | 34.3513 | 34.3584 | 33.8525 | 34.3319 | 36.1166 | 34.827 | 36.5709 | 36.4975 | 33.1297 | 92.6321 | 92.7352 | 92.8563
2022-09-08 06:22 | 8:32 | 19.9972 | 22.2167 | 24.5184 | 35.5421 | 34.2995 | 34.0957 | 34.6284 | 35.5676 | 36.524 | 37.5898 | 37.0087 | 38.2349 | 34.3752 | 34.3999 | 33.9926 | 35.1007 | 34.7186 | 35.3667 | 36.0501 | 36.3952 | 31.1149 | 30.0654 | 92.5776 | 34.6096 | 32.7071 | 34.6362 | 32.815 | 32.8353 | 33.1719 | 34.4459 | 34.0783 | 33.8561 | 37.0835 | 36.1203 | 33.1756 | 34.343 | 36.14 | 36.4355 | 37.2067 | 36.1126 | 32.8079 | 32.301 | 34.1795 | 34.4167 | 32.582 | 34.4636 | 34.3351 | 34.356 | 34.3274 | 34.3515 | 34.3529 | 33.8268 | 34.2932 | 36.1248 | 34.813 | 36.5688 | 36.4864 | 33.1326 | 92.4769 | 92.5915 | 92.746
2022-09-08 06:22 | 8:32 | 19.6683 | 21.8477 | 24.1569 | 35.5034 | 34.3152 | 34.1155 | 34.6465 | 35.5616 | 36.4999 | 37.5709 | 37.0036 | 38.2229 | 34.391 | 34.4051 | 33.9965 | 35.1185 | 34.7208 | 35.3597 | 36.0485 | 36.3776 | 31.225 | 30.2754 | 92.4042 | 34.685 | 32.7053 | 34.6291 | 32.8011 | 32.8539 | 33.1651 | 34.4513 | 34.0608 | 33.8744 | 37.089 | 36.1019 | 33.1811 | 34.3363 | 36.127 | 36.4662 | 37.2122 | 36.1116 | 32.8114 | 32.3089 | 34.1745 | 34.43 | 32.5822 | 34.4865 | 34.3438 | 34.3552 | 34.3211 | 34.3565 | 34.3337 | 33.8439 | 34.3274 | 36.1247 | 34.8054 | 36.5717 | 36.505 | 33.1346 | 92.3402 | 92.4956 | 92.6517
2022-09-08 06:22 | 8:32 | 19.3207 | 21.5005 | 23.8573 | 35.4823 | 34.312 | 34.0907 | 34.6192 | 35.5686 | 36.5169 | 37.5833 | 37.0057 | 38.2075 | 34.3965 | 34.408 | 33.9961 | 35.1339 | 34.7392 | 35.344 | 36.0805 | 36.4053 | 31.3082 | 30.4458 | 92.4238 | 34.6955 | 32.7421 | 34.65 | 32.8124 | 32.8308 | 33.1778 | 34.4551 | 34.0694 | 33.8676 | 37.0752 | 36.1067 | 33.168 | 34.3297 | 36.1203 | 36.4472 | 37.2084 | 36.1253 | 32.8161 | 32.3212 | 34.1904 | 34.4418 | 32.5949 | 34.4951 | 34.332 | 34.3595 | 34.2981 | 34.3451 | 34.3691 | 33.8381 | 34.3211 | 36.1348 | 34.7891 | 36.5643 | 36.4815 | 33.1476 | 92.2675 | 92.3586 | 92.5873
2022-09-08 06:22 | 8:32 | 19.0147 | 21.1446 | 23.5979 | 35.3683 | 34.3025 | 34.0937 | 34.6107 | 35.5708 | 36.5162 | 37.5749 | 37.0033 | 38.2319 | 34.4021 | 34.3934 | 33.9945 | 35.1105 | 34.7327 | 35.3637 | 36.0753 | 36.4096 | 31.3725 | 30.5789 | 92.2805 | 34.6983 | 32.7262 | 34.6499 | 32.8156 | 32.8458 | 33.1761 | 34.4654 | 34.0565 | 33.8576 | 37.0925 | 36.1062 | 33.1874 | 34.3319 | 36.1019 | 36.4572 | 37.209 | 36.14 | 32.816 | 32.3149 | 34.1917 | 34.4483 | 32.5879 | 34.4804 | 34.3407 | 34.3552 | 34.3031 | 34.3516 | 34.3538 | 33.8443 | 34.2981 | 36.1305 | 34.8012 | 36.5662 | 36.4915 | 33.1501 | 92.0997 | 92.1949 | 92.4144
2022-09-08 06:23 | 8:33 | 18.7403 | 20.8177 | 23.3074 | 35.3256 | 34.3123 | 34.0991 | 34.6152 | 35.5781 | 36.5378 | 37.5788 | 37.0105 | 38.2199 | 34.3889 | 34.4028 | 34.0093 | 35.1299 | 34.7344 | 35.3556 | 36.0564 | 36.3893 | 31.4511 | 30.6716 | 92.1688 | 34.6627 | 32.7343 | 34.6564 | 32.8079 | 32.8441 | 33.1756 | 34.4481 | 34.0681 | 33.8613 | 37.0909 | 36.1274 | 33.1707 | 34.3389 | 36.1067 | 36.4613 | 37.2192 | 36.127 | 32.8267 | 32.3321 | 34.1924 | 34.4311 | 32.5996 | 34.4792 | 34.3383 | 34.3697 | 34.3331 | 34.3424 | 34.3608 | 33.8472 | 34.3031 | 36.1141 | 34.8066 | 36.561 | 36.5183 | 33.1462 | 92.0326 | 92.0189 | 92.4008
2022-09-08 06:23 | 8:33 | 18.4588 | 20.5241 | 23.0199 | 35.2861 | 34.2951 | 34.0791 | 34.6173 | 35.5699 | 36.5236 | 37.5786 | 37.0063 | 38.2112 | 34.378 | 34.3976 | 34.0029 | 35.1249 | 34.7379 | 35.3477 | 36.0613 | 36.4046 | 31.5331 | 30.7557 | 92.1327 | 34.6956 | 32.7428 | 34.6592 | 32.8114 | 32.837 | 33.1811 | 34.4288 | 34.0705 | 33.8684 | 37.0971 | 36.1287 | 33.1715 | 34.325 | 36.1062 | 36.4596 | 37.2358 | 36.1203 | 32.8237 | 32.3547 | 34.2277 | 34.4586 | 32.6032 | 34.4727 | 34.3452 | 34.3657 | 34.3046 | 34.3396 | 34.3752 | 33.838 | 34.3331 | 36.137 | 34.8011 | 36.5757 | 36.4863 | 33.1499 | 91.9118 | 91.9352 | 92.3819
2022-09-08 06:23 | 8:33 | 18.1727 | 20.1792 | 22.7742 | 35.2647 | 34.3191 | 34.0688 | 34.6229 | 35.5518 | 36.5236 | 37.5743 | 37.023 | 38.2344 | 34.3996 | 34.396 | 34.0111 | 35.124 | 34.7236 | 35.3511 | 36.0628 | 36.3973 | 31.5711 | 30.8301 | 91.9611 | 34.7062 | 32.7241 | 34.6475 | 32.8161 | 32.819 | 33.168 | 34.45 | 34.0686 | 33.8746 | 37.1029 | 36.1141 | 33.1753 | 34.3454 | 36.1274 | 36.4634 | 37.2089 | 36.1019 | 32.826 | 32.3404 | 34.2121 | 34.4584 | 32.6161 | 34.4823 | 34.3527 | 34.3775 | 34.3074 | 34.3479 | 34.3791 | 33.8328 | 34.3046 | 36.1585 | 34.7974 | 36.5753 | 36.5058 | 33.1437 | 91.7554 | 91.7934 | 92.2481
2022-09-08 06:23 | 8:33 | 17.8729 | 19.8665 | 22.5265 | 35.2098 | 34.326 | 34.0677 | 34.6191 | 35.551 | 36.532 | 37.5905 | 37.032 | 38.2311 | 34.3981 | 34.3892 | 33.9859 | 35.105 | 34.732 | 35.3548 | 36.0441 | 36.4094 | 31.5969 | 30.9013 | 91.8765 | 34.7404 | 32.7306 | 34.6383 | 32.816 | 32.8657 | 33.1874 | 34.4658 | 34.0511 | 33.8901 | 37.0846 | 36.1351 | 33.1724 | 34.3553 | 36.1287 | 36.4419 | 37.2274 | 36.1067 | 32.8354 | 32.3361 | 34.2039 | 34.4574 | 32.6161 | 34.493 | 34.3428 | 34.3693 | 34.31 | 34.3382 | 34.3809 | 33.8537 | 34.3074 | 36.1333 | 34.8079 | 36.5819 | 36.5023 | 33.1507 | 91.7097 | 91.6616 | 92.1647
2022-09-08 06:23 | 8:33 | 17.6389 | 19.5663 | 22.2818 | 35.2129 | 34.3135 | 34.091 | 34.5932 | 35.5549 | 36.5304 | 37.5705 | 37.0136 | 38.2336 | 34.3971 | 34.3887 | 34.0107 | 35.1187 | 34.7403 | 35.3666 | 36.0467 | 36.4027 | 31.6317 | 30.9464 | 91.9948 | 34.7591 | 32.7335 | 34.6425 | 32.8267 | 32.8376 | 33.1707 | 34.4399 | 34.0712 | 33.8551 | 37.0818 | 36.1144 | 33.1791 | 34.3378 | 36.1141 | 36.4366 | 37.2383 | 36.1062 | 32.8247 | 32.3354 | 34.2156 | 34.4625 | 32.6243 | 34.4885 | 34.3482 | 34.3806 | 34.3083 | 34.3254 | 34.3785 | 33.849 | 34.31 | 36.1521 | 34.803 | 36.5798 | 36.5002 | 33.163 | 91.7144 | 91.71 | 92.2539
2022-09-08 06:23 | 8:33 | 17.3956 | 19.3359 | 22.0099 | 35.0767 | 34.3122 | 34.0943 | 34.5955 | 35.5469 | 36.5302 | 37.5747 | 37.0179 | 38.2146 | 34.3947 | 34.3996 | 34.0136 | 35.1114 | 34.7376 | 35.3571 | 36.0436 | 36.4021 | 31.6742 | 30.9866 | 91.9508 | 34.749 | 32.7417 | 34.6625 | 32.8237 | 32.832 | 33.1715 | 34.4626 | 34.0607 | 33.8543 | 37.0941 | 36.1181 | 33.1869 | 34.3446 | 36.1351 | 36.447 | 37.2344 | 36.1274 | 32.7943 | 32.3644 | 34.2251 | 34.4649 | 32.6083 | 34.5082 | 34.3473 | 34.3865 | 34.3052 | 34.3443 | 34.3936 | 33.844 | 34.3083 | 36.1307 | 34.7899 | 36.5778 | 36.4964 | 33.1561 | 91.7666 | 91.7445 | 92.3219
2022-09-08 06:24 | 8:33 | 17.189 | 19.0836 | 21.7253 | 35.1036 | 34.3412 | 34.0769 | 34.602 | 35.5506 | 36.5399 | 37.5933 | 37.0052 | 38.2247 | 34.3805 | 34.3967 | 34.0173 | 35.1034 | 34.7513 | 35.3338 | 36.055 | 36.4113 | 31.7096 | 31.0138 | 92.0559 | 34.7712 | 32.7286 | 34.6529 | 32.826 | 32.8404 | 33.1753 | 34.4766 | 34.0863 | 33.8613 | 37.1055 | 36.0927 | 33.156 | 34.3284 | 36.1144 | 36.4784 | 37.2379 | 36.1287 | 32.8231 | 32.3693 | 34.221 | 34.4727 | 32.6527 | 34.514 | 34.3667 | 34.3695 | 34.3101 | 34.3375 | 34.3852 | 33.8464 | 34.3052 | 36.1405 | 34.803 | 36.5708 | 36.5254 | 33.1611 | 91.8901 | 91.8662 | 92.3367
2022-09-08 06:24 | 8:34 | 17.0184 | 18.8156 | 21.5244 | 34.9487 | 34.3055 | 34.0692 | 34.587 | 35.5457 | 36.5397 | 37.5581 | 37.0158 | 38.2217 | 34.374 | 34.4045 | 34.0034 | 35.1113 | 34.7592 | 35.3206 | 36.0566 | 36.3983 | 31.7391 | 31.0549 | 92.045 | 34.7686 | 32.7426 | 34.645 | 32.8354 | 32.8492 | 33.1724 | 34.4754 | 34.0525 | 33.8642 | 37.0996 | 36.1032 | 33.1686 | 34.327 | 36.1181 | 36.4572 | 37.2302 | 36.1141 | 32.8165 | 32.36 | 34.2389 | 34.4767 | 32.6343 | 34.5151 | 34.3587 | 34.3931 | 34.2874 | 34.3347 | 34.3935 | 33.8474 | 34.3101 | 36.1511 | 34.7996 | 36.5612 | 36.5118 | 33.1376 | 91.9925 | 92.0406 | 92.4926
2022-09-08 06:24 | 8:34 | 16.7214 | 18.6185 | 21.2777 | 35.0068 | 34.3285 | 34.0951 | 34.5752 | 35.5381 | 36.5165 | 37.563 | 37.002 | 38.2317 | 34.3944 | 34.393 | 33.999 | 35.1137 | 34.7506 | 35.3398 | 36.0407 | 36.3899 | 31.7639 | 31.0706 | 91.9909 | 34.8199 | 32.7557 | 34.6473 | 32.8247 | 32.8439 | 33.1791 | 34.4627 | 34.0629 | 33.8601 | 37.0762 | 36.1003 | 33.1808 | 34.3031 | 36.0927 | 36.4431 | 37.2221 | 36.1351 | 32.8097 | 32.3637 | 34.2386 | 34.479 | 32.6286 | 34.5029 | 34.3461 | 34.3943 | 34.2824 | 34.313 | 34.3933 | 33.8692 | 34.2874 | 36.142 | 34.7848 | 36.568 | 36.5186 | 33.1545 | 92.0632 | 92.1985 | 92.5065
2022-09-08 06:24 | 8:34 | 16.5256 | 18.3336 | 21.0528 | 34.9594 | 34.3392 | 34.0701 | 34.5779 | 35.565 | 36.5328 | 37.5823 | 37.0273 | 38.2326 | 34.3735 | 34.3789 | 34.0085 | 35.0936 | 34.7323 | 35.3405 | 36.0473 | 36.394 | 31.7768 | 31.1169 | 92.2329 | 34.8595 | 32.7261 | 34.6408 | 32.7943 | 32.8412 | 33.1869 | 34.4626 | 34.0563 | 33.8451 | 37.0721 | 36.1122 | 33.1728 | 34.323 | 36.1032 | 36.4583 | 37.2234 | 36.1144 | 32.8197 | 32.3831 | 34.2537 | 34.4742 | 32.6589 | 34.5135 | 34.3722 | 34.3859 | 34.2803 | 34.3244 | 34.4112 | 33.866 | 34.2824 | 36.1392 | 34.7816 | 36.5565 | 36.5125 | 33.1522 | 92.184 | 92.3227 | 92.5519
2022-09-08 06:24 | 8:34 | 16.2608 | 18.0993 | 20.8269 | 34.8628 | 34.32 | 34.0788 | 34.5738 | 35.5347 | 36.5342 | 37.5762 | 37.0073 | 38.217 | 34.3824 | 34.4024 | 34.017 | 35.1096 | 34.7275 | 35.3477 | 36.0357 | 36.3931 | 31.8065 | 31.1319 | 92.3686 | 34.7742 | 32.7458 | 34.6628 | 32.8231 | 32.8311 | 33.156 | 34.4599 | 34.0533 | 33.8546 | 37.0936 | 36.1046 | 33.1774 | 34.3175 | 36.1003 | 36.4424 | 37.2372 | 36.1181 | 32.7978 | 32.3802 | 34.2622 | 34.4909 | 32.6519 | 34.5204 | 34.3576 | 34.3905 | 34.2928 | 34.3288 | 34.4102 | 33.8514 | 34.2803 | 36.1408 | 34.7919 | 36.573 | 36.4982 | 33.1709 | 92.346 | 92.5303 | 92.6266
2022-09-08 06:24 | 8:34 | 16.1379 | 17.8731 | 20.5841 | 34.8758 | 34.3113 | 34.0586 | 34.5716 | 35.523 | 36.5448 | 37.573 | 37.0185 | 38.2083 | 34.3984 | 34.3758 | 34.0155 | 35.1076 | 34.737 | 35.3316 | 36.0215 | 36.3879 | 31.8336 | 31.1818 | 92.4896 | 34.8416 | 32.7462 | 34.6355 | 32.8165 | 32.8142 | 33.1686 | 34.4452 | 34.0629 | 33.8531 | 37.1074 | 36.1195 | 33.1709 | 34.3215 | 36.1122 | 36.4515 | 37.2288 | 36.0927 | 32.8118 | 32.3981 | 34.2587 | 34.4961 | 32.6653 | 34.5062 | 34.3737 | 34.4121 | 34.3179 | 34.3239 | 34.3972 | 33.85 | 34.2928 | 36.1434 | 34.773 | 36.5744 | 36.5085 | 33.1527 | 92.5401 | 92.6861 | 92.8005
2022-09-08 06:25 | 8:35 | 16.06 | 17.686 | 20.4411 | 34.8049 | 34.3247 | 34.0702 | 34.5699 | 35.5283 | 36.5453 | 37.5638 | 37.0109 | 38.2315 | 34.3694 | 34.3835 | 34.0002 | 35.0821 | 34.7294 | 35.302 | 36.0109 | 36.3946 | 31.8696 | 31.1776 | 92.596 | 34.8337 | 32.7414 | 34.6458 | 32.8097 | 32.8299 | 33.1808 | 34.4656 | 34.0531 | 33.8463 | 37.0959 | 36.1148 | 33.17 | 34.2901 | 36.1046 | 36.4585 | 37.2426 | 36.1032 | 32.8205 | 32.3863 | 34.2474 | 34.4751 | 32.6662 | 34.5082 | 34.3758 | 34.3987 | 34.285 | 34.3225 | 34.399 | 33.8647 | 34.3179 | 36.1282 | 34.7815 | 36.5831 | 36.4999 | 33.1677 | 92.6801 | 92.8279 | 92.8682
2022-09-08 06:25 | 8:35 | 15.7191 | 17.4669 | 20.1932 | 34.7105 | 34.3203 | 34.0547 | 34.5526 | 35.5419 | 36.5199 | 37.5713 | 37.0093 | 38.2213 | 34.3869 | 34.394 | 34.0137 | 35.1087 | 34.7243 | 35.3288 | 36.0111 | 36.3973 | 31.892 | 31.2123 | 92.5633 | 34.8069 | 32.7374 | 34.6465 | 32.8197 | 32.8315 | 33.1728 | 34.4652 | 34.0475 | 33.848 | 37.0986 | 36.0997 | 33.1594 | 34.2934 | 36.1195 | 36.4554 | 37.247 | 36.1003 | 32.8132 | 32.3903 | 34.2601 | 34.4882 | 32.6641 | 34.5172 | 34.3654 | 34.4099 | 34.2998 | 34.3261 | 34.3997 | 33.8619 | 34.285 | 36.1348 | 34.7738 | 36.5659 | 36.5109 | 33.1536 | 92.7536 | 93.0131 | 92.9168
2022-09-08 06:25 | 8:35 | 15.564 | 17.263 | 20.0114 | 34.6672 | 34.3395 | 34.0514 | 34.5519 | 35.5396 | 36.537 | 37.5714 | 37.0107 | 38.2177 | 34.3765 | 34.3846 | 34.0189 | 35.0887 | 34.7235 | 35.3263 | 35.9867 | 36.4004 | 31.9061 | 31.2154 | 92.7352 | 34.8062 | 32.7417 | 34.636 | 32.7978 | 32.8198 | 33.1774 | 34.4613 | 34.0277 | 33.8453 | 37.0876 | 36.1287 | 33.1724 | 34.3083 | 36.1148 | 36.4539 | 37.2193 | 36.1122 | 32.7928 | 32.3927 | 34.2495 | 34.4833 | 32.6771 | 34.5361 | 34.3736 | 34.4176 | 34.2824 | 34.3142 | 34.3953 | 33.8541 | 34.2998 | 36.1443 | 34.782 | 36.5755 | 36.4949 | 33.1522 | 92.9878 | 93.1374 | 93.024
2022-09-08 06:25 | 8:35 | 15.3467 | 17.0668 | 19.8104 | 34.7258 | 34.3274 | 34.0517 | 34.5409 | 35.5286 | 36.5271 | 37.5658 | 37.0004 | 38.2221 | 34.3905 | 34.3948 | 34.0062 | 35.113 | 34.7443 | 35.3193 | 36.0168 | 36.3962 | 31.9108 | 31.2244 | 92.742 | 34.8486 | 32.7405 | 34.6427 | 32.8118 | 32.8464 | 33.1709 | 34.441 | 34.0401 | 33.8363 | 37.079 | 36.1037 | 33.1581 | 34.2812 | 36.0997 | 36.4423 | 37.2439 | 36.1046 | 32.8188 | 32.3828 | 34.2676 | 34.4939 | 32.6913 | 34.5264 | 34.365 | 34.4144 | 34.2983 | 34.3062 | 34.3881 | 33.8691 | 34.2824 | 36.1403 | 34.7824 | 36.5654 | 36.5218 | 33.1433 | 93.192 | 93.3152 | 93.2017
2022-09-08 06:25 | 8:35 | 15.1921 | 16.9176 | 19.6176 | 34.7091 | 34.3328 | 34.0417 | 34.5287 | 35.535 | 36.5326 | 37.553 | 37.0015 | 38.216 | 34.3809 | 34.3811 | 33.999 | 35.0891 | 34.7264 | 35.336 | 36.0093 | 36.3934 | 31.9485 | 31.2423 | 92.7064 | 34.8213 | 32.7462 | 34.6512 | 32.8205 | 32.8322 | 33.17 | 34.4579 | 34.0451 | 33.8506 | 37.0891 | 36.1158 | 33.1793 | 34.2978 | 36.1287 | 36.4518 | 37.2369 | 36.1195 | 32.8021 | 32.3851 | 34.2712 | 34.4834 | 32.7183 | 34.5442 | 34.3742 | 34.4039 | 34.2804 | 34.2966 | 34.3895 | 33.8698 | 34.2983 | 36.1314 | 34.7977 | 36.5699 | 36.5192 | 33.1591 | 93.2475 | 93.492 | 93.2276
2022-09-08 06:25 | 8:35 | 15.1904 | 16.7306 | 19.4517 | 34.5787 | 34.3128 | 34.0443 | 34.5149 | 35.5226 | 36.5273 | 37.5555 | 36.984 | 38.2126 | 34.3786 | 34.3827 | 34.0031 | 35.0901 | 34.7237 | 35.3273 | 36.0197 | 36.3993 | 31.9612 | 31.262 | 92.9125 | 34.7999 | 32.7422 | 34.6494 | 32.8132 | 32.8361 | 33.1594 | 34.4557 | 34.0358 | 33.8454 | 37.0919 | 36.1192 | 33.1661 | 34.2907 | 36.1037 | 36.4328 | 37.2253 | 36.1148 | 32.8091 | 32.3909 | 34.2823 | 34.497 | 32.7013 | 34.5428 | 34.3771 | 34.413 | 34.303 | 34.2999 | 34.3994 | 33.8605 | 34.2804 | 36.1525 | 34.7854 | 36.5624 | 36.4927 | 33.172 | 93.4659 | 93.6801 | 93.3304
2022-09-08 06:26 | 8:35 | 14.8862 | 16.5618 | 19.2964 | 34.53 | 34.3345 | 34.0276 | 34.5138 | 35.5253 | 36.5259 | 37.5533 | 36.9933 | 38.2047 | 34.3724 | 34.3788 | 34.0038 | 35.0804 | 34.7249 | 35.3144 | 35.9925 | 36.4102 | 31.9769 | 31.2969 | 92.8952 | 34.822 | 32.7184 | 34.6408 | 32.7928 | 32.8228 | 33.1724 | 34.4394 | 34.0376 | 33.8424 | 37.0875 | 36.1286 | 33.1637 | 34.2955 | 36.1158 | 36.4366 | 37.2131 | 36.0997 | 32.8075 | 32.4172 | 34.2638 | 34.5004 | 32.7091 | 34.5469 | 34.3799 | 34.4088 | 34.2928 | 34.2922 | 34.4104 | 33.8882 | 34.303 | 36.1609 | 34.7808 | 36.56 | 36.525 | 33.1834 | 93.6038 | 93.8085 | 93.4545
2022-09-08 06:26 | 8:36 | 14.7422 | 16.4174 | 19.0989 | 34.6026 | 34.3254 | 34.0354 | 34.4999 | 35.5127 | 36.5476 | 37.5402 | 36.9837 | 38.2186 | 34.3617 | 34.3685 | 34.0066 | 35.088 | 34.7254 | 35.3175 | 35.9892 | 36.3699 | 32.0012 | 31.2934 | 92.9744 | 34.8768 | 32.7268 | 34.6401 | 32.8188 | 32.851 | 33.1581 | 34.4507 | 34.0384 | 33.8447 | 37.0949 | 36.1108 | 33.1929 | 34.2804 | 36.1192 | 36.4405 | 37.2368 | 36.1287 | 32.8023 | 32.3992 | 34.2698 | 34.4852 | 32.7273 | 34.5614 | 34.3882 | 34.4049 | 34.2835 | 34.2822 | 34.41 | 33.8757 | 34.2928 | 36.1427 | 34.7651 | 36.5655 | 36.5118 | 33.1432 | 93.771 | 94.0211 | 93.5552
2022-09-08 06:26 | 8:36 | 14.5883 | 16.2302 | 19.0337 | 34.4905 | 34.3324 | 34.0241 | 34.4961 | 35.5036 | 36.5105 | 37.5492 | 36.9966 | 38.19 | 34.3917 | 34.3588 | 33.9888 | 35.0759 | 34.7149 | 35.3101 | 35.9922 | 36.3786 | 32.0162 | 31.3026 | 93.3083 | 34.9226 | 32.7577 | 34.6424 | 32.8021 | 32.8275 | 33.1793 | 34.4667 | 34.0406 | 33.8516 | 37.0887 | 36.1203 | 33.1817 | 34.2712 | 36.1286 | 36.4324 | 37.2479 | 36.1037 | 32.8185 | 32.39 | 34.2675 | 34.5059 | 32.7208 | 34.5579 | 34.3901 | 34.4066 | 34.272 | 34.294 | 34.4086 | 33.875 | 34.2835 | 36.1611 | 34.7781 | 36.5353 | 36.5075 | 33.1725 | 93.9679 | 94.1043 | 93.6346
2022-09-08 06:26 | 8:36 | 14.4376 | 16.0981 | 18.8214 | 34.4412 | 34.3556 | 34.0299 | 34.5055 | 35.5092 | 36.5219 | 37.5428 | 36.9814 | 38.216 | 34.3685 | 34.3591 | 34.0055 | 35.0822 | 34.7167 | 35.2968 | 36.0112 | 36.3838 | 32.023 | 31.2937 | 93.5097 | 34.8667 | 32.7577 | 34.6476 | 32.8091 | 32.828 | 33.1661 | 34.4559 | 34.0314 | 33.8293 | 37.0819 | 36.1183 | 33.1686 | 34.2872 | 36.1108 | 36.4337 | 37.236 | 36.1158 | 32.8093 | 32.4069 | 34.282 | 34.4973 | 32.7219 | 34.5718 | 34.3811 | 34.4155 | 34.3029 | 34.2755 | 34.3999 | 33.8866 | 34.272 | 36.1396 | 34.7756 | 36.5607 | 36.5217 | 33.1579 | 94.1831 | 94.2736 | 93.8162
2022-09-08 06:26 | 8:36 | 14.2767 | 15.9696 | 18.6452 | 34.3306 | 34.3549 | 34.025 | 34.5155 | 35.5151 | 36.5198 | 37.5412 | 36.9892 | 38.1909 | 34.3758 | 34.3635 | 33.9975 | 35.0934 | 34.7145 | 35.2989 | 35.9838 | 36.377 | 32.0449 | 31.3039 | 93.6085 | 34.8592 | 32.7366 | 34.652 | 32.8075 | 32.8318 | 33.1637 | 34.4604 | 34.0357 | 33.8458 | 37.0608 | 36.115 | 33.1679 | 34.2679 | 36.1203 | 36.4358 | 37.2285 | 36.1192 | 32.8195 | 32.4233 | 34.2742 | 34.4897 | 32.7315 | 34.5798 | 34.3834 | 34.4052 | 34.2874 | 34.2824 | 34.4051 | 33.8863 | 34.3029 | 36.1438 | 34.7716 | 36.5573 | 36.5249 | 33.1519 | 94.3347 | 94.3744 | 93.8976
2022-09-08 06:26 | 8:36 | 14.1698 | 15.8052 | 18.5237 | 34.39 | 34.3554 | 34.0292 | 34.5054 | 35.5043 | 36.5285 | 37.5563 | 36.9904 | 38.2032 | 34.3758 | 34.3685 | 33.9888 | 35.0806 | 34.7007 | 35.3109 | 35.9907 | 36.406 | 32.0578 | 31.3217 | 93.6127 | 34.8703 | 32.7383 | 34.638 | 32.8023 | 32.8264 | 33.1929 | 34.4645 | 34.0336 | 33.8396 | 37.0857 | 36.1322 | 33.1757 | 34.2768 | 36.1183 | 36.4349 | 37.2407 | 36.1286 | 32.8206 | 32.4232 | 34.2976 | 34.4937 | 32.7551 | 34.5926 | 34.3804 | 34.4237 | 34.2985 | 34.2851 | 34.408 | 33.8848 | 34.2874 | 36.1268 | 34.7817 | 36.5591 | 36.4915 | 33.1777 | 94.3956 | 94.5281 | 93.9215
2022-09-08 06:27 | 8:37 | 14.0605 | 15.6574 | 18.3872 | 34.3683 | 34.3584 | 34.0275 | 34.4867 | 35.5113 | 36.5224 | 37.5532 | 36.993 | 38.2017 | 34.3582 | 34.3706 | 33.9754 | 35.1005 | 34.7253 | 35.2936 | 35.9841 | 36.3773 | 32.0872 | 31.3453 | 93.5293 | 34.8796 | 32.7495 | 34.6301 | 32.8185 | 32.8517 | 33.1817 | 34.4559 | 34.0304 | 33.8408 | 37.0705 | 36.1257 | 33.1592 | 34.2794 | 36.115 | 36.4369 | 37.2305 | 36.1108 | 32.8021 | 32.4253 | 34.2939 | 34.503 | 32.7592 | 34.5829 | 34.3854 | 34.4104 | 34.302 | 34.3019 | 34.3934 | 33.8785 | 34.2985 | 36.1455 | 34.7698 | 36.5725 | 36.515 | 33.1495 | 94.5611 | 94.6765 | 93.9829
2022-09-08 06:27 | 8:37 | 13.9538 | 15.5376 | 18.2472 | 34.304 | 34.3529 | 34.0126 | 34.4822 | 35.5027 | 36.5105 | 37.5442 | 36.9904 | 38.1977 | 34.3744 | 34.341 | 33.9902 | 35.0813 | 34.7064 | 35.2961 | 35.9672 | 36.38 | 32.1109 | 31.3614 | 93.7317 | 34.883 | 32.7469 | 34.6407 | 32.8093 | 32.8144 | 33.1686 | 34.4474 | 34.0314 | 33.8228 | 37.0709 | 36.1176 | 33.1583 | 34.2644 | 36.1322 | 36.4401 | 37.2367 | 36.1203 | 32.8109 | 32.4338 | 34.293 | 34.4896 | 32.747 | 34.5959 | 34.387 | 34.4256 | 34.3034 | 34.2693 | 34.4028 | 33.8892 | 34.302 | 36.1444 | 34.77 | 36.5735 | 36.5086 | 33.1416 | 94.7095 | 94.7465 | 94.045
2022-09-08 06:27 | 8:37 | 13.8796 | 15.4192 | 18.1125 | 34.3033 | 34.3337 | 34.0147 | 34.468 | 35.4943 | 36.5121 | 37.5519 | 36.9793 | 38.196 | 34.3915 | 34.3583 | 33.9792 | 35.084 | 34.7161 | 35.304 | 35.9865 | 36.3847 | 32.1165 | 31.3477 | 93.8169 | 34.8537 | 32.751 | 34.6372 | 32.8195 | 32.8248 | 33.1679 | 34.4398 | 34.0288 | 33.8273 | 37.085 | 36.1068 | 33.1819 | 34.2682 | 36.1257 | 36.4406 | 37.2507 | 36.1183 | 32.8146 | 32.4145 | 34.293 | 34.5039 | 32.754 | 34.5986 | 34.3774 | 34.4147 | 34.3089 | 34.2663 | 34.3976 | 33.8847 | 34.3034 | 36.1427 | 34.7899 | 36.5615 | 36.5025 | 33.1752 | 94.8085 | 94.808 | 94.1558
2022-09-08 06:27 | 8:37 | 13.6811 | 15.2574 | 18.0082 | 34.2047 | 34.3691 | 34.0195 | 34.476 | 35.5049 | 36.5217 | 37.5416 | 37.0146 | 38.1911 | 34.355 | 34.3644 | 33.9807 | 35.0844 | 34.7028 | 35.3053 | 35.9785 | 36.372 | 32.1326 | 31.359 | 93.6328 | 34.8877 | 32.7477 | 34.6481 | 32.8206 | 32.8248 | 33.1757 | 34.4607 | 34.0408 | 33.8297 | 37.0779 | 36.1103 | 33.1897 | 34.2674 | 36.1176 | 36.4364 | 37.222 | 36.115 | 32.803 | 32.4273 | 34.2844 | 34.508 | 32.7591 | 34.6172 | 34.3795 | 34.4178 | 34.3035 | 34.2629 | 34.396 | 33.8823 | 34.3089 | 36.1311 | 34.796 | 36.5694 | 36.491 | 33.1458 | 94.8859 | 94.8302 | 94.1849
2022-09-08 06:27 | 8:37 | 13.5716 | 15.1458 | 17.8695 | 34.2233 | 34.3538 | 34.0369 | 34.4674 | 35.4981 | 36.5234 | 37.5372 | 36.9949 | 38.1965 | 34.3686 | 34.3421 | 33.9915 | 35.0722 | 34.7115 | 35.2888 | 35.963 | 36.3815 | 32.1566 | 31.369 | 93.9509 | 34.9346 | 32.7387 | 34.6446 | 32.8021 | 32.8179 | 33.1592 | 34.4427 | 34.0189 | 33.834 | 37.0706 | 36.1095 | 33.1855 | 34.2829 | 36.1068 | 36.4506 | 37.2469 | 36.1322 | 32.8223 | 32.4627 | 34.2907 | 34.516 | 32.7684 | 34.6093 | 34.372 | 34.4085 | 34.3069 | 34.2881 | 34.3892 | 33.8997 | 34.3035 | 36.1296 | 34.7933 | 36.5711 | 36.4975 | 33.1538 | 94.9756 | 94.9475 | 94.22
2022-09-08 06:27 | 8:37 | 13.4502 | 15.0096 | 17.7468 | 34.1821 | 34.3608 | 34.0027 | 34.4562 | 35.4904 | 36.5217 | 37.5296 | 36.9902 | 38.1999 | 34.3723 | 34.3474 | 33.9732 | 35.0769 | 34.689 | 35.298 | 35.9669 | 36.3705 | 32.1498 | 31.379 | 94.03 | 34.8784 | 32.7576 | 34.6446 | 32.8109 | 32.8373 | 33.1583 | 34.4319 | 34.0252 | 33.8297 | 37.0732 | 36.1132 | 33.1664 | 34.2705 | 36.1103 | 36.442 | 37.2269 | 36.1257 | 32.8116 | 32.4432 | 34.2968 | 34.5161 | 32.7897 | 34.5912 | 34.3821 | 34.4113 | 34.3106 | 34.2826 | 34.3887 | 33.8792 | 34.3069 | 36.1401 | 34.7633 | 36.567 | 36.5131 | 33.1441 | 95.0816 | 94.9528 | 94.299
2022-09-08 06:28 | 8:38 | 13.401 | 14.8927 | 17.6204 | 34.2165 | 34.3752 | 34.032 | 34.4629 | 35.4871 | 36.5082 | 37.5387 | 36.982 | 38.1825 | 34.3692 | 34.3342 | 33.9833 | 35.0819 | 34.7087 | 35.2968 | 35.9809 | 36.3673 | 32.1693 | 31.3858 | 94.1013 | 34.9622 | 32.735 | 34.6682 | 32.8146 | 32.8357 | 33.1819 | 34.4401 | 34.0173 | 33.8244 | 37.0677 | 36.1112 | 33.176 | 34.2613 | 36.1095 | 36.434 | 37.222 | 36.1176 | 32.8157 | 32.4341 | 34.2968 | 34.529 | 32.7892 | 34.6071 | 34.3728 | 34.4305 | 34.2978 | 34.2842 | 34.3996 | 33.8809 | 34.3106 | 36.1441 | 34.7635 | 36.5662 | 36.5054 | 33.1538 | 95.0349 | 94.906 | 94.2772
2022-09-08 06:28 | 8:38 | 13.3425 | 14.7582 | 17.5436 | 34.1913 | 34.3791 | 34.0062 | 34.4602 | 35.4789 | 36.5242 | 37.5277 | 36.9873 | 38.2028 | 34.3657 | 34.3607 | 33.9804 | 35.0854 | 34.7149 | 35.2862 | 35.9723 | 36.3578 | 32.191 | 31.4143 | 93.9262 | 34.9205 | 32.7531 | 34.6509 | 32.803 | 32.8294 | 33.1897 | 34.4413 | 34.0268 | 33.8288 | 37.067 | 36.1373 | 33.1644 | 34.2646 | 36.1132 | 36.4556 | 37.2462 | 36.1068 | 32.8056 | 32.4573 | 34.3074 | 34.5147 | 32.8089 | 34.6388 | 34.3738 | 34.4197 | 34.2906 | 34.3017 | 34.3967 | 33.906 | 34.2978 | 36.1191 | 34.7556 | 36.5499 | 36.508 | 33.1463 | 94.8331 | 94.8691 | 94.1386
2022-09-08 06:28 | 8:38 | 13.1632 | 14.6639 | 17.3997 | 34.0764 | 34.3809 | 34.0227 | 34.4634 | 35.4989 | 36.5204 | 37.5222 | 36.9777 | 38.1898 | 34.3557 | 34.3311 | 33.978 | 35.0677 | 34.71 | 35.2841 | 35.952 | 36.3624 | 32.2011 | 31.4143 | 93.782 | 34.9624 | 32.7504 | 34.6466 | 32.8223 | 32.8398 | 33.1855 | 34.4575 | 34.0355 | 33.8333 | 37.062 | 36.1363 | 33.1633 | 34.2533 | 36.1112 | 36.4446 | 37.2242 | 36.1103 | 32.8093 | 32.4646 | 34.3287 | 34.5066 | 32.7864 | 34.6239 | 34.3427 | 34.4433 | 34.303 | 34.2799 | 34.4045 | 33.8717 | 34.2906 | 36.1387 | 34.7862 | 36.5768 | 36.5158 | 33.1422 | 94.6236 | 94.669 | 94.0066
2022-09-08 06:28 | 8:38 | 12.9978 | 14.4271 | 17.2905 | 34.0863 | 34.3785 | 33.9991 | 34.4593 | 35.4971 | 36.5151 | 37.5084 | 36.9695 | 38.1895 | 34.3825 | 34.3288 | 33.9621 | 35.0799 | 34.7172 | 35.2726 | 35.9465 | 36.3487 | 32.2213 | 31.4102 | 93.6809 | 34.9082 | 32.733 | 34.6578 | 32.8116 | 32.8207 | 33.1664 | 34.4357 | 34.0226 | 33.8362 | 37.0757 | 36.1274 | 33.1715 | 34.2527 | 36.1373 | 36.4161 | 37.2208 | 36.1095 | 32.8211 | 32.4546 | 34.3106 | 34.5228 | 32.8289 | 34.6256 | 34.3797 | 34.4169 | 34.3096 | 34.2571 | 34.393 | 33.8993 | 34.303 | 36.1148 | 34.7795 | 36.5703 | 36.4916 | 33.131 | 94.3418 | 94.4955 | 93.8608
2022-09-08 06:28 | 8:38 | 12.4934 | 12.4203 | 16.7594 | 33.9779 | 34.3936 | 33.9995 | 34.4491 | 35.4842 | 36.5095 | 37.5111 | 37.0021 | 38.2005 | 34.3747 | 34.345 | 33.964 | 35.064 | 34.6952 | 35.2979 | 35.9413 | 36.3646 | 32.184 | 31.4038 | 93.4484 | 34.9272 | 32.7432 | 34.6615 | 32.8157 | 32.8391 | 33.176 | 34.4282 | 34.0201 | 33.8235 | 37.0641 | 36.137 | 33.173 | 34.255 | 36.1363 | 36.4231 | 37.2098 | 36.1132 | 32.8372 | 32.4914 | 34.319 | 34.5094 | 32.819 | 34.6313 | 34.3911 | 34.4257 | 34.3166 | 34.2722 | 34.3789 | 33.9028 | 34.3096 | 36.1383 | 34.7697 | 36.5667 | 36.4863 | 33.1286 | 94.1303 | 94.2937 | 93.7528
2022-09-08 06:28 | 8:38 | 15.0647 | 12.8703 | 18.2563 | 34.0649 | 34.3852 | 34.024 | 34.441 | 35.4787 | 36.5044 | 37.5049 | 36.9832 | 38.1917 | 34.3441 | 34.3416 | 33.9526 | 35.0726 | 34.6917 | 35.2708 | 35.9441 | 36.3566 | 32.2016 | 31.4365 | 93.3107 | 34.9666 | 32.7354 | 34.6545 | 32.8056 | 32.8393 | 33.1644 | 34.4282 | 34.0215 | 33.828 | 37.0669 | 36.116 | 33.1613 | 34.25 | 36.1274 | 36.425 | 37.2008 | 36.1112 | 32.835 | 32.4607 | 34.3213 | 34.5258 | 32.8294 | 34.6337 | 34.3755 | 34.4334 | 34.3011 | 34.2711 | 34.4024 | 33.8823 | 34.3166 | 36.1153 | 34.7844 | 36.5406 | 36.5048 | 33.1377 | 94.0031 | 94.0962 | 93.6269
2022-09-08 06:29 | 8:38 | 17.2111 | 14.3016 | 20.1688 | 34.1525 | 34.3935 | 34.0005 | 34.4334 | 35.4808 | 36.4971 | 37.5117 | 36.9934 | 38.172 | 34.3611 | 34.3332 | 33.9465 | 35.0667 | 34.6919 | 35.2988 | 35.9277 | 36.3359 | 32.2225 | 31.418 | 93.3363 | 34.9119 | 32.7386 | 34.6533 | 32.8093 | 32.8171 | 33.1633 | 34.4286 | 34.018 | 33.8334 | 37.0802 | 36.1389 | 33.181 | 34.2716 | 36.137 | 36.4244 | 37.2241 | 36.1373 | 32.8177 | 32.4751 | 34.33 | 34.5116 | 32.829 | 34.6241 | 34.382 | 34.4252 | 34.3074 | 34.2737 | 34.3758 | 33.8892 | 34.3011 | 36.142 | 34.7933 | 36.567 | 36.5069 | 33.1407 | 93.8747 | 93.9789 | 93.5697
2022-09-08 06:29 | 8:39 | 18.804 | 15.9623 | 21.9126 | 34.3807 | 34.3933 | 34.0089 | 34.4485 | 35.4812 | 36.5062 | 37.511 | 37 | 38.1965 | 34.363 | 34.3311 | 33.9663 | 35.0907 | 34.6996 | 35.2735 | 35.956 | 36.3547 | 32.2168 | 31.4408 | 93.2928 | 34.9581 | 32.7351 | 34.6718 | 32.8211 | 32.8192 | 33.1715 | 34.4241 | 34.0287 | 33.8309 | 37.0744 | 36.1311 | 33.1674 | 34.2636 | 36.116 | 36.4307 | 37.2224 | 36.1363 | 32.8213 | 32.4702 | 34.3102 | 34.5179 | 32.8493 | 34.6386 | 34.3912 | 34.4299 | 34.314 | 34.2811 | 34.3835 | 33.8871 | 34.3074 | 36.117 | 34.7666 | 36.5675 | 36.5048 | 33.1255 | 93.7648 | 93.8774 | 93.5648
2022-09-08 06:29 | 8:39 | 20.1995 | 17.7686 | 23.3874 | 34.473 | 34.4112 | 34.0023 | 34.4344 | 35.4758 | 36.5067 | 37.4955 | 37.0015 | 38.1803 | 34.3513 | 34.3335 | 33.931 | 35.0716 | 34.7156 | 35.2507 | 35.9387 | 36.3555 | 32.2453 | 31.4406 | 93.145 | 34.9417 | 32.7353 | 34.6891 | 32.8372 | 32.8308 | 33.173 | 34.4533 | 34.0333 | 33.8275 | 37.0725 | 36.1391 | 33.1735 | 34.2291 | 36.1389 | 36.4249 | 37.2031 | 36.1274 | 32.8414 | 32.4792 | 34.3209 | 34.519 | 32.8521 | 34.6481 | 34.3907 | 34.4195 | 34.3114 | 34.2745 | 34.394 | 33.9098 | 34.314 | 36.1381 | 34.7859 | 36.5616 | 36.4985 | 33.1353 | 93.6783 | 93.7748 | 93.4802
2022-09-08 06:29 | 8:39 | 21.3463 | 19.4118 | 24.6589 | 34.5092 | 34.4102 | 34.0144 | 34.439 | 35.4684 | 36.4821 | 37.5035 | 36.9897 | 38.1874 | 34.3515 | 34.3579 | 33.9591 | 35.0595 | 34.6858 | 35.279 | 35.9284 | 36.3258 | 32.2734 | 31.4366 | 93.2051 | 34.9857 | 32.7456 | 34.6704 | 32.835 | 32.8319 | 33.1613 | 34.424 | 34.0308 | 33.8282 | 37.0598 | 36.1097 | 33.1642 | 34.2599 | 36.1311 | 36.4204 | 37.2189 | 36.137 | 32.8352 | 32.4779 | 34.3394 | 34.5507 | 32.8666 | 34.638 | 34.3867 | 34.4276 | 34.3255 | 34.2622 | 34.3846 | 33.8799 | 34.3114 | 36.1118 | 34.7758 | 36.5756 | 36.4823 | 33.1116 | 93.5632 | 93.6535 | 93.3751
2022-09-08 06:29 | 8:39 | 22.3614 | 20.9174 | 25.6431 | 34.636 | 34.3972 | 34.0256 | 34.3771 | 35.4722 | 36.4935 | 37.5075 | 36.978 | 38.192 | 34.3565 | 34.3336 | 33.9325 | 35.0653 | 34.6964 | 35.279 | 35.9246 | 36.3393 | 32.2965 | 31.4436 | 93.2012 | 35.0159 | 32.7576 | 34.6594 | 32.8177 | 32.8349 | 33.181 | 34.4193 | 34.0166 | 33.8492 | 37.0726 | 36.1344 | 33.1614 | 34.2697 | 36.1391 | 36.4028 | 37.226 | 36.116 | 32.8223 | 32.4648 | 34.3216 | 34.5283 | 32.8627 | 34.6683 | 34.3711 | 34.4221 | 34.3178 | 34.27 | 34.3948 | 33.8952 | 34.3255 | 36.1069 | 34.7687 | 36.5416 | 36.4961 | 33.1219 | 93.4915 | 93.5948 | 93.3921
2022-09-08 06:29 | 8:39 | 23.2473 | 22.3601 | 26.4727 | 34.7062 | 34.399 | 34.017 | 34.4213 | 35.4796 | 36.4916 | 37.5111 | 36.9796 | 38.1803 | 34.3451 | 34.344 | 33.958 | 35.0646 | 34.6816 | 35.283 | 35.9534 | 36.3561 | 32.3188 | 31.5053 | 93.1012 | 34.9653 | 32.7435 | 34.683 | 32.8213 | 32.8135 | 33.1674 | 34.425 | 33.9976 | 33.8385 | 37.0451 | 36.1545 | 33.1703 | 34.2717 | 36.1097 | 36.4215 | 37.2018 | 36.1389 | 32.8329 | 32.5137 | 34.3417 | 34.55 | 32.8689 | 34.6732 | 34.3948 | 34.4092 | 34.3201 | 34.2511 | 34.3811 | 33.8949 | 34.3178 | 36.1133 | 34.7821 | 36.5813 | 36.4935 | 33.1301 | 93.4327 | 93.553 | 93.3265
2022-09-08 06:30 | 8:40 | 24.0237 | 23.5705 | 27.1675 | 34.9033 | 34.3997 | 34.0155 | 34.4598 | 35.4931 | 36.5055 | 37.486 | 37.004 | 38.1805 | 34.3516 | 34.3444 | 33.9276 | 35.0993 | 34.693 | 35.2788 | 35.9637 | 36.3427 | 32.3698 | 31.4758 | 93.0952 | 35.0016 | 32.7365 | 34.6821 | 32.8414 | 32.842 | 33.1735 | 34.433 | 34.0333 | 33.8344 | 37.0712 | 36.1421 | 33.1645 | 34.2739 | 36.1344 | 36.4191 | 37.2027 | 36.1311 | 32.8383 | 32.4854 | 34.3418 | 34.5475 | 32.8872 | 34.6487 | 34.3971 | 34.4068 | 34.3068 | 34.2481 | 34.3827 | 33.9113 | 34.3201 | 36.1162 | 34.7709 | 36.5576 | 36.5077 | 33.1239 | 93.3478 | 93.526 | 93.2627
2022-09-08 06:30 | 8:40 | 24.6893 | 24.6085 | 27.7463 | 34.8716 | 34.3953 | 34.0188 | 34.4385 | 35.5045 | 36.5011 | 37.509 | 36.983 | 38.1903 | 34.3424 | 34.3359 | 33.9658 | 35.0977 | 34.6851 | 35.2684 | 35.9439 | 36.3382 | 32.3977 | 31.4924 | 93.0314 | 35.0864 | 32.7568 | 34.6706 | 32.8352 | 32.8249 | 33.1642 | 34.4273 | 34.0335 | 33.8258 | 37.0791 | 36.1481 | 33.1854 | 34.2854 | 36.1545 | 36.4111 | 37.2224 | 36.1391 | 32.8339 | 32.5097 | 34.3366 | 34.5275 | 32.8835 | 34.662 | 34.3993 | 34.42 | 34.3392 | 34.2468 | 34.3788 | 33.8936 | 34.3068 | 36.1107 | 34.7826 | 36.557 | 36.4911 | 33.1349 | 93.2201 | 93.4315 | 93.2506
2022-09-08 06:30 | 8:40 | 25.2977 | 25.4914 | 28.2219 | 34.9814 | 34.3881 | 34.0345 | 34.4368 | 35.4782 | 36.5042 | 37.5124 | 36.9997 | 38.2199 | 34.3396 | 34.3496 | 33.9422 | 35.0879 | 34.684 | 35.2769 | 35.9677 | 36.3522 | 32.4259 | 31.5115 | 92.903 | 35.0479 | 32.7539 | 34.694 | 32.8223 | 32.8184 | 33.1614 | 34.4244 | 34.0236 | 33.8289 | 37.071 | 36.1479 | 33.1781 | 34.2661 | 36.1421 | 36.4387 | 37.2224 | 36.1097 | 32.8524 | 32.4766 | 34.3399 | 34.5475 | 32.8696 | 34.6666 | 34.3896 | 34.4177 | 34.3227 | 34.261 | 34.3685 | 33.8753 | 34.3392 | 36.1118 | 34.7763 | 36.5599 | 36.4992 | 33.1213 | 93.2113 | 93.3135 | 93.2313
2022-09-08 06:30 | 8:40 | 25.8108 | 26.2961 | 28.5954 | 35.0787 | 34.3895 | 34.0482 | 34.4599 | 35.5028 | 36.5107 | 37.5124 | 37.0058 | 38.192 | 34.3479 | 34.349 | 33.9559 | 35.0782 | 34.7027 | 35.2879 | 35.9648 | 36.3503 | 32.5055 | 31.5114 | 92.8154 | 35.0586 | 32.7495 | 34.6807 | 32.8329 | 32.8194 | 33.1703 | 34.464 | 34.0304 | 33.8351 | 37.0661 | 36.154 | 33.1652 | 34.2751 | 36.1481 | 36.4077 | 37.2161 | 36.1344 | 32.8391 | 32.5149 | 34.362 | 34.5557 | 32.9192 | 34.6702 | 34.4007 | 34.4024 | 34.3351 | 34.2557 | 34.3588 | 33.9084 | 34.3227 | 36.1293 | 34.7918 | 36.5682 | 36.5112 | 33.1375 | 93.1121 | 93.2749 | 93.1949
2022-09-08 06:30 | 8:40 | 27.2161 | 20.3369 | 26.6828 | 34.894 | 34.3994 | 34.0441 | 34.4641 | 35.5027 | 36.5011 | 37.5111 | 37.0067 | 38.2011 | 34.3382 | 34.3373 | 33.9727 | 35.0984 | 34.6972 | 35.2956 | 35.9797 | 36.3512 | 32.7155 | 31.5231 | 92.684 | 35.0649 | 32.7717 | 34.6911 | 32.8383 | 32.8218 | 33.1645 | 34.4325 | 34.0249 | 33.8556 | 37.0693 | 36.1638 | 33.1686 | 34.2889 | 36.1479 | 36.4304 | 37.221 | 36.1545 | 32.8552 | 32.5067 | 34.3717 | 34.5697 | 32.909 | 34.6651 | 34.4009 | 34.4244 | 34.3438 | 34.2413 | 34.3591 | 33.9095 | 34.3351 | 36.1391 | 34.7874 | 36.5701 | 36.5046 | 33.1359 | 92.9219 | 93.1878 | 92.9496
2022-09-08 06:30 | 8:40 | 27.9969 | 24.9837 | 27.2211 | 34.868 | 34.4104 | 34.0382 | 34.4675 | 35.4935 | 36.5021 | 37.5163 | 37.0183 | 38.1978 | 34.3254 | 34.3445 | 33.9446 | 35.0994 | 34.6976 | 35.3075 | 35.9916 | 36.343 | 32.7885 | 31.531 | 92.692 | 35.0865 | 32.7676 | 34.686 | 32.8339 | 32.8309 | 33.1854 | 34.4264 | 34.021 | 33.8241 | 37.0851 | 36.1394 | 33.182 | 34.2968 | 36.154 | 36.4325 | 37.2092 | 36.1421 | 32.8503 | 32.5283 | 34.3735 | 34.5657 | 32.9218 | 34.6731 | 34.4088 | 34.4303 | 34.332 | 34.2545 | 34.3635 | 33.9085 | 34.3438 | 36.1466 | 34.7917 | 36.5789 | 36.5063 | 33.1382 | 92.868 | 93.091 | 93.0046
2022-09-08 06:31 | 8:40 | 30.7581 | 29.1285 | 28.7782 | 35.0603 | 34.41 | 34.0416 | 34.4817 | 35.499 | 36.5161 | 37.516 | 37.0154 | 38.2315 | 34.3443 | 34.315 | 33.9593 | 35.092 | 34.6921 | 35.2896 | 35.9766 | 36.3432 | 32.8615 | 31.9876 | 92.6804 | 35.0967 | 32.7793 | 34.7042 | 32.8524 | 32.8382 | 33.1781 | 34.4353 | 34.0465 | 33.8421 | 37.0769 | 36.1515 | 33.1711 | 34.2957 | 36.1638 | 36.4155 | 37.2287 | 36.1481 | 32.8349 | 32.5087 | 34.3798 | 34.5808 | 32.9399 | 34.6689 | 34.4076 | 34.3986 | 34.3407 | 34.2747 | 34.3685 | 33.9107 | 34.332 | 36.1278 | 34.7944 | 36.5612 | 36.513 | 33.1553 | 92.8687 | 93.1132 | 92.946
2022-09-08 06:31 | 8:41 | 32.1534 | 29.6736 | 29.7135 | 35.1873 | 34.4086 | 34.0658 | 34.5049 | 35.5095 | 36.5219 | 37.5209 | 37.0064 | 38.2024 | 34.3375 | 34.341 | 33.957 | 35.1151 | 34.6962 | 35.3048 | 35.9913 | 36.347 | 33.2319 | 32.5982 | 92.6046 | 35.163 | 32.7618 | 34.7064 | 32.8391 | 32.8302 | 33.1652 | 34.4408 | 34.0259 | 33.8592 | 37.0702 | 36.1592 | 33.187 | 34.2843 | 36.1394 | 36.4224 | 37.2052 | 36.1479 | 32.8628 | 32.5375 | 34.381 | 34.5794 | 32.932 | 34.6886 | 34.4104 | 34.4138 | 34.3383 | 34.2582 | 34.3706 | 33.9209 | 34.3407 | 36.1367 | 34.7814 | 36.5716 | 36.5224 | 33.1518 | 92.7511 | 92.9693 | 92.8874
2022-09-08 06:31 | 8:41 | 33.118 | 29.8014 | 30.2053 | 35.3273 | 34.3999 | 34.053 | 34.5052 | 35.5096 | 36.5261 | 37.5384 | 37.0169 | 38.2131 | 34.3347 | 34.3511 | 33.9673 | 35.1078 | 34.7074 | 35.2977 | 36.0015 | 36.3469 | 33.7973 | 32.8061 | 92.5186 | 35.1546 | 32.7829 | 34.6874 | 32.8552 | 32.8428 | 33.1686 | 34.4251 | 34.0524 | 33.8318 | 37.073 | 36.1632 | 33.1739 | 34.3049 | 36.1515 | 36.433 | 37.2087 | 36.154 | 32.8489 | 32.5381 | 34.3797 | 34.5777 | 32.9443 | 34.6795 | 34.3919 | 34.4144 | 34.3452 | 34.2571 | 34.341 | 33.9288 | 34.3383 | 36.1435 | 34.7918 | 36.565 | 36.5084 | 33.1412 | 92.6795 | 92.8408 | 92.7476
2022-09-08 06:31 | 8:41 | 33.7992 | 29.9301 | 30.587 | 35.3346 | 34.4051 | 34.0684 | 34.5266 | 35.5012 | 36.5109 | 37.5452 | 37.0099 | 38.2198 | 34.313 | 34.3333 | 33.9634 | 35.1057 | 34.6968 | 35.3192 | 36.0174 | 36.3451 | 34.2503 | 32.6516 | 92.5175 | 35.1228 | 32.7746 | 34.6927 | 32.8503 | 32.8365 | 33.182 | 34.4394 | 34.0449 | 33.8289 | 37.0853 | 36.1401 | 33.1725 | 34.2977 | 36.1592 | 36.4374 | 37.214 | 36.1638 | 32.8664 | 32.5334 | 34.4016 | 34.5945 | 32.9476 | 34.6868 | 34.415 | 34.3916 | 34.3527 | 34.2629 | 34.3583 | 33.9074 | 34.3452 | 36.1483 | 34.7979 | 36.5624 | 36.5395 | 33.18 | 92.5813 | 92.7561 | 92.6662
2022-09-08 06:31 | 8:41 | 34.0519 | 30.0656 | 30.8347 | 35.4108 | 34.408 | 34.0691 | 34.5409 | 35.5294 | 36.5186 | 37.5317 | 37.0111 | 38.2268 | 34.3244 | 34.3394 | 33.9629 | 35.111 | 34.6822 | 35.3011 | 36.0012 | 36.3799 | 34.3887 | 32.4631 | 92.5154 | 35.1748 | 32.7697 | 34.6882 | 32.8349 | 32.8345 | 33.1711 | 34.4297 | 34.0665 | 33.8562 | 37.0987 | 36.1404 | 33.1747 | 34.3115 | 36.1632 | 36.4222 | 37.2171 | 36.1394 | 32.8576 | 32.5364 | 34.3889 | 34.5971 | 32.9662 | 34.7065 | 34.4018 | 34.3969 | 34.3428 | 34.2689 | 34.3644 | 33.9431 | 34.3527 | 36.1476 | 34.793 | 36.5632 | 36.5214 | 33.1664 | 92.4282 | 92.6222 | 92.5567
2022-09-08 06:31 | 8:41 | 34.083 | 30.1837 | 31.066 | 35.4789 | 34.3934 | 34.0886 | 34.548 | 35.52 | 36.5211 | 37.5477 | 37.0042 | 38.2336 | 34.3288 | 34.3388 | 33.9877 | 35.1216 | 34.6924 | 35.334 | 36.0128 | 36.3846 | 34.4113 | 32.3132 | 92.376 | 35.2393 | 32.7872 | 34.7157 | 32.8628 | 32.8603 | 33.187 | 34.4364 | 34.0389 | 33.8444 | 37.082 | 36.1308 | 33.1677 | 34.3207 | 36.1401 | 36.4337 | 37.2257 | 36.1515 | 32.8576 | 32.547 | 34.4193 | 34.6183 | 32.9701 | 34.7049 | 34.3877 | 34.4054 | 34.3482 | 34.2512 | 34.3421 | 33.9313 | 34.3428 | 36.1421 | 34.7892 | 36.5858 | 36.5221 | 33.1683 | 92.3629 | 92.4797 | 92.5572
2022-09-08 06:32 | 8:42 | 33.9716 | 30.3189 | 31.0834 | 35.4964 | 34.4028 | 34.1013 | 34.5487 | 35.5193 | 36.5307 | 37.5422 | 37.0145 | 38.22 | 34.3239 | 34.326 | 33.9811 | 35.1131 | 34.6948 | 35.321 | 36.0283 | 36.3705 | 34.409 | 32.178 | 92.2818 | 35.2553 | 32.785 | 34.7006 | 32.8489 | 32.8543 | 33.1739 | 34.4404 | 34.0346 | 33.8458 | 37.0874 | 36.1443 | 33.1866 | 34.3075 | 36.1404 | 36.4383 | 37.2166 | 36.1592 | 32.8694 | 32.5519 | 34.4093 | 34.6226 | 32.9904 | 34.7016 | 34.4101 | 34.39 | 34.3473 | 34.28 | 34.3474 | 33.9195 | 34.3482 | 36.1421 | 34.794 | 36.5764 | 36.5296 | 33.1798 | 92.2567 | 92.36 | 92.494
2022-09-08 06:32 | 8:42 | 32.638 | 30.4292 | 31.0839 | 35.5826 | 34.3976 | 34.0805 | 34.5324 | 35.5315 | 36.5138 | 37.5422 | 37.0162 | 38.2191 | 34.3225 | 34.3241 | 33.975 | 35.1191 | 34.6991 | 35.331 | 36.0337 | 36.3783 | 34.4303 | 32.1101 | 92.1872 | 35.2422 | 32.7825 | 34.6935 | 32.8664 | 32.8517 | 33.1725 | 34.4396 | 34.06 | 33.8415 | 37.0919 | 36.1475 | 33.191 | 34.3212 | 36.1308 | 36.4424 | 37.2237 | 36.1632 | 32.8614 | 32.5574 | 34.4171 | 34.6168 | 32.9777 | 34.7166 | 34.4087 | 34.3894 | 34.3667 | 34.251 | 34.3342 | 33.9424 | 34.3473 | 36.1569 | 34.8065 | 36.5799 | 36.5212 | 33.1877 | 92.1207 | 92.2705 | 92.3841
2022-09-08 06:32 | 8:42 | 31.8732 | 30.5104 | 31.1883 | 35.7031 | 34.396 | 34.085 | 34.4621 | 35.507 | 36.523 | 37.5488 | 37.013 | 38.2202 | 34.3261 | 34.3041 | 33.9784 | 35.1075 | 34.6949 | 35.3139 | 36.0375 | 36.3512 | 34.4579 | 32.1003 | 92.0891 | 35.3335 | 32.778 | 34.6928 | 32.8576 | 32.8598 | 33.1747 | 34.4574 | 34.0434 | 33.8429 | 37.0932 | 36.1726 | 33.1969 | 34.3141 | 36.1443 | 36.4396 | 37.2291 | 36.1401 | 32.8657 | 32.5566 | 34.4241 | 34.6127 | 32.9711 | 34.7223 | 34.4137 | 34.389 | 34.3587 | 34.2677 | 34.3607 | 33.9336 | 34.3667 | 36.1458 | 34.8006 | 36.5504 | 36.5293 | 33.1723 | 91.9567 | 92.1547 | 92.2068
2022-09-08 06:32 | 8:42 | 31.6643 | 30.5998 | 31.2675 | 35.7243 | 34.3892 | 34.0854 | 34.4935 | 35.533 | 36.5196 | 37.5493 | 37.0127 | 38.2228 | 34.3142 | 34.323 | 33.9733 | 35.1012 | 34.708 | 35.3351 | 36.0404 | 36.3606 | 34.5408 | 32.0839 | 92.0539 | 35.2909 | 32.7903 | 34.6962 | 32.8576 | 32.8428 | 33.1677 | 34.4236 | 34.0526 | 33.8484 | 37.0913 | 36.1364 | 33.1918 | 34.3253 | 36.1475 | 36.4546 | 37.2316 | 36.1404 | 32.8715 | 32.5715 | 34.4528 | 34.6363 | 32.9948 | 34.7238 | 34.4213 | 34.3754 | 34.3461 | 34.2712 | 34.3311 | 33.9439 | 34.3587 | 36.1468 | 34.7959 | 36.5655 | 36.5489 | 33.1696 | 91.7906 | 92.0111 | 92.2493
2022-09-08 06:32 | 8:42 | 31.6257 | 30.656 | 31.3245 | 35.7393 | 34.3887 | 34.1007 | 34.5384 | 35.5514 | 36.5058 | 37.549 | 37.0187 | 38.2228 | 34.3062 | 34.3222 | 33.979 | 35.116 | 34.6956 | 35.3323 | 36.0654 | 36.3706 | 34.5813 | 32.0784 | 91.8873 | 35.3346 | 32.7942 | 34.6982 | 32.8694 | 32.8527 | 33.1866 | 34.4379 | 34.0553 | 33.8552 | 37.079 | 36.1599 | 33.1886 | 34.3198 | 36.1726 | 36.4504 | 37.2431 | 36.1308 | 32.8722 | 32.5569 | 34.4199 | 34.6312 | 32.9858 | 34.733 | 34.4203 | 34.4017 | 34.3722 | 34.2596 | 34.3288 | 33.9236 | 34.3461 | 36.1446 | 34.7811 | 36.5639 | 36.5305 | 33.2262 | 91.7242 | 91.859 | 92.1133
2022-09-08 06:32 | 8:42 | 31.6239 | 30.7052 | 31.3713 | 35.7463 | 34.3996 | 34.0919 | 34.5572 | 35.5384 | 36.5238 | 37.5545 | 37.0274 | 38.2333 | 34.2966 | 34.3071 | 33.9793 | 35.1187 | 34.6932 | 35.3383 | 36.0445 | 36.3899 | 34.6457 | 32.0838 | 91.7215 | 35.3184 | 32.8124 | 34.7169 | 32.8614 | 32.8583 | 33.191 | 34.4289 | 34.0594 | 33.8512 | 37.0893 | 36.1362 | 33.2021 | 34.3214 | 36.1364 | 36.4432 | 37.2416 | 36.1443 | 32.8723 | 32.579 | 34.4419 | 34.66 | 33.014 | 34.7508 | 34.4138 | 34.391 | 34.3576 | 34.265 | 34.345 | 33.9638 | 34.3722 | 36.1637 | 34.8005 | 36.5652 | 36.5188 | 33.2013 | 91.593 | 91.7284 | 92.0583
2022-09-08 06:33 | 8:42 | 31.3786 | 30.7377 | 31.452 | 35.7578 | 34.3967 | 34.0884 | 34.5132 | 35.5369 | 36.5275 | 37.5605 | 37.0033 | 38.2251 | 34.2999 | 34.3169 | 33.9882 | 35.1374 | 34.7095 | 35.3233 | 36.0482 | 36.373 | 34.7099 | 32.1082 | 91.7086 | 35.358 | 32.8095 | 34.7002 | 32.8657 | 32.8689 | 33.1969 | 34.4559 | 34.0379 | 33.847 | 37.0705 | 36.1452 | 33.1904 | 34.3066 | 36.1599 | 36.4448 | 37.2265 | 36.1475 | 32.869 | 32.5794 | 34.4493 | 34.6598 | 32.9906 | 34.741 | 34.4019 | 34.3897 | 34.3737 | 34.2678 | 34.3416 | 33.9378 | 34.3576 | 36.1519 | 34.7943 | 36.5768 | 36.5236 | 33.2166 | 91.4768 | 91.6248 | 91.9539
2022-09-08 06:33 | 8:43 | 31.5605 | 30.7937 | 31.4997 | 35.7241 | 34.4045 | 34.0835 | 34.4707 | 35.5356 | 36.5208 | 37.5834 | 37.0172 | 38.227 | 34.2922 | 34.3129 | 33.9868 | 35.1366 | 34.7041 | 35.3402 | 36.0882 | 36.3985 | 34.7799 | 32.1212 | 91.6846 | 35.3708 | 32.8093 | 34.6954 | 32.8715 | 32.8424 | 33.1918 | 34.4586 | 34.0507 | 33.8521 | 37.0802 | 36.1538 | 33.1957 | 34.3105 | 36.1362 | 36.447 | 37.2471 | 36.1726 | 32.8761 | 32.6116 | 34.4878 | 34.6825 | 33.0171 | 34.7555 | 34.4181 | 34.4178 | 34.3758 | 34.2611 | 34.3332 | 33.9469 | 34.3737 | 36.1762 | 34.8007 | 36.5696 | 36.5287 | 33.2114 | 91.4176 | 91.5797 | 91.9164
2022-09-08 06:33 | 8:43 | 31.5613 | 30.8235 | 31.5641 | 35.8963 | 34.393 | 34.0921 | 34.4899 | 35.5573 | 36.5308 | 37.5837 | 37.0135 | 38.2152 | 34.2822 | 34.3319 | 33.9916 | 35.1149 | 34.7057 | 35.3429 | 36.0622 | 36.4001 | 34.8671 | 32.1651 | 91.68 | 35.3905 | 32.8049 | 34.7026 | 32.8722 | 32.8627 | 33.1886 | 34.4648 | 34.0394 | 33.8641 | 37.0971 | 36.156 | 33.189 | 34.2989 | 36.1452 | 36.4386 | 37.2649 | 36.1364 | 32.874 | 32.5982 | 34.472 | 34.6706 | 33.0179 | 34.7413 | 34.4279 | 34.3883 | 34.3654 | 34.2842 | 34.3311 | 33.964 | 34.3758 | 36.1638 | 34.7809 | 36.5736 | 36.5128 | 33.2108 | 91.3899 | 91.5434 | 91.9149
2022-09-08 06:33 | 8:43 | 31.3467 | 30.8851 | 31.6325 | 35.7917 | 34.3789 | 34.1106 | 34.5646 | 35.5624 | 36.5293 | 37.5915 | 37.029 | 38.248 | 34.294 | 34.2932 | 34.0049 | 35.1096 | 34.6997 | 35.354 | 36.0792 | 36.4052 | 35.0957 | 32.3713 | 91.6202 | 35.4008 | 32.828 | 34.6948 | 32.8723 | 32.8759 | 33.2021 | 34.4566 | 34.0493 | 33.8688 | 37.0915 | 36.147 | 33.196 | 34.3214 | 36.1538 | 36.4456 | 37.2363 | 36.1599 | 32.87 | 32.6094 | 34.4648 | 34.6801 | 33.0311 | 34.7649 | 34.4259 | 34.3888 | 34.3736 | 34.2468 | 34.3335 | 33.9582 | 34.3654 | 36.1711 | 34.7864 | 36.5742 | 36.5548 | 33.2236 | 91.4772 | 91.6365 | 91.9615
2022-09-08 06:33 | 8:43 | 31.4969 | 30.9185 | 31.7025 | 36.0035 | 34.4024 | 34.0967 | 34.5427 | 35.5568 | 36.531 | 37.5749 | 37.0212 | 38.2371 | 34.2755 | 34.3274 | 34.0015 | 35.1207 | 34.7021 | 35.3404 | 36.0775 | 36.4064 | 35.254 | 32.4007 | 91.7511 | 35.4019 | 32.8208 | 34.6959 | 32.869 | 32.8587 | 33.1904 | 34.4484 | 34.053 | 33.8632 | 37.0954 | 36.1471 | 33.2011 | 34.326 | 36.156 | 36.4494 | 37.2347 | 36.1362 | 32.8642 | 32.6099 | 34.4673 | 34.6772 | 33.0225 | 34.7473 | 34.429 | 34.3921 | 34.365 | 34.2913 | 34.3579 | 33.9522 | 34.3736 | 36.1863 | 34.7806 | 36.5695 | 36.5524 | 33.2423 | 91.6217 | 91.7811 | 92.1072
2022-09-08 06:33 | 8:43 | 31.6048 | 30.949 | 31.7661 | 35.9982 | 34.3758 | 34.1019 | 34.5451 | 35.5431 | 36.5448 | 37.6002 | 37.0147 | 38.2195 | 34.2824 | 34.3211 | 34.0042 | 35.1092 | 34.7084 | 35.3612 | 36.0835 | 36.4185 | 35.3505 | 32.374 | 91.842 | 35.443 | 32.8095 | 34.7116 | 32.8761 | 32.864 | 33.1957 | 34.4692 | 34.0316 | 33.851 | 37.0979 | 36.1458 | 33.2114 | 34.3139 | 36.147 | 36.4513 | 37.2535 | 36.1452 | 32.8516 | 32.6243 | 34.4849 | 34.6975 | 33.0509 | 34.7707 | 34.4305 | 34.3827 | 34.3742 | 34.2656 | 34.3336 | 33.9539 | 34.365 | 36.1851 | 34.7745 | 36.5767 | 36.5334 | 33.2391 | 91.6943 | 91.9327 | 92.098
2022-09-08 06:34 | 8:44 | 31.6238 | 30.98 | 31.8061 | 36.0197 | 34.3835 | 34.0908 | 34.5015 | 35.5581 | 36.54 | 37.5817 | 36.9963 | 38.2167 | 34.2851 | 34.2981 | 33.9984 | 35.1129 | 34.7049 | 35.3466 | 36.0803 | 36.4 | 35.4268 | 32.3533 | 91.7797 | 35.471 | 32.8359 | 34.7036 | 32.874 | 32.8668 | 33.189 | 34.455 | 34.0264 | 33.8524 | 37.088 | 36.1307 | 33.2067 | 34.3264 | 36.1471 | 36.4292 | 37.2688 | 36.1538 | 32.8685 | 32.6176 | 34.4857 | 34.7107 | 33.0424 | 34.7569 | 34.4485 | 34.3639 | 34.3771 | 34.2704 | 34.344 | 33.9434 | 34.3742 | 36.1663 | 34.7788 | 36.5676 | 36.5473 | 33.2622 | 91.8475 | 92.1172 | 92.2083
2022-09-08 06:34 | 8:44 | 31.6771 | 31.0423 | 31.8326 | 36.0369 | 34.394 | 34.1167 | 34.5556 | 35.5412 | 36.5475 | 37.6108 | 37.0096 | 38.2316 | 34.3019 | 34.3031 | 33.9835 | 35.1191 | 34.6967 | 35.3484 | 36.0966 | 36.3983 | 35.4723 | 32.3858 | 92.1466 | 35.434 | 32.8433 | 34.7032 | 32.87 | 32.8515 | 33.196 | 34.465 | 34.0271 | 33.8601 | 37.1002 | 36.1465 | 33.2061 | 34.3254 | 36.1458 | 36.4589 | 37.2564 | 36.156 | 32.8586 | 32.6366 | 34.4957 | 34.7137 | 33.0703 | 34.7761 | 34.4344 | 34.3606 | 34.3799 | 34.2802 | 34.3444 | 33.9757 | 34.3771 | 36.1979 | 34.7908 | 36.5852 | 36.5473 | 33.2571 | 92.1304 | 92.2648 | 92.4503
2022-09-08 06:34 | 8:44 | 31.5678 | 31.065 | 31.8823 | 35.9725 | 34.3846 | 34.0986 | 34.5766 | 35.5618 | 36.5449 | 37.6124 | 37.0138 | 38.2344 | 34.2693 | 34.3331 | 33.9961 | 35.1013 | 34.7022 | 35.3755 | 36.0994 | 36.4048 | 35.3953 | 32.4192 | 92.3345 | 35.5237 | 32.8409 | 34.7078 | 32.8642 | 32.8627 | 33.2011 | 34.4804 | 34.0503 | 33.8726 | 37.0966 | 36.1655 | 33.203 | 34.3134 | 36.1307 | 36.4492 | 37.259 | 36.147 | 32.8681 | 32.6335 | 34.5157 | 34.723 | 33.0808 | 34.7806 | 34.4402 | 34.3735 | 34.3882 | 34.2751 | 34.3359 | 33.9744 | 34.3799 | 36.1761 | 34.7975 | 36.5882 | 36.5578 | 33.2639 | 92.305 | 92.4708 | 92.5323
2022-09-08 06:34 | 8:44 | 31.5374 | 31.1167 | 31.9216 | 36.0809 | 34.3948 | 34.0971 | 34.5659 | 35.5501 | 36.5448 | 37.6118 | 37.0178 | 38.2516 | 34.2663 | 34.3046 | 33.9947 | 35.1117 | 34.705 | 35.348 | 36.1028 | 36.4112 | 35.4288 | 32.4493 | 92.3527 | 35.4912 | 32.848 | 34.7047 | 32.8516 | 32.8654 | 33.2114 | 34.4762 | 34.0373 | 33.85 | 37.0876 | 36.1546 | 33.2298 | 34.3136 | 36.1465 | 36.4515 | 37.2779 | 36.1471 | 32.8747 | 32.6321 | 34.5164 | 34.7287 | 33.0669 | 34.7687 | 34.4501 | 34.3815 | 34.3901 | 34.2851 | 34.3496 | 33.9873 | 34.3882 | 36.1895 | 34.7745 | 36.5804 | 36.5629 | 33.2583 | 92.5183 | 92.6432 | 92.6448
2022-09-08 06:34 | 8:44 | 31.5069 | 31.1521 | 31.9598 | 36.0698 | 34.3811 | 34.0972 | 34.5637 | 35.5621 | 36.5189 | 37.5864 | 37.0043 | 38.2234 | 34.2629 | 34.3074 | 33.9959 | 35.1123 | 34.7127 | 35.3571 | 36.0979 | 36.4131 | 35.4764 | 32.5077 | 92.4527 | 35.4612 | 32.8345 | 34.7065 | 32.8685 | 32.882 | 33.2067 | 34.473 | 34.0243 | 33.8383 | 37.1052 | 36.1024 | 33.2073 | 34.3071 | 36.1655 | 36.4487 | 37.2745 | 36.1458 | 32.8734 | 32.6474 | 34.517 | 34.7217 | 33.0814 | 34.7845 | 34.4605 | 34.3729 | 34.3811 | 34.2754 | 34.349 | 33.9804 | 34.3901 | 36.1844 | 34.7926 | 36.5647 | 36.5373 | 33.2592 | 92.6795 | 92.7353 | 92.7408
2022-09-08 06:34 | 8:44 | 32.063 | 31.1929 | 32.0272 | 36.1203 | 34.3827 | 34.0967 | 34.5339 | 35.558 | 36.5332 | 37.5895 | 36.9956 | 38.2119 | 34.2881 | 34.31 | 34.0108 | 35.1225 | 34.7007 | 35.3621 | 36.1114 | 36.4085 | 35.4824 | 32.4978 | 92.3904 | 35.569 | 32.8416 | 34.6882 | 32.8586 | 32.865 | 33.2061 | 34.4755 | 34.049 | 33.8499 | 37.1044 | 36.1439 | 33.2094 | 34.3026 | 36.1546 | 36.4382 | 37.2651 | 36.1307 | 32.852 | 32.6356 | 34.5236 | 34.7333 | 33.071 | 34.7905 | 34.4474 | 34.3434 | 34.3834 | 34.2948 | 34.3373 | 33.9927 | 34.3811 | 36.167 | 34.7951 | 36.5699 | 36.545 | 33.2526 | 92.7749 | 92.9072 | 92.7814
2022-09-08 06:35 | 8:44 | 31.9182 | 30.9744 | 32.0365 | 36.1925 | 34.3788 | 34.0898 | 34.5621 | 35.5596 | 36.5241 | 37.6041 | 37.0063 | 38.2306 | 34.2826 | 34.3083 | 33.9905 | 35.1046 | 34.6992 | 35.3465 | 36.095 | 36.4286 | 33.5752 | 32.0688 | 92.4869 | 35.5254 | 32.8332 | 34.6991 | 32.8681 | 32.86 | 33.203 | 34.4747 | 34.0412 | 33.8557 | 37.0716 | 36.1415 | 33.204 | 34.3267 | 36.1024 | 36.4288 | 37.2807 | 36.1465 | 32.854 | 32.6612 | 34.5317 | 34.7494 | 33.0841 | 34.777 | 34.4614 | 34.3884 | 34.3804 | 34.2815 | 34.3445 | 34.0072 | 34.3834 | 36.1728 | 34.7822 | 36.607 | 36.5617 | 33.2884 | 92.9825 | 93.0935 | 92.8496
2022-09-08 06:35 | 8:45 | 30.0764 | 30.6387 | 31.7911 | 36.0936 | 34.3685 | 34.0979 | 34.5647 | 35.5489 | 36.5395 | 37.6106 | 37.0056 | 38.2348 | 34.2842 | 34.3052 | 34.0073 | 35.1023 | 34.6957 | 35.3632 | 36.1082 | 36.4194 | 29.3105 | 30.077 | 92.6849 | 35.4594 | 32.849 | 34.7107 | 32.8747 | 32.8584 | 33.2298 | 34.483 | 34.0261 | 33.8325 | 37.1091 | 36.1665 | 33.2061 | 34.2989 | 36.1439 | 36.466 | 37.2777 | 36.1655 | 32.8819 | 32.669 | 34.5259 | 34.7511 | 33.1143 | 34.7831 | 34.4744 | 34.3738 | 34.3854 | 34.2925 | 34.315 | 33.9729 | 34.3804 | 36.1948 | 34.8023 | 36.5738 | 36.5477 | 33.2867 | 93.1673 | 93.2647 | 93.0516
2022-09-08 06:35 | 8:45 | 31.1182 | 26.06 | 31.7355 | 36.1788 | 34.3588 | 34.0871 | 34.5586 | 35.5709 | 36.5482 | 37.6005 | 37.0068 | 38.2382 | 34.3017 | 34.3101 | 34.0068 | 35.0869 | 34.6755 | 35.352 | 36.1114 | 36.42 | 28.5973 | 28.1717 | 92.7802 | 35.3546 | 32.8504 | 34.7052 | 32.8734 | 32.8717 | 33.2073 | 34.4862 | 34.0212 | 33.8521 | 37.1088 | 36.1703 | 33.219 | 34.2982 | 36.1415 | 36.4438 | 37.2818 | 36.1546 | 32.8649 | 32.6546 | 34.5453 | 34.7473 | 33.0756 | 34.7774 | 34.4566 | 34.3652 | 34.387 | 34.2835 | 34.341 | 33.9905 | 34.3854 | 36.1819 | 34.7749 | 36.5675 | 36.5506 | 33.2872 | 93.3923 | 93.4597 | 93.1222
2022-09-08 06:35 | 8:45 | 31.3819 | 25.8813 | 31.8022 | 36.2338 | 34.3591 | 34.0912 | 34.4966 | 35.548 | 36.5376 | 37.6107 | 36.9747 | 38.2182 | 34.2799 | 34.2874 | 33.9871 | 35.0996 | 34.6908 | 35.3443 | 36.097 | 36.4211 | 27.5221 | 26.9583 | 92.8097 | 35.238 | 32.8447 | 34.6991 | 32.852 | 32.8452 | 33.2094 | 34.4818 | 34.0172 | 33.8436 | 37.058 | 36.1522 | 33.1967 | 34.2983 | 36.1665 | 36.4365 | 37.2756 | 36.1024 | 32.8637 | 32.6709 | 34.5411 | 34.7529 | 33.1006 | 34.7835 | 34.4636 | 34.3593 | 34.3774 | 34.2959 | 34.3511 | 34.0039 | 34.387 | 36.1987 | 34.7654 | 36.5783 | 36.5618 | 33.2502 | 93.6108 | 93.6584 | 93.1743
2022-09-08 06:35 | 8:45 | 31.4341 | 26.1649 | 31.8689 | 36.1547 | 34.3635 | 34.1062 | 34.5354 | 35.5375 | 36.554 | 37.599 | 36.9992 | 38.2114 | 34.2571 | 34.2824 | 34.0229 | 35.0916 | 34.6981 | 35.376 | 36.1163 | 36.4241 | 28.1265 | 26.0113 | 92.7586 | 35.1684 | 32.8382 | 34.7079 | 32.854 | 32.8792 | 33.204 | 34.4798 | 34.0215 | 33.8452 | 37.0789 | 36.1556 | 33.2328 | 34.2844 | 36.1703 | 36.4578 | 37.2898 | 36.1439 | 32.8606 | 32.6708 | 34.5529 | 34.7772 | 33.1067 | 34.7978 | 34.4865 | 34.3494 | 34.3795 | 34.28 | 34.3333 | 34.0029 | 34.3774 | 36.1853 | 34.76 | 36.5615 | 36.5503 | 33.2774 | 93.7299 | 93.8898 | 93.3152
2022-09-08 06:35 | 8:45 | 31.4741 | 26.6791 | 31.9323 | 36.3188 | 34.3685 | 34.1168 | 34.572 | 35.5492 | 36.5368 | 37.6047 | 37.0045 | 38.2137 | 34.2722 | 34.2803 | 34.0177 | 35.0858 | 34.7018 | 35.3618 | 36.114 | 36.4395 | 28.5563 | 24.9624 | 92.8438 | 35.0781 | 32.8374 | 34.6993 | 32.8819 | 32.8718 | 33.2061 | 34.4751 | 34.0082 | 33.8525 | 37.0881 | 36.1558 | 33.1976 | 34.2887 | 36.1522 | 36.4485 | 37.2794 | 36.1415 | 32.8748 | 32.6642 | 34.5224 | 34.7657 | 33.0975 | 34.8125 | 34.4951 | 34.3707 | 34.372 | 34.271 | 34.3394 | 33.9885 | 34.3795 | 36.1944 | 34.773 | 36.5773 | 36.5438 | 33.2639 | 93.933 | 94.057 | 93.4272
2022-09-08 06:36 | 8:46 | 31.4692 | 27.3131 | 31.9833 | 36.3199 | 34.3706 | 34.0994 | 34.5643 | 35.5568 | 36.5338 | 37.6161 | 36.9933 | 38.2229 | 34.2711 | 34.2928 | 33.9912 | 35.0979 | 34.699 | 35.3652 | 36.109 | 36.4306 | 28.4783 | 24.1729 | 93.015 | 34.9463 | 32.8332 | 34.7084 | 32.8649 | 32.8566 | 33.219 | 34.4932 | 33.9985 | 33.8444 | 37.1029 | 36.1775 | 33.2069 | 34.2826 | 36.1556 | 36.4445 | 37.2937 | 36.1665 | 32.8558 | 32.6729 | 34.5208 | 34.7527 | 33.1072 | 34.7854 | 34.4804 | 34.3494 | 34.3821 | 34.2752 | 34.3388 | 34.0195 | 34.372 | 36.2098 | 34.7976 | 36.5707 | 36.5552 | 33.2595 | 94.1101 | 94.3186 | 93.5442
2022-09-08 06:36 | 8:46 | 31.5359 | 28.3731 | 32.0689 | 36.3571 | 34.341 | 34.0929 | 34.57 | 35.559 | 36.5393 | 37.5942 | 36.9973 | 38.1975 | 34.2737 | 34.3179 | 33.9997 | 35.0975 | 34.6877 | 35.3559 | 36.0904 | 36.4195 | 28.1431 | 23.6678 | 93.3533 | 34.8854 | 32.8317 | 34.6774 | 32.8637 | 32.8602 | 33.1967 | 34.4755 | 34.0129 | 33.8439 | 37.0629 | 36.1568 | 33.2003 | 34.2898 | 36.1558 | 36.44 | 37.292 | 36.1703 | 32.8635 | 32.6819 | 34.5435 | 34.7786 | 33.1272 | 34.7775 | 34.4792 | 34.354 | 34.3728 | 34.3047 | 34.326 | 34.0036 | 34.3821 | 36.1998 | 34.7652 | 36.5782 | 36.5395 | 33.2531 | 94.2859 | 94.4698 | 93.6522
2022-09-08 06:36 | 8:46 | 31.6031 | 29.2155 | 32.1122 | 36.2598 | 34.3583 | 34.0766 | 34.5782 | 35.5434 | 36.5359 | 37.6132 | 36.9757 | 38.1968 | 34.2811 | 34.285 | 33.9996 | 35.0921 | 34.7046 | 35.3708 | 36.1067 | 36.4146 | 27.7296 | 23.2183 | 93.4881 | 34.7643 | 32.8263 | 34.7013 | 32.8606 | 32.8655 | 33.2328 | 34.4883 | 34.0071 | 33.8324 | 37.0804 | 36.1687 | 33.2015 | 34.2961 | 36.1775 | 36.4344 | 37.2787 | 36.1522 | 32.8742 | 32.6492 | 34.551 | 34.7615 | 33.1319 | 34.788 | 34.4727 | 34.3477 | 34.3738 | 34.2929 | 34.3241 | 34.0092 | 34.3728 | 36.1985 | 34.7712 | 36.5717 | 36.5398 | 33.2429 | 94.4071 | 94.6418 | 93.9168
2022-09-08 06:36 | 8:46 | 31.7018 | 29.8082 | 32.1665 | 36.3905 | 34.3644 | 34.0971 | 34.5867 | 35.5464 | 36.5344 | 37.5996 | 36.9893 | 38.2137 | 34.2745 | 34.2998 | 34.0068 | 35.1027 | 34.691 | 35.3614 | 36.1236 | 36.4204 | 27.4208 | 22.8875 | 93.7629 | 34.812 | 32.813 | 34.7035 | 32.8748 | 32.8542 | 33.1976 | 34.5038 | 34.0238 | 33.8309 | 37.0973 | 36.1735 | 33.2153 | 34.3097 | 36.1568 | 36.434 | 37.3113 | 36.1556 | 32.8716 | 32.6764 | 34.55 | 34.7777 | 33.1058 | 34.788 | 34.4823 | 34.3478 | 34.3427 | 34.2865 | 34.3041 | 33.9975 | 34.3738 | 36.1781 | 34.7639 | 36.5576 | 36.5574 | 33.2603 | 94.5787 | 94.7599 | 93.9543
2022-09-08 06:36 | 8:46 | 31.787 | 30.217 | 32.226 | 36.4018 | 34.3421 | 34.0936 | 34.5769 | 35.5341 | 36.5498 | 37.6017 | 36.9858 | 38.228 | 34.2622 | 34.2824 | 34.0011 | 35.0902 | 34.6982 | 35.375 | 36.1067 | 36.4123 | 27.0423 | 22.5927 | 93.7607 | 34.6244 | 32.8366 | 34.7145 | 32.8558 | 32.8485 | 33.2069 | 34.4789 | 34.0131 | 33.8231 | 37.0751 | 36.164 | 33.1992 | 34.3146 | 36.1687 | 36.4296 | 37.2811 | 36.1558 | 32.8659 | 32.6968 | 34.5588 | 34.7712 | 33.1285 | 34.7956 | 34.493 | 34.3526 | 34.3797 | 34.2938 | 34.323 | 34.034 | 34.3427 | 36.1926 | 34.7586 | 36.5766 | 36.5259 | 33.2568 | 94.7826 | 94.8995 | 94.1089
2022-09-08 06:36 | 8:46 | 31.8292 | 30.4916 | 32.2661 | 36.486 | 34.3474 | 34.0803 | 34.598 | 35.5459 | 36.5489 | 37.6281 | 36.9835 | 38.2076 | 34.27 | 34.2983 | 33.9918 | 35.0772 | 34.7037 | 35.3622 | 36.115 | 36.4061 | 26.5988 | 22.371 | 93.9321 | 34.5841 | 32.818 | 34.6968 | 32.8635 | 32.8542 | 33.2003 | 34.4757 | 33.9941 | 33.8298 | 37.0981 | 36.1724 | 33.1889 | 34.2752 | 36.1735 | 36.4286 | 37.279 | 36.1775 | 32.871 | 32.6789 | 34.5509 | 34.7712 | 33.1003 | 34.7846 | 34.4885 | 34.3511 | 34.3911 | 34.2823 | 34.3222 | 34.0021 | 34.3797 | 36.1817 | 34.7652 | 36.568 | 36.5454 | 33.2503 | 94.886 | 94.9922 | 94.2082
2022-09-08 06:37 | 8:46 | 31.9002 | 30.6904 | 32.316 | 36.3428 | 34.3342 | 34.0828 | 34.6103 | 35.5359 | 36.517 | 37.6092 | 36.9868 | 38.2353 | 34.2511 | 34.2804 | 33.9977 | 35.0966 | 34.6818 | 35.3554 | 36.1185 | 36.412 | 26.0717 | 22.1532 | 93.8126 | 34.6199 | 32.8186 | 34.6981 | 32.8742 | 32.8617 | 33.2015 | 34.4657 | 33.9943 | 33.8463 | 37.0837 | 36.175 | 33.2059 | 34.2866 | 36.164 | 36.4329 | 37.3033 | 36.1568 | 32.8836 | 32.6981 | 34.5515 | 34.7619 | 33.1285 | 34.783 | 34.5082 | 34.3259 | 34.3755 | 34.2969 | 34.3071 | 33.9965 | 34.3911 | 36.2071 | 34.7892 | 36.5606 | 36.5268 | 33.2446 | 94.9524 | 95.0931 | 94.2035
2022-09-08 06:37 | 8:47 | 31.9567 | 30.8162 | 32.3533 | 36.5103 | 34.3607 | 34.102 | 34.6114 | 35.5349 | 36.5176 | 37.6032 | 36.9892 | 38.2155 | 34.2481 | 34.303 | 33.9942 | 35.0692 | 34.7086 | 35.3762 | 36.1035 | 36.4117 | 25.5805 | 21.9048 | 93.8619 | 34.6833 | 32.8153 | 34.6972 | 32.8716 | 32.8612 | 33.2153 | 34.4676 | 33.9943 | 33.8308 | 37.0694 | 36.1654 | 33.1867 | 34.2911 | 36.1724 | 36.4419 | 37.2884 | 36.1687 | 32.8739 | 32.69 | 34.5258 | 34.7569 | 33.1182 | 34.7948 | 34.514 | 34.3255 | 34.382 | 34.2948 | 34.3169 | 34.0121 | 34.3755 | 36.1766 | 34.7601 | 36.5744 | 36.5335 | 33.2364 | 94.9796 | 95.1741 | 94.1967
2022-09-08 06:37 | 8:47 | 32.0171 | 30.955 | 32.3857 | 36.4907 | 34.3311 | 34.0805 | 34.6034 | 35.5449 | 36.5345 | 37.6014 | 36.9778 | 38.2217 | 34.2468 | 34.2928 | 34.0205 | 35.085 | 34.7047 | 35.3687 | 36.1087 | 36.4004 | 24.9992 | 21.8108 | 93.8216 | 34.4486 | 32.8341 | 34.699 | 32.8659 | 32.8538 | 33.1992 | 34.4701 | 33.9821 | 33.8398 | 37.0782 | 36.1857 | 33.2051 | 34.284 | 36.175 | 36.4429 | 37.2868 | 36.1735 | 32.9012 | 32.6962 | 34.5434 | 34.7572 | 33.1223 | 34.7839 | 34.5151 | 34.3294 | 34.3912 | 34.2814 | 34.3129 | 33.9992 | 34.382 | 36.1811 | 34.7727 | 36.5541 | 36.5322 | 33.2482 | 94.9735 | 95.1283 | 94.1223
2022-09-08 06:37 | 8:47 | 32.0679 | 31.0304 | 32.4549 | 36.442 | 34.3288 | 34.0998 | 34.6114 | 35.5559 | 36.5288 | 37.6003 | 37.0017 | 38.1969 | 34.261 | 34.2835 | 34.0059 | 35.0682 | 34.6919 | 35.3484 | 36.1113 | 36.3967 | 24.4348 | 21.5017 | 93.8396 | 34.3617 | 32.8185 | 34.6944 | 32.871 | 32.8524 | 33.1889 | 34.464 | 34.017 | 33.8402 | 37.0833 | 36.1598 | 33.1932 | 34.2807 | 36.1654 | 36.4351 | 37.2778 | 36.164 | 32.8893 | 32.692 | 34.5394 | 34.7587 | 33.1113 | 34.7888 | 34.5029 | 34.3144 | 34.3907 | 34.2944 | 34.3319 | 34.0119 | 34.3912 | 36.1894 | 34.7514 | 36.5834 | 36.5352 | 33.2138 | 94.8092 | 95.0541 | 94.0672
2022-09-08 06:37 | 8:47 | 32.1255 | 31.1037 | 32.4966 | 36.4375 | 34.345 | 34.1013 | 34.5996 | 35.5509 | 36.5273 | 37.5976 | 36.9766 | 38.2198 | 34.2557 | 34.272 | 33.9872 | 35.0894 | 34.6918 | 35.3433 | 36.1103 | 36.412 | 23.8068 | 21.2122 | 93.7937 | 34.3491 | 32.8284 | 34.7181 | 32.8836 | 32.8159 | 33.2059 | 34.4948 | 33.9934 | 33.8214 | 37.0885 | 36.1464 | 33.1858 | 34.2917 | 36.1857 | 36.4341 | 37.2722 | 36.1724 | 32.8918 | 32.6912 | 34.543 | 34.7682 | 33.115 | 34.789 | 34.5135 | 34.3282 | 34.3867 | 34.2867 | 34.2932 | 33.9995 | 34.3907 | 36.1567 | 34.764 | 36.5596 | 36.5448 | 33.219 | 94.5998 | 94.8285 | 93.9137
2022-09-08 06:37 | 8:47 | 32.1766 | 31.1755 | 32.5411 | 36.4532 | 34.3416 | 34.1013 | 34.6201 | 35.5636 | 36.5474 | 37.6121 | 36.9865 | 38.2187 | 34.2413 | 34.3029 | 33.9897 | 35.0822 | 34.7071 | 35.3568 | 36.1129 | 36.4085 | 23.207 | 20.7675 | 93.6723 | 34.2097 | 32.8019 | 34.6931 | 32.8739 | 32.8208 | 33.1867 | 34.4654 | 34.0059 | 33.8265 | 37.0626 | 36.1741 | 33.2034 | 34.2838 | 36.1598 | 36.432 | 37.2953 | 36.175 | 32.8653 | 32.7085 | 34.5328 | 34.7538 | 33.106 | 34.8 | 34.5204 | 34.3192 | 34.3711 | 34.2902 | 34.3274 | 33.9974 | 34.3867 | 36.1736 | 34.7754 | 36.5763 | 36.5177 | 33.2413 | 94.4106 | 94.6392 | 93.7865
2022-09-08 06:38 | 8:47 | 32.2229 | 31.2475 | 32.585 | 36.6336 | 34.3332 | 34.1051 | 34.6338 | 35.5494 | 36.5229 | 37.6055 | 36.9923 | 38.2171 | 34.2545 | 34.2874 | 33.9855 | 35.084 | 34.7246 | 35.3769 | 36.1177 | 36.3807 | 22.2608 | 20.4065 | 93.6063 | 34.1563 | 32.825 | 34.7067 | 32.9012 | 32.8306 | 33.2051 | 34.4739 | 33.9955 | 33.8072 | 37.0872 | 36.1755 | 33.1943 | 34.2984 | 36.1464 | 36.4432 | 37.2863 | 36.1654 | 32.8835 | 32.6961 | 34.5498 | 34.7689 | 33.1054 | 34.7841 | 34.5062 | 34.3273 | 34.3948 | 34.3059 | 34.3211 | 34.0117 | 34.3711 | 36.1714 | 34.765 | 36.5719 | 36.5306 | 33.2056 | 94.2093 | 94.4163 | 93.6911
2022-09-08 06:38 | 8:48 | 32.2779 | 31.2633 | 32.6153 | 36.6383 | 34.3311 | 34.121 | 34.627 | 35.5658 | 36.5413 | 37.5991 | 36.9783 | 38.2072 | 34.2747 | 34.2985 | 34.0016 | 35.0914 | 34.7014 | 35.3714 | 36.1234 | 36.4121 | 21.0724 | 20.0131 | 93.3408 | 33.9975 | 32.8132 | 34.7033 | 32.8893 | 32.8304 | 33.1932 | 34.4827 | 34.0038 | 33.8454 | 37.0807 | 36.1823 | 33.1903 | 34.3072 | 36.1741 | 36.4436 | 37.2739 | 36.1857 | 32.9036 | 32.682 | 34.5488 | 34.7592 | 33.1113 | 34.7904 | 34.5082 | 34.3116 | 34.3971 | 34.2955 | 34.2981 | 33.9947 | 34.3948 | 36.1623 | 34.7773 | 36.5547 | 36.5077 | 33.2173 | 94.0703 | 94.172 | 93.6217
2022-09-08 06:38 | 8:48 | 32.3098 | 31.3246 | 32.6656 | 36.642 | 34.3335 | 34.1165 | 34.6537 | 35.553 | 36.5363 | 37.6191 | 36.9933 | 38.2015 | 34.2582 | 34.302 | 33.9881 | 35.073 | 34.7107 | 35.3538 | 36.0975 | 36.4081 | 18.8483 | 19.5259 | 93.3418 | 33.9912 | 32.8182 | 34.6898 | 32.8918 | 32.8202 | 33.1858 | 34.4669 | 34.0205 | 33.825 | 37.0988 | 36.1928 | 33.2077 | 34.3173 | 36.1755 | 36.434 | 37.2803 | 36.1598 | 32.9035 | 32.6844 | 34.547 | 34.7553 | 33.1066 | 34.7866 | 34.5172 | 34.3166 | 34.3993 | 34.306 | 34.3031 | 34.0224 | 34.3971 | 36.1583 | 34.7782 | 36.5553 | 36.529 | 33.2197 | 93.9616 | 94.0438 | 93.5678
2022-09-08 06:38 | 8:48 | 32.3539 | 31.3393 | 32.7238 | 36.7245 | 34.3579 | 34.0969 | 34.6382 | 35.5637 | 36.5366 | 37.6085 | 36.9916 | 38.2078 | 34.2571 | 34.3034 | 33.9776 | 35.0972 | 34.7216 | 35.3593 | 36.1251 | 36.3969 | 17.6192 | 18.8856 | 93.3087 | 34.0345 | 32.811 | 34.7114 | 32.8653 | 32.82 | 33.2034 | 34.4735 | 34.0035 | 33.831 | 37.091 | 36.1747 | 33.1884 | 34.306 | 36.1823 | 36.4269 | 37.2873 | 36.1464 | 32.8956 | 32.7032 | 34.5302 | 34.7658 | 33.0925 | 34.7872 | 34.5361 | 34.3075 | 34.3896 | 34.3017 | 34.3331 | 34.0244 | 34.3993 | 36.1854 | 34.773 | 36.5708 | 36.5089 | 33.202 | 93.8784 | 93.9583 | 93.5127
2022-09-08 06:38 | 8:48 | 32.3805 | 29.7755 | 32.7588 | 36.6025 | 34.3336 | 34.1241 | 34.656 | 35.5627 | 36.5312 | 37.6061 | 37.0021 | 38.2108 | 34.2629 | 34.3089 | 33.999 | 35.0893 | 34.7026 | 35.3449 | 36.103 | 36.3871 | 18.8004 | 19.2026 | 93.2549 | 33.8127 | 32.7902 | 34.6932 | 32.8835 | 32.81 | 33.1943 | 34.4535 | 34.0106 | 33.8332 | 37.0882 | 36.1995 | 33.1946 | 34.3123 | 36.1928 | 36.4224 | 37.2835 | 36.1741 | 32.8877 | 32.705 | 34.5333 | 34.7444 | 33.0907 | 34.8089 | 34.5264 | 34.3067 | 34.4007 | 34.3127 | 34.3046 | 34.0125 | 34.3896 | 36.1681 | 34.7638 | 36.5684 | 36.5175 | 33.2025 | 93.7133 | 93.8451 | 93.3645
2022-09-08 06:38 | 8:48 | 31.8485 | 25.802 | 31.7937 | 36.6462 | 34.344 | 34.1246 | 34.63 | 35.5758 | 36.5269 | 37.5898 | 36.9829 | 38.2153 | 34.2689 | 34.3035 | 33.9731 | 35.0897 | 34.7155 | 35.3591 | 36.1157 | 36.4007 | 20.537 | 20.5185 | 93.1616 | 33.7351 | 32.7786 | 34.7259 | 32.9036 | 32.8124 | 33.1903 | 34.4637 | 33.9867 | 33.8146 | 37.093 | 36.195 | 33.1787 | 34.3108 | 36.1747 | 36.4381 | 37.2864 | 36.1755 | 32.8875 | 32.6852 | 34.507 | 34.766 | 33.0853 | 34.811 | 34.5442 | 34.2951 | 34.4009 | 34.2973 | 34.3074 | 33.9978 | 34.4007 | 36.1678 | 34.7838 | 36.5528 | 36.5176 | 33.2108 | 93.6587 | 93.7636 | 93.3431
2022-09-08 06:39 | 8:49 | 31.5554 | 24.5173 | 31.0029 | 36.6428 | 34.3444 | 34.1298 | 34.6593 | 35.5709 | 36.5463 | 37.5945 | 36.9813 | 38.2135 | 34.2512 | 34.3069 | 34.0055 | 35.1044 | 34.7101 | 35.3518 | 36.1139 | 36.389 | 20.8443 | 20.4148 | 93.2053 | 33.8348 | 32.806 | 34.7297 | 32.9035 | 32.8265 | 33.2077 | 34.4607 | 33.9934 | 33.8334 | 37.0844 | 36.2061 | 33.1819 | 34.3101 | 36.1995 | 36.4245 | 37.262 | 36.1823 | 32.8937 | 32.7158 | 34.5074 | 34.7565 | 33.0769 | 34.7976 | 34.5428 | 34.2843 | 34.4088 | 34.2945 | 34.31 | 34.0185 | 34.4009 | 36.1742 | 34.7758 | 36.5573 | 36.5176 | 33.2122 | 93.5123 | 93.6645 | 93.3272
2022-09-08 06:39 | 8:49 | 31.2397 | 24.3345 | 30.3251 | 36.5299 | 34.3359 | 34.1337 | 34.6628 | 35.5742 | 36.5196 | 37.5974 | 36.9846 | 38.2156 | 34.28 | 34.3106 | 33.9805 | 35.0957 | 34.7339 | 35.3456 | 36.1241 | 36.3993 | 20.8833 | 20.3616 | 92.9417 | 33.9237 | 32.8219 | 34.6985 | 32.8956 | 32.795 | 33.1884 | 34.4494 | 34.0045 | 33.8346 | 37.0821 | 36.1966 | 33.1772 | 34.3108 | 36.195 | 36.4245 | 37.2996 | 36.1928 | 32.8847 | 32.691 | 34.5295 | 34.7578 | 33.0913 | 34.7928 | 34.5469 | 34.2711 | 34.4076 | 34.3198 | 34.3083 | 33.9965 | 34.4088 | 36.1622 | 34.7583 | 36.5873 | 36.5091 | 33.2073 | 93.4063 | 93.5558 | 93.2296
2022-09-08 06:39 | 8:49 | 30.8587 | 24.2901 | 29.8892 | 36.5653 | 34.3496 | 34.1317 | 34.6735 | 35.5769 | 36.5226 | 37.6007 | 36.9884 | 38.2102 | 34.251 | 34.2978 | 33.9901 | 35.08 | 34.7221 | 35.3787 | 36.1003 | 36.3805 | 21.3376 | 20.3878 | 92.9761 | 33.7092 | 32.7959 | 34.7248 | 32.8877 | 32.7947 | 33.1946 | 34.4545 | 34.0118 | 33.8199 | 37.1153 | 36.2017 | 33.1918 | 34.3067 | 36.2061 | 36.4426 | 37.2875 | 36.1747 | 32.8872 | 32.6774 | 34.5111 | 34.7608 | 33.0829 | 34.7908 | 34.5614 | 34.281 | 34.4104 | 34.2975 | 34.3052 | 33.9983 | 34.4076 | 36.1673 | 34.7823 | 36.5622 | 36.524 | 33.212 | 93.4355 | 93.4873 | 93.2352
2022-09-08 06:39 | 8:49 | 30.5534 | 24.3193 | 29.6378 | 36.4873 | 34.349 | 34.1076 | 34.6912 | 35.568 | 36.5329 | 37.5918 | 37.0013 | 38.214 | 34.2677 | 34.2906 | 33.9948 | 35.1007 | 34.7221 | 35.3593 | 36.095 | 36.3748 | 22.0152 | 20.3585 | 93.0389 | 33.7118 | 32.7971 | 34.7322 | 32.8875 | 32.8079 | 33.1787 | 34.4438 | 34.0165 | 33.8408 | 37.0932 | 36.2052 | 33.1982 | 34.3134 | 36.1966 | 36.4328 | 37.2672 | 36.1995 | 32.9036 | 32.6829 | 34.5177 | 34.7609 | 33.0774 | 34.797 | 34.5579 | 34.2811 | 34.3919 | 34.311 | 34.3101 | 34.0059 | 34.4104 | 36.1601 | 34.773 | 36.5667 | 36.5228 | 33.2061 | 93.4338 | 93.4449 | 93.2243
2022-09-08 06:39 | 8:49 | 30.227 | 24.3127 | 29.4276 | 36.4203 | 34.3373 | 34.1279 | 34.685 | 35.5638 | 36.5451 | 37.6039 | 37.0048 | 38.2169 | 34.2712 | 34.303 | 34.0057 | 35.0968 | 34.7336 | 35.3732 | 36.0902 | 36.396 | 22.5855 | 20.2618 | 93.1035 | 33.9115 | 32.7854 | 34.7249 | 32.8937 | 32.807 | 33.1819 | 34.4513 | 34.0164 | 33.8394 | 37.0826 | 36.2115 | 33.1892 | 34.3022 | 36.2017 | 36.4336 | 37.306 | 36.195 | 32.8877 | 32.6936 | 34.514 | 34.7589 | 33.0833 | 34.8018 | 34.5718 | 34.2883 | 34.415 | 34.2995 | 34.2874 | 34.0179 | 34.3919 | 36.1691 | 34.7772 | 36.5608 | 36.5109 | 33.2123 | 93.3805 | 93.4405 | 93.2977
2022-09-08 06:39 | 8:49 | 29.997 | 24.3172 | 29.364 | 36.4476 | 34.3445 | 34.133 | 34.6968 | 35.5678 | 36.5465 | 37.6174 | 36.9884 | 38.2229 | 34.2596 | 34.3096 | 33.9823 | 35.0993 | 34.7101 | 35.354 | 36.1108 | 36.3891 | 23.0007 | 20.2701 | 93.0078 | 33.8374 | 32.8227 | 34.7292 | 32.8847 | 32.8043 | 33.1772 | 34.4499 | 33.9995 | 33.8375 | 37.0888 | 36.1987 | 33.1955 | 34.3155 | 36.2052 | 36.4352 | 37.2766 | 36.2061 | 32.9128 | 32.6941 | 34.5172 | 34.7575 | 33.0662 | 34.8042 | 34.5798 | 34.2546 | 34.4018 | 34.3152 | 34.2824 | 34.011 | 34.415 | 36.1635 | 34.7708 | 36.5769 | 36.5283 | 33.2076 | 93.3828 | 93.4083 | 93.1161
2022-09-08 06:40 | 8:49 | 29.4629 | 24.3378 | 29.0602 | 36.3275 | 34.315 | 34.1091 | 34.6972 | 35.583 | 36.5397 | 37.6121 | 36.992 | 38.2239 | 34.265 | 34.3166 | 33.9834 | 35.1063 | 34.7335 | 35.3721 | 36.0901 | 36.3935 | 23.3286 | 20.2764 | 92.9606 | 33.9116 | 32.8202 | 34.7332 | 32.8872 | 32.8007 | 33.1918 | 34.4391 | 34.0127 | 33.8339 | 37.0957 | 36.1923 | 33.1876 | 34.3033 | 36.2115 | 36.4412 | 37.2895 | 36.1966 | 32.9041 | 32.6859 | 34.5182 | 34.7694 | 33.0618 | 34.812 | 34.5926 | 34.2671 | 34.3877 | 34.312 | 34.2803 | 34.0132 | 34.4018 | 36.1571 | 34.7714 | 36.5493 | 36.5232 | 33.2177 | 93.2502 | 93.3519 | 93.046
2022-09-08 06:40 | 8:50 | 28.9915 | 24.2957 | 28.9344 | 36.3303 | 34.341 | 34.1151 | 34.7053 | 35.5903 | 36.5425 | 37.6019 | 37.0269 | 38.2505 | 34.2678 | 34.3011 | 33.9951 | 35.1108 | 34.7439 | 35.3584 | 36.0843 | 36.3898 | 23.5717 | 20.2437 | 92.9036 | 33.8894 | 32.8118 | 34.7269 | 32.9036 | 32.8107 | 33.1982 | 34.4467 | 34.0044 | 33.829 | 37.1022 | 36.2191 | 33.2114 | 34.3103 | 36.1987 | 36.4567 | 37.284 | 36.2017 | 32.9231 | 32.696 | 34.5162 | 34.7863 | 33.0473 | 34.7855 | 34.5829 | 34.2517 | 34.4101 | 34.3025 | 34.2928 | 34.0225 | 34.3877 | 36.1613 | 34.7815 | 36.5766 | 36.5105 | 33.2113 | 93.1008 | 93.2738 | 92.9083
2022-09-08 06:40 | 8:50 | 28.5319 | 24.0988 | 28.6795 | 36.3821 | 34.3511 | 34.1247 | 34.697 | 35.5849 | 36.5478 | 37.607 | 36.9983 | 38.2309 | 34.2611 | 34.3074 | 33.9873 | 35.0965 | 34.7205 | 35.3663 | 36.0933 | 36.3713 | 23.7757 | 20.1649 | 92.8898 | 33.8585 | 32.8 | 34.7443 | 32.8877 | 32.8029 | 33.1892 | 34.456 | 34.0081 | 33.8475 | 37.1012 | 36.2144 | 33.1967 | 34.3084 | 36.1923 | 36.4365 | 37.2713 | 36.2052 | 32.8981 | 32.6845 | 34.5207 | 34.7486 | 33.0742 | 34.8033 | 34.5959 | 34.24 | 34.4087 | 34.3123 | 34.3179 | 34.0161 | 34.4101 | 36.1761 | 34.7741 | 36.5725 | 36.5252 | 33.2183 | 93.0341 | 93.237 | 92.9313
2022-09-08 06:40 | 8:50 | 28.1089 | 24.014 | 28.3687 | 36.3636 | 34.3333 | 34.1069 | 34.7248 | 35.5861 | 36.5433 | 37.6195 | 37.0228 | 38.2293 | 34.2842 | 34.314 | 33.9928 | 35.099 | 34.7244 | 35.367 | 36.1037 | 36.4059 | 23.947 | 20.1728 | 92.9347 | 33.8584 | 32.7839 | 34.726 | 32.9128 | 32.8067 | 33.1955 | 34.4722 | 34.0171 | 33.849 | 37.1145 | 36.2003 | 33.1985 | 34.3089 | 36.2191 | 36.4547 | 37.3125 | 36.2115 | 32.9249 | 32.678 | 34.5183 | 34.7866 | 33.0525 | 34.7877 | 34.5986 | 34.2794 | 34.4137 | 34.2951 | 34.285 | 34.0005 | 34.4087 | 36.163 | 34.7866 | 36.5829 | 36.5351 | 33.224 | 93.06 | 93.1882 | 93.0145
2022-09-08 06:40 | 8:50 | 27.6861 | 23.8253 | 28.1166 | 36.3289 | 34.3394 | 34.1135 | 34.7182 | 35.5931 | 36.5333 | 37.6021 | 37.0071 | 38.2189 | 34.2468 | 34.3114 | 34.0063 | 35.1176 | 34.7478 | 35.3407 | 36.086 | 36.3824 | 24.0577 | 20.0015 | 92.9142 | 33.7388 | 32.8081 | 34.728 | 32.9041 | 32.8193 | 33.1876 | 34.467 | 34.0166 | 33.8291 | 37.1064 | 36.2112 | 33.1935 | 34.3001 | 36.2144 | 36.4442 | 37.3045 | 36.1987 | 32.9224 | 32.7075 | 34.5202 | 34.7872 | 33.0592 | 34.7982 | 34.6172 | 34.2745 | 34.4213 | 34.3191 | 34.2998 | 34.001 | 34.4137 | 36.1759 | 34.7831 | 36.5697 | 36.5244 | 33.2112 | 93.0021 | 93.1368 | 92.9855
2022-09-08 06:40 | 8:50 | 27.3156 | 23.6685 | 27.8341 | 36.2404 | 34.3388 | 34.1211 | 34.713 | 35.5884 | 36.5351 | 37.6015 | 37.0161 | 38.2355 | 34.2913 | 34.3255 | 33.9913 | 35.1127 | 34.7458 | 35.3596 | 36.0956 | 36.3958 | 24.1514 | 20.0061 | 92.8631 | 33.7722 | 32.813 | 34.7446 | 32.9231 | 32.8012 | 33.2114 | 34.4518 | 34.0201 | 33.8506 | 37.1023 | 36.1988 | 33.1911 | 34.3205 | 36.2003 | 36.4444 | 37.2983 | 36.1923 | 32.9102 | 32.6947 | 34.5072 | 34.777 | 33.0553 | 34.7965 | 34.6093 | 34.2607 | 34.4203 | 34.326 | 34.2824 | 33.9911 | 34.4213 | 36.1828 | 34.7536 | 36.5829 | 36.5188 | 33.234 | 92.9192 | 93.0726 | 92.8422
2022-09-08 06:41 | 8:51 | 26.9547 | 23.6102 | 27.6019 | 36.2825 | 34.326 | 34.1221 | 34.7236 | 35.6033 | 36.5443 | 37.6152 | 37.0034 | 38.2297 | 34.2656 | 34.3178 | 34.0106 | 35.0953 | 34.7371 | 35.3518 | 36.0935 | 36.4028 | 24.2256 | 19.8446 | 92.7445 | 33.8201 | 32.8064 | 34.7274 | 32.8981 | 32.8211 | 33.1967 | 34.4499 | 34.0271 | 33.8505 | 37.1153 | 36.2076 | 33.183 | 34.3199 | 36.2112 | 36.4427 | 37.3016 | 36.2191 | 32.9239 | 32.68 | 34.518 | 34.7879 | 33.0551 | 34.7947 | 34.5912 | 34.2476 | 34.4138 | 34.3135 | 34.2983 | 33.9912 | 34.4203 | 36.1824 | 34.7839 | 36.5635 | 36.5173 | 33.2354 | 92.8048 | 92.9822 | 92.7577
2022-09-08 06:41 | 8:51 | 26.6302 | 23.6605 | 27.4443 | 36.1387 | 34.3241 | 34.1344 | 34.7155 | 35.6017 | 36.548 | 37.6096 | 36.9876 | 38.227 | 34.2704 | 34.3201 | 33.9945 | 35.0896 | 34.7564 | 35.3634 | 36.0795 | 36.3827 | 24.3189 | 20.037 | 92.6513 | 33.8306 | 32.8251 | 34.7358 | 32.9249 | 32.8182 | 33.1985 | 34.4474 | 34.0351 | 33.8541 | 37.1098 | 36.2184 | 33.1726 | 34.3158 | 36.1988 | 36.4519 | 37.2753 | 36.2144 | 32.9115 | 32.6779 | 34.5069 | 34.7685 | 33.0639 | 34.806 | 34.6071 | 34.2379 | 34.4019 | 34.3122 | 34.2804 | 33.983 | 34.4138 | 36.1979 | 34.7629 | 36.5765 | 36.5274 | 33.2244 | 92.6578 | 92.8739 | 92.5696
2022-09-08 06:41 | 8:51 | 26.1327 | 23.387 | 27.1124 | 36.2449 | 34.3041 | 34.1237 | 34.7212 | 35.5953 | 36.553 | 37.6009 | 37.0157 | 38.2247 | 34.2802 | 34.3068 | 34.0083 | 35.1015 | 34.7541 | 35.3457 | 36.0813 | 36.3927 | 24.3592 | 19.7168 | 92.6486 | 33.8822 | 32.8098 | 34.7469 | 32.9224 | 32.8214 | 33.1935 | 34.4469 | 34.0096 | 33.8398 | 37.1139 | 36.2141 | 33.1875 | 34.3339 | 36.2076 | 36.4436 | 37.3021 | 36.2003 | 32.9246 | 32.6823 | 34.5168 | 34.791 | 33.0406 | 34.7878 | 34.6388 | 34.2642 | 34.4181 | 34.3412 | 34.303 | 33.9913 | 34.4019 | 36.1867 | 34.7817 | 36.579 | 36.5168 | 33.2358 | 92.5417 | 92.7635 | 92.6291
2022-09-08 06:41 | 8:51 | 25.2888 | 23.3082 | 26.5795 | 36.0668 | 34.323 | 34.1208 | 34.7221 | 35.5919 | 36.5592 | 37.5942 | 37.0096 | 38.2429 | 34.2751 | 34.3392 | 34.0013 | 35.1056 | 34.7262 | 35.3596 | 36.0626 | 36.4042 | 24.3251 | 19.6257 | 92.5783 | 33.9179 | 32.8168 | 34.7412 | 32.9102 | 32.8189 | 33.1911 | 34.4523 | 34.0126 | 33.8566 | 37.1175 | 36.2253 | 33.1959 | 34.325 | 36.2184 | 36.4442 | 37.2905 | 36.2112 | 32.9249 | 32.6758 | 34.5164 | 34.7741 | 33.053 | 34.7781 | 34.6239 | 34.257 | 34.4279 | 34.3055 | 34.2928 | 33.9896 | 34.4181 | 36.204 | 34.7572 | 36.5586 | 36.523 | 33.2187 | 92.4572 | 92.6535 | 92.4533
2022-09-08 06:41 | 8:51 | 22.0779 | 23.3761 | 26.0307 | 36.1148 | 34.3222 | 34.1143 | 34.7116 | 35.5988 | 36.5719 | 37.6086 | 37.0163 | 38.22 | 34.2851 | 34.3227 | 34.0189 | 35.0993 | 34.7661 | 35.352 | 36.0891 | 36.4022 | 24.2884 | 19.7518 | 92.4553 | 33.7586 | 32.8238 | 34.7338 | 32.9239 | 32.8137 | 33.183 | 34.4586 | 34.0199 | 33.8654 | 37.1223 | 36.2058 | 33.1938 | 34.3065 | 36.2141 | 36.4492 | 37.3018 | 36.1988 | 32.9176 | 32.6891 | 34.5088 | 34.7812 | 33.0503 | 34.7884 | 34.6256 | 34.261 | 34.4259 | 34.3285 | 34.2835 | 34.002 | 34.4279 | 36.1847 | 34.7783 | 36.5705 | 36.5125 | 33.2537 | 92.3569 | 92.5911 | 92.3981
2022-09-08 06:41 | 8:51 | 21.5516 | 23.2275 | 25.7719 | 35.9765 | 34.3071 | 34.1225 | 34.7034 | 35.5907 | 36.5616 | 37.6127 | 37.0057 | 38.2319 | 34.2754 | 34.3351 | 33.9996 | 35.1114 | 34.7549 | 35.3456 | 36.0643 | 36.4048 | 24.1996 | 19.6842 | 92.3962 | 33.6295 | 32.7946 | 34.7399 | 32.9115 | 32.8144 | 33.1726 | 34.4537 | 34.0097 | 33.8244 | 37.1177 | 36.2064 | 33.1912 | 34.3246 | 36.2253 | 36.4194 | 37.2989 | 36.2076 | 32.9001 | 32.6911 | 34.5211 | 34.7817 | 33.0369 | 34.7998 | 34.6313 | 34.2401 | 34.429 | 34.3392 | 34.272 | 34.0134 | 34.4259 | 36.1838 | 34.7755 | 36.5973 | 36.5291 | 33.2382 | 92.233 | 92.4136 | 92.2812
2022-09-08 06:42 | 8:51 | 21.3775 | 23.0581 | 25.4763 | 36.0105 | 34.3169 | 34.1254 | 34.7211 | 35.603 | 36.5517 | 37.5983 | 36.9942 | 38.2592 | 34.2948 | 34.3438 | 34.0075 | 35.1097 | 34.7458 | 35.3599 | 36.0625 | 36.3974 | 24.0373 | 19.5724 | 92.3383 | 33.6057 | 32.8119 | 34.7368 | 32.9246 | 32.8219 | 33.1875 | 34.4415 | 34.0399 | 33.8471 | 37.1339 | 36.1921 | 33.1912 | 34.3125 | 36.2058 | 36.4424 | 37.2916 | 36.2184 | 32.9243 | 32.675 | 34.5142 | 34.7954 | 33.0324 | 34.8021 | 34.6337 | 34.2519 | 34.4305 | 34.32 | 34.3029 | 34.0112 | 34.429 | 36.1974 | 34.7808 | 36.6011 | 36.5246 | 33.2428 | 92.135 | 92.2755 | 92.2718
2022-09-08 06:42 | 8:52 | 21.2814 | 22.916 | 25.2186 | 36.065 | 34.3129 | 34.122 | 34.708 | 35.6108 | 36.5734 | 37.6086 | 36.9999 | 38.2465 | 34.2815 | 34.332 | 34.0056 | 35.101 | 34.7816 | 35.3491 | 36.0622 | 36.4 | 23.8335 | 19.5104 | 92.2957 | 33.5949 | 32.8156 | 34.743 | 32.9249 | 32.8274 | 33.1959 | 34.4582 | 34.0355 | 33.8675 | 37.1069 | 36.1936 | 33.2022 | 34.329 | 36.2064 | 36.4485 | 37.2825 | 36.2141 | 32.8999 | 32.693 | 34.5346 | 34.8035 | 33.0385 | 34.8157 | 34.6241 | 34.2418 | 34.4485 | 34.3113 | 34.2874 | 34.0018 | 34.4305 | 36.1737 | 34.7762 | 36.5809 | 36.5213 | 33.2577 | 92.0566 | 92.1921 | 92.1896
2022-09-08 06:42 | 8:52 | 21.1571 | 22.6917 | 25.0615 | 35.9383 | 34.3319 | 34.1091 | 34.7127 | 35.5772 | 36.5705 | 37.6158 | 37.0164 | 38.2503 | 34.2925 | 34.3407 | 34.0145 | 35.1164 | 34.7747 | 35.3307 | 36.0725 | 36.4112 | 23.6345 | 19.6566 | 92.3086 | 33.607 | 32.816 | 34.7137 | 32.9176 | 32.8165 | 33.1938 | 34.4539 | 34.008 | 33.858 | 37.1073 | 36.1949 | 33.202 | 34.3235 | 36.1921 | 36.4509 | 37.3039 | 36.2253 | 32.9198 | 32.6692 | 34.538 | 34.7879 | 33.057 | 34.7975 | 34.6386 | 34.2244 | 34.4344 | 34.3247 | 34.2985 | 34.0162 | 34.4485 | 36.1765 | 34.7985 | 36.5843 | 36.5251 | 33.2724 | 92.0643 | 92.1631 | 92.2318
2022-09-08 06:42 | 8:52 | 21.0277 | 22.5295 | 24.8528 | 35.8467 | 34.2932 | 34.1477 | 34.6854 | 35.6001 | 36.5512 | 37.5994 | 37.0225 | 38.2237 | 34.2835 | 34.3383 | 34.0295 | 35.1087 | 34.7582 | 35.3368 | 36.0655 | 36.3891 | 23.4312 | 19.704 | 92.3502 | 33.4072 | 32.8263 | 34.7343 | 32.9001 | 32.8176 | 33.1912 | 34.4521 | 34.0315 | 33.8705 | 37.1224 | 36.2136 | 33.2179 | 34.3226 | 36.1936 | 36.4629 | 37.2963 | 36.2058 | 32.9116 | 32.6721 | 34.5376 | 34.8174 | 33.0203 | 34.7961 | 34.6481 | 34.231 | 34.4402 | 34.3203 | 34.302 | 34.017 | 34.4344 | 36.1793 | 34.7684 | 36.5646 | 36.5404 | 33.2448 | 92.1358 | 92.2741 | 92.4117
2022-09-08 06:42 | 8:52 | 20.8756 | 22.3536 | 24.7079 | 35.9165 | 34.3274 | 34.1344 | 34.7021 | 35.5886 | 36.5595 | 37.6009 | 37.0158 | 38.2359 | 34.2959 | 34.3452 | 34.0213 | 35.1112 | 34.7748 | 35.3715 | 36.0787 | 36.3882 | 23.1935 | 19.6793 | 92.4812 | 33.4253 | 32.8257 | 34.7525 | 32.9243 | 32.8065 | 33.1912 | 34.4495 | 34.0157 | 33.8448 | 37.1255 | 36.2042 | 33.1922 | 34.3016 | 36.1949 | 36.4484 | 37.3172 | 36.2064 | 32.9082 | 32.676 | 34.5249 | 34.7926 | 33.0172 | 34.7908 | 34.638 | 34.2241 | 34.4501 | 34.3395 | 34.3034 | 33.9856 | 34.4402 | 36.218 | 34.7694 | 36.6021 | 36.5273 | 33.261 | 92.2773 | 92.3797 | 92.4765
2022-09-08 06:42 | 8:52 | 20.8852 | 22.2199 | 24.6193 | 35.7826 | 34.3211 | 34.1231 | 34.7043 | 35.5931 | 36.5625 | 37.6156 | 37.0047 | 38.2375 | 34.28 | 34.3527 | 34.0192 | 35.1031 | 34.7723 | 35.3561 | 36.0609 | 36.4093 | 22.9725 | 19.6554 | 92.4682 | 33.5639 | 32.8181 | 34.725 | 32.8999 | 32.802 | 33.2022 | 34.4402 | 34.0089 | 33.8439 | 37.1216 | 36.1882 | 33.1989 | 34.3207 | 36.2136 | 36.4452 | 37.2912 | 36.1921 | 32.8987 | 32.6665 | 34.5139 | 34.8051 | 33.0154 | 34.7834 | 34.6683 | 34.2276 | 34.4605 | 34.3274 | 34.3089 | 33.9903 | 34.4501 | 36.2107 | 34.782 | 36.5719 | 36.5367 | 33.255 | 92.3515 | 92.5199 | 92.5584
2022-09-08 06:43 | 8:53 | 20.6552 | 22.0047 | 24.4289 | 35.7011 | 34.2981 | 34.1197 | 34.6969 | 35.63 | 36.5525 | 37.5825 | 36.9996 | 38.2371 | 34.271 | 34.3428 | 34.0144 | 35.1035 | 34.7667 | 35.3483 | 36.0575 | 36.416 | 22.7044 | 19.6255 | 92.5231 | 33.5723 | 32.8224 | 34.743 | 32.9198 | 32.7994 | 33.202 | 34.4567 | 34.0158 | 33.8616 | 37.1236 | 36.1747 | 33.1879 | 34.2959 | 36.2042 | 36.4605 | 37.2977 | 36.1936 | 32.8964 | 32.6642 | 34.5298 | 34.8084 | 33.0006 | 34.7918 | 34.6732 | 34.2263 | 34.4474 | 34.3328 | 34.3035 | 34.0003 | 34.4605 | 36.2201 | 34.7659 | 36.5972 | 36.5118 | 33.2424 | 92.4782 | 92.6214 | 92.5241
2022-09-08 06:43 | 8:53 | 20.4721 | 21.816 | 24.3222 | 35.7741 | 34.3031 | 34.1036 | 34.6636 | 35.6053 | 36.5599 | 37.6108 | 37.0128 | 38.2303 | 34.2752 | 34.3482 | 34.0147 | 35.1153 | 34.7693 | 35.3483 | 36.0546 | 36.3957 | 22.5187 | 19.4639 | 92.5709 | 33.5473 | 32.8258 | 34.7191 | 32.9116 | 32.7955 | 33.2179 | 34.4481 | 34.0078 | 33.842 | 37.1224 | 36.1807 | 33.1838 | 34.3177 | 36.1882 | 36.4477 | 37.3018 | 36.1949 | 32.888 | 32.6728 | 34.5158 | 34.8085 | 33.0022 | 34.7853 | 34.6487 | 34.233 | 34.4614 | 34.3128 | 34.3069 | 34.0015 | 34.4474 | 36.2081 | 34.7698 | 36.5871 | 36.5208 | 33.2618 | 92.5685 | 92.7382 | 92.6075
2022-09-08 06:43 | 8:53 | 20.4401 | 21.6765 | 24.1671 | 35.6578 | 34.3331 | 34.113 | 34.6938 | 35.5748 | 36.5583 | 37.6137 | 37.0206 | 38.2319 | 34.3047 | 34.3473 | 34.0145 | 35.1031 | 34.7737 | 35.3324 | 36.0617 | 36.4044 | 22.3772 | 19.4272 | 92.7094 | 33.4864 | 32.8087 | 34.7265 | 32.9082 | 32.8028 | 33.1922 | 34.4526 | 34.0034 | 33.8518 | 37.1168 | 36.1891 | 33.201 | 34.3194 | 36.1747 | 36.4415 | 37.3077 | 36.2136 | 32.886 | 32.6794 | 34.5148 | 34.799 | 32.9854 | 34.8044 | 34.662 | 34.2272 | 34.4744 | 34.3345 | 34.3106 | 33.9862 | 34.4614 | 36.1954 | 34.7886 | 36.5787 | 36.5256 | 33.2674 | 92.7123 | 92.8816 | 92.696
2022-09-08 06:43 | 8:53 | 20.3583 | 21.5175 | 23.9955 | 35.6944 | 34.3046 | 34.1016 | 34.6618 | 35.5822 | 36.5589 | 37.607 | 37.0112 | 38.2396 | 34.2929 | 34.3667 | 34.024 | 35.1049 | 34.7774 | 35.3428 | 36.0585 | 36.3977 | 22.2281 | 19.3894 | 92.8531 | 33.5168 | 32.8185 | 34.7185 | 32.8987 | 32.795 | 33.1989 | 34.4511 | 33.9946 | 33.8384 | 37.1116 | 36.1684 | 33.1699 | 34.3104 | 36.1807 | 36.4562 | 37.3002 | 36.2042 | 32.8837 | 32.6662 | 34.5258 | 34.7937 | 32.9847 | 34.7997 | 34.6666 | 34.2318 | 34.4566 | 34.3254 | 34.2978 | 33.9881 | 34.4744 | 36.1971 | 34.7692 | 36.5774 | 36.5118 | 33.2755 | 92.9169 | 93.0585 | 92.894
2022-09-08 06:43 | 8:53 | 20.1759 | 21.3818 | 23.8752 | 35.6996 | 34.3074 | 34.1087 | 34.679 | 35.5888 | 36.5516 | 37.5976 | 37.0041 | 38.2174 | 34.2865 | 34.3587 | 34.0207 | 35.099 | 34.7727 | 35.3475 | 36.041 | 36.4071 | 22.0861 | 19.2787 | 92.9368 | 33.318 | 32.796 | 34.7347 | 32.8964 | 32.7935 | 33.1879 | 34.4442 | 34.0067 | 33.8341 | 37.1225 | 36.2046 | 33.1949 | 34.3137 | 36.1891 | 36.4375 | 37.2925 | 36.1882 | 32.8919 | 32.6595 | 34.5116 | 34.7896 | 32.9905 | 34.7988 | 34.6702 | 34.2093 | 34.4636 | 34.3324 | 34.2906 | 33.995 | 34.4566 | 36.2138 | 34.7629 | 36.5763 | 36.5575 | 33.2534 | 93.0299 | 93.2525 | 92.9739
2022-09-08 06:43 | 8:53 | 20.037 | 21.2014 | 23.7163 | 35.666 | 34.31 | 34.0894 | 34.6234 | 35.5815 | 36.5628 | 37.5962 | 37.0074 | 38.2252 | 34.2938 | 34.3461 | 34.0274 | 35.0934 | 34.7514 | 35.333 | 36.0354 | 36.4083 | 21.967 | 19.1325 | 93.0937 | 33.3914 | 32.8147 | 34.7137 | 32.888 | 32.7751 | 33.1838 | 34.4402 | 34.0018 | 33.8449 | 37.1112 | 36.1833 | 33.1945 | 34.2967 | 36.1684 | 36.4377 | 37.2987 | 36.1747 | 32.8976 | 32.6402 | 34.5004 | 34.763 | 32.9691 | 34.806 | 34.6651 | 34.2245 | 34.4865 | 34.3556 | 34.303 | 33.9746 | 34.4636 | 36.1628 | 34.761 | 36.5844 | 36.5114 | 33.2505 | 93.2325 | 93.4125 | 93.1108
2022-09-08 06:44 | 8:53 | 19.9126 | 21.1012 | 23.6083 | 35.551 | 34.3083 | 34.0911 | 34.5758 | 35.5768 | 36.559 | 37.592 | 36.9802 | 38.2327 | 34.2823 | 34.3722 | 34.0154 | 35.1004 | 34.7711 | 35.3338 | 36.0321 | 36.4105 | 21.8846 | 19.1288 | 93.07 | 33.27 | 32.8068 | 34.6964 | 32.886 | 32.775 | 33.201 | 34.437 | 33.9896 | 33.8492 | 37.1056 | 36.1896 | 33.1733 | 34.2985 | 36.2046 | 36.4479 | 37.2915 | 36.1807 | 32.8785 | 32.6441 | 34.5045 | 34.793 | 32.99 | 34.7827 | 34.6731 | 34.2142 | 34.4951 | 34.3549 | 34.3096 | 33.9995 | 34.4865 | 36.2021 | 34.7686 | 36.578 | 36.5387 | 33.2535 | 93.2961 | 93.554 | 93.0989
2022-09-08 06:44 | 8:54 | 19.8576 | 20.9398 | 23.5382 | 35.6501 | 34.3052 | 34.0925 | 34.6033 | 35.5892 | 36.5537 | 37.5764 | 36.9996 | 38.2354 | 34.2969 | 34.3576 | 34.0017 | 35.0919 | 34.7658 | 35.3324 | 36.0229 | 36.3875 | 21.8152 | 19.0865 | 93.1997 | 33.3623 | 32.8063 | 34.7032 | 32.8837 | 32.7662 | 33.1699 | 34.4418 | 33.9808 | 33.8452 | 37.1035 | 36.1997 | 33.1956 | 34.301 | 36.1833 | 36.4207 | 37.2893 | 36.1891 | 32.9018 | 32.6316 | 34.5086 | 34.7684 | 32.9445 | 34.8071 | 34.6689 | 34.2266 | 34.4804 | 34.3554 | 34.3166 | 33.9764 | 34.4951 | 36.1734 | 34.7733 | 36.5664 | 36.5248 | 33.2532 | 93.4324 | 93.7622 | 93.2655
2022-09-08 06:44 | 8:54 | 19.7856 | 20.8117 | 23.3791 | 35.4947 | 34.3101 | 34.0981 | 34.6056 | 35.5701 | 36.5645 | 37.6008 | 36.9932 | 38.2323 | 34.2948 | 34.3737 | 34.0141 | 35.1039 | 34.7661 | 35.3306 | 36.0429 | 36.3992 | 21.7684 | 18.9248 | 93.2541 | 33.2632 | 32.7913 | 34.7101 | 32.8919 | 32.7841 | 33.1949 | 34.4329 | 33.9952 | 33.8333 | 37.1166 | 36.1916 | 33.1914 | 34.304 | 36.1896 | 36.4341 | 37.2813 | 36.1684 | 32.8872 | 32.626 | 34.4856 | 34.7571 | 32.9666 | 34.8211 | 34.6886 | 34.2283 | 34.4792 | 34.3584 | 34.3011 | 33.9731 | 34.4804 | 36.1892 | 34.7618 | 36.5692 | 36.5276 | 33.2492 | 93.6395 | 93.9747 | 93.3546
2022-09-08 06:44 | 8:54 | 19.659 | 20.6763 | 23.2359 | 35.5533 | 34.2874 | 34.0954 | 34.6448 | 35.59 | 36.5577 | 37.601 | 37 | 38.2249 | 34.2814 | 34.3758 | 33.9965 | 35.0992 | 34.7719 | 35.3113 | 36.0371 | 36.3898 | 21.7434 | 18.8421 | 93.4044 | 33.3152 | 32.8033 | 34.7005 | 32.8976 | 32.776 | 33.1945 | 34.4513 | 33.9924 | 33.855 | 37.1137 | 36.1685 | 33.1775 | 34.2964 | 36.1997 | 36.4411 | 37.3039 | 36.2046 | 32.8789 | 32.6548 | 34.505 | 34.7788 | 32.9541 | 34.8375 | 34.6795 | 34.2437 | 34.4727 | 34.3529 | 34.3074 | 33.9611 | 34.4792 | 36.1756 | 34.7679 | 36.5838 | 36.5306 | 33.2443 | 93.825 | 94.1304 | 93.4834
2022-09-08 06:44 | 8:54 | 19.4793 | 20.4515 | 23.1057 | 35.5589 | 34.2824 | 34.0953 | 34.6202 | 35.5905 | 36.5516 | 37.5923 | 36.9887 | 38.2245 | 34.2944 | 34.3654 | 34.0218 | 35.0829 | 34.7578 | 35.3308 | 35.9949 | 36.4096 | 21.6916 | 18.6992 | 93.5718 | 33.026 | 32.7889 | 34.7158 | 32.8785 | 32.7724 | 33.1733 | 34.4248 | 33.988 | 33.8406 | 37.104 | 36.1897 | 33.1831 | 34.2888 | 36.1916 | 36.4432 | 37.2932 | 36.1833 | 32.8889 | 32.6444 | 34.4823 | 34.7612 | 32.9443 | 34.848 | 34.6868 | 34.2337 | 34.4823 | 34.3337 | 34.314 | 33.9674 | 34.4727 | 36.1759 | 34.7625 | 36.5659 | 36.5164 | 33.2521 | 93.9712 | 94.3215 | 93.6199
2022-09-08 06:44 | 8:54 | 19.4956 | 20.5076 | 22.9987 | 35.4871 | 34.2803 | 34.1153 | 34.6587 | 35.5698 | 36.5688 | 37.5891 | 37.0023 | 38.2282 | 34.2867 | 34.3736 | 34.0145 | 35.0983 | 34.784 | 35.3275 | 36.0207 | 36.401 | 21.6647 | 18.6542 | 93.6121 | 33.0616 | 32.815 | 34.7042 | 32.9018 | 32.7753 | 33.1956 | 34.4522 | 33.9775 | 33.8332 | 37.1016 | 36.1596 | 33.1843 | 34.2836 | 36.1685 | 36.4311 | 37.2762 | 36.1896 | 32.8677 | 32.6486 | 34.4847 | 34.7854 | 32.9264 | 34.8342 | 34.7065 | 34.2249 | 34.493 | 34.3691 | 34.3114 | 33.9741 | 34.4823 | 36.1804 | 34.7548 | 36.5908 | 36.5359 | 33.2569 | 94.128 | 94.5011 | 93.735
2022-09-08 06:45 | 8:55 | 19.4436 | 20.4063 | 22.979 | 35.4873 | 34.2928 | 34.0846 | 34.6495 | 35.5848 | 36.5822 | 37.5852 | 36.9794 | 38.2331 | 34.2902 | 34.365 | 34.0057 | 35.0877 | 34.7779 | 35.323 | 36.017 | 36.3983 | 21.6432 | 18.7113 | 93.7679 | 33.1429 | 32.8005 | 34.7104 | 32.8872 | 32.7523 | 33.1914 | 34.4428 | 33.9974 | 33.8234 | 37.0938 | 36.1958 | 33.1826 | 34.2898 | 36.1897 | 36.4487 | 37.2949 | 36.1997 | 32.878 | 32.6364 | 34.5098 | 34.7768 | 32.9511 | 34.843 | 34.7049 | 34.2222 | 34.4885 | 34.3538 | 34.3255 | 33.9964 | 34.493 | 36.1904 | 34.7689 | 36.586 | 36.4978 | 33.265 | 94.3243 | 94.6829 | 93.847
2022-09-08 06:45 | 8:55 | 19.3056 | 20.2195 | 22.82 | 35.5334 | 34.3179 | 34.1051 | 34.6392 | 35.5743 | 36.5649 | 37.5978 | 36.9926 | 38.2215 | 34.3059 | 34.3742 | 34.0138 | 35.0896 | 34.7644 | 35.3259 | 35.9967 | 36.4053 | 21.5913 | 18.6137 | 93.8931 | 33.0946 | 32.8143 | 34.7078 | 32.8789 | 32.7802 | 33.1775 | 34.4408 | 33.981 | 33.8427 | 37.0996 | 36.1698 | 33.171 | 34.2863 | 36.1596 | 36.436 | 37.2946 | 36.1916 | 32.8834 | 32.6299 | 34.4949 | 34.7808 | 32.9415 | 34.844 | 34.7016 | 34.2036 | 34.5082 | 34.3608 | 34.3178 | 33.9737 | 34.4885 | 36.1907 | 34.7679 | 36.5905 | 36.5204 | 33.2483 | 94.4507 | 94.9249 | 94.0553
2022-09-08 06:45 | 8:55 | 19.3606 | 20.17 | 22.6829 | 35.3873 | 34.285 | 34.1087 | 34.5955 | 35.5668 | 36.5491 | 37.59 | 36.9787 | 38.23 | 34.2955 | 34.3771 | 34.0265 | 35.1002 | 34.7692 | 35.3068 | 35.997 | 36.3942 | 21.5483 | 18.6064 | 94.0542 | 33.0928 | 32.7866 | 34.697 | 32.8889 | 32.7546 | 33.1831 | 34.4124 | 33.9765 | 33.8198 | 37.0959 | 36.1887 | 33.164 | 34.2893 | 36.1958 | 36.4217 | 37.2913 | 36.1685 | 32.8611 | 32.6154 | 34.4659 | 34.7572 | 32.9042 | 34.846 | 34.7166 | 34.2465 | 34.514 | 34.3752 | 34.3201 | 33.96 | 34.5082 | 36.1732 | 34.7573 | 36.5589 | 36.4948 | 33.2397 | 94.6533 | 95.1 | 94.1116
2022-09-08 06:45 | 8:55 | 19.1131 | 20 | 22.5706 | 35.3068 | 34.2998 | 34.0827 | 34.5567 | 35.5592 | 36.5689 | 37.5876 | 36.9809 | 38.2344 | 34.306 | 34.3799 | 34.0076 | 35.0966 | 34.7723 | 35.3004 | 35.9999 | 36.3838 | 21.5167 | 18.561 | 94.0592 | 32.9452 | 32.7914 | 34.6974 | 32.8677 | 32.7543 | 33.1843 | 34.4452 | 33.9809 | 33.8239 | 37.1168 | 36.1867 | 33.1767 | 34.2841 | 36.1698 | 36.4385 | 37.2821 | 36.1897 | 32.8835 | 32.6195 | 34.4678 | 34.7587 | 32.9228 | 34.8479 | 34.7223 | 34.2557 | 34.5151 | 34.3791 | 34.3068 | 33.9628 | 34.514 | 36.1797 | 34.7681 | 36.5669 | 36.4864 | 33.2501 | 94.7612 | 95.2451 | 94.2103
2022-09-08 06:45 | 8:55 | 19.0899 | 19.8874 | 22.4772 | 35.2678 | 34.2824 | 34.0877 | 34.5363 | 35.5607 | 36.5634 | 37.5705 | 36.9739 | 38.2034 | 34.3017 | 34.3882 | 34.0197 | 35.098 | 34.7679 | 35.3038 | 35.9837 | 36.3807 | 21.4843 | 18.4354 | 94.1959 | 33.0646 | 32.8071 | 34.7142 | 32.878 | 32.749 | 33.1826 | 34.4123 | 33.9882 | 33.845 | 37.1013 | 36.1783 | 33.1609 | 34.2884 | 36.1887 | 36.4494 | 37.2867 | 36.1596 | 32.8956 | 32.6044 | 34.4692 | 34.7489 | 32.8971 | 34.8606 | 34.7238 | 34.2392 | 34.5029 | 34.3809 | 34.3392 | 33.9535 | 34.5151 | 36.1505 | 34.7503 | 36.5604 | 36.5048 | 33.2084 | 94.9667 | 95.3992 | 94.409
2022-09-08 06:45 | 8:55 | 18.9528 | 19.8085 | 22.3741 | 35.2883 | 34.2983 | 34.0974 | 34.6161 | 35.5801 | 36.5505 | 37.5581 | 36.9967 | 38.2222 | 34.3127 | 34.3901 | 34.0125 | 35.0881 | 34.7704 | 35.3066 | 36.0027 | 36.3991 | 21.4634 | 18.4433 | 94.3513 | 33.0765 | 32.7982 | 34.6932 | 32.8834 | 32.7683 | 33.171 | 34.4333 | 33.9815 | 33.8116 | 37.0874 | 36.2049 | 33.1759 | 34.2961 | 36.1867 | 36.4186 | 37.2976 | 36.1958 | 32.882 | 32.6195 | 34.4663 | 34.7547 | 32.9339 | 34.8575 | 34.733 | 34.2272 | 34.5135 | 34.3785 | 34.3227 | 33.9662 | 34.5029 | 36.173 | 34.7675 | 36.5806 | 36.5028 | 33.2391 | 95.1849 | 95.5438 | 94.4438
2022-09-08 06:46 | 8:56 | 18.8837 | 19.7287 | 22.348 | 35.2495 | 34.2804 | 34.0885 | 34.6146 | 35.5735 | 36.5609 | 37.5832 | 36.9951 | 38.2007 | 34.2973 | 34.3811 | 34.0013 | 35.1014 | 34.7799 | 35.2962 | 35.9936 | 36.3764 | 21.4214 | 18.3046 | 94.4309 | 32.8539 | 32.7904 | 34.6913 | 32.8611 | 32.7651 | 33.164 | 34.4255 | 33.9542 | 33.8208 | 37.1045 | 36.1992 | 33.1737 | 34.2869 | 36.1783 | 36.4274 | 37.2633 | 36.1698 | 32.8878 | 32.5934 | 34.4531 | 34.7314 | 32.9008 | 34.8698 | 34.7508 | 34.2286 | 34.5204 | 34.3936 | 34.3351 | 33.9287 | 34.5135 | 36.1493 | 34.7751 | 36.5721 | 36.5059 | 33.2203 | 95.2074 | 95.6429 | 94.5255
2022-09-08 06:46 | 8:56 | 18.8141 | 19.6506 | 22.2237 | 35.2869 | 34.303 | 34.0912 | 34.5909 | 35.5538 | 36.5576 | 37.5813 | 36.9735 | 38.2065 | 34.2945 | 34.3834 | 34.0272 | 35.0962 | 34.7525 | 35.3 | 35.9847 | 36.38 | 21.3753 | 18.2185 | 94.4125 | 33.23 | 32.7905 | 34.7179 | 32.8835 | 32.7602 | 33.1767 | 34.4132 | 33.9716 | 33.8161 | 37.0905 | 36.1731 | 33.16 | 34.2853 | 36.2049 | 36.4334 | 37.283 | 36.1887 | 32.8822 | 32.6035 | 34.4646 | 34.7399 | 32.9008 | 34.8798 | 34.741 | 34.2417 | 34.5062 | 34.3852 | 34.3438 | 33.932 | 34.5204 | 36.1461 | 34.7837 | 36.5576 | 36.4982 | 33.2363 | 95.2159 | 95.7039 | 94.5568
2022-09-08 06:46 | 8:56 | 18.749 | 19.4882 | 22.1527 | 35.2647 | 34.2928 | 34.0826 | 34.6265 | 35.5785 | 36.5548 | 37.5936 | 36.9814 | 38.2317 | 34.3198 | 34.3804 | 34.0207 | 35.0908 | 34.7636 | 35.2985 | 35.986 | 36.3792 | 21.3667 | 18.2295 | 94.4417 | 32.8768 | 32.7971 | 34.6975 | 32.8956 | 32.7566 | 33.1609 | 34.4208 | 33.978 | 33.8267 | 37.0977 | 36.1575 | 33.1731 | 34.2848 | 36.1992 | 36.4245 | 37.2809 | 36.1867 | 32.8737 | 32.6025 | 34.4575 | 34.7374 | 32.9118 | 34.8929 | 34.7555 | 34.2426 | 34.5082 | 34.3935 | 34.332 | 33.9617 | 34.5062 | 36.1697 | 34.7614 | 36.5862 | 36.5106 | 33.2362 | 95.4149 | 95.8498 | 94.7455
2022-09-08 06:46 | 8:56 | 18.6997 | 19.4513 | 22.071 | 35.2003 | 34.2835 | 34.0868 | 34.6264 | 35.5628 | 36.5564 | 37.5714 | 36.9883 | 38.2201 | 34.2975 | 34.3854 | 34.0171 | 35.0864 | 34.7754 | 35.3054 | 35.9809 | 36.3825 | 21.3585 | 18.1318 | 94.5763 | 32.8959 | 32.7726 | 34.6963 | 32.882 | 32.7643 | 33.1759 | 34.4166 | 33.9789 | 33.8333 | 37.0997 | 36.1996 | 33.1479 | 34.2891 | 36.1731 | 36.4292 | 37.2598 | 36.1783 | 32.8629 | 32.5826 | 34.4909 | 34.7463 | 32.9064 | 34.8688 | 34.7413 | 34.2332 | 34.5172 | 34.3933 | 34.3407 | 33.9504 | 34.5082 | 36.1762 | 34.7761 | 36.597 | 36.5033 | 33.2329 | 95.4159 | 95.8327 | 94.6934
2022-09-08 06:46 | 8:56 | 18.6422 | 19.3675 | 21.9827 | 35.145 | 34.272 | 34.1026 | 34.604 | 35.5735 | 36.5577 | 37.5692 | 36.9793 | 38.2266 | 34.311 | 34.387 | 34.0071 | 35.0931 | 34.7567 | 35.3002 | 35.9635 | 36.3604 | 21.3324 | 18.0264 | 94.5159 | 32.9608 | 32.7802 | 34.697 | 32.8878 | 32.7488 | 33.1737 | 34.4055 | 33.9793 | 33.8188 | 37.1038 | 36.1654 | 33.1642 | 34.285 | 36.1575 | 36.4317 | 37.2718 | 36.2049 | 32.8486 | 32.5845 | 34.4637 | 34.736 | 32.9327 | 34.8901 | 34.7649 | 34.2406 | 34.5361 | 34.4112 | 34.3383 | 33.9377 | 34.5172 | 36.1617 | 34.7583 | 36.5797 | 36.4957 | 33.1986 | 95.3512 | 95.7544 | 94.5735
2022-09-08 06:46 | 8:56 | 18.5902 | 19.2716 | 21.8463 | 35.1358 | 34.3029 | 34.0764 | 34.6293 | 35.5882 | 36.5683 | 37.574 | 36.9877 | 38.217 | 34.2995 | 34.3774 | 34.0078 | 35.0714 | 34.7665 | 35.284 | 35.9619 | 36.3624 | 21.3182 | 17.9962 | 94.3598 | 32.8819 | 32.7917 | 34.7012 | 32.8822 | 32.7759 | 33.16 | 34.4152 | 33.9784 | 33.8287 | 37.096 | 36.1814 | 33.1561 | 34.2712 | 36.1996 | 36.4257 | 37.2449 | 36.1992 | 32.8697 | 32.5918 | 34.4557 | 34.7372 | 32.8903 | 34.9122 | 34.7473 | 34.2448 | 34.5264 | 34.4102 | 34.3452 | 33.9383 | 34.5361 | 36.1683 | 34.7803 | 36.5795 | 36.4997 | 33.2269 | 95.1142 | 95.4993 | 94.3782
2022-09-08 06:47 | 8:56 | 18.4877 | 19.1915 | 21.7745 | 35.1795 | 34.2874 | 34.0867 | 34.6075 | 35.5473 | 36.5621 | 37.5736 | 36.9995 | 38.1984 | 34.3152 | 34.3795 | 34.0053 | 35.0963 | 34.7537 | 35.284 | 35.968 | 36.3659 | 21.3473 | 17.9363 | 94.2505 | 32.8227 | 32.7811 | 34.6979 | 32.8737 | 32.7757 | 33.1731 | 34.4181 | 33.9864 | 33.8102 | 37.0955 | 36.174 | 33.1591 | 34.2983 | 36.1654 | 36.4162 | 37.2697 | 36.1731 | 32.8654 | 32.5807 | 34.4654 | 34.7278 | 32.898 | 34.8823 | 34.7707 | 34.2515 | 34.5442 | 34.3972 | 34.3527 | 33.9494 | 34.5264 | 36.1579 | 34.766 | 36.5668 | 36.4992 | 33.2036 | 94.8874 | 95.2567 | 94.2381
2022-09-08 06:47 | 8:57 | 18.4305 | 19.1315 | 21.705 | 35.1063 | 34.2985 | 34.0853 | 34.5946 | 35.5533 | 36.5561 | 37.5471 | 36.9723 | 38.2068 | 34.312 | 34.372 | 33.9782 | 35.0934 | 34.7595 | 35.2653 | 35.9549 | 36.3497 | 21.3397 | 17.8515 | 94.1012 | 32.8013 | 32.7667 | 34.6802 | 32.8629 | 32.76 | 33.1479 | 34.4133 | 33.9617 | 33.8075 | 37.0989 | 36.1651 | 33.1395 | 34.2849 | 36.1814 | 36.4121 | 37.2487 | 36.1575 | 32.8639 | 32.5522 | 34.433 | 34.7046 | 32.8767 | 34.9189 | 34.7569 | 34.2489 | 34.5428 | 34.399 | 34.3428 | 33.9229 | 34.5442 | 36.1408 | 34.7726 | 36.5721 | 36.4923 | 33.1886 | 94.7001 | 94.9997 | 94.0898
2022-09-08 06:47 | 8:57 | 18.4119 | 19.0647 | 21.6454 | 35.1489 | 34.302 | 34.0731 | 34.5895 | 35.5522 | 36.5425 | 37.5595 | 36.9786 | 38.2006 | 34.3025 | 34.3821 | 33.9999 | 35.0902 | 34.7529 | 35.2659 | 35.9596 | 36.3555 | 21.3377 | 17.9002 | 93.9564 | 32.9868 | 32.7639 | 34.6854 | 32.8486 | 32.7567 | 33.1642 | 34.3927 | 33.9646 | 33.8252 | 37.0963 | 36.1887 | 33.1601 | 34.2743 | 36.174 | 36.4081 | 37.273 | 36.1996 | 32.8591 | 32.5833 | 34.4412 | 34.7208 | 32.8948 | 34.9073 | 34.7761 | 34.2584 | 34.5469 | 34.3997 | 34.3482 | 33.9408 | 34.5428 | 36.1511 | 34.7485 | 36.5625 | 36.4984 | 33.1955 | 94.5014 | 94.7917 | 93.9312
2022-09-08 06:47 | 8:57 | 18.3599 | 18.9901 | 21.5943 | 35.1387 | 34.3034 | 34.0836 | 34.5479 | 35.562 | 36.5435 | 37.5483 | 36.9869 | 38.2082 | 34.3123 | 34.3728 | 33.9848 | 35.0742 | 34.7446 | 35.2525 | 35.956 | 36.3509 | 21.3348 | 17.8087 | 93.8871 | 32.8972 | 32.7679 | 34.6958 | 32.8697 | 32.7402 | 33.1561 | 34.3989 | 33.9633 | 33.8186 | 37.0849 | 36.201 | 33.1697 | 34.2864 | 36.1651 | 36.4181 | 37.2538 | 36.1654 | 32.856 | 32.5611 | 34.4212 | 34.7115 | 32.8632 | 34.898 | 34.7806 | 34.2592 | 34.5614 | 34.3953 | 34.3473 | 33.9275 | 34.5469 | 36.1205 | 34.7814 | 36.5688 | 36.4801 | 33.1797 | 94.3231 | 94.6525 | 93.8106
2022-09-08 06:47 | 8:57 | 18.2923 | 18.9152 | 21.5273 | 35.0794 | 34.3089 | 34.0649 | 34.5682 | 35.566 | 36.554 | 37.5532 | 36.9858 | 38.2005 | 34.2951 | 34.3738 | 33.9785 | 35.0764 | 34.7607 | 35.2758 | 35.9337 | 36.3466 | 21.3577 | 17.7782 | 93.8306 | 32.7944 | 32.7577 | 34.7054 | 32.8654 | 32.7353 | 33.1591 | 34.3989 | 33.9609 | 33.8186 | 37.0997 | 36.154 | 33.1555 | 34.2729 | 36.1887 | 36.4309 | 37.2504 | 36.1814 | 32.8712 | 32.5675 | 34.431 | 34.7096 | 32.8756 | 34.9271 | 34.7687 | 34.2644 | 34.5579 | 34.3881 | 34.3667 | 33.9191 | 34.5614 | 36.138 | 34.7689 | 36.5814 | 36.4843 | 33.1735 | 94.1863 | 94.5124 | 93.7991
2022-09-08 06:47 | 8:57 | 18.2649 | 18.8377 | 21.4587 | 35.14 | 34.3035 | 34.0774 | 34.6048 | 35.5526 | 36.5524 | 37.5374 | 36.9983 | 38.2105 | 34.3191 | 34.3427 | 33.9767 | 35.0969 | 34.7523 | 35.2632 | 35.9503 | 36.3608 | 21.3592 | 17.7565 | 93.8661 | 32.8734 | 32.751 | 34.6877 | 32.8639 | 32.7337 | 33.1395 | 34.4059 | 33.983 | 33.8127 | 37.0759 | 36.1974 | 33.1482 | 34.2994 | 36.201 | 36.4102 | 37.2425 | 36.174 | 32.8617 | 32.5564 | 34.4318 | 34.6955 | 32.8816 | 34.9286 | 34.7845 | 34.2636 | 34.5718 | 34.3895 | 34.3587 | 33.9174 | 34.5579 | 36.1291 | 34.7712 | 36.5885 | 36.4764 | 33.1711 | 94.116 | 94.3764 | 93.7429
2022-09-08 06:48 | 8:58 | 18.1952 | 18.7553 | 21.3894 | 34.9742 | 34.3069 | 34.096 | 34.5957 | 35.5533 | 36.5419 | 37.5502 | 36.993 | 38.2147 | 34.326 | 34.3797 | 33.9791 | 35.0939 | 34.7713 | 35.2803 | 35.9302 | 36.3465 | 21.3598 | 17.717 | 93.7504 | 32.5782 | 32.746 | 34.7109 | 32.8591 | 32.7342 | 33.1601 | 34.3899 | 33.9875 | 33.7998 | 37.0911 | 36.1557 | 33.1125 | 34.2876 | 36.154 | 36.4194 | 37.2407 | 36.1651 | 32.8647 | 32.5717 | 34.4512 | 34.6914 | 32.8788 | 34.9239 | 34.7905 | 34.249 | 34.5798 | 34.3994 | 34.3461 | 33.9414 | 34.5718 | 36.1361 | 34.7615 | 36.562 | 36.4859 | 33.1936 | 93.9839 | 94.2939 | 93.6759
2022-09-08 06:48 | 8:58 | 18.1818 | 18.7349 | 21.3454 | 35.009 | 34.3106 | 34.0923 | 34.5861 | 35.5459 | 36.5356 | 37.5298 | 36.9846 | 38.2199 | 34.3135 | 34.3911 | 33.9935 | 35.0828 | 34.7461 | 35.27 | 35.9292 | 36.3556 | 21.3752 | 17.6794 | 93.7071 | 32.7013 | 32.7577 | 34.6966 | 32.856 | 32.7331 | 33.1697 | 34.3904 | 33.9776 | 33.8324 | 37.0917 | 36.1726 | 33.1459 | 34.2808 | 36.1974 | 36.4196 | 37.2487 | 36.1887 | 32.8562 | 32.5479 | 34.4251 | 34.695 | 32.8823 | 34.9364 | 34.777 | 34.2604 | 34.5926 | 34.4104 | 34.3722 | 33.9376 | 34.5798 | 36.1205 | 34.7703 | 36.5782 | 36.4707 | 33.1819 | 93.926 | 94.2097 | 93.6678
2022-09-08 06:48 | 8:58 | 18.2391 | 18.7136 | 21.2673 | 35.0299 | 34.2978 | 34.1016 | 34.5885 | 35.5487 | 36.553 | 37.548 | 37.0022 | 38.2136 | 34.3122 | 34.3755 | 33.9789 | 35.1047 | 34.7565 | 35.2602 | 35.9317 | 36.3293 | 21.3839 | 17.6881 | 93.6386 | 32.8955 | 32.7478 | 34.6972 | 32.8712 | 32.7495 | 33.1555 | 34.3955 | 33.9905 | 33.829 | 37.0825 | 36.1733 | 33.134 | 34.293 | 36.1557 | 36.4329 | 37.2339 | 36.201 | 32.8767 | 32.5417 | 34.4282 | 34.6895 | 32.8681 | 34.9199 | 34.7831 | 34.2658 | 34.5829 | 34.41 | 34.3576 | 33.9079 | 34.5926 | 36.1369 | 34.7648 | 36.5764 | 36.4727 | 33.1562 | 93.8024 | 94.0885 | 93.5994
2022-09-08 06:48 | 8:58 | 18.0685 | 18.6151 | 21.2379 | 34.9822 | 34.2906 | 34.0834 | 34.544 | 35.5474 | 36.5434 | 37.5358 | 37.0012 | 38.2172 | 34.3412 | 34.382 | 33.9838 | 35.084 | 34.7583 | 35.2626 | 35.938 | 36.3513 | 21.3872 | 17.6081 | 93.6205 | 32.7973 | 32.7426 | 34.6849 | 32.8617 | 32.7426 | 33.1482 | 34.3825 | 33.9693 | 33.8058 | 37.0941 | 36.1474 | 33.1718 | 34.2793 | 36.1726 | 36.4274 | 37.2384 | 36.154 | 32.8751 | 32.5501 | 34.4207 | 34.6978 | 32.8425 | 34.9312 | 34.7774 | 34.2647 | 34.5959 | 34.4086 | 34.3737 | 33.8713 | 34.5829 | 36.1206 | 34.7694 | 36.5737 | 36.4688 | 33.1763 | 93.7599 | 94.0301 | 93.526
2022-09-08 06:48 | 8:58 | 18.0318 | 18.5567 | 21.1206 | 34.9705 | 34.303 | 34.0987 | 34.5868 | 35.5545 | 36.5215 | 37.545 | 37.0006 | 38.2172 | 34.3055 | 34.3912 | 33.9823 | 35.1037 | 34.7553 | 35.2716 | 35.9231 | 36.3554 | 21.403 | 17.6072 | 93.5879 | 32.6434 | 32.7601 | 34.6707 | 32.8647 | 32.7439 | 33.1125 | 34.4081 | 33.9809 | 33.8295 | 37.1177 | 36.1818 | 33.1559 | 34.2778 | 36.1733 | 36.4236 | 37.2225 | 36.1974 | 32.8693 | 32.5509 | 34.4231 | 34.6889 | 32.8331 | 34.9281 | 34.7835 | 34.2524 | 34.5986 | 34.3999 | 34.3758 | 33.9025 | 34.5959 | 36.0988 | 34.7685 | 36.5836 | 36.4672 | 33.1697 | 93.7008 | 93.9569 | 93.5562
2022-09-08 06:48 | 8:58 | 18.0232 | 18.5749 | 21.1138 | 34.9895 | 34.3096 | 34.1017 | 34.5442 | 35.5376 | 36.5435 | 37.5326 | 36.992 | 38.2152 | 34.3285 | 34.3907 | 33.9811 | 35.096 | 34.7526 | 35.2796 | 35.923 | 36.3484 | 21.3846 | 17.5841 | 93.5479 | 32.8302 | 32.7415 | 34.7095 | 32.8562 | 32.742 | 33.1459 | 34.3739 | 33.9694 | 33.8381 | 37.0874 | 36.1774 | 33.145 | 34.2856 | 36.1474 | 36.4257 | 37.2337 | 36.1557 | 32.8585 | 32.5367 | 34.4271 | 34.684 | 32.8496 | 34.9229 | 34.7978 | 34.2657 | 34.6172 | 34.4051 | 34.3654 | 33.9159 | 34.5986 | 36.1148 | 34.7765 | 36.5813 | 36.4871 | 33.1634 | 93.6174 | 93.8888 | 93.4682
2022-09-08 06:49 | 8:58 | 17.9357 | 18.4692 | 21.0493 | 34.884 | 34.3166 | 34.0916 | 34.5867 | 35.5503 | 36.5437 | 37.5322 | 36.9794 | 38.2032 | 34.3392 | 34.3867 | 33.9867 | 35.1031 | 34.7546 | 35.2729 | 35.9203 | 36.3385 | 21.3544 | 17.5487 | 93.4619 | 32.7608 | 32.7424 | 34.6892 | 32.8767 | 32.7567 | 33.134 | 34.3791 | 33.9734 | 33.8261 | 37.0853 | 36.1926 | 33.1516 | 34.2891 | 36.1818 | 36.4291 | 37.2533 | 36.1726 | 32.8298 | 32.5444 | 34.4175 | 34.6928 | 32.8303 | 34.9221 | 34.8125 | 34.2619 | 34.6093 | 34.408 | 34.3736 | 33.9163 | 34.6172 | 36.0946 | 34.7644 | 36.5749 | 36.4549 | 33.1665 | 93.5743 | 93.8947 | 93.3905
2022-09-08 06:49 | 8:59 | 17.9364 | 18.446 | 20.9928 | 34.9015 | 34.3011 | 34.0941 | 34.5665 | 35.5516 | 36.5387 | 37.5383 | 37.0121 | 38.2227 | 34.32 | 34.3711 | 33.9821 | 35.0768 | 34.7597 | 35.2637 | 35.9187 | 36.3487 | 21.3732 | 17.6234 | 93.3884 | 32.7564 | 32.7475 | 34.6959 | 32.8751 | 32.74 | 33.1718 | 34.3883 | 33.9893 | 33.8218 | 37.0921 | 36.1892 | 33.1327 | 34.2991 | 36.1774 | 36.4201 | 37.2456 | 36.1733 | 32.8725 | 32.5518 | 34.4304 | 34.6982 | 32.872 | 34.9409 | 34.7854 | 34.2921 | 34.5912 | 34.3934 | 34.365 | 33.9164 | 34.6093 | 36.1386 | 34.7736 | 36.5744 | 36.4655 | 33.1736 | 93.5622 | 93.828 | 93.4216
2022-09-08 06:49 | 8:59 | 18.0403 | 18.3843 | 20.9821 | 34.8972 | 34.3074 | 34.1046 | 34.5686 | 35.5536 | 36.5398 | 37.5453 | 36.9981 | 38.2279 | 34.3113 | 34.3948 | 33.9926 | 35.1034 | 34.76 | 35.2642 | 35.9174 | 36.3426 | 21.3509 | 17.5302 | 93.4592 | 32.703 | 32.7579 | 34.7007 | 32.8693 | 32.7387 | 33.1559 | 34.3841 | 33.9931 | 33.8246 | 37.102 | 36.1928 | 33.1432 | 34.3022 | 36.1926 | 36.4207 | 37.2191 | 36.1474 | 32.8594 | 32.5389 | 34.4203 | 34.6888 | 32.8212 | 34.9503 | 34.7775 | 34.2835 | 34.6071 | 34.4028 | 34.3742 | 33.8982 | 34.5912 | 36.112 | 34.7785 | 36.5649 | 36.4657 | 33.1651 | 93.5589 | 93.7531 | 93.4391
2022-09-08 06:49 | 8:59 | 17.8692 | 18.3553 | 20.9933 | 34.7759 | 34.314 | 34.1057 | 34.5902 | 35.5513 | 36.5485 | 37.5358 | 37.0041 | 38.2154 | 34.3247 | 34.3971 | 33.9836 | 35.1142 | 34.7554 | 35.2615 | 35.924 | 36.3586 | 21.3529 | 17.4465 | 93.386 | 32.6663 | 32.7542 | 34.6966 | 32.8585 | 32.726 | 33.145 | 34.383 | 34.0114 | 33.8332 | 37.0832 | 36.1733 | 33.1513 | 34.2896 | 36.1892 | 36.4188 | 37.2321 | 36.1818 | 32.8655 | 32.5442 | 34.4196 | 34.6991 | 32.8629 | 34.9589 | 34.788 | 34.2763 | 34.6388 | 34.3976 | 34.3771 | 33.8994 | 34.6071 | 36.1128 | 34.7591 | 36.5873 | 36.4755 | 33.1568 | 93.493 | 93.6472 | 93.3521
2022-09-08 06:49 | 8:59 | 17.8083 | 18.2999 | 20.8588 | 34.8206 | 34.3114 | 34.0801 | 34.5705 | 35.5742 | 36.5426 | 37.538 | 36.9988 | 38.2248 | 34.3203 | 34.3993 | 34.0058 | 35.1193 | 34.7639 | 35.2597 | 35.9208 | 36.3437 | 21.3444 | 17.4358 | 93.3161 | 32.7323 | 32.7417 | 34.6854 | 32.8298 | 32.7392 | 33.1516 | 34.3703 | 33.9843 | 33.8196 | 37.1001 | 36.1849 | 33.1562 | 34.3057 | 36.1928 | 36.4368 | 37.2164 | 36.1774 | 32.8488 | 32.528 | 34.429 | 34.7062 | 32.8281 | 34.9422 | 34.788 | 34.2662 | 34.6239 | 34.396 | 34.3799 | 33.9062 | 34.6388 | 36.1303 | 34.7698 | 36.5609 | 36.4753 | 33.1791 | 93.382 | 93.5431 | 93.235
2022-09-08 06:49 | 8:59 | 17.7944 | 18.2538 | 20.8464 | 34.7454 | 34.3255 | 34.1152 | 34.577 | 35.5561 | 36.5519 | 37.5517 | 37.0017 | 38.2329 | 34.3395 | 34.3896 | 33.9941 | 35.1005 | 34.7659 | 35.2609 | 35.9307 | 36.3369 | 21.3338 | 17.4215 | 93.225 | 32.5695 | 32.7295 | 34.699 | 32.8725 | 32.7357 | 33.1327 | 34.388 | 33.9885 | 33.833 | 37.1002 | 36.1702 | 33.1379 | 34.2816 | 36.1733 | 36.4258 | 37.2336 | 36.1926 | 32.8673 | 32.5383 | 34.4493 | 34.7081 | 32.8212 | 34.9552 | 34.7956 | 34.2883 | 34.6256 | 34.3892 | 34.3882 | 33.8863 | 34.6239 | 36.1396 | 34.7959 | 36.5834 | 36.4869 | 33.1683 | 93.256 | 93.4777 | 93.1431
2022-09-08 06:50 | 9:00 | 17.8751 | 18.1856 | 20.7746 | 34.7172 | 34.3178 | 34.1018 | 34.5887 | 35.5592 | 36.5423 | 37.5344 | 37.0072 | 38.2233 | 34.3274 | 34.4007 | 34.0198 | 35.1121 | 34.7476 | 35.2732 | 35.9205 | 36.3473 | 21.3347 | 17.4348 | 93.1731 | 32.6679 | 32.7335 | 34.688 | 32.8594 | 32.7163 | 33.1432 | 34.3785 | 33.9848 | 33.8473 | 37.0965 | 36.1713 | 33.1506 | 34.3181 | 36.1849 | 36.4246 | 37.2265 | 36.1892 | 32.8621 | 32.5669 | 34.4334 | 34.7305 | 32.8304 | 34.9741 | 34.7846 | 34.2702 | 34.6313 | 34.3887 | 34.3901 | 33.889 | 34.6256 | 36.1344 | 34.7747 | 36.5701 | 36.4944 | 33.181 | 93.1731 | 93.4059 | 93.1335
2022-09-08 06:50 | 9:00 | 17.8946 | 18.2163 | 20.7909 | 34.8338 | 34.3201 | 34.0929 | 34.5698 | 35.5597 | 36.5527 | 37.5388 | 37.0272 | 38.2217 | 34.3328 | 34.4009 | 34.0089 | 35.1039 | 34.7699 | 35.264 | 35.9333 | 36.3537 | 21.3223 | 17.402 | 93.1566 | 32.5684 | 32.7443 | 34.6803 | 32.8655 | 32.7487 | 33.1513 | 34.3956 | 33.9983 | 33.8393 | 37.083 | 36.1848 | 33.1518 | 34.3025 | 36.1702 | 36.4438 | 37.2179 | 36.1928 | 32.8512 | 32.5492 | 34.4327 | 34.7043 | 32.8218 | 34.9802 | 34.783 | 34.2901 | 34.6337 | 34.3996 | 34.3811 | 33.9072 | 34.6313 | 36.1399 | 34.7567 | 36.5861 | 36.4748 | 33.1727 | 93.1263 | 93.3084 | 93.0639
2022-09-08 06:50 | 9:00 | 17.7126 | 18.0891 | 20.705 | 34.7551 | 34.3068 | 34.1025 | 34.6007 | 35.5478 | 36.5372 | 37.5439 | 36.989 | 38.2431 | 34.3128 | 34.4088 | 33.9797 | 35.1215 | 34.7681 | 35.2659 | 35.9276 | 36.3494 | 21.3101 | 17.3257 | 93.1172 | 32.7221 | 32.7475 | 34.7116 | 32.8488 | 32.7401 | 33.1562 | 34.3951 | 34.0024 | 33.8378 | 37.098 | 36.176 | 33.1402 | 34.3012 | 36.1713 | 36.4334 | 37.2206 | 36.1733 | 32.8662 | 32.5343 | 34.4167 | 34.7118 | 32.825 | 34.9786 | 34.7948 | 34.2698 | 34.6241 | 34.3967 | 34.3834 | 33.9008 | 34.6337 | 36.1406 | 34.7606 | 36.5761 | 36.4833 | 33.1839 | 93.053 | 93.2246 | 92.9989
2022-09-08 06:50 | 9:00 | 17.6508 | 18.0721 | 20.6949 | 34.8605 | 34.3392 | 34.0949 | 34.5754 | 35.567 | 36.5356 | 37.5448 | 37.0134 | 38.2464 | 34.3345 | 34.4076 | 34.0051 | 35.1207 | 34.7543 | 35.2654 | 35.9241 | 36.3572 | 21.2971 | 17.3244 | 93.0001 | 33.0215 | 32.7356 | 34.6904 | 32.8673 | 32.7373 | 33.1379 | 34.39 | 33.9841 | 33.8354 | 37.0919 | 36.1797 | 33.1416 | 34.283 | 36.1848 | 36.4488 | 37.2164 | 36.1849 | 32.8609 | 32.518 | 34.4382 | 34.7109 | 32.8199 | 34.9939 | 34.7839 | 34.2599 | 34.6386 | 34.4045 | 34.3804 | 33.8998 | 34.6241 | 36.1333 | 34.7673 | 36.5797 | 36.465 | 33.1926 | 92.8872 | 93.056 | 92.9177
2022-09-08 06:50 | 9:00 | 17.6216 | 18.0096 | 20.5944 | 34.6609 | 34.3227 | 34.1108 | 34.5833 | 35.5739 | 36.5483 | 37.5405 | 37.0143 | 38.2415 | 34.3254 | 34.4104 | 33.9946 | 35.1167 | 34.7615 | 35.2743 | 35.9289 | 36.3459 | 21.2683 | 17.2902 | 92.9548 | 32.799 | 32.7389 | 34.6937 | 32.8621 | 32.7486 | 33.1506 | 34.3883 | 33.9975 | 33.8343 | 37.101 | 36.1776 | 33.1526 | 34.2989 | 36.176 | 36.4315 | 37.2374 | 36.1702 | 32.8562 | 32.5298 | 34.4318 | 34.7077 | 32.8055 | 34.9865 | 34.7888 | 34.2579 | 34.6481 | 34.393 | 34.3854 | 33.9031 | 34.6386 | 36.1355 | 34.7793 | 36.6011 | 36.4785 | 33.1837 | 92.7622 | 92.9423 | 92.8679
2022-09-08 06:50 | 9:00 | 17.5965 | 17.9951 | 20.5477 | 34.7383 | 34.3351 | 34.0978 | 34.5868 | 35.5753 | 36.5554 | 37.5316 | 37.0013 | 38.2464 | 34.3324 | 34.3919 | 34.0001 | 35.1237 | 34.7796 | 35.2675 | 35.9154 | 36.3565 | 21.2574 | 17.2388 | 92.9036 | 32.6497 | 32.7279 | 34.6827 | 32.8512 | 32.7373 | 33.1518 | 34.3905 | 33.998 | 33.8253 | 37.0919 | 36.1807 | 33.1422 | 34.2951 | 36.1797 | 36.4387 | 37.2147 | 36.1713 | 32.8587 | 32.542 | 34.4157 | 34.7132 | 32.8073 | 34.9823 | 34.789 | 34.2835 | 34.638 | 34.3789 | 34.387 | 33.8849 | 34.6481 | 36.14 | 34.7793 | 36.5837 | 36.4776 | 33.2032 | 92.6841 | 92.8211 | 92.7432
2022-09-08 06:51 | 9:00 | 17.5136 | 17.9411 | 20.5047 | 34.6691 | 34.3438 | 34.1197 | 34.598 | 35.5615 | 36.5637 | 37.5235 | 37.0214 | 38.2482 | 34.3556 | 34.415 | 33.9902 | 35.1062 | 34.761 | 35.2595 | 35.9147 | 36.3473 | 21.2262 | 17.237 | 92.7495 | 32.5315 | 32.7292 | 34.6826 | 32.8662 | 32.7383 | 33.1402 | 34.3961 | 33.998 | 33.8334 | 37.0952 | 36.1717 | 33.1358 | 34.306 | 36.1776 | 36.4367 | 37.2156 | 36.1848 | 32.8314 | 32.5383 | 34.4359 | 34.7085 | 32.8124 | 35.0187 | 34.8 | 34.2687 | 34.6683 | 34.4024 | 34.3774 | 33.9033 | 34.638 | 36.135 | 34.7657 | 36.5732 | 36.4752 | 33.1981 | 92.5291 | 92.6393 | 92.6497
2022-09-08 06:51 | 9:01 | 17.6078 | 17.9269 | 20.4843 | 34.6445 | 34.332 | 34.1108 | 34.5784 | 35.562 | 36.5415 | 37.5401 | 37.0344 | 38.232 | 34.3549 | 34.4018 | 33.9872 | 35.1232 | 34.748 | 35.2803 | 35.9216 | 36.3629 | 21.2289 | 17.243 | 92.69 | 32.6843 | 32.7155 | 34.6765 | 32.8609 | 32.7455 | 33.1416 | 34.3826 | 33.9849 | 33.8401 | 37.0997 | 36.1662 | 33.1591 | 34.3113 | 36.1807 | 36.433 | 37.2385 | 36.176 | 32.8379 | 32.5331 | 34.4295 | 34.7285 | 32.7773 | 35.0046 | 34.7841 | 34.2935 | 34.6732 | 34.3758 | 34.3795 | 33.8868 | 34.6683 | 36.1533 | 34.7693 | 36.591 | 36.4809 | 33.1954 | 92.4095 | 92.5676 | 92.5617
2022-09-08 06:51 | 9:01 | 17.4563 | 17.8136 | 20.4575 | 34.6055 | 34.3407 | 34.1202 | 34.5827 | 35.5756 | 36.5438 | 37.53 | 37.0043 | 38.2453 | 34.3554 | 34.3877 | 33.9966 | 35.1111 | 34.7795 | 35.2633 | 35.9115 | 36.3587 | 21.2468 | 17.2511 | 92.515 | 32.7793 | 32.7433 | 34.6716 | 32.8562 | 32.7147 | 33.1526 | 34.3808 | 34.0067 | 33.8357 | 37.1047 | 36.1584 | 33.1345 | 34.3128 | 36.1717 | 36.4281 | 37.2473 | 36.1797 | 32.8502 | 32.5302 | 34.423 | 34.7188 | 32.7985 | 35.0083 | 34.7904 | 34.2831 | 34.6487 | 34.3835 | 34.372 | 33.8907 | 34.6732 | 36.1348 | 34.7677 | 36.5752 | 36.5027 | 33.1837 | 92.2462 | 92.3647 | 92.4749
2022-09-08 06:51 | 9:01 | 17.4226 | 17.8132 | 20.4155 | 34.6932 | 34.3383 | 34.1236 | 34.595 | 35.5697 | 36.5425 | 37.5509 | 37.0109 | 38.2317 | 34.3584 | 34.4101 | 33.9819 | 35.1186 | 34.7782 | 35.2821 | 35.9113 | 36.343 | 21.2282 | 17.1272 | 92.5084 | 32.5995 | 32.7521 | 34.6659 | 32.8587 | 32.7311 | 33.1422 | 34.3763 | 34.004 | 33.8461 | 37.1049 | 36.1616 | 33.1413 | 34.3113 | 36.1662 | 36.4414 | 37.2215 | 36.1776 | 32.8398 | 32.5311 | 34.4599 | 34.7129 | 32.7789 | 35.021 | 34.7866 | 34.2733 | 34.662 | 34.394 | 34.3821 | 33.8903 | 34.6487 | 36.1611 | 34.7637 | 36.5907 | 36.4807 | 33.1777 | 92.1373 | 92.2286 | 92.3454
2022-09-08 06:51 | 9:01 | 17.3815 | 17.7692 | 20.3788 | 34.6536 | 34.3452 | 34.121 | 34.5726 | 35.5651 | 36.5715 | 37.55 | 37.0235 | 38.2673 | 34.3529 | 34.4087 | 33.9874 | 35.1175 | 34.75 | 35.2738 | 35.9263 | 36.3665 | 21.2057 | 17.121 | 92.4001 | 32.6195 | 32.7205 | 34.676 | 32.8314 | 32.739 | 33.1358 | 34.3875 | 33.9947 | 33.842 | 37.0899 | 36.1595 | 33.1255 | 34.3198 | 36.1584 | 36.4355 | 37.2266 | 36.1807 | 32.8157 | 32.5145 | 34.4363 | 34.7142 | 32.7831 | 35.0189 | 34.7872 | 34.27 | 34.6666 | 34.3846 | 34.3728 | 33.8727 | 34.662 | 36.1683 | 34.7843 | 36.5892 | 36.4723 | 33.1911 | 92.0472 | 92.1638 | 92.2994
2022-09-08 06:51 | 9:01 | 17.3469 | 17.7408 | 20.3328 | 34.695 | 34.3527 | 34.1077 | 34.579 | 35.5607 | 36.5414 | 37.5678 | 37.035 | 38.2313 | 34.3337 | 34.4137 | 33.9994 | 35.1252 | 34.7476 | 35.2854 | 35.9162 | 36.3683 | 21.2007 | 17.0625 | 92.4081 | 32.3688 | 32.734 | 34.6761 | 32.8379 | 32.7159 | 33.1591 | 34.3867 | 34.0174 | 33.8328 | 37.1067 | 36.1813 | 33.1409 | 34.3097 | 36.1616 | 36.4455 | 37.2176 | 36.1717 | 32.8162 | 32.5193 | 34.4275 | 34.7393 | 32.7818 | 35.0206 | 34.8089 | 34.2664 | 34.6702 | 34.3948 | 34.3738 | 33.8768 | 34.6666 | 36.1351 | 34.7693 | 36.5812 | 36.4839 | 33.1993 | 92.1206 | 92.1908 | 92.4776
2022-09-08 06:52 | 9:02 | 17.37 | 17.7385 | 20.3189 | 34.5352 | 34.3428 | 34.1168 | 34.5855 | 35.5548 | 36.5532 | 37.5566 | 37.0202 | 38.251 | 34.3691 | 34.4213 | 34.0272 | 35.1034 | 34.7646 | 35.2817 | 35.9244 | 36.3604 | 21.1643 | 17.1171 | 92.4217 | 32.5639 | 32.7306 | 34.676 | 32.8502 | 32.7192 | 33.1345 | 34.3832 | 33.9827 | 33.8421 | 37.1059 | 36.1534 | 33.1237 | 34.3258 | 36.1595 | 36.445 | 37.2382 | 36.1662 | 32.8227 | 32.5087 | 34.4233 | 34.7258 | 32.7794 | 35.0322 | 34.811 | 34.2876 | 34.6651 | 34.3811 | 34.3427 | 33.8848 | 34.6702 | 36.1481 | 34.7753 | 36.5816 | 36.4922 | 33.1944 | 92.1762 | 92.2573 | 92.4039
2022-09-08 06:52 | 9:02 | 17.3644 | 17.7166 | 20.3049 | 34.6044 | 34.3482 | 34.1179 | 34.567 | 35.571 | 36.5536 | 37.5563 | 37.0165 | 38.2388 | 34.3538 | 34.4203 | 34.0087 | 35.1371 | 34.7719 | 35.2556 | 35.9167 | 36.3638 | 21.1748 | 17.0945 | 92.5133 | 32.4632 | 32.7359 | 34.6838 | 32.8398 | 32.7434 | 33.1413 | 34.4001 | 34.006 | 33.8523 | 37.1099 | 36.1581 | 33.1375 | 34.3159 | 36.1813 | 36.4459 | 37.2275 | 36.1584 | 32.8226 | 32.5281 | 34.4482 | 34.7229 | 32.7483 | 35.0413 | 34.7976 | 34.2728 | 34.6731 | 34.3827 | 34.3797 | 33.8713 | 34.6651 | 36.1463 | 34.7722 | 36.5711 | 36.4905 | 33.2072 | 92.2738 | 92.352 | 92.5886
2022-09-08 06:52 | 9:02 | 17.2891 | 17.6406 | 20.2518 | 34.5284 | 34.3473 | 34.1112 | 34.5813 | 35.5609 | 36.5486 | 37.5473 | 37.026 | 38.2542 | 34.3608 | 34.4138 | 33.9907 | 35.1195 | 34.7624 | 35.2729 | 35.9257 | 36.3379 | 21.1546 | 17.0928 | 92.5485 | 32.6226 | 32.7309 | 34.6556 | 32.8157 | 32.7225 | 33.1255 | 34.3891 | 33.9932 | 33.8475 | 37.1083 | 36.1344 | 33.1371 | 34.3158 | 36.1534 | 36.4438 | 37.2102 | 36.1616 | 32.8305 | 32.5143 | 34.4323 | 34.732 | 32.7775 | 35.032 | 34.7928 | 34.2819 | 34.6689 | 34.3788 | 34.3911 | 33.8841 | 34.6731 | 36.1789 | 34.771 | 36.5713 | 36.473 | 33.1791 | 92.3438 | 92.497 | 92.6243
2022-09-08 06:52 | 9:02 | 17.2516 | 17.6133 | 20.2095 | 34.5495 | 34.3667 | 34.1321 | 34.5931 | 35.5637 | 36.5502 | 37.5459 | 37.0164 | 38.2583 | 34.3752 | 34.4019 | 34.0087 | 35.1265 | 34.7714 | 35.2715 | 35.8994 | 36.3575 | 21.1297 | 17.0385 | 92.7209 | 32.4401 | 32.7263 | 34.6713 | 32.8162 | 32.7228 | 33.1409 | 34.4055 | 34.0028 | 33.8478 | 37.1193 | 36.1531 | 33.115 | 34.2983 | 36.1581 | 36.4373 | 37.2395 | 36.1595 | 32.8083 | 32.4912 | 34.4454 | 34.7299 | 32.756 | 35.0465 | 34.7908 | 34.2796 | 34.6886 | 34.3685 | 34.3755 | 33.8749 | 34.6689 | 36.155 | 34.7518 | 36.5984 | 36.4963 | 33.1986 | 92.5671 | 92.6665 | 92.7844
2022-09-08 06:52 | 9:02 | 17.3155 | 17.6135 | 20.1508 | 34.5103 | 34.3587 | 34.1103 | 34.5794 | 35.5579 | 36.5504 | 37.5448 | 37.0217 | 38.2447 | 34.3791 | 34.4181 | 34.0035 | 35.1208 | 34.7678 | 35.2682 | 35.9171 | 36.3676 | 21.0616 | 17.0126 | 92.7325 | 32.5571 | 32.7195 | 34.6658 | 32.8227 | 32.7238 | 33.1237 | 34.384 | 33.9989 | 33.8351 | 37.118 | 36.1653 | 33.1137 | 34.2933 | 36.1344 | 36.4344 | 37.2138 | 36.1813 | 32.8063 | 32.507 | 34.4299 | 34.7256 | 32.7199 | 35.0418 | 34.797 | 34.3035 | 34.6795 | 34.3588 | 34.382 | 33.8874 | 34.6886 | 36.1545 | 34.7624 | 36.581 | 36.4929 | 33.1967 | 92.6412 | 92.7569 | 92.7116
2022-09-08 06:52 | 9:02 | 17.2245 | 17.609 | 20.1655 | 34.6556 | 34.3461 | 34.1047 | 34.5841 | 35.5728 | 36.5715 | 37.5485 | 37.0086 | 38.2345 | 34.3809 | 34.4279 | 33.9975 | 35.1133 | 34.7707 | 35.2751 | 35.9197 | 36.3735 | 21.0461 | 17.0232 | 92.7529 | 32.563 | 32.7226 | 34.6607 | 32.8226 | 32.7248 | 33.1375 | 34.3662 | 33.9927 | 33.8257 | 37.0968 | 36.1545 | 33.1308 | 34.2973 | 36.1531 | 36.4228 | 37.2273 | 36.1534 | 32.8006 | 32.5139 | 34.433 | 34.7172 | 32.7508 | 35.047 | 34.8018 | 34.3005 | 34.6868 | 34.3591 | 34.3912 | 33.8749 | 34.6795 | 36.1613 | 34.7424 | 36.5839 | 36.4973 | 33.2024 | 92.7401 | 92.8933 | 92.8455
2022-09-08 06:53 | 9:02 | 17.2375 | 17.5543 | 20.135 | 34.4547 | 34.3722 | 34.1198 | 34.5771 | 35.5659 | 36.5526 | 37.5379 | 37.0291 | 38.2373 | 34.3785 | 34.4259 | 34.0163 | 35.111 | 34.7608 | 35.2539 | 35.9021 | 36.3579 | 21.0112 | 17.0246 | 92.8139 | 32.4799 | 32.7104 | 34.6548 | 32.8305 | 32.7143 | 33.1371 | 34.3764 | 33.9931 | 33.8075 | 37.1016 | 36.127 | 33.1165 | 34.3002 | 36.1653 | 36.4316 | 37.2306 | 36.1581 | 32.8064 | 32.5183 | 34.4261 | 34.7261 | 32.7361 | 35.0654 | 34.8042 | 34.302 | 34.7065 | 34.3635 | 34.3907 | 33.868 | 34.6868 | 36.1564 | 34.7666 | 36.5904 | 36.479 | 33.2028 | 92.8565 | 93.0378 | 92.885
2022-09-08 06:53 | 9:03 | 17.3228 | 17.5618 | 20.1316 | 34.451 | 34.3576 | 34.1014 | 34.5859 | 35.5518 | 36.5467 | 37.5479 | 37.0199 | 38.2236 | 34.3936 | 34.429 | 33.9798 | 35.1205 | 34.7612 | 35.2719 | 35.9011 | 36.3569 | 20.97 | 16.9608 | 92.9607 | 32.3732 | 32.7326 | 34.6472 | 32.8083 | 32.6971 | 33.115 | 34.3679 | 33.9781 | 33.8085 | 37.1046 | 36.1534 | 33.1182 | 34.3107 | 36.1545 | 36.445 | 37.2152 | 36.1344 | 32.8056 | 32.4986 | 34.4148 | 34.7127 | 32.7372 | 35.068 | 34.812 | 34.293 | 34.7049 | 34.3685 | 34.3867 | 33.8838 | 34.7065 | 36.1504 | 34.765 | 36.5756 | 36.4705 | 33.1916 | 92.9753 | 93.1826 | 92.9911
2022-09-08 06:53 | 9:03 | 17.1935 | 17.4975 | 20.057 | 34.5531 | 34.3737 | 34.0809 | 34.5719 | 35.5441 | 36.5535 | 37.5492 | 37.0116 | 38.2275 | 34.3852 | 34.4305 | 33.9885 | 35.1024 | 34.7497 | 35.2672 | 35.9058 | 36.3688 | 20.9591 | 16.9543 | 93.0487 | 32.454 | 32.6948 | 34.6556 | 32.8063 | 32.7118 | 33.1137 | 34.3801 | 33.9758 | 33.8245 | 37.1018 | 36.1171 | 33.1264 | 34.2944 | 36.127 | 36.4412 | 37.2274 | 36.1531 | 32.8111 | 32.4936 | 34.411 | 34.7042 | 32.721 | 35.0674 | 34.7855 | 34.2838 | 34.7016 | 34.3706 | 34.3711 | 33.8684 | 34.7049 | 36.1439 | 34.7611 | 36.5849 | 36.4928 | 33.1921 | 93.1606 | 93.3605 | 93.1763
2022-09-08 06:53 | 9:03 | 17.1886 | 17.434 | 20.0562 | 34.4065 | 34.3758 | 34.101 | 34.5702 | 35.5604 | 36.554 | 37.5515 | 37.0144 | 38.2362 | 34.3935 | 34.4485 | 34.0038 | 35.1101 | 34.744 | 35.2588 | 35.8777 | 36.3483 | 20.9148 | 16.9211 | 93.1744 | 32.4265 | 32.7039 | 34.6433 | 32.8006 | 32.7097 | 33.1308 | 34.383 | 33.9776 | 33.8102 | 37.1002 | 36.1355 | 33.1272 | 34.2866 | 36.1534 | 36.4299 | 37.2179 | 36.1653 | 32.7863 | 32.489 | 34.4294 | 34.715 | 32.7067 | 35.0739 | 34.8033 | 34.3006 | 34.7166 | 34.341 | 34.3948 | 33.8522 | 34.7016 | 36.1463 | 34.7668 | 36.5889 | 36.477 | 33.1855 | 93.3178 | 93.5425 | 93.2819
2022-09-08 06:53 | 9:03 | 17.1528 | 17.4466 | 20.0413 | 34.5094 | 34.3654 | 34.1163 | 34.5702 | 35.5458 | 36.5302 | 37.5479 | 37.0037 | 38.248 | 34.3933 | 34.4344 | 33.9939 | 35.1144 | 34.7593 | 35.2509 | 35.8756 | 36.3631 | 20.8748 | 16.9286 | 93.2892 | 32.4722 | 32.7147 | 34.6397 | 32.8064 | 32.7003 | 33.1165 | 34.3888 | 33.9687 | 33.8198 | 37.0852 | 36.1397 | 33.1263 | 34.3036 | 36.1171 | 36.4386 | 37.2083 | 36.1545 | 32.7927 | 32.473 | 34.4132 | 34.6954 | 32.7066 | 35.0721 | 34.7877 | 34.2917 | 34.7223 | 34.3583 | 34.3971 | 33.8561 | 34.7166 | 36.1463 | 34.7579 | 36.5853 | 36.4701 | 33.1918 | 93.4756 | 93.7225 | 93.3981
2022-09-08 06:53 | 9:03 | 17.0867 | 17.3784 | 19.9852 | 34.4334 | 34.3736 | 34.0977 | 34.5596 | 35.5696 | 36.5371 | 37.533 | 36.9995 | 38.2206 | 34.4112 | 34.4402 | 34.0001 | 35.1086 | 34.7495 | 35.2454 | 35.8838 | 36.3449 | 20.8814 | 16.8906 | 93.4212 | 32.4981 | 32.692 | 34.6442 | 32.8056 | 32.7037 | 33.1182 | 34.3949 | 33.9813 | 33.8109 | 37.0905 | 36.1186 | 33.1322 | 34.2854 | 36.1355 | 36.4346 | 37.2125 | 36.127 | 32.8032 | 32.4876 | 34.4013 | 34.6979 | 32.715 | 35.0772 | 34.7982 | 34.2787 | 34.7238 | 34.3644 | 34.3993 | 33.8469 | 34.7223 | 36.1405 | 34.7582 | 36.5848 | 36.465 | 33.1977 | 93.5947 | 93.9124 | 93.4693
2022-09-08 06:54 | 9:04 | 17.0616 | 17.3974 | 19.9649 | 34.5149 | 34.365 | 34.1113 | 34.552 | 35.5622 | 36.538 | 37.5356 | 36.9945 | 38.2203 | 34.4102 | 34.4501 | 33.9922 | 35.0964 | 34.735 | 35.2478 | 35.8825 | 36.3698 | 20.8481 | 16.873 | 93.4527 | 32.2728 | 32.6917 | 34.6232 | 32.8111 | 32.6738 | 33.1264 | 34.3876 | 33.9707 | 33.84 | 37.1083 | 36.1284 | 33.0969 | 34.2967 | 36.1397 | 36.4079 | 37.205 | 36.1534 | 32.7832 | 32.4779 | 34.4031 | 34.7042 | 32.7041 | 35.0718 | 34.7965 | 34.2874 | 34.733 | 34.3421 | 34.3896 | 33.8413 | 34.7238 | 36.1571 | 34.7464 | 36.5795 | 36.4554 | 33.1801 | 93.7431 | 94.0597 | 93.5522
2022-09-08 06:54 | 9:04 | 17.0988 | 17.4269 | 19.9726 | 34.4827 | 34.3742 | 34.1045 | 34.5663 | 35.5454 | 36.5493 | 37.538 | 36.9967 | 38.2398 | 34.3972 | 34.4605 | 34.0095 | 35.0951 | 34.7485 | 35.2559 | 35.8848 | 36.3532 | 20.8262 | 16.8975 | 93.6385 | 32.3182 | 32.7077 | 34.6433 | 32.7863 | 32.7178 | 33.1272 | 34.3823 | 33.9692 | 33.8279 | 37.0919 | 36.1036 | 33.111 | 34.2946 | 36.1186 | 36.4209 | 37.2242 | 36.1171 | 32.7931 | 32.4637 | 34.4035 | 34.7054 | 32.7094 | 35.0819 | 34.7947 | 34.2823 | 34.7508 | 34.3474 | 34.4007 | 33.8566 | 34.733 | 36.132 | 34.7613 | 36.5855 | 36.4652 | 33.1831 | 93.8829 | 94.2256 | 93.6223
2022-09-08 06:54 | 9:04 | 17.0973 | 17.4027 | 19.9537 | 34.5048 | 34.3771 | 34.0796 | 34.559 | 35.5601 | 36.5438 | 37.5426 | 37.0107 | 38.2064 | 34.399 | 34.4474 | 33.9825 | 35.0906 | 34.755 | 35.2509 | 35.8689 | 36.3489 | 20.8228 | 16.8913 | 93.689 | 32.2149 | 32.6998 | 34.621 | 32.7927 | 32.6968 | 33.1263 | 34.3863 | 34.0014 | 33.8082 | 37.0942 | 36.1313 | 33.1114 | 34.2981 | 36.1284 | 36.4131 | 37.1936 | 36.1355 | 32.7598 | 32.4695 | 34.4058 | 34.6906 | 32.7037 | 35.1024 | 34.806 | 34.3038 | 34.741 | 34.3342 | 34.4009 | 33.8537 | 34.7508 | 36.1317 | 34.7491 | 36.5861 | 36.4665 | 33.1809 | 94.0144 | 94.3589 | 93.7516
2022-09-08 06:54 | 9:04 | 16.9951 | 17.3343 | 19.8878 | 34.3706 | 34.3799 | 34.1025 | 34.555 | 35.5545 | 36.5374 | 37.5517 | 36.9773 | 38.2242 | 34.3997 | 34.4614 | 33.9871 | 35.1054 | 34.7402 | 35.2426 | 35.8778 | 36.3506 | 20.81 | 16.818 | 93.7455 | 32.1521 | 32.7061 | 34.6192 | 32.8032 | 32.7039 | 33.1322 | 34.3897 | 33.9872 | 33.8077 | 37.073 | 36.1165 | 33.1051 | 34.2742 | 36.1036 | 36.4166 | 37.2284 | 36.1397 | 32.7904 | 32.4712 | 34.3988 | 34.717 | 32.6849 | 35.0842 | 34.7878 | 34.3108 | 34.7555 | 34.3607 | 34.4088 | 33.8312 | 34.741 | 36.1364 | 34.7594 | 36.5941 | 36.4854 | 33.1756 | 94.1412 | 94.5672 | 93.9086
2022-09-08 06:54 | 9:04 | 17.2002 | 17.3224 | 19.874 | 34.4537 | 34.3882 | 34.0976 | 34.5519 | 35.5536 | 36.5281 | 37.5333 | 37.011 | 38.2364 | 34.3953 | 34.4744 | 33.985 | 35.0996 | 34.7367 | 35.2365 | 35.8606 | 36.3705 | 20.764 | 16.8352 | 93.9313 | 32.3087 | 32.6743 | 34.6133 | 32.7832 | 32.7143 | 33.0969 | 34.3816 | 33.9841 | 33.8186 | 37.1062 | 36.1213 | 33.1058 | 34.2833 | 36.1313 | 36.4329 | 37.2131 | 36.1186 | 32.7866 | 32.4615 | 34.4086 | 34.6944 | 32.6751 | 35.0826 | 34.7781 | 34.307 | 34.7413 | 34.3311 | 34.4076 | 33.8541 | 34.7555 | 36.1407 | 34.7481 | 36.5679 | 36.4708 | 33.174 | 94.4053 | 94.7942 | 94.0282
2022-09-08 06:54 | 9:04 | 17.0739 | 17.3872 | 19.8645 | 34.4496 | 34.3901 | 34.0922 | 34.5618 | 35.5586 | 36.5358 | 37.5332 | 36.9961 | 38.2298 | 34.3881 | 34.4566 | 34.0028 | 35.0851 | 34.7544 | 35.2432 | 35.8783 | 36.3536 | 20.7531 | 16.8591 | 94.0415 | 32.4602 | 32.7057 | 34.6287 | 32.7931 | 32.6929 | 33.111 | 34.369 | 33.9799 | 33.8143 | 37.0872 | 36.1098 | 33.0988 | 34.2743 | 36.1165 | 36.4333 | 37.2123 | 36.1284 | 32.7666 | 32.4704 | 34.3857 | 34.6958 | 32.6783 | 35.0848 | 34.7884 | 34.3032 | 34.7649 | 34.3288 | 34.4104 | 33.8501 | 34.7413 | 36.1327 | 34.7693 | 36.5914 | 36.4545 | 33.1806 | 94.559 | 95.005 | 94.2154
2022-09-08 06:55 | 9:04 | 17.0198 | 17.3387 | 19.8731 | 34.4521 | 34.3811 | 34.1078 | 34.5462 | 35.5719 | 36.5278 | 37.5491 | 36.9857 | 38.2193 | 34.3895 | 34.4636 | 33.9857 | 35.1001 | 34.726 | 35.2517 | 35.86 | 36.3577 | 20.737 | 16.8212 | 94.1272 | 32.3876 | 32.6899 | 34.6128 | 32.7598 | 32.6971 | 33.1114 | 34.3936 | 33.9626 | 33.8049 | 37.0691 | 36.1087 | 33.1046 | 34.2691 | 36.1213 | 36.4166 | 37.1976 | 36.1036 | 32.7711 | 32.4293 | 34.4012 | 34.6666 | 32.6633 | 35.0822 | 34.7998 | 34.2988 | 34.7473 | 34.345 | 34.3919 | 33.8297 | 34.7649 | 36.1427 | 34.7348 | 36.5696 | 36.4664 | 33.1749 | 94.6748 | 95.1583 | 94.1946
2022-09-08 06:55 | 9:05 | 16.9806 | 17.2802 | 19.8221 | 34.3585 | 34.3834 | 34.0845 | 34.5529 | 35.5537 | 36.56 | 37.5291 | 36.9947 | 38.2321 | 34.3994 | 34.4865 | 33.9918 | 35.1031 | 34.7375 | 35.2443 | 35.8896 | 36.349 | 20.7351 | 16.7873 | 94.1933 | 32.4514 | 32.6707 | 34.6123 | 32.7904 | 32.6823 | 33.1051 | 34.3894 | 33.9834 | 33.7998 | 37.0825 | 36.1203 | 33.0883 | 34.2639 | 36.1098 | 36.4196 | 37.2216 | 36.1313 | 32.7861 | 32.4589 | 34.387 | 34.6799 | 32.6821 | 35.1058 | 34.8021 | 34.2945 | 34.7707 | 34.3416 | 34.415 | 33.8531 | 34.7473 | 36.1428 | 34.7496 | 36.5845 | 36.4729 | 33.1649 | 94.7901 | 95.2997 | 94.312
2022-09-08 06:55 | 9:05 | 16.9712 | 17.2724 | 19.8094 | 34.3683 | 34.3804 | 34.1048 | 34.5549 | 35.5618 | 36.544 | 37.5228 | 36.9988 | 38.2207 | 34.4104 | 34.4951 | 33.983 | 35.0972 | 34.7463 | 35.2554 | 35.8634 | 36.3377 | 20.7016 | 16.7534 | 94.3546 | 32.4261 | 32.6802 | 34.6112 | 32.7866 | 32.6833 | 33.1058 | 34.374 | 33.9586 | 33.8032 | 37.0789 | 36.1235 | 33.0909 | 34.2671 | 36.1087 | 36.4214 | 37.2081 | 36.1165 | 32.7596 | 32.4395 | 34.3761 | 34.6819 | 32.6426 | 35.1095 | 34.8157 | 34.3044 | 34.7569 | 34.3332 | 34.4018 | 33.8328 | 34.7707 | 36.1363 | 34.7571 | 36.5679 | 36.4675 | 33.1702 | 94.9751 | 95.4452 | 94.4434
2022-09-08 06:55 | 9:05 | 16.9513 | 17.2562 | 19.7838 | 34.3771 | 34.3854 | 34.1055 | 34.546 | 35.5536 | 36.535 | 37.5555 | 36.9811 | 38.2173 | 34.41 | 34.4804 | 33.9781 | 35.0761 | 34.7384 | 35.2649 | 35.8749 | 36.3494 | 20.6993 | 16.7752 | 94.4475 | 32.4117 | 32.6826 | 34.6039 | 32.7666 | 32.6929 | 33.0988 | 34.3771 | 33.9677 | 33.8119 | 37.0712 | 36.1074 | 33.0977 | 34.2815 | 36.1203 | 36.4148 | 37.2019 | 36.1213 | 32.7649 | 32.4338 | 34.373 | 34.6847 | 32.6901 | 35.1037 | 34.7975 | 34.3057 | 34.7761 | 34.3311 | 34.3877 | 33.8391 | 34.7569 | 36.1319 | 34.7506 | 36.5802 | 36.4561 | 33.1603 | 95.1476 | 95.5945 | 94.5313
2022-09-08 06:55 | 9:05 | 16.9972 | 17.3105 | 19.7912 | 34.3817 | 34.387 | 34.0994 | 34.5602 | 35.5462 | 36.5415 | 37.524 | 36.9988 | 38.2124 | 34.4086 | 34.4792 | 33.9789 | 35.0885 | 34.725 | 35.2402 | 35.8792 | 36.3493 | 20.6791 | 16.7903 | 94.496 | 32.3027 | 32.6904 | 34.5966 | 32.7711 | 32.6893 | 33.1046 | 34.3738 | 33.9624 | 33.8012 | 37.072 | 36.1256 | 33.0867 | 34.2889 | 36.1235 | 36.406 | 37.1899 | 36.1098 | 32.7664 | 32.421 | 34.3858 | 34.6708 | 32.6767 | 35.1091 | 34.7961 | 34.2996 | 34.7806 | 34.3335 | 34.4101 | 33.8247 | 34.7761 | 36.1209 | 34.7471 | 36.5682 | 36.4711 | 33.1501 | 95.2829 | 95.713 | 94.5983
2022-09-08 06:55 | 9:05 | 16.9693 | 17.2675 | 19.7703 | 34.3011 | 34.3774 | 34.1016 | 34.5501 | 35.5369 | 36.5376 | 37.5384 | 36.9786 | 38.2165 | 34.3999 | 34.4727 | 33.9776 | 35.077 | 34.7145 | 35.2244 | 35.8449 | 36.3493 | 20.6816 | 16.7658 | 94.5615 | 32.3941 | 32.6685 | 34.6062 | 32.7861 | 32.6862 | 33.0883 | 34.37 | 33.9625 | 33.7982 | 37.0617 | 36.0905 | 33.0708 | 34.2725 | 36.1074 | 36.4382 | 37.1946 | 36.1087 | 32.7709 | 32.4185 | 34.384 | 34.6585 | 32.6591 | 35.1197 | 34.7908 | 34.305 | 34.7687 | 34.3579 | 34.4087 | 33.8303 | 34.7806 | 36.1222 | 34.7492 | 36.5718 | 36.455 | 33.1337 | 95.3936 | 95.7794 | 94.6607
2022-09-08 06:56 | 9:05 | 16.923 | 17.2259 | 19.7717 | 34.4546 | 34.3795 | 34.0986 | 34.5389 | 35.5457 | 36.5513 | 37.5377 | 36.9983 | 38.2137 | 34.4051 | 34.4823 | 33.9734 | 35.1039 | 34.7279 | 35.2358 | 35.8642 | 36.3459 | 20.6855 | 16.7396 | 94.6338 | 32.126 | 32.6487 | 34.6021 | 32.7596 | 32.6942 | 33.0909 | 34.3836 | 33.9631 | 33.8069 | 37.0735 | 36.1092 | 33.0907 | 34.2821 | 36.1256 | 36.4228 | 37.1653 | 36.1203 | 32.7427 | 32.4162 | 34.3858 | 34.6557 | 32.6549 | 35.1026 | 34.7834 | 34.3183 | 34.7845 | 34.3336 | 34.4137 | 33.8141 | 34.7687 | 36.1002 | 34.7453 | 36.5821 | 36.4567 | 33.1345 | 95.433 | 95.8465 | 94.7971
2022-09-08 06:56 | 9:06 | 16.949 | 17.2353 | 19.7378 | 34.3006 | 34.372 | 34.0792 | 34.5629 | 35.5428 | 36.5307 | 37.5268 | 36.9855 | 38.2144 | 34.408 | 34.493 | 33.9762 | 35.0845 | 34.7225 | 35.2272 | 35.8559 | 36.3256 | 20.671 | 16.725 | 94.5885 | 32.4297 | 32.6701 | 34.5756 | 32.7649 | 32.6724 | 33.0977 | 34.3586 | 33.9611 | 33.7871 | 37.0738 | 36.1103 | 33.0774 | 34.2826 | 36.0905 | 36.412 | 37.1707 | 36.1235 | 32.745 | 32.4391 | 34.387 | 34.6601 | 32.6467 | 35.1356 | 34.7918 | 34.3151 | 34.7905 | 34.344 | 34.4213 | 33.794 | 34.7845 | 36.1111 | 34.7332 | 36.5778 | 36.4511 | 33.143 | 95.3171 | 95.7775 | 94.763
2022-09-08 06:56 | 9:06 | 16.939 | 17.2209 | 19.7026 | 34.3589 | 34.3821 | 34.1089 | 34.5447 | 35.5592 | 36.5147 | 37.5206 | 37.0023 | 38.2223 | 34.3934 | 34.4885 | 33.9744 | 35.1098 | 34.692 | 35.2315 | 35.8679 | 36.3242 | 20.6688 | 16.7035 | 94.5113 | 32.2543 | 32.6615 | 34.6067 | 32.7664 | 32.6793 | 33.0867 | 34.3648 | 33.9601 | 33.7937 | 37.0752 | 36.1107 | 33.0744 | 34.2563 | 36.1092 | 36.4096 | 37.1781 | 36.1074 | 32.7572 | 32.4333 | 34.3627 | 34.6538 | 32.6476 | 35.1281 | 34.7853 | 34.3258 | 34.777 | 34.3444 | 34.4203 | 33.8153 | 34.7905 | 36.1067 | 34.7692 | 36.5881 | 36.4525 | 33.136 | 95.2229 | 95.6566 | 94.6515
2022-09-08 06:56 | 9:06 | 16.8755 | 17.1957 | 19.6965 | 34.4063 | 34.3728 | 34.0834 | 34.5393 | 35.5351 | 36.528 | 37.5337 | 36.9715 | 38.2166 | 34.4028 | 34.5082 | 33.9642 | 35.0938 | 34.7158 | 35.2229 | 35.8535 | 36.3216 | 20.6693 | 16.6696 | 94.4096 | 32.3503 | 32.6399 | 34.5779 | 32.7709 | 32.6666 | 33.0708 | 34.356 | 33.9382 | 33.7884 | 37.0732 | 36.0929 | 33.0701 | 34.2656 | 36.1103 | 36.4116 | 37.172 | 36.1256 | 32.7416 | 32.4275 | 34.3795 | 34.6643 | 32.6459 | 35.1418 | 34.8044 | 34.3361 | 34.7831 | 34.3359 | 34.4138 | 33.8257 | 34.777 | 36.1115 | 34.7448 | 36.5915 | 36.4454 | 33.1139 | 94.9878 | 95.4346 | 94.4077
2022-09-08 06:56 | 9:06 | 16.8617 | 17.2012 | 19.6564 | 34.3287 | 34.3738 | 34.0865 | 34.5404 | 35.5464 | 36.5221 | 37.5159 | 36.9914 | 38.2029 | 34.3976 | 34.514 | 33.9655 | 35.0843 | 34.7227 | 35.2267 | 35.8533 | 36.3094 | 20.6718 | 16.6659 | 94.2877 | 32.179 | 32.6619 | 34.5936 | 32.7427 | 32.6675 | 33.0907 | 34.3526 | 33.9666 | 33.7763 | 37.0812 | 36.1131 | 33.0542 | 34.2722 | 36.1107 | 36.4065 | 37.1794 | 36.0905 | 32.7602 | 32.4128 | 34.3747 | 34.6484 | 32.6249 | 35.1222 | 34.7997 | 34.3346 | 34.7774 | 34.3496 | 34.4019 | 33.8005 | 34.7831 | 36.0868 | 34.7374 | 36.5666 | 36.4559 | 33.1224 | 94.7795 | 95.1833 | 94.3015
2022-09-08 06:56 | 9:06 | 16.8771 | 17.2034 | 19.6307 | 34.2619 | 34.3427 | 34.0712 | 34.518 | 35.5533 | 36.4947 | 37.5028 | 36.9835 | 38.194 | 34.396 | 34.5151 | 33.9627 | 35.0799 | 34.6901 | 35.2174 | 35.8593 | 36.3137 | 20.6852 | 16.746 | 94.1284 | 32.2832 | 32.6429 | 34.5793 | 32.745 | 32.6752 | 33.0774 | 34.3419 | 33.9627 | 33.782 | 37.0622 | 36.118 | 33.0789 | 34.265 | 36.0929 | 36.4028 | 37.1545 | 36.1092 | 32.7596 | 32.4049 | 34.3794 | 34.6525 | 32.6276 | 35.1328 | 34.7988 | 34.3449 | 34.7835 | 34.349 | 34.4181 | 33.789 | 34.7774 | 36.0897 | 34.7276 | 36.5705 | 36.4425 | 33.1122 | 94.6205 | 94.9455 | 94.1512
2022-09-08 06:57 | 9:07 | 16.869 | 17.1709 | 19.6732 | 34.229 | 34.3797 | 34.0739 | 34.5261 | 35.5435 | 36.5123 | 37.4941 | 36.9964 | 38.203 | 34.3892 | 34.5029 | 33.9517 | 35.09 | 34.7031 | 35.1987 | 35.8241 | 36.3122 | 20.7128 | 16.6357 | 94.0647 | 32.2203 | 32.6484 | 34.5821 | 32.7572 | 32.6619 | 33.0744 | 34.3352 | 33.9693 | 33.7956 | 37.0514 | 36.1025 | 33.0587 | 34.2677 | 36.1131 | 36.3916 | 37.178 | 36.1103 | 32.7557 | 32.4148 | 34.3792 | 34.6411 | 32.63 | 35.147 | 34.806 | 34.3281 | 34.7978 | 34.3373 | 34.4279 | 33.8172 | 34.7835 | 36.0762 | 34.7286 | 36.5749 | 36.4346 | 33.117 | 94.4863 | 94.7928 | 94.0883
2022-09-08 06:57 | 9:07 | 16.8366 | 17.1505 | 19.6269 | 34.2598 | 34.3911 | 34.0983 | 34.5246 | 35.5259 | 36.5258 | 37.5099 | 36.9675 | 38.1977 | 34.3887 | 34.5135 | 33.9619 | 35.0775 | 34.693 | 35.2218 | 35.8428 | 36.3175 | 20.7056 | 16.5957 | 94.0833 | 32.2212 | 32.628 | 34.5719 | 32.7416 | 32.663 | 33.0701 | 34.344 | 33.9656 | 33.7769 | 37.0662 | 36.1009 | 33.067 | 34.2691 | 36.118 | 36.3909 | 37.1539 | 36.1107 | 32.7594 | 32.4003 | 34.3633 | 34.6307 | 32.6276 | 35.1542 | 34.7827 | 34.3266 | 34.8125 | 34.3445 | 34.4259 | 33.789 | 34.7978 | 36.0819 | 34.7496 | 36.5479 | 36.4425 | 33.1013 | 94.4488 | 94.6588 | 94.1074
2022-09-08 06:57 | 9:07 | 16.8829 | 17.1552 | 19.6723 | 34.1708 | 34.3755 | 34.0817 | 34.5287 | 35.5196 | 36.4803 | 37.4918 | 36.9989 | 38.2121 | 34.3996 | 34.5204 | 33.9388 | 35.096 | 34.6868 | 35.2154 | 35.824 | 36.3278 | 20.7336 | 16.6179 | 93.9204 | 32.3192 | 32.6482 | 34.5855 | 32.7602 | 32.6416 | 33.0542 | 34.3506 | 33.9498 | 33.7742 | 37.0615 | 36.1201 | 33.0725 | 34.2575 | 36.1025 | 36.4016 | 37.1413 | 36.0929 | 32.7569 | 32.4062 | 34.3742 | 34.6379 | 32.6253 | 35.1467 | 34.8071 | 34.3258 | 34.7854 | 34.315 | 34.429 | 33.7681 | 34.8125 | 36.0676 | 34.7439 | 36.5849 | 36.4255 | 33.105 | 94.3034 | 94.5832 | 93.8823
2022-09-08 06:57 | 9:07 | 16.8828 | 17.1474 | 19.618 | 34.2454 | 34.382 | 34.0721 | 34.5094 | 35.5532 | 36.4965 | 37.484 | 37.0008 | 38.2078 | 34.3967 | 34.5062 | 33.944 | 35.0875 | 34.6946 | 35.1998 | 35.8113 | 36.2966 | 20.7529 | 16.5887 | 93.8758 | 32.18 | 32.6392 | 34.5868 | 32.7596 | 32.652 | 33.0789 | 34.3689 | 33.9664 | 33.7739 | 37.0618 | 36.1066 | 33.0594 | 34.2656 | 36.1009 | 36.3993 | 37.1693 | 36.1131 | 32.7567 | 32.3966 | 34.358 | 34.6532 | 32.6114 | 35.1581 | 34.8211 | 34.3246 | 34.7775 | 34.341 | 34.4305 | 33.78 | 34.7854 | 36.0796 | 34.7529 | 36.5673 | 36.4229 | 33.0836 | 94.1329 | 94.408 | 93.8559
2022-09-08 06:57 | 9:07 | 16.8161 | 17.0437 | 19.6066 | 34.1769 | 34.3912 | 34.0729 | 34.5161 | 35.5217 | 36.4896 | 37.4916 | 36.999 | 38.2117 | 34.4045 | 34.5082 | 33.9386 | 35.0791 | 34.7013 | 35.208 | 35.827 | 36.2919 | 20.7785 | 16.5937 | 93.7669 | 32.0423 | 32.6315 | 34.5669 | 32.7557 | 32.6398 | 33.0587 | 34.3391 | 33.9549 | 33.7727 | 37.0483 | 36.1002 | 33.0802 | 34.2773 | 36.1201 | 36.4043 | 37.1523 | 36.118 | 32.7565 | 32.413 | 34.3393 | 34.6281 | 32.6257 | 35.1678 | 34.8375 | 34.3525 | 34.788 | 34.3511 | 34.4485 | 33.7847 | 34.7775 | 36.0707 | 34.7363 | 36.5814 | 36.4503 | 33.0834 | 94.0162 | 94.3106 | 93.7028
2022-09-08 06:57 | 9:07 | 16.7541 | 17.0341 | 19.5874 | 34.2307 | 34.3907 | 34.0833 | 34.519 | 35.5333 | 36.5251 | 37.4914 | 36.9898 | 38.2214 | 34.393 | 34.5172 | 33.9473 | 35.0918 | 34.6994 | 35.2111 | 35.8272 | 36.3093 | 20.7687 | 16.5902 | 93.7367 | 32.1661 | 32.6424 | 34.5928 | 32.7594 | 32.6653 | 33.067 | 34.3284 | 33.9599 | 33.7753 | 37.0412 | 36.0926 | 33.0738 | 34.2753 | 36.1066 | 36.3995 | 37.1533 | 36.1025 | 32.7563 | 32.3813 | 34.3513 | 34.6484 | 32.6236 | 35.1587 | 34.848 | 34.3515 | 34.788 | 34.3333 | 34.4344 | 33.7571 | 34.788 | 36.0561 | 34.7475 | 36.5804 | 36.4292 | 33.0739 | 93.9837 | 94.2482 | 93.7687
2022-09-08 06:58 | 9:07 | 16.7555 | 17.0099 | 19.5748 | 34.2437 | 34.3867 | 34.0774 | 34.5177 | 35.5407 | 36.4999 | 37.4953 | 36.9915 | 38.2174 | 34.3789 | 34.5361 | 33.9539 | 35.0857 | 34.6922 | 35.22 | 35.8186 | 36.2841 | 20.7763 | 16.5456 | 93.7685 | 32.3929 | 32.644 | 34.582 | 32.7569 | 32.6643 | 33.0725 | 34.3425 | 33.9662 | 33.7636 | 37.0564 | 36.085 | 33.0624 | 34.2812 | 36.1002 | 36.3916 | 37.1352 | 36.1009 | 32.7561 | 32.3855 | 34.3515 | 34.6245 | 32.6366 | 35.1817 | 34.8342 | 34.349 | 34.7956 | 34.3394 | 34.4402 | 33.7762 | 34.788 | 36.0752 | 34.7457 | 36.5697 | 36.4361 | 33.1003 | 93.946 | 94.1911 | 93.8002
2022-09-08 06:58 | 9:08 | 16.7739 | 17.0712 | 19.5388 | 34.2202 | 34.3711 | 34.0806 | 34.5412 | 35.5343 | 36.4969 | 37.4826 | 37.0003 | 38.2114 | 34.4024 | 34.5264 | 33.9414 | 35.0932 | 34.6802 | 35.2199 | 35.8205 | 36.3132 | 20.7698 | 16.5988 | 93.7217 | 31.926 | 32.6339 | 34.5982 | 32.7567 | 32.6721 | 33.0594 | 34.3302 | 33.9553 | 33.7897 | 37.0608 | 36.0774 | 33.0632 | 34.2646 | 36.0926 | 36.4107 | 37.1657 | 36.1201 | 32.7559 | 32.3879 | 34.3392 | 34.6262 | 32.6078 | 35.1778 | 34.843 | 34.3519 | 34.7846 | 34.3388 | 34.4501 | 33.7626 | 34.7956 | 36.0797 | 34.7478 | 36.5611 | 36.4123 | 33.0871 | 93.8419 | 94.1011 | 93.6646
2022-09-08 06:58 | 9:08 | 16.8382 | 17.0451 | 19.5246 | 34.2758 | 34.3948 | 34.0901 | 34.5119 | 35.5449 | 36.5051 | 37.4908 | 37.0004 | 38.22 | 34.3758 | 34.5442 | 33.9435 | 35.0766 | 34.6813 | 35.2081 | 35.8055 | 36.2979 | 20.7763 | 16.6306 | 93.6 | 32.1511 | 32.6228 | 34.5838 | 32.7426 | 32.6318 | 33.0802 | 34.343 | 33.966 | 33.7718 | 37.0672 | 36.0697 | 33.0639 | 34.2798 | 36.1 | 36.4118 | 37.1443 | 36.1066 | 32.7557 | 32.3809 | 34.3219 | 34.6208 | 32.6171 | 35.1687 | 34.844 | 34.3619 | 34.783 | 34.326 | 34.4605 | 33.7833 | 34.7846 | 36.0557 | 34.7402 | 36.5788 | 36.4289 | 33.0792 | 93.794 | 94.0348 | 93.5636
2022-09-08 06:58 | 9:08 | 16.7335 | 17.0013 | 19.5476 | 34.2324 | 34.3971 | 34.0752 | 34.5151 | 35.5435 | 36.4886 | 37.4847 | 36.9973 | 38.2 | 34.3835 | 34.5428 | 33.9481 | 35.0746 | 34.6908 | 35.2174 | 35.8086 | 36.3064 | 20.7919 | 16.6188 | 93.6322 | 32.4337 | 32.6214 | 34.5855 | 32.7301 | 32.6505 | 33.0738 | 34.337 | 33.98 | 33.7731 | 37.0491 | 36.0621 | 33.0647 | 34.2753 | 36.1074 | 36.3944 | 37.1523 | 36.1002 | 32.7555 | 32.3726 | 34.3362 | 34.636 | 32.5933 | 35.1678 | 34.846 | 34.3367 | 34.7948 | 34.3241 | 34.4474 | 33.7961 | 34.783 | 36.0763 | 34.74 | 36.5622 | 36.4267 | 33.0796 | 93.7813 | 93.95 | 93.6462
2022-09-08 06:58 | 9:08 | 16.7644 | 17.0483 | 19.548 | 34.2392 | 34.3993 | 34.0895 | 34.5432 | 35.5311 | 36.5026 | 37.4994 | 37.0014 | 38.2216 | 34.394 | 34.5469 | 33.9276 | 35.0913 | 34.6857 | 35.2067 | 35.8235 | 36.2917 | 20.7819 | 16.5685 | 93.6048 | 32.346 | 32.6382 | 34.5546 | 32.7512 | 32.6663 | 33.0624 | 34.351 | 33.9674 | 33.7832 | 37.0647 | 36.0545 | 33.0654 | 34.2751 | 36.1148 | 36.4022 | 37.1439 | 36.0926 | 32.7553 | 32.3873 | 34.3367 | 34.6234 | 32.5943 | 35.1604 | 34.8479 | 34.3546 | 34.7839 | 34.3041 | 34.4614 | 33.7424 | 34.7948 | 36.0728 | 34.7406 | 36.5851 | 36.4181 | 33.0718 | 93.6876 | 93.8874 | 93.5927
2022-09-08 06:58 | 9:08 | 16.7628 | 17.0016 | 19.5331 | 34.1968 | 34.3896 | 34.0816 | 34.523 | 35.5412 | 36.5005 | 37.4946 | 37.0109 | 38.2128 | 34.3846 | 34.5614 | 33.9258 | 35.0777 | 34.6826 | 35.2013 | 35.8174 | 36.2807 | 20.7756 | 16.5374 | 93.5559 | 32.139 | 32.6232 | 34.5836 | 32.7328 | 32.6401 | 33.0632 | 34.338 | 33.9632 | 33.7853 | 37.061 | 36.0469 | 33.0662 | 34.2965 | 36.1222 | 36.412 | 37.1366 | 36.1 | 32.7551 | 32.3685 | 34.3376 | 34.6429 | 32.6252 | 35.1737 | 34.8606 | 34.3545 | 34.7888 | 34.323 | 34.4744 | 33.7706 | 34.7839 | 36.0772 | 34.7429 | 36.5872 | 36.4252 | 33.0695 | 93.6369 | 93.7841 | 93.6462

## SD CARD data
Date Time | State | CRailTemp | LRefrigTemp | LREvapTemp | RRefrigTemp | RREvapTemp | CompAO | ColdRailMode | LRefrigMode | RRefrigMode | ColdRSolen | LRefrigSolen | RRefrigSolen | CompDO
2022-09-07 11:58 | 2 | 81.6 | 84.2 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.2 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.2 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.2 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.6 | 84.3 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.6 | 84.3 | 84.1 | 84.2 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.6 | 84.3 | 84.1 | 84.3 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.6 | 84.3 | 84.1 | 84.3 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.3 | 84.1 | 84.3 | 84.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:58 | 1 | 81.6 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.1 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 11:59 | 1 | 81.7 | 84.3 | 84.2 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:00 | 1 | 81.7 | 84.3 | 84.2 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.2 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.2 | 84.3 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.2 | 84.4 | 84.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.2 | 84.4 | 84.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.2 | 84.4 | 84.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:00 | 1 | 81.7 | 84.4 | 84.1 | 84.4 | 84.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 81.7 | 84.4 | 83.7 | 84.4 | 83.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 81.6 | 84.4 | 83 | 84.4 | 82.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 81.5 | 84.3 | 81.2 | 84.4 | 81.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 81.3 | 84.1 | 79.2 | 84.3 | 80.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 81.1 | 83.8 | 77.1 | 84.1 | 79.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:01 | 1 | 80.8 | 83.6 | 75.3 | 83.9 | 78 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 80.4 | 83.3 | 73.8 | 83.7 | 76.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 80.1 | 83 | 72.5 | 83.6 | 75.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 79.6 | 82.7 | 71.4 | 83.4 | 75.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 79.2 | 82.4 | 70.5 | 83.3 | 74.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 78.7 | 82.1 | 69.5 | 83.1 | 73.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:02 | 1 | 78.3 | 81.9 | 68.7 | 83 | 73 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 77.8 | 81.6 | 67.9 | 82.7 | 72.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 77.3 | 81.4 | 67.2 | 82.6 | 71.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 76.8 | 81.2 | 66.3 | 82.4 | 71.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 76.4 | 80.9 | 65.5 | 82.2 | 70.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 75.9 | 80.7 | 64.8 | 82 | 70.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:03 | 1 | 75.3 | 80.5 | 64 | 81.8 | 69.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 74.8 | 80.2 | 63.3 | 81.6 | 68.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 74.3 | 80 | 62.5 | 81.3 | 68.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 73.8 | 79.7 | 61.8 | 81.1 | 67.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 73.2 | 79.5 | 61 | 80.9 | 66.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 72.7 | 79.2 | 60.3 | 80.7 | 66.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:04 | 1 | 72.2 | 79 | 59.6 | 80.4 | 65.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 71.6 | 78.7 | 58.9 | 80.2 | 64.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 71.1 | 78.4 | 58.3 | 80 | 63.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 70.6 | 78.1 | 57.6 | 79.7 | 63 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 70 | 77.8 | 57 | 79.4 | 62.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 69.5 | 77.6 | 56.5 | 79.2 | 61.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:05 | 1 | 68.9 | 77.3 | 56 | 79 | 60.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 68.4 | 77 | 55.4 | 78.7 | 60.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 67.9 | 76.7 | 55.1 | 78.4 | 59.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 67.4 | 76.4 | 54.6 | 78.1 | 59 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 66.9 | 76.1 | 54 | 77.8 | 58.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 66.3 | 75.9 | 53.6 | 77.6 | 57.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:06 | 1 | 65.8 | 75.5 | 53.1 | 77.3 | 57.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 65.3 | 75.2 | 52.7 | 77 | 57 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 64.8 | 75 | 52.2 | 76.7 | 56.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 64.3 | 74.7 | 51.8 | 76.4 | 56 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 63.8 | 74.4 | 51.5 | 76.1 | 55.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 63.3 | 74.1 | 51.1 | 75.9 | 55.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:07 | 1 | 62.8 | 73.8 | 50.7 | 75.6 | 54.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 62.3 | 73.6 | 50.3 | 75.3 | 54.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 61.9 | 73.3 | 49.9 | 75 | 54.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 61.4 | 73 | 49.6 | 74.8 | 53.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 60.9 | 72.7 | 49.2 | 74.5 | 53.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 60.5 | 72.4 | 48.9 | 74.2 | 52.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:08 | 1 | 60 | 72.2 | 48.5 | 73.9 | 52.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 59.6 | 71.9 | 48.2 | 73.6 | 52.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 59.2 | 71.6 | 47.9 | 73.4 | 51.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 58.8 | 71.4 | 47.6 | 73.1 | 51.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 58.4 | 71.1 | 47.3 | 72.8 | 51.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 57.9 | 70.8 | 47 | 72.6 | 50.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:09 | 1 | 57.5 | 70.6 | 46.7 | 72.3 | 50.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 57.1 | 70.3 | 46.4 | 72 | 50.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 56.7 | 70 | 46.1 | 71.8 | 49.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 56.3 | 69.7 | 45.8 | 71.5 | 49.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 55.9 | 69.5 | 45.5 | 71.3 | 49.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 55.6 | 69.3 | 45.2 | 71 | 48.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:10 | 1 | 55.3 | 69 | 44.9 | 70.7 | 48.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 54.9 | 68.7 | 44.6 | 70.4 | 48.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 54.6 | 68.5 | 44.4 | 70.2 | 48 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 54.1 | 68.2 | 44.1 | 69.9 | 47.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 53.8 | 68 | 43.9 | 69.7 | 47.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 53.4 | 67.8 | 43.6 | 69.4 | 47.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:11 | 1 | 53.1 | 67.5 | 43.4 | 69.1 | 47.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 52.8 | 67.3 | 43.1 | 68.9 | 46.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 52.4 | 67 | 42.9 | 68.7 | 46.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 52.1 | 66.8 | 42.7 | 68.4 | 46.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 51.7 | 66.5 | 42.4 | 68.1 | 46 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 51.4 | 66.3 | 42.2 | 67.9 | 45.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:12 | 1 | 51.1 | 66 | 41.9 | 67.6 | 45.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 50.8 | 65.8 | 41.7 | 67.4 | 45.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 50.5 | 65.6 | 41.5 | 67.1 | 45.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 50.2 | 65.4 | 41.3 | 66.9 | 44.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 49.9 | 65.1 | 41.1 | 66.6 | 44.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 49.6 | 64.9 | 40.9 | 66.4 | 44.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:13 | 1 | 49.2 | 64.7 | 40.6 | 66.2 | 44.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 48.9 | 64.5 | 40.5 | 66 | 44 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 48.7 | 64.2 | 40.3 | 65.8 | 43.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 48.4 | 64 | 40.1 | 65.5 | 43.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 48.1 | 63.8 | 39.9 | 65.3 | 43.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 47.8 | 63.6 | 39.6 | 65.1 | 43.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:14 | 1 | 47.6 | 63.3 | 39.5 | 64.8 | 43 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 47.3 | 63.1 | 39.3 | 64.6 | 42.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 47.1 | 62.9 | 39.2 | 64.4 | 42.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 46.8 | 62.7 | 38.9 | 64.2 | 42.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 46.5 | 62.5 | 38.8 | 64 | 42.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 46.3 | 62.2 | 38.6 | 63.8 | 42.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:15 | 1 | 46 | 62 | 38.4 | 63.6 | 41.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 45.8 | 61.8 | 38.2 | 63.3 | 41.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 45.5 | 61.6 | 38.1 | 63.1 | 41.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 45.3 | 61.4 | 37.9 | 62.9 | 41.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 45 | 61.1 | 37.7 | 62.7 | 41.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 44.8 | 60.9 | 37.6 | 62.4 | 41 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:16 | 1 | 44.6 | 60.7 | 37.4 | 62.2 | 40.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 44.4 | 60.6 | 37.2 | 62 | 40.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 44.1 | 60.4 | 37.1 | 61.8 | 40.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 43.9 | 60.2 | 36.9 | 61.6 | 40.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 43.7 | 59.9 | 36.7 | 61.4 | 40.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 43.5 | 59.7 | 36.5 | 61.2 | 40.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:17 | 1 | 43.3 | 59.6 | 36.4 | 61 | 39.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 43.1 | 59.4 | 36.2 | 60.8 | 39.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 42.9 | 59.2 | 36 | 60.6 | 39.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 42.7 | 59 | 35.9 | 60.4 | 39.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 42.5 | 58.8 | 35.7 | 60.2 | 39.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 42.3 | 58.6 | 35.6 | 60 | 39.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:18 | 1 | 42.1 | 58.4 | 35.4 | 59.9 | 39 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41.9 | 58.2 | 35.3 | 59.7 | 38.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41.7 | 58 | 35.1 | 59.5 | 38.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41.5 | 57.8 | 35 | 59.2 | 38.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41.3 | 57.7 | 34.8 | 59 | 38.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41.2 | 57.5 | 34.7 | 58.8 | 38.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:19 | 1 | 41 | 57.3 | 34.5 | 58.6 | 38 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 40.8 | 57.1 | 34.4 | 58.5 | 37.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 40.6 | 56.9 | 34.2 | 58.3 | 37.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 40.4 | 56.8 | 34.1 | 58.1 | 37.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 40.3 | 56.6 | 33.9 | 57.9 | 37.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 40.1 | 56.4 | 33.8 | 57.7 | 37.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:20 | 1 | 39.9 | 56.2 | 33.7 | 57.6 | 37.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 39.8 | 56.1 | 33.5 | 57.4 | 37 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 39.5 | 55.9 | 33.3 | 57.2 | 36.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 39.4 | 55.7 | 33.2 | 57 | 36.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 39.3 | 55.5 | 33.1 | 56.9 | 36.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 39.2 | 55.4 | 33 | 56.6 | 36.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:21 | 1 | 38.9 | 55.3 | 32.8 | 56.5 | 36.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 38.8 | 55.1 | 32.7 | 56.3 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 38.6 | 55 | 32.6 | 56.2 | 36 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 38.5 | 54.8 | 32.4 | 55.9 | 35.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 38.2 | 54.6 | 32.3 | 55.8 | 35.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 38.1 | 54.5 | 32.1 | 55.6 | 35.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:22 | 1 | 37.9 | 54.3 | 32 | 55.4 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37.8 | 54.2 | 31.9 | 55.5 | 35.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37.6 | 54 | 31.7 | 55.2 | 35.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37.4 | 53.8 | 31.6 | 55.1 | 35 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37.3 | 53.7 | 31.5 | 54.9 | 34.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37.1 | 53.5 | 31.4 | 54.7 | 34.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:23 | 1 | 37 | 53.3 | 31.2 | 54.6 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36.8 | 53.1 | 31.1 | 54.4 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36.7 | 53 | 31 | 54.2 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36.5 | 52.8 | 30.9 | 54.1 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36.4 | 52.7 | 30.8 | 53.9 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36.2 | 52.5 | 30.6 | 53.6 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:24 | 1 | 36 | 52.4 | 30.5 | 53.5 | 33.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.9 | 52.2 | 30.4 | 53.3 | 33.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.8 | 52.1 | 30.3 | 53.2 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.6 | 51.9 | 30.2 | 53.1 | 33.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.5 | 51.8 | 30 | 52.9 | 33.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.3 | 51.6 | 29.9 | 52.7 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:25 | 1 | 35.2 | 51.4 | 29.7 | 52.6 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 35.1 | 51.3 | 29.6 | 52.5 | 32.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 34.9 | 51.1 | 29.5 | 52.3 | 32.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 34.8 | 51 | 29.4 | 52.1 | 32.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 34.6 | 50.8 | 29.2 | 51.9 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 34.5 | 50.7 | 29.1 | 51.8 | 32.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:26 | 1 | 34.4 | 50.5 | 29 | 51.6 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 34.3 | 50.4 | 28.9 | 51.5 | 32.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 34.1 | 50.2 | 28.8 | 51.3 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 34 | 50.1 | 28.6 | 51.2 | 31.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 33.9 | 49.9 | 28.5 | 51 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 33.7 | 49.8 | 28.4 | 50.8 | 31.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:27 | 1 | 33.6 | 49.7 | 28.3 | 50.7 | 31.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 33.5 | 49.5 | 28.2 | 50.5 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 33.3 | 49.4 | 28.1 | 50.4 | 31.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 33.2 | 49.2 | 27.9 | 50.2 | 31.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 33.1 | 49.1 | 27.8 | 50 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 33 | 48.9 | 27.7 | 49.8 | 30.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:28 | 1 | 32.8 | 48.8 | 27.6 | 49.7 | 30.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.8 | 48.6 | 27.4 | 49.6 | 30.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.6 | 48.5 | 27.3 | 49.4 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.4 | 48.3 | 27.2 | 49.2 | 30.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.4 | 48.2 | 27.1 | 49.1 | 30.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.3 | 48.1 | 27 | 48.9 | 30.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:29 | 1 | 32.1 | 47.9 | 26.8 | 48.9 | 30.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 32 | 47.8 | 26.8 | 48.7 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 31.9 | 47.6 | 26.9 | 48.6 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 31.8 | 47.6 | 27.6 | 48.4 | 29.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 31.6 | 47.5 | 28.4 | 48.3 | 29.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 31.5 | 47.4 | 28.6 | 48.1 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:30 | 1 | 31.4 | 47.3 | 28.5 | 48 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 31.3 | 47.2 | 28.4 | 47.8 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 31.2 | 47.1 | 28.3 | 47.7 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 31.1 | 47 | 28.2 | 47.5 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 31 | 46.9 | 28.1 | 47.4 | 29.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 30.9 | 46.9 | 28 | 47.3 | 29.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:31 | 1 | 30.8 | 46.8 | 27.9 | 47.1 | 29.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.7 | 46.7 | 27.8 | 47 | 29.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.7 | 46.6 | 27.7 | 46.8 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.6 | 46.5 | 27.6 | 46.7 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.5 | 46.4 | 27.5 | 46.5 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.4 | 46.3 | 27.4 | 46.4 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:32 | 1 | 30.3 | 46.2 | 27.3 | 46.3 | 28.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 30.2 | 46.2 | 27.2 | 46.1 | 28.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 30.1 | 46.1 | 27.1 | 46.1 | 28.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 30.1 | 46 | 27.1 | 45.9 | 28.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 30 | 45.9 | 27 | 45.8 | 28.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 29.9 | 45.8 | 26.9 | 45.7 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:33 | 1 | 29.8 | 45.7 | 26.8 | 45.5 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.8 | 45.6 | 26.8 | 45.4 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.7 | 45.5 | 26.7 | 45.4 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.6 | 45.5 | 26.6 | 45.2 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.6 | 45.4 | 26.5 | 45.1 | 28.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.5 | 45.3 | 26.4 | 45 | 28.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:34 | 1 | 29.5 | 45.2 | 26.3 | 44.9 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29.4 | 45 | 26.2 | 44.7 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29.3 | 45 | 26 | 44.6 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29.3 | 44.9 | 25.9 | 44.5 | 27.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29.2 | 44.7 | 25.7 | 44.4 | 27.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29.1 | 44.6 | 25.6 | 44.3 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:35 | 1 | 29 | 44.5 | 25.5 | 44.2 | 27.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.9 | 44.4 | 25.3 | 44.1 | 27.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.9 | 44.3 | 25.1 | 44 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.8 | 44.2 | 24.9 | 43.8 | 27.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.8 | 44.1 | 24.7 | 43.8 | 27 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.7 | 44 | 24.6 | 43.7 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:36 | 1 | 28.6 | 43.8 | 24.3 | 43.5 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.5 | 43.8 | 24.1 | 43.4 | 26.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.5 | 43.7 | 23.9 | 43.3 | 26.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.5 | 43.5 | 23.8 | 43.2 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.4 | 43.4 | 23.6 | 43 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.3 | 43.3 | 23.4 | 43 | 26.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:37 | 1 | 28.2 | 43.2 | 23.2 | 42.8 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 28.1 | 43 | 23 | 42.7 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 28 | 42.9 | 22.8 | 42.6 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 27.9 | 42.8 | 22.6 | 42.5 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 27.8 | 42.6 | 22.4 | 42.4 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 27.7 | 42.6 | 22.2 | 42.3 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:38 | 1 | 27.6 | 42.4 | 22.1 | 42.2 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27.5 | 42.3 | 22 | 42.1 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27.4 | 42.2 | 21.9 | 41.9 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27.3 | 42.1 | 21.7 | 41.8 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27.2 | 41.9 | 21.6 | 41.7 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27.1 | 41.8 | 21.5 | 41.7 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:39 | 1 | 27 | 41.6 | 21.3 | 41.6 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.9 | 41.6 | 21.3 | 41.5 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.8 | 41.4 | 21.2 | 41.4 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.7 | 41.3 | 21.1 | 41.4 | 27.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.6 | 41.2 | 21 | 41.3 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.4 | 41.1 | 20.9 | 41.2 | 26.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:40 | 1 | 26.3 | 41 | 20.9 | 41.2 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 26.2 | 40.9 | 20.8 | 41.1 | 26.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 26.1 | 40.7 | 20.8 | 41 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 26 | 40.7 | 20.7 | 41 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 25.9 | 40.6 | 20.7 | 40.9 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 25.8 | 40.4 | 20.7 | 40.8 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:41 | 1 | 25.7 | 40.3 | 20.6 | 40.7 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.6 | 40.2 | 20.6 | 40.6 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.5 | 40.2 | 20.5 | 40.5 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.4 | 40.1 | 20.4 | 40.4 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.3 | 39.9 | 20.4 | 40.3 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.2 | 39.8 | 20.3 | 40.3 | 25.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:42 | 1 | 25.2 | 39.7 | 20.2 | 40.1 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 25.1 | 39.7 | 20.1 | 40 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 25 | 39.6 | 20.1 | 39.9 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 24.9 | 39.5 | 20.1 | 39.8 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 24.8 | 39.3 | 20.1 | 39.8 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 24.7 | 39.2 | 20 | 39.7 | 24.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:43 | 1 | 24.7 | 39.2 | 19.9 | 39.6 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.6 | 39.1 | 19.8 | 39.5 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.5 | 39 | 19.7 | 39.4 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.5 | 38.9 | 19.6 | 39.3 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.4 | 38.8 | 19.5 | 39.3 | 24.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.4 | 38.7 | 19.4 | 39.2 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:44 | 1 | 24.3 | 38.6 | 19.3 | 39 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 24.2 | 38.5 | 19.2 | 38.9 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 24.1 | 38.4 | 19.1 | 38.8 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 24.1 | 38.3 | 19.1 | 38.8 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 24 | 38.2 | 19 | 38.7 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 23.9 | 38 | 18.8 | 38.6 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:45 | 1 | 23.8 | 37.9 | 18.8 | 38.5 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.9 | 18.7 | 38.4 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.8 | 18.6 | 38.2 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.7 | 18.6 | 38.1 | 22.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.6 | 18.5 | 38 | 22.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.5 | 18.4 | 37.9 | 22.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:46 | 1 | 23.8 | 37.4 | 18.3 | 37.8 | 22.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.8 | 37.3 | 18.3 | 37.7 | 22.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.8 | 37.2 | 18.3 | 37.6 | 22.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.8 | 37.1 | 18.2 | 37.5 | 22.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.8 | 37 | 18.1 | 37.4 | 22 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.8 | 36.9 | 18 | 37.3 | 21.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:47 | 1 | 23.9 | 36.8 | 17.9 | 37.2 | 21.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.9 | 36.7 | 17.8 | 37.1 | 21.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.9 | 36.7 | 17.7 | 37 | 21.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.8 | 36.6 | 17.7 | 36.9 | 21.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.8 | 36.5 | 17.6 | 36.8 | 21.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.8 | 36.4 | 17.5 | 36.7 | 21 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:48 | 1 | 23.8 | 36.3 | 17.5 | 36.6 | 20.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:49 | 1 | 23.6 | 36.2 | 17.4 | 36.5 | 20.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:49 | 1 | 23.6 | 36.1 | 17.2 | 36.4 | 20.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:49 | 1 | 23.5 | 36 | 17.1 | 36.2 | 20.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 12:49 | 1 | 23.5 | 35.9 | 17.1 | 36.2 | 20.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 12:49 | 1 | 23.5 | 35.9 | 17 | 36.1 | 20.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 12:49 | 1 | 23.4 | 35.8 | 16.7 | 36 | 20.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 12:49 | 1 | 23.3 | 35.8 | 16.9 | 35.9 | 20.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:49 | 1 | 23.2 | 35.7 | 17.7 | 35.9 | 19.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 23.1 | 35.6 | 19.4 | 35.8 | 19.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 23 | 35.6 | 21.5 | 35.7 | 20.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 22.8 | 35.6 | 23.3 | 35.6 | 21.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 22.4 | 35.6 | 25.1 | 35.5 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 22.1 | 35.6 | 26.6 | 35.4 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:50 | 1 | 21.7 | 35.6 | 27.8 | 35.4 | 27.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:51 | 1 | 21.1 | 35.7 | 28.7 | 35.4 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:51 | 1 | 20.6 | 35.7 | 29.4 | 35.3 | 29.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:51 | 1 | 19.9 | 35.8 | 30 | 35.3 | 30.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 12:51 | 1 | 19.9 | 35.8 | 30 | 35.3 | 30.1 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 12:51 | 1 | 19.3 | 35.9 | 29.9 | 35.4 | 30.5 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 12:51 | 1 | 18.6 | 35.9 | 29.3 | 35.4 | 30.6 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 12:51 | 1 | 17.9 | 36 | 29.6 | 35.4 | 30.9 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 12:51 | 1 | 17.9 | 36 | 29.6 | 35.4 | 30.9 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 12:51 | 1 | 17.9 | 36 | 29.6 | 35.4 | 30.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 17.5 | 36.1 | 30.2 | 35.5 | 31.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 17 | 36.2 | 30.6 | 35.5 | 31.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 16.6 | 36.3 | 30.9 | 35.7 | 31.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 16.4 | 36.3 | 31.2 | 35.7 | 32 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 16.1 | 36.5 | 31.3 | 35.8 | 32.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:52 | 1 | 16 | 36.5 | 31.4 | 35.8 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 15.9 | 36.6 | 31.5 | 35.9 | 32.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 15.9 | 36.7 | 31.6 | 36 | 32.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 15.9 | 36.7 | 31.6 | 36 | 32.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 16.1 | 36.8 | 31.6 | 36.1 | 32.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 16.3 | 36.8 | 31.7 | 36.2 | 32.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:53 | 1 | 16.5 | 36.9 | 31.7 | 36.3 | 33 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 16.8 | 37 | 31.7 | 36.3 | 33.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 17 | 37 | 31.7 | 36.4 | 33.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 17.3 | 37 | 31.8 | 36.4 | 33.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 17.6 | 37.1 | 31.8 | 36.5 | 33.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 17.8 | 37.1 | 31.9 | 36.5 | 34.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:54 | 1 | 18.1 | 37.2 | 31.9 | 36.6 | 34.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 18.4 | 37.2 | 32 | 36.7 | 34.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 18.7 | 37.2 | 32.1 | 36.7 | 35.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 19 | 37.3 | 32.1 | 36.8 | 35.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 19.4 | 37.3 | 32.1 | 36.8 | 35.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 19.6 | 37.4 | 32.2 | 36.9 | 35.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:55 | 1 | 20 | 37.4 | 32.4 | 37 | 36.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 20.3 | 37.4 | 32.6 | 37 | 36.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 20.6 | 37.5 | 33 | 37 | 36.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 20.9 | 37.5 | 33.3 | 37.1 | 36.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 21.2 | 37.6 | 33.6 | 37.1 | 36.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 21.6 | 37.6 | 33.9 | 37.2 | 37 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 21.9 | 37.6 | 34.2 | 37.3 | 37.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:56 | 1 | 22 | 37.7 | 34.2 | 37.4 | 37.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 22.2 | 37.7 | 34.3 | 37.4 | 37.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 22.5 | 37.7 | 33.8 | 37.4 | 36.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 22.8 | 37.8 | 31.9 | 37.5 | 35.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 23 | 37.8 | 31.5 | 37.5 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 23.2 | 37.8 | 31.9 | 37.5 | 35.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:57 | 1 | 23.3 | 37.8 | 32.6 | 37.6 | 35.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 23.3 | 37.8 | 33.1 | 37.6 | 36.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 23.1 | 37.9 | 33.7 | 37.7 | 36.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 22.8 | 37.9 | 34.1 | 37.7 | 37.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 22.4 | 37.9 | 34.4 | 37.8 | 37.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 21.9 | 38 | 34.7 | 37.8 | 37.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:58 | 1 | 21.2 | 38 | 35 | 37.9 | 38 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:59 | 1 | 20.6 | 38.1 | 35.2 | 38 | 38.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 12:59 | 1 | 19.9 | 38.1 | 35.4 | 38 | 38.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 19.9 | 38.1 | 35.4 | 38 | 38.4 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 19.9 | 38.1 | 35.4 | 38 | 38.4 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 19.2 | 38.2 | 35.5 | 38.1 | 38.5 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 18.3 | 38.2 | 35.7 | 38.1 | 38.7 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 17.7 | 38.2 | 35.9 | 38.2 | 38.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 17.7 | 38.2 | 35.9 | 38.2 | 38.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 12:59 | 1 | 17 | 38.3 | 36 | 38.3 | 39 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 16.4 | 38.4 | 36.2 | 38.4 | 39.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 15.9 | 38.5 | 36.7 | 38.4 | 39.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 15.5 | 38.5 | 37.1 | 38.5 | 39.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 15.2 | 38.6 | 37.5 | 38.6 | 39.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 15.1 | 38.7 | 37.7 | 38.7 | 39.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:00 | 1 | 15 | 38.7 | 37.8 | 38.8 | 39.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:01 | 1 | 14.9 | 38.8 | 37.9 | 38.9 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:01 | 1 | 14.9 | 38.9 | 38.1 | 38.9 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:01 | 1 | 14.9 | 38.9 | 38.1 | 39 | 40 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:01 | 1 | 14.9 | 38.9 | 38.1 | 39 | 40 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:01 | 1 | 15.1 | 39 | 38.2 | 39.1 | 40.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:01 | 1 | 15.3 | 39.1 | 38.4 | 39.2 | 40.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:01 | 1 | 15.5 | 39.2 | 38.5 | 39.3 | 40.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:02 | 1 | 15.8 | 39.3 | 38.7 | 39.3 | 40.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:02 | 1 | 16.1 | 39.3 | 38.8 | 39.3 | 40.4 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:02 | 1 | 16.1 | 39.3 | 38.8 | 39.3 | 40.4 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:02 | 1 | 16.4 | 39.3 | 38.9 | 39.4 | 40.5 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:02 | 1 | 16.7 | 39.4 | 38.4 | 39.5 | 39.5 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:02 | 1 | 17.1 | 39.4 | 38.2 | 39.5 | 36.6 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:02 | 1 | 17.4 | 39.5 | 38.3 | 39.6 | 34.1 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 17.6 | 39.5 | 38.4 | 39.6 | 32.3 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 17.9 | 39.6 | 38.6 | 39.5 | 30.4 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 18.1 | 39.6 | 38.7 | 39.5 | 28.5 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 18.4 | 39.7 | 38.7 | 39.4 | 26.8 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 18.6 | 39.7 | 38.8 | 39.3 | 25.3 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:03 | 1 | 18.9 | 39.8 | 38.8 | 39.3 | 23.9 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:04 | 1 | 19.2 | 39.8 | 38.8 | 39.2 | 22.6 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:04 | 1 | 19.4 | 39.8 | 38.7 | 39 | 21.4 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:04 | 1 | 19.6 | 39.9 | 38.6 | 38.8 | 20.2 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:04 | 1 | 19.9 | 39.9 | 38.5 | 38.7 | 19.2 | 4.5 | 1 | 1 | 1 | 0 | 0 | 1 | 1
2022-09-07 13:04 | 1 | 20 | 40 | 38.5 | 38.6 | 18.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:04 | 1 | 20.2 | 40 | 38.1 | 38.4 | 18.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:04 | 1 | 20.4 | 40 | 35 | 38.3 | 18.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 20.7 | 40 | 31.8 | 38 | 18.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 21 | 39.9 | 29.4 | 37.9 | 19.3 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 21.2 | 39.8 | 29 | 37.7 | 19.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 21.5 | 39.7 | 28.4 | 37.6 | 20.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 21.7 | 39.7 | 27.6 | 37.4 | 21.3 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 22 | 39.6 | 26.9 | 37.2 | 21.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:05 | 1 | 22 | 39.6 | 26.8 | 37.2 | 21.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 22.3 | 39.5 | 26.2 | 37.1 | 22.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 22.5 | 39.5 | 25.5 | 37 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 22.7 | 39.4 | 24.9 | 36.9 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 22.9 | 39.3 | 24.4 | 36.8 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 23.1 | 39.3 | 24 | 36.8 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:06 | 1 | 23.3 | 39.2 | 23.8 | 36.7 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.4 | 39.1 | 23.5 | 36.6 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.5 | 38.9 | 23.2 | 36.6 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.6 | 38.8 | 22.9 | 36.5 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.6 | 38.7 | 22.6 | 36.5 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.7 | 38.6 | 22.4 | 36.4 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:07 | 1 | 23.8 | 38.5 | 22.1 | 36.3 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 38.4 | 21.9 | 36.2 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 38.3 | 21.7 | 36.2 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 38.1 | 21.5 | 36.1 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 38 | 21.2 | 36.1 | 23.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 37.8 | 21 | 36 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:08 | 1 | 23.8 | 37.8 | 20.9 | 35.9 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:08 | 1 | 23.8 | 37.7 | 20.8 | 35.9 | 22.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.8 | 37.6 | 20.4 | 35.8 | 22.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.8 | 37.5 | 19.6 | 35.8 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.7 | 37.3 | 18.8 | 35.7 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.6 | 37.2 | 18.1 | 35.6 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.5 | 37 | 17.5 | 35.6 | 28.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:09 | 1 | 23.4 | 36.8 | 16.8 | 35.5 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:10 | 1 | 23.2 | 36.6 | 16.2 | 35.5 | 29.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:10 | 1 | 23 | 36.4 | 15.6 | 35.5 | 30.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:10 | 1 | 22.8 | 36.3 | 15.1 | 35.4 | 30.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:10 | 1 | 22.6 | 36.1 | 14.6 | 35.4 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:10 | 1 | 22.4 | 35.9 | 14.2 | 35.4 | 31.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:10 | 1 | 22.3 | 35.9 | 14.1 | 35.4 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:10 | 1 | 22.1 | 35.7 | 13.5 | 35.4 | 31.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 21.8 | 35.5 | 14.1 | 35.4 | 31.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 21.5 | 35.3 | 16.4 | 35.3 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 21.1 | 35.2 | 18.9 | 35.3 | 31.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 20.7 | 35.1 | 21.4 | 35.3 | 32 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 20.2 | 35.1 | 23.7 | 35.3 | 32 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:11 | 1 | 19.9 | 35 | 24.6 | 35.3 | 32.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 13:11 | 1 | 19.9 | 35 | 24.6 | 35.3 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:11 | 1 | 19.6 | 35 | 25.6 | 35.3 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:12 | 1 | 19 | 35 | 26.3 | 35.4 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:12 | 1 | 18.4 | 35 | 27.2 | 35.4 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:12 | 1 | 18.1 | 35 | 27.8 | 35.4 | 31.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:12 | 1 | 18.1 | 35 | 27.8 | 35.4 | 31.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:12 | 1 | 17.8 | 35 | 28.4 | 35.4 | 31.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:12 | 1 | 17.4 | 35 | 29.2 | 35.4 | 31.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:12 | 1 | 16.9 | 35 | 29.9 | 35.5 | 31.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:12 | 1 | 16.5 | 35.1 | 30.4 | 35.5 | 31.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 16.3 | 35.1 | 30.8 | 35.5 | 32 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 16.1 | 35.2 | 31 | 35.6 | 32.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 15.9 | 35.3 | 31.2 | 35.6 | 32.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 15.9 | 35.4 | 31.3 | 35.7 | 32.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 15.9 | 35.5 | 31.4 | 35.7 | 32.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:13 | 1 | 15.9 | 35.5 | 31.5 | 35.8 | 32.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 16.1 | 35.6 | 31.6 | 35.8 | 33 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 16.2 | 35.7 | 31.6 | 35.9 | 33.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 16.4 | 35.8 | 31.6 | 35.9 | 33.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 16.7 | 35.9 | 31.7 | 35.9 | 33.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 16.9 | 35.9 | 31.8 | 36 | 33.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:14 | 1 | 17.2 | 36 | 31.9 | 36 | 34 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 17.5 | 36 | 32 | 36.1 | 34.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 17.7 | 36.1 | 32.1 | 36.1 | 34.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 18 | 36.1 | 32.1 | 36.1 | 34.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 18.2 | 36.2 | 32.1 | 36.2 | 34.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 18.5 | 36.2 | 32.2 | 36.2 | 34.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:15 | 1 | 18.8 | 36.3 | 32.3 | 36.1 | 35.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 19.1 | 36.3 | 32.4 | 36.4 | 35.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 19.4 | 36.4 | 32.7 | 36.1 | 35.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 19.7 | 36.4 | 32.9 | 36.3 | 35.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 20 | 36.5 | 33.1 | 36.4 | 35.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 20.3 | 36.5 | 33.3 | 36.6 | 36 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:16 | 1 | 20.5 | 36.5 | 33.5 | 36.6 | 36.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:17 | 1 | 20.9 | 36.6 | 33.6 | 36.7 | 36.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:17 | 1 | 21.1 | 36.6 | 33.8 | 36.7 | 36.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:17 | 1 | 21.4 | 36.7 | 33.9 | 36.4 | 36.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:17 | 1 | 21.7 | 36.7 | 34 | 36.6 | 36.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:17 | 1 | 22 | 36.8 | 34.1 | 36.7 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:17 | 1 | 22 | 36.8 | 34.1 | 36.7 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:17 | 1 | 22.2 | 36.8 | 34.1 | 36.5 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 22.6 | 36.9 | 32.9 | 36.8 | 35.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 22.8 | 36.9 | 31.3 | 36.8 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 23 | 36.9 | 31.3 | 36.9 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 23.2 | 36.9 | 31.8 | 36.4 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 23.2 | 36.9 | 32.4 | 36.6 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:18 | 1 | 23.1 | 36.9 | 32.9 | 36.8 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 22.8 | 37 | 33.3 | 37 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 22.5 | 37 | 33.6 | 36.8 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 22.1 | 37 | 33.9 | 37 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 21.6 | 37 | 34.1 | 37.1 | 37.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 21 | 37.1 | 34.4 | 37.2 | 37.2 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 20.4 | 37.1 | 34.4 | 37.2 | 37.5 | 3.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:19 | 1 | 19.9 | 37.1 | 34.5 | 37.3 | 37.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:19 | 1 | 19.9 | 37.1 | 34.5 | 37.3 | 37.6 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 19.6 | 37.1 | 34.6 | 37.3 | 37.7 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 19 | 37.2 | 34.8 | 37.3 | 37.8 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 18.3 | 37.2 | 34.9 | 36.8 | 37.9 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 17.9 | 37.2 | 34.9 | 37.3 | 38 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 17.7 | 37.3 | 35 | 37.4 | 38.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 17.2 | 37.3 | 35.1 | 37.5 | 38.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:20 | 1 | 16.6 | 37.3 | 35.5 | 37.6 | 38.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 16.2 | 37.4 | 36 | 37.6 | 38.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 15.9 | 37.5 | 36.5 | 37.7 | 38.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 15.8 | 37.6 | 36.7 | 37.8 | 38.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 15.7 | 37.7 | 36.9 | 37.9 | 38.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 15.6 | 37.7 | 36.9 | 38 | 38.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:21 | 1 | 15.6 | 37.8 | 36.9 | 38.1 | 39 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 15.7 | 37.8 | 36.9 | 38.2 | 39.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 15.8 | 37.9 | 36.8 | 38.3 | 39.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 16 | 37.9 | 36.8 | 38.4 | 39.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 16.2 | 38 | 36.8 | 38.4 | 39.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 16.5 | 38.1 | 36.9 | 38.5 | 39.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:22 | 1 | 16.7 | 38.1 | 37 | 38.5 | 39.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 17.1 | 38.1 | 37.1 | 38.6 | 39.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 17.4 | 38.2 | 37.3 | 38.6 | 39.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 17.7 | 38.3 | 37.5 | 38.7 | 39.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 17.9 | 38.4 | 37.6 | 38.8 | 39.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 18.3 | 38.4 | 37.7 | 38.9 | 39.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:23 | 1 | 18.5 | 38.5 | 37.9 | 39 | 39.7 | 3 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 13:23 | 1 | 18.5 | 38.5 | 37.9 | 39 | 39.7 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:23 | 1 | 18.6 | 38.5 | 37.9 | 39 | 39.8 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 18.9 | 38.5 | 37.7 | 39.1 | 39.7 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 19.3 | 38.6 | 35.9 | 39.1 | 38.6 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 19.6 | 38.6 | 33.7 | 39.1 | 36.4 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 20 | 38.6 | 32 | 39.1 | 34.5 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 20.2 | 38.6 | 30.8 | 39 | 32.7 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:24 | 1 | 20.6 | 38.6 | 29.9 | 39 | 31.3 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 20.9 | 38.5 | 29.3 | 38.9 | 30.1 | 3.9 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 21.1 | 38.5 | 29.5 | 38.9 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 21.2 | 38.5 | 29.5 | 38.9 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 21.4 | 38.4 | 29.6 | 38.8 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 21.7 | 38.4 | 29.3 | 38.7 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 22 | 38.4 | 28.7 | 38.6 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:25 | 1 | 22.1 | 38.4 | 28 | 38.5 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 22.4 | 38.3 | 27.4 | 38.4 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 22.6 | 38.3 | 27 | 38.3 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 22.7 | 38.2 | 26.5 | 38.2 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 22.9 | 38.2 | 26.2 | 38.1 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 23.1 | 38.2 | 26 | 38 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:26 | 1 | 23.2 | 38 | 25.7 | 37.9 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.3 | 38 | 25.5 | 37.8 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.4 | 38 | 25.3 | 37.8 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.6 | 37.9 | 25.1 | 37.7 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.7 | 37.9 | 25 | 37.6 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.8 | 37.8 | 24.8 | 37.6 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:27 | 1 | 23.9 | 37.7 | 24.5 | 37.5 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24 | 37.6 | 24.3 | 37.3 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24.1 | 37.6 | 24 | 37.3 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24.1 | 37.4 | 23.8 | 37.2 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24.2 | 37.4 | 23.5 | 37.1 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24.3 | 37.3 | 23.2 | 37 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:28 | 1 | 24.3 | 37.2 | 23 | 36.9 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.3 | 37.1 | 22.7 | 36.8 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.4 | 37.1 | 22.5 | 36.7 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.4 | 37 | 22.2 | 36.6 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.4 | 36.9 | 21.9 | 36.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.4 | 36.8 | 21.8 | 36.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:29 | 1 | 24.4 | 36.7 | 21.6 | 36.3 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:30 | 1 | 24.5 | 36.6 | 21.3 | 36.2 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:30 | 1 | 24.5 | 36.5 | 21.2 | 36.1 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:30 | 1 | 24.4 | 36.4 | 20.9 | 36 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:30 | 1 | 24.4 | 36.3 | 20.7 | 35.9 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:30 | 1 | 24.4 | 36.3 | 20.6 | 35.9 | 22 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:30 | 1 | 24.4 | 36.2 | 20.4 | 35.8 | 21.8 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:30 | 1 | 24.4 | 36 | 19.8 | 35.6 | 22 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:30 | 1 | 24.3 | 35.9 | 19.2 | 35.5 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 24.3 | 35.9 | 19 | 35.5 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 24.2 | 35.8 | 18.2 | 35.4 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 24.1 | 35.7 | 18.1 | 35.3 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 23.9 | 35.6 | 19.5 | 35.3 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 23.6 | 35.5 | 21.5 | 35.2 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:31 | 1 | 23.3 | 35.5 | 23.4 | 35.2 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 22.9 | 35.4 | 25.3 | 35.2 | 30 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 22.4 | 35.4 | 26.9 | 35.1 | 30.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 21.8 | 35.4 | 28.1 | 35.2 | 30.9 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 21.2 | 35.4 | 29 | 35.1 | 31.2 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 20.5 | 35.4 | 29.6 | 35.1 | 31.5 | 3.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:32 | 1 | 19.9 | 35.4 | 30.1 | 35.1 | 31.6 | 3 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 13:32 | 1 | 19.9 | 35.4 | 30.1 | 35.1 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:32 | 1 | 19.8 | 35.4 | 30.1 | 35.2 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:33 | 1 | 19 | 35.4 | 29.8 | 35.2 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:33 | 1 | 18.3 | 35.4 | 29.5 | 35.2 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:33 | 1 | 17.8 | 35.5 | 29.8 | 35.2 | 31.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:33 | 1 | 17.8 | 35.5 | 29.8 | 35.2 | 31.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:33 | 1 | 17.6 | 35.5 | 29.9 | 35.2 | 31.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:33 | 1 | 17.2 | 35.5 | 30.4 | 35.3 | 31.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:33 | 1 | 16.7 | 35.5 | 30.8 | 35.3 | 31.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 2 | 15.9 | 35.7 | 31.2 | 35.4 | 32.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 1 | 15.7 | 35.7 | 31.3 | 35.5 | 32.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 1 | 15.7 | 35.8 | 31.4 | 35.5 | 32.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 1 | 15.7 | 35.8 | 31.5 | 35.5 | 32.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 1 | 15.6 | 35.9 | 31.6 | 35.6 | 32.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:34 | 1 | 15.7 | 35.9 | 31.6 | 35.6 | 32.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 15.9 | 36 | 31.7 | 35.7 | 32.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 16 | 36 | 31.7 | 35.7 | 33.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 16.2 | 36 | 31.8 | 35.7 | 33.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 16.4 | 36.1 | 31.9 | 35.8 | 33.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 16.7 | 36.1 | 32 | 35.8 | 33.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:35 | 1 | 17 | 36.1 | 32.1 | 35.9 | 33.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 17.3 | 36.2 | 32.2 | 35.9 | 34 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 17.6 | 36.2 | 32.4 | 35.9 | 34.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 17.8 | 36.3 | 32.5 | 36 | 34.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 18 | 36.3 | 32.8 | 36 | 34.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 18.4 | 36.3 | 33 | 36.1 | 34.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:36 | 1 | 18.7 | 36.4 | 33.2 | 36.1 | 34.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 18.9 | 36.4 | 33.4 | 36.2 | 35.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 19.3 | 36.4 | 33.5 | 36.2 | 35.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 19.6 | 36.5 | 33.6 | 36.2 | 35.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 19.8 | 36.5 | 33.8 | 36.3 | 35.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 20.2 | 36.5 | 33.9 | 36.3 | 35.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:37 | 1 | 20.5 | 36.6 | 33.9 | 36.4 | 36 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 20.7 | 36.6 | 34 | 36.4 | 36.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 21.1 | 36.6 | 34.1 | 36.5 | 36.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 21.3 | 36.7 | 34.2 | 36.5 | 36.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 21.6 | 36.7 | 34.3 | 36.6 | 36.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 21.9 | 36.8 | 34.4 | 36.6 | 36.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:38 | 1 | 22 | 36.8 | 34.4 | 36.6 | 36.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:38 | 1 | 22.2 | 36.8 | 34.4 | 36.7 | 36.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 22.4 | 36.8 | 33.9 | 36.8 | 36.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 22.8 | 36.9 | 32 | 36.8 | 35 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 22.9 | 36.9 | 31.4 | 36.8 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 23 | 36.9 | 31.4 | 36.8 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 23.1 | 37.1 | 31.8 | 36.8 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 23.2 | 37.8 | 32.5 | 36.8 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:39 | 1 | 23.2 | 38.6 | 33.6 | 36.9 | 35.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:40 | 1 | 22.9 | 39.5 | 34.7 | 37.1 | 36.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:40 | 1 | 22.8 | 40 | 35.5 | 37.2 | 36.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:40 | 1 | 22.6 | 40.3 | 35.9 | 37.3 | 37.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:40 | 1 | 22.2 | 40.9 | 34.3 | 37.5 | 37.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:40 | 1 | 21.7 | 41.6 | 32.3 | 37.7 | 38.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:40 | 1 | 21.2 | 42 | 30.1 | 38 | 39 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:40 | 1 | 20.8 | 42.5 | 28.3 | 38.2 | 39.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 20.5 | 43 | 27.1 | 38.4 | 40 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 20.1 | 43.3 | 26.3 | 38.7 | 40.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 19.9 | 43.4 | 25.8 | 38.8 | 40.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 19.9 | 43.4 | 25.7 | 38.8 | 40.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 19.8 | 43.5 | 25.6 | 38.9 | 40.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 13:41 | 1 | 19.8 | 43.5 | 25.6 | 39 | 40.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:41 | 1 | 19.6 | 43.7 | 25.3 | 39.1 | 40.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:41 | 1 | 19.5 | 43.8 | 25.9 | 39.3 | 38.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:41 | 1 | 19.3 | 44 | 26.4 | 39.5 | 36 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.2 | 44.8 | 26.7 | 39.5 | 34 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.2 | 45.3 | 27 | 39.6 | 33 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.2 | 45.4 | 27 | 39.6 | 32.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.1 | 45.6 | 27.2 | 39.7 | 32.1 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.1 | 45.5 | 27.3 | 39.7 | 31.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.2 | 45.2 | 27.3 | 39.7 | 31 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:42 | 1 | 19.3 | 44.8 | 27.4 | 39.7 | 30.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 19.4 | 44.5 | 27.4 | 39.5 | 30.1 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 19.6 | 44.1 | 27.5 | 39.5 | 29.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 19.7 | 43.8 | 27.6 | 39.4 | 29.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 19.9 | 43.5 | 27.7 | 39.3 | 29.4 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 20 | 43.2 | 27.7 | 39.2 | 29.4 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:43 | 1 | 20.2 | 42.9 | 27.7 | 39.2 | 29.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 20.4 | 42.7 | 27.7 | 39.1 | 29.1 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 20.5 | 42.4 | 27.7 | 39 | 29 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 20.7 | 42.2 | 27.7 | 39 | 28.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 21 | 42 | 27.7 | 38.9 | 28.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 21.2 | 41.8 | 27.7 | 38.9 | 28.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:44 | 1 | 21.3 | 41.7 | 27.6 | 38.8 | 28.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 21.6 | 41.4 | 27.4 | 38.7 | 28 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 21.8 | 41.3 | 27.1 | 38.6 | 27.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 22 | 41.2 | 26.9 | 38.5 | 27.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 22 | 41.1 | 26.9 | 38.5 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 22.2 | 41 | 26.5 | 38.4 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 22.4 | 40.8 | 26.1 | 38.4 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:45 | 1 | 22.7 | 40.6 | 25.6 | 38.3 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 22.9 | 40.5 | 25.1 | 38.2 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 23.1 | 40.3 | 24.6 | 38.1 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 23.3 | 40.2 | 24.2 | 38 | 24.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 23.5 | 40 | 23.8 | 37.8 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 23.7 | 39.9 | 23.4 | 37.7 | 24.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:46 | 1 | 23.9 | 39.7 | 23 | 37.6 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.1 | 39.5 | 22.7 | 37.5 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.3 | 39.4 | 22.5 | 37.4 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.4 | 39.3 | 22.2 | 37.3 | 22.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.6 | 39.1 | 22 | 37.1 | 22.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.7 | 39 | 21.8 | 37 | 22.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:47 | 1 | 24.7 | 38.8 | 21.6 | 36.8 | 22.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 38.6 | 21.4 | 36.8 | 22.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 38.5 | 21.2 | 36.6 | 22 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 38.3 | 21 | 36.5 | 21.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 38.2 | 20.7 | 36.3 | 21.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 38 | 20.5 | 36.2 | 21.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:48 | 1 | 24.7 | 37.8 | 20.4 | 36.1 | 21.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.7 | 37.7 | 20.1 | 36 | 21.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.6 | 37.6 | 19.9 | 35.9 | 21 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.5 | 37.4 | 19.7 | 35.8 | 20.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.4 | 37.2 | 19.5 | 35.6 | 20.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.4 | 37.1 | 19.3 | 35.5 | 20.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:49 | 1 | 24.3 | 37 | 19.1 | 35.4 | 20.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:50 | 1 | 24.2 | 36.8 | 18.9 | 35.3 | 20.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:50 | 1 | 24 | 36.7 | 18.7 | 35.2 | 20.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:50 | 1 | 23.9 | 36.5 | 18.5 | 35 | 20 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 13:50 | 1 | 23.8 | 36.4 | 18.4 | 34.9 | 19.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:50 | 1 | 23.8 | 36.4 | 18.3 | 34.9 | 19.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:50 | 1 | 23.7 | 36.2 | 18.1 | 34.8 | 19.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:50 | 1 | 23.5 | 36.1 | 17.6 | 34.7 | 20.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 13:51 | 1 | 23.4 | 35.9 | 17 | 34.6 | 21.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 23.4 | 35.9 | 16.9 | 34.6 | 21.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 23.3 | 35.8 | 15.9 | 34.5 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 23.1 | 35.5 | 15.9 | 34.4 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 22.9 | 35.4 | 17.5 | 34.3 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 22.6 | 35.3 | 19.5 | 34.3 | 27.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:51 | 1 | 22.2 | 35.2 | 21.7 | 34.2 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:52 | 1 | 21.8 | 35.2 | 23.7 | 34.2 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:52 | 1 | 21.3 | 35.1 | 25.5 | 34.2 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:52 | 1 | 20.7 | 35.1 | 26.9 | 34.2 | 30.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:52 | 1 | 20.1 | 35.1 | 28.2 | 34.2 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:52 | 1 | 19.9 | 35.1 | 28.4 | 34.2 | 30.8 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 13:52 | 1 | 19.9 | 35.1 | 28.4 | 34.2 | 30.8 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:52 | 1 | 19.5 | 35.1 | 28.8 | 34.2 | 30.9 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:52 | 1 | 18.7 | 35.1 | 28.3 | 34.2 | 30.5 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:53 | 1 | 18.1 | 35.1 | 28.5 | 34.3 | 30.3 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 13:53 | 1 | 17.9 | 35.1 | 28.7 | 34.3 | 30.3 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 17.9 | 35.1 | 28.7 | 34.3 | 30.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 17.6 | 35.1 | 29.3 | 34.3 | 30.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 17.1 | 35.2 | 30 | 34.3 | 31 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 16.7 | 35.3 | 30.4 | 34.4 | 31.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 16.4 | 35.3 | 30.8 | 34.4 | 31.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:53 | 1 | 16.2 | 35.4 | 31 | 34.5 | 31.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 16.1 | 35.4 | 31.2 | 34.5 | 31.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 15.9 | 35.5 | 31.3 | 34.6 | 32 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 15.9 | 35.5 | 31.3 | 34.7 | 32.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 16 | 35.6 | 31.4 | 34.7 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 16.1 | 35.7 | 31.5 | 34.8 | 32.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:54 | 1 | 16.2 | 35.8 | 31.5 | 34.8 | 32.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 16.4 | 35.8 | 31.6 | 34.9 | 32.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 16.7 | 35.9 | 31.6 | 35 | 32.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 16.9 | 35.9 | 31.6 | 35 | 32.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 17.2 | 35.9 | 31.7 | 35.1 | 32.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 17.5 | 36 | 31.7 | 35.1 | 32.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:55 | 1 | 17.6 | 36 | 31.7 | 35.2 | 32.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 18 | 36.1 | 31.7 | 35.2 | 32.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 18.2 | 36.1 | 31.8 | 35.2 | 32.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 18.6 | 36.2 | 31.8 | 35.3 | 33 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 18.9 | 36.2 | 31.8 | 35.4 | 33.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 19.1 | 36.2 | 31.9 | 35.4 | 33.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:56 | 1 | 19.5 | 36.3 | 32 | 35.4 | 33.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 19.8 | 36.3 | 32.1 | 35.5 | 33.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 20.1 | 36.3 | 32.1 | 35.5 | 33.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 20.4 | 36.4 | 32.1 | 35.6 | 34 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 20.7 | 36.4 | 32.1 | 35.6 | 34.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 21 | 36.4 | 32.1 | 35.7 | 34.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:57 | 1 | 21.4 | 36.5 | 32.2 | 35.7 | 34.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:58 | 1 | 21.6 | 36.5 | 32.2 | 35.7 | 34.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 13:58 | 1 | 22 | 36.5 | 32.3 | 35.8 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:58 | 1 | 22 | 36.5 | 32.3 | 35.8 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:58 | 1 | 22.2 | 36.6 | 32.3 | 35.8 | 34.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:58 | 1 | 22.6 | 36.6 | 31.8 | 35.9 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:58 | 1 | 22.8 | 36.6 | 31.5 | 35.9 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:58 | 1 | 23.1 | 36.6 | 31.6 | 35.9 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 23.2 | 36.6 | 31.7 | 36 | 33.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 23.3 | 36.6 | 31.8 | 36 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 23.2 | 36.7 | 32 | 36 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 22.9 | 36.7 | 32.1 | 36 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 22.7 | 36.7 | 32.2 | 36.1 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 22.6 | 36.7 | 32.2 | 36.1 | 34.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 13:59 | 1 | 22.1 | 36.9 | 32.4 | 36.1 | 35.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:00 | 1 | 21.5 | 37.5 | 32.9 | 36.1 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:00 | 1 | 20.9 | 38.3 | 33.8 | 36.3 | 35.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:00 | 1 | 20.7 | 38.6 | 34.1 | 36.4 | 35.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:00 | 1 | 20.2 | 39.2 | 34.8 | 36.5 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:00 | 1 | 19.9 | 39.4 | 35.2 | 36.5 | 36.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:00 | 1 | 19.9 | 39.4 | 35.2 | 36.5 | 36.4 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:00 | 1 | 19.9 | 39.5 | 35.2 | 36.5 | 36.4 | 3.8 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:00 | 1 | 19.6 | 39.6 | 35.5 | 36.6 | 36.7 | 3.8 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:00 | 1 | 18.9 | 39.7 | 34.2 | 36.7 | 37.1 | 3.8 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:00 | 1 | 18.1 | 39.7 | 33.4 | 36.8 | 37.5 | 3.8 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 17.8 | 39.7 | 33.3 | 36.8 | 37.6 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 17.6 | 39.7 | 33.4 | 36.9 | 37.7 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 16.9 | 39.6 | 33.9 | 36.9 | 37.9 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 16.4 | 39.5 | 34.7 | 37 | 38 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 16.2 | 39.5 | 35.1 | 37.1 | 38.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 16 | 39.5 | 35.3 | 37.1 | 38.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 15.7 | 39.6 | 35.8 | 37.2 | 38.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:01 | 1 | 15.4 | 40.1 | 36.4 | 37.3 | 38.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:02 | 1 | 15.3 | 40.7 | 37 | 37.4 | 38.4 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:02 | 1 | 15.3 | 41.5 | 37.6 | 37.6 | 38.7 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:02 | 1 | 15.2 | 41.6 | 37.7 | 37.6 | 38.7 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:02 | 1 | 15.2 | 42.2 | 38.3 | 37.8 | 39.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:02 | 1 | 15.2 | 42.3 | 38.7 | 38 | 39.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:02 | 1 | 15.2 | 42.4 | 38.8 | 38 | 39.3 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:02 | 1 | 15.3 | 42.4 | 39.3 | 38.2 | 39.6 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:02 | 1 | 15.5 | 42.4 | 39.4 | 38.3 | 39.8 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:03 | 1 | 15.7 | 42.3 | 39.6 | 38.4 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:03 | 1 | 15.9 | 42.3 | 39.8 | 38.5 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:03 | 1 | 16.2 | 42.2 | 39.9 | 38.6 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:03 | 1 | 16.3 | 42.2 | 40 | 38.6 | 39.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:03 | 1 | 16.5 | 42.1 | 40 | 38.7 | 39.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:03 | 1 | 16.8 | 42.1 | 39.2 | 38.7 | 39.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:03 | 1 | 17.1 | 42 | 36.7 | 38.8 | 38.7 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 17.5 | 41.8 | 34.5 | 38.9 | 36.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 17.6 | 41.7 | 33 | 38.9 | 34.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 17.9 | 41.5 | 31.8 | 38.9 | 32.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 18.2 | 41.3 | 31.1 | 38.8 | 31.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 18.5 | 41.2 | 30.9 | 38.7 | 31.4 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:04 | 1 | 18.8 | 41 | 30.9 | 38.6 | 31.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 19.1 | 40.9 | 31 | 38.6 | 30.9 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 19.3 | 40.8 | 30.7 | 38.6 | 30.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 19.7 | 40.6 | 30.3 | 38.5 | 30.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 19.9 | 40.5 | 29.8 | 38.5 | 29.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 20.2 | 40.3 | 29.2 | 38.4 | 29.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:05 | 1 | 20.4 | 40.2 | 28.8 | 38.3 | 29.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 20.7 | 40.1 | 28.4 | 38.3 | 29 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 21 | 39.9 | 27.9 | 38.3 | 28.8 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 21.3 | 39.8 | 27.5 | 38.2 | 28.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 21.5 | 39.7 | 27.2 | 38.1 | 28.1 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 21.8 | 39.5 | 26.8 | 38.1 | 27.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 22 | 39.5 | 26.6 | 38 | 27.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:06 | 1 | 22.1 | 39.4 | 26.4 | 38 | 27.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 22.3 | 39.3 | 26.1 | 37.9 | 26.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 22.6 | 39.2 | 25.8 | 37.8 | 26.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 22.8 | 39.1 | 25.5 | 37.7 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 23 | 38.9 | 25.1 | 37.6 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 23.3 | 38.9 | 24.8 | 37.5 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:07 | 1 | 23.5 | 38.7 | 24.5 | 37.4 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 23.6 | 38.6 | 24.1 | 37.3 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 23.8 | 38.4 | 23.9 | 37.2 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 24 | 38.3 | 23.6 | 37.1 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 24.2 | 38.2 | 23.4 | 37 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 24.3 | 38.1 | 23.1 | 36.9 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:08 | 1 | 24.4 | 37.9 | 22.8 | 36.8 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 24.5 | 37.8 | 22.6 | 36.7 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 24.6 | 37.7 | 22.4 | 36.6 | 23.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 24.7 | 37.6 | 22.1 | 36.5 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 24.8 | 37.4 | 21.9 | 36.4 | 22.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 24.9 | 37.3 | 21.7 | 36.3 | 22.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:09 | 1 | 25 | 37.2 | 21.5 | 36.1 | 22.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25 | 37.1 | 21.3 | 36 | 22.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25 | 36.9 | 21 | 35.9 | 22 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25.1 | 36.8 | 20.9 | 35.8 | 21.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25.1 | 36.7 | 20.7 | 35.7 | 21.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25.1 | 36.5 | 20.5 | 35.6 | 21.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:10 | 1 | 25.1 | 36.5 | 20.3 | 35.5 | 21.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 36.3 | 20.1 | 35.4 | 21.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 36.2 | 20 | 35.3 | 21.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 36 | 19.8 | 35.2 | 21.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 35.9 | 19.7 | 35.1 | 21 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 35.9 | 19.7 | 35.1 | 21 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 35.8 | 19.4 | 35 | 20.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:11 | 1 | 25.1 | 35.8 | 19.3 | 34.9 | 20.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:11 | 1 | 25 | 35.7 | 19.2 | 34.8 | 20.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 24.9 | 35.6 | 20.4 | 34.8 | 19.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 24.8 | 35.5 | 22.3 | 34.7 | 20.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 24.7 | 35.5 | 24 | 34.6 | 22.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 24.5 | 35.4 | 25.5 | 34.5 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 24.1 | 35.4 | 26.9 | 34.4 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:12 | 1 | 23.6 | 35.4 | 28.1 | 34.4 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 23.1 | 35.4 | 28.9 | 34.4 | 28 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 22.5 | 35.4 | 29.5 | 34.4 | 28.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 21.9 | 35.4 | 30 | 34.3 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 21.2 | 35.5 | 30.4 | 34.3 | 30.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 20.5 | 35.5 | 30.7 | 34.3 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:13 | 1 | 19.9 | 35.5 | 30.9 | 34.4 | 30.8 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 14:13 | 1 | 19.9 | 35.5 | 30.9 | 34.4 | 30.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:13 | 1 | 19.7 | 35.6 | 31 | 34.4 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:14 | 1 | 19.1 | 35.7 | 30.6 | 34.4 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:14 | 1 | 18.9 | 35.7 | 30.3 | 34.4 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:14 | 1 | 18.1 | 35.9 | 29.9 | 34.4 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:14 | 1 | 17.7 | 36.3 | 30 | 34.4 | 31.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 17.7 | 36.3 | 30 | 34.4 | 31.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 17.4 | 36.6 | 30.3 | 34.4 | 31.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 16.7 | 37.4 | 30.7 | 34.6 | 31.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 16.2 | 38.2 | 31.1 | 34.8 | 31.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 15.8 | 39.1 | 31.4 | 34.9 | 31.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 14:14 | 1 | 15.6 | 39.5 | 31.4 | 35 | 32 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 15.5 | 39.8 | 31.5 | 35.1 | 32 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 15.4 | 40 | 31.5 | 35.1 | 32.1 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 15.1 | 40.5 | 31.7 | 35.3 | 32.3 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 15 | 40.6 | 31.9 | 35.5 | 32.5 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 14.9 | 40.6 | 32 | 35.6 | 32.8 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 14.9 | 40.5 | 32.3 | 35.7 | 33 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:15 | 1 | 14.9 | 40.4 | 32.8 | 35.7 | 33.2 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 15 | 40.3 | 33.4 | 35.8 | 33.5 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 15.2 | 40.1 | 33.9 | 35.9 | 33.8 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 15.3 | 40 | 34.4 | 35.9 | 34.1 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 15.6 | 40 | 34.8 | 36 | 34.3 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 15.8 | 39.9 | 35.1 | 36 | 34.5 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:16 | 1 | 16 | 39.9 | 35.2 | 36.1 | 34.6 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:16 | 1 | 16.1 | 39.8 | 35.4 | 36.1 | 34.7 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 16.4 | 39.8 | 35 | 36.2 | 34.6 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 16.7 | 39.7 | 33.3 | 36.2 | 33.6 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 17.1 | 39.6 | 31.6 | 36.2 | 32.9 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 17.4 | 39.5 | 31.2 | 36.3 | 33 | 4.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 17.7 | 39.4 | 30.4 | 36.3 | 33.4 | 4.3 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:17 | 1 | 17.8 | 39.2 | 29 | 36.3 | 33.9 | 4.2 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 18.1 | 39.1 | 27.6 | 36.3 | 34.3 | 4.2 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 18.3 | 39 | 26.2 | 36.4 | 34.6 | 4.2 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 18.5 | 38.8 | 25 | 36.4 | 34.9 | 4.1 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 18.8 | 38.7 | 23.9 | 36.4 | 35.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 19.1 | 38.5 | 23.1 | 36.4 | 35.4 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:18 | 1 | 19.3 | 38.3 | 22.4 | 36.4 | 35.6 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 19.5 | 38.1 | 21.6 | 36.4 | 35.7 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 19.7 | 37.9 | 21 | 36.4 | 35.8 | 3.7 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 20 | 37.6 | 20.4 | 36.4 | 35.9 | 3.6 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 20.2 | 37.4 | 20 | 36.4 | 36 | 3.5 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 20.4 | 37.2 | 19.5 | 36.4 | 36 | 3.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:19 | 1 | 20.7 | 37 | 19 | 36.4 | 36 | 3.4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:20 | 1 | 20.8 | 36.8 | 18.7 | 36.4 | 36.1 | 3.3 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:20 | 1 | 21.1 | 36.5 | 18.4 | 36.4 | 36.1 | 3.2 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:20 | 1 | 21.3 | 36.3 | 18 | 36.3 | 36.1 | 3.1 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:20 | 1 | 21.6 | 36.1 | 17.8 | 36.3 | 36.1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:20 | 1 | 21.8 | 35.9 | 17.6 | 36.3 | 36.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 1
2022-09-07 14:20 | 1 | 21.8 | 35.9 | 17.6 | 36.3 | 36.1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:20 | 1 | 21.8 | 35.9 | 17.6 | 36.3 | 36.1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:20 | 1 | 22 | 35.8 | 17.5 | 36.3 | 36.1 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:20 | 1 | 22 | 35.7 | 17.7 | 36.3 | 36.1 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:21 | 1 | 22.3 | 35.6 | 19.5 | 36.3 | 36.2 | 3.9 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-07 14:21 | 1 | 22.5 | 35.4 | 21.9 | 36.3 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:21 | 1 | 22.5 | 35.4 | 22.4 | 36.3 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:21 | 1 | 22.7 | 35.4 | 25 | 36.3 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:21 | 1 | 23 | 35.4 | 27.1 | 36.3 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:21 | 1 | 23.3 | 35.3 | 28.5 | 36.3 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:21 | 1 | 23.6 | 35.3 | 29.5 | 36.3 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 23.8 | 35.4 | 30.2 | 36.4 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 24.1 | 35.4 | 30.6 | 36.4 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 24.4 | 35.4 | 30.9 | 36.5 | 37 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 24.7 | 35.5 | 31.1 | 36.5 | 37.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 25 | 35.6 | 31.3 | 36.6 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:22 | 1 | 25.3 | 35.6 | 31.4 | 36.6 | 37.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:23 | 1 | 25.6 | 35.6 | 31.4 | 36.7 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:23 | 1 | 26 | 35.7 | 31.5 | 36.7 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:23 | 1 | 26.2 | 35.8 | 31.5 | 36.8 | 37.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:23 | 1 | 26.6 | 35.8 | 31.6 | 36.9 | 37.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 14:23 | 1 | 26.9 | 35.8 | 31.6 | 36.9 | 37.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:23 | 1 | 27 | 35.8 | 31.6 | 36.9 | 37.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:23 | 1 | 27.3 | 35.9 | 31.6 | 36.9 | 37.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:24 | 1 | 27.6 | 36 | 31.7 | 37 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:24 | 1 | 27.9 | 36 | 31.6 | 37 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:24 | 1 | 28.1 | 36 | 31.6 | 37.1 | 37.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:24 | 1 | 28.2 | 36 | 31.6 | 37.1 | 37.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:24 | 1 | 28.4 | 36.1 | 31.6 | 37.1 | 35.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:24 | 1 | 28.5 | 36.1 | 31.6 | 37.1 | 33.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:24 | 1 | 28.4 | 36.2 | 31.6 | 37.1 | 31.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.5 | 36.2 | 31.6 | 37.1 | 30.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.5 | 36.2 | 31.7 | 37.1 | 29 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.5 | 36.3 | 31.7 | 37.1 | 28.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.5 | 36.3 | 31.7 | 37.1 | 27.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.4 | 36.4 | 31.7 | 37.1 | 26.7 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:25 | 1 | 28.4 | 36.4 | 31.8 | 37.1 | 26.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28.4 | 36.5 | 31.8 | 37.1 | 25.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28.3 | 36.5 | 31.8 | 37 | 25.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28.2 | 36.6 | 31.8 | 37 | 24.8 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28.2 | 36.6 | 31.8 | 36.9 | 24.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28.1 | 36.7 | 31.8 | 36.9 | 24 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:26 | 1 | 28 | 36.7 | 31.9 | 36.8 | 23.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 28 | 36.7 | 31.9 | 36.8 | 23 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 27.9 | 36.8 | 31.9 | 36.7 | 22.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 27.8 | 36.8 | 31.9 | 36.6 | 22 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 27.7 | 36.9 | 31.9 | 36.5 | 21.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 27.6 | 36.9 | 32 | 36.5 | 20.9 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:27 | 1 | 27.5 | 36.9 | 32.1 | 36.4 | 20.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 27.4 | 37 | 32.2 | 36.2 | 19.9 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 27.3 | 37 | 32.3 | 36.1 | 19.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 27.2 | 37.1 | 32.4 | 36 | 19.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 27.1 | 37.1 | 32.6 | 35.9 | 18.8 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 27 | 37.1 | 32.7 | 35.8 | 18.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:28 | 1 | 26.9 | 37.2 | 32.8 | 35.7 | 18.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.7 | 37.2 | 32.9 | 35.5 | 18.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.6 | 37.3 | 33 | 35.4 | 17.8 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.5 | 37.3 | 33.1 | 35.3 | 17.7 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.3 | 37.4 | 33.1 | 35.2 | 17.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.2 | 37.4 | 33.2 | 35.1 | 17.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:29 | 1 | 26.1 | 37.4 | 33.3 | 34.9 | 17.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:29 | 1 | 26.1 | 37.4 | 33.3 | 34.9 | 17.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 26 | 37.5 | 33.3 | 34.8 | 16.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 25.8 | 37.5 | 33.4 | 34.6 | 17.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 25.6 | 37.6 | 33.5 | 34.6 | 18.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 25.4 | 37.6 | 33.5 | 34.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 25.1 | 37.7 | 33.6 | 34.4 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:30 | 1 | 24.7 | 37.7 | 33.7 | 34.3 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 24.2 | 37.7 | 33.8 | 34.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 23.7 | 37.8 | 33.9 | 34.3 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 23.1 | 37.8 | 34 | 34.3 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 22.5 | 37.9 | 34.1 | 34.3 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 21.8 | 37.9 | 34.2 | 34.3 | 30 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:31 | 1 | 21.1 | 37.9 | 34.3 | 34.3 | 30.5 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:32 | 1 | 20.4 | 38 | 34.4 | 34.3 | 30.9 | 3.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:32 | 1 | 19.9 | 38 | 34.4 | 34.3 | 31.1 | 3 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 14:32 | 1 | 19.9 | 38 | 34.4 | 34.3 | 31.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 0
2022-09-07 14:32 | 1 | 19.6 | 38 | 34.5 | 34.4 | 31.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 0
2022-09-07 14:32 | 1 | 19 | 38.1 | 34.6 | 34.4 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:32 | 1 | 19 | 38.1 | 34.6 | 34.4 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:32 | 1 | 18.2 | 38.1 | 34.6 | 34.4 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 14:32 | 1 | 17.9 | 38.1 | 34.5 | 34.5 | 30.1 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:32 | 1 | 17.7 | 38.1 | 34.3 | 34.5 | 30.3 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:32 | 1 | 17.2 | 38.2 | 34.3 | 34.6 | 30.8 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 16.7 | 38.2 | 34.5 | 34.6 | 31.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 16.3 | 38.2 | 34.8 | 34.7 | 31.5 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 16 | 38.3 | 35.1 | 34.8 | 31.7 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 15.9 | 38.3 | 35.3 | 34.8 | 31.9 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 15.7 | 38.4 | 35.4 | 34.9 | 32 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:33 | 1 | 15.7 | 38.4 | 35.5 | 35 | 32.1 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 15.7 | 38.4 | 35.6 | 35.1 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 15.8 | 38.5 | 35.7 | 35.2 | 32.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 15.9 | 38.5 | 35.7 | 35.2 | 32.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 16.1 | 38.6 | 35.7 | 35.3 | 32.6 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 16.3 | 38.6 | 35.8 | 35.3 | 32.7 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:34 | 1 | 16.5 | 38.6 | 35.8 | 35.4 | 32.8 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:35 | 1 | 16.8 | 38.7 | 35.9 | 35.4 | 32.9 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:35 | 1 | 17 | 38.7 | 35.9 | 35.5 | 33 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:35 | 1 | 17 | 38.7 | 35.9 | 35.5 | 33 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 14:35 | 1 | 17 | 38.7 | 35.9 | 35.5 | 33 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.1 | 38.7 | 35.9 | 35.5 | 33 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.2 | 38.8 | 35.9 | 35.5 | 33 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.3 | 39 | 35.9 | 35.5 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.3 | 39 | 35.9 | 35.5 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.4 | 39 | 36 | 35.5 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.4 | 39.2 | 36 | 35.6 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.4 | 39.3 | 36 | 35.6 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.4 | 39.4 | 36 | 35.6 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 17.6 | 40.1 | 36.3 | 35.9 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 18 | 40.3 | 36.4 | 36.1 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:35 | 1 | 18.3 | 40.4 | 36.1 | 36.3 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 18.6 | 40.4 | 35.9 | 36.3 | 33.1 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 18.9 | 40.3 | 35.7 | 36.4 | 33.2 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 19.4 | 40.3 | 35.3 | 36.4 | 33.4 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 19.8 | 40.2 | 34.8 | 36.5 | 33.6 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 20.4 | 40.1 | 34.5 | 36.5 | 34 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:36 | 1 | 20.9 | 40.1 | 34.2 | 36.5 | 34.3 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:37 | 1 | 21.5 | 40 | 34.1 | 36.6 | 34.5 | 0.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 14:37 | 1 | 22 | 40 | 34 | 36.6 | 34.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 14:37 | 1 | 22.1 | 39.9 | 33.9 | 36.6 | 34.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 14:37 | 1 | 22.2 | 39.9 | 33.9 | 36.6 | 34.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 14:37 | 1 | 22.6 | 39.9 | 33.8 | 37.1 | 34.9 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:37 | 1 | 22.6 | 39.9 | 33.8 | 37.2 | 34.9 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:37 | 1 | 23 | 39.9 | 33.8 | 38.9 | 35.1 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:37 | 1 | 23.2 | 39.9 | 33.8 | 39.5 | 35.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:37 | 1 | 23.7 | 40 | 33.8 | 39.9 | 35.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:37 | 1 | 24.1 | 40 | 34 | 40 | 36.5 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 24.6 | 40.1 | 34.4 | 39.9 | 37.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 24.9 | 40.1 | 34.7 | 39.7 | 37.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 25.3 | 40.1 | 35 | 39.6 | 37.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 25.7 | 40.1 | 35.7 | 39.5 | 37.6 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 26 | 40.2 | 36.5 | 39.4 | 37.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:38 | 1 | 26.2 | 40.2 | 37 | 39.3 | 38 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 26.6 | 40.2 | 37.5 | 39.3 | 38.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 26.8 | 40.3 | 37.8 | 39.2 | 38.3 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 27 | 40.3 | 38 | 39.2 | 38.4 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 27.2 | 40.3 | 38.2 | 39.2 | 38.6 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 27.5 | 40.4 | 38.4 | 39.1 | 38.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:39 | 1 | 27.7 | 40.4 | 38.5 | 39.1 | 38.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 27.9 | 40.5 | 38.6 | 39.1 | 38.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 28.2 | 40.5 | 38.7 | 39.1 | 38.9 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 28.4 | 40.6 | 38.8 | 39.1 | 39 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 28.5 | 40.6 | 38.9 | 39.1 | 39 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 28.8 | 40.7 | 39 | 39.1 | 39.1 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:40 | 1 | 29 | 40.7 | 39.1 | 39.1 | 39.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 29.2 | 40.8 | 39.2 | 39.1 | 39.3 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 29.4 | 40.8 | 39.3 | 39.1 | 39.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 29.6 | 40.9 | 39.3 | 39.2 | 39.3 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 29.9 | 40.9 | 39.4 | 39.2 | 39.4 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 30.1 | 41 | 39.4 | 39.2 | 39.4 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:41 | 1 | 30.3 | 41.1 | 39.5 | 39.3 | 39.5 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 30.6 | 41.1 | 39.6 | 39.2 | 39.6 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 30.8 | 41.1 | 39.7 | 39.3 | 39.6 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 30.9 | 41.2 | 39.8 | 39.3 | 39.7 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 31.2 | 41.3 | 39.9 | 39.4 | 39.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 31.4 | 41.3 | 39.9 | 39.4 | 39.8 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:42 | 1 | 31.7 | 41.4 | 40 | 39.5 | 39.9 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 31.9 | 41.5 | 40.1 | 39.5 | 39.9 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 32.1 | 41.5 | 40.1 | 39.6 | 40 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 32.4 | 41.6 | 40.2 | 39.6 | 40.1 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 32.6 | 41.6 | 40.3 | 39.7 | 40.1 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 32.8 | 41.6 | 40.3 | 39.8 | 40.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:43 | 1 | 33.1 | 41.7 | 40.4 | 39.8 | 40.2 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 33.3 | 41.8 | 40.5 | 39.9 | 40.3 | 0.8 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 33.5 | 41.8 | 40.5 | 39.9 | 40.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 33.7 | 41.9 | 40.6 | 40 | 40.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 33.9 | 42 | 39.7 | 40 | 38.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 34.1 | 42 | 37.7 | 40.1 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:44 | 1 | 34.2 | 42 | 35.9 | 40.1 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.3 | 41.9 | 34.3 | 40.1 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.4 | 41.9 | 33.1 | 40.1 | 32 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.5 | 41.8 | 32.2 | 40 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.5 | 41.7 | 31.4 | 40 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.5 | 41.5 | 30.8 | 39.9 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:45 | 1 | 34.5 | 41.4 | 30.3 | 39.9 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.6 | 41.3 | 29.8 | 39.8 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.6 | 41.3 | 29.5 | 39.8 | 30.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.5 | 41.1 | 29.1 | 39.7 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.5 | 41 | 28.8 | 39.6 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.5 | 40.9 | 28.5 | 39.5 | 29.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:46 | 1 | 34.4 | 40.8 | 28.3 | 39.5 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 34.3 | 40.7 | 28.1 | 39.5 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 34.3 | 40.6 | 27.8 | 39.4 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 34.2 | 40.5 | 27.5 | 39.4 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 34.1 | 40.3 | 27.2 | 39.3 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 34 | 40.2 | 27 | 39.3 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:47 | 1 | 33.9 | 40.1 | 26.8 | 39.2 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.8 | 40 | 26.5 | 39.2 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.7 | 39.9 | 26.3 | 39.1 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.6 | 39.8 | 26.2 | 39.1 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.5 | 39.7 | 26 | 39 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.4 | 39.5 | 26 | 38.9 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:48 | 1 | 33.3 | 39.4 | 26.6 | 38.9 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 33.2 | 39.4 | 28 | 38.8 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 33.1 | 39.4 | 28.2 | 38.8 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 33 | 39.3 | 27.9 | 38.7 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 32.8 | 39.2 | 27.5 | 38.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 32.7 | 39.2 | 27.3 | 38.6 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:49 | 1 | 32.6 | 39.2 | 27 | 38.5 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32.6 | 39.1 | 26.8 | 38.5 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32.5 | 39 | 26.6 | 38.5 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32.3 | 39 | 26.3 | 38.4 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32.2 | 38.9 | 26.1 | 38.4 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32.1 | 38.9 | 25.8 | 38.3 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:50 | 1 | 32 | 38.8 | 25.6 | 38.2 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 32 | 38.7 | 25.4 | 38.2 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 31.9 | 38.6 | 25.2 | 38.1 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 31.8 | 38.6 | 24.9 | 38.1 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 31.7 | 38.5 | 24.8 | 38 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 31.6 | 38.4 | 24.6 | 38 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:51 | 1 | 31.5 | 38.3 | 24.3 | 37.9 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31.4 | 38.2 | 24.2 | 37.9 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31.3 | 38.1 | 24 | 37.8 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31.2 | 38 | 23.8 | 37.7 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31.1 | 37.8 | 23.5 | 37.7 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31.1 | 37.8 | 23.4 | 37.6 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:52 | 1 | 31 | 37.7 | 23.2 | 37.6 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.9 | 37.6 | 23 | 37.5 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.8 | 37.5 | 22.9 | 37.4 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.7 | 37.4 | 22.7 | 37.3 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.5 | 37.3 | 22.5 | 37.2 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.4 | 37.2 | 22.4 | 37.2 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:53 | 1 | 30.4 | 37.1 | 22.2 | 37.1 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 30.3 | 36.9 | 22.1 | 37 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 30.1 | 36.8 | 21.9 | 37 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 30 | 36.7 | 21.7 | 36.9 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 29.9 | 36.6 | 21.6 | 36.8 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 29.8 | 36.5 | 21.4 | 36.8 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:54 | 1 | 29.7 | 36.5 | 21.2 | 36.7 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:55 | 1 | 29.6 | 36.3 | 21.1 | 36.6 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:55 | 1 | 29.5 | 36.2 | 21 | 36.5 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:55 | 1 | 29.4 | 36.1 | 20.9 | 36.5 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:55 | 1 | 29.3 | 36 | 20.8 | 36.4 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 14:55 | 1 | 29.3 | 35.9 | 20.7 | 36.3 | 22.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:55 | 1 | 29.2 | 35.9 | 20.6 | 36.3 | 22.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:55 | 1 | 29 | 35.8 | 20.4 | 36.2 | 22.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.9 | 35.7 | 20.3 | 36.1 | 21.8 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.8 | 35.6 | 21.5 | 36 | 21.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.7 | 35.5 | 23.2 | 36 | 20.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.6 | 35.5 | 24.8 | 35.9 | 19.9 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.5 | 35.5 | 26.3 | 35.8 | 19.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:56 | 1 | 28.4 | 35.5 | 27.4 | 35.7 | 18.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 28.3 | 35.5 | 28.5 | 35.5 | 18 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 28.2 | 35.6 | 29.1 | 35.4 | 17.7 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 28.1 | 35.6 | 29.7 | 35.3 | 17.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 27.9 | 35.7 | 30.2 | 35.2 | 16.8 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 27.7 | 35.7 | 30.5 | 35.1 | 16.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 27.6 | 35.8 | 30.7 | 35 | 16.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 14:57 | 1 | 27.5 | 35.8 | 30.8 | 34.9 | 16.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 27.4 | 35.9 | 30.9 | 34.8 | 15.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 27.3 | 35.9 | 31 | 34.7 | 15.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 27 | 36 | 31.1 | 34.6 | 16.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 26.9 | 36.1 | 31.2 | 34.5 | 18.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 26.5 | 36.2 | 31.3 | 34.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:58 | 1 | 26.1 | 36.2 | 31.4 | 34.3 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 25.7 | 36.2 | 31.4 | 34.3 | 24 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 25.1 | 36.3 | 31.5 | 34.3 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 24.5 | 36.4 | 31.5 | 34.2 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 23.9 | 36.4 | 31.5 | 34.2 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 23.2 | 36.4 | 31.6 | 34.2 | 29 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 14:59 | 1 | 22.5 | 36.5 | 31.6 | 34.2 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:00 | 1 | 21.8 | 36.5 | 31.6 | 34.2 | 30.2 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:00 | 1 | 21 | 36.6 | 31.7 | 34.2 | 30.6 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:00 | 1 | 20.3 | 36.6 | 31.7 | 34.3 | 30.9 | 3.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:00 | 1 | 19.9 | 36.6 | 31.7 | 34.3 | 31 | 3.2 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 15:00 | 1 | 19.9 | 36.6 | 31.7 | 34.3 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:00 | 1 | 19.5 | 36.6 | 31.7 | 34.3 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:00 | 1 | 18.8 | 36.6 | 31.4 | 34.3 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:00 | 1 | 18.1 | 36.7 | 31.2 | 34.4 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:00 | 1 | 17.8 | 36.7 | 31.2 | 34.4 | 31.2 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:00 | 1 | 17.8 | 36.7 | 31.2 | 34.4 | 31.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 17.6 | 36.7 | 31.2 | 34.5 | 31.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 17 | 36.7 | 31.4 | 34.5 | 31.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 16.7 | 36.7 | 31.5 | 34.6 | 31.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 16.4 | 36.8 | 31.6 | 34.6 | 31.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 16.2 | 36.8 | 31.6 | 34.7 | 31.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:01 | 1 | 16.1 | 36.8 | 31.7 | 34.8 | 32 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16 | 36.8 | 31.7 | 34.9 | 32.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16 | 36.9 | 31.7 | 34.9 | 32.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16 | 36.9 | 31.8 | 35 | 32.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16.2 | 36.9 | 31.8 | 35 | 32.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16.4 | 36.9 | 31.8 | 35.1 | 32.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:02 | 1 | 16.6 | 36.9 | 31.8 | 35.2 | 32.3 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 16.9 | 36.9 | 31.9 | 35.2 | 32.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 17.2 | 36.9 | 31.9 | 35.3 | 32.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 17.4 | 37 | 32 | 35.3 | 32.5 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 17.6 | 37 | 32.1 | 35.4 | 32.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 18 | 37 | 32.3 | 35.4 | 32.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:03 | 1 | 18.3 | 37 | 32.4 | 35.5 | 32.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 18.6 | 37 | 32.6 | 35.5 | 32.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 19 | 37 | 32.8 | 35.6 | 32.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 19.3 | 37.1 | 33 | 35.6 | 33 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 19.7 | 37.1 | 33.2 | 35.7 | 33.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 20 | 37.1 | 33.4 | 35.7 | 33.4 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:04 | 1 | 20.3 | 37.1 | 33.6 | 35.8 | 33.6 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:05 | 1 | 20.7 | 37.2 | 33.8 | 35.8 | 33.8 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:05 | 1 | 21 | 37.2 | 33.9 | 35.9 | 33.9 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:05 | 1 | 21.4 | 37.2 | 34 | 35.9 | 34.1 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:05 | 1 | 21.8 | 37.3 | 34.2 | 36 | 34.2 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:05 | 1 | 22 | 37.3 | 34.2 | 36 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:05 | 1 | 22.2 | 37.3 | 34.3 | 36 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:05 | 1 | 22.5 | 37.4 | 33.9 | 36.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 22.8 | 37.4 | 32.7 | 36.1 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 23.2 | 37.4 | 32.3 | 36.1 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 23.5 | 37.4 | 32.6 | 36.2 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 23.7 | 37.4 | 33 | 36.2 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 23.8 | 37.4 | 33.3 | 36.2 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:06 | 1 | 23.9 | 37.4 | 33.7 | 36.3 | 33.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 23.9 | 37.5 | 33.9 | 36.3 | 34 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 23.7 | 37.5 | 34.2 | 36.3 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 23.4 | 37.5 | 34.3 | 36.3 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 23.1 | 37.6 | 34.5 | 36.4 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 22.6 | 37.6 | 34.7 | 36.4 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:07 | 1 | 22.2 | 37.6 | 34.8 | 36.4 | 35 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:08 | 1 | 21.6 | 37.7 | 34.9 | 36.5 | 35.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:08 | 1 | 21.1 | 37.7 | 35 | 36.5 | 35.4 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:08 | 1 | 20.5 | 37.8 | 35.1 | 36.6 | 35.5 | 3.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:08 | 1 | 19.9 | 37.8 | 35.2 | 36.6 | 35.7 | 3 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:08 | 1 | 19.9 | 37.8 | 35.2 | 36.6 | 35.7 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:08 | 1 | 19.9 | 37.8 | 35.2 | 36.6 | 35.7 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:08 | 1 | 19.3 | 37.8 | 35.3 | 36.6 | 35.9 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:08 | 1 | 18.7 | 37.9 | 35.4 | 36.7 | 36 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 18.2 | 37.9 | 35.5 | 36.7 | 36.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 18.1 | 37.9 | 35.5 | 36.7 | 36.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 17.7 | 38 | 35.6 | 36.8 | 36.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 17.3 | 38 | 35.7 | 36.8 | 36.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 16.9 | 38.1 | 35.9 | 36.9 | 36.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 16.7 | 38.1 | 36.2 | 36.9 | 36.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:09 | 1 | 16.5 | 38.2 | 36.5 | 37 | 36.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 16.4 | 38.3 | 36.8 | 37.1 | 37.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 16.4 | 38.3 | 37 | 37.1 | 37.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 16.4 | 38.4 | 37 | 37.2 | 37.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 16.5 | 38.4 | 37.1 | 37.2 | 37.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 16.7 | 38.5 | 37.2 | 37.3 | 37.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:10 | 1 | 17 | 38.6 | 37.2 | 37.4 | 37.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 17.2 | 38.6 | 37.2 | 37.5 | 37.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 17.5 | 38.7 | 37.3 | 37.6 | 38 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 17.8 | 38.7 | 37.4 | 37.6 | 38.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 18 | 38.8 | 37.5 | 37.7 | 38.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 18.4 | 38.8 | 37.6 | 37.7 | 38.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:11 | 1 | 18.7 | 38.9 | 37.8 | 37.8 | 38.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:12 | 1 | 19.1 | 39 | 37.9 | 37.8 | 38.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:12 | 1 | 19.5 | 39.1 | 38 | 37.9 | 38.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:12 | 1 | 19.5 | 39.1 | 38 | 38 | 38.6 | 4 | 1 | 1 | 1 | 0 | 0 | 1 | 0
2022-09-07 15:12 | 1 | 19.5 | 39.1 | 38 | 38 | 38.6 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:12 | 1 | 19.8 | 39.1 | 38.1 | 38 | 38.6 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:12 | 1 | 20.2 | 39.1 | 37.2 | 38 | 38.1 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:12 | 1 | 20.6 | 39.2 | 35.3 | 38.1 | 36.4 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:12 | 1 | 21 | 39.2 | 33.5 | 38.1 | 34.4 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 21.3 | 39.2 | 32.1 | 38.1 | 32.8 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 21.6 | 39.1 | 30.9 | 38.2 | 31.9 | 4.2 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 22 | 39.1 | 30.1 | 38.2 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 22 | 39 | 30 | 38.2 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 22.3 | 39 | 29.5 | 38.1 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 22.6 | 38.9 | 29.2 | 38.1 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:13 | 1 | 22.9 | 38.8 | 29.1 | 38.1 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 23.2 | 38.8 | 29.3 | 38.1 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 23.6 | 38.7 | 29.8 | 38.1 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 23.9 | 38.7 | 30.1 | 38.1 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 24.2 | 38.7 | 29.8 | 38 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 24.6 | 38.6 | 29.6 | 38 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:14 | 1 | 24.9 | 38.6 | 29.3 | 38 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 25.2 | 38.5 | 29 | 38 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 25.6 | 38.5 | 28.7 | 37.9 | 28.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 25.8 | 38.5 | 28.4 | 37.9 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 26.1 | 38.4 | 28.1 | 37.9 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 26.3 | 38.3 | 27.7 | 37.8 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:15 | 1 | 26.6 | 38.2 | 27.4 | 37.8 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 26.9 | 38.2 | 27.1 | 37.8 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 27.1 | 38.1 | 26.8 | 37.7 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 27.4 | 38 | 26.6 | 37.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 27.5 | 38 | 26.2 | 37.7 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 27.8 | 37.9 | 26 | 37.6 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:16 | 1 | 28 | 37.8 | 25.7 | 37.6 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.1 | 37.7 | 25.5 | 37.5 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.2 | 37.7 | 25.2 | 37.4 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.4 | 37.6 | 25 | 37.4 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.5 | 37.5 | 24.8 | 37.3 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.5 | 37.4 | 24.5 | 37.3 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:17 | 1 | 28.6 | 37.3 | 24.3 | 37.2 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.6 | 37.2 | 24.1 | 37.1 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.7 | 37.1 | 23.8 | 37.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.7 | 37 | 23.6 | 37 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.8 | 36.9 | 23.4 | 36.9 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.8 | 36.8 | 23.2 | 36.9 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:18 | 1 | 28.8 | 36.7 | 23 | 36.8 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.6 | 22.8 | 36.8 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.5 | 22.5 | 36.7 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.4 | 22.4 | 36.6 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.3 | 22.2 | 36.5 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.2 | 22 | 36.5 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:19 | 1 | 28.8 | 36.1 | 21.8 | 36.4 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:20 | 1 | 28.8 | 36 | 21.6 | 36.3 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:20 | 1 | 28.8 | 35.9 | 21.6 | 36.3 | 22.5 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:20 | 1 | 28.7 | 35.9 | 21.5 | 36.2 | 22.3 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:20 | 1 | 28.7 | 35.7 | 21 | 36.1 | 22.1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:20 | 1 | 28.7 | 35.6 | 21.2 | 36 | 21.5 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:20 | 1 | 28.6 | 35.6 | 22.5 | 36 | 20.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:20 | 1 | 28.5 | 35.5 | 24.1 | 35.8 | 19.8 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 28.5 | 35.5 | 25.7 | 35.7 | 19.1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 28.5 | 35.5 | 27 | 35.6 | 18.4 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 28.3 | 35.5 | 28 | 35.5 | 17.7 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 28.2 | 35.5 | 28.8 | 35.3 | 17.2 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 28.1 | 35.6 | 29.5 | 35.2 | 16.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:21 | 1 | 27.9 | 35.6 | 29.9 | 35.2 | 16 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:22 | 1 | 27.7 | 35.7 | 30.3 | 35 | 15.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:22 | 1 | 27.7 | 35.7 | 30.4 | 34.9 | 15.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:22 | 1 | 27.6 | 35.7 | 30.6 | 34.8 | 15.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:22 | 1 | 27.4 | 35.8 | 30.8 | 34.7 | 15 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:22 | 1 | 27.2 | 35.9 | 31 | 34.6 | 16.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:22 | 1 | 27 | 35.9 | 31.1 | 34.4 | 17.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:22 | 1 | 26.6 | 35.9 | 31.2 | 34.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 26.3 | 36 | 31.3 | 34.3 | 22 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 25.8 | 36 | 31.3 | 34.2 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 25.2 | 36.1 | 31.4 | 34.2 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 24.6 | 36.1 | 31.4 | 34.1 | 27 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 24 | 36.2 | 31.5 | 34.1 | 28 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:23 | 1 | 23.2 | 36.2 | 31.5 | 34.1 | 28.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:24 | 1 | 22.5 | 36.2 | 31.6 | 34.1 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:24 | 1 | 21.8 | 36.3 | 31.6 | 34.1 | 30.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:24 | 1 | 21 | 36.3 | 31.6 | 34.1 | 30.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:24 | 1 | 20.3 | 36.4 | 31.6 | 34.2 | 30.9 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:24 | 1 | 19.9 | 36.4 | 31.6 | 34.2 | 31 | 4 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 15:24 | 1 | 19.9 | 36.4 | 31.6 | 34.2 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:24 | 1 | 19.5 | 36.4 | 31.7 | 34.2 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:24 | 1 | 18.7 | 36.4 | 31.4 | 34.2 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:25 | 1 | 18 | 36.4 | 31 | 34.3 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:25 | 1 | 17.7 | 36.4 | 31 | 34.4 | 31.1 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 0
2022-09-07 15:25 | 1 | 17.7 | 36.4 | 31 | 34.4 | 31.1 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 17.7 | 36.4 | 31 | 34.4 | 31.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 17.4 | 36.5 | 31 | 34.4 | 31.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 16.9 | 36.5 | 31.2 | 34.4 | 31.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 16.4 | 36.5 | 31.3 | 34.5 | 31.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 16 | 36.5 | 31.5 | 34.5 | 31.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:25 | 1 | 15.7 | 36.5 | 31.6 | 34.6 | 31.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.6 | 36.6 | 31.6 | 34.7 | 32 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.5 | 36.6 | 31.6 | 34.7 | 32.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.5 | 36.6 | 31.7 | 34.8 | 32.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.5 | 36.6 | 31.7 | 34.8 | 32.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.7 | 36.7 | 31.8 | 34.9 | 32.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:26 | 1 | 15.8 | 36.7 | 31.8 | 35 | 32.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 16 | 36.7 | 31.8 | 35 | 32.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 16.3 | 36.7 | 31.8 | 35.1 | 32.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 16.6 | 36.7 | 31.9 | 35.2 | 32.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 16.8 | 36.7 | 31.9 | 35.2 | 32.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 17.2 | 36.7 | 32 | 35.3 | 32.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:27 | 1 | 17.5 | 36.8 | 32.1 | 35.3 | 32.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 17.8 | 36.8 | 32.2 | 35.4 | 32.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 18.1 | 36.8 | 32.4 | 35.4 | 32.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 18.4 | 36.8 | 32.5 | 35.5 | 33 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 18.7 | 36.8 | 32.7 | 35.5 | 33.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 19.1 | 36.8 | 32.9 | 35.6 | 33.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:28 | 1 | 19.4 | 36.9 | 33 | 35.6 | 33.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 19.7 | 36.9 | 33.3 | 35.7 | 33.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 20.1 | 36.9 | 33.4 | 35.7 | 33.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 20.4 | 36.9 | 33.6 | 35.8 | 33.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 20.8 | 37 | 33.8 | 35.8 | 34 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 21.1 | 37 | 33.8 | 35.8 | 34.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:29 | 1 | 21.4 | 37 | 34 | 35.9 | 34.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:30 | 1 | 21.8 | 37.1 | 34.1 | 35.9 | 34.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:30 | 1 | 22 | 37.1 | 34.2 | 36 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:30 | 1 | 22.1 | 37.1 | 34.2 | 36 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:30 | 1 | 22.5 | 37.2 | 34 | 36.1 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:30 | 1 | 22.8 | 37.2 | 32.7 | 36.1 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:30 | 1 | 23.1 | 37.2 | 32.2 | 36.1 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:30 | 1 | 23.3 | 37.2 | 32.5 | 36.2 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.6 | 37.2 | 32.9 | 36.2 | 32.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.7 | 37.2 | 33.2 | 36.2 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.7 | 37.2 | 33.6 | 36.2 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.7 | 37.3 | 33.9 | 36.3 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.4 | 37.3 | 34.1 | 36.3 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:31 | 1 | 23.2 | 37.3 | 34.3 | 36.3 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 22.8 | 37.4 | 34.4 | 36.4 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 22.4 | 37.4 | 34.6 | 36.4 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 21.8 | 37.4 | 34.7 | 36.4 | 35 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 21.3 | 37.5 | 34.9 | 36.5 | 35.1 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 20.8 | 37.5 | 34.9 | 36.5 | 35.3 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 20.1 | 37.6 | 35 | 36.5 | 35.5 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:32 | 1 | 19.9 | 37.6 | 35.1 | 36.6 | 35.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:32 | 1 | 19.9 | 37.6 | 35.1 | 36.6 | 35.5 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 19.5 | 37.6 | 35.1 | 36.6 | 35.6 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 18.9 | 37.7 | 35.2 | 36.6 | 35.8 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 18.2 | 37.7 | 35.3 | 36.7 | 35.9 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 18 | 37.7 | 35.4 | 36.7 | 36 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 17.7 | 37.7 | 35.4 | 36.7 | 36 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 17.3 | 37.8 | 35.5 | 36.7 | 36.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:33 | 1 | 16.8 | 37.8 | 35.7 | 36.8 | 36.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16.4 | 37.9 | 36 | 36.8 | 36.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16.2 | 37.9 | 36.2 | 36.9 | 36.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16 | 38 | 36.5 | 37 | 36.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16 | 38 | 36.6 | 37 | 37 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16 | 38.1 | 36.7 | 37.1 | 37.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:34 | 1 | 16 | 38.2 | 36.8 | 37.1 | 37.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 16.1 | 38.2 | 36.9 | 37.2 | 37.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 16.3 | 38.3 | 36.9 | 37.3 | 37.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 16.5 | 38.3 | 37 | 37.3 | 37.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 16.8 | 38.4 | 37 | 37.4 | 37.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 17.1 | 38.5 | 37.1 | 37.5 | 38 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:35 | 1 | 17.4 | 38.5 | 37.1 | 37.5 | 38.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 17.7 | 38.6 | 37.3 | 37.6 | 38.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 17.9 | 38.6 | 37.4 | 37.6 | 38.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 18.3 | 38.7 | 37.5 | 37.8 | 38.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 18.6 | 38.7 | 37.7 | 37.8 | 38.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 19 | 38.8 | 37.8 | 37.8 | 38.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:36 | 1 | 19.3 | 38.9 | 37.9 | 37.9 | 38.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 19.6 | 39 | 38 | 37.9 | 38.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 20.1 | 39 | 38.2 | 38 | 38.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 20.4 | 39.1 | 38.3 | 38.1 | 38.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 20.8 | 39.1 | 38.4 | 38.2 | 39 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 21.1 | 39.2 | 38.5 | 38.3 | 39 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:37 | 1 | 21.4 | 39.3 | 38.6 | 38.3 | 39.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:38 | 1 | 21.8 | 39.3 | 38.7 | 38.4 | 39.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:38 | 1 | 22 | 39.3 | 38.8 | 38.4 | 39.2 | 4.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:38 | 1 | 22.1 | 39.3 | 38.8 | 38.4 | 39.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:38 | 1 | 22.4 | 39.4 | 38.6 | 38.5 | 39.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:38 | 1 | 22.8 | 39.4 | 37 | 38.5 | 38 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:38 | 1 | 23.2 | 39.5 | 35.1 | 38.6 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:38 | 1 | 23.4 | 39.5 | 33.4 | 38.6 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 23.8 | 39.4 | 32.3 | 38.6 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 24 | 39.4 | 31.4 | 38.6 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 24.4 | 39.3 | 30.6 | 38.6 | 31.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 24.7 | 39.2 | 29.9 | 38.6 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 25 | 39.2 | 29.4 | 38.6 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:39 | 1 | 25.3 | 39.2 | 29 | 38.6 | 30.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 25.6 | 39.1 | 28.6 | 38.6 | 30.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 25.9 | 39 | 28.4 | 38.5 | 30.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 26.2 | 38.9 | 28.1 | 38.5 | 29.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 26.4 | 38.8 | 27.8 | 38.5 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 26.7 | 38.7 | 27.5 | 38.4 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:40 | 1 | 26.9 | 38.6 | 27.3 | 38.4 | 29.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 27.1 | 38.5 | 27 | 38.4 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 27.4 | 38.4 | 26.9 | 38.3 | 28.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 27.6 | 38.3 | 26.6 | 38.3 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 27.8 | 38.2 | 26.3 | 38.2 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 28 | 38.1 | 26.1 | 38.2 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:41 | 1 | 28.1 | 38 | 25.8 | 38.1 | 27.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.2 | 37.9 | 25.6 | 38.1 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.4 | 37.8 | 25.4 | 38 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.5 | 37.7 | 25.2 | 38 | 27.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.5 | 37.6 | 25 | 37.9 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.6 | 37.5 | 24.8 | 37.9 | 26.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:42 | 1 | 28.7 | 37.4 | 24.7 | 37.8 | 26.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.8 | 37.3 | 24.5 | 37.7 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.8 | 37.2 | 24.3 | 37.7 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.8 | 37.1 | 24.1 | 37.6 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.9 | 37 | 23.9 | 37.6 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.9 | 36.9 | 23.7 | 37.5 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:43 | 1 | 28.9 | 36.8 | 23.5 | 37.4 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.7 | 23.3 | 37.4 | 25.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.6 | 23.1 | 37.3 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.5 | 25.5 | 37.2 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.5 | 26.2 | 37.1 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.4 | 25.7 | 37.1 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:44 | 1 | 29 | 36.4 | 25.3 | 37 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 29 | 36.4 | 25 | 37 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 28.9 | 36.4 | 24.7 | 36.9 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 28.9 | 36.3 | 24.5 | 36.8 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 28.9 | 36.3 | 24.3 | 36.7 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 28.9 | 36.3 | 24.2 | 36.7 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:45 | 1 | 28.9 | 36.3 | 24 | 36.6 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.9 | 36.2 | 23.9 | 36.6 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.8 | 36.2 | 23.7 | 36.5 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.8 | 36.2 | 23.6 | 36.5 | 23.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.8 | 36.2 | 23.3 | 36.4 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.8 | 36.1 | 23 | 36.3 | 23 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:46 | 1 | 28.7 | 36 | 22.8 | 36.2 | 22.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:47 | 1 | 28.7 | 36 | 22.6 | 36.1 | 22.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 15:47 | 1 | 28.7 | 35.9 | 22.5 | 36.1 | 22.7 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:47 | 1 | 28.7 | 35.9 | 22.3 | 36.1 | 22.6 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:47 | 1 | 28.6 | 35.8 | 21.9 | 36 | 22.3 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:47 | 1 | 28.5 | 35.8 | 22.1 | 35.9 | 21.7 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:47 | 1 | 28.5 | 35.7 | 23.5 | 35.8 | 20.8 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:47 | 1 | 28.5 | 35.6 | 25.1 | 35.8 | 19.9 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 28.4 | 35.6 | 26.5 | 35.6 | 19.1 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 28.3 | 35.6 | 27.7 | 35.5 | 18.3 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 28.2 | 35.6 | 28.6 | 35.5 | 17.7 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 28 | 35.7 | 29.3 | 35.4 | 17 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 27.9 | 35.7 | 29.8 | 35.2 | 16.4 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:48 | 1 | 27.8 | 35.8 | 30.2 | 35.1 | 15.8 | 4.3 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 15:49 | 1 | 27.7 | 35.8 | 30.4 | 34.9 | 15.5 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 27.6 | 35.8 | 30.5 | 34.9 | 15.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 27.4 | 35.9 | 30.8 | 34.8 | 14.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 27.2 | 35.9 | 31 | 34.6 | 15.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 27 | 36 | 31.1 | 34.5 | 16.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 26.7 | 36 | 31.2 | 34.4 | 18.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:49 | 1 | 26.3 | 36.1 | 31.3 | 34.3 | 20.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 25.9 | 36.1 | 31.3 | 34.2 | 22.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 25.4 | 36.2 | 31.4 | 34.2 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 24.8 | 36.2 | 31.4 | 34.2 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 24.1 | 36.2 | 31.5 | 34.1 | 27.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 23.4 | 36.3 | 31.5 | 34.1 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:50 | 1 | 22.7 | 36.3 | 31.5 | 34.1 | 29.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:51 | 1 | 22 | 36.4 | 31.6 | 34.1 | 29.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:51 | 1 | 21.2 | 36.4 | 31.6 | 34.2 | 30.4 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:51 | 1 | 20.4 | 36.4 | 31.6 | 34.2 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:51 | 1 | 19.9 | 36.4 | 31.6 | 34.2 | 30.9 | 4 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 15:51 | 1 | 19.9 | 36.4 | 31.6 | 34.2 | 30.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:51 | 1 | 19.7 | 36.4 | 31.7 | 34.2 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:51 | 1 | 18.9 | 36.5 | 31.4 | 34.3 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:51 | 1 | 18.1 | 36.5 | 30.9 | 34.3 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 15:52 | 1 | 17.7 | 36.5 | 30.7 | 34.4 | 31 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 17.7 | 36.5 | 30.7 | 34.4 | 31 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 17.6 | 36.5 | 30.7 | 34.4 | 31 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 17 | 36.5 | 30.8 | 34.4 | 31 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 16.5 | 36.5 | 31 | 34.5 | 31.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 16 | 36.6 | 31.1 | 34.5 | 31.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 15.8 | 36.6 | 31.3 | 34.6 | 31.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:52 | 1 | 15.7 | 36.6 | 31.4 | 34.7 | 31.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.5 | 36.6 | 31.5 | 34.7 | 31.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.5 | 36.6 | 31.5 | 34.7 | 31.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.5 | 36.6 | 31.6 | 34.8 | 31.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.6 | 36.7 | 31.6 | 34.9 | 32 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.7 | 36.7 | 31.7 | 35 | 32 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:53 | 1 | 15.9 | 36.7 | 31.7 | 35 | 32.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 16.2 | 36.7 | 31.7 | 35 | 32.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 16.4 | 36.7 | 31.8 | 35.1 | 32.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 16.7 | 36.7 | 31.8 | 35.2 | 32.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 17 | 36.8 | 31.8 | 35.2 | 32.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 17.4 | 36.8 | 31.8 | 35.2 | 32.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:54 | 1 | 17.7 | 36.8 | 31.8 | 35.3 | 32.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 17.8 | 36.8 | 31.9 | 35.3 | 32.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 18.2 | 36.8 | 31.9 | 35.4 | 32.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 18.4 | 36.8 | 32 | 35.4 | 32.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 18.8 | 36.9 | 32.2 | 35.5 | 32.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 19.1 | 36.9 | 32.3 | 35.5 | 32.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:55 | 1 | 19.4 | 36.9 | 32.6 | 35.6 | 32.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 19.8 | 36.9 | 32.7 | 35.6 | 32.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 20.1 | 37 | 33 | 35.7 | 33.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 20.4 | 37 | 33.2 | 35.7 | 33.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 20.7 | 37 | 33.4 | 35.8 | 33.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 21 | 37 | 33.7 | 35.8 | 33.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:56 | 1 | 21.3 | 37.1 | 33.8 | 35.9 | 33.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:57 | 1 | 21.7 | 37.1 | 34 | 35.9 | 34 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:57 | 1 | 22 | 37.1 | 34.1 | 35.9 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:57 | 1 | 22 | 37.2 | 34.1 | 35.9 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:57 | 1 | 22.3 | 37.2 | 34.1 | 36 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:57 | 1 | 22.7 | 37.2 | 33.6 | 36 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:57 | 1 | 23 | 37.3 | 33.5 | 36.1 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:57 | 1 | 23.2 | 37.3 | 33.5 | 36.1 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 23.4 | 37.3 | 33.7 | 36.1 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 23.5 | 37.3 | 33.9 | 36.2 | 32.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 23.5 | 37.3 | 34.1 | 36.2 | 33 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 23.4 | 37.4 | 34.3 | 36.2 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 23.2 | 37.4 | 34.4 | 36.2 | 33.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:58 | 1 | 22.9 | 37.4 | 34.5 | 36.3 | 33.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 22.6 | 37.5 | 34.6 | 36.3 | 34 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 22.1 | 37.5 | 34.7 | 36.3 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 21.6 | 37.6 | 34.9 | 36.4 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 21 | 37.6 | 35 | 36.4 | 34.7 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 20.5 | 37.6 | 35.1 | 36.4 | 34.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 15:59 | 1 | 19.9 | 37.7 | 35.2 | 36.5 | 35.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 15:59 | 1 | 19.9 | 37.7 | 35.2 | 36.5 | 35.1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 15:59 | 1 | 19.9 | 37.7 | 35.2 | 36.5 | 35.1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 19.3 | 37.7 | 35.3 | 36.5 | 35.2 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 18.7 | 37.8 | 35.4 | 36.5 | 35.4 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 18.1 | 37.8 | 35.4 | 36.6 | 35.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 18.1 | 37.8 | 35.5 | 36.6 | 35.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 17.6 | 37.8 | 35.5 | 36.6 | 35.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 17.1 | 37.9 | 35.7 | 36.6 | 35.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:00 | 1 | 16.7 | 37.9 | 35.9 | 36.7 | 36.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.5 | 38 | 36.2 | 36.7 | 36.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.3 | 38.1 | 36.5 | 36.8 | 36.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.2 | 38.1 | 36.7 | 36.9 | 36.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.1 | 38.2 | 36.8 | 37 | 37 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.1 | 38.2 | 36.8 | 37 | 37.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:01 | 1 | 16.2 | 38.3 | 36.8 | 37.1 | 37.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:02 | 1 | 16.4 | 38.4 | 36.9 | 37.1 | 37.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:02 | 2 | 17 | 38.5 | 37 | 37.3 | 37.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:02 | 1 | 17.3 | 38.5 | 37.1 | 37.3 | 37.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:02 | 1 | 17.6 | 38.6 | 37.2 | 37.4 | 37.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 17.9 | 38.6 | 37.4 | 37.4 | 38 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 18.1 | 38.7 | 37.5 | 37.5 | 38.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 18.5 | 38.8 | 37.6 | 37.6 | 38.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 18.9 | 38.8 | 37.7 | 37.6 | 38.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 19.2 | 38.8 | 37.9 | 37.7 | 38.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:03 | 1 | 19.6 | 38.9 | 38 | 37.7 | 38.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 19.9 | 39 | 38.1 | 37.8 | 38.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 20.3 | 39.1 | 38.2 | 37.8 | 38.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 20.7 | 39.1 | 38.3 | 37.9 | 38.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 21 | 39.2 | 38.4 | 38 | 38.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 21.4 | 39.2 | 38.5 | 38.1 | 38.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:04 | 1 | 21.7 | 39.3 | 38.6 | 38.1 | 39 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 22.1 | 39.3 | 38.7 | 38.2 | 39 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 22.4 | 39.4 | 38.8 | 38.2 | 39.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 22.8 | 39.4 | 38.9 | 38.3 | 39.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 23.1 | 39.5 | 39 | 38.4 | 39.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 23.4 | 39.5 | 39.1 | 38.4 | 39.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:05 | 1 | 23.8 | 39.6 | 39.2 | 38.5 | 39.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 24.1 | 39.6 | 39.3 | 38.6 | 39.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 24.4 | 39.7 | 39.3 | 38.6 | 39.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 24.7 | 39.8 | 39.3 | 38.7 | 39.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 25 | 39.9 | 39.4 | 38.8 | 39.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 25.3 | 39.9 | 39.5 | 38.8 | 39.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:06 | 1 | 25.6 | 40 | 39.6 | 38.9 | 39.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 25.9 | 40 | 39.6 | 39 | 39.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 26.1 | 40.1 | 39.7 | 39 | 39.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 26.4 | 40.1 | 39.8 | 39.1 | 39.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 26.7 | 40.2 | 39.9 | 39.2 | 40 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 27 | 40.2 | 39.9 | 39.3 | 40 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:07 | 1 | 27.2 | 40.3 | 40 | 39.2 | 40.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 27.5 | 40.4 | 40.1 | 39.3 | 40.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 27.7 | 40.4 | 40.1 | 39.4 | 40.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 28 | 40.5 | 40.2 | 39.4 | 40.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 28.2 | 40.5 | 40.3 | 39.5 | 40.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 28.5 | 40.6 | 40.3 | 39.6 | 40.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:08 | 1 | 28.7 | 40.7 | 40.4 | 39.6 | 40.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 28.9 | 40.8 | 40.5 | 39.7 | 40.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 29.2 | 40.8 | 40.5 | 39.8 | 40.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 29.4 | 40.8 | 40.6 | 39.8 | 40.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 29.7 | 40.9 | 40.6 | 39.9 | 40.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 30 | 40.9 | 40.7 | 40 | 40.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:09 | 1 | 30.2 | 41 | 40.8 | 40 | 40.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:10 | 1 | 30.5 | 41.1 | 40.8 | 40.1 | 40.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:10 | 1 | 30.7 | 41.1 | 40.9 | 40.1 | 40.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:10 | 1 | 31 | 41.2 | 41 | 40.2 | 40.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 16:10 | 1 | 31.3 | 41.3 | 41.1 | 40.3 | 40.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:44 | 1 | 80.2 | 89 | 90.2 | 85.9 | 86.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:44 | 1 | 80.3 | 89 | 90.2 | 85.9 | 86.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:44 | 1 | 80.3 | 89 | 90.2 | 86 | 86.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:44 | 1 | 80.3 | 89 | 90.2 | 86 | 86.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.4 | 89 | 90.1 | 86 | 86.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.5 | 89 | 90.1 | 86.1 | 86.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.5 | 89 | 90.1 | 86.1 | 87 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.5 | 89 | 90.1 | 86.1 | 87 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.6 | 89 | 90.1 | 86.2 | 87 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:45 | 1 | 80.6 | 89 | 90.1 | 86.2 | 87 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.6 | 89 | 90.1 | 86.2 | 87 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.7 | 89 | 90.1 | 86.2 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.7 | 89 | 90.1 | 86.3 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.7 | 89 | 90.1 | 86.3 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.8 | 89 | 90.1 | 86.3 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:46 | 1 | 80.8 | 89 | 90.2 | 86.3 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 80.8 | 89 | 90.2 | 86.3 | 87.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 80.9 | 89 | 90.2 | 86.4 | 87.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 80.9 | 89 | 90.2 | 86.4 | 87.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 81 | 89 | 90.3 | 86.5 | 87.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 81 | 89 | 90.4 | 86.5 | 87.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:47 | 1 | 81 | 89 | 90.4 | 86.5 | 87.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81 | 89 | 90.5 | 86.6 | 87.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81.1 | 89.1 | 90.6 | 86.6 | 87.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81.1 | 89.1 | 90.8 | 86.6 | 87.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81.2 | 89.1 | 90.9 | 86.7 | 87.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81.2 | 89.2 | 91 | 86.7 | 87.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:48 | 1 | 81.2 | 89.3 | 91.2 | 86.7 | 87.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.3 | 89.3 | 91.3 | 86.8 | 87.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.3 | 89.4 | 91.4 | 86.8 | 87.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.3 | 89.4 | 91.5 | 86.8 | 87.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.4 | 89.5 | 91.6 | 86.9 | 87.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.4 | 89.5 | 91.7 | 86.9 | 87.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:49 | 1 | 81.4 | 89.6 | 91.8 | 86.9 | 88 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.5 | 89.7 | 92 | 87 | 88 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.5 | 89.7 | 92.1 | 87 | 88 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.6 | 89.8 | 92.1 | 87 | 88.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.6 | 89.8 | 92.2 | 87.1 | 88.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.6 | 89.9 | 92.3 | 87.2 | 88.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:50 | 1 | 81.7 | 89.9 | 92.3 | 87.2 | 88.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.7 | 90 | 92.3 | 87.2 | 88.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.8 | 90 | 92.4 | 87.3 | 88.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.8 | 90.1 | 92.4 | 87.4 | 88.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.9 | 90.1 | 92.5 | 87.4 | 88.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.9 | 90.2 | 92.5 | 87.4 | 88.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:51 | 1 | 81.9 | 90.2 | 92.5 | 87.5 | 88.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82 | 90.2 | 92.6 | 87.6 | 88.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82 | 90.3 | 92.6 | 87.6 | 88.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82.1 | 90.3 | 92.6 | 87.6 | 88.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82.1 | 90.3 | 92.5 | 87.7 | 88.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82.2 | 90.3 | 92.5 | 87.8 | 88.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:52 | 1 | 82.2 | 90.4 | 92.5 | 87.8 | 88.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.3 | 90.4 | 92.5 | 87.9 | 88.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.3 | 90.4 | 92.4 | 87.9 | 89 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.3 | 90.4 | 92.4 | 87.9 | 89 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.4 | 90.4 | 92.4 | 88 | 89 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.4 | 90.4 | 92.4 | 88 | 89.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:53 | 1 | 82.5 | 90.4 | 92.3 | 88.1 | 89.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.5 | 90.5 | 92.3 | 88.1 | 89.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.6 | 90.5 | 92.2 | 88.1 | 89.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.6 | 90.5 | 92.2 | 88.2 | 89.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.7 | 90.5 | 92.2 | 88.2 | 89.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.7 | 90.5 | 92.1 | 88.3 | 89.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:54 | 1 | 82.7 | 90.5 | 92.1 | 88.3 | 89.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 82.8 | 90.5 | 92 | 88.3 | 89.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 82.8 | 90.5 | 92 | 88.4 | 89.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 82.8 | 90.5 | 92 | 88.4 | 89.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 82.9 | 90.5 | 92 | 88.4 | 89.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 82.9 | 90.5 | 92 | 88.4 | 89.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:55 | 1 | 83 | 90.5 | 92 | 88.5 | 89.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83 | 90.5 | 92 | 88.5 | 89.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83.1 | 90.5 | 92 | 88.5 | 89.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83.1 | 90.5 | 92 | 88.5 | 89.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83.1 | 90.5 | 92 | 88.6 | 89.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83.2 | 90.5 | 92 | 88.6 | 89.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:56 | 1 | 83.2 | 90.5 | 92 | 88.6 | 89.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.2 | 90.5 | 92 | 88.6 | 89.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.3 | 90.5 | 92 | 88.6 | 89.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.3 | 90.5 | 92 | 88.6 | 89.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.4 | 90.5 | 92.1 | 88.6 | 89.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.4 | 90.5 | 92.1 | 88.7 | 89.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:57 | 1 | 83.4 | 90.5 | 92.1 | 88.7 | 89.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.5 | 90.5 | 92.1 | 88.7 | 89.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.5 | 90.5 | 92.2 | 88.7 | 89.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.5 | 90.5 | 92.2 | 88.7 | 89.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.6 | 90.5 | 92.3 | 88.7 | 89.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.6 | 90.5 | 92.4 | 88.7 | 89.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:58 | 1 | 83.7 | 90.6 | 92.5 | 88.7 | 89.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.8 | 90.6 | 92.6 | 88.7 | 89.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.8 | 90.6 | 92.8 | 88.7 | 89.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.8 | 90.7 | 92.9 | 88.8 | 89.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.9 | 90.8 | 93 | 88.8 | 90 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.9 | 90.8 | 93.1 | 88.8 | 90 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 17:59 | 1 | 83.9 | 90.8 | 93.3 | 88.9 | 90 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84 | 90.9 | 93.4 | 88.9 | 90.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84 | 90.9 | 93.4 | 88.9 | 90.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84.1 | 91 | 93.5 | 89 | 90.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84.1 | 91.1 | 93.6 | 89 | 90.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84.2 | 91.1 | 93.7 | 89 | 90.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:00 | 1 | 84.2 | 91.1 | 93.7 | 89.1 | 90.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.2 | 91.2 | 93.8 | 89.1 | 90.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.3 | 91.2 | 93.8 | 89.2 | 90.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.3 | 91.3 | 93.8 | 89.2 | 90.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.3 | 91.3 | 93.9 | 89.3 | 90.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.4 | 91.4 | 93.9 | 89.3 | 90.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:01 | 1 | 84.4 | 91.4 | 93.9 | 89.3 | 90.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.5 | 91.4 | 93.9 | 89.4 | 90.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.5 | 91.5 | 94 | 89.4 | 90.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.5 | 91.5 | 94 | 89.5 | 90.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.6 | 91.5 | 94 | 89.5 | 90.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.6 | 91.5 | 94 | 89.5 | 90.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:02 | 1 | 84.7 | 91.6 | 94 | 89.6 | 90.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.7 | 91.6 | 94 | 89.6 | 90.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.7 | 91.6 | 94 | 89.6 | 90.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.8 | 91.6 | 94 | 89.7 | 90.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.8 | 91.6 | 94 | 89.7 | 90.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.9 | 91.6 | 93.9 | 89.7 | 90.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:03 | 1 | 84.9 | 91.6 | 93.9 | 89.8 | 90.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 84.9 | 91.6 | 93.9 | 89.8 | 90.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 85 | 91.6 | 93.8 | 89.8 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 85 | 91.6 | 93.8 | 89.9 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 85 | 91.6 | 93.8 | 89.9 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 85.1 | 91.6 | 93.7 | 89.9 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:04 | 1 | 85.1 | 91.6 | 93.7 | 89.9 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.2 | 91.6 | 93.7 | 89.9 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.2 | 91.6 | 93.6 | 90 | 90.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.2 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.2 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.3 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:05 | 1 | 85.3 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.3 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.4 | 91.6 | 93.6 | 90 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.4 | 91.6 | 93.6 | 90.1 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.5 | 91.6 | 93.6 | 90.1 | 91 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.5 | 91.6 | 93.6 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:06 | 1 | 85.5 | 91.6 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.5 | 91.6 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.6 | 91.6 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.6 | 91.5 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.6 | 91.5 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.7 | 91.5 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:07 | 1 | 85.7 | 91.5 | 93.5 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.7 | 91.5 | 93.4 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.8 | 91.5 | 93.4 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.8 | 91.5 | 93.4 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.8 | 91.4 | 93.4 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.9 | 91.4 | 93.3 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:08 | 1 | 85.9 | 91.4 | 93.3 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 85.9 | 91.4 | 93.3 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 86 | 91.4 | 93.3 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 86 | 91.4 | 93.4 | 90.1 | 91.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 86 | 91.4 | 93.4 | 90.1 | 91.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 86 | 91.4 | 93.5 | 90.2 | 91.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:09 | 1 | 86.1 | 91.4 | 93.6 | 90.2 | 91.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.1 | 91.4 | 93.7 | 90.2 | 91.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.1 | 91.5 | 93.7 | 90.2 | 91.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.2 | 91.5 | 93.8 | 90.2 | 91.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.2 | 91.5 | 93.8 | 90.3 | 91.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.2 | 91.5 | 93.9 | 90.3 | 91.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:10 | 1 | 86.3 | 91.5 | 93.9 | 90.3 | 91.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.3 | 91.5 | 94 | 90.3 | 91.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.3 | 91.6 | 94 | 90.4 | 91.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.3 | 91.6 | 94.1 | 90.4 | 91.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.4 | 91.6 | 94.1 | 90.4 | 91.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.4 | 91.6 | 94.1 | 90.5 | 91.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:11 | 1 | 86.4 | 91.7 | 94.2 | 90.5 | 91.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.5 | 91.7 | 94.2 | 90.5 | 91.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.5 | 91.7 | 94.2 | 90.5 | 91.5 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.5 | 91.7 | 94.2 | 90.6 | 91.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.6 | 91.7 | 94.2 | 90.6 | 91.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.6 | 91.8 | 94.2 | 90.6 | 91.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:12 | 1 | 86.6 | 91.8 | 94.1 | 90.6 | 91.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.6 | 91.8 | 94.1 | 90.6 | 91.6 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.7 | 91.8 | 94.1 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.7 | 91.8 | 94.1 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.7 | 91.8 | 94 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.8 | 91.8 | 94 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:13 | 1 | 86.8 | 91.8 | 94 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 86.8 | 91.8 | 93.9 | 90.7 | 91.7 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 86.8 | 91.8 | 93.9 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 86.9 | 91.8 | 93.8 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 86.9 | 91.8 | 93.8 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 86.9 | 91.8 | 93.8 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:14 | 1 | 87 | 91.8 | 93.7 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87 | 91.8 | 93.6 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87 | 91.8 | 93.6 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87 | 91.8 | 93.6 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87.1 | 91.8 | 93.5 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87.1 | 91.7 | 93.5 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:15 | 1 | 87.1 | 91.7 | 93.5 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.1 | 91.7 | 93.4 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.2 | 91.7 | 93.4 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.2 | 91.7 | 93.4 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.2 | 91.7 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.3 | 91.7 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:16 | 1 | 87.3 | 91.6 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.3 | 91.6 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.3 | 91.6 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.4 | 91.6 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.4 | 91.6 | 93.3 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.4 | 91.6 | 93.2 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:17 | 1 | 87.4 | 91.6 | 93.2 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.5 | 91.6 | 93.2 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.5 | 91.5 | 93.2 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.5 | 91.5 | 93.2 | 90.8 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.5 | 91.5 | 93.2 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.6 | 91.5 | 93.2 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:18 | 1 | 87.6 | 91.5 | 93.2 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.6 | 91.5 | 93.2 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.6 | 91.5 | 93.2 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.6 | 91.5 | 93.3 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.7 | 91.5 | 93.3 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.7 | 91.5 | 93.3 | 90.7 | 91.8 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:19 | 1 | 87.7 | 91.5 | 93.4 | 90.7 | 91.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.7 | 91.5 | 93.4 | 90.7 | 91.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.8 | 91.5 | 93.5 | 90.7 | 91.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.8 | 91.5 | 93.6 | 90.8 | 91.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.8 | 91.5 | 93.7 | 90.8 | 91.9 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.8 | 91.5 | 93.7 | 90.8 | 92 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:20 | 1 | 87.9 | 91.5 | 93.8 | 90.8 | 92 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 87.9 | 91.6 | 93.9 | 90.8 | 92 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 87.9 | 91.6 | 94 | 90.9 | 92.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 87.9 | 91.6 | 94 | 90.9 | 92.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 87.9 | 91.6 | 94 | 90.9 | 92.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 88 | 91.7 | 94.1 | 90.9 | 92.1 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:21 | 1 | 88 | 91.7 | 94.1 | 90.9 | 92.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88 | 91.7 | 94.2 | 91 | 92.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88 | 91.8 | 94.2 | 91 | 92.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88.1 | 91.8 | 94.2 | 91 | 92.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88.1 | 91.8 | 94.2 | 91 | 92.2 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88.1 | 91.8 | 94.2 | 91 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:22 | 1 | 88.1 | 91.8 | 94.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.1 | 91.9 | 94.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.2 | 91.9 | 94.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.2 | 91.9 | 94.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.2 | 91.9 | 94.2 | 91.2 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.2 | 91.9 | 94.2 | 91.2 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:23 | 1 | 88.3 | 91.9 | 94.1 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.3 | 91.9 | 94.1 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.3 | 91.9 | 94.1 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.3 | 91.9 | 94.1 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.3 | 91.9 | 94 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.4 | 91.9 | 94 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:24 | 1 | 88.4 | 91.9 | 93.9 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.4 | 91.9 | 93.9 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.4 | 91.9 | 93.9 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.4 | 91.9 | 93.8 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.8 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.8 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.8 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.7 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.7 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:25 | 1 | 88.5 | 91.9 | 93.7 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.5 | 91.9 | 93.7 | 91.3 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.5 | 91.9 | 93.7 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.5 | 91.9 | 93.6 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.6 | 91.9 | 93.6 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.6 | 91.8 | 93.6 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.6 | 91.8 | 93.5 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:26 | 1 | 88.6 | 91.8 | 93.5 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.6 | 91.8 | 93.5 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.7 | 91.8 | 93.4 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.7 | 91.8 | 93.4 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.7 | 91.8 | 93.4 | 91.2 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.7 | 91.8 | 93.3 | 91.1 | 92.4 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:27 | 1 | 88.8 | 91.7 | 93.3 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.8 | 91.7 | 93.3 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.8 | 91.7 | 93.3 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.8 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.8 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.8 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:28 | 1 | 88.9 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 88.9 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 88.9 | 91.7 | 93.2 | 91.1 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 88.9 | 91.7 | 93.2 | 91 | 92.3 | 4 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 88.9 | 91.7 | 93.2 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 89 | 91.7 | 93.2 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:29 | 1 | 89 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89.1 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89.1 | 91.7 | 93.1 | 91 | 92.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 18:30 | 1 | 89.1 | 91.7 | 93.1 | 91 | 92.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:30 | 1 | 89.1 | 91.7 | 93.1 | 91 | 92.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 89.1 | 91.7 | 93 | 91 | 91.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 89.1 | 91.7 | 92.3 | 91 | 90 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 89.1 | 91.7 | 89.9 | 91 | 88.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 89 | 91.7 | 87 | 91 | 86.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 88.8 | 91.6 | 84.5 | 90.9 | 84.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:31 | 1 | 88.6 | 91.5 | 82.2 | 90.9 | 82.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 88.3 | 91.4 | 80.4 | 90.7 | 81.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 88 | 91.2 | 78.7 | 90.6 | 80.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 87.7 | 91.1 | 77.4 | 90.5 | 79.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 87.3 | 90.8 | 76.2 | 90.4 | 78.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 87 | 90.7 | 75.3 | 90.2 | 77.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:32 | 1 | 86.5 | 90.5 | 74.3 | 90 | 76.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 86.1 | 90.2 | 73.6 | 89.9 | 76.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 85.7 | 90 | 72.8 | 89.7 | 75.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 85.2 | 89.7 | 72.1 | 89.5 | 74.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 84.8 | 89.5 | 71.6 | 89.3 | 74.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 84.3 | 89.3 | 71 | 89.1 | 73.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:33 | 1 | 83.8 | 89 | 70.4 | 88.9 | 73.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 83.3 | 88.7 | 69.9 | 88.7 | 72.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 82.8 | 88.5 | 69.3 | 88.4 | 72.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 82.4 | 88.2 | 68.9 | 88.2 | 71.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 81.9 | 88 | 68.3 | 88 | 71.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 81.4 | 87.7 | 67.9 | 87.8 | 70.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:34 | 1 | 81 | 87.4 | 67.4 | 87.5 | 70.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 80.5 | 87.2 | 66.9 | 87.3 | 69.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 80.1 | 86.9 | 66.4 | 87 | 69.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 79.6 | 86.6 | 66 | 86.8 | 69.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 79.1 | 86.3 | 65.5 | 86.5 | 68.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 78.7 | 86 | 65.1 | 86.3 | 68.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:35 | 1 | 78.2 | 85.7 | 64.7 | 86 | 67.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 77.8 | 85.4 | 64.3 | 85.7 | 67.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 77.3 | 85.1 | 63.8 | 85.5 | 67 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 76.8 | 84.9 | 63.4 | 85.2 | 66.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 76.3 | 84.6 | 63.1 | 84.9 | 66.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 75.9 | 84.4 | 62.7 | 84.7 | 66 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:36 | 1 | 75.5 | 84.1 | 62.4 | 84.5 | 65.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 75.1 | 83.8 | 62 | 84.2 | 65.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 74.6 | 83.5 | 61.8 | 83.9 | 65 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 74.2 | 83.3 | 61.4 | 83.7 | 64.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 73.7 | 83 | 61.1 | 83.4 | 64.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 73.3 | 82.8 | 60.9 | 83.2 | 64.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:37 | 1 | 72.9 | 82.5 | 60.6 | 83 | 63.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 72.5 | 82.2 | 60.3 | 82.7 | 63.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 72.1 | 81.9 | 60.1 | 82.5 | 63.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 71.7 | 81.7 | 59.8 | 82.1 | 62.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 71.3 | 81.5 | 59.5 | 81.9 | 62.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 70.9 | 81.2 | 59.3 | 81.7 | 62.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:38 | 1 | 70.5 | 81 | 59 | 81.5 | 62.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 70.2 | 80.7 | 58.8 | 81.2 | 61.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 69.8 | 80.5 | 58.6 | 81 | 61.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 69.4 | 80.2 | 58.3 | 80.8 | 61.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 69 | 80 | 58.1 | 80.6 | 61.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 68.7 | 79.8 | 57.9 | 80.4 | 60.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:39 | 1 | 68.4 | 79.5 | 57.7 | 80.1 | 60.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 68 | 79.3 | 57.5 | 79.9 | 60.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 67.7 | 79.1 | 57.3 | 79.7 | 60.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 67.3 | 78.8 | 57.2 | 79.5 | 60.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 67 | 78.6 | 57 | 79.2 | 59.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 66.7 | 78.4 | 56.8 | 79 | 59.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:40 | 1 | 66.4 | 78.2 | 56.7 | 78.8 | 59.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 66 | 78 | 56.5 | 78.6 | 59.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 65.8 | 77.7 | 56.4 | 78.4 | 59.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 65.5 | 77.5 | 56.2 | 78.2 | 58.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 65.2 | 77.3 | 56.1 | 78 | 58.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 64.9 | 77.1 | 55.9 | 77.8 | 58.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:41 | 1 | 64.6 | 77 | 55.7 | 77.6 | 58.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 64.3 | 76.7 | 55.6 | 77.3 | 58.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 64.1 | 76.6 | 55.4 | 77.1 | 58 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 63.8 | 76.4 | 55.4 | 76.9 | 57.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 63.5 | 76.2 | 55.2 | 76.7 | 57.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 63.3 | 76 | 55.1 | 76.5 | 57.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:42 | 1 | 63.1 | 75.7 | 54.9 | 76.3 | 57.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 62.8 | 75.5 | 54.7 | 76.1 | 57.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 62.6 | 75.3 | 54.5 | 75.9 | 57 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 62.3 | 75.2 | 54.3 | 75.7 | 56.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 62.1 | 75 | 54.1 | 75.5 | 56.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 61.8 | 74.8 | 53.9 | 75.3 | 56.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:43 | 1 | 61.6 | 74.6 | 53.7 | 75.1 | 56.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 61.4 | 74.4 | 53.5 | 74.9 | 56 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 61.2 | 74.2 | 53.3 | 74.7 | 55.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 61 | 74 | 53.1 | 74.5 | 55.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 60.7 | 73.9 | 52.9 | 74.3 | 55.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 60.5 | 73.7 | 52.7 | 74.1 | 55.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:44 | 1 | 60.3 | 73.4 | 52.5 | 73.9 | 55.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 60.1 | 73.3 | 52.3 | 73.7 | 55.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 59.9 | 73.1 | 52.1 | 73.5 | 54.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 59.7 | 72.9 | 51.9 | 73.3 | 54.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 59.5 | 72.7 | 51.7 | 73.1 | 54.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 59.3 | 72.5 | 51.6 | 72.9 | 54.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:45 | 1 | 59 | 72.3 | 51.4 | 72.7 | 54.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 58.8 | 72.2 | 51.2 | 72.5 | 53.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 58.6 | 72 | 51 | 72.4 | 53.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 58.4 | 71.8 | 50.8 | 72.2 | 53.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 58.2 | 71.6 | 50.6 | 72 | 53.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 58 | 71.5 | 50.5 | 71.8 | 53.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:46 | 1 | 57.9 | 71.3 | 50.3 | 71.7 | 53 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 57.7 | 71 | 50.1 | 71.5 | 52.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 57.5 | 70.9 | 49.9 | 71.3 | 52.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 57.3 | 70.7 | 49.7 | 71 | 52.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 57.1 | 70.5 | 49.6 | 70.9 | 52.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 56.9 | 70.3 | 49.4 | 70.7 | 52.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:47 | 1 | 56.7 | 70.1 | 49.2 | 70.5 | 52 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 56.6 | 70 | 49.1 | 70.3 | 51.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 56.4 | 69.8 | 48.9 | 70.1 | 51.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 56.2 | 69.6 | 48.8 | 69.9 | 51.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 56 | 69.4 | 48.6 | 69.7 | 51.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 55.9 | 69.3 | 48.5 | 69.6 | 51.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:48 | 1 | 55.7 | 69.1 | 48.3 | 69.4 | 51 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 55.6 | 69 | 48.2 | 69.2 | 50.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 55.5 | 68.8 | 48 | 69 | 50.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 55.4 | 68.6 | 47.9 | 68.8 | 50.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 55.2 | 68.5 | 47.7 | 68.6 | 50.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 55 | 68.3 | 47.6 | 68.5 | 50.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:49 | 1 | 54.8 | 68.1 | 47.5 | 68.3 | 50.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 54.7 | 68 | 47.3 | 68.1 | 50 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 54.5 | 67.8 | 47.2 | 67.9 | 49.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 54.3 | 67.6 | 47.1 | 67.8 | 49.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 54.2 | 67.5 | 47 | 67.6 | 49.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 54 | 67.3 | 46.9 | 67.4 | 49.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:50 | 1 | 53.9 | 67.1 | 46.7 | 67.3 | 49.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 53.7 | 67 | 46.6 | 67.1 | 49.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 53.5 | 66.8 | 46.5 | 66.9 | 49 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 53.4 | 66.6 | 46.4 | 66.7 | 48.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 53.2 | 66.5 | 46.3 | 66.6 | 48.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 53.1 | 66.3 | 46.2 | 66.4 | 48.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:51 | 1 | 52.9 | 66.2 | 46.1 | 66.3 | 48.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.8 | 66 | 46 | 66.1 | 48.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.6 | 65.9 | 46 | 65.9 | 48.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.5 | 65.7 | 45.9 | 65.7 | 48.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.4 | 65.6 | 45.7 | 65.6 | 48 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.2 | 65.4 | 45.6 | 65.4 | 48 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:52 | 1 | 52.1 | 65.3 | 45.5 | 65.2 | 47.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.9 | 65.1 | 45.4 | 65.1 | 47.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.8 | 65 | 45.3 | 64.9 | 47.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.7 | 64.9 | 45.1 | 64.8 | 47.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.5 | 64.7 | 45.1 | 64.6 | 47.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.4 | 64.6 | 44.9 | 64.5 | 47.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:53 | 1 | 51.2 | 64.4 | 44.8 | 64.4 | 47.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 51.2 | 64.3 | 44.7 | 64.2 | 47 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 51 | 64.1 | 44.5 | 64.1 | 46.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 50.9 | 64 | 44.4 | 63.9 | 46.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 50.8 | 63.9 | 44.3 | 63.8 | 46.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 50.7 | 63.7 | 44.1 | 63.6 | 46.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:54 | 1 | 50.5 | 63.6 | 44.1 | 63.5 | 46.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 50.4 | 63.5 | 43.9 | 63.3 | 46.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 50.3 | 63.3 | 43.8 | 63.2 | 46.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 50.2 | 63.2 | 43.7 | 63 | 46 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 50 | 63 | 43.6 | 62.8 | 45.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 49.9 | 62.9 | 43.4 | 62.7 | 45.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:55 | 1 | 49.8 | 62.8 | 43.3 | 62.5 | 45.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.7 | 62.6 | 43.2 | 62.4 | 45.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.6 | 62.5 | 43 | 62.3 | 45.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.4 | 62.4 | 42.9 | 62.1 | 45.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.3 | 62.2 | 42.8 | 62 | 45.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.2 | 62.1 | 42.6 | 61.8 | 45 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:56 | 1 | 49.1 | 62 | 42.6 | 61.7 | 44.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 49 | 61.8 | 42.4 | 61.5 | 44.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 48.8 | 61.7 | 42.3 | 61.4 | 44.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 48.7 | 61.5 | 42.1 | 61.2 | 44.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 48.6 | 61.4 | 42 | 61.1 | 44.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 48.5 | 61.2 | 41.9 | 60.9 | 44.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:57 | 1 | 48.4 | 61.1 | 41.8 | 60.8 | 44.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 48.3 | 61 | 41.6 | 60.7 | 44 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 48.1 | 60.8 | 41.5 | 60.5 | 43.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 48 | 60.7 | 41.4 | 60.4 | 43.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 47.9 | 60.5 | 41.2 | 60.2 | 43.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 47.8 | 60.4 | 41.1 | 60.1 | 43.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:58 | 1 | 47.7 | 60.3 | 41 | 59.9 | 43.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47.6 | 60.2 | 40.9 | 59.8 | 43.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47.5 | 60 | 40.8 | 59.7 | 43.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47.3 | 59.9 | 40.7 | 59.5 | 43 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47.2 | 59.8 | 40.6 | 59.4 | 42.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47.1 | 59.7 | 40.5 | 59.2 | 42.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 18:59 | 1 | 47 | 59.5 | 40.4 | 59.1 | 42.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.9 | 59.4 | 40.3 | 59 | 42.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.8 | 59.3 | 40.2 | 58.9 | 42.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.7 | 59.2 | 40.1 | 58.7 | 42.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.5 | 59 | 40 | 58.6 | 42.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.5 | 58.9 | 39.9 | 58.5 | 42.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:00 | 1 | 46.4 | 58.8 | 39.8 | 58.3 | 42 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 46.2 | 58.6 | 39.7 | 58.2 | 42 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 46.1 | 58.5 | 39.5 | 58.1 | 41.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 46 | 58.4 | 39.5 | 58 | 41.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 45.9 | 58.3 | 39.4 | 57.8 | 41.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 45.8 | 58.1 | 39.3 | 57.7 | 41.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:01 | 1 | 45.7 | 58 | 39.2 | 57.6 | 41.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.6 | 57.9 | 39.1 | 57.4 | 41.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.5 | 57.8 | 39.1 | 57.3 | 41.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.4 | 57.7 | 39 | 57.2 | 41.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.3 | 57.5 | 38.9 | 57 | 41 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.2 | 57.4 | 38.8 | 56.9 | 41 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:02 | 1 | 45.1 | 57.3 | 38.7 | 56.7 | 40.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 45 | 57.2 | 38.7 | 56.6 | 40.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 44.9 | 57.1 | 38.6 | 56.5 | 40.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 44.8 | 57 | 38.5 | 56.4 | 40.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 44.7 | 56.8 | 38.4 | 56.3 | 40.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 44.6 | 56.8 | 38.3 | 56.1 | 40.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:03 | 1 | 44.5 | 56.7 | 38.2 | 56 | 40.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44.4 | 56.5 | 38.1 | 55.9 | 40.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44.4 | 56.4 | 38.1 | 55.8 | 40.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44.2 | 56.3 | 37.9 | 55.6 | 40.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44.1 | 56.2 | 37.9 | 55.6 | 40 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44.1 | 56.1 | 37.8 | 55.4 | 39.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:04 | 1 | 44 | 56 | 37.7 | 55.5 | 39.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.9 | 55.9 | 37.6 | 55.3 | 39.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.8 | 55.8 | 37.5 | 55.3 | 39.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.7 | 55.7 | 37.4 | 55.2 | 39.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.6 | 55.6 | 37.3 | 55 | 39.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.5 | 55.5 | 37.2 | 54.9 | 39.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:05 | 1 | 43.5 | 55.5 | 37.1 | 54.8 | 39.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 43.3 | 55.4 | 37 | 54.7 | 39.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 43.2 | 55.3 | 36.9 | 54.6 | 39.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 43.2 | 55.2 | 36.7 | 54.4 | 39 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 43.1 | 55.1 | 36.7 | 54.3 | 39 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 43 | 54.9 | 36.6 | 54.1 | 38.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:06 | 1 | 42.9 | 54.9 | 36.5 | 54.1 | 38.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.8 | 54.8 | 36.4 | 53.9 | 38.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.8 | 54.7 | 36.3 | 53.8 | 38.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.7 | 54.5 | 36.2 | 53.7 | 38.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.6 | 54.4 | 36 | 53.6 | 38.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.5 | 54.3 | 35.9 | 53.5 | 38.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:07 | 1 | 42.4 | 54.2 | 35.8 | 53.4 | 38.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 42.3 | 54 | 35.7 | 53.3 | 38 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 42.3 | 54 | 35.6 | 53.2 | 37.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 42.2 | 53.9 | 35.6 | 53.1 | 37.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 42.1 | 53.8 | 35.5 | 52.9 | 37.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 42 | 53.6 | 35.4 | 52.8 | 37.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:08 | 1 | 41.9 | 53.6 | 35.3 | 52.8 | 37.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.8 | 53.5 | 35.2 | 52.6 | 37.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.8 | 53.3 | 35 | 52.5 | 37.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.7 | 53.2 | 34.9 | 52.4 | 37.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.6 | 53.1 | 34.8 | 52.3 | 37.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.5 | 53 | 34.7 | 52.2 | 37.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:09 | 1 | 41.4 | 52.9 | 34.6 | 52 | 37 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 41.3 | 52.8 | 34.5 | 52 | 36.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 41.3 | 52.7 | 34.4 | 51.8 | 36.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 41.2 | 52.6 | 34.3 | 51.7 | 36.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 41.1 | 52.5 | 34.3 | 51.6 | 36.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 41 | 52.4 | 34.2 | 51.5 | 36.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:10 | 1 | 40.9 | 52.3 | 34.1 | 51.4 | 36.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.9 | 52.2 | 34 | 51.3 | 36.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.8 | 52.1 | 33.9 | 51.2 | 36.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.7 | 52 | 33.8 | 51.1 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.6 | 51.9 | 33.7 | 51 | 36 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.5 | 51.8 | 33.6 | 50.9 | 35.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:11 | 1 | 40.4 | 51.7 | 33.6 | 50.8 | 35.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40.4 | 51.6 | 33.5 | 50.7 | 35.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40.3 | 51.5 | 33.4 | 50.6 | 35.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40.2 | 51.4 | 33.4 | 50.5 | 35.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40.1 | 51.3 | 33.3 | 50.4 | 35.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40 | 51.2 | 33.3 | 50.2 | 35.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:12 | 1 | 40 | 51.1 | 33.2 | 50.1 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.9 | 51 | 33.1 | 50.1 | 35.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.8 | 50.9 | 33 | 49.9 | 35.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.8 | 50.8 | 33 | 49.8 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.7 | 50.7 | 33 | 49.7 | 35.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.6 | 50.6 | 32.9 | 49.6 | 35 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:13 | 1 | 39.5 | 50.6 | 32.8 | 49.5 | 35 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.4 | 50.5 | 32.7 | 49.4 | 34.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.4 | 50.4 | 32.7 | 49.3 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.3 | 50.3 | 32.6 | 49.2 | 34.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.3 | 50.2 | 32.6 | 49.1 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.2 | 50.1 | 32.5 | 49.1 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:14 | 1 | 39.1 | 50 | 32.5 | 49 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 39 | 49.9 | 32.4 | 48.9 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 39 | 49.8 | 32.3 | 48.8 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 38.9 | 49.7 | 32.2 | 48.7 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 38.8 | 49.7 | 32.1 | 48.6 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 38.8 | 49.5 | 32.1 | 48.5 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:15 | 1 | 38.7 | 49.4 | 32 | 48.4 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.6 | 49.4 | 31.9 | 48.4 | 34 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.6 | 49.3 | 31.8 | 48.3 | 34 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.5 | 49.2 | 31.7 | 48.2 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.4 | 49.1 | 31.6 | 48.1 | 33.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.4 | 49.1 | 31.5 | 48 | 33.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:16 | 1 | 38.3 | 49 | 31.4 | 47.9 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 38.2 | 48.9 | 31.3 | 47.8 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 38.1 | 48.8 | 31.3 | 47.7 | 33.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 38 | 48.7 | 31.2 | 47.7 | 33.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 38 | 48.6 | 31.1 | 47.6 | 33.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 37.9 | 48.6 | 31 | 47.5 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:17 | 1 | 37.8 | 48.5 | 30.9 | 47.4 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.8 | 48.4 | 30.8 | 47.3 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.7 | 48.3 | 30.8 | 47.2 | 33 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.6 | 48.3 | 30.7 | 47.1 | 32.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.5 | 48.2 | 30.6 | 47 | 32.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.5 | 48.1 | 30.5 | 46.9 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:18 | 1 | 37.4 | 48 | 30.4 | 46.8 | 32.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 37.3 | 47.9 | 30.4 | 46.8 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 37.2 | 47.8 | 30.3 | 46.7 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 37.2 | 47.7 | 30.2 | 46.6 | 32.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 37.1 | 47.7 | 30.2 | 46.5 | 32.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 37 | 47.6 | 30.1 | 46.4 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:19 | 1 | 36.9 | 47.5 | 30 | 46.3 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.9 | 47.4 | 29.9 | 46.2 | 32.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.8 | 47.3 | 29.9 | 46.2 | 32.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.7 | 47.2 | 29.8 | 46.1 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.7 | 47.1 | 29.7 | 46 | 31.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.6 | 47 | 29.6 | 45.9 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:20 | 1 | 36.5 | 46.9 | 29.5 | 45.8 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.4 | 46.9 | 29.5 | 45.7 | 31.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.3 | 46.8 | 29.4 | 45.6 | 31.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.3 | 46.7 | 29.3 | 45.5 | 31.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.2 | 46.6 | 29.2 | 45.5 | 31.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.2 | 46.5 | 29.1 | 45.4 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:21 | 1 | 36.1 | 46.4 | 29.1 | 45.3 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 36 | 46.4 | 29 | 45.2 | 31.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 36 | 46.3 | 29 | 45.1 | 31.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 35.9 | 46.2 | 28.9 | 45 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 35.8 | 46.1 | 28.9 | 44.9 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 35.8 | 46 | 28.8 | 44.9 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:22 | 1 | 35.7 | 45.9 | 28.7 | 44.8 | 30.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.6 | 45.9 | 28.7 | 44.7 | 30.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.6 | 45.8 | 28.7 | 44.6 | 30.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.5 | 45.8 | 28.6 | 44.6 | 30.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.4 | 45.7 | 28.6 | 44.5 | 30.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.4 | 45.6 | 28.5 | 44.4 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:23 | 1 | 35.3 | 45.6 | 28.5 | 44.3 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 35.2 | 45.5 | 28.5 | 44.2 | 30.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 35.2 | 45.4 | 28.5 | 44.1 | 30.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 35.1 | 45.3 | 28.4 | 44.1 | 30.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 35 | 45.3 | 28.4 | 44 | 30.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 35 | 45.2 | 28.3 | 43.9 | 30.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:24 | 1 | 34.9 | 45.1 | 28.2 | 43.8 | 30.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.8 | 45 | 28.2 | 43.7 | 30.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.7 | 45 | 28.2 | 43.7 | 30.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.7 | 44.9 | 28.1 | 43.6 | 30.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.6 | 44.8 | 28.1 | 43.5 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.6 | 44.8 | 28 | 43.5 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:25 | 1 | 34.5 | 44.7 | 28 | 43.4 | 29.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.5 | 44.6 | 27.9 | 43.3 | 29.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.5 | 44.5 | 27.8 | 43.2 | 29.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.4 | 44.4 | 27.8 | 43.2 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.3 | 44.4 | 27.8 | 43.1 | 29.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.2 | 44.3 | 27.7 | 43 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:26 | 1 | 34.2 | 44.3 | 27.6 | 43 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 34.1 | 44.2 | 27.6 | 42.9 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 34.1 | 44.1 | 27.5 | 42.8 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 34.1 | 44.1 | 27.4 | 42.8 | 29.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 34 | 44 | 27.3 | 42.7 | 29.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 34 | 44 | 27.2 | 42.6 | 29.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:27 | 1 | 33.9 | 43.9 | 27.2 | 42.5 | 29.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.9 | 43.8 | 27.1 | 42.4 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.8 | 43.7 | 27 | 42.3 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.7 | 43.7 | 26.9 | 42.3 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.7 | 43.6 | 26.8 | 42.2 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.6 | 43.5 | 26.7 | 42.1 | 28.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:28 | 1 | 33.6 | 43.4 | 26.7 | 42.1 | 28.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.5 | 43.4 | 26.6 | 42 | 28.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.5 | 43.3 | 26.6 | 41.9 | 28.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.4 | 43.3 | 26.5 | 41.9 | 28.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.4 | 43.2 | 26.5 | 41.8 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.3 | 43.2 | 26.5 | 41.7 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:29 | 1 | 33.3 | 43.1 | 26.7 | 41.6 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33.2 | 43.1 | 27.1 | 41.6 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33.1 | 43.1 | 27.7 | 41.5 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33 | 43 | 27.9 | 41.5 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33 | 43 | 27.9 | 41.4 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33 | 43 | 27.9 | 41.3 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:30 | 1 | 33 | 42.9 | 27.8 | 41.3 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.9 | 42.9 | 27.7 | 41.2 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.8 | 42.9 | 27.6 | 41.1 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.8 | 42.8 | 27.5 | 41.1 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.8 | 42.8 | 27.5 | 41 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.8 | 42.8 | 27.4 | 41 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:31 | 1 | 32.7 | 42.7 | 27.3 | 40.9 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.7 | 42.7 | 27.2 | 40.9 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.6 | 42.6 | 27 | 40.8 | 28.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.6 | 42.6 | 26.8 | 40.7 | 28.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.6 | 42.5 | 26.7 | 40.7 | 28.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.5 | 42.4 | 26.5 | 40.6 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:32 | 1 | 32.5 | 42.4 | 26.4 | 40.6 | 28.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.5 | 42.3 | 26.2 | 40.5 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.4 | 42.3 | 26.1 | 40.5 | 28.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.4 | 42.2 | 26 | 40.4 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.3 | 42.2 | 25.9 | 40.3 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.3 | 42.1 | 25.8 | 40.3 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:33 | 1 | 32.2 | 42 | 25.6 | 40.3 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32.2 | 42 | 25.6 | 40.2 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32.2 | 41.9 | 25.5 | 40.1 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32.1 | 41.8 | 25.5 | 40.1 | 28.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32 | 41.8 | 25.4 | 40.1 | 28.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32 | 41.7 | 25.3 | 40 | 28.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:34 | 1 | 32 | 41.6 | 25.3 | 39.9 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.9 | 41.6 | 25.2 | 39.9 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.9 | 41.6 | 25.2 | 39.9 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.8 | 41.5 | 25.1 | 39.8 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.8 | 41.5 | 25.1 | 39.8 | 28.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.7 | 41.4 | 25.1 | 39.7 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:35 | 1 | 31.7 | 41.3 | 25 | 39.7 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.7 | 41.3 | 25 | 39.6 | 27.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.6 | 41.2 | 24.9 | 39.6 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.5 | 41.1 | 24.9 | 39.6 | 27.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.5 | 41.1 | 24.9 | 39.5 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.5 | 41 | 24.8 | 39.4 | 27.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:36 | 1 | 31.4 | 41 | 24.8 | 39.4 | 27.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.4 | 40.9 | 24.7 | 39.4 | 27 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.4 | 40.9 | 24.6 | 39.3 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.3 | 40.8 | 24.6 | 39.3 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.3 | 40.8 | 24.5 | 39.2 | 26.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.2 | 40.7 | 24.4 | 39.2 | 26.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:37 | 1 | 31.2 | 40.6 | 24.4 | 39.1 | 26.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 31.1 | 40.6 | 24.4 | 39.1 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 31 | 40.5 | 24.2 | 39 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 31 | 40.5 | 24.2 | 38.9 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 31 | 40.4 | 24.1 | 38.8 | 26.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 31 | 40.4 | 24.1 | 38.8 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:38 | 1 | 30.9 | 40.3 | 24 | 38.7 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.9 | 40.3 | 23.9 | 38.6 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.8 | 40.2 | 23.8 | 38.6 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.7 | 40.1 | 23.7 | 38.5 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.7 | 40.1 | 23.6 | 38.4 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.7 | 40 | 23.6 | 38.4 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:39 | 1 | 30.6 | 39.9 | 23.5 | 38.3 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.6 | 39.9 | 23.4 | 38.2 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.5 | 39.8 | 23.3 | 38.1 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.4 | 39.8 | 23.2 | 38 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.4 | 39.7 | 23.1 | 38 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.3 | 39.7 | 23 | 37.9 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:40 | 1 | 30.3 | 39.6 | 23 | 37.8 | 25.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30.3 | 39.5 | 22.9 | 37.8 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30.2 | 39.5 | 22.9 | 37.7 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30.2 | 39.4 | 22.8 | 37.6 | 24.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30.1 | 39.3 | 22.7 | 37.6 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30.1 | 39.3 | 22.6 | 37.5 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:41 | 1 | 30 | 39.3 | 22.6 | 37.5 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.9 | 39.2 | 22.5 | 37.4 | 24.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.9 | 39.2 | 22.4 | 37.3 | 24.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.8 | 39.1 | 22.4 | 37.2 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.7 | 39 | 22.3 | 37.2 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.7 | 38.9 | 22.3 | 37.1 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:42 | 1 | 29.6 | 38.9 | 22.2 | 37 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.6 | 38.9 | 22.2 | 37 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.6 | 38.8 | 22.1 | 36.9 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.5 | 38.7 | 22.1 | 36.9 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.4 | 38.7 | 22 | 36.8 | 24.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.4 | 38.6 | 22 | 36.7 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:43 | 1 | 29.3 | 38.5 | 21.8 | 36.6 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29.3 | 38.5 | 21.8 | 36.5 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29.2 | 38.4 | 21.8 | 36.4 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29.1 | 38.4 | 21.7 | 36.4 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29.1 | 38.3 | 21.7 | 36.3 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29.1 | 38.2 | 21.7 | 36.3 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:44 | 1 | 29 | 38.2 | 21.6 | 36.3 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 29 | 38.1 | 21.6 | 36.2 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 28.9 | 38.1 | 21.6 | 36.1 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 28.8 | 38 | 21.6 | 36 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 28.8 | 38 | 21.5 | 36 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 28.8 | 37.9 | 21.5 | 36 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:45 | 1 | 28.7 | 37.8 | 21.5 | 35.9 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.7 | 37.8 | 21.5 | 35.8 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.6 | 37.7 | 21.4 | 35.8 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.6 | 37.6 | 21.4 | 35.7 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.5 | 37.6 | 21.4 | 35.7 | 23.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.5 | 37.6 | 21.3 | 35.6 | 23.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:46 | 1 | 28.5 | 37.5 | 21.3 | 35.5 | 23.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:47 | 1 | 28.5 | 37.5 | 21.3 | 35.5 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:47 | 1 | 28.5 | 37.5 | 21.3 | 35.4 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:47 | 1 | 28.5 | 37.4 | 21.2 | 35.4 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:47 | 1 | 28.4 | 37.4 | 21.1 | 35.4 | 23.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:47 | 1 | 28.3 | 37.3 | 20.7 | 35.3 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:47 | 1 | 28.3 | 37.2 | 20.4 | 35.3 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:47 | 1 | 28.3 | 37.1 | 20.1 | 35.2 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 28.2 | 37 | 19.7 | 35.2 | 28.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 28.1 | 37 | 19.5 | 35.2 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 28 | 36.9 | 19.1 | 35.2 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 27.9 | 36.8 | 18.8 | 35.2 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 27.8 | 36.7 | 18.5 | 35.2 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:48 | 1 | 27.7 | 36.6 | 18.3 | 35.2 | 31.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 27.6 | 36.5 | 18 | 35.2 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 27.5 | 36.4 | 17.8 | 35.2 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 27.4 | 36.2 | 17.6 | 35.2 | 32.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 27.2 | 36.1 | 17.4 | 35.3 | 32.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 27.1 | 36 | 17.1 | 35.3 | 32.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:49 | 1 | 26.9 | 35.9 | 16.9 | 35.3 | 32.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:50 | 1 | 26.8 | 35.8 | 16.6 | 35.3 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:50 | 1 | 26.7 | 35.6 | 16.4 | 35.3 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:50 | 1 | 26.5 | 35.5 | 16.2 | 35.3 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 19:50 | 1 | 26.4 | 35.4 | 16.2 | 35.3 | 33.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:50 | 1 | 26.3 | 35.4 | 16 | 35.3 | 33.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:50 | 1 | 26.2 | 35.3 | 15.6 | 35.4 | 33.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:50 | 1 | 26 | 35.2 | 16.3 | 35.4 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 25.9 | 35.1 | 18.3 | 35.4 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 25.8 | 35 | 20.4 | 35.4 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 25.5 | 35 | 22.7 | 35.4 | 34.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 25.3 | 35 | 24.8 | 35.4 | 35 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 24.9 | 35 | 26.6 | 35.5 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:51 | 1 | 24.5 | 35 | 28 | 35.5 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 24.1 | 35.1 | 29 | 35.6 | 35.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 23.6 | 35.1 | 29.7 | 35.7 | 35.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 23.2 | 35.2 | 30.3 | 35.7 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 22.6 | 35.3 | 30.7 | 35.8 | 36.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 22.1 | 35.4 | 31 | 35.8 | 36.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:52 | 1 | 21.5 | 35.5 | 31.2 | 35.9 | 36.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:53 | 1 | 20.8 | 35.6 | 31.4 | 35.9 | 36.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:53 | 1 | 20.2 | 35.7 | 31.5 | 36 | 37 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 19:53 | 1 | 19.9 | 35.7 | 31.5 | 36.1 | 37.1 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 19:53 | 1 | 19.9 | 35.7 | 31.5 | 36.1 | 37.1 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 19:53 | 1 | 19.6 | 35.8 | 31.6 | 36.1 | 37.1 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 19:53 | 1 | 18.9 | 35.9 | 31.2 | 36.2 | 36.2 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 19:53 | 1 | 18.2 | 35.9 | 31.1 | 36.2 | 35.4 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 19:53 | 1 | 18 | 36 | 31.1 | 36.2 | 35.3 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 19:53 | 1 | 18 | 36 | 31.1 | 36.2 | 35.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:53 | 1 | 17.7 | 36 | 31.2 | 36.3 | 35.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 17.2 | 36.1 | 31.3 | 36.3 | 35.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 16.7 | 36.2 | 31.5 | 36.4 | 35.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 16.3 | 36.3 | 31.7 | 36.5 | 36.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 16.1 | 36.4 | 31.8 | 36.5 | 36.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 15.9 | 36.5 | 31.9 | 36.6 | 37 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:54 | 1 | 15.8 | 36.6 | 32.2 | 36.7 | 37.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 15.8 | 36.7 | 32.9 | 36.8 | 37.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 15.8 | 36.8 | 33.7 | 36.9 | 37.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 15.9 | 36.9 | 34.4 | 37 | 38.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 16 | 37 | 35.1 | 37.1 | 38.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 16.3 | 37.2 | 35.5 | 37.2 | 38.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:55 | 1 | 16.5 | 37.3 | 35.9 | 37.4 | 38.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 16.8 | 37.5 | 36.2 | 37.5 | 39 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 17.1 | 37.6 | 36.5 | 37.6 | 39.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 17.5 | 37.7 | 36.7 | 37.7 | 39.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 17.7 | 37.8 | 37 | 37.8 | 39.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 18 | 37.9 | 37.1 | 37.9 | 39.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:56 | 1 | 18.4 | 38.1 | 37.3 | 38 | 39.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 18.7 | 38.2 | 37.5 | 38.2 | 39.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 19.2 | 38.3 | 37.7 | 38.3 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 19.5 | 38.4 | 37.9 | 38.4 | 40.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 19.9 | 38.6 | 38 | 38.5 | 40.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 20.2 | 38.7 | 38.2 | 38.6 | 40.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:57 | 1 | 20.6 | 38.8 | 38.4 | 38.7 | 40.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:58 | 1 | 20.9 | 38.9 | 38.5 | 38.8 | 40.5 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 19:58 | 1 | 21 | 39 | 38.5 | 38.9 | 40.5 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-07 19:58 | 1 | 21 | 39 | 38.5 | 38.9 | 40.5 | 4.5 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-07 19:58 | 1 | 21.4 | 39 | 38.6 | 39 | 40.6 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 19:58 | 1 | 21.7 | 39.1 | 38.2 | 39.1 | 40.2 | 4.5 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-07 19:58 | 1 | 22 | 39.2 | 37.1 | 39.1 | 39.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:58 | 1 | 22.1 | 39.2 | 36.5 | 39.1 | 39 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:58 | 1 | 22.4 | 39.3 | 34.7 | 39.2 | 37.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:58 | 1 | 22.7 | 39.2 | 33.2 | 39.2 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 23.1 | 39.2 | 31.9 | 39.2 | 33.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 23.4 | 39.2 | 31 | 39.2 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 23.7 | 39.2 | 30.3 | 39.2 | 31.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 24.1 | 39.2 | 29.7 | 39.2 | 30.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 24.5 | 39.3 | 29.2 | 39.1 | 29.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 19:59 | 1 | 24.8 | 39.3 | 28.7 | 39 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 25.1 | 39.2 | 28.4 | 38.9 | 28.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 25.4 | 39.2 | 28.1 | 38.8 | 28.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 25.7 | 39.2 | 27.8 | 38.7 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 26 | 39.1 | 27.5 | 38.6 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 26.3 | 39.1 | 27.2 | 38.5 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:00 | 1 | 26.6 | 39.1 | 27 | 38.4 | 27 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 26.8 | 39 | 26.7 | 38.4 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 27 | 38.9 | 26.5 | 38.3 | 26.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 27.3 | 38.9 | 26.3 | 38.2 | 26.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 27.4 | 38.9 | 26 | 38.1 | 26.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 27.6 | 38.8 | 25.8 | 38 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:01 | 1 | 27.8 | 38.7 | 25.6 | 37.9 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28 | 38.6 | 25.4 | 37.7 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28.1 | 38.6 | 25.2 | 37.6 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28.2 | 38.5 | 25 | 37.5 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28.3 | 38.5 | 24.8 | 37.4 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28.4 | 38.4 | 24.6 | 37.3 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:02 | 1 | 28.4 | 38.3 | 24.5 | 37.2 | 25.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.5 | 38.3 | 24.3 | 37.1 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.6 | 38.2 | 24.1 | 37.1 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.6 | 38.1 | 24 | 37 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.7 | 38.1 | 24.4 | 36.9 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.7 | 38 | 25.2 | 36.8 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:03 | 1 | 28.7 | 38 | 25.4 | 36.7 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.8 | 38 | 25.4 | 36.6 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.8 | 37.9 | 25.3 | 36.6 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.8 | 37.9 | 25.2 | 36.5 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.8 | 37.9 | 25 | 36.5 | 26 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.9 | 37.9 | 24.8 | 36.5 | 25.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:04 | 1 | 28.9 | 37.9 | 24.6 | 36.4 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.8 | 24.4 | 36.4 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.8 | 24.2 | 36.3 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.8 | 24 | 36.3 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.8 | 23.9 | 36.2 | 25.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.7 | 23.7 | 36.2 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:05 | 1 | 28.9 | 37.7 | 23.5 | 36.1 | 24.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.7 | 23.4 | 36 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.6 | 23.2 | 36 | 24.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.6 | 23.1 | 35.9 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.5 | 23 | 35.9 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.4 | 22.8 | 35.8 | 24.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:06 | 1 | 28.9 | 37.4 | 22.7 | 35.7 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:07 | 1 | 28.9 | 37.3 | 22.6 | 35.6 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:07 | 1 | 28.8 | 37.3 | 22.5 | 35.5 | 23.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:07 | 1 | 28.8 | 37.2 | 22.4 | 35.4 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:07 | 1 | 28.8 | 37.2 | 22.4 | 35.4 | 23.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:07 | 1 | 28.8 | 37.1 | 22.2 | 35.4 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:07 | 1 | 28.8 | 37.1 | 22 | 35.3 | 23.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:07 | 1 | 28.7 | 37 | 21.7 | 35.2 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.6 | 37 | 21.2 | 35.2 | 25.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.6 | 36.9 | 20.8 | 35.2 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.5 | 36.8 | 20.5 | 35.1 | 28.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.5 | 36.7 | 20.1 | 35.1 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.5 | 36.6 | 19.7 | 35.1 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:08 | 1 | 28.4 | 36.5 | 19.5 | 35.1 | 30.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 28.2 | 36.4 | 19.1 | 35.1 | 31.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 28.1 | 36.3 | 18.9 | 35.1 | 31.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 28 | 36.2 | 18.6 | 35.1 | 31.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 27.9 | 36.1 | 18.4 | 35.1 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 27.8 | 35.9 | 18.1 | 35.1 | 32.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:09 | 1 | 27.6 | 35.8 | 17.8 | 35.1 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:10 | 1 | 27.4 | 35.7 | 17.7 | 35.1 | 32.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:10 | 1 | 27.2 | 35.6 | 17.5 | 35.1 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:10 | 1 | 27.1 | 35.5 | 17.3 | 35.1 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:10 | 1 | 27.1 | 35.4 | 17.2 | 35.1 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:10 | 1 | 27 | 35.3 | 17 | 35.1 | 32.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:10 | 1 | 26.8 | 35.2 | 16.6 | 35.1 | 33.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:10 | 1 | 26.5 | 35.1 | 17.6 | 35.1 | 33.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 26.4 | 35 | 19.6 | 35.1 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 26 | 34.9 | 21.8 | 35.2 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 25.7 | 34.9 | 24 | 35.2 | 34.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 25.3 | 34.9 | 25.9 | 35.2 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 24.8 | 34.9 | 27.4 | 35.2 | 34.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:11 | 1 | 24.3 | 34.9 | 28.6 | 35.3 | 34.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 23.6 | 35 | 29.4 | 35.3 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 23 | 35.1 | 30.1 | 35.4 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 22.3 | 35.2 | 30.5 | 35.4 | 35.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 21.6 | 35.2 | 30.9 | 35.5 | 35.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 20.9 | 35.3 | 31.1 | 35.5 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:12 | 1 | 20.1 | 35.4 | 31.3 | 35.6 | 36.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:13 | 1 | 19.9 | 35.4 | 31.3 | 35.6 | 36.3 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 20:13 | 1 | 19.9 | 35.4 | 31.3 | 35.6 | 36.3 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:13 | 1 | 19.5 | 35.4 | 31.4 | 35.7 | 36.4 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:13 | 1 | 18.8 | 35.5 | 30.9 | 35.7 | 35.5 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:13 | 1 | 18.1 | 35.6 | 31 | 35.7 | 34.9 | 3.8 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:13 | 1 | 17.8 | 35.6 | 31.1 | 35.8 | 34.8 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 20:13 | 1 | 17.8 | 35.6 | 31.1 | 35.8 | 34.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:13 | 1 | 17.5 | 35.7 | 31.3 | 35.8 | 34.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:13 | 1 | 16.9 | 35.7 | 31.4 | 35.9 | 35 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:13 | 1 | 16.5 | 35.8 | 31.6 | 35.9 | 35.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 16.1 | 35.9 | 31.7 | 36 | 35.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 15.8 | 36 | 31.9 | 36.1 | 36 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 15.6 | 36.1 | 32.1 | 36.2 | 36.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 15.5 | 36.2 | 32.3 | 36.3 | 36.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 15.5 | 36.3 | 32.5 | 36.3 | 36.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:14 | 1 | 15.4 | 36.3 | 32.7 | 36.4 | 37.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 15.5 | 36.4 | 33 | 36.5 | 37.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 15.7 | 36.5 | 33.4 | 36.6 | 37.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 15.9 | 36.6 | 33.8 | 36.7 | 37.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 16.2 | 36.7 | 34.2 | 36.8 | 37.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 16.5 | 36.8 | 34.6 | 36.9 | 38.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:15 | 1 | 16.8 | 36.9 | 35 | 37 | 38.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 17.1 | 37 | 35.3 | 37.1 | 38.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 17.5 | 37.1 | 35.6 | 37.2 | 38.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 17.7 | 37.2 | 35.9 | 37.3 | 38.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 18 | 37.3 | 36.1 | 37.4 | 38.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 18.4 | 37.4 | 36.4 | 37.5 | 39 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:16 | 1 | 18.7 | 37.5 | 36.5 | 37.6 | 39.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 19.1 | 37.6 | 36.8 | 37.7 | 39.2 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 19.4 | 37.7 | 36.9 | 37.8 | 39.3 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 19.8 | 37.8 | 37.1 | 37.8 | 39.4 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 20.1 | 37.9 | 37.2 | 38 | 39.6 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 20.4 | 38 | 37.4 | 38.1 | 39.7 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:17 | 1 | 20.8 | 38.1 | 37.6 | 38.2 | 39.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:18 | 1 | 21.2 | 38.2 | 37.7 | 38.3 | 39.8 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:18 | 1 | 21.6 | 38.3 | 37.8 | 38.4 | 39.9 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:18 | 1 | 21.9 | 38.4 | 38 | 38.5 | 40.1 | 3.8 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:18 | 1 | 22 | 38.5 | 38 | 38.6 | 40.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:18 | 1 | 22.2 | 38.6 | 38.1 | 38.6 | 40.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:18 | 1 | 22.6 | 38.7 | 37.6 | 38.7 | 39.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:18 | 1 | 22.9 | 38.7 | 36 | 38.8 | 38.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:19 | 1 | 23.3 | 38.7 | 35.5 | 38.8 | 38.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:19 | 1 | 23.6 | 38.7 | 35.7 | 38.9 | 38.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:19 | 1 | 23.8 | 38.8 | 36.2 | 38.9 | 38.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:19 | 1 | 23.8 | 38.9 | 36.4 | 39 | 38.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 20:19 | 1 | 23.9 | 38.9 | 36.7 | 39 | 38.7 | 4.5 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 20:19 | 1 | 23.9 | 39 | 36.9 | 39 | 38.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:19 | 1 | 24 | 39 | 36.9 | 39.1 | 36.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:19 | 1 | 24 | 39.1 | 35.2 | 39.1 | 34.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24 | 39.1 | 33.7 | 39.1 | 32.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24 | 39.1 | 32.8 | 39.1 | 30.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24 | 39.1 | 31.6 | 39 | 30 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24 | 39.1 | 30.7 | 39 | 29.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24 | 39.1 | 30 | 38.9 | 29.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:20 | 1 | 24.1 | 39.1 | 29.4 | 38.8 | 29.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.1 | 39.1 | 28.8 | 38.7 | 28.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.2 | 39.1 | 28.4 | 38.7 | 28.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.3 | 39.1 | 27.9 | 38.6 | 27.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.5 | 39.1 | 27.6 | 38.5 | 27.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.5 | 39 | 27.3 | 38.4 | 27.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:21 | 1 | 24.6 | 39 | 27.2 | 38.3 | 27.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 24.8 | 38.9 | 27.1 | 38.2 | 26.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 24.9 | 38.9 | 27 | 38.2 | 26.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 25.1 | 38.8 | 26.8 | 38.1 | 26.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 25.2 | 38.8 | 26.7 | 38 | 26.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 25.3 | 38.7 | 26.4 | 37.8 | 26.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:22 | 1 | 25.5 | 38.7 | 26.2 | 37.7 | 25.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 25.7 | 38.6 | 26.1 | 37.6 | 25.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 25.8 | 38.5 | 25.8 | 37.5 | 25.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 26 | 38.5 | 25.6 | 37.4 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 26.2 | 38.4 | 25.5 | 37.3 | 25.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 26.3 | 38.3 | 25.3 | 37.2 | 25.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:23 | 1 | 26.5 | 38.3 | 25.1 | 37.1 | 25 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 26.7 | 38.2 | 24.9 | 37.1 | 24.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 26.8 | 38.2 | 24.7 | 37 | 24.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 26.9 | 38.1 | 24.6 | 36.9 | 24.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 27 | 38 | 24.4 | 36.8 | 24.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 27.1 | 38 | 24.4 | 36.7 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:24 | 1 | 27.2 | 37.9 | 25.1 | 36.5 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.4 | 37.9 | 25.7 | 36.4 | 24.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.5 | 37.9 | 25.7 | 36.4 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.6 | 37.8 | 25.7 | 36.3 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.7 | 37.8 | 25.5 | 36.2 | 24.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.8 | 37.8 | 25.3 | 36.2 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:25 | 1 | 27.8 | 37.8 | 25.2 | 36.1 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 27.9 | 37.7 | 25 | 36 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 27.9 | 37.7 | 24.7 | 35.9 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 28 | 37.7 | 24.6 | 35.9 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 28.1 | 37.7 | 24.3 | 35.8 | 24.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 28.1 | 37.7 | 24.1 | 35.7 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:26 | 1 | 28.1 | 37.6 | 24 | 35.6 | 24 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:27 | 1 | 28.2 | 37.6 | 23.8 | 35.5 | 23.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:27 | 1 | 28.2 | 37.6 | 23.7 | 35.4 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:27 | 1 | 28.2 | 37.6 | 23.6 | 35.4 | 23.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:27 | 1 | 28.3 | 37.5 | 23.4 | 35.3 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:27 | 1 | 28.3 | 37.5 | 23.2 | 35.3 | 23.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:27 | 1 | 28.3 | 37.4 | 23 | 35.2 | 24.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:27 | 1 | 28.3 | 37.3 | 22.6 | 35.2 | 25.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.3 | 37.3 | 22.2 | 35.2 | 26.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.3 | 37.2 | 21.8 | 35.1 | 28 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.3 | 37.1 | 21.4 | 35.1 | 29 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.3 | 37 | 21 | 35.1 | 29.9 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.3 | 36.9 | 20.7 | 35.1 | 30.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:28 | 1 | 28.2 | 36.8 | 20.4 | 35.1 | 31 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 28.2 | 36.7 | 20 | 35.1 | 31.4 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 28.1 | 36.7 | 19.8 | 35.1 | 31.7 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 28 | 36.5 | 19.5 | 35.1 | 32 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 27.8 | 36.4 | 19.3 | 35.1 | 32.2 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 27.7 | 36.3 | 19 | 35.1 | 32.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:29 | 1 | 27.7 | 36.2 | 18.8 | 35.1 | 32.5 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 27.6 | 36 | 18.5 | 35.2 | 32.6 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 27.4 | 36 | 18.2 | 35.2 | 32.8 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 27.3 | 35.9 | 18.1 | 35.2 | 33 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 27.1 | 35.7 | 17.8 | 35.2 | 33.1 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 26.9 | 35.6 | 17.6 | 35.2 | 33.3 | 4.5 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:30 | 1 | 26.8 | 35.4 | 17.6 | 35.2 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:30 | 1 | 26.8 | 35.4 | 17.5 | 35.2 | 33.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 26.7 | 35.3 | 17.1 | 35.2 | 33.9 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 26.5 | 35.2 | 17.1 | 35.2 | 34.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 26.3 | 35.1 | 18.5 | 35.2 | 34.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 26.1 | 35 | 20.5 | 35.2 | 34.5 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 25.8 | 35 | 22.7 | 35.2 | 34.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:31 | 1 | 25.4 | 35 | 24.7 | 35.2 | 34.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 25 | 35 | 26.6 | 35.3 | 35 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 24.5 | 35 | 28 | 35.3 | 35.2 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 23.9 | 35 | 29 | 35.4 | 35.4 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 23.3 | 35 | 29.7 | 35.4 | 35.6 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 22.6 | 35.1 | 30.3 | 35.5 | 35.8 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:32 | 1 | 22 | 35.1 | 30.7 | 35.5 | 36 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:33 | 1 | 21.2 | 35.2 | 31 | 35.6 | 36.1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:33 | 1 | 20.6 | 35.3 | 31.2 | 35.7 | 36.3 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:33 | 1 | 19.9 | 35.4 | 31.4 | 35.7 | 36.5 | 3.8 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 20:33 | 1 | 19.9 | 35.4 | 31.4 | 35.7 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:33 | 1 | 19.9 | 35.4 | 31.4 | 35.7 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:33 | 1 | 19.1 | 35.5 | 31.2 | 35.7 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:33 | 1 | 18.4 | 35.6 | 30.9 | 35.8 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:33 | 1 | 17.9 | 35.6 | 31 | 35.8 | 34.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 20:33 | 1 | 17.9 | 35.6 | 31 | 35.8 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:33 | 1 | 17.8 | 35.6 | 31 | 35.8 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 17.3 | 35.7 | 31.2 | 35.9 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 16.8 | 35.8 | 31.4 | 36 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 16.4 | 35.9 | 31.6 | 36 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 16.1 | 36 | 31.7 | 36.1 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 15.9 | 36 | 31.8 | 36.1 | 35.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:34 | 1 | 15.7 | 36.1 | 32 | 36.2 | 36.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 15.7 | 36.2 | 32.1 | 36.3 | 36.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 15.7 | 36.3 | 32.3 | 36.4 | 36.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 15.7 | 36.3 | 32.5 | 36.5 | 37 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 15.9 | 36.4 | 32.7 | 36.5 | 37.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 16.1 | 36.5 | 33 | 36.6 | 37.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:35 | 1 | 16.3 | 36.6 | 33.3 | 36.7 | 37.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 16.5 | 36.6 | 33.7 | 36.8 | 37.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 16.8 | 36.7 | 34.1 | 36.9 | 38 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 17.2 | 36.8 | 34.5 | 37 | 38.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 17.5 | 36.9 | 34.9 | 37.1 | 38.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 17.8 | 37 | 35.2 | 37.2 | 38.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:36 | 1 | 18 | 37.1 | 35.5 | 37.3 | 38.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 18.4 | 37.2 | 35.7 | 37.3 | 38.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 18.8 | 37.3 | 36 | 37.4 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 19 | 37.4 | 36.2 | 37.5 | 39 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 19.5 | 37.5 | 36.4 | 37.6 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 19.8 | 37.6 | 36.6 | 37.7 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:37 | 1 | 20.1 | 37.7 | 36.8 | 37.8 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 20.5 | 37.8 | 37 | 37.9 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 20.8 | 37.9 | 37.1 | 38 | 39.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 21.1 | 37.9 | 37.3 | 38.1 | 39.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 21.5 | 38 | 37.4 | 38.2 | 39.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 21.9 | 38.1 | 37.6 | 38.3 | 39.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:38 | 1 | 22 | 38.2 | 37.7 | 38.3 | 39.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:38 | 1 | 22.2 | 38.2 | 37.7 | 38.4 | 40 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 22.6 | 38.3 | 37.3 | 38.5 | 39.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 22.9 | 38.4 | 35.4 | 38.6 | 38.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 23.2 | 38.5 | 33.6 | 38.6 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 23.6 | 38.5 | 32.1 | 38.6 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 23.8 | 38.5 | 31.1 | 38.6 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:39 | 1 | 24.2 | 38.5 | 30.4 | 38.6 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 24.5 | 38.5 | 29.8 | 38.6 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 24.8 | 38.5 | 29.5 | 38.6 | 30.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 25.2 | 38.5 | 29.5 | 38.5 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 25.4 | 38.5 | 29.5 | 38.5 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 25.8 | 38.5 | 29.6 | 38.4 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:40 | 1 | 26.1 | 38.6 | 29.5 | 38.3 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 26.3 | 38.6 | 29.2 | 38.3 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 26.6 | 38.6 | 28.9 | 38.2 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 26.9 | 38.6 | 28.6 | 38.1 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 27.2 | 38.6 | 28.3 | 38 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 27.3 | 38.6 | 27.9 | 37.9 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:41 | 1 | 27.6 | 38.6 | 27.5 | 37.8 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 27.8 | 38.6 | 27.2 | 37.7 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 28 | 38.5 | 26.9 | 37.6 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 28.2 | 38.5 | 26.5 | 37.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 28.4 | 38.5 | 26.3 | 37.4 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 28.5 | 38.5 | 26 | 37.4 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:42 | 1 | 28.5 | 38.4 | 25.8 | 37.3 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 28.6 | 38.4 | 25.6 | 37.2 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 28.8 | 38.3 | 25.3 | 37.1 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 28.9 | 38.3 | 25.2 | 37 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 28.9 | 38.2 | 25 | 36.9 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 29 | 38.2 | 24.9 | 36.8 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:43 | 1 | 29 | 38.1 | 24.8 | 36.8 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.1 | 38 | 24.6 | 36.7 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.1 | 38 | 24.5 | 36.6 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.2 | 38 | 24.3 | 36.5 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.2 | 37.9 | 24.2 | 36.5 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.3 | 37.8 | 24.1 | 36.5 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:44 | 1 | 29.3 | 37.8 | 24 | 36.4 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.8 | 23.8 | 36.3 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.7 | 23.7 | 36.3 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.6 | 23.6 | 36.3 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.6 | 23.5 | 36.2 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.5 | 23.3 | 36.1 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:45 | 1 | 29.3 | 37.5 | 23.2 | 36 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.3 | 37.4 | 23.1 | 35.9 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.3 | 37.4 | 23 | 35.8 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.3 | 37.3 | 22.9 | 35.7 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.3 | 37.3 | 22.8 | 35.7 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.2 | 37.2 | 22.6 | 35.6 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:46 | 1 | 29.2 | 37.1 | 22.5 | 35.6 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:47 | 1 | 29.2 | 37.1 | 22.4 | 35.5 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:47 | 1 | 29.1 | 37.1 | 22.3 | 35.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:47 | 1 | 29.1 | 37.1 | 22.3 | 35.4 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:47 | 1 | 29.1 | 37 | 22.2 | 35.4 | 23.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:47 | 1 | 29 | 36.9 | 22 | 35.3 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:47 | 1 | 29 | 36.8 | 21.7 | 35.2 | 24.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:47 | 1 | 28.9 | 36.8 | 21.3 | 35.2 | 25.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.9 | 36.7 | 21.1 | 35.1 | 27.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.8 | 36.6 | 20.8 | 35.1 | 28.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.8 | 36.5 | 20.5 | 35.1 | 29.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.7 | 36.4 | 20.2 | 35 | 30 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.6 | 36.3 | 20 | 35 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:48 | 1 | 28.5 | 36.2 | 19.7 | 35 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 28.5 | 36.1 | 19.5 | 35 | 31.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 28.3 | 36.1 | 19.3 | 35 | 31.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 28.2 | 36 | 19 | 35 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 28.1 | 35.9 | 18.9 | 35 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 27.9 | 35.8 | 18.7 | 35.1 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:49 | 1 | 27.8 | 35.7 | 18.5 | 35.1 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:50 | 1 | 27.7 | 35.6 | 18.3 | 35.1 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 20:50 | 1 | 27.6 | 35.4 | 18.1 | 35.1 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:50 | 1 | 27.6 | 35.4 | 18.1 | 35.1 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:50 | 1 | 27.4 | 35.3 | 17.9 | 35.1 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:50 | 1 | 27.2 | 35.2 | 17.7 | 35.1 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:50 | 1 | 27.1 | 35.2 | 18.8 | 35.1 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:50 | 1 | 26.9 | 35.1 | 20.8 | 35.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 26.6 | 35 | 22.9 | 35.1 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 26.2 | 35 | 24.9 | 35.2 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 25.8 | 35 | 26.7 | 35.2 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 25.3 | 35 | 28.2 | 35.2 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 24.8 | 35 | 29.1 | 35.2 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:51 | 1 | 24.2 | 35.1 | 29.9 | 35.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 23.6 | 35.2 | 30.3 | 35.3 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 22.9 | 35.2 | 30.8 | 35.4 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 22.2 | 35.3 | 31 | 35.5 | 36 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 21.5 | 35.4 | 31.3 | 35.5 | 36.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 20.8 | 35.4 | 31.4 | 35.6 | 36.3 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:52 | 1 | 20 | 35.5 | 31.4 | 35.6 | 36.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 20:53 | 1 | 19.9 | 35.5 | 31.5 | 35.6 | 36.5 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 20:53 | 1 | 19.9 | 35.5 | 31.5 | 35.6 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:53 | 1 | 19.3 | 35.6 | 31.5 | 35.7 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:53 | 1 | 18.7 | 35.6 | 31 | 35.7 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:53 | 1 | 18 | 35.7 | 31.1 | 35.8 | 35 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 20:53 | 1 | 17.8 | 35.7 | 31.2 | 35.8 | 35 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 20:53 | 1 | 17.8 | 35.7 | 31.2 | 35.8 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:53 | 1 | 17.5 | 35.8 | 31.3 | 35.9 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:53 | 1 | 17 | 35.9 | 31.4 | 35.9 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:53 | 1 | 16.5 | 35.9 | 31.6 | 36 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 16.2 | 36 | 31.7 | 36 | 35.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 16 | 36.1 | 31.8 | 36.1 | 36.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 15.8 | 36.2 | 31.9 | 36.2 | 36.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 15.8 | 36.3 | 32.1 | 36.3 | 36.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 15.8 | 36.3 | 32.3 | 36.4 | 37 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:54 | 1 | 15.8 | 36.4 | 32.4 | 36.5 | 37.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 16 | 36.5 | 32.6 | 36.5 | 37.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 16.2 | 36.6 | 32.8 | 36.6 | 37.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 16.4 | 36.7 | 33.1 | 36.7 | 37.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 16.7 | 36.7 | 33.5 | 36.7 | 38 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 17 | 36.8 | 33.9 | 36.8 | 38.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:55 | 1 | 17.3 | 36.9 | 34.3 | 36.9 | 38.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 17.6 | 36.9 | 34.7 | 37 | 38.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 17.8 | 37 | 35 | 37.1 | 38.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 18.1 | 37.1 | 35.3 | 37.2 | 38.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 18.5 | 37.2 | 35.6 | 37.3 | 38.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 18.9 | 37.3 | 35.8 | 37.4 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:56 | 1 | 19.2 | 37.4 | 36 | 37.5 | 39.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 19.5 | 37.4 | 36.2 | 37.6 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 19.9 | 37.5 | 36.4 | 37.7 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 20.2 | 37.6 | 36.6 | 37.8 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 20.6 | 37.7 | 36.8 | 37.9 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 20.9 | 37.8 | 36.9 | 38 | 39.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:57 | 1 | 21.3 | 37.9 | 37.1 | 38.1 | 39.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:58 | 1 | 21.6 | 38 | 37.3 | 38.2 | 39.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:58 | 1 | 21.9 | 38.1 | 37.4 | 38.3 | 39.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 20:58 | 1 | 22 | 38.1 | 37.4 | 38.3 | 39.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:58 | 1 | 22.3 | 38.2 | 37.5 | 38.4 | 39.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:58 | 1 | 22.6 | 38.3 | 36.8 | 38.5 | 39.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:58 | 1 | 23 | 38.4 | 34.9 | 38.6 | 37.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:58 | 1 | 23.3 | 38.4 | 33.1 | 38.6 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 23.7 | 38.4 | 31.8 | 38.6 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 23.9 | 38.4 | 30.8 | 38.6 | 33 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 24.3 | 38.4 | 30.2 | 38.6 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 24.6 | 38.4 | 29.8 | 38.6 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 24.9 | 38.4 | 29.6 | 38.6 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 20:59 | 1 | 25.2 | 38.5 | 29.6 | 38.5 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 25.6 | 38.5 | 29.7 | 38.4 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 25.9 | 38.5 | 29.7 | 38.4 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 26.1 | 38.5 | 29.4 | 38.3 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 26.4 | 38.5 | 29.2 | 38.2 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 26.7 | 38.5 | 29 | 38.2 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:00 | 1 | 27 | 38.5 | 28.7 | 38.1 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 27.2 | 38.5 | 28.5 | 38.1 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 27.4 | 38.5 | 28.2 | 38 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 27.7 | 38.5 | 27.9 | 37.9 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 27.8 | 38.5 | 27.6 | 37.9 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 28.1 | 38.5 | 27.4 | 37.8 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:01 | 1 | 28.3 | 38.5 | 27.1 | 37.8 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 28.5 | 38.5 | 26.9 | 37.7 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 28.5 | 38.5 | 26.6 | 37.6 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 28.6 | 38.4 | 26.4 | 37.5 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 28.8 | 38.4 | 26.2 | 37.5 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 28.9 | 38.4 | 26 | 37.4 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:02 | 1 | 29 | 38.4 | 25.8 | 37.3 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.1 | 38.3 | 25.6 | 37.3 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.2 | 38.3 | 25.4 | 37.2 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.3 | 38.2 | 25.2 | 37.1 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.4 | 38.2 | 25 | 37 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.4 | 38.1 | 24.9 | 36.9 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:03 | 1 | 29.4 | 38.1 | 24.7 | 36.8 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.4 | 38 | 24.5 | 36.7 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.5 | 38 | 24.3 | 36.6 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.5 | 37.9 | 24.2 | 36.6 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.5 | 37.9 | 24 | 36.5 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.5 | 37.8 | 23.9 | 36.4 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:04 | 1 | 29.6 | 37.7 | 23.8 | 36.3 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.6 | 37.7 | 23.6 | 36.2 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.6 | 37.6 | 23.4 | 36.1 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.6 | 37.6 | 23.2 | 36.1 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.5 | 37.5 | 23.1 | 36 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.5 | 37.5 | 22.9 | 35.9 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:05 | 1 | 29.5 | 37.4 | 22.8 | 35.8 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:06 | 1 | 29.5 | 37.3 | 22.7 | 35.7 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:06 | 1 | 29.4 | 37.3 | 22.6 | 35.6 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:06 | 1 | 29.4 | 37.2 | 22.4 | 35.6 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:06 | 1 | 29.4 | 37.2 | 22.3 | 35.5 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:06 | 1 | 29.3 | 37.2 | 22.3 | 35.4 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:06 | 1 | 29.3 | 37.1 | 22.2 | 35.4 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:06 | 1 | 29.3 | 37 | 22.1 | 35.3 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 29.2 | 37 | 21.9 | 35.3 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 29.1 | 36.9 | 21.6 | 35.2 | 24.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 29 | 36.8 | 21.3 | 35.1 | 26.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 29 | 36.7 | 21 | 35.1 | 27.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 28.9 | 36.7 | 20.7 | 35 | 28.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:07 | 1 | 28.9 | 36.6 | 20.4 | 35 | 29.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.8 | 36.5 | 20.1 | 35 | 30.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.7 | 36.4 | 19.9 | 35 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.6 | 36.3 | 19.7 | 35 | 31.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.4 | 36.2 | 19.4 | 35 | 31.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.4 | 36.1 | 19.2 | 35 | 32 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:08 | 1 | 28.2 | 36 | 19.1 | 35 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 28.1 | 35.9 | 18.8 | 35 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 28 | 35.8 | 18.6 | 35 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 27.9 | 35.7 | 18.5 | 35 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 27.8 | 35.6 | 18.3 | 35 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 27.6 | 35.5 | 18.1 | 35.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:09 | 1 | 27.5 | 35.4 | 18.1 | 35.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:09 | 1 | 27.4 | 35.4 | 17.9 | 35.1 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 27.3 | 35.2 | 17.6 | 35.1 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 27.1 | 35.2 | 18.2 | 35.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 26.9 | 35.1 | 20.1 | 35.1 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 26.7 | 35 | 22.2 | 35.1 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 26.3 | 35 | 24.3 | 35.1 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:10 | 1 | 25.9 | 35 | 26.2 | 35.2 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 25.4 | 35 | 27.7 | 35.2 | 35 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 24.9 | 35 | 28.8 | 35.2 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 24.4 | 35 | 29.6 | 35.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 23.7 | 35.1 | 30.2 | 35.4 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 23.1 | 35.2 | 30.7 | 35.4 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:11 | 1 | 22.4 | 35.3 | 31 | 35.5 | 36 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:12 | 1 | 21.7 | 35.3 | 31.2 | 35.5 | 36.2 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:12 | 1 | 21 | 35.4 | 31.3 | 35.6 | 36.3 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:12 | 1 | 20.2 | 35.5 | 31.5 | 35.6 | 36.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:12 | 1 | 19.9 | 35.5 | 31.5 | 35.7 | 36.6 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 21:12 | 1 | 19.9 | 35.5 | 31.5 | 35.7 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:12 | 1 | 19.5 | 35.6 | 31.5 | 35.7 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:12 | 1 | 18.9 | 35.6 | 31.1 | 35.8 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:12 | 1 | 18.1 | 35.7 | 31.1 | 35.8 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:13 | 1 | 17.9 | 35.7 | 31.2 | 35.8 | 35.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 17.9 | 35.7 | 31.2 | 35.8 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 17.7 | 35.7 | 31.3 | 35.9 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 17.1 | 35.8 | 31.4 | 35.9 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 16.7 | 35.9 | 31.6 | 36 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 16.3 | 36 | 31.7 | 36.1 | 35.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 16 | 36.1 | 31.8 | 36.2 | 36.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:13 | 1 | 15.8 | 36.1 | 31.9 | 36.2 | 36.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 15.8 | 36.2 | 32 | 36.3 | 36.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 15.8 | 36.3 | 32.1 | 36.4 | 36.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 15.8 | 36.4 | 32.2 | 36.5 | 37.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 15.9 | 36.5 | 32.4 | 36.6 | 37.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 16.1 | 36.6 | 32.5 | 36.6 | 37.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:14 | 1 | 16.3 | 36.6 | 32.7 | 36.7 | 37.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 16.5 | 36.7 | 32.9 | 36.8 | 38 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 16.8 | 36.7 | 33.3 | 36.9 | 38.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 17.1 | 36.8 | 33.6 | 36.9 | 38.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 17.5 | 36.9 | 34 | 37 | 38.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 17.7 | 36.9 | 34.4 | 37.1 | 38.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:15 | 1 | 18 | 37 | 34.7 | 37.2 | 38.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 18.3 | 37.1 | 34.9 | 37.3 | 38.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 18.7 | 37.2 | 35.2 | 37.4 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 19 | 37.3 | 35.4 | 37.5 | 39 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 19.3 | 37.3 | 35.7 | 37.6 | 39.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 19.8 | 37.4 | 35.9 | 37.7 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:16 | 1 | 20.1 | 37.5 | 36.1 | 37.8 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 20.4 | 37.6 | 36.3 | 37.8 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 20.8 | 37.7 | 36.5 | 37.9 | 39.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 21.1 | 37.8 | 36.7 | 38 | 39.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 21.5 | 37.9 | 36.9 | 38.1 | 39.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 21.8 | 38 | 37 | 38.2 | 39.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:17 | 1 | 22 | 38 | 37.1 | 38.3 | 39.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:17 | 1 | 22.1 | 38 | 37.2 | 38.3 | 39.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 22.5 | 38.1 | 36.9 | 38.4 | 39.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 22.9 | 38.2 | 35.3 | 38.5 | 38.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 23.2 | 38.2 | 33.4 | 38.5 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 23.5 | 38.2 | 32.1 | 38.6 | 35 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 23.8 | 38.3 | 31 | 38.6 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:18 | 1 | 24.1 | 38.3 | 30.3 | 38.6 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 24.5 | 38.3 | 29.9 | 38.6 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 24.8 | 38.3 | 29.7 | 38.5 | 30.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 25.1 | 38.3 | 29.7 | 38.5 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 25.4 | 38.3 | 29.8 | 38.5 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 25.7 | 38.4 | 29.8 | 38.4 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:19 | 1 | 26 | 38.4 | 29.5 | 38.3 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 26.3 | 38.4 | 29.2 | 38.2 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 26.5 | 38.4 | 28.9 | 38.1 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 26.8 | 38.4 | 28.7 | 38.1 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 27 | 38.4 | 28.5 | 38 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 27.3 | 38.4 | 28.1 | 37.9 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:20 | 1 | 27.5 | 38.4 | 27.8 | 37.8 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 27.7 | 38.4 | 27.5 | 37.7 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 28 | 38.4 | 27.1 | 37.7 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 28.1 | 38.4 | 26.8 | 37.6 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 28.3 | 38.4 | 26.5 | 37.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 28.5 | 38.4 | 26.3 | 37.4 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:21 | 1 | 28.6 | 38.4 | 26.1 | 37.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 28.8 | 38.4 | 25.9 | 37.2 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 28.9 | 38.3 | 25.8 | 37.2 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 29 | 38.3 | 25.6 | 37.1 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 29.2 | 38.3 | 25.5 | 37.1 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 29.3 | 38.2 | 25.3 | 37 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:22 | 1 | 29.4 | 38.2 | 25.1 | 37 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.5 | 38.2 | 25 | 36.9 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.6 | 38.1 | 24.8 | 36.8 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.7 | 38.1 | 24.7 | 36.8 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.8 | 38 | 24.6 | 36.7 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.8 | 38 | 24.4 | 36.7 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:23 | 1 | 29.9 | 37.9 | 24.3 | 36.6 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 29.9 | 37.9 | 24.1 | 36.5 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 29.9 | 37.8 | 24 | 36.4 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 29.9 | 37.8 | 23.8 | 36.3 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 30 | 37.7 | 23.7 | 36.3 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 30 | 37.7 | 23.5 | 36.2 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:24 | 1 | 30 | 37.6 | 23.4 | 36.1 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.5 | 23.3 | 36.1 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.5 | 23.1 | 36 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.5 | 23 | 35.9 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.4 | 22.8 | 35.9 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.3 | 22.7 | 35.8 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:25 | 1 | 30 | 37.3 | 22.6 | 35.7 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:26 | 1 | 30 | 37.2 | 22.5 | 35.6 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:26 | 1 | 29.9 | 37.1 | 22.4 | 35.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:26 | 1 | 29.9 | 37.1 | 22.3 | 35.5 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:26 | 1 | 29.9 | 37.1 | 22.3 | 35.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:26 | 1 | 29.8 | 37.1 | 22.2 | 35.4 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:26 | 1 | 29.7 | 37 | 22.1 | 35.3 | 23.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:26 | 1 | 29.7 | 36.9 | 21.8 | 35.2 | 24 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.7 | 36.8 | 21.5 | 35.2 | 25.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.6 | 36.8 | 21.1 | 35.2 | 26.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.5 | 36.7 | 20.8 | 35.1 | 27.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.5 | 36.6 | 20.6 | 35.1 | 28.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.4 | 36.5 | 20.3 | 35.1 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:27 | 1 | 29.3 | 36.4 | 20.1 | 35.1 | 30.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 29.2 | 36.3 | 19.8 | 35.1 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 29.1 | 36.2 | 19.5 | 35.1 | 31.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 29 | 36.1 | 19.4 | 35.1 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 28.9 | 36 | 19.1 | 35.1 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 28.7 | 36 | 18.9 | 35.1 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:28 | 1 | 28.7 | 35.9 | 18.7 | 35.1 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:29 | 1 | 28.5 | 35.8 | 18.5 | 35.1 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:29 | 1 | 28.5 | 35.6 | 18.4 | 35.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:29 | 1 | 28.3 | 35.5 | 18.3 | 35.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:29 | 1 | 28.2 | 35.4 | 18.1 | 35.1 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:29 | 1 | 28.2 | 35.4 | 18.1 | 35.1 | 33.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:29 | 1 | 28.1 | 35.3 | 17.7 | 35.1 | 33.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:29 | 1 | 27.9 | 35.2 | 17.7 | 35.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 27.8 | 35.1 | 19.1 | 35.1 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 27.5 | 35 | 21.1 | 35.1 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 27.2 | 35 | 23.3 | 35.2 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 26.9 | 35 | 25.2 | 35.2 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 26.5 | 35 | 27 | 35.2 | 35 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:30 | 1 | 25.9 | 35 | 28.3 | 35.2 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 25.4 | 35 | 29.2 | 35.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 24.9 | 35.1 | 29.9 | 35.3 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 24.2 | 35.2 | 30.4 | 35.4 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 23.5 | 35.2 | 30.8 | 35.5 | 36 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 22.9 | 35.3 | 31 | 35.5 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:31 | 1 | 22.2 | 35.4 | 31.3 | 35.6 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:32 | 1 | 21.5 | 35.5 | 31.4 | 35.6 | 36.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:32 | 1 | 20.8 | 35.5 | 31.4 | 35.7 | 36.6 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:32 | 1 | 20.1 | 35.6 | 31.5 | 35.8 | 36.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:32 | 1 | 19.9 | 35.6 | 31.6 | 35.8 | 36.8 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 21:32 | 1 | 19.9 | 35.6 | 31.6 | 35.8 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:32 | 1 | 19.5 | 35.7 | 31.6 | 35.8 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:32 | 1 | 18.8 | 35.7 | 31.2 | 35.9 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:32 | 1 | 18.2 | 35.8 | 31.3 | 36 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:33 | 1 | 18 | 35.8 | 31.3 | 36 | 35.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 18 | 35.8 | 31.3 | 36 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 17.7 | 35.9 | 31.4 | 36 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 17.3 | 35.9 | 31.5 | 36.1 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 16.9 | 36 | 31.6 | 36.1 | 35.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 16.7 | 36.1 | 31.7 | 36.2 | 36.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 16.5 | 36.2 | 31.9 | 36.3 | 36.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:33 | 1 | 16.5 | 36.3 | 32 | 36.4 | 36.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 16.5 | 36.3 | 32.1 | 36.5 | 37 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 16.6 | 36.4 | 32.3 | 36.5 | 37.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 16.8 | 36.5 | 32.5 | 36.7 | 37.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 17.1 | 36.6 | 32.7 | 36.7 | 37.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 17.4 | 36.7 | 32.9 | 36.8 | 37.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:34 | 1 | 17.7 | 36.7 | 33.3 | 36.9 | 38.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 18 | 36.8 | 33.6 | 37 | 38.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 18.3 | 36.8 | 33.8 | 37.1 | 38.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 18.7 | 36.9 | 34.1 | 37.1 | 38.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 19.1 | 37 | 34.3 | 37.2 | 38.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 19.5 | 37.1 | 34.6 | 37.3 | 38.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:35 | 1 | 19.9 | 37.1 | 34.8 | 37.4 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:36 | 1 | 20.4 | 37.2 | 35 | 37.5 | 39 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:36 | 1 | 20.7 | 37.3 | 35.3 | 37.6 | 39.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:36 | 1 | 21.2 | 37.4 | 35.5 | 37.7 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:36 | 1 | 21.6 | 37.4 | 35.7 | 37.8 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:36 | 1 | 22 | 37.5 | 35.9 | 37.8 | 39.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 21:36 | 1 | 22 | 37.5 | 35.9 | 37.9 | 39.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 21:36 | 1 | 22.2 | 37.6 | 36 | 37.9 | 39.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:36 | 1 | 22.5 | 37.6 | 36 | 37.9 | 39.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 22.8 | 37.7 | 35 | 38 | 38.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 23.3 | 37.8 | 33.5 | 38.1 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 23.6 | 37.8 | 32 | 38.1 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 24 | 37.8 | 31.2 | 38.1 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 24.3 | 37.8 | 30.7 | 38.1 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:37 | 1 | 24.7 | 37.9 | 30.6 | 38.1 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 25 | 37.9 | 30.4 | 38.1 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 25.3 | 37.9 | 30.1 | 38.1 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 25.6 | 37.9 | 29.7 | 38.1 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 25.9 | 38 | 29.3 | 38 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 26.2 | 38 | 29 | 37.9 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:38 | 1 | 26.5 | 38 | 28.8 | 37.9 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 26.7 | 38.1 | 28.6 | 37.8 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 27 | 38.1 | 28.4 | 37.8 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 27.3 | 38.1 | 28.1 | 37.7 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 27.5 | 38.1 | 27.8 | 37.6 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 27.7 | 38.1 | 27.4 | 37.5 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:39 | 1 | 28 | 38.1 | 27.1 | 37.4 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.1 | 38.1 | 26.8 | 37.3 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.3 | 38.1 | 26.5 | 37.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.5 | 38.1 | 26.2 | 37.2 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.5 | 38.1 | 26 | 37.1 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.6 | 38 | 25.7 | 37 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:40 | 1 | 28.7 | 38 | 25.5 | 36.9 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 28.9 | 38 | 25.4 | 36.8 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 29 | 38 | 25.3 | 36.7 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 29 | 37.9 | 25.1 | 36.6 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 29.1 | 37.9 | 25 | 36.6 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 29.1 | 37.9 | 24.8 | 36.6 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:41 | 1 | 29.2 | 37.8 | 24.6 | 36.5 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.2 | 37.8 | 24.4 | 36.4 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.3 | 37.7 | 24.3 | 36.4 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.3 | 37.7 | 24.2 | 36.4 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.3 | 37.7 | 24.1 | 36.3 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.4 | 37.6 | 23.9 | 36.3 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:42 | 1 | 29.4 | 37.5 | 23.8 | 36.1 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.5 | 23.6 | 36.1 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.5 | 23.4 | 36 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.4 | 23.3 | 35.9 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.3 | 23.2 | 35.9 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.3 | 23 | 35.8 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:43 | 1 | 29.4 | 37.3 | 22.9 | 35.7 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:44 | 1 | 29.4 | 37.2 | 22.8 | 35.7 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:44 | 1 | 29.4 | 37.1 | 22.6 | 35.6 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:44 | 1 | 29.3 | 37.1 | 22.5 | 35.5 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:44 | 1 | 29.3 | 37.1 | 22.4 | 35.5 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:44 | 1 | 29.3 | 37.1 | 22.4 | 35.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:44 | 1 | 29.3 | 37 | 22.3 | 35.4 | 23.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:44 | 1 | 29.3 | 36.9 | 22.2 | 35.3 | 23.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 29.2 | 36.9 | 21.9 | 35.2 | 24 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 29.2 | 36.8 | 21.6 | 35.1 | 25.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 29.1 | 36.7 | 21.3 | 35.1 | 26.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 29.1 | 36.7 | 20.9 | 35.1 | 27.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 29 | 36.6 | 20.7 | 35 | 28.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:45 | 1 | 28.9 | 36.5 | 20.4 | 35 | 29.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.8 | 36.4 | 20.1 | 35 | 30.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.7 | 36.3 | 19.8 | 35 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.6 | 36.3 | 19.5 | 35 | 31.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.5 | 36.2 | 19.4 | 35 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.4 | 36.1 | 19.1 | 35 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:46 | 1 | 28.4 | 36 | 18.9 | 35 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:47 | 1 | 28.3 | 35.8 | 18.7 | 35 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:47 | 1 | 28.2 | 35.7 | 18.5 | 35 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:47 | 1 | 28.1 | 35.6 | 18.3 | 35 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:47 | 1 | 27.9 | 35.5 | 18.1 | 35 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 21:47 | 1 | 27.9 | 35.4 | 18 | 35 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:47 | 1 | 27.8 | 35.4 | 18 | 35 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:47 | 1 | 27.6 | 35.3 | 17.6 | 35.1 | 34 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 27.5 | 35.2 | 17.9 | 35.1 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 27.3 | 35.1 | 19.7 | 35.1 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 27.1 | 35 | 21.7 | 35.1 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 26.8 | 35 | 23.9 | 35.1 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 26.4 | 35 | 25.7 | 35.1 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:48 | 1 | 25.9 | 35 | 27.4 | 35.2 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 25.4 | 35 | 28.5 | 35.2 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 24.8 | 35 | 29.4 | 35.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 24.2 | 35.1 | 30.1 | 35.4 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 23.6 | 35.2 | 30.5 | 35.4 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 23 | 35.3 | 30.9 | 35.4 | 36 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:49 | 1 | 22.2 | 35.3 | 31.1 | 35.5 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:50 | 1 | 21.6 | 35.4 | 31.3 | 35.5 | 36.4 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:50 | 1 | 20.9 | 35.5 | 31.4 | 35.7 | 36.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:50 | 1 | 20.1 | 35.6 | 31.5 | 35.7 | 36.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 21:50 | 1 | 19.9 | 35.6 | 31.5 | 35.7 | 36.8 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 21:50 | 1 | 19.9 | 35.6 | 31.5 | 35.7 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:50 | 1 | 19.5 | 35.6 | 31.5 | 35.8 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:50 | 1 | 18.8 | 35.7 | 31.1 | 35.8 | 36 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:50 | 1 | 18.2 | 35.8 | 31.1 | 35.8 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 21:51 | 1 | 17.9 | 35.8 | 31.2 | 35.9 | 35.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 17.9 | 35.8 | 31.2 | 35.9 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 17.7 | 35.9 | 31.3 | 35.9 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 17.3 | 35.9 | 31.5 | 36 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 16.9 | 36 | 31.6 | 36.1 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 16.6 | 36.1 | 31.6 | 36.1 | 35.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 16.4 | 36.1 | 31.7 | 36.2 | 36 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:51 | 1 | 16.4 | 36.2 | 31.9 | 36.3 | 36.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 16.4 | 36.3 | 32 | 36.3 | 36.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 16.5 | 36.4 | 32.1 | 36.4 | 37 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 16.6 | 36.5 | 32.2 | 36.5 | 37.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 16.9 | 36.6 | 32.4 | 36.6 | 37.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 17.1 | 36.6 | 32.6 | 36.6 | 37.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:52 | 1 | 17.4 | 36.7 | 32.9 | 36.7 | 37.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 17.7 | 36.7 | 33.1 | 36.8 | 38.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 18 | 36.8 | 33.4 | 36.9 | 38.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 18.4 | 36.8 | 33.7 | 37 | 38.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 18.7 | 36.9 | 34 | 37.1 | 38.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 19.1 | 37 | 34.2 | 37.1 | 38.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:53 | 1 | 19.5 | 37.1 | 34.4 | 37.2 | 38.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 19.9 | 37.1 | 34.6 | 37.3 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 20.3 | 37.2 | 34.8 | 37.4 | 39 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 20.7 | 37.3 | 35 | 37.5 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 21.1 | 37.4 | 35.1 | 37.6 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 21.4 | 37.5 | 35.3 | 37.7 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:54 | 1 | 21.9 | 37.5 | 35.5 | 37.8 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 21:55 | 1 | 22 | 37.6 | 35.6 | 37.8 | 39.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 22.3 | 37.6 | 35.7 | 37.9 | 39.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 22.7 | 37.7 | 35.3 | 38 | 39.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 23 | 37.7 | 33.9 | 38 | 38.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 23.4 | 37.8 | 32.3 | 38.1 | 36.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 23.7 | 37.8 | 31.3 | 38.1 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:55 | 1 | 24.1 | 37.8 | 30.8 | 38.1 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 24.4 | 37.8 | 30.7 | 38.1 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 24.7 | 37.9 | 30.5 | 38.1 | 30.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 25 | 37.9 | 30.2 | 38.1 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 25.3 | 37.9 | 29.8 | 38 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 25.6 | 38 | 29.4 | 38 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:56 | 1 | 25.9 | 38 | 29.1 | 38 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 26.1 | 38 | 28.8 | 37.9 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 26.4 | 38.1 | 28.6 | 37.8 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 26.6 | 38.1 | 28.4 | 37.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 26.9 | 38.1 | 28.1 | 37.7 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 27.2 | 38.1 | 27.8 | 37.6 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:57 | 1 | 27.3 | 38.1 | 27.5 | 37.5 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 27.6 | 38.1 | 27.1 | 37.4 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 27.8 | 38.1 | 26.9 | 37.3 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 27.9 | 38.1 | 26.6 | 37.2 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 28.1 | 38.1 | 26.3 | 37.1 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 28.3 | 38 | 26.2 | 37.1 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:58 | 1 | 28.4 | 38 | 26 | 37 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.4 | 38 | 25.8 | 37 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.5 | 38 | 25.6 | 37 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.7 | 38 | 25.4 | 36.9 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.8 | 37.9 | 25.2 | 36.8 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.9 | 37.9 | 25.1 | 36.8 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 21:59 | 1 | 28.9 | 37.9 | 24.8 | 36.7 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29 | 37.8 | 24.7 | 36.7 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29.1 | 37.8 | 24.5 | 36.6 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29.1 | 37.7 | 24.4 | 36.5 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29.1 | 37.7 | 24.2 | 36.4 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29.1 | 37.7 | 24.1 | 36.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:00 | 1 | 29.1 | 37.6 | 23.9 | 36.3 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.5 | 23.7 | 36.2 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.5 | 23.5 | 36.1 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.5 | 23.4 | 36 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.4 | 23.3 | 35.9 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.3 | 23.1 | 35.9 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:01 | 1 | 29.2 | 37.3 | 23 | 35.8 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.2 | 37.2 | 22.8 | 35.7 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.2 | 37.2 | 22.7 | 35.7 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.1 | 37.1 | 22.6 | 35.6 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.1 | 37.1 | 22.4 | 35.5 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.1 | 37 | 22.3 | 35.5 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:02 | 1 | 29.1 | 37 | 22.3 | 35.4 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:02 | 1 | 29.1 | 37 | 22.2 | 35.4 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 29 | 36.9 | 22.1 | 35.3 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 29 | 36.9 | 21.8 | 35.2 | 23.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 28.9 | 36.8 | 21.5 | 35.1 | 25 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 28.9 | 36.7 | 21.2 | 35 | 26.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 28.8 | 36.6 | 20.9 | 35 | 27.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:03 | 1 | 28.8 | 36.5 | 20.6 | 35 | 28.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.7 | 36.5 | 20.3 | 35 | 29.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.6 | 36.4 | 20.1 | 34.9 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.5 | 36.3 | 19.8 | 34.9 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.5 | 36.2 | 19.6 | 34.9 | 31.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.4 | 36.1 | 19.4 | 34.9 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:04 | 1 | 28.3 | 36 | 19.1 | 34.9 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 28.2 | 35.9 | 18.9 | 34.9 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 28.1 | 35.8 | 18.7 | 35 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 27.9 | 35.7 | 18.5 | 35 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 27.8 | 35.6 | 18.3 | 35 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 27.7 | 35.5 | 18.2 | 35 | 33.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-07 22:05 | 1 | 27.6 | 35.4 | 18.1 | 35 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:05 | 1 | 27.5 | 35.4 | 18 | 35 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 27.4 | 35.3 | 17.6 | 35 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 27.3 | 35.2 | 17.8 | 35 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 27.1 | 35.1 | 19.5 | 35 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 26.9 | 35 | 21.5 | 35.1 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 26.6 | 35 | 23.6 | 35.1 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:06 | 1 | 26.2 | 35 | 25.6 | 35.1 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 25.8 | 35 | 27.1 | 35.2 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 25.3 | 35 | 28.4 | 35.2 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 24.7 | 35 | 29.3 | 35.3 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 24.1 | 35 | 30 | 35.3 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 23.5 | 35.1 | 30.5 | 35.4 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:07 | 1 | 22.8 | 35.2 | 30.8 | 35.5 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:08 | 1 | 22 | 35.3 | 31.1 | 35.5 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:08 | 1 | 21.4 | 35.3 | 31.2 | 35.6 | 36.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:08 | 1 | 20.7 | 35.5 | 31.4 | 35.6 | 36.6 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:08 | 1 | 20 | 35.5 | 31.5 | 35.7 | 36.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-07 22:08 | 1 | 19.9 | 35.5 | 31.5 | 35.7 | 36.8 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-07 22:08 | 1 | 19.9 | 35.5 | 31.5 | 35.7 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 22:08 | 1 | 19.3 | 35.6 | 31.5 | 35.8 | 36.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 22:08 | 1 | 18.6 | 35.7 | 31 | 35.8 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 22:09 | 1 | 18 | 35.8 | 31.2 | 35.9 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-07 22:09 | 1 | 17.9 | 35.8 | 31.2 | 35.9 | 35.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 17.9 | 35.8 | 31.2 | 35.9 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 17.6 | 35.8 | 31.3 | 35.9 | 35.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 17.2 | 35.9 | 31.4 | 36 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 16.8 | 36 | 31.5 | 36.1 | 35.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 16.5 | 36.1 | 31.6 | 36.1 | 35.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:09 | 1 | 16.4 | 36.2 | 31.7 | 36.2 | 36.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 16.3 | 36.2 | 31.8 | 36.3 | 36.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 16.3 | 36.3 | 32 | 36.4 | 36.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 16.4 | 36.4 | 32.1 | 36.5 | 37.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 16.6 | 36.4 | 32.2 | 36.5 | 37.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 16.8 | 36.5 | 32.4 | 36.6 | 37.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:10 | 1 | 17.1 | 36.6 | 32.7 | 36.7 | 37.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 17.4 | 36.7 | 32.8 | 36.8 | 38 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 17.7 | 36.7 | 33.1 | 36.8 | 38.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 18 | 36.8 | 33.3 | 36.9 | 38.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 18.3 | 36.8 | 33.6 | 37 | 38.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 18.7 | 36.9 | 33.9 | 37.1 | 38.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:11 | 1 | 19.1 | 37 | 34.1 | 37.1 | 38.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 19.5 | 37 | 34.3 | 37.2 | 38.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 19.9 | 37.1 | 34.5 | 37.3 | 39 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 20.3 | 37.2 | 34.6 | 37.4 | 39.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 20.7 | 37.2 | 34.8 | 37.5 | 39.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 21.1 | 37.3 | 34.9 | 37.6 | 39.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:12 | 1 | 21.5 | 37.4 | 35.1 | 37.7 | 39.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:13 | 1 | 21.9 | 37.5 | 35.3 | 37.8 | 39.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:13 | 1 | 21.9 | 37.5 | 35.3 | 37.8 | 39.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-07 22:13 | 1 | 22 | 37.5 | 35.3 | 37.8 | 39.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-07 22:13 | 1 | 22.2 | 37.6 | 35.4 | 37.9 | 39.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 22.3 | 37.6 | 35.4 | 37.9 | 39.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 22.6 | 37.7 | 35 | 38 | 39.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 22.7 | 37.7 | 34.7 | 38.1 | 39.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 23 | 38.1 | 33.8 | 38.2 | 39.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 23.4 | 38.4 | 32.6 | 38.5 | 38.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:13 | 1 | 23.8 | 38.5 | 31.7 | 38.8 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 24.1 | 38.6 | 31.1 | 39 | 35.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 24.4 | 38.6 | 30.9 | 39.1 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 24.6 | 38.6 | 30.8 | 39.1 | 33.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 24.9 | 38.6 | 30.8 | 39.2 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 25 | 38.6 | 30.8 | 39.2 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 25.3 | 38.6 | 30.8 | 39.2 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:14 | 1 | 25.5 | 38.7 | 30.8 | 39.3 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 25.9 | 38.9 | 30.7 | 39.4 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 26.1 | 39.1 | 30.7 | 39.6 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 26.4 | 39.3 | 30.7 | 39.7 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 26.4 | 39.4 | 30.7 | 39.8 | 33.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 26.7 | 39.6 | 30.7 | 40 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 27 | 39.7 | 30.7 | 40.3 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:15 | 1 | 27.2 | 39.8 | 30.7 | 40.5 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 27.5 | 39.9 | 30.6 | 40.7 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 27.5 | 39.9 | 30.6 | 40.7 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 27.8 | 39.9 | 30.5 | 40.9 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 27.9 | 39.9 | 30.5 | 40.9 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28 | 39.9 | 30.5 | 40.9 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28.1 | 40 | 30.5 | 41 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28.3 | 40 | 30.5 | 41.1 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28.4 | 40 | 30.5 | 41.2 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28.5 | 40.1 | 30.5 | 41.2 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:16 | 1 | 28.6 | 40.3 | 30.6 | 41.4 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 28.8 | 40.4 | 30.6 | 41.6 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.1 | 40.4 | 30.6 | 41.8 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.2 | 40.4 | 30.6 | 41.9 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.4 | 40.4 | 30.5 | 41.9 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.4 | 40.4 | 30.4 | 41.9 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.6 | 40.4 | 30.4 | 41.9 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:17 | 1 | 29.8 | 40.4 | 30.3 | 42 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 29.9 | 40.5 | 30.3 | 42 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 29.9 | 40.5 | 30.2 | 42 | 35 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.1 | 40.6 | 30.2 | 42.2 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.2 | 40.7 | 30.3 | 42.3 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.4 | 40.8 | 30.3 | 42.4 | 35.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.5 | 40.8 | 30.3 | 42.5 | 35.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.6 | 40.8 | 30.3 | 42.5 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:18 | 1 | 30.6 | 40.8 | 30.3 | 42.5 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 30.8 | 40.8 | 30.2 | 42.5 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 30.9 | 40.8 | 30.2 | 42.6 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 30.9 | 40.9 | 30.2 | 42.7 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 30.9 | 41 | 30.2 | 42.7 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 31 | 41.2 | 30.3 | 42.9 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 31.2 | 41.2 | 30.4 | 43 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:19 | 1 | 31.3 | 41.3 | 30.4 | 43 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.3 | 41.3 | 30.5 | 43 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.4 | 41.3 | 30.5 | 43 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.4 | 41.3 | 30.5 | 43.1 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.5 | 41.3 | 30.5 | 43.1 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.5 | 41.3 | 30.5 | 43.1 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.6 | 41.5 | 30.5 | 43.2 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.6 | 41.5 | 30.5 | 43.2 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.6 | 41.6 | 30.5 | 43.2 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.6 | 41.6 | 30.5 | 43.2 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:20 | 1 | 31.7 | 41.6 | 30.5 | 43.3 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 31.7 | 41.7 | 30.5 | 43.3 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 31.8 | 41.7 | 30.6 | 43.5 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 31.9 | 41.9 | 30.7 | 44.1 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 31.9 | 42.1 | 30.7 | 44.6 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 31.9 | 42.3 | 30.8 | 45.1 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 32 | 42.7 | 31 | 45.8 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 32.1 | 42.9 | 31.1 | 46.1 | 36 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:21 | 1 | 32.2 | 42.9 | 31.1 | 46.2 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.2 | 42.9 | 31.1 | 46.2 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.2 | 42.9 | 31.1 | 46.2 | 36.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.3 | 42.9 | 31.1 | 46.5 | 36.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.3 | 43.1 | 31.2 | 47.3 | 36.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.4 | 43.3 | 31.2 | 47.7 | 36.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.4 | 43.4 | 31.3 | 48.2 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.5 | 43.6 | 31.4 | 48.7 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:22 | 1 | 32.5 | 43.7 | 31.5 | 48.8 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.6 | 43.7 | 31.5 | 48.8 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.6 | 43.7 | 31.5 | 48.7 | 37.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.7 | 43.7 | 31.5 | 48.6 | 37.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.8 | 43.7 | 31.5 | 49 | 37.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.8 | 43.8 | 31.6 | 49.5 | 37.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.9 | 43.9 | 31.6 | 49.8 | 37.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 32.9 | 43.9 | 31.7 | 50 | 37.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:23 | 1 | 33 | 44.1 | 31.8 | 50.2 | 37.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33 | 44.1 | 31.8 | 50.2 | 37.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.1 | 44.1 | 31.8 | 49.9 | 37.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.2 | 44.1 | 31.9 | 49.7 | 37.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.2 | 44.1 | 31.9 | 49.5 | 37.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.2 | 44.1 | 31.9 | 49.3 | 37.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.3 | 44.1 | 31.9 | 49.2 | 37.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:24 | 1 | 33.4 | 44.1 | 31.9 | 49.4 | 37.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.4 | 44.2 | 31.9 | 49.5 | 37.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.4 | 44.2 | 31.9 | 49.5 | 37.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.5 | 44.4 | 31.9 | 49.6 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.5 | 44.4 | 32 | 49.5 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.6 | 44.4 | 32 | 49.3 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.6 | 44.4 | 32 | 49.3 | 37.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.6 | 44.4 | 32 | 49 | 36.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:25 | 1 | 33.7 | 44.4 | 32 | 48.9 | 36.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.7 | 44.5 | 32 | 48.8 | 36.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.8 | 44.6 | 32 | 48.7 | 36.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.8 | 44.7 | 32 | 48.5 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.8 | 44.7 | 32 | 48.5 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.8 | 44.7 | 32 | 48.5 | 36.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.9 | 44.8 | 32.1 | 48.5 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.9 | 44.9 | 32.1 | 48.5 | 36.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:26 | 1 | 33.9 | 44.9 | 32.1 | 48.5 | 36 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34 | 44.9 | 32.1 | 48.5 | 35.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34 | 44.9 | 32.1 | 48.4 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34 | 44.9 | 32.1 | 48.3 | 35.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34.1 | 44.9 | 32.1 | 48.2 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34.2 | 44.9 | 32.1 | 48.2 | 35.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34.2 | 45 | 32.1 | 48.2 | 35.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:27 | 1 | 34.2 | 45 | 32.1 | 48.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.2 | 45 | 32.1 | 48.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.2 | 45 | 32.1 | 48.3 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.2 | 45.2 | 32.1 | 48.3 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.3 | 45.7 | 32.1 | 48.2 | 35.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.3 | 46.2 | 32.1 | 48.2 | 35 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.3 | 46.7 | 32.1 | 48.1 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.3 | 46.7 | 32.1 | 48.1 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:28 | 1 | 34.4 | 47.3 | 32.2 | 48 | 34.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.4 | 47.5 | 32.3 | 47.9 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.4 | 47.6 | 32.3 | 47.9 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.4 | 47.7 | 32.3 | 47.8 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.4 | 47.9 | 32.3 | 47.7 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.4 | 48 | 32.3 | 47.7 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.5 | 48.3 | 32.4 | 47.6 | 34.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.5 | 48.4 | 32.4 | 47.5 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:29 | 1 | 34.5 | 48.3 | 32.4 | 47.4 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.5 | 48.2 | 32.4 | 47.3 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 48 | 32.4 | 47.2 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 48 | 32.4 | 47.2 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 47.9 | 32.4 | 47.1 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 47.9 | 32.4 | 47.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 47.9 | 32.4 | 47.1 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 47.9 | 32.4 | 47 | 34 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 48.7 | 32.4 | 46.9 | 34 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 48.9 | 32.4 | 46.8 | 34 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 48.9 | 32.4 | 46.8 | 34 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:30 | 1 | 34.6 | 49.6 | 32.4 | 46.8 | 33.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.7 | 49.9 | 32.4 | 46.7 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.7 | 49.9 | 32.4 | 46.6 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.7 | 49.8 | 32.4 | 46.5 | 33.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.7 | 49.8 | 32.4 | 46.4 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.7 | 50.3 | 32.4 | 46.3 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.8 | 50.8 | 32.4 | 46.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:31 | 1 | 34.8 | 51 | 32.4 | 46.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 51.3 | 32.4 | 46.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 51.9 | 32.4 | 46.1 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 52.5 | 32.5 | 46.1 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 52.8 | 32.6 | 46 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 52.9 | 32.6 | 46 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 52.9 | 32.6 | 46 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 53 | 32.6 | 46 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 53.1 | 32.6 | 45.9 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 53.1 | 32.6 | 45.9 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 53.1 | 32.7 | 45.9 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 53.1 | 32.7 | 45.9 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:32 | 1 | 34.8 | 52.9 | 32.7 | 45.8 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.6 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.6 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.4 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.4 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.4 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.4 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.3 | 32.7 | 45.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52.1 | 32.7 | 45.6 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 52 | 32.6 | 45.6 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.9 | 32.6 | 45.6 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.9 | 32.6 | 45.5 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.9 | 32.6 | 45.5 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.8 | 32.6 | 45.5 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.8 | 32.6 | 45.5 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.8 | 32.6 | 45.5 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:33 | 1 | 34.9 | 51.6 | 32.5 | 45.4 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 34.9 | 51.4 | 32.5 | 45.4 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 34.9 | 51.2 | 32.4 | 45.3 | 33.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 35 | 51 | 32.3 | 45.3 | 33.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 35 | 50.7 | 32.3 | 45.2 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 35 | 50.5 | 32.2 | 45.1 | 33 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:34 | 1 | 35 | 50.3 | 32.1 | 45.1 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 50.2 | 32 | 45 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 50 | 31.9 | 44.9 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 49.9 | 31.8 | 44.9 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 49.7 | 31.8 | 44.8 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 49.6 | 31.8 | 44.7 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:35 | 1 | 35 | 49.4 | 31.8 | 44.7 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 35 | 49.3 | 31.7 | 44.6 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 35 | 49.2 | 31.6 | 44.6 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 35 | 49 | 31.6 | 44.5 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 35 | 48.9 | 31.5 | 44.4 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 35 | 48.8 | 31.5 | 44.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:36 | 1 | 34.9 | 48.6 | 31.4 | 44.3 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48.6 | 31.4 | 44.2 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48.5 | 31.3 | 44.2 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48.3 | 31.2 | 44.1 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48.2 | 31.2 | 44.1 | 32 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48.1 | 31.2 | 44 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:37 | 1 | 34.9 | 48 | 31.1 | 43.9 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.9 | 31.1 | 43.8 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.8 | 31 | 43.8 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.7 | 31 | 43.7 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.6 | 30.9 | 43.7 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.6 | 30.8 | 43.6 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:38 | 1 | 34.8 | 47.5 | 30.8 | 43.6 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.7 | 47.4 | 30.7 | 43.5 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.7 | 47.3 | 30.6 | 43.5 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.7 | 47.2 | 30.6 | 43.4 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.7 | 47.1 | 30.5 | 43.3 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.7 | 47.1 | 30.5 | 43.3 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:39 | 1 | 34.6 | 47 | 30.4 | 43.3 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.6 | 46.9 | 30.3 | 43.2 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.6 | 46.8 | 30.2 | 43.2 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.6 | 46.7 | 30.1 | 43.1 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.6 | 46.7 | 30 | 43.1 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.5 | 46.6 | 29.8 | 43 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:40 | 1 | 34.5 | 46.5 | 29.7 | 43 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.5 | 46.5 | 29.6 | 42.9 | 30.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.5 | 46.4 | 29.5 | 42.9 | 30.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.4 | 46.3 | 29.4 | 42.9 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.4 | 46.3 | 29.3 | 42.8 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.4 | 46.2 | 29.1 | 42.7 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:41 | 1 | 34.4 | 46.2 | 29 | 42.7 | 30.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.4 | 46.1 | 28.8 | 42.7 | 30.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.3 | 46 | 28.7 | 42.6 | 30.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.3 | 46 | 28.6 | 42.6 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.3 | 45.9 | 28.4 | 42.5 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.2 | 45.9 | 28.4 | 42.5 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:42 | 1 | 34.2 | 45.8 | 28.3 | 42.4 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 34.1 | 45.7 | 28.2 | 42.4 | 30.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 34.1 | 45.7 | 28.1 | 42.3 | 30.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 34.1 | 45.6 | 28 | 42.3 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 34 | 45.5 | 27.8 | 42.3 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 33.9 | 45.5 | 27.7 | 42.2 | 29.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:43 | 1 | 33.9 | 45.4 | 27.6 | 42.2 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.9 | 45.3 | 27.5 | 42.1 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.8 | 45.3 | 27.4 | 42.1 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.8 | 45.2 | 27.3 | 42.1 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.7 | 45.2 | 27.1 | 42 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.6 | 45.1 | 27.1 | 42 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:44 | 1 | 33.6 | 45.1 | 27 | 41.9 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.6 | 45 | 26.9 | 41.9 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.5 | 45 | 26.8 | 41.8 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.5 | 44.9 | 26.7 | 41.8 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.4 | 44.8 | 26.6 | 41.8 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.4 | 44.8 | 26.5 | 41.7 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:45 | 1 | 33.3 | 44.7 | 26.4 | 41.7 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33.3 | 44.6 | 26.3 | 41.6 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33.2 | 44.5 | 26.2 | 41.6 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33.1 | 44.5 | 26.2 | 41.6 | 28.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33.1 | 44.5 | 26.1 | 41.5 | 28.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33.1 | 44.4 | 26 | 41.5 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:46 | 1 | 33 | 44.4 | 25.9 | 41.4 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 33 | 44.3 | 25.8 | 41.4 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 32.9 | 44.2 | 25.8 | 41.4 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 32.9 | 44.2 | 25.7 | 41.3 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 32.8 | 44.1 | 25.6 | 41.3 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 32.7 | 44.1 | 25.6 | 41.3 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:47 | 1 | 32.7 | 44 | 25.5 | 41.2 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.7 | 44 | 25.3 | 41.2 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.6 | 43.9 | 25.3 | 41.2 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.6 | 43.9 | 25.2 | 41.1 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.5 | 43.8 | 25.2 | 41.1 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.5 | 43.8 | 25.2 | 41.1 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:48 | 1 | 32.4 | 43.7 | 25 | 41 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.4 | 43.7 | 25 | 41 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.3 | 43.6 | 24.9 | 41 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.2 | 43.5 | 24.9 | 40.9 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.2 | 43.5 | 24.8 | 40.9 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.2 | 43.5 | 24.7 | 40.9 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:49 | 1 | 32.1 | 43.4 | 24.6 | 40.8 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 32.1 | 43.4 | 24.6 | 40.8 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 32 | 43.3 | 24.6 | 40.8 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 31.9 | 43.3 | 24.5 | 40.7 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 31.9 | 43.2 | 24.4 | 40.7 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 31.8 | 43.2 | 24.4 | 40.7 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:50 | 1 | 31.8 | 43.1 | 24.3 | 40.6 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.7 | 43.1 | 24.2 | 40.6 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.7 | 43 | 24.2 | 40.6 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.7 | 42.9 | 24.1 | 40.5 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.6 | 42.9 | 24 | 40.5 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.5 | 42.9 | 24 | 40.5 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:51 | 1 | 31.5 | 42.8 | 24 | 40.5 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.4 | 42.8 | 23.9 | 40.4 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.4 | 42.8 | 23.8 | 40.4 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.3 | 42.7 | 23.8 | 40.4 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.3 | 42.6 | 23.7 | 40.3 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.2 | 42.6 | 23.7 | 40.3 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:52 | 1 | 31.2 | 42.6 | 23.6 | 40.3 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 31.1 | 42.5 | 23.5 | 40.3 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 31.1 | 42.4 | 23.5 | 40.2 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 31 | 42.4 | 23.5 | 40.2 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 30.9 | 42.4 | 23.4 | 40.2 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 30.9 | 42.3 | 23.3 | 40.1 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:53 | 1 | 30.8 | 42.3 | 23.3 | 40.1 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.8 | 42.2 | 23.2 | 40.1 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.7 | 42.2 | 23.2 | 40.1 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.7 | 42.1 | 23.1 | 40 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.7 | 42 | 23.1 | 40 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.6 | 42 | 23 | 40 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:54 | 1 | 30.6 | 41.9 | 23 | 40 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.5 | 41.9 | 23 | 39.9 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.5 | 41.9 | 22.9 | 39.9 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.4 | 41.8 | 22.9 | 39.9 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.4 | 41.8 | 22.8 | 39.8 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.3 | 41.7 | 22.8 | 39.8 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:55 | 1 | 30.3 | 41.7 | 22.7 | 39.8 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.3 | 41.6 | 22.7 | 39.8 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.2 | 41.6 | 22.7 | 39.7 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.2 | 41.6 | 22.7 | 39.7 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.1 | 41.5 | 22.6 | 39.7 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.1 | 41.4 | 22.6 | 39.7 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:56 | 1 | 30.1 | 41.4 | 22.6 | 39.6 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 30 | 41.4 | 22.6 | 39.6 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 30 | 41.3 | 22.5 | 39.6 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 30 | 41.3 | 22.5 | 39.6 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 29.9 | 41.3 | 22.5 | 39.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 29.9 | 41.2 | 22.4 | 39.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:57 | 1 | 29.8 | 41.2 | 22.4 | 39.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.8 | 41.2 | 22.4 | 39.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.8 | 41.1 | 22.3 | 39.4 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.7 | 41.1 | 22.3 | 39.4 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.7 | 41.1 | 22.3 | 39.4 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.7 | 41 | 22.2 | 39.4 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:58 | 1 | 29.6 | 41 | 22.2 | 39.3 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.6 | 41 | 22.2 | 39.3 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.6 | 40.9 | 22.2 | 39.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.5 | 40.9 | 22.1 | 39.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.5 | 40.9 | 22.1 | 39.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.5 | 40.8 | 22.1 | 39.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 22:59 | 1 | 29.5 | 40.8 | 22 | 39.3 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.4 | 40.8 | 22 | 39.2 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.4 | 40.8 | 22 | 39.2 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.4 | 40.7 | 22 | 39.2 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.3 | 40.7 | 21.9 | 39.2 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.3 | 40.7 | 21.9 | 39.2 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:00 | 1 | 29.3 | 40.6 | 21.9 | 39.1 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.3 | 40.6 | 21.8 | 39.1 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.2 | 40.6 | 21.8 | 39.1 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.2 | 40.5 | 21.8 | 39.1 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.2 | 40.5 | 21.7 | 39.1 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.1 | 40.5 | 21.7 | 39 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:01 | 1 | 29.1 | 40.5 | 21.7 | 39 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29.1 | 40.4 | 21.6 | 39 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29.1 | 40.4 | 21.6 | 39 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29 | 40.4 | 21.5 | 38.9 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29 | 40.3 | 21.5 | 38.9 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29 | 40.3 | 21.5 | 38.9 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:02 | 1 | 29 | 40.3 | 21.4 | 38.9 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.9 | 40.3 | 21.4 | 38.9 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.9 | 40.2 | 21.4 | 38.9 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.9 | 40.2 | 21.4 | 38.8 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.8 | 40.2 | 21.3 | 38.8 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.8 | 40.2 | 21.3 | 38.8 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:03 | 1 | 28.8 | 40.1 | 21.2 | 38.8 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.8 | 40.1 | 21.2 | 38.8 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.7 | 40.1 | 21.2 | 38.7 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.7 | 40.1 | 21.1 | 38.7 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.7 | 40 | 21.1 | 38.7 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.7 | 40 | 21.1 | 38.7 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:04 | 1 | 28.6 | 40 | 21.1 | 38.7 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.6 | 40 | 21 | 38.6 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.6 | 39.9 | 21 | 38.6 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.6 | 39.9 | 21 | 38.6 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.6 | 39.9 | 21 | 38.6 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.6 | 39.9 | 21 | 38.6 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:05 | 1 | 28.7 | 39.8 | 21 | 38.6 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 28.8 | 39.8 | 20.9 | 38.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 28.9 | 39.8 | 20.9 | 38.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 29 | 39.8 | 20.9 | 38.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 29.1 | 39.7 | 20.9 | 38.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 29.2 | 39.7 | 20.9 | 38.5 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:06 | 1 | 29.2 | 39.7 | 20.9 | 38.5 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.3 | 39.7 | 20.8 | 38.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.3 | 39.7 | 20.8 | 38.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.4 | 39.6 | 20.8 | 38.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.4 | 39.6 | 20.8 | 38.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.4 | 39.6 | 20.8 | 38.4 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:07 | 1 | 29.5 | 39.6 | 20.8 | 38.4 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.5 | 39.5 | 20.8 | 38.4 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.5 | 39.5 | 20.8 | 38.3 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.5 | 39.5 | 20.7 | 38.3 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.5 | 39.5 | 20.7 | 38.3 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.5 | 39.5 | 20.7 | 38.3 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:08 | 1 | 29.4 | 39.4 | 20.7 | 38.3 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.4 | 39.4 | 20.7 | 38.3 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.4 | 39.4 | 20.7 | 38.2 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.3 | 39.4 | 20.7 | 38.2 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.3 | 39.4 | 20.7 | 38.2 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.3 | 39.4 | 20.7 | 38.2 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:09 | 1 | 29.2 | 39.3 | 20.7 | 38.2 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 29.2 | 39.3 | 20.7 | 38.2 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 29.1 | 39.3 | 20.7 | 38.2 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 29 | 39.3 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 29 | 39.3 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 29 | 39.3 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:10 | 1 | 28.9 | 39.2 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.9 | 39.3 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.9 | 39.3 | 20.6 | 38.1 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.8 | 39.2 | 20.5 | 38.1 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.8 | 39.2 | 20.5 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.7 | 39.2 | 20.5 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:11 | 1 | 28.7 | 39.2 | 20.4 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.7 | 39.1 | 20.4 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.6 | 39.1 | 20.4 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.6 | 39.1 | 20.3 | 38 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.5 | 39.1 | 20.3 | 38 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.5 | 39 | 20.3 | 38 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:12 | 1 | 28.5 | 39 | 20.2 | 37.9 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.5 | 39 | 20.2 | 37.9 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.5 | 39 | 20.2 | 37.9 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.4 | 39 | 20.2 | 37.9 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.4 | 38.9 | 20.2 | 37.9 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.3 | 38.9 | 20.1 | 37.9 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:13 | 1 | 28.3 | 38.9 | 20.1 | 37.9 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.3 | 38.9 | 20.1 | 37.8 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.2 | 38.9 | 20.1 | 37.8 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.2 | 38.8 | 20.1 | 37.8 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.2 | 38.8 | 20 | 37.8 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.1 | 38.8 | 20 | 37.8 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:14 | 1 | 28.1 | 38.8 | 20 | 37.8 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 28.1 | 38.7 | 20 | 37.8 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 28 | 38.7 | 20 | 37.8 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 28 | 38.7 | 20 | 37.8 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 28 | 38.7 | 19.9 | 37.7 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 27.9 | 38.7 | 19.9 | 37.7 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:15 | 1 | 27.9 | 38.6 | 19.9 | 37.7 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.9 | 38.6 | 19.9 | 37.7 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.9 | 38.6 | 19.9 | 37.7 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.8 | 38.6 | 19.9 | 37.7 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.8 | 38.5 | 19.9 | 37.7 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.8 | 38.5 | 19.9 | 37.6 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:16 | 1 | 27.8 | 38.5 | 19.9 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.8 | 38.5 | 19.9 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.7 | 38.4 | 19.8 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.7 | 38.4 | 19.8 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.7 | 38.4 | 19.8 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.7 | 38.4 | 19.8 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:17 | 1 | 27.7 | 38.4 | 19.8 | 37.6 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.7 | 38.4 | 19.8 | 37.5 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.6 | 38.4 | 19.8 | 37.5 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:18 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.6 | 38.3 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.5 | 38.2 | 19.8 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.5 | 38.2 | 19.7 | 37.5 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.5 | 38.2 | 19.7 | 37.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:19 | 1 | 27.5 | 38.2 | 19.7 | 37.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.5 | 38.2 | 19.7 | 37.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.5 | 38.2 | 19.7 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.4 | 38.2 | 19.7 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.4 | 38.1 | 19.6 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.4 | 38.1 | 19.6 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:20 | 1 | 27.4 | 38.1 | 19.6 | 37.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.4 | 38.1 | 19.6 | 37.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.4 | 38.1 | 19.6 | 37.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.3 | 38.1 | 19.6 | 37.3 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.3 | 38.1 | 19.5 | 37.3 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.3 | 38 | 19.5 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:21 | 1 | 27.3 | 38 | 19.5 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.3 | 38 | 19.5 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.3 | 38 | 19.4 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.3 | 38 | 19.4 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.2 | 38 | 19.4 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.2 | 38 | 19.4 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:22 | 1 | 27.2 | 37.9 | 19.3 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.2 | 37.9 | 19.3 | 37.2 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.2 | 37.9 | 19.3 | 37.2 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.1 | 37.9 | 19.3 | 37.2 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.1 | 37.9 | 19.3 | 37.2 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.1 | 37.9 | 19.2 | 37.2 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:23 | 1 | 27.1 | 37.8 | 19.2 | 37.2 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27.1 | 37.8 | 19.2 | 37.2 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27.1 | 37.8 | 19.2 | 37.2 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27 | 37.8 | 19.2 | 37.2 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27 | 37.8 | 19.2 | 37.2 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27 | 37.8 | 19.2 | 37.1 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:24 | 1 | 27 | 37.8 | 19.1 | 37.1 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 27 | 37.8 | 19.1 | 37.1 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 27 | 37.7 | 19.1 | 37.1 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:25 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.9 | 37.7 | 19.1 | 37.1 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.8 | 37.7 | 19.1 | 37 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.8 | 37.6 | 19.1 | 37 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.8 | 37.6 | 19.1 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:26 | 1 | 26.8 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.8 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.8 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.8 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.8 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.7 | 37.6 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:27 | 1 | 26.7 | 37.5 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 37 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:28 | 1 | 26.7 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.7 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.6 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.6 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.6 | 37.5 | 19 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.6 | 37.4 | 18.9 | 36.9 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:29 | 1 | 26.6 | 37.4 | 18.9 | 36.9 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.6 | 37.4 | 18.9 | 36.9 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.6 | 37.4 | 18.9 | 36.9 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.6 | 37.4 | 18.9 | 36.9 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.6 | 37.4 | 18.9 | 36.8 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.5 | 37.4 | 18.9 | 36.8 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:30 | 1 | 26.5 | 37.4 | 18.9 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.8 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.8 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.8 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.8 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.7 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:31 | 1 | 26.5 | 37.4 | 18.7 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.5 | 37.3 | 18.7 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.4 | 37.3 | 18.6 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.4 | 37.3 | 18.6 | 36.8 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.4 | 37.3 | 18.6 | 36.7 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.4 | 37.3 | 18.6 | 36.7 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:32 | 1 | 26.4 | 37.3 | 18.6 | 36.7 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.4 | 37.3 | 18.6 | 36.7 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.4 | 37.3 | 18.6 | 36.7 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.3 | 37.3 | 18.6 | 36.7 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:33 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.3 | 37.2 | 18.5 | 36.7 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.2 | 37.2 | 18.5 | 36.7 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.2 | 37.2 | 18.5 | 36.7 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:34 | 1 | 26.2 | 37.2 | 18.5 | 36.6 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.2 | 37.1 | 18.5 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.2 | 37.1 | 18.4 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.2 | 37.1 | 18.4 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.2 | 37.1 | 18.4 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.1 | 37.1 | 18.4 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:35 | 1 | 26.1 | 37.1 | 18.4 | 36.6 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37.1 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37.1 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37.1 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:36 | 1 | 26.1 | 37 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26.1 | 37 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26.1 | 37 | 18.4 | 36.6 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26 | 37 | 18.4 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26 | 37 | 18.4 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26 | 37 | 18.4 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:37 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:38 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 26 | 37 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 26 | 36.9 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 25.9 | 36.9 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 25.9 | 36.9 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:39 | 1 | 25.9 | 36.9 | 18.3 | 36.5 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.3 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:40 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.9 | 36.9 | 18.2 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.9 | 36.9 | 18.1 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.9 | 36.8 | 18.1 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.9 | 36.8 | 18.1 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:41 | 1 | 25.8 | 36.8 | 18.1 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18.1 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:42 | 1 | 25.8 | 36.8 | 18 | 36.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.8 | 36.8 | 18 | 36.3 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.8 | 36.8 | 18 | 36.3 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.8 | 36.8 | 18 | 36.3 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.7 | 36.8 | 17.9 | 36.3 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:43 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:44 | 1 | 25.7 | 36.7 | 17.9 | 36.3 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.7 | 17.9 | 36.3 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.7 | 17.9 | 36.3 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.7 | 17.9 | 36.3 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.6 | 17.9 | 36.3 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.6 | 17.9 | 36.3 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:45 | 1 | 25.6 | 36.6 | 17.9 | 36.3 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.9 | 36.3 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.9 | 36.2 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.9 | 36.2 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.9 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.9 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:46 | 1 | 25.6 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.6 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:47 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.6 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:48 | 1 | 25.5 | 36.5 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.5 | 36.5 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.5 | 36.5 | 17.8 | 36.2 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.5 | 36.5 | 17.8 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.5 | 36.5 | 17.8 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.5 | 36.5 | 17.8 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:49 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:50 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.6 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:51 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.4 | 36.5 | 17.7 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.4 | 36.4 | 17.6 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.3 | 36.4 | 17.6 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.3 | 36.4 | 17.6 | 36.1 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.3 | 36.4 | 17.6 | 36.1 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:52 | 1 | 25.3 | 36.4 | 17.6 | 36.1 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.6 | 36 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.6 | 36 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.6 | 36 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.5 | 36 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.5 | 36 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:53 | 1 | 25.3 | 36.4 | 17.5 | 36 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.3 | 36.3 | 17.5 | 36 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:54 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:55 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.2 | 36.3 | 17.5 | 36 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:56 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:57 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.5 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:58 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25.1 | 36.3 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25.1 | 36.2 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25.1 | 36.2 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-07 23:59 | 1 | 25 | 36.2 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.4 | 35.9 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.4 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.4 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.3 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 | 1 | 25 | 36.2 | 17.3 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.3 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.3 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.3 | 35.8 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.2 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.2 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:01 | 1 | 25 | 36.2 | 17.2 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 25 | 36.2 | 17.2 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 25 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:02 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:03 | 1 | 24.9 | 36.2 | 17.1 | 35.8 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.9 | 36.1 | 17.1 | 35.8 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.8 | 36.1 | 17 | 35.8 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.8 | 36.1 | 17 | 35.8 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:04 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:05 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.8 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.8 | 36.1 | 17.1 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.8 | 36.1 | 17.1 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.8 | 36.1 | 17.1 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.8 | 36.1 | 17.1 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:06 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17.1 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:07 | 1 | 24.7 | 36.1 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:08 | 1 | 24.7 | 36 | 17 | 35.7 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:09 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 17 | 35.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 17 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 17 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:10 | 1 | 24.7 | 36 | 16.9 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.7 | 36 | 16.9 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.7 | 36 | 16.9 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.7 | 36 | 16.9 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.6 | 36 | 16.9 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.6 | 36 | 16.8 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:11 | 1 | 24.6 | 36 | 16.8 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.8 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:12 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.6 | 36 | 16.7 | 35.6 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.5 | 36 | 16.7 | 35.5 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:13 | 1 | 24.5 | 36 | 16.7 | 35.5 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 36 | 16.7 | 35.5 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 36 | 16.7 | 35.5 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 36 | 16.7 | 35.5 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:14 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:15 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.5 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:16 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.5 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.4 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:17 | 1 | 24.4 | 35.9 | 16.7 | 35.4 | 19.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 16.7 | 35.4 | 19.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 16.6 | 35.4 | 19.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 16.3 | 35.4 | 20.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 16 | 35.4 | 21.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 15.7 | 35.4 | 22.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:18 | 1 | 24.4 | 35.9 | 15.5 | 35.4 | 24 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.4 | 35.9 | 15.2 | 35.4 | 25.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.3 | 35.9 | 15 | 35.5 | 26.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.3 | 35.9 | 14.8 | 35.5 | 27.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.3 | 35.9 | 14.6 | 35.5 | 28 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.1 | 35.9 | 14.4 | 35.5 | 28.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:19 | 1 | 24.1 | 35.8 | 14.2 | 35.5 | 29 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 24 | 35.8 | 14 | 35.6 | 29.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 24 | 35.8 | 13.9 | 35.6 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 23.9 | 35.8 | 13.7 | 35.6 | 30.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 23.8 | 35.7 | 13.5 | 35.7 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 23.8 | 35.7 | 13.3 | 35.7 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:20 | 1 | 23.7 | 35.7 | 13.2 | 35.7 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.6 | 35.7 | 13.1 | 35.8 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.5 | 35.6 | 12.9 | 35.8 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.4 | 35.6 | 12.8 | 35.8 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.3 | 35.6 | 12.7 | 35.9 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.2 | 35.5 | 12.6 | 35.9 | 31.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:21 | 1 | 23.1 | 35.5 | 12.4 | 35.9 | 31.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:22 | 1 | 23 | 35.5 | 12.3 | 36 | 31.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:22 | 1 | 23 | 35.4 | 12.2 | 36 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:22 | 1 | 22.9 | 35.4 | 12.1 | 36 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:22 | 1 | 22.8 | 35.4 | 11.5 | 36.1 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:22 | 1 | 22.7 | 35.3 | 11.3 | 36.1 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:22 | 1 | 22.6 | 35.3 | 12.1 | 36.1 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:22 | 1 | 22.4 | 35.3 | 13.5 | 36.2 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 22.1 | 35.2 | 15.3 | 36.2 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 21.9 | 35.2 | 17.1 | 36.2 | 31.7 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 21.5 | 35.2 | 18.7 | 36.3 | 31.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 21.1 | 35.2 | 20.3 | 36.3 | 31.7 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 20.6 | 35.2 | 21.7 | 36.3 | 31.7 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:23 | 1 | 20.1 | 35.2 | 23 | 36.4 | 31.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:24 | 1 | 19.9 | 35.2 | 23.4 | 36.4 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 00:24 | 1 | 19.9 | 35.2 | 23.4 | 36.4 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 00:24 | 1 | 19.6 | 35.2 | 24.2 | 36.4 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 00:24 | 1 | 19.1 | 35.3 | 24.8 | 36.4 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 00:24 | 1 | 18.6 | 35.3 | 25.9 | 36.5 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 00:24 | 1 | 18.5 | 35.3 | 26.2 | 36.5 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 00:24 | 1 | 18.5 | 35.3 | 26.2 | 36.5 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:24 | 1 | 18.2 | 35.4 | 27.1 | 36.5 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:24 | 1 | 17.8 | 35.5 | 28.1 | 36.5 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:24 | 1 | 17.7 | 35.5 | 28.8 | 36.5 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.5 | 35.6 | 29.4 | 36.6 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.3 | 35.6 | 29.9 | 36.6 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.3 | 35.7 | 30.2 | 36.6 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.2 | 35.8 | 30.5 | 36.7 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.3 | 35.9 | 30.7 | 36.7 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:25 | 1 | 17.5 | 36 | 30.8 | 36.7 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 17.7 | 36.1 | 30.9 | 36.8 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 17.7 | 36.1 | 31 | 36.8 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 18 | 36.2 | 31.1 | 36.8 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 18.2 | 36.4 | 31.1 | 36.8 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 18.6 | 36.4 | 31.2 | 36.9 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:26 | 1 | 18.8 | 36.5 | 31.2 | 36.9 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 19.2 | 36.6 | 31.3 | 36.9 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 19.5 | 36.7 | 31.3 | 37 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 19.8 | 36.7 | 31.3 | 37 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 20.2 | 36.8 | 31.4 | 37 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 20.5 | 36.8 | 31.4 | 37.1 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:27 | 1 | 20.9 | 36.9 | 31.4 | 37.1 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:28 | 1 | 21.3 | 37 | 31.4 | 37.1 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:28 | 1 | 21.6 | 37 | 31.4 | 37.1 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:28 | 1 | 22 | 37.1 | 31.5 | 37.1 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:28 | 1 | 22 | 37.1 | 31.5 | 37.2 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:28 | 1 | 22.3 | 37.2 | 31.5 | 37.2 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:28 | 1 | 22.7 | 37.2 | 31.4 | 37.2 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:28 | 1 | 23.1 | 37.2 | 31 | 37.2 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.3 | 37.3 | 30.9 | 37.3 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.6 | 37.3 | 30.9 | 37.3 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.8 | 37.4 | 31 | 37.3 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.8 | 37.4 | 31.1 | 37.3 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.8 | 37.4 | 31.2 | 37.3 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:29 | 1 | 23.6 | 37.5 | 31.3 | 37.4 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:30 | 1 | 23.5 | 37.5 | 31.3 | 37.4 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:30 | 1 | 23.1 | 37.5 | 31.3 | 37.4 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:30 | 1 | 22.9 | 37.6 | 31.4 | 37.4 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:30 | 1 | 22.8 | 37.6 | 31.4 | 37.4 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:30 | 1 | 22.4 | 37.6 | 30.7 | 37.4 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:30 | 1 | 21.9 | 37.6 | 28.5 | 37.4 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:30 | 1 | 21.5 | 37.6 | 26.5 | 37.5 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 21.1 | 37.6 | 25.1 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 20.8 | 37.6 | 24.1 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 20.5 | 37.6 | 23.2 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 20.3 | 37.6 | 22.4 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 20.1 | 37.6 | 21.7 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 20 | 37.6 | 21 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:31 | 1 | 19.9 | 37.6 | 21 | 37.5 | 32.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.8 | 37.6 | 20.4 | 37.5 | 32.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.8 | 37.5 | 20 | 37.5 | 32.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.7 | 37.5 | 19.9 | 37.5 | 32.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.7 | 37.4 | 19.9 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.7 | 37.4 | 19.9 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:32 | 1 | 19.7 | 37.3 | 19.8 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 19.7 | 37.3 | 19.5 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 19.7 | 37.2 | 19.1 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 19.8 | 37.2 | 18.7 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 19.9 | 37.1 | 18.3 | 37.5 | 32.2 | 3.9 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 20 | 37 | 17.9 | 37.5 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:33 | 1 | 20.2 | 36.9 | 17.6 | 37.5 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 20.4 | 36.9 | 17.2 | 37.5 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 20.6 | 36.8 | 16.8 | 37.5 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 20.8 | 36.7 | 16.4 | 37.5 | 32.2 | 3.8 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 21.1 | 36.6 | 16 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 21.1 | 36.6 | 16 | 37.5 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 21.3 | 36.6 | 15.8 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:34 | 1 | 21.5 | 36.5 | 15.8 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 21.8 | 36.4 | 15.8 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 21.9 | 36.3 | 15.8 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 22.1 | 36.2 | 15.7 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 22.2 | 36.2 | 15.5 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 22.3 | 36.1 | 15.4 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:35 | 1 | 22.4 | 36 | 15.3 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.4 | 35.9 | 15.2 | 37.5 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.5 | 35.9 | 15.1 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.5 | 35.8 | 14.9 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.5 | 35.7 | 14.8 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.5 | 35.6 | 14.7 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:36 | 1 | 22.5 | 35.6 | 14.6 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:37 | 1 | 22.5 | 35.6 | 14.5 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:37 | 1 | 22.5 | 35.5 | 14.3 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:37 | 1 | 22.5 | 35.5 | 14.2 | 37.4 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 00:37 | 1 | 22.5 | 35.4 | 14.2 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:37 | 1 | 22.5 | 35.4 | 14 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:37 | 1 | 22.4 | 35.4 | 13.6 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:37 | 1 | 22.3 | 35.3 | 14 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 22.2 | 35.2 | 15.5 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 22.1 | 35.2 | 17.6 | 37.4 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 21.9 | 35.2 | 19.2 | 37.4 | 32.4 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 21.6 | 35.2 | 21 | 37.4 | 32.4 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 21.2 | 35.2 | 22.7 | 37.4 | 32.4 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:38 | 1 | 20.8 | 35.2 | 24.1 | 37.4 | 32.4 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:39 | 1 | 20.4 | 35.2 | 25.4 | 37.4 | 32.4 | 3.6 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 00:39 | 1 | 19.9 | 35.2 | 26.4 | 37.4 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 00:39 | 1 | 19.9 | 35.2 | 26.4 | 37.4 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 00:39 | 1 | 19.9 | 35.2 | 26.5 | 37.4 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 00:39 | 1 | 19.4 | 35.2 | 26.5 | 37.4 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 00:39 | 1 | 18.9 | 35.3 | 25.6 | 37.4 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 00:39 | 1 | 18.5 | 35.3 | 26.3 | 37.4 | 32.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 00:39 | 1 | 18.5 | 35.3 | 26.3 | 37.4 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:39 | 1 | 18.5 | 35.3 | 26.3 | 37.4 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:39 | 1 | 18.1 | 35.3 | 27.6 | 37.4 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.8 | 35.4 | 28.4 | 37.4 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.7 | 35.5 | 29.2 | 37.4 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.6 | 35.6 | 29.7 | 37.4 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.6 | 35.7 | 30.1 | 37.5 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.6 | 35.7 | 30.4 | 37.5 | 33.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:40 | 1 | 17.6 | 35.8 | 30.7 | 37.5 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 17.6 | 35.8 | 30.8 | 37.5 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 17.8 | 35.9 | 30.9 | 37.5 | 33.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 18 | 36 | 31.1 | 37.5 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 18.2 | 36 | 31.1 | 37.5 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 18.5 | 36.1 | 31.2 | 37.5 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:41 | 1 | 18.8 | 36.1 | 31.2 | 37.6 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 19.1 | 36.2 | 31.3 | 37.6 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 19.5 | 36.3 | 31.3 | 37.6 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 19.8 | 36.3 | 31.3 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 20.1 | 36.4 | 31.4 | 37.6 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 20.5 | 36.5 | 31.4 | 37.6 | 34.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:42 | 1 | 20.8 | 36.5 | 31.4 | 37.6 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:43 | 1 | 21.2 | 36.5 | 31.4 | 37.7 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:43 | 1 | 21.6 | 36.6 | 31.5 | 37.7 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 00:43 | 1 | 22 | 36.6 | 31.5 | 37.7 | 35.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:43 | 1 | 22 | 36.6 | 31.5 | 37.7 | 35.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:43 | 1 | 22.4 | 36.7 | 31.5 | 37.7 | 35.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:43 | 1 | 22.7 | 36.7 | 31.5 | 37.7 | 34.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:43 | 1 | 23.1 | 36.7 | 31.4 | 37.7 | 33.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 23.4 | 36.9 | 31.3 | 37.8 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 23.8 | 36.9 | 31.3 | 37.8 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 24.1 | 36.9 | 31.3 | 37.8 | 29.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 24.4 | 37 | 31.4 | 37.8 | 28.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 24.7 | 37 | 31.4 | 37.8 | 28 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:44 | 1 | 24.9 | 37.1 | 31.4 | 37.8 | 27.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 25.2 | 37.2 | 31.4 | 37.8 | 26.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 25.4 | 37.2 | 31.4 | 37.8 | 26.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 25.5 | 37.2 | 31.5 | 37.8 | 25.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 25.7 | 37.3 | 31.5 | 37.8 | 26.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 25.9 | 37.4 | 31.5 | 37.8 | 26.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:45 | 1 | 26 | 37.5 | 31.5 | 37.8 | 25.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:46 | 1 | 26.1 | 37.5 | 31.5 | 37.8 | 25.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:46 | 1 | 26.2 | 37.5 | 31.6 | 37.8 | 24.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 00:46 | 1 | 26.2 | 37.6 | 31.6 | 37.8 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:46 | 1 | 26.3 | 37.6 | 31.6 | 37.8 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:46 | 1 | 26.4 | 37.7 | 30.9 | 37.8 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:46 | 1 | 26.5 | 37.7 | 29.7 | 37.8 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:46 | 1 | 26.5 | 37.7 | 28.7 | 37.7 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 26.6 | 37.8 | 28 | 37.7 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 26.7 | 37.8 | 27.5 | 37.7 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 26.8 | 37.9 | 27.1 | 37.7 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 26.9 | 37.9 | 26.9 | 37.7 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 27 | 37.9 | 26.6 | 37.7 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:47 | 1 | 27.1 | 38 | 26.4 | 37.7 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.1 | 38 | 26.3 | 37.6 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.2 | 38 | 26 | 37.6 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.3 | 38 | 25.7 | 37.6 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.4 | 38.1 | 25.4 | 37.6 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.4 | 38.1 | 25.1 | 37.6 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:48 | 1 | 27.5 | 38.1 | 24.9 | 37.6 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.6 | 38.1 | 24.6 | 37.5 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.7 | 38.1 | 24.4 | 37.5 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.7 | 38.1 | 24.1 | 37.5 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.8 | 38.1 | 23.9 | 37.5 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.9 | 38.1 | 23.7 | 37.5 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:49 | 1 | 27.9 | 38.1 | 23.5 | 37.5 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 27.9 | 38.2 | 23.3 | 37.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 28 | 38.2 | 23.1 | 37.4 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 28 | 38.2 | 22.9 | 37.4 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 28 | 38.2 | 22.7 | 37.4 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 28.1 | 38.1 | 22.5 | 37.4 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:50 | 1 | 28.1 | 38.1 | 22.4 | 37.3 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38.1 | 22.2 | 37.3 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38.1 | 22.1 | 37.3 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38.1 | 21.9 | 37.3 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38.1 | 21.8 | 37.3 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38.1 | 21.6 | 37.2 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:51 | 1 | 28.1 | 38 | 21.4 | 37.2 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 28.1 | 38 | 21.3 | 37.2 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 28.1 | 38 | 21.2 | 37.2 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 28 | 38 | 21.1 | 37.2 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 28 | 38 | 20.9 | 37.1 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 28 | 37.9 | 20.8 | 37.1 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:52 | 1 | 27.9 | 37.9 | 20.7 | 37.1 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.9 | 37.9 | 20.6 | 37.1 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.9 | 37.9 | 20.5 | 37.1 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.8 | 37.8 | 20.4 | 37 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.8 | 37.8 | 20.3 | 37 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.7 | 37.8 | 20.1 | 37 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:53 | 1 | 27.7 | 37.8 | 20 | 37 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.5 | 37.7 | 20 | 37 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.5 | 37.7 | 19.9 | 36.9 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.5 | 37.7 | 19.8 | 36.9 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.4 | 37.6 | 19.7 | 36.9 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.4 | 37.6 | 19.7 | 36.9 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:54 | 1 | 27.3 | 37.6 | 19.6 | 36.9 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27.3 | 37.6 | 19.5 | 36.8 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27.1 | 37.5 | 19.4 | 36.8 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27.1 | 37.5 | 19.4 | 36.8 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27.1 | 37.5 | 19.3 | 36.8 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27 | 37.4 | 19.3 | 36.8 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:55 | 1 | 27 | 37.4 | 19.2 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.9 | 37.4 | 19.2 | 36.7 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.9 | 37.3 | 19.1 | 36.7 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.8 | 37.3 | 19.1 | 36.7 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.7 | 37.3 | 19 | 36.7 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.7 | 37.3 | 19 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:56 | 1 | 26.6 | 37.2 | 18.9 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.6 | 37.2 | 18.9 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.5 | 37.2 | 18.8 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.4 | 37.1 | 18.8 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.4 | 37.1 | 18.8 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.4 | 37.1 | 18.7 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:57 | 1 | 26.3 | 37.1 | 18.7 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.3 | 37.1 | 18.7 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.2 | 37 | 18.6 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.2 | 37 | 18.6 | 36.5 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.1 | 37 | 18.5 | 36.5 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.1 | 37 | 18.5 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:58 | 1 | 26.1 | 37 | 18.5 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 26 | 37 | 18.4 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 26 | 36.9 | 18.4 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 25.9 | 36.9 | 18.4 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 25.9 | 36.9 | 18.3 | 36.4 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 25.9 | 36.9 | 18.3 | 36.4 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 00:59 | 1 | 25.8 | 36.9 | 18.2 | 36.4 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.8 | 36.9 | 18.2 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.7 | 36.8 | 18.2 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.7 | 36.8 | 18.2 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.7 | 36.8 | 18.1 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.6 | 36.8 | 18.1 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:00 | 1 | 25.6 | 36.8 | 18.1 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.6 | 36.8 | 18 | 36.3 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.5 | 36.8 | 18 | 36.3 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.5 | 36.7 | 18 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.4 | 36.7 | 18 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.4 | 36.7 | 18 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:01 | 1 | 25.4 | 36.7 | 17.9 | 36.2 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.4 | 36.7 | 17.9 | 36.2 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.3 | 36.7 | 17.9 | 36.2 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.3 | 36.7 | 17.8 | 36.2 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.3 | 36.6 | 17.8 | 36.2 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.2 | 36.6 | 17.8 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:02 | 1 | 25.2 | 36.6 | 17.8 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.2 | 36.6 | 17.7 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.2 | 36.6 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.1 | 36.6 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.1 | 36.6 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.1 | 36.6 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:03 | 1 | 25.1 | 36.6 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 25 | 36.5 | 17.7 | 36.1 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 25 | 36.5 | 17.6 | 36.1 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 25 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 25 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 24.9 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:04 | 1 | 24.9 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.9 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.9 | 36.5 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.9 | 36.5 | 17.6 | 36 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.8 | 36.5 | 17.6 | 36 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.8 | 36.5 | 17.6 | 36 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:05 | 1 | 24.8 | 36.5 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.8 | 36.5 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.8 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.8 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:06 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.7 | 36.4 | 17.5 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.7 | 36.4 | 17.5 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.6 | 36.4 | 17.5 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.6 | 36.4 | 17.5 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:07 | 1 | 24.6 | 36.4 | 17.5 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.6 | 36.4 | 17.5 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.6 | 36.4 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.6 | 36.4 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.6 | 36.4 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.5 | 36.4 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:08 | 1 | 24.5 | 36.4 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.4 | 17.4 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.3 | 17.4 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.3 | 17.4 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.3 | 17.4 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.3 | 17.3 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:09 | 1 | 24.5 | 36.3 | 17.3 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.3 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.3 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.3 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.3 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.2 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:10 | 1 | 24.4 | 36.3 | 17.2 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.4 | 36.3 | 17.2 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.4 | 36.3 | 17.2 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.4 | 36.3 | 17.1 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.3 | 36.3 | 17.1 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.3 | 36.3 | 17.1 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:11 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.3 | 36.2 | 17.1 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:12 | 1 | 24.2 | 36.2 | 17.1 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17.1 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:13 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.2 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.1 | 36.2 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:14 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:15 | 1 | 24.1 | 36.1 | 17 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24.1 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24.1 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24.1 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:16 | 1 | 24 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:17 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:18 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:18 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:18 | 1 | 24 | 36.1 | 16.9 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:18 | 1 | 24 | 36.1 | 16.9 | 35.4 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:18 | 1 | 24 | 36.1 | 16.9 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:18 | 1 | 24 | 36 | 16.9 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:18 | 1 | 24 | 36 | 16.7 | 35.4 | 19.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 24 | 36 | 16.4 | 35.4 | 20.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 24 | 36 | 16.2 | 35.4 | 22.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 24 | 36 | 15.9 | 35.4 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 23.9 | 36 | 15.6 | 35.4 | 25 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 23.9 | 36 | 15.4 | 35.4 | 26.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:19 | 1 | 23.9 | 36 | 15.2 | 35.4 | 27.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.9 | 35.9 | 15 | 35.4 | 27.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.8 | 35.9 | 14.8 | 35.4 | 28.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.8 | 35.9 | 14.7 | 35.5 | 29 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.7 | 35.9 | 14.5 | 35.5 | 29.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.7 | 35.8 | 14.3 | 35.5 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:20 | 1 | 23.6 | 35.8 | 14.2 | 35.5 | 30 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.5 | 35.8 | 14 | 35.5 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.4 | 35.8 | 13.8 | 35.6 | 30.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.3 | 35.7 | 13.7 | 35.6 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.2 | 35.7 | 13.5 | 35.6 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.2 | 35.6 | 13.4 | 35.6 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:21 | 1 | 23.1 | 35.6 | 13.3 | 35.7 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:22 | 1 | 23 | 35.6 | 13.2 | 35.7 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:22 | 1 | 22.9 | 35.5 | 13.1 | 35.7 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:22 | 1 | 22.8 | 35.5 | 12.9 | 35.7 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:22 | 1 | 22.7 | 35.4 | 12.8 | 35.8 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:22 | 1 | 22.7 | 35.4 | 12.8 | 35.8 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:22 | 1 | 22.6 | 35.4 | 12.7 | 35.8 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:22 | 1 | 22.5 | 35.4 | 12.1 | 35.8 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 22.4 | 35.3 | 12.6 | 35.8 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 22.3 | 35.3 | 14 | 35.9 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 22.1 | 35.2 | 15.8 | 35.9 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 21.8 | 35.2 | 17.7 | 35.9 | 31.6 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 21.5 | 35.2 | 19.3 | 35.9 | 31.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:23 | 1 | 21.2 | 35.2 | 20.8 | 36 | 31.6 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:24 | 1 | 20.7 | 35.2 | 22.3 | 36 | 31.7 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:24 | 1 | 20.2 | 35.2 | 23.5 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:24 | 1 | 19.9 | 35.2 | 24.3 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 01:24 | 1 | 19.9 | 35.2 | 24.3 | 36 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 01:24 | 1 | 19.8 | 35.2 | 24.7 | 36 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 01:24 | 1 | 19.3 | 35.3 | 25.3 | 36.1 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 01:24 | 1 | 18.8 | 35.3 | 26 | 36.1 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 01:24 | 1 | 18.4 | 35.4 | 26.8 | 36.1 | 31 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 01:24 | 1 | 18.4 | 35.4 | 26.8 | 36.1 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:24 | 1 | 18.3 | 35.4 | 27.2 | 36.1 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.9 | 35.4 | 28.1 | 36.2 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.7 | 35.5 | 28.8 | 36.2 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.5 | 35.6 | 29.3 | 36.2 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.4 | 35.7 | 29.8 | 36.2 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.2 | 35.7 | 30.1 | 36.3 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:25 | 1 | 17.2 | 35.8 | 30.4 | 36.3 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 17.2 | 35.9 | 30.6 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 17.4 | 36 | 30.8 | 36.4 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 17.5 | 36.1 | 30.9 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 17.7 | 36.1 | 31 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 17.9 | 36.2 | 31 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:26 | 1 | 18.1 | 36.3 | 31.1 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 18.4 | 36.4 | 31.1 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 18.8 | 36.4 | 31.2 | 36.6 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 19 | 36.5 | 31.2 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 19.4 | 36.5 | 31.3 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 19.7 | 36.6 | 31.3 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:27 | 1 | 20 | 36.7 | 31.3 | 36.7 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 20.4 | 36.8 | 31.3 | 36.7 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 20.8 | 36.8 | 31.4 | 36.7 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 21.1 | 36.8 | 31.4 | 36.7 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 21.5 | 36.9 | 31.4 | 36.8 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 21.8 | 36.9 | 31.4 | 36.8 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:28 | 1 | 22 | 37 | 31.4 | 36.8 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:28 | 1 | 22.2 | 37 | 31.4 | 36.8 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 22.5 | 37 | 31.5 | 36.8 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 22.8 | 37.1 | 31.2 | 36.9 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 23.2 | 37.1 | 31 | 36.9 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 23.5 | 37.1 | 31 | 36.9 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 23.6 | 37.2 | 31 | 36.9 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:29 | 1 | 23.8 | 37.2 | 31 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 23.8 | 37.2 | 31.1 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 23.7 | 37.2 | 31.2 | 37 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 23.6 | 37.3 | 31.2 | 37 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 23.3 | 37.3 | 31.3 | 37 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 23 | 37.3 | 31.3 | 37 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:30 | 1 | 22.6 | 37.3 | 31.3 | 37.1 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:31 | 1 | 22.1 | 37.4 | 31.4 | 37.1 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:31 | 1 | 21.5 | 37.4 | 31.4 | 37.1 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:31 | 1 | 21 | 37.4 | 31.4 | 37.1 | 32.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:31 | 1 | 20.4 | 37.4 | 31.4 | 37.1 | 32.7 | 3.6 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 01:31 | 1 | 19.9 | 37.4 | 31.5 | 37.1 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:31 | 1 | 19.9 | 37.4 | 31.5 | 37.1 | 32.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 01:31 | 1 | 19.9 | 37.4 | 31.5 | 37.1 | 32.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 01:31 | 1 | 19.3 | 37.5 | 31.5 | 37.1 | 32.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 18.7 | 37.5 | 31.5 | 37.2 | 32.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 18.2 | 37.5 | 31.5 | 37.2 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 18.2 | 37.5 | 31.5 | 37.2 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 17.7 | 37.5 | 31.5 | 37.2 | 33.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 17.5 | 37.5 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 17.2 | 37.5 | 31.6 | 37.2 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:32 | 1 | 17.1 | 37.6 | 31.6 | 37.2 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 17 | 37.6 | 31.6 | 37.3 | 33.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 16.9 | 37.6 | 31.6 | 37.3 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 16.9 | 37.6 | 31.7 | 37.3 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 17 | 37.6 | 31.7 | 37.3 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 17.2 | 37.6 | 31.7 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:33 | 1 | 17.4 | 37.6 | 31.7 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 17.7 | 37.7 | 31.7 | 37.4 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 17.8 | 37.7 | 31.7 | 37.4 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 18.1 | 37.7 | 31.7 | 37.4 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 18.4 | 37.7 | 31.7 | 37.4 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 18.7 | 37.7 | 31.7 | 37.4 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:34 | 1 | 19 | 37.7 | 31.7 | 37.4 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 19.5 | 37.7 | 31.7 | 37.5 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 19.8 | 37.7 | 31.7 | 37.5 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 20.2 | 37.7 | 31.8 | 37.5 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 20.5 | 37.8 | 31.8 | 37.5 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 20.9 | 37.8 | 31.8 | 37.5 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:35 | 1 | 21.2 | 37.8 | 31.8 | 37.5 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:36 | 1 | 21.7 | 37.8 | 31.8 | 37.5 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 01:36 | 1 | 22 | 37.8 | 31.8 | 37.5 | 34.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:36 | 1 | 22.1 | 37.8 | 31.8 | 37.5 | 34.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:36 | 1 | 22.4 | 37.8 | 31.8 | 37.5 | 34.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:36 | 1 | 22.8 | 37.8 | 31.7 | 37.5 | 33.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 01:36 | 1 | 22.9 | 37.8 | 31.6 | 37.6 | 33.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:36 | 1 | 23.1 | 37.8 | 31 | 37.6 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:36 | 1 | 23.5 | 37.8 | 30.2 | 37.6 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 23.8 | 37.8 | 29.6 | 37.6 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 24.1 | 37.8 | 29.2 | 37.6 | 30.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 24.3 | 37.8 | 28.9 | 37.6 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 24.7 | 37.9 | 28.6 | 37.6 | 29.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 24.9 | 37.9 | 28.5 | 37.6 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:37 | 1 | 25.2 | 37.9 | 28.4 | 37.6 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 25.4 | 37.9 | 28.3 | 37.6 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 25.7 | 37.9 | 28.1 | 37.6 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 26 | 37.9 | 27.9 | 37.6 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 26.2 | 37.9 | 27.7 | 37.6 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 26.5 | 37.9 | 27.4 | 37.6 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:38 | 1 | 26.6 | 38 | 27.1 | 37.6 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 26.9 | 38 | 26.9 | 37.6 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 27.1 | 38 | 26.6 | 37.6 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 27.3 | 38 | 26.4 | 37.6 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 27.4 | 38 | 26.2 | 37.6 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 27.6 | 38 | 25.9 | 37.6 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:39 | 1 | 27.8 | 38 | 25.8 | 37.6 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 27.9 | 38 | 25.6 | 37.6 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 28.1 | 38 | 25.3 | 37.6 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 28.1 | 38 | 25.1 | 37.5 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 28.2 | 38 | 24.9 | 37.5 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 28.3 | 38 | 24.7 | 37.5 | 26 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:40 | 1 | 28.4 | 38 | 24.5 | 37.5 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.4 | 38 | 24.4 | 37.5 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.5 | 38 | 24.2 | 37.5 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.5 | 38 | 24 | 37.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.6 | 38 | 23.8 | 37.4 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.6 | 38 | 23.6 | 37.4 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:41 | 1 | 28.6 | 38 | 23.5 | 37.4 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 23.3 | 37.4 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 23.1 | 37.4 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 22.9 | 37.3 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 22.7 | 37.3 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 22.6 | 37.3 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:42 | 1 | 28.7 | 38 | 22.4 | 37.3 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.7 | 38 | 22.2 | 37.2 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.7 | 38 | 22 | 37.2 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.7 | 38 | 21.9 | 37.2 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.6 | 37.9 | 21.7 | 37.2 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.6 | 37.9 | 21.6 | 37.2 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:43 | 1 | 28.6 | 37.9 | 21.5 | 37.1 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.5 | 37.9 | 21.4 | 37.1 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.4 | 37.9 | 21.3 | 37.1 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.4 | 37.9 | 21.1 | 37.1 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.5 | 37.9 | 21 | 37 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.4 | 37.8 | 20.9 | 37 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:44 | 1 | 28.4 | 37.8 | 20.8 | 37 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28.2 | 37.8 | 20.7 | 36.9 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28.2 | 37.8 | 20.6 | 36.9 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28.1 | 37.8 | 20.5 | 36.9 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28.1 | 37.7 | 20.4 | 36.9 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28 | 37.7 | 20.4 | 36.9 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:45 | 1 | 28 | 37.7 | 20.3 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.9 | 37.7 | 20.2 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.8 | 37.7 | 20.1 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.7 | 37.7 | 20 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.7 | 37.6 | 19.9 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.6 | 37.6 | 19.8 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:46 | 1 | 27.5 | 37.6 | 19.8 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.5 | 37.6 | 19.7 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.4 | 37.6 | 19.6 | 36.6 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.3 | 37.5 | 19.6 | 36.6 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.3 | 37.5 | 19.5 | 36.6 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.2 | 37.5 | 19.5 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:47 | 1 | 27.1 | 37.5 | 19.4 | 36.5 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 27.1 | 37.5 | 19.3 | 36.5 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 27 | 37.4 | 19.3 | 36.5 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 26.9 | 37.4 | 19.2 | 36.5 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 26.9 | 37.4 | 19.2 | 36.4 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 26.8 | 37.3 | 19.1 | 36.4 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:48 | 1 | 26.8 | 37.3 | 19.1 | 36.4 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.7 | 37.3 | 19 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.6 | 37.3 | 18.9 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.6 | 37.2 | 18.9 | 36.3 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.5 | 37.2 | 18.9 | 36.3 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.4 | 37.2 | 18.8 | 36.3 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:49 | 1 | 26.4 | 37.1 | 18.8 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.4 | 37.1 | 18.7 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.3 | 37.1 | 18.7 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.3 | 37.1 | 18.6 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.2 | 37 | 18.6 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.1 | 37 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:50 | 1 | 26.1 | 37 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 26.1 | 37 | 18.5 | 36.1 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 26 | 36.9 | 18.4 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 25.9 | 36.9 | 18.4 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 25.9 | 36.9 | 18.3 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 25.9 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:51 | 1 | 25.8 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.8 | 36.8 | 18.2 | 36 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.7 | 36.8 | 18.2 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.7 | 36.8 | 18.2 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.7 | 36.8 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.6 | 36.8 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:52 | 1 | 25.6 | 36.7 | 18.1 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.5 | 36.7 | 18.1 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.5 | 36.7 | 18 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.5 | 36.7 | 18 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.4 | 36.7 | 18 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.4 | 36.7 | 17.9 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:53 | 1 | 25.3 | 36.6 | 17.9 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.3 | 36.6 | 17.9 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.3 | 36.6 | 17.9 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.2 | 36.6 | 17.9 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.2 | 36.6 | 17.8 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.2 | 36.6 | 17.8 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:54 | 1 | 25.2 | 36.6 | 17.8 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25.1 | 36.6 | 17.8 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25.1 | 36.5 | 17.8 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25.1 | 36.5 | 17.8 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25 | 36.5 | 17.8 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25 | 36.5 | 17.7 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:55 | 1 | 25 | 36.5 | 17.7 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 25 | 36.5 | 17.7 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 24.9 | 36.5 | 17.7 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 24.9 | 36.5 | 17.7 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 24.9 | 36.5 | 17.7 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 24.9 | 36.4 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:56 | 1 | 24.9 | 36.4 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.8 | 36.4 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.8 | 36.4 | 17.7 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:57 | 1 | 24.7 | 36.4 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.7 | 36.4 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.7 | 36.4 | 17.6 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.7 | 36.4 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.7 | 36.3 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.6 | 36.3 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:58 | 1 | 24.6 | 36.3 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.6 | 36.3 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.6 | 36.3 | 17.5 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.6 | 36.3 | 17.5 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 01:59 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.5 | 36.2 | 17.4 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.5 | 36.2 | 17.4 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.5 | 36.2 | 17.4 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.5 | 36.2 | 17.3 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:00 | 1 | 24.4 | 36.2 | 17.3 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.3 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.3 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.2 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.2 | 17.2 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:01 | 1 | 24.4 | 36.1 | 16.9 | 35.4 | 19.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.3 | 36.1 | 16.7 | 35.4 | 21.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.3 | 36.1 | 16.4 | 35.4 | 22.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.3 | 36.1 | 16.2 | 35.4 | 24.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.3 | 36.1 | 16 | 35.4 | 25.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.2 | 36.1 | 15.8 | 35.4 | 26.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:02 | 1 | 24.2 | 36.1 | 15.6 | 35.4 | 27.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 24.2 | 36 | 15.4 | 35.4 | 28.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 24.1 | 36 | 15.2 | 35.4 | 28.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 24 | 36 | 15.1 | 35.4 | 29.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 23.9 | 35.9 | 14.9 | 35.4 | 29.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 23.9 | 35.9 | 14.7 | 35.5 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:03 | 1 | 23.8 | 35.9 | 14.6 | 35.5 | 30.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.7 | 35.8 | 14.5 | 35.5 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.7 | 35.8 | 14.4 | 35.5 | 30.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.6 | 35.7 | 14.3 | 35.5 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.5 | 35.7 | 14.1 | 35.6 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.4 | 35.7 | 14 | 35.6 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:04 | 1 | 23.4 | 35.6 | 13.9 | 35.6 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:05 | 1 | 23.3 | 35.6 | 13.8 | 35.6 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:05 | 1 | 23.2 | 35.5 | 13.7 | 35.7 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:05 | 1 | 23.1 | 35.5 | 13.6 | 35.7 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:05 | 1 | 23 | 35.5 | 13.5 | 35.7 | 31.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:05 | 1 | 23 | 35.4 | 13.5 | 35.7 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:05 | 1 | 22.9 | 35.4 | 13.4 | 35.7 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:05 | 1 | 22.8 | 35.4 | 12.9 | 35.8 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 22.8 | 35.3 | 13.3 | 35.8 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 22.6 | 35.3 | 14.7 | 35.8 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 22.4 | 35.2 | 16.5 | 35.8 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 22.2 | 35.2 | 18.3 | 35.9 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 21.8 | 35.2 | 19.9 | 35.9 | 31.5 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:06 | 1 | 21.5 | 35.2 | 21.5 | 35.9 | 31.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:07 | 1 | 21.1 | 35.2 | 22.9 | 35.9 | 31.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:07 | 1 | 20.6 | 35.2 | 24.2 | 36 | 31.6 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:07 | 1 | 20.2 | 35.2 | 25.4 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:07 | 1 | 19.9 | 35.2 | 25.8 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 02:07 | 1 | 19.9 | 35.2 | 25.8 | 36 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:07 | 1 | 19.6 | 35.3 | 26.3 | 36 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:07 | 1 | 19.1 | 35.3 | 26.5 | 36.1 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:07 | 1 | 18.6 | 35.4 | 27.2 | 36.1 | 31 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:08 | 1 | 18.4 | 35.4 | 27.5 | 36.1 | 31 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 18.4 | 35.4 | 27.5 | 36.1 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 18.1 | 35.5 | 28.1 | 36.1 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 17.8 | 35.5 | 28.8 | 36.1 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 17.6 | 35.6 | 29.3 | 36.2 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 17.4 | 35.7 | 29.8 | 36.2 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 17.2 | 35.8 | 30.2 | 36.2 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:08 | 1 | 17.1 | 35.8 | 30.5 | 36.3 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.1 | 35.9 | 30.7 | 36.3 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.2 | 36 | 30.9 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.4 | 36.1 | 31 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.5 | 36.2 | 31.1 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.7 | 36.3 | 31.2 | 36.4 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:09 | 1 | 17.9 | 36.3 | 31.2 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 18.1 | 36.4 | 31.3 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 18.4 | 36.5 | 31.3 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 18.7 | 36.6 | 31.4 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 19 | 36.6 | 31.4 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 19.4 | 36.7 | 31.5 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:10 | 1 | 19.7 | 36.7 | 31.5 | 36.6 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 20.1 | 36.8 | 31.5 | 36.7 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 20.4 | 36.9 | 31.5 | 36.7 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 20.8 | 36.9 | 31.6 | 36.7 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 21.1 | 36.9 | 31.6 | 36.7 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 21.5 | 37 | 31.6 | 36.8 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:11 | 1 | 21.8 | 37 | 31.6 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:12 | 1 | 22 | 37.1 | 31.6 | 36.8 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 22.3 | 37.1 | 31.6 | 36.8 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 22.6 | 37.1 | 31.6 | 36.8 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 22.9 | 37.2 | 31.5 | 36.9 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 23.2 | 37.2 | 31.4 | 36.9 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 23.5 | 37.2 | 31.4 | 36.9 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:12 | 1 | 23.7 | 37.3 | 31.4 | 36.9 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 23.8 | 37.3 | 31.4 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 23.8 | 37.3 | 31.4 | 37 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 23.7 | 37.3 | 31.4 | 37 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 23.6 | 37.4 | 31.5 | 37 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 23.3 | 37.4 | 31.5 | 37 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:13 | 1 | 22.9 | 37.4 | 31.5 | 37 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 22.6 | 37.4 | 31.6 | 37.1 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 22.1 | 37.5 | 31.6 | 37.1 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 21.6 | 37.5 | 31.6 | 37.1 | 32.8 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 21 | 37.5 | 31.6 | 37.1 | 32.9 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 20.5 | 37.5 | 31.6 | 37.1 | 33 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:14 | 1 | 19.9 | 37.5 | 31.6 | 37.1 | 33.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:14 | 1 | 19.9 | 37.5 | 31.6 | 37.1 | 33.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:14 | 1 | 19.9 | 37.5 | 31.6 | 37.1 | 33.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:15 | 1 | 19.4 | 37.6 | 31.7 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 19.4 | 37.6 | 31.7 | 37.2 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 18.8 | 37.6 | 31.7 | 37.2 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 18.2 | 37.6 | 31.7 | 37.2 | 33.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 18.2 | 37.6 | 31.7 | 37.2 | 33.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 17.8 | 37.6 | 31.6 | 37.2 | 33.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 17.5 | 37.6 | 31.6 | 37.2 | 33.7 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:15 | 1 | 17.2 | 37.6 | 31.7 | 37.2 | 34 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 17 | 37.6 | 31.7 | 37.2 | 34.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 16.9 | 37.7 | 31.8 | 37.3 | 34.4 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 16.8 | 37.7 | 31.8 | 37.3 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 16.8 | 37.7 | 31.8 | 37.3 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 16.9 | 37.7 | 31.8 | 37.3 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:16 | 1 | 17 | 37.7 | 31.8 | 37.3 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 17.2 | 37.7 | 31.8 | 37.4 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 17.5 | 37.7 | 31.8 | 37.4 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 17.7 | 37.8 | 31.9 | 37.4 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 17.9 | 37.8 | 31.9 | 37.4 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 18.2 | 37.8 | 31.9 | 37.4 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 02:17 | 1 | 18.5 | 37.8 | 31.9 | 37.5 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:17 | 1 | 18.5 | 37.8 | 31.9 | 37.5 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 18.8 | 37.8 | 31.9 | 37.5 | 34.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 19.1 | 37.8 | 31.8 | 37.5 | 34.1 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 19.4 | 37.8 | 31.4 | 37.5 | 33.5 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 19.7 | 37.8 | 30.4 | 37.5 | 33.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 20.1 | 37.8 | 29.5 | 37.5 | 33.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:18 | 1 | 20.4 | 37.8 | 28.7 | 37.5 | 33.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 02:19 | 1 | 20.5 | 37.8 | 28.2 | 37.6 | 33.4 | 4 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 20.6 | 37.8 | 27.8 | 37.6 | 33.5 | 4.1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 20.9 | 37.8 | 27.1 | 37.6 | 33 | 4.1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 21.1 | 37.8 | 26.9 | 37.6 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 21.2 | 37.8 | 26.7 | 37.6 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 21.4 | 37.8 | 26.5 | 37.6 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 21.7 | 37.8 | 26.2 | 37.6 | 30.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:19 | 1 | 21.9 | 37.8 | 25.9 | 37.6 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 22.2 | 37.8 | 25.7 | 37.6 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 22.5 | 37.8 | 25.5 | 37.6 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 22.8 | 37.8 | 25.4 | 37.6 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 23 | 37.8 | 25.2 | 37.6 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 23.3 | 37.8 | 25.1 | 37.6 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:20 | 1 | 23.6 | 37.8 | 24.9 | 37.6 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 23.8 | 37.8 | 24.8 | 37.6 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 24.1 | 37.8 | 24.6 | 37.6 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 24.3 | 37.8 | 24.4 | 37.5 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 24.6 | 37.7 | 24.3 | 37.5 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 24.9 | 37.7 | 24.2 | 37.5 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:21 | 1 | 25 | 37.7 | 24 | 37.5 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 25.3 | 37.7 | 23.9 | 37.5 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 25.5 | 37.7 | 23.8 | 37.5 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 25.6 | 37.7 | 23.6 | 37.5 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 25.8 | 37.7 | 23.5 | 37.4 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 26 | 37.7 | 23.3 | 37.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:22 | 1 | 26.2 | 37.7 | 23.1 | 37.4 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.3 | 37.7 | 23 | 37.4 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.4 | 37.7 | 22.8 | 37.4 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.5 | 37.7 | 22.7 | 37.3 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.7 | 37.7 | 22.6 | 37.3 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.8 | 37.7 | 22.5 | 37.3 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:23 | 1 | 26.9 | 37.7 | 22.3 | 37.3 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 26.9 | 37.7 | 22.2 | 37.2 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 27 | 37.7 | 22 | 37.2 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 27.1 | 37.7 | 21.9 | 37.2 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 27.1 | 37.7 | 21.7 | 37.2 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 27.1 | 37.7 | 21.6 | 37.1 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:24 | 1 | 27.2 | 37.7 | 21.4 | 37.1 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.2 | 37.6 | 21.3 | 37.1 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.2 | 37.6 | 21.2 | 37.1 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.2 | 37.6 | 21.1 | 37 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.3 | 37.6 | 20.9 | 37 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.3 | 37.6 | 20.9 | 37 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:25 | 1 | 27.3 | 37.6 | 20.8 | 36.9 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.3 | 37.6 | 20.7 | 36.9 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.3 | 37.6 | 20.6 | 36.9 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.2 | 37.6 | 20.5 | 36.9 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.2 | 37.6 | 20.4 | 36.8 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.2 | 37.6 | 20.3 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:26 | 1 | 27.2 | 37.5 | 20.2 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27.2 | 37.5 | 20.1 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27.1 | 37.5 | 20.1 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27.1 | 37.5 | 20 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27.1 | 37.5 | 19.9 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27 | 37.5 | 19.8 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:27 | 1 | 27 | 37.4 | 19.8 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 27 | 37.4 | 19.7 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 26.9 | 37.4 | 19.6 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 26.9 | 37.4 | 19.5 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 26.8 | 37.4 | 19.5 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 26.7 | 37.3 | 19.4 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:28 | 1 | 26.7 | 37.3 | 19.3 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.7 | 37.3 | 19.2 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.6 | 37.3 | 19.2 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.5 | 37.2 | 19.1 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.5 | 37.2 | 19.1 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.5 | 37.2 | 19 | 36.3 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:29 | 1 | 26.4 | 37.2 | 19 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.4 | 37.2 | 18.9 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.3 | 37.1 | 18.9 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.3 | 37.1 | 18.8 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.2 | 37.1 | 18.7 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.2 | 37.1 | 18.7 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:30 | 1 | 26.1 | 37 | 18.7 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 26.1 | 37 | 18.6 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 26.1 | 37 | 18.6 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 26 | 37 | 18.5 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 26 | 36.9 | 18.5 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 25.9 | 36.9 | 18.4 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:31 | 1 | 25.9 | 36.9 | 18.4 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.8 | 36.9 | 18.4 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.8 | 36.9 | 18.3 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.7 | 36.8 | 18.3 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.7 | 36.8 | 18.2 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.7 | 36.8 | 18.2 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:32 | 1 | 25.6 | 36.8 | 18.2 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.6 | 36.8 | 18.1 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.5 | 36.7 | 18.1 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.5 | 36.7 | 18.1 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.5 | 36.7 | 18.1 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.4 | 36.7 | 18.1 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:33 | 1 | 25.4 | 36.7 | 18 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.3 | 36.7 | 18 | 35.8 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.3 | 36.7 | 18 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.3 | 36.6 | 18 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.2 | 36.6 | 17.9 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.2 | 36.6 | 17.9 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:34 | 1 | 25.2 | 36.6 | 17.9 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25.2 | 36.6 | 17.9 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25.1 | 36.6 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25.1 | 36.6 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25.1 | 36.6 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25 | 36.5 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:35 | 1 | 25 | 36.5 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 25 | 36.5 | 17.8 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 25 | 36.5 | 17.8 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 24.9 | 36.5 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 24.9 | 36.5 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 24.9 | 36.5 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:36 | 1 | 24.9 | 36.5 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.8 | 36.5 | 17.7 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.8 | 36.4 | 17.6 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.8 | 36.4 | 17.7 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:37 | 1 | 24.7 | 36.4 | 17.7 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.7 | 36.4 | 17.6 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.7 | 36.4 | 17.6 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.7 | 36.4 | 17.6 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.7 | 36.4 | 17.6 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.6 | 36.4 | 17.6 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:38 | 1 | 24.6 | 36.4 | 17.6 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.6 | 36.3 | 17.5 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:39 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:40 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:40 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:40 | 1 | 24.5 | 36.3 | 17.4 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:40 | 1 | 24.5 | 36.3 | 17.3 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:40 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:40 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 18.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:40 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 18.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.4 | 36.2 | 17.3 | 35.4 | 18.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.4 | 36.2 | 17.1 | 35.4 | 19.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.4 | 36.2 | 16.8 | 35.4 | 21.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.4 | 36.2 | 16.5 | 35.4 | 22.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.3 | 36.2 | 16.3 | 35.4 | 24 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:41 | 1 | 24.3 | 36.2 | 16.1 | 35.4 | 25.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24.3 | 36.1 | 15.9 | 35.4 | 26.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24.2 | 36.1 | 15.7 | 35.4 | 27.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24.2 | 36.1 | 15.5 | 35.4 | 28 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24.1 | 36.1 | 15.4 | 35.4 | 28.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24.1 | 36 | 15.2 | 35.4 | 28.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:42 | 1 | 24 | 36 | 15 | 35.4 | 29.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.9 | 36 | 14.9 | 35.5 | 29.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.8 | 35.9 | 14.8 | 35.5 | 29.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.8 | 35.9 | 14.6 | 35.5 | 30.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.7 | 35.9 | 14.5 | 35.5 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.6 | 35.8 | 14.4 | 35.6 | 30.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:43 | 1 | 23.5 | 35.8 | 14.3 | 35.6 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23.5 | 35.7 | 14.1 | 35.6 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23.4 | 35.7 | 14 | 35.6 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23.3 | 35.7 | 14 | 35.7 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23.2 | 35.6 | 13.9 | 35.7 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23.1 | 35.6 | 13.8 | 35.7 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:44 | 1 | 23 | 35.5 | 13.6 | 35.7 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:45 | 1 | 23 | 35.5 | 13.5 | 35.8 | 31.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 02:45 | 1 | 22.9 | 35.4 | 13.5 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:45 | 1 | 22.9 | 35.4 | 13.5 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:45 | 1 | 22.8 | 35.4 | 13.2 | 35.8 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:45 | 1 | 22.7 | 35.3 | 12.9 | 35.9 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:45 | 1 | 22.6 | 35.3 | 13.8 | 35.9 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:45 | 1 | 22.5 | 35.3 | 15.5 | 35.9 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 22.3 | 35.2 | 17.4 | 35.9 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 22 | 35.2 | 19.1 | 36 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 21.7 | 35.2 | 20.6 | 36 | 31.5 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 21.3 | 35.2 | 22.2 | 36 | 31.6 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 20.9 | 35.2 | 23.6 | 36 | 31.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:46 | 1 | 20.4 | 35.2 | 24.8 | 36.1 | 31.6 | 3.6 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:47 | 1 | 19.9 | 35.2 | 25.6 | 36.1 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 02:47 | 1 | 19.9 | 35.2 | 25.6 | 36.1 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:47 | 1 | 19.9 | 35.2 | 25.8 | 36.1 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:47 | 1 | 19.4 | 35.2 | 26.2 | 36.1 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:47 | 1 | 18.9 | 35.3 | 26.7 | 36.1 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 02:47 | 1 | 18.4 | 35.4 | 27.4 | 36.2 | 31 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:47 | 1 | 18.4 | 35.4 | 27.4 | 36.2 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:47 | 1 | 18.4 | 35.4 | 27.6 | 36.2 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:47 | 1 | 18 | 35.4 | 28.5 | 36.2 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:47 | 1 | 17.6 | 35.5 | 29 | 36.2 | 31.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.6 | 35.6 | 29.5 | 36.3 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.4 | 35.7 | 30 | 36.3 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.3 | 35.8 | 30.3 | 36.3 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.2 | 35.8 | 30.5 | 36.3 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.2 | 35.9 | 30.8 | 36.4 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:48 | 1 | 17.3 | 36 | 30.9 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 17.5 | 36.1 | 31 | 36.4 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 17.7 | 36.1 | 31.1 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 17.8 | 36.2 | 31.2 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 18.1 | 36.3 | 31.2 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 18.4 | 36.4 | 31.3 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:49 | 1 | 18.6 | 36.4 | 31.3 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 18.9 | 36.6 | 31.4 | 36.6 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 19.3 | 36.6 | 31.4 | 36.7 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 19.6 | 36.6 | 31.4 | 36.7 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 20 | 36.7 | 31.5 | 36.7 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 20.3 | 36.7 | 31.5 | 36.7 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:50 | 1 | 20.6 | 36.8 | 31.5 | 36.8 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:51 | 1 | 21 | 36.9 | 31.5 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:51 | 1 | 21.3 | 36.9 | 31.6 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:51 | 1 | 21.8 | 36.9 | 31.6 | 36.9 | 33 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:51 | 1 | 22 | 37 | 31.6 | 36.9 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:51 | 1 | 22.1 | 37 | 31.6 | 36.9 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:51 | 1 | 22.4 | 37 | 31.6 | 36.9 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:51 | 1 | 22.8 | 37.1 | 31.5 | 36.9 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.1 | 37.1 | 31.4 | 37 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.4 | 37.1 | 31.3 | 37 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.6 | 37.2 | 31.3 | 37 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.8 | 37.2 | 31.3 | 37 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.8 | 37.2 | 31.4 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:52 | 1 | 23.8 | 37.3 | 31.4 | 37.1 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 23.6 | 37.3 | 31.4 | 37.1 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 23.4 | 37.3 | 31.5 | 37.1 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 23.1 | 37.4 | 31.5 | 37.1 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 22.7 | 37.4 | 31.5 | 37.1 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 22.3 | 37.4 | 31.5 | 37.1 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:53 | 1 | 21.8 | 37.4 | 31.6 | 37.2 | 32.9 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:54 | 1 | 21.3 | 37.4 | 31.6 | 37.2 | 33 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:54 | 1 | 20.8 | 37.5 | 31.6 | 37.2 | 33 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:54 | 1 | 20.2 | 37.5 | 31.6 | 37.2 | 33.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 02:54 | 1 | 19.9 | 37.5 | 31.6 | 37.2 | 33.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:54 | 1 | 19.9 | 37.5 | 31.6 | 37.2 | 33.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:54 | 1 | 19.6 | 37.5 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:54 | 1 | 19 | 37.5 | 31.7 | 37.2 | 33.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:54 | 1 | 18.5 | 37.5 | 31.7 | 37.2 | 33.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 18.3 | 37.5 | 31.7 | 37.3 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 18 | 37.5 | 31.7 | 37.3 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 17.7 | 37.6 | 31.7 | 37.3 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 17.4 | 37.6 | 31.8 | 37.3 | 33.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 17.2 | 37.6 | 31.9 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 17 | 37.6 | 32 | 37.3 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:55 | 1 | 17 | 37.6 | 32.1 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17 | 37.6 | 32.1 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17 | 37.7 | 32.2 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17.2 | 37.7 | 32.2 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17.4 | 37.7 | 32.1 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17.6 | 37.7 | 32.1 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:56 | 1 | 17.8 | 37.7 | 32.1 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 18.1 | 37.7 | 32.1 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 18.4 | 37.7 | 32.2 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 18.7 | 37.7 | 32.2 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 19.1 | 37.8 | 32.2 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 19.4 | 37.8 | 32.2 | 37.6 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:57 | 1 | 19.7 | 37.8 | 32.3 | 37.6 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 20.1 | 37.8 | 32.3 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 20.5 | 37.8 | 32.3 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 20.8 | 37.8 | 32.4 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 21.2 | 37.8 | 32.4 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 21.6 | 37.8 | 32.5 | 37.7 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 02:58 | 1 | 22 | 37.8 | 32.5 | 37.7 | 34.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:58 | 1 | 22 | 37.8 | 32.5 | 37.7 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 22.3 | 37.9 | 32.6 | 37.7 | 34.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 22.7 | 37.9 | 32 | 37.7 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 23 | 37.9 | 31.2 | 37.7 | 33 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 23.4 | 37.9 | 30.9 | 37.7 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 23.7 | 37.9 | 30.4 | 37.7 | 30.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 02:59 | 1 | 24 | 37.9 | 30 | 37.7 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 24.4 | 37.9 | 29.5 | 37.8 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 24.6 | 38 | 29.1 | 37.8 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 24.9 | 38 | 28.9 | 37.8 | 29.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 25.2 | 38 | 28.7 | 37.8 | 28.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 25.5 | 38 | 28.6 | 37.8 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:00 | 1 | 25.7 | 38 | 28.4 | 37.8 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 26 | 38 | 28.2 | 37.8 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 26.2 | 38.1 | 27.9 | 37.8 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 26.4 | 38.1 | 27.6 | 37.8 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 26.7 | 38.1 | 27.3 | 37.8 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 26.9 | 38.1 | 27 | 37.7 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:01 | 1 | 27.1 | 38.1 | 26.7 | 37.7 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 27.3 | 38.1 | 26.4 | 37.7 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 27.4 | 38.1 | 26.2 | 37.7 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 27.6 | 38.2 | 25.9 | 37.7 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 27.8 | 38.2 | 25.7 | 37.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 28 | 38.2 | 25.5 | 37.7 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:02 | 1 | 28 | 38.2 | 25.3 | 37.7 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.2 | 38.2 | 25 | 37.7 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.3 | 38.2 | 24.9 | 37.6 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.4 | 38.2 | 24.7 | 37.6 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.5 | 38.2 | 24.5 | 37.6 | 25.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.5 | 38.2 | 24.3 | 37.6 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:03 | 1 | 28.5 | 38.2 | 24.1 | 37.6 | 25.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.6 | 38.2 | 24 | 37.6 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.6 | 38.2 | 23.8 | 37.5 | 24.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.6 | 38.2 | 23.6 | 37.5 | 24.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.7 | 38.2 | 23.4 | 37.5 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.7 | 38.2 | 23.2 | 37.5 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:04 | 1 | 28.7 | 38.2 | 23.1 | 37.4 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.7 | 38.1 | 22.9 | 37.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.7 | 38.1 | 22.7 | 37.4 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.8 | 38.1 | 22.5 | 37.4 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.8 | 38.1 | 22.4 | 37.3 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.7 | 38.1 | 22.3 | 37.3 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:05 | 1 | 28.7 | 38.1 | 22.1 | 37.3 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.7 | 38.1 | 21.9 | 37.3 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.7 | 38.1 | 21.8 | 37.2 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.7 | 38.1 | 21.6 | 37.2 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.6 | 38 | 21.5 | 37.2 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.6 | 38 | 21.3 | 37.2 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:06 | 1 | 28.6 | 38 | 21.2 | 37.1 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.5 | 38 | 21.1 | 37.1 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.4 | 38 | 21 | 37.1 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.5 | 38 | 20.8 | 37.1 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.4 | 38 | 20.7 | 37 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.4 | 37.9 | 20.6 | 37 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:07 | 1 | 28.3 | 37.9 | 20.5 | 37 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 28.2 | 37.9 | 20.4 | 36.9 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 28.1 | 37.9 | 20.3 | 36.9 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 28 | 37.9 | 20.3 | 36.9 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 28 | 37.8 | 20.2 | 36.9 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 27.9 | 37.8 | 20.1 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:08 | 1 | 27.9 | 37.8 | 20 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.8 | 37.8 | 19.9 | 36.8 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.7 | 37.8 | 19.8 | 36.8 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.6 | 37.8 | 19.7 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.6 | 37.7 | 19.6 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.5 | 37.7 | 19.5 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:09 | 1 | 27.4 | 37.7 | 19.5 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27.3 | 37.7 | 19.4 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27.3 | 37.7 | 19.4 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27.2 | 37.6 | 19.3 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27.1 | 37.6 | 19.2 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27.1 | 37.6 | 19.1 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:10 | 1 | 27 | 37.6 | 19.1 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 27 | 37.5 | 19 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 26.9 | 37.5 | 19 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 26.8 | 37.5 | 18.9 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 26.7 | 37.5 | 18.9 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 26.6 | 37.4 | 18.8 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:11 | 1 | 26.6 | 37.4 | 18.8 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.5 | 37.4 | 18.7 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.5 | 37.4 | 18.6 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.4 | 37.3 | 18.6 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.4 | 37.3 | 18.6 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.3 | 37.3 | 18.5 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:12 | 1 | 26.2 | 37.3 | 18.5 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 26.2 | 37.2 | 18.4 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 26.2 | 37.2 | 18.4 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 26.1 | 37.2 | 18.3 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 26 | 37.2 | 18.3 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 26 | 37.1 | 18.3 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:13 | 1 | 25.9 | 37.1 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.9 | 37.1 | 18.2 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.8 | 37 | 18.2 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.8 | 37 | 18.1 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.8 | 37 | 18.1 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.7 | 37 | 18.1 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:14 | 1 | 25.6 | 36.9 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.6 | 36.9 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.6 | 36.9 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.5 | 36.9 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.5 | 36.9 | 17.9 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.5 | 36.8 | 17.9 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:15 | 1 | 25.4 | 36.8 | 17.9 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.4 | 36.8 | 17.9 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.3 | 36.8 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.3 | 36.8 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.3 | 36.7 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.2 | 36.7 | 17.8 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:16 | 1 | 25.2 | 36.7 | 17.8 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25.2 | 36.7 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25.1 | 36.7 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25.1 | 36.7 | 17.7 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25.1 | 36.7 | 17.7 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25 | 36.6 | 17.6 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:17 | 1 | 25 | 36.6 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 25 | 36.6 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 25 | 36.6 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 24.9 | 36.6 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 24.9 | 36.6 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 24.9 | 36.6 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:18 | 1 | 24.8 | 36.5 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.8 | 36.5 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.8 | 36.5 | 17.5 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.8 | 36.5 | 17.5 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.7 | 36.5 | 17.4 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.7 | 36.5 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:19 | 1 | 24.7 | 36.5 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.7 | 36.5 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.7 | 36.4 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.6 | 36.4 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.6 | 36.4 | 17.3 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.6 | 36.4 | 17.3 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:20 | 1 | 24.6 | 36.4 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.5 | 36.4 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.5 | 36.4 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.5 | 36.4 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.5 | 36.3 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.5 | 36.3 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:21 | 1 | 24.4 | 36.3 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.4 | 36.3 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.4 | 36.3 | 17.2 | 35.6 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.4 | 36.3 | 17.1 | 35.6 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.4 | 36.3 | 17.1 | 35.6 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.3 | 36.3 | 17.1 | 35.6 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:22 | 1 | 24.3 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.3 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.3 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.3 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.3 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:23 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.5 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.5 | 18.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.5 | 18.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.4 | 18.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.4 | 18.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:24 | 1 | 24.2 | 36.1 | 17.1 | 35.4 | 18.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 16.9 | 35.4 | 19.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 16.7 | 35.4 | 20.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 16.4 | 35.4 | 22.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 16.2 | 35.4 | 23.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 16 | 35.4 | 25 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:25 | 1 | 24.1 | 36.1 | 15.7 | 35.4 | 26 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 24 | 36 | 15.5 | 35.4 | 27 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 24 | 36 | 15.4 | 35.4 | 27.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 24 | 36 | 15.2 | 35.4 | 28.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 23.9 | 36 | 15 | 35.4 | 28.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 23.8 | 35.9 | 14.8 | 35.5 | 29.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:26 | 1 | 23.7 | 35.9 | 14.6 | 35.5 | 29.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.7 | 35.9 | 14.5 | 35.5 | 29.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.6 | 35.8 | 14.4 | 35.5 | 30 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.6 | 35.8 | 14.2 | 35.5 | 30.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.5 | 35.8 | 14.1 | 35.6 | 30.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.4 | 35.7 | 14 | 35.6 | 30.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:27 | 1 | 23.4 | 35.7 | 13.8 | 35.6 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 23.3 | 35.7 | 13.7 | 35.6 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 23.2 | 35.6 | 13.5 | 35.7 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 23.1 | 35.6 | 13.4 | 35.7 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 23 | 35.5 | 13.3 | 35.7 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 22.9 | 35.5 | 13.2 | 35.8 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 03:28 | 1 | 22.9 | 35.4 | 13.2 | 35.8 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:28 | 1 | 22.8 | 35.4 | 13.1 | 35.8 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 22.7 | 35.4 | 12.8 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 22.7 | 35.3 | 12.5 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 22.5 | 35.3 | 13.6 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 22.4 | 35.2 | 15.3 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 22.1 | 35.2 | 17.4 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:29 | 1 | 21.9 | 35.2 | 18.9 | 35.9 | 31.4 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:30 | 1 | 21.6 | 35.2 | 20.6 | 36 | 31.4 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:30 | 1 | 21.2 | 35.2 | 22.2 | 36 | 31.5 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:30 | 1 | 20.7 | 35.2 | 23.4 | 36 | 31.5 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:30 | 1 | 20.2 | 35.2 | 24.7 | 36.1 | 31.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:30 | 1 | 19.9 | 35.2 | 25.3 | 36.1 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 03:30 | 1 | 19.9 | 35.2 | 25.3 | 36.1 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 03:30 | 1 | 19.7 | 35.2 | 25.8 | 36.1 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 03:30 | 1 | 19.2 | 35.2 | 26.1 | 36.1 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 03:31 | 1 | 18.7 | 35.3 | 26.7 | 36.1 | 30.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 03:31 | 1 | 18.5 | 35.4 | 27.2 | 36.1 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 18.5 | 35.4 | 27.2 | 36.1 | 30.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 18.2 | 35.4 | 27.6 | 36.2 | 30.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 17.9 | 35.5 | 28.4 | 36.2 | 30.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 17.7 | 35.5 | 29 | 36.2 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 17.4 | 35.6 | 29.5 | 36.2 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:31 | 1 | 17.3 | 35.7 | 30 | 36.3 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.2 | 35.8 | 30.3 | 36.3 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.2 | 35.8 | 30.6 | 36.3 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.2 | 35.9 | 30.7 | 36.4 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.3 | 36 | 30.9 | 36.4 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.5 | 36.1 | 31 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:32 | 1 | 17.7 | 36.2 | 31.1 | 36.5 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 17.8 | 36.2 | 31.2 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 18.1 | 36.3 | 31.3 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 18.4 | 36.4 | 31.3 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 18.7 | 36.4 | 31.3 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 19 | 36.5 | 31.4 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:33 | 1 | 19.3 | 36.6 | 31.4 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 19.6 | 36.7 | 31.4 | 36.7 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 20 | 36.7 | 31.5 | 36.7 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 20.4 | 36.7 | 31.5 | 36.7 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 20.7 | 36.8 | 31.5 | 36.8 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 21.1 | 36.8 | 31.5 | 36.8 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:34 | 1 | 21.4 | 36.9 | 31.6 | 36.8 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:35 | 1 | 21.8 | 36.9 | 31.6 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:35 | 1 | 22 | 37 | 31.6 | 36.9 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:35 | 1 | 22.1 | 37 | 31.6 | 36.9 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:35 | 1 | 22.5 | 37 | 31.6 | 36.9 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:35 | 1 | 22.8 | 37.1 | 31.5 | 36.9 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:35 | 1 | 23.1 | 37.1 | 31.4 | 36.9 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:35 | 1 | 23.5 | 37.1 | 31.3 | 37 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.7 | 37.2 | 31.3 | 37 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.8 | 37.2 | 31.3 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.8 | 37.2 | 31.4 | 37 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.8 | 37.3 | 31.4 | 37 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.6 | 37.3 | 31.4 | 37.1 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:36 | 1 | 23.4 | 37.3 | 31.5 | 37.1 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 23.1 | 37.3 | 31.5 | 37.1 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 22.7 | 37.4 | 31.5 | 37.1 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 22.2 | 37.4 | 31.5 | 37.1 | 32.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 21.7 | 37.4 | 31.6 | 37.1 | 32.9 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 21.2 | 37.4 | 31.6 | 37.2 | 33 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:37 | 1 | 20.6 | 37.5 | 31.6 | 37.2 | 33.1 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:38 | 1 | 20.1 | 37.5 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 03:38 | 1 | 19.9 | 37.5 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 19.9 | 37.5 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 19.5 | 37.5 | 31.7 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 19 | 37.5 | 31.7 | 37.2 | 33.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 18.4 | 37.5 | 31.7 | 37.2 | 33.4 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 18.2 | 37.5 | 31.7 | 37.2 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 17.9 | 37.5 | 31.7 | 37.3 | 33.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:38 | 1 | 17.6 | 37.6 | 31.8 | 37.3 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 17.3 | 37.6 | 31.9 | 37.3 | 33.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 17.1 | 37.6 | 32 | 37.3 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 16.9 | 37.6 | 32.2 | 37.3 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 16.9 | 37.6 | 32.3 | 37.3 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 16.9 | 37.6 | 32.4 | 37.4 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:39 | 1 | 17 | 37.7 | 32.5 | 37.4 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 17.1 | 37.7 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 17.3 | 37.7 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 17.6 | 37.7 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 17.7 | 37.7 | 32.5 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 18 | 37.7 | 32.6 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:40 | 1 | 18.3 | 37.7 | 32.6 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 18.6 | 37.7 | 32.6 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 18.9 | 37.8 | 32.7 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 19.3 | 37.8 | 32.7 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 19.6 | 37.8 | 32.7 | 37.6 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 20.1 | 37.8 | 32.8 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:41 | 1 | 20.4 | 37.8 | 32.8 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:42 | 1 | 20.8 | 37.8 | 32.9 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:42 | 1 | 21.1 | 37.8 | 32.9 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:42 | 1 | 21.5 | 37.9 | 32.9 | 37.6 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:42 | 1 | 21.9 | 37.9 | 33 | 37.7 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 03:42 | 1 | 22 | 37.9 | 33 | 37.7 | 34.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:42 | 1 | 22.3 | 37.9 | 33 | 37.7 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:42 | 1 | 22.6 | 37.9 | 32.7 | 37.7 | 34.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 23 | 37.9 | 31.7 | 37.7 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 23.3 | 37.9 | 31 | 37.7 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 23.6 | 37.9 | 30.7 | 37.7 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 23.9 | 37.9 | 30.3 | 37.7 | 30.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 24.3 | 38 | 29.8 | 37.7 | 30.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:43 | 1 | 24.5 | 38 | 29.4 | 37.7 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 24.8 | 38 | 29.1 | 37.7 | 29.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 25 | 38 | 28.8 | 37.7 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 25.4 | 38 | 28.7 | 37.7 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 25.7 | 38.1 | 28.6 | 37.7 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 25.9 | 38.1 | 28.5 | 37.7 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:44 | 1 | 26.1 | 38.1 | 28.4 | 37.7 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 26.4 | 38.1 | 28.2 | 37.7 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 26.6 | 38.1 | 27.9 | 37.7 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 26.8 | 38.2 | 27.6 | 37.7 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 27.1 | 38.2 | 27.3 | 37.7 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 27.2 | 38.2 | 27 | 37.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:45 | 1 | 27.4 | 38.2 | 26.7 | 37.7 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 27.6 | 38.2 | 26.4 | 37.7 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 27.7 | 38.2 | 26.2 | 37.7 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 27.9 | 38.2 | 25.9 | 37.7 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 28 | 38.2 | 25.7 | 37.7 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 28.2 | 38.3 | 25.4 | 37.7 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:46 | 1 | 28.3 | 38.3 | 25.2 | 37.6 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.4 | 38.3 | 25 | 37.6 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.5 | 38.3 | 24.8 | 37.6 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.5 | 38.3 | 24.5 | 37.6 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.6 | 38.3 | 24.4 | 37.6 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.6 | 38.3 | 24.2 | 37.6 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:47 | 1 | 28.7 | 38.3 | 23.9 | 37.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.7 | 38.3 | 23.7 | 37.5 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.7 | 38.3 | 23.6 | 37.5 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.7 | 38.3 | 23.4 | 37.5 | 24.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.8 | 38.3 | 23.2 | 37.5 | 24.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.8 | 38.2 | 23 | 37.4 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:48 | 1 | 28.8 | 38.2 | 22.8 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.8 | 38.2 | 22.7 | 37.4 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.8 | 38.2 | 22.5 | 37.4 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.8 | 38.2 | 22.4 | 37.3 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.8 | 38.2 | 22.2 | 37.3 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.8 | 38.2 | 22 | 37.3 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:49 | 1 | 28.7 | 38.2 | 21.9 | 37.3 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.7 | 38.1 | 21.7 | 37.2 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.7 | 38.1 | 21.5 | 37.2 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.6 | 38.1 | 21.5 | 37.2 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.5 | 38.1 | 21.3 | 37.2 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.5 | 38.1 | 21.2 | 37.1 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:50 | 1 | 28.5 | 38 | 21.1 | 37.1 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.5 | 38 | 20.9 | 37.1 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.4 | 38 | 20.8 | 37 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.3 | 38 | 20.7 | 37 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.3 | 38 | 20.6 | 37 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.2 | 38 | 20.5 | 37 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:51 | 1 | 28.2 | 37.9 | 20.4 | 36.9 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 28.1 | 37.9 | 20.3 | 36.9 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 28 | 37.9 | 20.2 | 36.9 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 28 | 37.9 | 20.1 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 27.9 | 37.9 | 20 | 36.8 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 27.8 | 37.8 | 20 | 36.8 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:52 | 1 | 27.7 | 37.8 | 19.9 | 36.8 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.6 | 37.8 | 19.8 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.6 | 37.8 | 19.7 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.5 | 37.8 | 19.6 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.4 | 37.7 | 19.6 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.4 | 37.7 | 19.5 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:53 | 1 | 27.3 | 37.7 | 19.5 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 27.2 | 37.7 | 19.4 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 27.2 | 37.7 | 19.3 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 27.1 | 37.6 | 19.3 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 27 | 37.6 | 19.2 | 36.5 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 26.9 | 37.6 | 19.1 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:54 | 1 | 26.9 | 37.6 | 19.1 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.8 | 37.6 | 19.1 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.8 | 37.5 | 19 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.7 | 37.5 | 19 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.7 | 37.5 | 18.9 | 36.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.6 | 37.5 | 18.9 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:55 | 1 | 26.5 | 37.5 | 18.8 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.4 | 37.5 | 18.8 | 36.3 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.4 | 37.4 | 18.7 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.3 | 37.4 | 18.7 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.3 | 37.4 | 18.6 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.3 | 37.4 | 18.6 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:56 | 1 | 26.2 | 37.4 | 18.5 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 26.1 | 37.3 | 18.5 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 26.1 | 37.3 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 26 | 37.3 | 18.4 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 26 | 37.3 | 18.4 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 25.9 | 37.3 | 18.3 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:57 | 1 | 25.9 | 37.2 | 18.3 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.8 | 37.2 | 18.2 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.8 | 37.2 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.7 | 37.2 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.7 | 37.1 | 18.1 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.7 | 37.1 | 18.1 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:58 | 1 | 25.6 | 37.1 | 18.1 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.6 | 37.1 | 18 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.5 | 37 | 18 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.5 | 37 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.4 | 37 | 17.9 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.4 | 37 | 17.9 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 03:59 | 1 | 25.4 | 36.9 | 17.9 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.3 | 36.9 | 17.8 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.3 | 36.9 | 17.8 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.2 | 36.8 | 17.8 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.2 | 36.8 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.2 | 36.8 | 17.8 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:00 | 1 | 25.1 | 36.8 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 25.1 | 36.7 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 25.1 | 36.7 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 25 | 36.7 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 25 | 36.7 | 17.6 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 25 | 36.7 | 17.7 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:01 | 1 | 24.9 | 36.7 | 17.7 | 35.9 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.9 | 36.6 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.9 | 36.6 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.9 | 36.6 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.8 | 36.6 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.8 | 36.6 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:02 | 1 | 24.8 | 36.6 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.8 | 36.5 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.7 | 36.5 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.7 | 36.5 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.7 | 36.5 | 17.5 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.7 | 36.5 | 17.5 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:03 | 1 | 24.6 | 36.5 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.6 | 36.5 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.6 | 36.5 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.6 | 36.5 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.6 | 36.4 | 17.5 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.5 | 36.4 | 17.4 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:04 | 1 | 24.5 | 36.4 | 17.4 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.5 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.5 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.5 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.4 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.4 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:05 | 1 | 24.4 | 36.4 | 17.4 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.4 | 36.3 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.4 | 36.3 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.4 | 36.3 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.3 | 36.3 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.3 | 36.3 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:06 | 1 | 24.3 | 36.3 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.3 | 36.3 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.3 | 36.3 | 17.2 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.3 | 36.3 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.3 | 36.3 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.2 | 36.3 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:07 | 1 | 24.2 | 36.3 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:08 | 1 | 24.2 | 36.2 | 17.1 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:09 | 1 | 24.2 | 36.2 | 17.1 | 35.4 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.2 | 17.1 | 35.4 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.2 | 17.1 | 35.4 | 19 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.2 | 16.9 | 35.4 | 19.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.2 | 16.6 | 35.4 | 20.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.2 | 16.4 | 35.4 | 22.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:09 | 1 | 24.1 | 36.1 | 16.1 | 35.4 | 23.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 24.1 | 36.1 | 15.9 | 35.4 | 25 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 24 | 36.1 | 15.7 | 35.4 | 26.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 24 | 36.1 | 15.4 | 35.4 | 27 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 24 | 36.1 | 15.3 | 35.4 | 27.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 23.9 | 36 | 15.1 | 35.4 | 28.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:10 | 1 | 23.8 | 36 | 14.9 | 35.4 | 28.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.8 | 36 | 14.7 | 35.5 | 29.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.7 | 36 | 14.6 | 35.5 | 29.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.6 | 35.9 | 14.4 | 35.5 | 29.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.6 | 35.9 | 14.3 | 35.5 | 29.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.5 | 35.8 | 14.2 | 35.5 | 30.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:11 | 1 | 23.4 | 35.8 | 14.1 | 35.6 | 30.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 23.4 | 35.8 | 14 | 35.6 | 30.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 23.3 | 35.7 | 13.8 | 35.6 | 30.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 23.2 | 35.7 | 13.7 | 35.6 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 23.1 | 35.6 | 13.6 | 35.7 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 23 | 35.6 | 13.6 | 35.7 | 30.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:12 | 1 | 22.9 | 35.6 | 13.4 | 35.7 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:13 | 1 | 22.8 | 35.5 | 13.3 | 35.7 | 31 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:13 | 1 | 22.7 | 35.5 | 13.2 | 35.8 | 31.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 04:13 | 1 | 22.6 | 35.4 | 13.2 | 35.8 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:13 | 1 | 22.6 | 35.4 | 13.2 | 35.8 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:13 | 1 | 22.5 | 35.3 | 12.7 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:13 | 1 | 22.4 | 35.3 | 12.7 | 35.8 | 31.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:13 | 1 | 22.3 | 35.3 | 13.9 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 22.2 | 35.2 | 15.7 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 22 | 35.2 | 17.7 | 35.9 | 31.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 21.7 | 35.2 | 19.2 | 36 | 31.4 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 21.3 | 35.2 | 20.9 | 36 | 31.4 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 20.9 | 35.2 | 22.4 | 36 | 31.5 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:14 | 1 | 20.5 | 35.2 | 23.7 | 36 | 31.5 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:15 | 1 | 20.1 | 35.2 | 24.8 | 36.1 | 31.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:15 | 1 | 19.9 | 35.2 | 25.1 | 36.1 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 04:15 | 1 | 19.9 | 35.2 | 25.1 | 36.1 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 04:15 | 1 | 19.5 | 35.2 | 25.7 | 36.1 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 04:15 | 1 | 19.1 | 35.3 | 26.1 | 36.1 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 04:15 | 1 | 18.5 | 35.4 | 27 | 36.2 | 30.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 04:15 | 1 | 18.5 | 35.4 | 27.2 | 36.2 | 30.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:15 | 1 | 18.5 | 35.4 | 27.2 | 36.2 | 30.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:15 | 1 | 18.1 | 35.4 | 27.9 | 36.2 | 30.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:15 | 1 | 17.8 | 35.5 | 28.6 | 36.2 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.6 | 35.5 | 29.2 | 36.2 | 31.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.4 | 35.6 | 29.7 | 36.3 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.3 | 35.7 | 30.1 | 36.3 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.3 | 35.8 | 30.4 | 36.3 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.3 | 35.9 | 30.6 | 36.4 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:16 | 1 | 17.4 | 35.9 | 30.8 | 36.4 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 17.5 | 36 | 30.9 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 17.7 | 36.1 | 31 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 17.8 | 36.2 | 31.1 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 18 | 36.3 | 31.2 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 18.3 | 36.4 | 31.2 | 36.5 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:17 | 1 | 18.6 | 36.4 | 31.2 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 18.9 | 36.4 | 31.3 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 19.2 | 36.5 | 31.3 | 36.6 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 19.5 | 36.5 | 31.4 | 36.7 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 19.9 | 36.6 | 31.4 | 36.7 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 20.2 | 36.7 | 31.4 | 36.7 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:18 | 1 | 20.6 | 36.7 | 31.4 | 36.7 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:19 | 1 | 20.9 | 36.8 | 31.5 | 36.8 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:19 | 1 | 21.3 | 36.8 | 31.5 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:19 | 1 | 21.6 | 36.9 | 31.5 | 36.8 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:19 | 1 | 22 | 36.9 | 31.5 | 36.8 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:19 | 1 | 22 | 36.9 | 31.5 | 36.9 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:19 | 1 | 22.4 | 37 | 31.5 | 36.9 | 33 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:19 | 1 | 22.7 | 37 | 31.5 | 36.9 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.1 | 37 | 31.3 | 36.9 | 31.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.4 | 37.1 | 31.3 | 36.9 | 31.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.6 | 37.1 | 31.3 | 37 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.7 | 37.1 | 31.3 | 37 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.8 | 37.2 | 31.3 | 37 | 32 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:20 | 1 | 23.8 | 37.2 | 31.3 | 37 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 23.6 | 37.2 | 31.3 | 37 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 23.4 | 37.2 | 31.4 | 37.1 | 32.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 23 | 37.3 | 31.4 | 37.1 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 22.7 | 37.3 | 31.4 | 37.1 | 32.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 22.3 | 37.3 | 31.5 | 37.1 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:21 | 1 | 21.8 | 37.3 | 31.5 | 37.1 | 32.9 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:22 | 1 | 21.3 | 37.4 | 31.5 | 37.1 | 33 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:22 | 1 | 20.8 | 37.4 | 31.5 | 37.2 | 33.1 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:22 | 1 | 20.2 | 37.4 | 31.6 | 37.2 | 33.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:22 | 1 | 19.9 | 37.4 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:22 | 1 | 19.9 | 37.4 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:22 | 1 | 19.6 | 37.4 | 31.6 | 37.2 | 33.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:22 | 1 | 19 | 37.4 | 31.6 | 37.2 | 33.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:22 | 1 | 18.4 | 37.5 | 31.6 | 37.2 | 33.4 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 18.3 | 37.5 | 31.6 | 37.2 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 18 | 37.5 | 31.7 | 37.2 | 33.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 17.6 | 37.5 | 31.7 | 37.2 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 17.5 | 37.5 | 31.8 | 37.3 | 33.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 17.2 | 37.5 | 31.9 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 17.1 | 37.5 | 32.1 | 37.3 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:23 | 1 | 17 | 37.6 | 32.3 | 37.3 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17 | 37.6 | 32.4 | 37.3 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17.1 | 37.6 | 32.4 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17.2 | 37.6 | 32.4 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17.5 | 37.6 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17.7 | 37.6 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:24 | 1 | 17.8 | 37.7 | 32.5 | 37.4 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 18.1 | 37.7 | 32.6 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 18.4 | 37.7 | 32.7 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 18.7 | 37.7 | 32.7 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 19.1 | 37.7 | 32.8 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 19.4 | 37.7 | 32.8 | 37.5 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:25 | 1 | 19.8 | 37.7 | 32.9 | 37.5 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 20.1 | 37.7 | 32.9 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 20.5 | 37.8 | 32.9 | 37.6 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 20.8 | 37.8 | 33 | 37.6 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 21.2 | 37.8 | 33 | 37.6 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 21.6 | 37.8 | 33.1 | 37.6 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:26 | 1 | 22 | 37.8 | 33.1 | 37.6 | 34.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:26 | 1 | 22 | 37.8 | 33.1 | 37.6 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 22.4 | 37.8 | 33.1 | 37.7 | 34.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 22.7 | 37.8 | 32.5 | 37.7 | 34.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 23.1 | 37.8 | 31.4 | 37.7 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 23.4 | 37.9 | 30.9 | 37.7 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 23.7 | 37.9 | 30.6 | 37.7 | 30.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:27 | 1 | 24 | 37.9 | 30.2 | 37.7 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 24.4 | 37.9 | 29.7 | 37.7 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 24.6 | 37.9 | 29.3 | 37.7 | 29.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 24.9 | 37.9 | 29 | 37.7 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 25.2 | 37.9 | 28.8 | 37.7 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 25.5 | 37.9 | 28.6 | 37.7 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:28 | 1 | 25.7 | 38 | 28.5 | 37.7 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 26 | 38 | 28.3 | 37.7 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 26.2 | 38 | 28.1 | 37.7 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 26.4 | 38 | 27.7 | 37.7 | 28 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 26.7 | 38 | 27.5 | 37.7 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 26.9 | 38 | 27.1 | 37.7 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:29 | 1 | 27.1 | 38 | 26.9 | 37.7 | 27.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 27.3 | 38.1 | 26.5 | 37.7 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 27.5 | 38.1 | 26.3 | 37.7 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 27.6 | 38.1 | 26 | 37.7 | 26.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 27.8 | 38.1 | 25.8 | 37.7 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 28 | 38.1 | 25.5 | 37.6 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:30 | 1 | 28.1 | 38.1 | 25.3 | 37.6 | 26.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.2 | 38.1 | 25.1 | 37.6 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.3 | 38.1 | 24.9 | 37.6 | 25.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.4 | 38.1 | 24.6 | 37.6 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.5 | 38.1 | 24.5 | 37.6 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.5 | 38.1 | 24.3 | 37.6 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:31 | 1 | 28.5 | 38.1 | 24.1 | 37.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.6 | 38.1 | 23.9 | 37.5 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.6 | 38.1 | 23.8 | 37.5 | 25.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.6 | 38.1 | 23.6 | 37.5 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.7 | 38.1 | 23.4 | 37.5 | 25 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.7 | 38.1 | 23.2 | 37.4 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:32 | 1 | 28.7 | 38.1 | 23 | 37.4 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:33 | 1 | 28.7 | 38.1 | 22.9 | 37.4 | 23.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:33 | 1 | 28.7 | 38 | 22.7 | 37.4 | 23.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:33 | 1 | 28.8 | 38 | 22.6 | 37.3 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:33 | 1 | 28.8 | 38 | 22.6 | 37.3 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:33 | 1 | 28.8 | 38 | 22.3 | 37.3 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:33 | 1 | 28.7 | 38 | 21.8 | 37.3 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:33 | 1 | 28.7 | 38 | 22.2 | 37.3 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 28.6 | 38 | 23.4 | 37.2 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 28.5 | 38 | 24.8 | 37.2 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 28.3 | 38 | 25.9 | 37.2 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 28 | 38 | 27.1 | 37.2 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 27.6 | 38 | 28 | 37.2 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:34 | 1 | 27.1 | 38 | 28.6 | 37.2 | 29 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 26.5 | 38 | 29.2 | 37.2 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 25.9 | 38 | 29.7 | 37.2 | 29.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 25.2 | 38.1 | 30.1 | 37.2 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 24.6 | 38.1 | 30.3 | 37.2 | 30.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 23.8 | 38.1 | 30.6 | 37.2 | 30.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:35 | 1 | 23.1 | 38.1 | 30.8 | 37.2 | 31 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:36 | 1 | 22.3 | 38.2 | 30.9 | 37.2 | 31.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:36 | 1 | 21.6 | 38.2 | 31 | 37.2 | 31.3 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:36 | 1 | 20.9 | 38.2 | 31.1 | 37.2 | 31.4 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:36 | 1 | 20.2 | 38.3 | 31.2 | 37.2 | 31.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:36 | 1 | 19.9 | 38.3 | 31.2 | 37.2 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:36 | 1 | 19.9 | 38.3 | 31.2 | 37.2 | 31.5 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:36 | 1 | 19.4 | 38.3 | 31.3 | 37.2 | 31.6 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:36 | 1 | 18.7 | 38.3 | 31.3 | 37.2 | 31.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 18.1 | 38.4 | 31.3 | 37.2 | 31.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 17.9 | 38.4 | 31.3 | 37.2 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 17.6 | 38.4 | 31.4 | 37.3 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 17.1 | 38.4 | 31.4 | 37.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 16.8 | 38.4 | 31.5 | 37.3 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 16.5 | 38.5 | 31.6 | 37.3 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:37 | 1 | 16.3 | 38.5 | 31.7 | 37.3 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.3 | 38.5 | 31.8 | 37.4 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.2 | 38.5 | 31.8 | 37.4 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.3 | 38.6 | 31.9 | 37.4 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.4 | 38.6 | 31.9 | 37.4 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.7 | 38.6 | 32 | 37.4 | 32.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:38 | 1 | 16.9 | 38.6 | 32 | 37.5 | 33 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 17.1 | 38.6 | 32.1 | 37.5 | 33.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 17.4 | 38.7 | 32.1 | 37.5 | 33.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 17.7 | 38.7 | 32.2 | 37.5 | 33.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 18 | 38.7 | 32.3 | 37.5 | 33.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 18.4 | 38.7 | 32.4 | 37.6 | 33.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:39 | 1 | 18.7 | 38.7 | 32.5 | 37.6 | 33.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 19.1 | 38.7 | 32.5 | 37.6 | 33.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 19.4 | 38.7 | 32.6 | 37.6 | 33.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 19.8 | 38.8 | 32.7 | 37.6 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 20.2 | 38.8 | 32.8 | 37.6 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 20.6 | 38.8 | 32.9 | 37.7 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:40 | 1 | 21 | 38.8 | 32.9 | 37.7 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:41 | 1 | 21.4 | 38.8 | 33 | 37.7 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:41 | 1 | 21.7 | 38.8 | 33.1 | 37.7 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:41 | 1 | 22 | 38.8 | 33.1 | 37.7 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:41 | 1 | 22.1 | 38.8 | 33.2 | 37.7 | 34.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:41 | 1 | 22.5 | 38.8 | 33.1 | 37.8 | 34.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:41 | 1 | 22.9 | 38.9 | 32.6 | 37.8 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:41 | 1 | 23.2 | 38.9 | 32.5 | 37.8 | 33.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 23.5 | 38.9 | 32.5 | 37.8 | 33.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 23.8 | 38.9 | 32.7 | 37.8 | 33.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 23.9 | 38.9 | 32.9 | 37.8 | 33.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 24 | 38.9 | 33 | 37.8 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 24 | 38.9 | 33.1 | 37.8 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:42 | 1 | 23.9 | 38.9 | 33.2 | 37.9 | 33.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 23.7 | 38.9 | 33.3 | 37.9 | 33.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 23.4 | 38.9 | 33.3 | 37.9 | 33.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 23 | 38.9 | 33.4 | 37.9 | 34 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 22.6 | 38.8 | 33.4 | 37.9 | 34 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 22.2 | 38.8 | 33.5 | 37.9 | 34 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:43 | 1 | 21.7 | 38.8 | 33.5 | 37.9 | 34.1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:44 | 1 | 21.1 | 38.8 | 33.6 | 37.9 | 34.1 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:44 | 1 | 20.6 | 38.8 | 33.6 | 38 | 34.2 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:44 | 1 | 20 | 38.8 | 33.6 | 38 | 34.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 04:44 | 1 | 19.9 | 38.8 | 33.6 | 38 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:44 | 1 | 19.9 | 38.8 | 33.6 | 38 | 34.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:44 | 1 | 19.4 | 38.8 | 33.7 | 38 | 34.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:44 | 1 | 18.8 | 38.8 | 33.7 | 38 | 34.3 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:44 | 1 | 18.3 | 38.8 | 33.7 | 38 | 34.4 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 04:44 | 1 | 18.3 | 38.8 | 33.7 | 38 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17.8 | 38.8 | 33.8 | 38 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17.6 | 38.8 | 33.9 | 38 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17.3 | 38.8 | 34.1 | 38 | 34.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17.1 | 38.8 | 34.3 | 38.1 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17 | 38.8 | 34.4 | 38.1 | 35.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:45 | 1 | 17 | 38.8 | 34.6 | 38.1 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17 | 38.8 | 34.7 | 38.1 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17.1 | 38.8 | 34.8 | 38.1 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17.2 | 38.8 | 34.7 | 38.1 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17.5 | 38.8 | 34.6 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17.7 | 38.8 | 34.5 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:46 | 1 | 17.8 | 38.8 | 34.4 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 18.1 | 38.8 | 34.3 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 18.4 | 38.8 | 34.3 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 18.7 | 38.8 | 34.2 | 38.2 | 35.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 19.1 | 38.8 | 34.2 | 38.2 | 35.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 19.4 | 38.8 | 34.2 | 38.3 | 35.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:47 | 1 | 19.8 | 38.8 | 34.2 | 38.3 | 35.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:48 | 1 | 20.2 | 38.8 | 34.2 | 38.3 | 35.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:48 | 1 | 20.5 | 38.8 | 34.2 | 38.3 | 35.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 04:48 | 1 | 20.9 | 38.8 | 34.2 | 38.3 | 35.8 | 4.3 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 04:48 | 1 | 20.9 | 38.8 | 34.2 | 38.3 | 35.8 | 4.1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-08 04:48 | 1 | 20.9 | 38.8 | 34.2 | 38.3 | 35.8 | 4.1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
2022-09-08 04:48 | 1 | 21.1 | 38.8 | 34.3 | 38.3 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:48 | 1 | 21.3 | 38.8 | 34.3 | 38.3 | 35.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:48 | 1 | 21.6 | 38.8 | 33.5 | 38.3 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:48 | 1 | 22 | 38.8 | 32.1 | 38.4 | 34.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 22.4 | 38.8 | 30.9 | 38.4 | 32.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 22.7 | 38.8 | 30.4 | 38.4 | 31.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 23.1 | 38.8 | 30.4 | 38.4 | 30.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 23.4 | 38.8 | 30.1 | 38.4 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 23.7 | 38.8 | 29.9 | 38.4 | 29.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:49 | 1 | 24.1 | 38.8 | 29.7 | 38.4 | 29.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 24.4 | 38.8 | 29.4 | 38.4 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 24.7 | 38.8 | 29.3 | 38.4 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 25.1 | 38.8 | 29.1 | 38.4 | 29.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 25.3 | 38.8 | 29 | 38.4 | 29 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 25.7 | 38.8 | 28.9 | 38.4 | 28.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:50 | 1 | 25.9 | 38.8 | 28.8 | 38.4 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 26.2 | 38.8 | 28.6 | 38.3 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 26.5 | 38.8 | 28.5 | 38.3 | 28.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 26.7 | 38.8 | 28.2 | 38.3 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 26.9 | 38.8 | 27.9 | 38.3 | 28.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 27.2 | 38.9 | 27.6 | 38.3 | 28.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:51 | 1 | 27.4 | 38.9 | 27.4 | 38.3 | 27.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 27.6 | 38.9 | 27.1 | 38.3 | 27.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 27.8 | 38.9 | 26.9 | 38.3 | 27.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 28 | 38.9 | 26.6 | 38.2 | 27.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 28.2 | 38.9 | 26.4 | 38.2 | 27.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 28.3 | 38.9 | 26.1 | 38.2 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:52 | 1 | 28.4 | 38.9 | 25.9 | 38.2 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.4 | 38.9 | 25.7 | 38.2 | 26.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.6 | 38.9 | 25.5 | 38.2 | 26.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.7 | 38.9 | 25.3 | 38.1 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.8 | 38.9 | 25.1 | 38.1 | 27 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.8 | 38.9 | 24.9 | 38.1 | 26.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:53 | 1 | 28.9 | 38.9 | 24.8 | 38.1 | 26.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 28.9 | 38.9 | 24.6 | 38.1 | 26.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 29 | 38.9 | 24.4 | 38 | 25.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 29 | 38.9 | 24.2 | 38 | 25.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 29.1 | 38.9 | 24.1 | 38 | 25.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 29.1 | 38.9 | 23.9 | 38 | 25.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:54 | 1 | 29.1 | 38.9 | 23.8 | 38 | 24.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.1 | 38.8 | 23.6 | 37.9 | 24.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.1 | 38.8 | 23.4 | 37.9 | 24.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.1 | 38.8 | 23.3 | 37.9 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.2 | 38.8 | 23.1 | 37.9 | 24.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.2 | 38.8 | 22.9 | 37.8 | 24 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:55 | 1 | 29.1 | 38.8 | 22.8 | 37.8 | 23.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29.1 | 38.8 | 22.7 | 37.8 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29.1 | 38.8 | 22.5 | 37.8 | 23.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29.1 | 38.7 | 22.4 | 37.7 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29.1 | 38.7 | 22.3 | 37.7 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29 | 38.7 | 22.1 | 37.7 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:56 | 1 | 29 | 38.7 | 22 | 37.7 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 29 | 38.7 | 21.8 | 37.6 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 28.9 | 38.6 | 21.7 | 37.6 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 28.9 | 38.6 | 21.5 | 37.6 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 28.8 | 38.6 | 21.4 | 37.6 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 28.7 | 38.6 | 21.3 | 37.5 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:57 | 1 | 28.7 | 38.6 | 21.2 | 37.5 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.6 | 38.6 | 21.1 | 37.5 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.6 | 38.5 | 21 | 37.5 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.5 | 38.5 | 20.9 | 37.4 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.5 | 38.5 | 20.8 | 37.4 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.5 | 38.5 | 20.7 | 37.4 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:58 | 1 | 28.4 | 38.5 | 20.6 | 37.3 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 28.4 | 38.4 | 20.5 | 37.3 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 28.3 | 38.4 | 20.4 | 37.3 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 28.2 | 38.4 | 20.3 | 37.3 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 28.1 | 38.4 | 20.2 | 37.2 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 28 | 38.3 | 20.1 | 37.2 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 04:59 | 1 | 27.9 | 38.3 | 20.1 | 37.2 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.9 | 38.3 | 20 | 37.2 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.8 | 38.3 | 20 | 37.1 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.8 | 38.3 | 19.9 | 37.1 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.7 | 38.2 | 19.8 | 37.1 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.6 | 38.2 | 19.7 | 37.1 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:00 | 1 | 27.6 | 38.2 | 19.7 | 37 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.5 | 38.2 | 19.6 | 37 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.4 | 38.1 | 19.6 | 37 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.3 | 38.1 | 19.5 | 37 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.2 | 38.1 | 19.5 | 36.9 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.2 | 38.1 | 19.4 | 36.9 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:01 | 1 | 27.1 | 38 | 19.4 | 36.9 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 27.1 | 38 | 19.3 | 36.9 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 27 | 38 | 19.3 | 36.8 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 27 | 38 | 19.2 | 36.8 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 26.9 | 37.9 | 19.1 | 36.8 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 26.8 | 37.9 | 19.1 | 36.8 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:02 | 1 | 26.8 | 37.9 | 19.1 | 36.8 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.7 | 37.9 | 19 | 36.7 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.7 | 37.8 | 19 | 36.7 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.6 | 37.8 | 18.9 | 36.7 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.5 | 37.8 | 18.9 | 36.7 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.5 | 37.8 | 18.9 | 36.7 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:03 | 1 | 26.5 | 37.7 | 18.8 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.4 | 37.7 | 18.8 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.4 | 37.7 | 18.7 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.3 | 37.7 | 18.7 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.3 | 37.6 | 18.7 | 36.6 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.2 | 37.6 | 18.6 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:04 | 1 | 26.2 | 37.6 | 18.6 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 26.1 | 37.6 | 18.5 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 26.1 | 37.6 | 18.5 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 26 | 37.5 | 18.5 | 36.5 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 26 | 37.5 | 18.4 | 36.5 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 26 | 37.5 | 18.4 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:05 | 1 | 25.9 | 37.5 | 18.4 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.9 | 37.4 | 18.3 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.8 | 37.4 | 18.3 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.8 | 37.4 | 18.3 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.7 | 37.4 | 18.2 | 36.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.7 | 37.3 | 18.2 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:06 | 1 | 25.7 | 37.3 | 18.2 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.6 | 37.3 | 18.1 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.6 | 37.3 | 18.1 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.6 | 37.2 | 18.1 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.5 | 37.2 | 18.1 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.5 | 37.2 | 18 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:07 | 1 | 25.4 | 37.2 | 18 | 36.3 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.4 | 37.1 | 18 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.4 | 37.1 | 18 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.3 | 37.1 | 17.9 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.3 | 37.1 | 17.9 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.3 | 37 | 17.9 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:08 | 1 | 25.2 | 37 | 17.9 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.2 | 37 | 17.9 | 36.2 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.2 | 37 | 17.8 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.2 | 37 | 17.8 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.1 | 36.9 | 17.8 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.1 | 36.9 | 17.8 | 36.1 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:09 | 1 | 25.1 | 36.9 | 17.8 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 25 | 36.9 | 17.7 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 25 | 36.8 | 17.7 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 25 | 36.8 | 17.7 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 25 | 36.8 | 17.7 | 36.1 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 24.9 | 36.8 | 17.7 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:10 | 1 | 24.9 | 36.7 | 17.6 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.9 | 36.7 | 17.6 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.9 | 36.7 | 17.6 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.9 | 36.7 | 17.7 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.8 | 36.6 | 17.7 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.8 | 36.6 | 17.7 | 36 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:11 | 1 | 24.8 | 36.6 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.8 | 36.6 | 17.7 | 36 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.8 | 36.5 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.7 | 36.5 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.7 | 36.5 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.7 | 36.5 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:12 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.7 | 36.4 | 17.6 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.6 | 36.4 | 17.6 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.6 | 36.4 | 17.6 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.6 | 36.3 | 17.6 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.6 | 36.3 | 17.6 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:13 | 1 | 24.6 | 36.3 | 17.5 | 35.8 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.3 | 17.5 | 35.8 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.2 | 17.5 | 35.8 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.2 | 17.5 | 35.8 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.2 | 17.5 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.1 | 17.5 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:14 | 1 | 24.5 | 36.1 | 17.5 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.5 | 36.1 | 17.4 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.4 | 36 | 17.4 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.4 | 36 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.4 | 36 | 17.4 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.4 | 36 | 17.4 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:15 | 1 | 24.4 | 35.9 | 17.4 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.4 | 35.9 | 17.3 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.4 | 35.9 | 17.3 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.3 | 35.9 | 17.3 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.3 | 35.8 | 17.3 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.3 | 35.8 | 17.2 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:16 | 1 | 24.3 | 35.8 | 17.2 | 35.7 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.3 | 35.8 | 17.2 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.3 | 35.8 | 17.2 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.3 | 35.7 | 17.2 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.2 | 35.7 | 17.2 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.2 | 35.7 | 17.2 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:17 | 1 | 24.2 | 35.7 | 17.2 | 35.6 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.2 | 35.7 | 17.1 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.2 | 35.7 | 17.1 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.2 | 35.6 | 17.1 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.2 | 35.6 | 17.1 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.2 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:18 | 1 | 24.1 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.6 | 17 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.6 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:19 | 1 | 24.1 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24.1 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:20 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.5 | 17 | 35.5 | 19 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.5 | 17 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.5 | 17 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.4 | 17 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:21 | 1 | 24 | 35.4 | 17 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 16.9 | 35.5 | 19.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 16.8 | 35.4 | 19.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 16.7 | 35.4 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 17.4 | 35.4 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 18.7 | 35.4 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:22 | 1 | 23.9 | 35.4 | 20.2 | 35.4 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:22 | 1 | 23.8 | 35.4 | 21.6 | 35.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 23.6 | 35.4 | 22.9 | 35.4 | 23 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 23.4 | 35.5 | 24.1 | 35.4 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 23.1 | 35.5 | 25.2 | 35.4 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 22.6 | 35.5 | 26.2 | 35.4 | 26.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 22.2 | 35.6 | 27 | 35.4 | 27.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:23 | 1 | 21.8 | 35.7 | 27.7 | 35.4 | 27.9 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:24 | 1 | 21.3 | 35.8 | 28.4 | 35.5 | 28.5 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:24 | 1 | 20.7 | 35.9 | 28.7 | 35.5 | 28.8 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:24 | 1 | 20.2 | 35.9 | 29.1 | 35.5 | 29.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:24 | 1 | 19.9 | 36 | 29.2 | 35.5 | 29.3 | 3.6 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 05:24 | 1 | 19.9 | 36 | 29.2 | 35.5 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 05:24 | 1 | 19.6 | 36 | 29.4 | 35.5 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 05:24 | 1 | 19.1 | 36.1 | 28.6 | 35.6 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 05:24 | 1 | 18.5 | 36.1 | 28.8 | 35.6 | 29.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 05:25 | 1 | 18.3 | 36.2 | 29 | 35.6 | 29.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 18.3 | 36.2 | 29 | 35.6 | 29.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 18.1 | 36.2 | 29.4 | 35.6 | 29.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 17.7 | 36.3 | 29.8 | 35.7 | 30.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 17.4 | 36.3 | 30.2 | 35.7 | 30.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 17.2 | 36.4 | 30.4 | 35.7 | 30.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 17 | 36.5 | 30.7 | 35.8 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:25 | 1 | 17 | 36.5 | 30.8 | 35.8 | 31.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17 | 36.6 | 30.9 | 35.9 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17 | 36.7 | 31.1 | 35.9 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17.1 | 36.8 | 31.1 | 36 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17.3 | 36.8 | 31.2 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17.6 | 36.8 | 31.2 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:26 | 1 | 17.7 | 36.9 | 31.3 | 36.1 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 17.9 | 36.9 | 31.3 | 36.1 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 18.2 | 37 | 31.3 | 36.2 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 18.5 | 37 | 31.4 | 36.2 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 18.9 | 37.1 | 31.4 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 19.2 | 37.1 | 31.4 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:27 | 1 | 19.5 | 37.2 | 31.5 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 19.9 | 37.2 | 31.5 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 20.2 | 37.3 | 31.5 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 20.5 | 37.3 | 31.5 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 20.9 | 37.3 | 31.5 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 21.2 | 37.4 | 31.6 | 36.5 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:28 | 1 | 21.6 | 37.4 | 31.6 | 36.6 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:29 | 1 | 22 | 37.4 | 31.6 | 36.6 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:29 | 1 | 22 | 37.4 | 31.6 | 36.6 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:29 | 1 | 22.3 | 37.5 | 31.6 | 36.6 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:29 | 1 | 22.7 | 37.5 | 31.6 | 36.7 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:29 | 1 | 23 | 37.5 | 31.6 | 36.7 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:29 | 1 | 23.3 | 37.6 | 31.6 | 36.7 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:29 | 1 | 23.3 | 37.6 | 31.6 | 36.7 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:29 | 1 | 23.6 | 37.6 | 31.3 | 36.7 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 23.8 | 37.6 | 30 | 36.8 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 23.9 | 37.6 | 28.7 | 36.8 | 31.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 24 | 37.6 | 27.3 | 36.8 | 32 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 24.1 | 37.6 | 26.1 | 36.9 | 32 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 24.2 | 37.6 | 25.3 | 36.9 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:30 | 1 | 24.3 | 37.6 | 24.6 | 36.9 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.4 | 37.6 | 24.1 | 36.9 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.5 | 37.6 | 23.7 | 36.9 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.6 | 37.6 | 23.3 | 36.9 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.6 | 37.6 | 22.9 | 37 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.7 | 37.6 | 22.5 | 37 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:31 | 1 | 24.8 | 37.5 | 22.1 | 37 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 24.8 | 37.5 | 21.8 | 37 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 24.9 | 37.5 | 21.5 | 37 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 25 | 37.5 | 21.1 | 37 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 25 | 37.4 | 20.8 | 37 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 25.1 | 37.4 | 20.6 | 37 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:32 | 1 | 25.1 | 37.4 | 20.2 | 37 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.1 | 37.3 | 20 | 37.1 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.2 | 37.3 | 19.7 | 37.1 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.2 | 37.2 | 19.5 | 37.1 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.2 | 37.2 | 19.2 | 37.1 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.2 | 37.1 | 19 | 37.1 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:33 | 1 | 25.2 | 37.1 | 18.8 | 37.1 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.2 | 37 | 18.5 | 37.1 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.2 | 37 | 18.3 | 37.1 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.2 | 36.9 | 18.1 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.2 | 36.9 | 17.9 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.2 | 36.8 | 17.7 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:34 | 1 | 25.1 | 36.8 | 17.7 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 25.1 | 36.7 | 17.5 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 25 | 36.6 | 17.2 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 25 | 36.6 | 17 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 24.9 | 36.5 | 16.8 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 24.8 | 36.5 | 16.6 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:35 | 1 | 24.7 | 36.4 | 16.5 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.6 | 36.4 | 16.3 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.5 | 36.3 | 16.2 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.4 | 36.2 | 16 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.4 | 36.1 | 15.9 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.3 | 36.1 | 15.7 | 37.1 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:36 | 1 | 24.2 | 36 | 15.5 | 37.2 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 24.1 | 35.9 | 15.4 | 37.2 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 24 | 35.9 | 15.2 | 37.2 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 23.9 | 35.8 | 15.1 | 37.2 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 23.8 | 35.8 | 15 | 37.2 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 23.7 | 35.7 | 14.9 | 37.2 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:37 | 1 | 23.6 | 35.6 | 14.7 | 37.2 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:38 | 1 | 23.5 | 35.5 | 14.6 | 37.2 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 05:38 | 1 | 23.5 | 35.4 | 14.5 | 37.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:38 | 1 | 23.4 | 35.4 | 14.5 | 37.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:38 | 1 | 23.3 | 35.3 | 14 | 37.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:38 | 1 | 23.2 | 35.2 | 13.9 | 37.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:38 | 1 | 23.1 | 35.1 | 15.3 | 37.2 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:38 | 1 | 23 | 35 | 17.1 | 37.2 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 22.7 | 35 | 18.8 | 37.2 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 22.4 | 34.9 | 20.5 | 37.2 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 22 | 34.9 | 22.1 | 37.2 | 33.6 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 21.6 | 34.9 | 23.6 | 37.2 | 33.7 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 21.1 | 34.9 | 24.9 | 37.2 | 33.7 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:39 | 1 | 20.6 | 34.9 | 25.9 | 37.2 | 33.8 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:40 | 1 | 20.1 | 34.9 | 27 | 37.2 | 33.9 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 05:40 | 1 | 19.9 | 34.9 | 27.1 | 37.2 | 33.9 | 3.5 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 05:40 | 1 | 19.9 | 34.9 | 27.1 | 37.2 | 33.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 05:40 | 1 | 19.5 | 34.9 | 27.4 | 37.2 | 33.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 05:40 | 1 | 19 | 34.9 | 26.1 | 37.2 | 34 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 05:40 | 1 | 18.4 | 35 | 26.5 | 37.2 | 34 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 05:40 | 1 | 18.3 | 35 | 26.8 | 37.2 | 34.1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 05:40 | 1 | 18.3 | 35 | 26.8 | 37.2 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:40 | 1 | 18 | 35 | 27.7 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:40 | 1 | 17.6 | 35.1 | 28.5 | 37.3 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.5 | 35.2 | 29.2 | 37.3 | 34.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.4 | 35.2 | 29.7 | 37.3 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.3 | 35.3 | 30.1 | 37.3 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.3 | 35.4 | 30.5 | 37.3 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.3 | 35.4 | 30.7 | 37.3 | 34.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:41 | 1 | 17.4 | 35.5 | 30.9 | 37.4 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 17.6 | 35.5 | 31 | 37.4 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 17.7 | 35.6 | 31.1 | 37.4 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 17.9 | 35.6 | 31.2 | 37.4 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 18.1 | 35.7 | 31.2 | 37.4 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 18.4 | 35.8 | 31.2 | 37.5 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:42 | 1 | 18.7 | 35.9 | 31.3 | 37.5 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 19 | 35.9 | 31.3 | 37.5 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 19.4 | 36 | 31.4 | 37.5 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 19.8 | 36 | 31.4 | 37.5 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 20.1 | 36.1 | 31.4 | 37.6 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 20.5 | 36.2 | 31.5 | 37.6 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:43 | 1 | 20.8 | 36.2 | 31.5 | 37.6 | 35.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:44 | 1 | 21.3 | 36.2 | 31.5 | 37.6 | 35.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:44 | 1 | 21.6 | 36.3 | 31.5 | 37.6 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 05:44 | 1 | 22 | 36.3 | 31.5 | 37.7 | 35.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:44 | 1 | 22 | 36.3 | 31.5 | 37.7 | 35.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:44 | 1 | 22.4 | 36.4 | 31.6 | 37.7 | 35.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:44 | 1 | 22.7 | 36.4 | 31.6 | 37.7 | 35 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:44 | 1 | 23.1 | 36.5 | 31.6 | 37.7 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 23.5 | 36.5 | 31.5 | 37.7 | 31.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 23.8 | 36.6 | 31.5 | 37.7 | 30.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 24.1 | 36.6 | 31.5 | 37.7 | 29.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 24.4 | 36.7 | 31.5 | 37.8 | 28.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 24.6 | 36.8 | 31.5 | 37.8 | 27.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:45 | 1 | 24.9 | 36.8 | 31.5 | 37.8 | 27 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 25.1 | 36.9 | 31.6 | 37.8 | 26.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 25.3 | 36.9 | 31.6 | 37.8 | 25.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 25.6 | 37 | 31.6 | 37.8 | 25.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 25.7 | 37 | 31.6 | 37.8 | 25.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 25.8 | 37.1 | 31.6 | 37.8 | 24.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:46 | 1 | 26 | 37.2 | 31.6 | 37.7 | 24.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.1 | 37.2 | 31.7 | 37.7 | 23.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.2 | 37.2 | 31.7 | 37.7 | 23.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.3 | 37.3 | 31.7 | 37.7 | 23.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.3 | 37.4 | 31.7 | 37.7 | 22.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.4 | 37.4 | 31.7 | 37.7 | 22 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:47 | 1 | 26.5 | 37.4 | 31.8 | 37.6 | 21.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:48 | 1 | 26.5 | 37.5 | 31.8 | 37.6 | 20.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:48 | 1 | 26.5 | 37.5 | 31.8 | 37.6 | 20.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 05:48 | 1 | 26.5 | 37.6 | 31.8 | 37.6 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:48 | 1 | 26.5 | 37.6 | 31.7 | 37.6 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:48 | 1 | 26.5 | 37.6 | 31.2 | 37.5 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:48 | 1 | 26.6 | 37.7 | 30 | 37.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:48 | 1 | 26.6 | 37.7 | 28.7 | 37.5 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.7 | 27.6 | 37.4 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.8 | 26.7 | 37.4 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.8 | 26 | 37.4 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.8 | 25.6 | 37.4 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.8 | 25.2 | 37.3 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:49 | 1 | 26.6 | 37.9 | 24.9 | 37.3 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.6 | 37.9 | 24.5 | 37.3 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.6 | 37.9 | 24.3 | 37.3 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.7 | 37.9 | 24.1 | 37.2 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.7 | 38 | 24 | 37.2 | 23.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.7 | 38 | 23.8 | 37.2 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:50 | 1 | 26.7 | 38 | 23.7 | 37.2 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.8 | 38 | 23.7 | 37.2 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.8 | 38 | 23.6 | 37.2 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.8 | 38 | 23.6 | 37.1 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.8 | 38.1 | 23.6 | 37.1 | 23.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.9 | 38.1 | 23.5 | 37.1 | 23.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:51 | 1 | 26.9 | 38.1 | 23.4 | 37.1 | 23.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 26.9 | 38.1 | 23.2 | 37.1 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 26.9 | 38.1 | 23 | 37.1 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 27 | 38.1 | 22.8 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 27 | 38.1 | 22.6 | 37 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 27 | 38.1 | 22.5 | 37 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:52 | 1 | 27 | 38 | 22.4 | 37 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27 | 38 | 22.2 | 37 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27.1 | 38 | 22 | 37 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27.1 | 38 | 21.8 | 37 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27.1 | 38 | 21.7 | 36.9 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27.1 | 38 | 21.5 | 36.9 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:53 | 1 | 27.1 | 37.9 | 21.4 | 36.9 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.9 | 21.3 | 36.9 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.9 | 21.2 | 36.9 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.9 | 21 | 36.8 | 21.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.9 | 20.9 | 36.8 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.8 | 20.8 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:54 | 1 | 27.1 | 37.8 | 20.7 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27.1 | 37.8 | 20.6 | 36.8 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27.1 | 37.8 | 20.4 | 36.7 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27.1 | 37.8 | 20.3 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27 | 37.7 | 20.2 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27 | 37.7 | 20.1 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:55 | 1 | 27 | 37.7 | 20 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 27 | 37.7 | 19.9 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 26.9 | 37.6 | 19.8 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 26.9 | 37.6 | 19.7 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 26.9 | 37.6 | 19.6 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 26.8 | 37.6 | 19.6 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:56 | 1 | 26.8 | 37.5 | 19.5 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.8 | 37.5 | 19.4 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.7 | 37.5 | 19.3 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.7 | 37.5 | 19.2 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.6 | 37.4 | 19.2 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.6 | 37.4 | 19.1 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:57 | 1 | 26.5 | 37.4 | 19.1 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.5 | 37.4 | 19 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.4 | 37.3 | 18.9 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.4 | 37.3 | 18.9 | 36.4 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.4 | 37.3 | 18.8 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.3 | 37.2 | 18.8 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:58 | 1 | 26.3 | 37.2 | 18.7 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26.2 | 37.2 | 18.7 | 36.3 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26.1 | 37.2 | 18.6 | 36.3 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26.1 | 37.1 | 18.6 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26.1 | 37.1 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26 | 37.1 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 05:59 | 1 | 26 | 37 | 18.5 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 26 | 37 | 18.4 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 25.9 | 37 | 18.4 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 25.9 | 37 | 18.4 | 36.2 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 25.8 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 25.8 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:00 | 1 | 25.7 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.7 | 36.8 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.7 | 36.8 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.6 | 36.8 | 18.2 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.6 | 36.7 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.5 | 36.7 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:01 | 1 | 25.5 | 36.7 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.5 | 36.6 | 18 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.4 | 36.6 | 18 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.4 | 36.6 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.4 | 36.6 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.3 | 36.5 | 17.9 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:02 | 1 | 25.3 | 36.5 | 17.9 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.3 | 36.5 | 17.9 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.2 | 36.4 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.2 | 36.4 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.2 | 36.4 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.1 | 36.3 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:03 | 1 | 25.1 | 36.3 | 17.7 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 25.1 | 36.2 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 25 | 36.2 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 25 | 36.2 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 25 | 36.1 | 17.6 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 25 | 36.1 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:04 | 1 | 24.9 | 36.1 | 17.7 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.9 | 36 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.9 | 36 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.8 | 36 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.8 | 36 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.8 | 35.9 | 17.6 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:05 | 1 | 24.8 | 35.9 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.7 | 35.9 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.7 | 35.9 | 17.5 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.7 | 35.9 | 17.5 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.7 | 35.8 | 17.5 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.6 | 35.8 | 17.5 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:06 | 1 | 24.6 | 35.8 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.6 | 35.8 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.6 | 35.8 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.6 | 35.8 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.5 | 35.7 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.5 | 35.7 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:07 | 1 | 24.5 | 35.7 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.5 | 35.7 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.5 | 35.7 | 17.4 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.4 | 35.7 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.4 | 35.7 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.4 | 35.6 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:08 | 1 | 24.4 | 35.6 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.4 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.4 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.3 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.3 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.3 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:09 | 1 | 24.3 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.3 | 35.6 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.3 | 35.5 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.3 | 35.5 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.2 | 35.5 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.2 | 35.5 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:10 | 1 | 24.2 | 35.5 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.3 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.2 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.2 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:11 | 1 | 24.2 | 35.5 | 17.2 | 35.5 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 17.2 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 17.2 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 17.1 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 16.9 | 35.5 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 17 | 35.5 | 19 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 17.8 | 35.5 | 18.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:12 | 1 | 24.1 | 35.4 | 19.2 | 35.5 | 18.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:13 | 1 | 24.1 | 35.4 | 20.6 | 35.5 | 17.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:13 | 1 | 24.1 | 35.4 | 22 | 35.5 | 17.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:13 | 1 | 24.1 | 35.4 | 22.3 | 35.4 | 17.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:13 | 1 | 24.1 | 35.4 | 23.2 | 35.4 | 16.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:13 | 1 | 24 | 35.5 | 24.3 | 35.4 | 16 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:13 | 1 | 24 | 35.5 | 25.3 | 35.4 | 16.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:13 | 1 | 23.9 | 35.6 | 26.3 | 35.4 | 17.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 23.7 | 35.6 | 27 | 35.4 | 18.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 23.5 | 35.7 | 27.6 | 35.4 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 23.2 | 35.7 | 28.2 | 35.4 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 22.8 | 35.8 | 28.6 | 35.4 | 23.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 22.4 | 35.9 | 29 | 35.4 | 25 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:14 | 1 | 22 | 36 | 29.3 | 35.4 | 26 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:15 | 1 | 21.4 | 36.1 | 29.5 | 35.4 | 26.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:15 | 1 | 20.9 | 36.2 | 29.7 | 35.4 | 27.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:15 | 1 | 20.3 | 36.2 | 30 | 35.4 | 28.2 | 3.6 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:15 | 1 | 19.9 | 36.3 | 30.1 | 35.4 | 28.4 | 3.7 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 06:15 | 1 | 19.9 | 36.3 | 30.1 | 35.4 | 28.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 06:15 | 1 | 19.7 | 36.3 | 30.1 | 35.4 | 28.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 06:15 | 1 | 19.1 | 36.3 | 29.4 | 35.5 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 06:15 | 1 | 18.5 | 36.4 | 29 | 35.5 | 28.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 06:16 | 1 | 18.2 | 36.4 | 29.2 | 35.5 | 29.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 18.2 | 36.4 | 29.2 | 35.5 | 29.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 18 | 36.4 | 29.3 | 35.5 | 29.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 17.7 | 36.5 | 29.8 | 35.5 | 29.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 17.3 | 36.6 | 30.1 | 35.6 | 30.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 17.1 | 36.6 | 30.3 | 35.6 | 30.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 16.9 | 36.7 | 30.6 | 35.7 | 30.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:16 | 1 | 16.8 | 36.8 | 30.7 | 35.7 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 16.8 | 36.8 | 30.9 | 35.7 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 16.8 | 36.8 | 31 | 35.8 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 16.9 | 36.9 | 31.1 | 35.8 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 17.1 | 36.9 | 31.1 | 35.9 | 31.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 17.3 | 37 | 31.2 | 35.9 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:17 | 1 | 17.6 | 37.1 | 31.2 | 36 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 17.7 | 37.1 | 31.3 | 36 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 18 | 37.1 | 31.3 | 36 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 18.3 | 37.2 | 31.3 | 36.1 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 18.6 | 37.2 | 31.4 | 36.1 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 19 | 37.3 | 31.4 | 36.2 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:18 | 1 | 19.4 | 37.3 | 31.4 | 36.2 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 19.7 | 37.4 | 31.4 | 36.3 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 20.1 | 37.4 | 31.5 | 36.3 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 20.4 | 37.4 | 31.5 | 36.3 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 20.8 | 37.5 | 31.5 | 36.4 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 21.1 | 37.5 | 31.5 | 36.4 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:19 | 1 | 21.6 | 37.5 | 31.5 | 36.4 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:20 | 1 | 21.9 | 37.6 | 31.6 | 36.5 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:20 | 1 | 22 | 37.6 | 31.6 | 36.5 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:20 | 1 | 22.3 | 37.6 | 31.6 | 36.5 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:20 | 1 | 22.6 | 37.6 | 31.6 | 36.5 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:20 | 1 | 23 | 37.7 | 31.4 | 36.6 | 31.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:20 | 1 | 23.4 | 37.7 | 30.5 | 36.6 | 31.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:20 | 1 | 23.7 | 37.7 | 29.6 | 36.6 | 31.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 23.9 | 37.7 | 28.7 | 36.7 | 31.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 24.3 | 37.7 | 27.9 | 36.7 | 31.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 24.6 | 37.7 | 27 | 36.7 | 31.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 24.8 | 37.7 | 26.3 | 36.8 | 32 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 25 | 37.7 | 25.5 | 36.8 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:21 | 1 | 25.2 | 37.7 | 24.9 | 36.8 | 32.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 25.4 | 37.7 | 24.3 | 36.8 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 25.7 | 37.7 | 23.8 | 36.8 | 32.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 25.8 | 37.7 | 23.3 | 36.9 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 25.9 | 37.6 | 22.8 | 36.9 | 32.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 26.1 | 37.6 | 22.4 | 36.9 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:22 | 1 | 26.2 | 37.6 | 22 | 36.9 | 32.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.3 | 37.5 | 21.6 | 36.9 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.4 | 37.5 | 21.2 | 36.9 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.4 | 37.5 | 20.9 | 36.9 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.4 | 37.4 | 20.5 | 36.9 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.5 | 37.4 | 20.3 | 37 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:23 | 1 | 26.5 | 37.3 | 19.9 | 37 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.5 | 37.3 | 19.7 | 37 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.5 | 37.3 | 19.4 | 37 | 32.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.5 | 37.1 | 19.1 | 37 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.5 | 37.1 | 18.8 | 37 | 32.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.5 | 37.1 | 18.7 | 37 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:24 | 1 | 26.4 | 37 | 18.4 | 37 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 26.3 | 37 | 18.2 | 37 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 26.3 | 36.9 | 18 | 37 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 26.2 | 36.8 | 17.7 | 37 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 26.1 | 36.7 | 17.7 | 37 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 26 | 36.7 | 17.5 | 37 | 33 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:25 | 1 | 25.9 | 36.7 | 17.3 | 37 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.8 | 36.6 | 17.1 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.7 | 36.5 | 16.9 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.6 | 36.5 | 16.7 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.5 | 36.4 | 16.5 | 37.1 | 33.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.4 | 36.3 | 16.3 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:26 | 1 | 25.2 | 36.2 | 16.1 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 25.1 | 36.2 | 16 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 25 | 36.1 | 15.8 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 24.9 | 36.1 | 15.7 | 37.1 | 33.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 24.8 | 36 | 15.5 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 24.7 | 35.9 | 15.4 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:27 | 1 | 24.6 | 35.9 | 15.3 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:28 | 1 | 24.5 | 35.8 | 15.1 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:28 | 1 | 24.3 | 35.7 | 14.9 | 37.1 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:28 | 1 | 24.2 | 35.6 | 14.8 | 37.1 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:28 | 1 | 24.1 | 35.5 | 14.7 | 37.1 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 06:28 | 1 | 24 | 35.4 | 14.6 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:28 | 1 | 23.9 | 35.4 | 14.6 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:28 | 1 | 23.8 | 35.3 | 14.3 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 23.8 | 35.2 | 13.9 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 23.6 | 35.1 | 14.8 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 23.4 | 35 | 16.4 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 23.2 | 35 | 18.2 | 37.1 | 33.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 22.9 | 34.9 | 19.9 | 37.1 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:29 | 1 | 22.5 | 34.9 | 21.5 | 37.1 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 22.1 | 34.9 | 23 | 37.1 | 33.5 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 21.7 | 34.8 | 24.4 | 37.2 | 33.6 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 21.1 | 34.8 | 25.5 | 37.2 | 33.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 20.6 | 34.8 | 26.5 | 37.2 | 33.6 | 3.7 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 20 | 34.9 | 27.3 | 37.2 | 33.7 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 06:30 | 1 | 19.9 | 34.9 | 27.4 | 37.2 | 33.7 | 3.5 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 06:30 | 1 | 19.9 | 34.9 | 27.4 | 37.2 | 33.7 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 06:30 | 1 | 19.4 | 34.9 | 27.4 | 37.2 | 33.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 06:31 | 1 | 18.8 | 34.9 | 26.2 | 37.2 | 33.8 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 06:31 | 1 | 18.3 | 35 | 26.9 | 37.2 | 33.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 06:31 | 1 | 18.3 | 35 | 27 | 37.2 | 33.9 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 06:31 | 1 | 18.3 | 35 | 27 | 37.2 | 33.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:31 | 1 | 17.8 | 35.1 | 28 | 37.2 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:31 | 1 | 17.6 | 35.1 | 28.7 | 37.3 | 34 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:31 | 1 | 17.3 | 35.2 | 29.3 | 37.3 | 34.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:31 | 1 | 17.1 | 35.2 | 29.8 | 37.3 | 34.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17 | 35.3 | 30.2 | 37.3 | 34.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17 | 35.3 | 30.5 | 37.3 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17 | 35.4 | 30.7 | 37.3 | 34.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17.1 | 35.5 | 30.9 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17.3 | 35.5 | 31 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:32 | 1 | 17.5 | 35.6 | 31.1 | 37.4 | 34.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 17.6 | 35.6 | 31.2 | 37.4 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 17.9 | 35.7 | 31.2 | 37.4 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 18.2 | 35.8 | 31.2 | 37.4 | 34.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 18.5 | 35.9 | 31.3 | 37.5 | 34.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 18.8 | 35.9 | 31.3 | 37.5 | 34.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:33 | 1 | 19.1 | 35.9 | 31.3 | 37.5 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 19.5 | 36 | 31.4 | 37.5 | 34.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 19.9 | 36 | 31.4 | 37.5 | 35 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 20.3 | 36.1 | 31.4 | 37.5 | 35.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 20.6 | 36.1 | 31.4 | 37.6 | 35.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 21 | 36.2 | 31.5 | 37.6 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:34 | 1 | 21.3 | 36.2 | 31.5 | 37.6 | 35.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:35 | 1 | 21.7 | 36.3 | 31.5 | 37.6 | 35.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 06:35 | 1 | 22 | 36.3 | 31.5 | 37.6 | 35.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:35 | 1 | 22.1 | 36.3 | 31.5 | 37.6 | 35.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:35 | 1 | 22.4 | 36.4 | 31.5 | 37.7 | 35.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:35 | 1 | 22.8 | 36.4 | 31.5 | 37.7 | 34.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:35 | 1 | 23.2 | 36.5 | 31.5 | 37.7 | 32.5 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:35 | 1 | 23.5 | 36.5 | 31.5 | 37.7 | 30.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 23.8 | 36.6 | 31.5 | 37.7 | 29.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 24.1 | 36.7 | 31.5 | 37.7 | 28.9 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 24.4 | 36.7 | 31.5 | 37.7 | 28.1 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 24.6 | 36.7 | 31.5 | 37.7 | 27.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 24.8 | 36.8 | 31.5 | 37.7 | 26.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:36 | 1 | 25.1 | 36.8 | 31.5 | 37.7 | 26.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 25.3 | 36.9 | 31.5 | 37.7 | 25.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 25.4 | 37 | 31.6 | 37.7 | 25.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 25.6 | 37 | 31.6 | 37.7 | 24.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 25.8 | 37.1 | 31.6 | 37.7 | 24.4 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 25.9 | 37.1 | 31.6 | 37.7 | 24 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:37 | 1 | 26 | 37.2 | 31.6 | 37.7 | 23.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.1 | 37.3 | 31.6 | 37.7 | 23.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.1 | 37.3 | 31.6 | 37.6 | 22.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.2 | 37.4 | 31.7 | 37.6 | 22.3 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.3 | 37.4 | 31.7 | 37.6 | 21.7 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.3 | 37.4 | 31.7 | 37.6 | 21.2 | 4.1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
2022-09-08 06:38 | 1 | 26.4 | 37.6 | 31.7 | 37.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:38 | 1 | 26.4 | 37.6 | 31.7 | 37.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.4 | 37.6 | 31.6 | 37.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.4 | 37.6 | 31 | 37.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.5 | 37.6 | 29.7 | 37.5 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.5 | 37.7 | 28.5 | 37.4 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.5 | 37.7 | 27.5 | 37.4 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:39 | 1 | 26.5 | 37.7 | 26.7 | 37.4 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.5 | 37.8 | 26.1 | 37.4 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.6 | 37.8 | 25.6 | 37.3 | 22.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.6 | 37.8 | 25.3 | 37.3 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.6 | 37.9 | 25 | 37.3 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.7 | 37.9 | 24.8 | 37.3 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:40 | 1 | 26.7 | 37.9 | 24.6 | 37.2 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.7 | 37.9 | 24.4 | 37.2 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.8 | 37.9 | 24.2 | 37.2 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.8 | 38 | 24 | 37.2 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.8 | 38 | 23.8 | 37.1 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.9 | 38 | 23.6 | 37.1 | 23 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:41 | 1 | 26.9 | 38 | 23.4 | 37.1 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 26.9 | 38 | 23.2 | 37.1 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 27 | 38 | 23 | 37.1 | 22.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 27 | 38 | 22.8 | 37 | 22.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 27 | 38 | 22.6 | 37 | 22.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 27 | 38 | 22.5 | 37 | 22.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:42 | 1 | 27.1 | 38 | 22.3 | 37 | 22.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 38 | 22.1 | 37 | 22.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 37.9 | 22 | 37 | 22.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 37.9 | 21.8 | 36.9 | 22 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 37.9 | 21.6 | 36.9 | 21.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 37.9 | 21.5 | 36.9 | 21.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:43 | 1 | 27.1 | 37.9 | 21.3 | 36.9 | 21.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.8 | 21.2 | 36.9 | 21.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.8 | 21.1 | 36.8 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.8 | 21 | 36.8 | 21.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.8 | 20.9 | 36.8 | 21.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.8 | 20.7 | 36.8 | 21.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:44 | 1 | 27.1 | 37.7 | 20.6 | 36.7 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27.1 | 37.7 | 20.5 | 36.7 | 21.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27.1 | 37.7 | 20.4 | 36.7 | 21 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27.1 | 37.7 | 20.3 | 36.7 | 20.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27 | 37.7 | 20.2 | 36.7 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27 | 37.6 | 20.1 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:45 | 1 | 27 | 37.6 | 20 | 36.6 | 20.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 27 | 37.6 | 19.9 | 36.6 | 20.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 26.9 | 37.6 | 19.8 | 36.6 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 26.9 | 37.5 | 19.7 | 36.5 | 20.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 26.9 | 37.5 | 19.6 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 26.8 | 37.5 | 19.6 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:46 | 1 | 26.8 | 37.5 | 19.5 | 36.5 | 20.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.7 | 37.4 | 19.3 | 36.5 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.7 | 37.4 | 19.3 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.6 | 37.4 | 19.2 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.6 | 37.4 | 19.2 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.6 | 37.3 | 19.1 | 36.4 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:47 | 1 | 26.5 | 37.3 | 19 | 36.3 | 20.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.5 | 37.3 | 19 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.4 | 37.3 | 18.9 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.3 | 37.2 | 18.9 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.3 | 37.2 | 18.8 | 36.3 | 20.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.3 | 37.2 | 18.8 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:48 | 1 | 26.2 | 37.2 | 18.7 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26.2 | 37.1 | 18.7 | 36.2 | 20.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26.2 | 37.1 | 18.6 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26 | 37.1 | 18.6 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26 | 37 | 18.5 | 36.2 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26 | 37 | 18.5 | 36.1 | 20.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:49 | 1 | 26 | 37 | 18.4 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.9 | 37 | 18.4 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.9 | 36.9 | 18.4 | 36.1 | 20 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.8 | 36.9 | 18.3 | 36.1 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.8 | 36.9 | 18.3 | 36 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.8 | 36.8 | 18.2 | 36 | 19.9 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:50 | 1 | 25.7 | 36.8 | 18.2 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.7 | 36.8 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.6 | 36.7 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.6 | 36.7 | 18.1 | 36 | 19.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.5 | 36.7 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.5 | 36.7 | 18 | 36 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:51 | 1 | 25.5 | 36.6 | 17.9 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.4 | 36.6 | 17.9 | 35.9 | 19.7 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.4 | 36.6 | 17.9 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.3 | 36.5 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.3 | 36.5 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.3 | 36.5 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:52 | 1 | 25.2 | 36.4 | 17.8 | 35.9 | 19.6 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25.2 | 36.4 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25.2 | 36.4 | 17.7 | 35.9 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25.1 | 36.3 | 17.7 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25.1 | 36.3 | 17.6 | 35.8 | 19.5 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25.1 | 36.2 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:53 | 1 | 25 | 36.2 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 25 | 36.2 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 25 | 36.1 | 17.7 | 35.8 | 19.4 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 24.9 | 36.1 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 24.9 | 36.1 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 24.9 | 36 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:54 | 1 | 24.8 | 36 | 17.6 | 35.8 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.8 | 36 | 17.6 | 35.7 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.8 | 36 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.8 | 35.9 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.7 | 35.9 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.7 | 35.9 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:55 | 1 | 24.7 | 35.9 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.7 | 35.8 | 17.5 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.6 | 35.8 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.6 | 35.8 | 17.4 | 35.7 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.6 | 35.8 | 17.4 | 35.7 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.6 | 35.8 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:56 | 1 | 24.6 | 35.8 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.5 | 35.8 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.5 | 35.7 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.5 | 35.7 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.5 | 35.7 | 17.4 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.5 | 35.7 | 17.3 | 35.6 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:57 | 1 | 24.4 | 35.7 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.4 | 35.7 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.4 | 35.7 | 17.3 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.4 | 35.6 | 17.2 | 35.6 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.4 | 35.6 | 17.2 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.4 | 35.6 | 17.2 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:58 | 1 | 24.3 | 35.6 | 17.2 | 35.5 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.3 | 35.6 | 17.2 | 35.5 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.3 | 35.6 | 17.2 | 35.5 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.3 | 35.6 | 17.2 | 35.5 | 19.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.3 | 35.6 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.3 | 35.5 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 06:59 | 1 | 24.2 | 35.5 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.5 | 19.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.4 | 19.1 | 4.4 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.4 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 17.1 | 35.4 | 19.1 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:00 | 1 | 24.2 | 35.5 | 16.9 | 35.4 | 19.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.5 | 16.7 | 35.4 | 20.2 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.5 | 16.4 | 35.4 | 21.6 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.4 | 16.2 | 35.4 | 22.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.4 | 16.2 | 35.4 | 23 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.4 | 15.8 | 35.4 | 24.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:01 | 1 | 24.1 | 35.4 | 15.1 | 35.4 | 25.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:01 | 1 | 24 | 35.4 | 15.6 | 35.4 | 26.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 23.9 | 35.4 | 17.1 | 35.4 | 27.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 23.8 | 35.3 | 18.5 | 35.4 | 27.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 23.5 | 35.3 | 20.1 | 35.4 | 28.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 23.2 | 35.3 | 21.5 | 35.4 | 28.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 22.8 | 35.3 | 22.8 | 35.5 | 29 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:02 | 1 | 22.3 | 35.3 | 24.1 | 35.5 | 29.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:03 | 1 | 21.9 | 35.4 | 25.2 | 35.5 | 29.5 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:03 | 1 | 21.4 | 35.4 | 26.2 | 35.5 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:03 | 1 | 20.8 | 35.5 | 27 | 35.6 | 30 | 3.8 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:03 | 1 | 20.2 | 35.5 | 27.7 | 35.6 | 30.2 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:03 | 1 | 19.9 | 35.6 | 28 | 35.6 | 30.2 | 3.5 | 1 | 1 | 1 | 0 | 1 | 1 | 0
2022-09-08 07:03 | 1 | 19.9 | 35.6 | 28 | 35.6 | 30.2 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 07:03 | 1 | 19.6 | 35.7 | 28.2 | 35.6 | 30.3 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 07:03 | 1 | 19 | 35.7 | 27.7 | 35.7 | 30 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 07:04 | 1 | 18.5 | 35.8 | 28 | 35.7 | 29.8 | 4.4 | 1 | 1 | 1 | 1 | 1 | 1 | 0
2022-09-08 07:04 | 1 | 18.2 | 35.8 | 28.4 | 35.7 | 29.8 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 18.2 | 35.8 | 28.4 | 35.7 | 29.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 17.9 | 35.8 | 28.7 | 35.8 | 30 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 17.6 | 35.9 | 29.2 | 35.8 | 30.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 17.2 | 36 | 29.6 | 35.8 | 30.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 17 | 36 | 29.9 | 35.9 | 30.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:04 | 1 | 16.8 | 36.1 | 30.2 | 35.9 | 30.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 16.7 | 36.1 | 30.3 | 35.9 | 31 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 16.7 | 36.2 | 30.5 | 36 | 31.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 16.6 | 36.3 | 30.7 | 36 | 31.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 16.8 | 36.4 | 30.7 | 36.1 | 31.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 16.9 | 36.4 | 30.8 | 36.1 | 31.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:05 | 1 | 17.1 | 36.5 | 30.9 | 36.1 | 31.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 17.4 | 36.5 | 31 | 36.2 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 17.7 | 36.6 | 31.1 | 36.2 | 31.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 17.8 | 36.7 | 31.2 | 36.2 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 18.1 | 36.7 | 31.2 | 36.3 | 31.9 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 18.4 | 36.7 | 31.2 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:06 | 1 | 18.7 | 36.7 | 31.3 | 36.3 | 32 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 19.1 | 36.8 | 31.3 | 36.4 | 32.1 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 19.4 | 36.9 | 31.3 | 36.4 | 32.2 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 19.7 | 36.9 | 31.4 | 36.4 | 32.3 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 20.1 | 36.9 | 31.4 | 36.5 | 32.4 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 20.4 | 37 | 31.5 | 36.5 | 32.5 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:07 | 1 | 20.7 | 37 | 31.5 | 36.5 | 32.6 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:08 | 1 | 21.1 | 37.1 | 31.6 | 36.6 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:08 | 1 | 21.4 | 37.2 | 31.6 | 36.6 | 32.7 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:08 | 1 | 21.8 | 37.2 | 31.6 | 36.6 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:08 | 1 | 22 | 37.2 | 31.6 | 36.7 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:08 | 1 | 22.2 | 37.2 | 31.6 | 36.7 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:08 | 1 | 22.5 | 37.2 | 31.6 | 36.7 | 32.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:08 | 1 | 22.8 | 37.3 | 31.6 | 36.7 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.2 | 37.3 | 31.5 | 36.8 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.4 | 37.3 | 31.5 | 36.8 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.6 | 37.3 | 31.5 | 36.8 | 31.7 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.7 | 37.4 | 31.5 | 36.8 | 31.8 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.7 | 37.4 | 31.5 | 36.9 | 31.9 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:09 | 1 | 23.6 | 37.4 | 31.5 | 36.9 | 32.1 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 23.4 | 37.4 | 31.5 | 36.9 | 32.2 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 23.2 | 37.4 | 31.5 | 36.9 | 32.3 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 22.8 | 37.4 | 31.5 | 36.9 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 22.4 | 37.5 | 31.6 | 37 | 32.4 | 4.4 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 21.9 | 37.5 | 31.6 | 37 | 32.5 | 4.3 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:10 | 1 | 21.4 | 37.5 | 31.6 | 37 | 32.6 | 4.1 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:11 | 1 | 21 | 37.5 | 31.6 | 37 | 32.6 | 3.9 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:11 | 1 | 20.4 | 37.5 | 31.6 | 37 | 32.7 | 3.6 | 1 | 1 | 1 | 1 | 0 | 0 | 1
2022-09-08 07:11 | 1 | 19.9 | 37.5 | 31.7 | 37.1 | 32.8 | 3.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0
2022-09-08 07:11 | 1 | 19.9 | 37.5 | 31.7 | 37.1 | 32.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 07:11 | 1 | 19.8 | 37.5 | 31.7 | 37.1 | 32.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 07:11 | 1 | 19.2 | 37.5 | 31.7 | 37.1 | 32.8 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 07:11 | 1 | 18.6 | 37.5 | 31.7 | 37.1 | 32.9 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0
2022-09-08 07:11 | 1 | 18.3 | 37.6 | 31.7 | 37.1 | 32.9 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
2022-09-08 07:11 | 1 | 18.3 | 37.6 | 31.7 | 37.1 | 32.9 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:11 | 1 | 18.1 | 37.6 | 31.7 | 37.1 | 32.9 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 17.7 | 37.6 | 31.8 | 37.1 | 33.1 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 17.5 | 37.6 | 31.9 | 37.2 | 33.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 17.2 | 37.6 | 32.2 | 37.2 | 33.6 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 17 | 37.6 | 32.5 | 37.2 | 33.9 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 17 | 37.6 | 32.7 | 37.2 | 34 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:12 | 1 | 16.9 | 37.6 | 32.9 | 37.2 | 34.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 16.9 | 37.6 | 32.9 | 37.2 | 34.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 17.1 | 37.7 | 32.9 | 37.3 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 17.3 | 37.7 | 32.9 | 37.3 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 17.5 | 37.7 | 32.9 | 37.3 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 17.6 | 37.7 | 32.9 | 37.3 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:13 | 1 | 17.9 | 37.7 | 33 | 37.3 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:14 | 1 | 18.1 | 37.7 | 33 | 37.4 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:14 | 1 | 18.5 | 37.7 | 33 | 37.4 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 0
2022-09-08 07:14 | 1 | 18.7 | 37.7 | 33.1 | 37.4 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:14 | 1 | 18.8 | 37.7 | 33.1 | 37.4 | 34.3 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:14 | 1 | 19.2 | 37.7 | 33 | 37.4 | 34.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:14 | 1 | 19.6 | 37.7 | 32 | 37.4 | 33.6 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:14 | 1 | 19.9 | 37.7 | 31.2 | 37.5 | 33.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 20.2 | 37.7 | 30.6 | 37.5 | 33 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 20.6 | 37.7 | 30 | 37.5 | 33.1 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 20.9 | 37.7 | 29.1 | 37.5 | 33.2 | 4 | 1 | 1 | 1 | 0 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 21.1 | 37.7 | 28.4 | 37.5 | 33.3 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 21.1 | 37.7 | 28.3 | 37.5 | 33.4 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1
2022-09-08 07:15 | 1 | 21.5 | 37.7 | 27.3 | 37.5 | 33.5 | 4.1 | 1 | 1 | 1 | 1 | 1 | 0 | 1